## Cover
Powercor
Regulatory proposal 2026-31
Flood resilience
| Model number: | 5.02
2025-01-31
13

## Summary
Powercor
Lines flood resilience program
SUMMARY
RESULTS
[5 empty] | PV of costs | PV of benefits | NPV |  | Total capital cost
| Option |  |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30 |  | 2026-06-30
| Option 1 (base case) | No change to existing practices |  |  | 0 | 0 | 0 |  | 0
| Option 2 | Install taller poles |  |  | -12.0175 | 81.3071 | 69.2896 |  | 19.613
NPV
| Preferred option: |  | 2026-06-30
| Option 2 | Install taller poles | 69.2896
EXPENDITURE
Capital expenditure 2026-31
| 2026-06-30 |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Install taller poles |  | 3.9226 | 3.9226 | 3.9226 | 3.9226 | 3.9226 |  | 19.613
SENSITIVITIES
NPV
2026-06-30
| Option 2 |  | 69.2896
| Capex 10% higher |  | 68.0916
| Capex 10% lower |  | 70.3571
| Total benefits 10% higher |  | 77.2796
| Total benefits 10% lower |  | 61.1692
| Capex 10% higher & Total benefits 10% lower |  | 60.0364
End |  |  | . | . | . | . | . | . | .

## Total
Powercor
Lines flood resilience program
| Total number of identified spans identified |  |  | 726
| Number of spans that are part of SubT loop |  |  | 17
| Total number of spans assessed |  |  | 709
| Number of spans where option 2 is preferred option |  |  | 483
| Taller concrete poles required |  |  | 507
| Taller wood poles required |  |  | 328
| Total unique poles to be remediated |  |  | 835
| Total capital cost for feeders where option 2 is preferred |  | 2023-12-31 | 18629179.5849
| Overlapped wood poles | 46 |  | 867836.3534
| Overlapped concrete poles | 5 |  | 138172.4648
| Total 2026-31 program capex |  | 2023-12-31 | 17623170.7668
| Expenditure per year over 5 years |  | 2023-12-31 | 3524634.1534
| Expenditure per year over 5 years |  | 2026-06-30 | 3922609.9233

## Assumptions
Powercor
Lines flood resilience program
Project
|  | Business: |  | Powercor
|  | Descripton: |  | Lines flood resilience program
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Install taller poles
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Model start year |  |  |  | 2026-27 | [start]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions value date |  |  |  | 2023-06-30
Costs
[6 empty] | Wood pole | Concrete pole
|  | Average installed cost per pole |  | 2023-12-31 | 2023-12-31 | 18866.0077 | 27634.493
|  | Asset life (years) |  |  |  | 60
Demand
|  | Average to max. demand ratio |  |  | 50% | 50% | based on ZSS network average
|  | Demand growth from FY35 |  | pa |  | 0%
VCR
|  | Average outage (hours) |  |  |  | 20.2708
Outage hours tiers for VNR
|  | From: | To
|  | 12 | 24 |  |  | 8.2708
|  | 24 | 72 |  |  | 0
|  | 72 | 1000 |  |  | 0
Other risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 151432.8174 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 88.3577 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Demand
Powercor
Lines flood resilience program
| Feeder | SubT | Weighted average demand (MW, max of summer or winter)
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
| AC024 | FALSE | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19
| AC025 | FALSE | 7.72 | 7.83 | 8 | 8.16 | 8.22 | 8.28 | 8.45 | 8.67 | 8.76 | 8.76 | 8.76 | 8.76 | 8.76 | 8.76 | 8.76 | 8.76 | 8.76 | 8.76 | 8.76 | 8.76
| AC031 | FALSE | 2.16 | 2.17 | 2.19 | 2.2 | 2.21 | 2.22 | 2.24 | 2.26 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27
| AL002 | FALSE | 3.02 | 3.04 | 3.07 | 3.1 | 3.11 | 3.12 | 3.16 | 3.21 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22
| AL006 | FALSE | 4.76 | 4.86 | 4.96 | 5.06 | 5.12 | 5.2 | 5.32 | 5.44 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52
| AL007 | FALSE | 2.89 | 2.91 | 2.95 | 2.98 | 3.01 | 3.04 | 3.09 | 3.15 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
| AL011 | FALSE | 3.64 | 3.66 | 3.69 | 3.7 | 3.71 | 3.73 | 3.76 | 3.79 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81
| AL012 | FALSE | 4.33 | 4.39 | 4.44 | 4.5 | 4.54 | 4.58 | 4.65 | 4.71 | 4.74 | 4.74 | 4.74 | 4.74 | 4.74 | 4.74 | 4.74 | 4.74 | 4.74 | 4.74 | 4.74 | 4.74
| AL013 | FALSE | 1.36 | 1.36 | 1.37 | 1.37 | 1.38 | 1.38 | 1.38 | 1.39 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| AL014 | FALSE | 8.16 | 8.28 | 8.42 | 8.53 | 8.6 | 8.69 | 8.86 | 9.02 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1
| AP001 | FALSE | 3.68 | 3.77 | 3.88 | 3.97 | 4.06 | 4.14 | 4.25 | 4.36 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45
| AP003 | FALSE | 4.76 | 4.89 | 5.04 | 5.16 | 5.27 | 5.39 | 5.55 | 5.7 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8
| AP005 | FALSE | 5.72 | 5.93 | 6.11 | 6.29 | 6.45 | 6.64 | 6.89 | 7.1 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22
| AP006 | FALSE | 4.34 | 4.42 | 4.51 | 4.59 | 4.65 | 4.72 | 4.8 | 4.9 | 4.97 | 4.97 | 4.97 | 4.97 | 4.97 | 4.97 | 4.97 | 4.97 | 4.97 | 4.97 | 4.97 | 4.97
| AP007 | FALSE | 2.8 | 2.88 | 2.96 | 3.02 | 3.08 | 3.15 | 3.24 | 3.33 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
| AP008 | FALSE | 6.84 | 7.06 | 7.33 | 7.58 | 7.79 | 7.98 | 8.24 | 8.52 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75
| AP009 | FALSE | 6.21 | 6.31 | 6.43 | 6.54 | 6.63 | 6.71 | 6.83 | 6.95 | 7.03 | 7.03 | 7.03 | 7.03 | 7.03 | 7.03 | 7.03 | 7.03 | 7.03 | 7.03 | 7.03 | 7.03
| AP011 | FALSE | 2.52 | 2.57 | 2.63 | 2.69 | 2.73 | 2.78 | 2.85 | 2.91 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96
| AP012 | FALSE | 1.3 | 1.33 | 1.35 | 1.38 | 1.4 | 1.42 | 1.44 | 1.47 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49
| AP013 | FALSE | 2.51 | 2.6 | 2.7 | 2.79 | 2.86 | 2.94 | 3.03 | 3.14 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| AP014 | FALSE | 4.24 | 4.32 | 4.41 | 4.51 | 4.57 | 4.64 | 4.74 | 4.82 | 4.88 | 4.88 | 4.88 | 4.88 | 4.88 | 4.88 | 4.88 | 4.88 | 4.88 | 4.88 | 4.88 | 4.88
| AP015 | FALSE | 3.87 | 4 | 4.15 | 4.29 | 4.41 | 4.53 | 4.67 | 4.86 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
| AP017 | FALSE | 5.42 | 5.52 | 5.64 | 5.74 | 5.81 | 5.88 | 5.99 | 6.11 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18
| AP018 | FALSE | 3.15 | 3.19 | 3.23 | 3.28 | 3.32 | 3.37 | 3.41 | 3.46 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52
| AP019 | FALSE | 5.42 | 5.47 | 5.49 | 5.52 | 5.53 | 5.54 | 5.56 | 5.58 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
| AR002 | FALSE | 2.91 | 2.92 | 2.95 | 2.98 | 3 | 3.03 | 3.06 | 3.1 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12
| AR003 | FALSE | 4.93 | 4.99 | 5.06 | 5.12 | 5.15 | 5.19 | 5.25 | 5.34 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36
| AR004 | FALSE | 4.91 | 4.99 | 5.08 | 5.17 | 5.22 | 5.28 | 5.36 | 5.48 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54
| AR005 | FALSE | 3.06 | 3.08 | 3.13 | 3.16 | 3.18 | 3.2 | 3.25 | 3.3 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32
| AR006 | FALSE | 5.17 | 5.24 | 5.31 | 5.37 | 5.42 | 5.47 | 5.53 | 5.6 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65
| AR007 | FALSE | 4.29 | 4.31 | 4.33 | 4.35 | 4.34 | 4.35 | 4.38 | 4.43 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44
| AR009 | FALSE | 3.27 | 3.31 | 3.36 | 3.4 | 3.43 | 3.47 | 3.52 | 3.58 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62
| AR010 | FALSE | 4.72 | 4.84 | 4.99 | 5.12 | 5.22 | 5.33 | 5.49 | 5.64 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
| AR011 | FALSE | 3.99 | 4.06 | 4.14 | 4.19 | 4.23 | 4.29 | 4.4 | 4.47 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49
| AR012 | FALSE | 4.66 | 4.73 | 4.82 | 4.9 | 4.95 | 5.02 | 5.11 | 5.2 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25
| AR013 | FALSE | 2.5 | 2.52 | 2.55 | 2.57 | 2.57 | 2.58 | 2.61 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63
| ART023 | FALSE | 5.5 | 5.45 | 5.44 | 5.42 | 5.38 | 5.35 | 5.34 | 5.32 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29
| ART031 | FALSE | 3.98 | 3.95 | 3.96 | 3.95 | 3.94 | 3.91 | 3.92 | 3.94 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93
| ART033 | FALSE | 6.75 | 6.8 | 6.9 | 6.94 | 6.95 | 6.97 | 7.06 | 7.17 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14
| ART034 | FALSE | 5.45 | 5.46 | 5.49 | 5.51 | 5.5 | 5.49 | 5.52 | 5.57 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56
| AWT011 | FALSE | 1.33 | 3.09 | 4.66 | 5.28 | 5.91 | 6.4 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
| AWT021 | FALSE | 1.33 | 3.09 | 4.66 | 5.28 | 5.91 | 6.4 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
| B002 | FALSE | 2.62 | 2.68 | 2.74 | 2.79 | 2.85 | 2.9 | 2.97 | 3.02 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07
| B003 | FALSE | 2.25 | 2.3 | 2.37 | 2.43 | 2.47 | 2.51 | 2.58 | 2.67 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7
| B004 | FALSE | 3.61 | 3.74 | 3.89 | 4.01 | 4.12 | 4.24 | 4.4 | 4.56 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67
| B005 | FALSE | 3.58 | 3.62 | 3.66 | 3.69 | 3.69 | 3.7 | 3.75 | 3.81 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
| B006 | FALSE | 2.37 | 2.41 | 2.45 | 2.49 | 2.53 | 2.56 | 2.6 | 2.65 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69
| B011 | FALSE | 4.69 | 4.73 | 4.78 | 4.83 | 4.85 | 4.88 | 4.93 | 4.97 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99
| B012 | FALSE | 15.21 | 15.47 | 15.74 | 15.98 | 16.19 | 16.43 | 16.71 | 16.99 | 17.24 | 17.24 | 17.24 | 17.24 | 17.24 | 17.24 | 17.24 | 17.24 | 17.24 | 17.24 | 17.24 | 17.24
| B013 | FALSE | 3.46 | 3.54 | 3.65 | 3.72 | 3.8 | 3.88 | 3.98 | 4.09 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16
| B014 | FALSE | 2.7 | 2.77 | 2.85 | 2.92 | 2.98 | 3.04 | 3.11 | 3.19 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26
| B015 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| B016 | FALSE | 2.19 | 2.22 | 2.26 | 2.28 | 2.3 | 2.34 | 2.37 | 2.41 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43
| B021 | FALSE | 5.13 | 5.19 | 5.26 | 5.33 | 5.38 | 5.43 | 5.5 | 5.54 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57
| B025 | FALSE | 2.88 | 2.95 | 3.03 | 3.11 | 3.17 | 3.24 | 3.32 | 3.41 | 3.47 | 3.47 | 3.47 | 3.47 | 3.47 | 3.47 | 3.47 | 3.47 | 3.47 | 3.47 | 3.47 | 3.47
| B026_B027 | FALSE | 3.96 | 4.05 | 4.19 | 4.3 | 4.33 | 4.39 | 4.54 | 4.71 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72
| BAE011 | FALSE | 12.94 | 13.1 | 13.34 | 13.57 | 13.69 | 13.83 | 14.08 | 14.3 | 14.49 | 14.49 | 14.49 | 14.49 | 14.49 | 14.49 | 14.49 | 14.49 | 14.49 | 14.49 | 14.49 | 14.49
| BAE012 | FALSE | 12.45 | 12.64 | 12.85 | 13.02 | 13.13 | 13.3 | 13.59 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77
| BAE021 | FALSE | 0 | 0 | 3.89 | 3.97 | 4 | 4.04 | 4.13 | 4.22 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
| BAE022 | FALSE | 12.5 | 12.85 | 13.24 | 13.6 | 13.88 | 14.19 | 14.57 | 14.99 | 15.29 | 15.29 | 15.29 | 15.29 | 15.29 | 15.29 | 15.29 | 15.29 | 15.29 | 15.29 | 15.29 | 15.29
| BAN001 | FALSE | 6.35 | 6.35 | 6.37 | 6.35 | 6.33 | 6.33 | 6.37 | 6.41 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38
| BAN002 | FALSE | 10.43 | 10.48 | 10.56 | 10.6 | 10.6 | 10.67 | 10.74 | 10.79 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
| BAN003 | FALSE | 10.27 | 10.5 | 10.83 | 11.06 | 11.24 | 11.47 | 11.82 | 12.1 | 12.23 | 12.23 | 12.23 | 12.23 | 12.23 | 12.23 | 12.23 | 12.23 | 12.23 | 12.23 | 12.23 | 12.23
| BAN004 | FALSE | 10.27 | 10.27 | 10.33 | 10.32 | 10.31 | 10.33 | 10.42 | 10.47 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45
| BAN005 | FALSE | 8.38 | 8.3 | 8.2 | 8.13 | 8.05 | 7.96 | 7.9 | 7.91 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89
| BAN006 | FALSE | 11.1 | 11.24 | 11.41 | 11.58 | 11.61 | 11.71 | 11.9 | 12.16 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29
| BAN007 | FALSE | 10.68 | 1.1 | 1.12 | 1.13 | 1.14 | 1.15 | 1.18 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19
| BAN008 | FALSE | 9.1 | 0.09 | 0.09 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| BAN009 | FALSE | 10.6 | 10.61 | 10.67 | 10.75 | 10.72 | 10.73 | 10.81 | 10.94 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01
| BAN011 | FALSE | 14.96 | 15.28 | 15.76 | 16.21 | 16.36 | 16.52 | 17.01 | 17.65 | 17.84 | 17.84 | 17.84 | 17.84 | 17.84 | 17.84 | 17.84 | 17.84 | 17.84 | 17.84 | 17.84 | 17.84
| BAN013 | FALSE | 11.37 | 11.52 | 11.73 | 11.93 | 12.11 | 12.35 | 12.68 | 12.95 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11
| BAN015 | FALSE | 13.16 | 9.37 | 9.56 | 9.72 | 9.79 | 9.89 | 10.06 | 10.27 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45 | 10.45
| BAS011 | FALSE | 21.47 | 13 | 13.31 | 13.59 | 13.77 | 13.97 | 14.3 | 14.65 | 14.84 | 14.84 | 14.84 | 14.84 | 14.84 | 14.84 | 14.84 | 14.84 | 14.84 | 14.84 | 14.84 | 14.84
| BAS012 | FALSE | 7.47 | 6.46 | 6.49 | 6.5 | 6.49 | 6.53 | 6.57 | 6.61 | 6.62 | 6.62 | 6.62 | 6.62 | 6.62 | 6.62 | 6.62 | 6.62 | 6.62 | 6.62 | 6.62 | 6.62
| BAS014 | FALSE | 9.89 | 16.82 | 18.53 | 18.35 | 18.14 | 17.97 | 17.84 | 17.73 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
| BAS021 | FALSE | 5.79 | 5.87 | 5.99 | 6.08 | 6.14 | 6.25 | 6.38 | 6.5 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57
| BAS022 | FALSE | 13.04 | 13.24 | 13.49 | 9.81 | 9.88 | 9.99 | 10.2 | 10.43 | 10.62 | 10.62 | 10.62 | 10.62 | 10.62 | 10.62 | 10.62 | 10.62 | 10.62 | 10.62 | 10.62 | 10.62
| BAS023 | FALSE | 8.42 | 2.15 | 2.19 | 2.23 | 2.25 | 2.29 | 2.34 | 2.38 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
| BAS024 | FALSE | 16.02 | 10.44 | 10.77 | 11.09 | 11.35 | 11.64 | 11.99 | 12.38 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67
| BAS031 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS032 | FALSE | 12.28 | 12.32 | 12.5 | 12.61 | 12.71 | 12.86 | 13.07 | 13.33 | 13.49 | 13.49 | 13.49 | 13.49 | 13.49 | 13.49 | 13.49 | 13.49 | 13.49 | 13.49 | 13.49 | 13.49
| BAS033 | FALSE | 10.56 | 8.66 | 8.87 | 9.09 | 9.28 | 9.51 | 9.83 | 10.17 | 10.44 | 10.44 | 10.44 | 10.44 | 10.44 | 10.44 | 10.44 | 10.44 | 10.44 | 10.44 | 10.44 | 10.44
| BAS034 | FALSE | 11.2 | 11.34 | 11.51 | 11.65 | 11.74 | 11.85 | 12.02 | 12.3 | 12.39 | 12.39 | 12.39 | 12.39 | 12.39 | 12.39 | 12.39 | 12.39 | 12.39 | 12.39 | 12.39 | 12.39
| BBD013 | FALSE | 12.3 | 12.45 | 12.69 | 12.9 | 12.93 | 13 | 13.25 | 13.58 | 13.62 | 13.62 | 13.62 | 13.62 | 13.62 | 13.62 | 13.62 | 13.62 | 13.62 | 13.62 | 13.62 | 13.62
| BBD014 | FALSE | 12.34 | 12.24 | 12.19 | 12.12 | 11.98 | 11.87 | 11.85 | 11.86 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74
| BBD021 | FALSE | 8.74 | 8.78 | 8.9 | 8.98 | 8.96 | 8.96 | 9.09 | 9.26 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
| BBD022 | FALSE | 6.97 | 6.9 | 6.86 | 6.81 | 6.72 | 6.65 | 6.62 | 6.61 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55
| BC002 | FALSE | 4.99 | 6.96 | 7.62 | 7.65 | 7.66 | 7.65 | 7.64 | 7.64 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59
| BC003 | FALSE | 7.79 | 5.05 | 5.11 | 5.16 | 5.17 | 5.17 | 5.21 | 5.27 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26
| BC006 | FALSE | 2.67 | 2.74 | 2.81 | 2.86 | 2.91 | 2.97 | 3.05 | 3.12 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17
| BC007 | FALSE | 5.83 | 5.8 | 5.82 | 5.81 | 5.8 | 5.8 | 5.81 | 5.85 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82
| BC011 | FALSE | 3.06 | 3.11 | 3.18 | 3.24 | 3.29 | 3.33 | 3.4 | 3.47 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
| BC012 | FALSE | 4.16 | 4.18 | 4.24 | 4.29 | 4.33 | 4.36 | 4.41 | 4.48 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53
| BC013 | FALSE | 4.43 | 4.52 | 4.63 | 4.7 | 4.75 | 4.82 | 4.93 | 5.06 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09
| BC014 | FALSE | 2.53 | 2.58 | 2.64 | 2.69 | 2.74 | 2.79 | 2.84 | 2.9 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95
| BC015 | FALSE | 3.36 | 3.49 | 3.6 | 3.73 | 3.84 | 3.94 | 4.12 | 4.25 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32
| BC019 | FALSE | 6.31 | 6.27 | 6.24 | 6.21 | 6.17 | 6.12 | 6.1 | 6.08 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04
| BC020 | FALSE | 2.41 | 2.46 | 2.52 | 2.54 | 2.58 | 2.62 | 2.68 | 2.74 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78
| BC022 | FALSE | 2.29 | 2.35 | 2.42 | 2.48 | 2.52 | 2.57 | 2.64 | 2.72 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76
| BC024 | FALSE | 6.16 | 6.18 | 6.21 | 6.23 | 6.22 | 6.25 | 6.27 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33
| BET001 | FALSE | 14.77 | 14.87 | 15.07 | 15.24 | 15.36 | 15.47 | 15.68 | 15.94 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06
| BET002 | FALSE | 7 | 7.06 | 7.16 | 7.24 | 7.29 | 7.33 | 7.44 | 7.57 | 7.63 | 7.63 | 7.63 | 7.63 | 7.63 | 7.63 | 7.63 | 7.63 | 7.63 | 7.63 | 7.63 | 7.63
| BET003 | FALSE | 3.01 | 3 | 2.98 | 2.97 | 2.96 | 2.94 | 2.94 | 2.94 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92
| BET004 | FALSE | 9.93 | 10.06 | 10.22 | 10.34 | 10.45 | 10.53 | 10.71 | 10.9 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02
| BET005 | FALSE | 11.87 | 12.08 | 12.35 | 12.6 | 12.73 | 12.91 | 13.21 | 13.57 | 13.75 | 13.75 | 13.75 | 13.75 | 13.75 | 13.75 | 13.75 | 13.75 | 13.75 | 13.75 | 13.75 | 13.75
| BET006 | FALSE | 16.08 | 16.3 | 16.56 | 16.83 | 16.98 | 17.16 | 17.48 | 17.83 | 18.07 | 18.07 | 18.07 | 18.07 | 18.07 | 18.07 | 18.07 | 18.07 | 18.07 | 18.07 | 18.07 | 18.07
| BET007 | FALSE | 13.84 | 14.18 | 14.53 | 14.83 | 15.06 | 15.31 | 15.69 | 16.15 | 16.35 | 16.35 | 16.35 | 16.35 | 16.35 | 16.35 | 16.35 | 16.35 | 16.35 | 16.35 | 16.35 | 16.35
| BET008 | FALSE | 9.84 | 9.85 | 9.91 | 9.98 | 10 | 10.05 | 10.14 | 10.23 | 10.26 | 10.26 | 10.26 | 10.26 | 10.26 | 10.26 | 10.26 | 10.26 | 10.26 | 10.26 | 10.26 | 10.26
| BGO011 | FALSE | 3.95 | 3.93 | 3.92 | 3.9 | 3.87 | 3.84 | 3.83 | 3.82 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86
| BGO012 | FALSE | 7.16 | 7.17 | 7.21 | 7.22 | 7.22 | 7.22 | 7.28 | 7.35 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34
| BGO013 | FALSE | 7.45 | 7.63 | 7.85 | 8.03 | 8.2 | 8.38 | 8.62 | 8.88 | 9.07 | 9.07 | 9.07 | 9.07 | 9.07 | 9.07 | 9.07 | 9.07 | 9.07 | 9.07 | 9.07 | 9.07
| BGO014 | FALSE | 3.3 | 3.27 | 3.25 | 3.23 | 3.2 | 3.17 | 3.14 | 3.13 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12
| BGO022 | FALSE | 9.53 | 9.58 | 9.68 | 9.73 | 9.75 | 9.79 | 9.9 | 10.05 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08
| BGO023 | FALSE | 12.05 | 12.25 | 12.51 | 12.71 | 12.88 | 13.04 | 13.3 | 13.63 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84
| BGO024 | FALSE | 6.15 | 6.09 | 6.08 | 6.05 | 5.99 | 5.92 | 5.88 | 5.85 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75
| BK002 | FALSE | 3.05 | 3.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK003 | FALSE | 1.6 | 1.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK004 | FALSE | 2.61 | 2.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK005 | FALSE | 1.3 | 1.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK006 | FALSE | 0.88 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK007 | FALSE | 2.17 | 2.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK009 | FALSE | 2.3 | 2.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK010 | FALSE | 2.74 | 2.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK011 | FALSE | 3.32 | 3.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT016 | FALSE | 13.01 | 13.18 | 13.4 | 13.59 | 13.7 | 13.85 | 14.08 | 14.32 | 14.44 | 14.44 | 14.44 | 14.44 | 14.44 | 14.44 | 14.44 | 14.44 | 14.44 | 14.44 | 14.44 | 14.44
| BLT017 | FALSE | 10.08 | 10.17 | 10.27 | 10.39 | 10.46 | 10.52 | 10.65 | 10.82 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88
| BLT020 | FALSE | 8.36 | 8.59 | 8.82 | 9.04 | 9.24 | 9.44 | 9.66 | 9.88 | 10.09 | 10.09 | 10.09 | 10.09 | 10.09 | 10.09 | 10.09 | 10.09 | 10.09 | 10.09 | 10.09 | 10.09
| BLT021 | FALSE | 8.08 | 8.11 | 8.17 | 8.23 | 8.24 | 8.25 | 8.31 | 8.4 | 8.41 | 8.41 | 8.41 | 8.41 | 8.41 | 8.41 | 8.41 | 8.41 | 8.41 | 8.41 | 8.41 | 8.41
| BLT022 | FALSE | 8.06 | 8.17 | 8.36 | 8.44 | 8.44 | 8.53 | 8.73 | 8.91 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88
| BLT030 | FALSE | 7.1 | 7.18 | 7.28 | 7.39 | 7.43 | 7.49 | 7.6 | 7.75 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83
| BLT031 | FALSE | 2.25 | 2.27 | 2.31 | 2.34 | 2.35 | 2.36 | 2.4 | 2.45 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46
| BMH003 | FALSE | 7.66 | 7.92 | 8.19 | 8.41 | 8.61 | 8.86 | 9.23 | 9.53 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71
| BMH004 | FALSE | 8.99 | 9.32 | 9.72 | 10.07 | 10.39 | 10.73 | 11.19 | 11.74 | 12.15 | 12.15 | 12.15 | 12.15 | 12.15 | 12.15 | 12.15 | 12.15 | 12.15 | 12.15 | 12.15 | 12.15
| BMH005 | FALSE | 11.18 | 11.57 | 12.03 | 12.45 | 12.82 | 13.27 | 13.78 | 14.28 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72
| BMH006 | FALSE | 5.18 | 5.19 | 5.24 | 5.31 | 5.34 | 5.37 | 5.48 | 5.58 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65 | 5.65
| BQ011 | FALSE | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
| BQ012 | FALSE | 4.46 | 4.47 | 4.48 | 4.47 | 4.46 | 4.47 | 4.49 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51
| BQ013 | FALSE | 4.69 | 4.72 | 4.75 | 4.79 | 4.81 | 4.84 | 4.89 | 4.94 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99
| BQ014 | FALSE | 3.45 | 3.46 | 3.48 | 3.49 | 3.48 | 3.49 | 3.51 | 3.55 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56
| BQ017 | FALSE | 10.34 | 10.59 | 10.75 | 10.87 | 10.93 | 10.93 | 11.11 | 11.35 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41
| BQ021 | FALSE | 3.58 | 3.59 | 3.6 | 3.61 | 3.61 | 3.61 | 3.62 | 3.63 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64
| BQ024 | FALSE | 3.23 | 3.22 | 3.22 | 3.21 | 3.2 | 3.19 | 3.2 | 3.21 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22
| BQ025 | FALSE | 3.25 | 3.24 | 3.24 | 3.24 | 3.23 | 3.23 | 3.24 | 3.26 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27
| BQ026 | FALSE | 6.66 | 6.82 | 7.06 | 7.24 | 7.3 | 7.39 | 7.64 | 7.93 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96
| BQ027 | FALSE | 3.36 | 3.41 | 3.45 | 3.48 | 3.52 | 3.57 | 3.62 | 3.67 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69
| BQ032 | FALSE | 4.58 | 4.6 | 4.63 | 4.65 | 4.64 | 4.65 | 4.7 | 4.76 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77
| BQ034 | FALSE | 4.64 | 4.63 | 4.62 | 4.6 | 4.58 | 4.56 | 4.56 | 4.56 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55
| BQ035 | FALSE | 5.34 | 5.31 | 5.28 | 5.25 | 5.22 | 5.19 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17
| BQ036 | FALSE | 4.58 | 4.63 | 4.6 | 4.61 | 4.61 | 4.63 | 4.67 | 4.7 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69
| BQ037 | FALSE | 0.96 | 0.96 | 0.95 | 0.95 | 0.95 | 0.94 | 0.94 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
| BQ041 | FALSE | 4.78 | 4.78 | 4.82 | 4.85 | 4.87 | 4.91 | 4.97 | 5.06 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05
| BQ043 | FALSE | 4.67 | 4.65 | 4.64 | 4.62 | 4.6 | 4.59 | 4.59 | 4.6 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61
| BQ046 | FALSE | 1.73 | 1.77 | 1.83 | 1.88 | 1.89 | 1.91 | 1.98 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05
| BQ047 | FALSE | 8.68 | 9.1 | 9.26 | 9.37 | 9.39 | 9.43 | 9.59 | 9.77 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
| BQ051 | FALSE | 4.83 | 4.91 | 4.98 | 5.01 | 5.04 | 5.09 | 5.18 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25
| BQ052 | FALSE | 3.65 | 3.63 | 3.62 | 3.6 | 3.58 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57
| BQ053 | FALSE | 4.69 | 4.67 | 4.67 | 4.66 | 4.64 | 4.63 | 4.63 | 4.63 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62
| BQ056 | FALSE | 4.63 | 4.8 | 4.95 | 5.09 | 5.22 | 5.37 | 5.56 | 5.71 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82
| BQ057 | FALSE | 2.92 | 2.95 | 2.98 | 3 | 3 | 3.01 | 3.04 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08
| BQ061 | FALSE | 4.33 | 4.3 | 4.28 | 4.26 | 4.23 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21
| BQ062 | FALSE | 8.52 | 8.46 | 8.42 | 8.37 | 8.31 | 8.28 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27
| BQ065 | FALSE | 5.17 | 5.14 | 5.1 | 5.07 | 5.05 | 5 | 5.01 | 5.04 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05
| BQ066 | FALSE | 1.96 | 2.01 | 2.08 | 2.13 | 2.14 | 2.18 | 2.25 | 2.34 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35
| BQ067 | FALSE | 7.87 | 8 | 8.2 | 8.35 | 8.4 | 8.48 | 8.69 | 8.94 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98
| BW021 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001 | FALSE | 8.76 | 8.8 | 8.85 | 8.93 | 8.93 | 8.93 | 9.04 | 9.18 | 9.17 | 9.17 | 9.17 | 9.17 | 9.17 | 9.17 | 9.17 | 9.17 | 9.17 | 9.17 | 9.17 | 9.17
| CDN002 | FALSE | 2.06 | 2.1 | 2.15 | 2.2 | 2.21 | 2.22 | 2.28 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35
| CDN003 | FALSE | 3.53 | 3.51 | 3.51 | 3.49 | 3.46 | 3.43 | 3.42 | 3.4 | 3.37 | 3.37 | 3.37 | 3.37 | 3.37 | 3.37 | 3.37 | 3.37 | 3.37 | 3.37 | 3.37 | 3.37
| CDN004 | FALSE | 1.35 | 1.34 | 1.35 | 1.37 | 1.36 | 1.36 | 1.37 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39
| CDN006 | FALSE | 2.34 | 2.35 | 2.38 | 2.4 | 2.4 | 2.4 | 2.43 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47
| CFD021 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CFD023 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA003 | FALSE | 3.69 | 3.68 | 3.69 | 3.68 | 3.65 | 3.63 | 3.63 | 3.65 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62
| CHA005 | FALSE | 5.29 | 5.3 | 5.37 | 5.41 | 5.38 | 5.37 | 5.46 | 5.58 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55
| CHA006 | FALSE | 7.28 | 7.38 | 7.52 | 7.61 | 7.61 | 7.64 | 7.78 | 7.95 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93
| CHA007 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA008 | FALSE | 3.17 | 3.13 | 3.1 | 3.06 | 3.03 | 2.99 | 2.96 | 2.93 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91
| CHM011 | FALSE | 2.33 | 2.32 | 2.32 | 2.32 | 2.3 | 2.29 | 2.28 | 2.29 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27
| CL011 | FALSE | 5.16 | 5.21 | 5.28 | 5.3 | 5.34 | 5.4 | 5.48 | 5.56 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
| CL013 | FALSE | 4.88 | 5.13 | 5.13 | 5.12 | 5.1 | 5.08 | 5.08 | 5.1 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09
| CL014 | FALSE | 3.02 | 3.04 | 3.08 | 3.1 | 3.12 | 3.14 | 3.17 | 3.2 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22
| CL015 | FALSE | 2.52 | 2.55 | 2.59 | 2.62 | 2.64 | 2.66 | 2.7 | 2.74 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76
| CL016 | FALSE | 3.83 | 3.84 | 3.86 | 3.87 | 3.87 | 3.87 | 3.9 | 3.93 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94
| CL021 | FALSE | 3.51 | 3.56 | 3.61 | 3.65 | 3.68 | 3.73 | 3.78 | 3.85 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89
| CL022 | FALSE | 3.86 | 3.91 | 3.98 | 4.03 | 4.06 | 4.11 | 4.16 | 4.23 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26
| CL023 | FALSE | 4.44 | 4.39 | 4.39 | 4.42 | 4.43 | 4.47 | 4.51 | 4.59 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64
| CL026 | FALSE | 2.16 | 2.16 | 2.19 | 2.22 | 2.24 | 2.27 | 2.32 | 2.37 | 2.39 | 2.39 | 2.39 | 2.39 | 2.39 | 2.39 | 2.39 | 2.39 | 2.39 | 2.39 | 2.39 | 2.39
| CL027 | FALSE | 1.89 | 1.89 | 1.9 | 1.9 | 1.91 | 1.91 | 1.91 | 1.92 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93
| CL028 | FALSE | 5.06 | 5.08 | 5.1 | 5.12 | 5.13 | 5.14 | 5.16 | 5.19 | 5.21 | 5.21 | 5.21 | 5.21 | 5.21 | 5.21 | 5.21 | 5.21 | 5.21 | 5.21 | 5.21 | 5.21
| CL033 | FALSE | 3.49 | 3.56 | 3.64 | 3.71 | 3.76 | 3.81 | 3.89 | 3.99 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04
| CL035 | FALSE | 1.5 | 1.5 | 1.51 | 1.51 | 1.51 | 1.5 | 1.51 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53 | 1.53
| CL036 | FALSE | 4.54 | 4.59 | 4.66 | 4.71 | 4.75 | 4.79 | 4.82 | 4.89 | 4.91 | 4.91 | 4.91 | 4.91 | 4.91 | 4.91 | 4.91 | 4.91 | 4.91 | 4.91 | 4.91 | 4.91
| CL037 | FALSE | 3.43 | 3.42 | 3.45 | 3.46 | 3.47 | 3.49 | 3.54 | 3.63 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| CL038 | FALSE | 4.92 | 4.92 | 4.95 | 4.97 | 4.98 | 5.01 | 5.05 | 5.13 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16
| CLC001 | FALSE | 8.03 | 8.01 | 8.02 | 8.02 | 7.99 | 7.98 | 8.01 | 8.03 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02
| CLC002 | FALSE | 6.39 | 6.38 | 6.4 | 6.38 | 6.37 | 6.39 | 6.44 | 6.53 | 6.49 | 6.49 | 6.49 | 6.49 | 6.49 | 6.49 | 6.49 | 6.49 | 6.49 | 6.49 | 6.49 | 6.49
| CLC003 | FALSE | 7 | 7.09 | 7.25 | 7.38 | 7.41 | 7.48 | 7.63 | 7.84 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93 | 7.93
| CLC004 | FALSE | 8.49 | 9.64 | 9.68 | 9.71 | 9.69 | 9.68 | 9.74 | 9.82 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
| CLC006 | FALSE | 12.28 | 12.28 | 12.3 | 12.32 | 12.3 | 12.27 | 12.31 | 12.35 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37
| CLC012 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013 | FALSE | 6.77 | 6.84 | 6.99 | 7.12 | 7.19 | 7.26 | 7.34 | 7.5 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58
| CLC014 | FALSE | 7.59 | 7.62 | 7.68 | 7.72 | 7.71 | 7.7 | 7.72 | 7.8 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79
| CME014 | FALSE | 12.51 | 12.67 | 12.89 | 13.06 | 13.14 | 13.27 | 13.46 | 13.66 | 13.83 | 13.83 | 13.83 | 13.83 | 13.83 | 13.83 | 13.83 | 13.83 | 13.83 | 13.83 | 13.83 | 13.83
| CME015 | FALSE | 8.77 | 8.77 | 8.84 | 8.91 | 8.9 | 8.88 | 8.97 | 9.08 | 9.12 | 9.12 | 9.12 | 9.12 | 9.12 | 9.12 | 9.12 | 9.12 | 9.12 | 9.12 | 9.12 | 9.12
| CME016 | FALSE | 9.29 | 9.41 | 9.56 | 9.71 | 9.78 | 9.86 | 10.04 | 10.28 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38
| CME021 | FALSE | 7.19 | 7.19 | 7.23 | 7.24 | 7.22 | 7.2 | 7.23 | 7.28 | 7.27 | 7.27 | 7.27 | 7.27 | 7.27 | 7.27 | 7.27 | 7.27 | 7.27 | 7.27 | 7.27 | 7.27
| CME022 | FALSE | 10.36 | 10.28 | 10.23 | 10.17 | 10.1 | 10.02 | 9.97 | 9.93 | 9.88 | 9.88 | 9.88 | 9.88 | 9.88 | 9.88 | 9.88 | 9.88 | 9.88 | 9.88 | 9.88 | 9.88
| CMN001 | FALSE | 4.51 | 4.56 | 4.63 | 4.72 | 4.76 | 4.79 | 4.88 | 4.94 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02
| CMN002 | FALSE | 3.63 | 3.64 | 3.66 | 3.69 | 3.7 | 3.72 | 3.76 | 3.8 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82
| CMN003 | FALSE | 7 | 7.09 | 7.21 | 7.32 | 7.4 | 7.47 | 7.59 | 7.75 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79
| CMN004 | FALSE | 3.65 | 3.69 | 3.75 | 3.8 | 3.82 | 3.85 | 3.9 | 3.99 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| CMN005 | FALSE | 10.22 | 10.26 | 10.3 | 10.36 | 10.37 | 10.41 | 10.45 | 10.51 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56
| CMN008 | FALSE | 5.6 | 5.66 | 5.75 | 5.86 | 5.91 | 5.95 | 6.06 | 6.14 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23
| COB011 | FALSE | 6.78 | 6.89 | 7.07 | 7.2 | 7.22 | 7.29 | 7.48 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
| COB012 | FALSE | 1.26 | 1.27 | 1.28 | 1.29 | 1.29 | 1.29 | 1.31 | 1.33 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32
| COB021 | FALSE | 4.45 | 4.41 | 4.37 | 4.33 | 4.28 | 4.23 | 4.2 | 4.17 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14
| COB022 | FALSE | 6.2 | 6.13 | 6.08 | 6.02 | 5.95 | 5.89 | 5.84 | 5.8 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77
| CRO013 | FALSE | 4.69 | 4.72 | 4.78 | 4.81 | 4.81 | 4.82 | 4.87 | 4.95 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96
| CRO014 | FALSE | 1.49 | 1.48 | 1.48 | 1.48 | 1.47 | 1.47 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46
| CRO021 | FALSE | 5.77 | 5.74 | 5.72 | 5.7 | 5.66 | 5.62 | 5.62 | 5.63 | 5.58 | 5.58 | 5.58 | 5.58 | 5.58 | 5.58 | 5.58 | 5.58 | 5.58 | 5.58 | 5.58 | 5.58
| CRO022 | FALSE | 3.03 | 3 | 3.03 | 3.05 | 3.06 | 3.07 | 3.11 | 3.16 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
| CRO023 | FALSE | 1.1 | 1.1 | 1.11 | 1.11 | 1.1 | 1.1 | 1.11 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12
| CRO024 | FALSE | 0.22 | 0.22 | 0.23 | 0.23 | 0.24 | 0.24 | 0.24 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| CRO031 | FALSE | 10.39 | 10.38 | 10.36 | 10.33 | 10.27 | 10.22 | 10.19 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2
| CRO032 | FALSE | 18.96 | 19.38 | 20.05 | 20.61 | 20.75 | 21.03 | 21.69 | 22.54 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6
| CRO033 | FALSE | 6.28 | 6.26 | 6.25 | 6.23 | 6.21 | 6.18 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16
| CRO034 | FALSE | 4.68 | 4.63 | 4.59 | 4.55 | 4.51 | 4.47 | 4.45 | 4.43 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
| CTN001 | FALSE | 7.91 | 7.94 | 8.05 | 8.13 | 8.11 | 8.11 | 8.22 | 8.36 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32
| CTN002 | FALSE | 2.8 | 2.79 | 2.81 | 2.82 | 2.81 | 2.81 | 2.83 | 2.86 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85
| CTN003 | FALSE | 2.15 | 2.16 | 2.18 | 2.19 | 2.18 | 2.18 | 2.2 | 2.23 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22
| CTN004 | FALSE | 10.15 | 10.08 | 10.05 | 10.16 | 10.04 | 9.96 | 9.95 | 9.93 | 9.87 | 9.87 | 9.87 | 9.87 | 9.87 | 9.87 | 9.87 | 9.87 | 9.87 | 9.87 | 9.87 | 9.87
| CTN005 | FALSE | 1.42 | 1.42 | 1.41 | 1.41 | 1.39 | 1.38 | 1.37 | 1.36 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34
| CTN006 | FALSE | 6.38 | 6.37 | 6.39 | 6.39 | 6.35 | 6.32 | 6.33 | 6.36 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31
| CW002 | FALSE | 0 | 5.71 | 5.83 | 5.94 | 6.06 | 6.15 | 6.29 | 6.42 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52
| CW003 | FALSE | 0 | 6 | 6.15 | 6.27 | 6.36 | 6.48 | 6.66 | 6.84 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96
| CW004 | FALSE | 2.79 | 3.11 | 3.13 | 3.16 | 3.15 | 3.15 | 3.17 | 3.19 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
| CW005 | FALSE | 3.45 | 3.46 | 3.48 | 3.5 | 3.51 | 3.52 | 3.55 | 3.6 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62 | 3.62
| CW006 | FALSE | 1.41 | 1.46 | 1.5 | 1.55 | 1.59 | 1.63 | 1.68 | 1.73 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77
| CW007 | FALSE | 3.28 | 3.3 | 3.34 | 3.37 | 3.4 | 3.42 | 3.47 | 3.52 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55
| CW008 | FALSE | 1.52 | 1.56 | 1.59 | 1.63 | 1.66 | 1.69 | 1.73 | 1.76 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79
| CW009 | FALSE | 4.1 | 4.26 | 4.35 | 4.45 | 4.5 | 4.57 | 4.68 | 4.78 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89
| CW011 | FALSE | 3.4 | 3.47 | 3.56 | 3.64 | 3.7 | 3.76 | 3.85 | 3.95 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01
| CW012 | FALSE | 2.41 | 2.44 | 2.5 | 2.56 | 2.61 | 2.67 | 2.75 | 2.82 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87
| CW013 | FALSE | 1.75 | 1.77 | 1.79 | 1.8 | 1.81 | 1.83 | 1.84 | 1.86 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87
| CW014 | FALSE | 2.98 | 7.72 | 7.94 | 8.14 | 8.3 | 8.49 | 8.77 | 8.99 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14
| CW015 | FALSE | 7.13 | 7.24 | 7.33 | 7.41 | 7.45 | 7.49 | 7.59 | 7.68 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71
| CW017 | FALSE | 0 | 2.35 | 2.36 | 2.37 | 2.37 | 2.34 | 2.35 | 2.4 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41
| CW018 | FALSE | 0 | 0.32 | 0.33 | 0.33 | 0.33 | 0.34 | 0.34 | 0.34 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
| DA004 | FALSE | 0.92 | 0.91 | 0.9 | 0.9 | 0.89 | 0.88 | 0.88 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87
| DA005 | FALSE | 6.5 | 6.82 | 7.11 | 7.38 | 7.64 | 7.9 | 8.17 | 8.47 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73
| DA006 | FALSE | 5.89 | 6.13 | 6.4 | 6.67 | 6.86 | 7.07 | 7.35 | 7.64 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86
| DA007 | FALSE | 2.18 | 2.29 | 2.39 | 2.5 | 2.59 | 2.68 | 2.8 | 2.91 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01
| DA008 | FALSE | 3.18 | 3.15 | 3.13 | 3.12 | 3.1 | 3.09 | 3.1 | 3.15 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12
| DA009 | FALSE | 4.7 | 4.92 | 5.13 | 5.32 | 5.5 | 5.68 | 5.88 | 6.07 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26
| DA013 | FALSE | 0.85 | 0.89 | 0.92 | 0.96 | 0.99 | 1.03 | 1.06 | 1.1 | 1.13 | 1.13 | 1.13 | 1.13 | 1.13 | 1.13 | 1.13 | 1.13 | 1.13 | 1.13 | 1.13 | 1.13
| DA016 | FALSE | 2.69 | 2.67 | 2.65 | 2.63 | 2.61 | 2.59 | 2.57 | 2.56 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55
| DA020 | FALSE | 2.36 | 2.37 | 2.39 | 2.41 | 2.41 | 2.41 | 2.43 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47
| DA021 | FALSE | 5.88 | 5.95 | 5.98 | 6.01 | 6.04 | 6.06 | 6.11 | 6.15 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17
| DA022 | FALSE | 2.69 | 2.82 | 2.96 | 3.09 | 3.21 | 3.34 | 3.48 | 3.62 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75
| DA026 | FALSE | 2.31 | 2.3 | 2.29 | 2.28 | 2.26 | 2.24 | 2.24 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23
| DA027 | FALSE | 2.68 | 2.81 | 2.93 | 3.04 | 3.15 | 3.25 | 3.36 | 3.47 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59
| DA028 | FALSE | 1.54 | 1.53 | 1.53 | 1.53 | 1.52 | 1.52 | 1.51 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52 | 1.52
| DA029 | FALSE | 0.24 | 0.26 | 0.29 | 0.32 | 0.34 | 0.37 | 0.4 | 0.43 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
| DA030 | FALSE | 4.03 | 4 | 3.97 | 3.94 | 3.91 | 3.88 | 3.86 | 3.84 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82
| DA031 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL011 | FALSE | 11.39 | 11.68 | 12.04 | 12.4 | 12.62 | 12.91 | 13.26 | 13.79 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14
| DDL012 | FALSE | 9.65 | 9.77 | 9.95 | 10.14 | 10.21 | 10.31 | 10.4 | 10.7 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85
| DDL013 | FALSE | 12.34 | 12.7 | 13.2 | 13.65 | 13.81 | 14.1 | 14.52 | 15.24 | 15.72 | 15.72 | 15.72 | 15.72 | 15.72 | 15.72 | 15.72 | 15.72 | 15.72 | 15.72 | 15.72 | 15.72
| DDL014 | FALSE | 3 | 3.05 | 3.1 | 3.16 | 3.18 | 3.22 | 3.28 | 3.35 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| DDL021 | FALSE | 10.27 | 10.54 | 10.88 | 11.26 | 11.54 | 11.82 | 12.06 | 12.41 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74
| DDL022 | FALSE | 10.49 | 10.91 | 11.4 | 11.88 | 12.32 | 12.7 | 13.22 | 13.79 | 14.27 | 14.27 | 14.27 | 14.27 | 14.27 | 14.27 | 14.27 | 14.27 | 14.27 | 14.27 | 14.27 | 14.27
| DDL023 | FALSE | 12.87 | 13.36 | 13.96 | 14.54 | 14.92 | 15.39 | 15.96 | 16.67 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31
| DDL024 | FALSE | 9.32 | 9.6 | 9.93 | 10.22 | 10.49 | 10.75 | 11.06 | 11.45 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74 | 11.74
| DLF001 | FALSE | 6.22 | 6.56 | 6.91 | 7.23 | 7.52 | 7.82 | 8.16 | 8.53 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
| DLF002 | FALSE | 3.35 | 3.36 | 3.36 | 3.37 | 3.37 | 3.37 | 3.38 | 3.4 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42 | 3.42
| DLF003 | FALSE | 3.83 | 3.92 | 4.05 | 4.17 | 4.21 | 4.25 | 4.38 | 4.55 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6
| DLF063 | FALSE | 8.72 | 8.72 | 8.73 | 8.75 | 8.75 | 8.75 | 8.79 | 8.84 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89
| E021 | FALSE | 0.06 | 0.07 | 0.07 | 0.08 | 0.08 | 0.08 | 0.09 | 0.09 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| E032 | FALSE | 2.09 | 2.24 | 2.39 | 2.54 | 2.67 | 2.8 | 2.94 | 3.08 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| E033 | FALSE | 0.51 | 0.55 | 0.59 | 0.63 | 0.67 | 0.71 | 0.75 | 0.79 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| ECA001 | FALSE | 7.11 | 7.14 | 7.21 | 7.25 | 7.26 | 7.27 | 7.32 | 7.39 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41
| ECA003 | FALSE | 7.52 | 7.5 | 7.55 | 7.6 | 7.61 | 7.62 | 7.7 | 7.78 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81
| ECA005 | FALSE | 9.71 | 9.75 | 9.82 | 9.86 | 9.86 | 9.88 | 9.96 | 10.06 | 10.07 | 10.07 | 10.07 | 10.07 | 10.07 | 10.07 | 10.07 | 10.07 | 10.07 | 10.07 | 10.07 | 10.07
| ECA007 | FALSE | 6.48 | 6.44 | 6.42 | 6.34 | 6.16 | 5.99 | 5.93 | 6.06 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01
| ECA010 | FALSE | 8.03 | 8.07 | 8.18 | 8.24 | 8.27 | 8.32 | 8.44 | 8.6 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63
| ECA012 | FALSE | 7.55 | 7.64 | 7.79 | 7.9 | 7.93 | 7.99 | 8.17 | 8.37 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35
| EHK021 | FALSE | 12.04 | 12.17 | 12.38 | 12.58 | 12.66 | 12.74 | 12.93 | 13.21 | 13.31 | 13.31 | 13.31 | 13.31 | 13.31 | 13.31 | 13.31 | 13.31 | 13.31 | 13.31 | 13.31 | 13.31
| EHK022 | FALSE | 5.86 | 5.87 | 5.89 | 5.91 | 5.91 | 5.93 | 5.99 | 6.05 | 6.07 | 6.07 | 6.07 | 6.07 | 6.07 | 6.07 | 6.07 | 6.07 | 6.07 | 6.07 | 6.07 | 6.07
| EHK023 | FALSE | 8.73 | 8.82 | 8.94 | 9.04 | 9.1 | 9.15 | 9.3 | 9.44 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
| EHK024 | FALSE | 9.33 | 9.46 | 9.65 | 9.8 | 9.85 | 9.94 | 10.12 | 10.34 | 10.41 | 10.41 | 10.41 | 10.41 | 10.41 | 10.41 | 10.41 | 10.41 | 10.41 | 10.41 | 10.41 | 10.41
| EHK031 | FALSE | 10.63 | 10.89 | 11.21 | 11.47 | 11.71 | 11.95 | 12.29 | 12.71 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96
| EHK032 | FALSE | 0.78 | 0.79 | 0.79 | 0.8 | 0.8 | 0.8 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81
| EHK033 | FALSE | 13.87 | 14.21 | 14.6 | 14.96 | 15.32 | 15.68 | 16.16 | 16.72 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09
| EHK034 | FALSE | 5.85 | 5.79 | 5.77 | 5.76 | 5.74 | 5.72 | 5.73 | 5.74 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75
| ETSA001 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ETSA003 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F026 | FALSE | 1.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F027 | FALSE | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F028 | FALSE | 2.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F029 | FALSE | 2.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F030 | FALSE | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F032 | FALSE | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F033 | FALSE | 2.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F034 | FALSE | 2.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F035 | FALSE | 1.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F037 | FALSE | 3.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FB002 | FALSE | 3.34 | 3.63 | 3.9 | 4.16 | 4.4 | 4.63 | 4.88 | 5.12 | 5.35 | 5.35 | 5.35 | 5.35 | 5.35 | 5.35 | 5.35 | 5.35 | 5.35 | 5.35 | 5.35 | 5.35
| FB004 | FALSE | 0.19 | 0.21 | 0.23 | 0.24 | 0.26 | 0.27 | 0.28 | 0.3 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31
| FB005 | FALSE | 2.67 | 2.85 | 3.01 | 3.18 | 3.33 | 3.47 | 3.62 | 3.78 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94
| FB006 | FALSE | 3.61 | 3.92 | 4.22 | 4.5 | 4.77 | 5.03 | 5.29 | 5.56 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82
| FB010 | FALSE | 4.87 | 5.28 | 5.68 | 6.05 | 6.41 | 6.76 | 7.11 | 7.47 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82
| FB011 | FALSE | 6.79 | 7.36 | 7.91 | 8.43 | 8.93 | 9.4 | 9.9 | 10.39 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88
| FB013 | FALSE | 4.35 | 4.37 | 4.4 | 4.42 | 4.43 | 4.44 | 4.46 | 4.48 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
| FB014 | FALSE | 3 | 3.22 | 3.44 | 3.66 | 3.87 | 4.07 | 4.29 | 4.5 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72
| FB015 | FALSE | 4.25 | 4.63 | 4.97 | 5.31 | 5.62 | 5.93 | 6.24 | 6.55 | 6.86 | 6.86 | 6.86 | 6.86 | 6.86 | 6.86 | 6.86 | 6.86 | 6.86 | 6.86 | 6.86 | 6.86
| FB018 | FALSE | 5.57 | 6.02 | 6.46 | 6.89 | 7.29 | 7.68 | 8.08 | 8.48 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88
| FB019 | FALSE | 10.74 | 11.68 | 12.57 | 13.43 | 14.2 | 14.96 | 15.74 | 16.53 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31 | 17.31
| FB020 | FALSE | 6.25 | 6.57 | 6.92 | 7.23 | 7.45 | 7.7 | 8.03 | 8.4 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62
| FB022 | FALSE | 1.42 | 1.54 | 1.65 | 1.76 | 1.86 | 1.96 | 2.06 | 2.16 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26
| FB023 | FALSE | 2.18 | 2.31 | 2.49 | 2.67 | 2.85 | 3.02 | 3.2 | 3.39 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57
| FF084 | FALSE | 3.26 | 3.35 | 3.44 | 3.5 | 3.56 | 3.62 | 3.7 | 3.81 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84
| FF085 | FALSE | 1.59 | 1.59 | 1.61 | 1.62 | 1.61 | 1.61 | 1.63 | 1.66 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65
| FF086 | FALSE | 2.15 | 2.18 | 2.22 | 2.25 | 2.27 | 2.3 | 2.33 | 2.38 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
| FF091 | FALSE | 0.91 | 0.91 | 0.93 | 0.94 | 0.94 | 0.95 | 0.96 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
| FF092 | FALSE | 1.38 | 1.38 | 1.39 | 1.4 | 1.41 | 1.41 | 1.43 | 1.46 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47
| FF097 | FALSE | 2.18 | 2.2 | 2.22 | 2.24 | 2.23 | 2.22 | 2.22 | 2.21 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18
| FNS011 | FALSE | 7.91 | 7.98 | 8.11 | 8.2 | 8.23 | 8.29 | 8.41 | 8.57 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6
| FNS012 | FALSE | 6.48 | 6.59 | 6.73 | 6.85 | 6.94 | 7.04 | 7.19 | 7.41 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53
| FNS013 | FALSE | 11.43 | 11.66 | 11.92 | 12.2 | 12.44 | 12.69 | 13.01 | 13.39 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73
| FNS021 | FALSE | 11.34 | 13.12 | 14.86 | 15 | 15.07 | 15.17 | 15.36 | 15.6 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68
| FNS022 | FALSE | 6.16 | 6.3 | 6.47 | 6.64 | 6.76 | 6.89 | 7.06 | 7.25 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38
| FNS032 | FALSE | 5.05 | 5.09 | 5.17 | 5.22 | 5.25 | 5.27 | 5.34 | 5.43 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46
| FNS033 | FALSE | 0 | 0 | 0 | 0 | 0 | 9.98 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1
| FR001 | FALSE | 2.59 | 2.61 | 2.63 | 2.65 | 2.67 | 2.69 | 2.71 | 2.74 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77
| FR003 | FALSE | 2.8 | 2.82 | 2.82 | 2.82 | 2.83 | 2.83 | 2.83 | 2.84 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85
| FR004 | FALSE | 2.05 | 2.07 | 2.09 | 2.11 | 2.13 | 2.15 | 2.17 | 2.2 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23
| FR005 | FALSE | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
| FR007 | FALSE | 2.68 | 2.7 | 2.73 | 2.75 | 2.77 | 2.79 | 2.83 | 2.86 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89
| FR008 | FALSE | 3.74 | 3.65 | 3.56 | 3.47 | 3.39 | 3.31 | 3.24 | 3.18 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12
| FR009 | FALSE | 0.44 | 0.44 | 0.43 | 0.43 | 0.43 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
| FR013 | FALSE | 1.01 | 1.02 | 1.03 | 1.04 | 1.04 | 1.05 | 1.06 | 1.07 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08
| FR014 | FALSE | 3.34 | 3.33 | 3.29 | 3.25 | 3.19 | 3.14 | 3.1 | 3.06 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01
| FR015 | FALSE | 2.21 | 2.25 | 2.29 | 2.33 | 2.35 | 2.37 | 2.42 | 2.48 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
| FR016 | FALSE | 2.08 | 2.09 | 2.1 | 2.12 | 2.12 | 2.13 | 2.14 | 2.16 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18 | 2.18
| FR018 | FALSE | 2.94 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99
| FR019 | FALSE | 2.78 | 2.8 | 2.82 | 2.84 | 2.86 | 2.87 | 2.9 | 2.94 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97
| FR020 | FALSE | 2.67 | 2.69 | 2.72 | 2.75 | 2.77 | 2.79 | 2.83 | 2.87 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9
| FR024 | FALSE | 2.58 | 2.61 | 2.63 | 2.65 | 2.67 | 2.69 | 2.71 | 2.75 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78
| FR026 | FALSE | 3.48 | 3.88 | 3.91 | 3.93 | 3.93 | 3.94 | 3.97 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01 | 4.01
| FR027 | FALSE | 3.24 | 3.27 | 3.3 | 3.33 | 3.36 | 3.38 | 3.43 | 3.47 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51
| FR028 | FALSE | 2.63 | 2.66 | 2.7 | 2.73 | 2.75 | 2.78 | 2.82 | 2.87 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9
| FR029 | FALSE | 2.63 | 2.65 | 2.67 | 2.69 | 2.7 | 2.72 | 2.74 | 2.77 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| FR030 | FALSE | 0.85 | 0.86 | 0.87 | 0.88 | 0.88 | 0.89 | 0.9 | 0.91 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| FR031 | FALSE | 4.54 | 5.04 | 5.06 | 5.03 | 5.02 | 5.01 | 5.01 | 5.02 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01
| FR032 | FALSE | 3.34 | 3.26 | 3.18 | 3.1 | 3.02 | 2.95 | 2.89 | 2.84 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78
| GB011 | FALSE | 3.35 | 3.38 | 3.4 | 3.43 | 3.45 | 3.47 | 3.5 | 3.53 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56
| GB012 | FALSE | 7.22 | 7.29 | 7.37 | 7.44 | 7.49 | 7.54 | 7.62 | 7.71 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77
| GB014 | FALSE | 1.52 | 1.56 | 1.58 | 1.59 | 1.6 | 1.61 | 1.64 | 1.66 | 1.68 | 1.68 | 1.68 | 1.68 | 1.68 | 1.68 | 1.68 | 1.68 | 1.68 | 1.68 | 1.68 | 1.68
| GB031 | FALSE | 4.71 | 4.75 | 4.8 | 4.82 | 4.85 | 4.88 | 4.93 | 5 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03
| GB032 | FALSE | 3.38 | 3.4 | 3.43 | 3.46 | 3.48 | 3.5 | 3.52 | 3.55 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59
| GCY011 | FALSE | 13.03 | 13.19 | 13.4 | 13.58 | 13.64 | 13.84 | 14.02 | 14.29 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42
| GCY012 | FALSE | 6.33 | 6.3 | 6.26 | 6.24 | 6.2 | 6.16 | 6.13 | 6.12 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08
| GCY013 | FALSE | 5.03 | 5.03 | 5.04 | 5.06 | 5.06 | 5.06 | 5.08 | 5.1 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12
| GCY014 | FALSE | 13.12 | 13.24 | 13.4 | 13.62 | 13.68 | 13.81 | 13.98 | 14.18 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42 | 14.42
| GCY021 | FALSE | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.82 | 2.82 | 2.81 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| GCY022 | FALSE | 6.99 | 6.99 | 7.01 | 7.02 | 7 | 6.98 | 7 | 7.02 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99
| GCY023 | FALSE | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.78 | 1.79 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
| GCY024 | FALSE | 7.78 | 7.82 | 7.9 | 7.96 | 8 | 8.06 | 8.13 | 8.23 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28
| GHP011 | FALSE | 11.28 | 11.47 | 11.76 | 12 | 12.16 | 12.39 | 12.81 | 13.22 | 13.51 | 13.51 | 13.51 | 13.51 | 13.51 | 13.51 | 13.51 | 13.51 | 13.51 | 13.51 | 13.51 | 13.51
| GHP012 | FALSE | 10.43 | 10.61 | 10.83 | 11.03 | 11.15 | 11.32 | 11.54 | 11.83 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98
| GHP021 | FALSE | 9.43 | 9.7 | 10.02 | 10.3 | 10.51 | 10.75 | 11.14 | 11.57 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9
| GHP022 | FALSE | 6 | 6.1 | 6.24 | 6.34 | 6.4 | 6.47 | 6.61 | 6.78 | 6.84 | 6.84 | 6.84 | 6.84 | 6.84 | 6.84 | 6.84 | 6.84 | 6.84 | 6.84 | 6.84 | 6.84
| GL011 | FALSE | 6.01 | 6.32 | 6.29 | 6.27 | 6.26 | 6.28 | 6.33 | 6.35 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38
| GL012 | FALSE | 2.56 | 2.58 | 2.61 | 2.64 | 2.66 | 2.68 | 2.7 | 2.75 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76
| GL013 | FALSE | 4.62 | 4.69 | 4.79 | 4.87 | 4.92 | 4.99 | 5.08 | 5.2 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27
| GL014 | FALSE | 4.77 | 4.86 | 4.98 | 5.09 | 5.17 | 5.25 | 5.36 | 5.52 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61
| GL015 | FALSE | 5.39 | 5.51 | 5.67 | 5.79 | 5.87 | 6 | 6.15 | 6.31 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38
| GL021 | FALSE | 5.87 | 5.96 | 6.06 | 6.14 | 6.17 | 6.21 | 6.31 | 6.43 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47
| GL022 | FALSE | 8.47 | 8.58 | 8.74 | 8.85 | 8.91 | 9.03 | 9.15 | 9.35 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39
| GL023 | FALSE | 6.06 | 6.05 | 6.08 | 6.12 | 6.12 | 6.13 | 6.19 | 6.31 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34
| GL024 | FALSE | 7.03 | 7.13 | 7.26 | 7.36 | 7.44 | 7.54 | 7.66 | 7.78 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87
| GLE011 | FALSE | 3.13 | 3.14 | 3.17 | 3.2 | 3.2 | 3.21 | 3.24 | 3.28 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
| GLE012 | FALSE | 10.24 | 10.42 | 10.65 | 10.85 | 10.98 | 11.15 | 11.37 | 11.69 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85
| GLE013 | FALSE | 13.42 | 13.85 | 14.33 | 14.76 | 15.11 | 15.5 | 16.02 | 16.58 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92
| GLE021 | FALSE | 5.87 | 5.91 | 6 | 6.06 | 6.07 | 6.09 | 6.15 | 6.28 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29
| GLE022 | FALSE | 8.28 | 8.52 | 8.79 | 9.03 | 9.21 | 9.43 | 9.71 | 10.03 | 10.22 | 10.22 | 10.22 | 10.22 | 10.22 | 10.22 | 10.22 | 10.22 | 10.22 | 10.22 | 10.22 | 10.22
| GLE023 | FALSE | 2.28 | 2.28 | 2.29 | 2.29 | 2.3 | 2.3 | 2.31 | 2.32 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33
| GLE024 | FALSE | 11.45 | 11.55 | 11.68 | 11.74 | 11.76 | 11.82 | 11.96 | 12.13 | 12.16 | 12.16 | 12.16 | 12.16 | 12.16 | 12.16 | 12.16 | 12.16 | 12.16 | 12.16 | 12.16 | 12.16
| GLE031 | FALSE | 9.44 | 9.47 | 9.56 | 9.64 | 9.66 | 9.7 | 9.8 | 9.95 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02
| GLE032 | FALSE | 7.3 | 7.34 | 7.44 | 7.51 | 7.54 | 7.58 | 7.66 | 7.79 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81 | 7.81
| GLE033 | FALSE | 3.25 | 3.26 | 3.27 | 3.28 | 3.29 | 3.29 | 3.32 | 3.33 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32
| GSB011 | FALSE | 6.81 | 6.97 | 7.14 | 7.29 | 7.4 | 7.54 | 7.72 | 7.96 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
| GSB012 | FALSE | 12.7 | 12.96 | 13.3 | 13.59 | 13.78 | 13.99 | 14.32 | 14.79 | 15.08 | 15.08 | 15.08 | 15.08 | 15.08 | 15.08 | 15.08 | 15.08 | 15.08 | 15.08 | 15.08 | 15.08
| GSB013 | FALSE | 8.28 | 8.43 | 8.62 | 8.8 | 8.89 | 9.02 | 9.23 | 9.54 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7
| GSB014 | FALSE | 4.47 | 4.5 | 4.54 | 4.6 | 4.63 | 4.66 | 4.72 | 4.82 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86
| HSM001 | FALSE | 3.46 | 3.44 | 3.45 | 3.45 | 3.43 | 3.42 | 3.43 | 3.45 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43
| HSM002 | FALSE | 3.27 | 3.27 | 3.29 | 3.3 | 3.29 | 3.28 | 3.31 | 3.34 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32
| HSM003 | FALSE | 4.79 | 4.81 | 4.85 | 4.87 | 4.85 | 4.84 | 4.88 | 4.92 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9
| HSM004 | FALSE | 5.34 | 5.35 | 5.37 | 5.36 | 5.3 | 5.27 | 5.29 | 5.32 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27 | 5.27
| HSM005 | FALSE | 4.57 | 4.56 | 4.56 | 4.54 | 4.51 | 4.48 | 4.49 | 4.49 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46
| HSM006 | FALSE | 7.84 | 7.79 | 7.78 | 7.75 | 7.69 | 7.64 | 7.63 | 7.65 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
| HSM009 | FALSE | 7.54 | 7.52 | 7.58 | 7.6 | 7.58 | 7.55 | 7.58 | 7.58 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57
| HSM010 | FALSE | 9.16 | 9.08 | 9.09 | 9.08 | 9.02 | 8.97 | 8.99 | 9.02 | 8.96 | 8.96 | 8.96 | 8.96 | 8.96 | 8.96 | 8.96 | 8.96 | 8.96 | 8.96 | 8.96 | 8.96
| HTN011 | FALSE | 1.28 | 1.3 | 1.32 | 1.33 | 1.33 | 1.34 | 1.36 | 1.39 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| HTN012 | FALSE | 3.17 | 3.19 | 3.23 | 3.25 | 3.24 | 3.24 | 3.27 | 3.31 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29
| HTN013 | FALSE | 5.11 | 5.11 | 5.11 | 5.09 | 5.04 | 4.99 | 4.97 | 4.97 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9
| HTN032 | FALSE | 6.68 | 6.65 | 6.67 | 6.68 | 6.65 | 6.63 | 6.66 | 6.7 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67
| HTN033 | FALSE | 7.47 | 7.46 | 7.46 | 7.45 | 7.41 | 7.38 | 7.38 | 7.41 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37
| HTN034 | FALSE | 3.27 | 3.3 | 3.33 | 3.35 | 3.33 | 3.32 | 3.35 | 3.4 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
| HYT011 | FALSE | 2.65 | 2.7 | 2.78 | 2.88 | 2.9 | 2.93 | 3.01 | 3.12 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14
| JA001 | FALSE | 2.49 | 2.57 | 2.66 | 2.74 | 2.81 | 2.88 | 2.97 | 3.06 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
| JA002 | FALSE | 4.64 | 4.74 | 4.78 | 4.83 | 4.94 | 5.05 | 5.17 | 5.3 | 5.41 | 5.41 | 5.41 | 5.41 | 5.41 | 5.41 | 5.41 | 5.41 | 5.41 | 5.41 | 5.41 | 5.41
| JA003 | FALSE | 2.37 | 2.45 | 2.53 | 2.6 | 2.65 | 2.71 | 2.79 | 2.89 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93
| JA005 | FALSE | 14.56 | 15.09 | 15.48 | 15.93 | 16.35 | 16.78 | 17.27 | 17.78 | 18.23 | 18.23 | 18.23 | 18.23 | 18.23 | 18.23 | 18.23 | 18.23 | 18.23 | 18.23 | 18.23 | 18.23
| JA006 | FALSE | 5.89 | 6.1 | 6.33 | 6.55 | 6.74 | 6.94 | 7.17 | 7.39 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
| JA009 | FALSE | 2.69 | 2.87 | 2.95 | 3.01 | 3.06 | 3.12 | 3.19 | 3.27 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32
| JA010 | FALSE | 5.95 | 6.17 | 6.4 | 6.61 | 6.78 | 6.95 | 7.16 | 7.41 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59
| JA011 | FALSE | 8.55 | 8.85 | 9.17 | 9.45 | 9.72 | 9.99 | 10.28 | 10.6 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88 | 10.88
| JA013 | FALSE | 7.44 | 7.71 | 7.97 | 8.23 | 8.46 | 8.7 | 8.95 | 9.21 | 9.47 | 9.47 | 9.47 | 9.47 | 9.47 | 9.47 | 9.47 | 9.47 | 9.47 | 9.47 | 9.47 | 9.47
| JA014 | FALSE | 1.98 | 1.99 | 1.99 | 1.98 | 1.96 | 1.95 | 1.95 | 1.95 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93
| JA017 | FALSE | 3.49 | 3.61 | 3.73 | 3.85 | 3.95 | 4.06 | 4.17 | 4.29 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41
| JA018 | FALSE | 4.85 | 5.13 | 5.21 | 5.37 | 5.52 | 5.67 | 5.82 | 6 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16
| JA019 | FALSE | 9.37 | 9.56 | 9.76 | 9.92 | 10.06 | 10.19 | 10.34 | 10.49 | 10.66 | 10.66 | 10.66 | 10.66 | 10.66 | 10.66 | 10.66 | 10.66 | 10.66 | 10.66 | 10.66 | 10.66
| JA021 | FALSE | 2.55 | 2.64 | 2.74 | 2.83 | 2.91 | 2.98 | 3.07 | 3.17 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25
| JA022 | FALSE | 2.41 | 2.44 | 2.45 | 2.46 | 2.46 | 2.45 | 2.47 | 2.54 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
| JA025 | FALSE | 6.54 | 6.73 | 6.95 | 7.14 | 7.28 | 7.42 | 7.63 | 7.88 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03
| JA026 | FALSE | 2.37 | 2.47 | 2.56 | 2.66 | 2.74 | 2.83 | 2.92 | 3.01 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1
| JA027 | FALSE | 5.99 | 6.18 | 6.34 | 6.49 | 6.67 | 6.84 | 7.04 | 7.23 | 7.42 | 7.42 | 7.42 | 7.42 | 7.42 | 7.42 | 7.42 | 7.42 | 7.42 | 7.42 | 7.42 | 7.42
| JA029 | FALSE | 7.89 | 8.15 | 8.43 | 8.68 | 8.87 | 9.08 | 9.36 | 9.65 | 9.84 | 9.84 | 9.84 | 9.84 | 9.84 | 9.84 | 9.84 | 9.84 | 9.84 | 9.84 | 9.84 | 9.84
| JA033 | FALSE | 6 | 6.23 | 6.45 | 6.68 | 6.87 | 7.06 | 7.28 | 7.5 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71 | 7.71
| JA034 | FALSE | 3.12 | 3.23 | 3.35 | 3.47 | 3.56 | 3.66 | 3.79 | 3.92 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02
| JA035 | FALSE | 7.8 | 8.19 | 8.43 | 8.67 | 8.86 | 9.06 | 9.32 | 9.56 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
| JA037 | FALSE | 8.27 | 8.46 | 8.62 | 8.76 | 8.84 | 8.96 | 9.11 | 9.28 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44
| JA038 | FALSE | 5.63 | 5.76 | 5.89 | 6.01 | 6.12 | 6.23 | 6.36 | 6.5 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61
| JA041 | FALSE | 3.75 | 3.81 | 3.86 | 3.9 | 3.92 | 3.95 | 4 | 4.05 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07
| JA042 | FALSE | 9.35 | 9.7 | 10.05 | 10.4 | 10.71 | 11.01 | 11.4 | 11.72 | 12.04 | 12.04 | 12.04 | 12.04 | 12.04 | 12.04 | 12.04 | 12.04 | 12.04 | 12.04 | 12.04 | 12.04
| JA043 | FALSE | 6.68 | 6.93 | 7.17 | 7.4 | 7.61 | 7.81 | 8.03 | 8.26 | 8.49 | 8.49 | 8.49 | 8.49 | 8.49 | 8.49 | 8.49 | 8.49 | 8.49 | 8.49 | 8.49 | 8.49
| JA045 | FALSE | 3.24 | 3.36 | 3.48 | 3.59 | 3.69 | 3.79 | 3.9 | 4.03 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13
| JA046 | FALSE | 7.49 | 7.75 | 8.02 | 8.27 | 8.49 | 8.72 | 8.97 | 9.25 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
| K023 | FALSE | 4.07 | 4.11 | 4.16 | 4.21 | 4.23 | 4.24 | 4.29 | 4.34 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37 | 4.37
| K024 | FALSE | 5.87 | 5.96 | 6.06 | 6.16 | 6.22 | 6.28 | 6.38 | 6.5 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57
| K026 | FALSE | 3.33 | 3.34 | 3.37 | 3.41 | 3.42 | 3.44 | 3.49 | 3.53 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55
| K031 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| K032 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT002 | FALSE | 6.96 | 6.97 | 7 | 7.01 | 6.97 | 6.93 | 6.95 | 6.99 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95
| KGT003 | FALSE | 3.74 | 3.78 | 3.84 | 3.89 | 3.89 | 3.9 | 3.96 | 4.04 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03
| KGT004 | FALSE | 5.88 | 5.92 | 6.01 | 6.06 | 6.05 | 6.06 | 6.14 | 6.26 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23
| KGT005 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT012 | FALSE | 3.2 | 3.24 | 3.31 | 3.36 | 3.37 | 3.4 | 3.46 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55
| KRT013 | FALSE | 6.47 | 6.5 | 6.6 | 6.67 | 6.68 | 6.71 | 6.81 | 6.93 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95
| KRT022 | FALSE | 8.61 | 8.71 | 8.83 | 8.9 | 8.97 | 9.03 | 9.15 | 9.34 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39 | 9.39
| KRT023 | FALSE | 9.29 | 9.25 | 9.3 | 9.34 | 9.34 | 9.37 | 9.43 | 9.52 | 9.55 | 9.55 | 9.55 | 9.55 | 9.55 | 9.55 | 9.55 | 9.55 | 9.55 | 9.55 | 9.55 | 9.55
| KRT031 | FALSE | 16.87 | 16.86 | 16.9 | 16.95 | 16.96 | 16.95 | 16.98 | 17.04 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1
| KYM001 | FALSE | 8.03 | 8.08 | 8.2 | 8.32 | 8.33 | 8.35 | 8.46 | 8.63 | 8.69 | 8.69 | 8.69 | 8.69 | 8.69 | 8.69 | 8.69 | 8.69 | 8.69 | 8.69 | 8.69 | 8.69
| KYM002 | FALSE | 5.81 | 5.75 | 5.75 | 5.65 | 5.59 | 5.55 | 5.54 | 5.5 | 5.47 | 5.47 | 5.47 | 5.47 | 5.47 | 5.47 | 5.47 | 5.47 | 5.47 | 5.47 | 5.47 | 5.47
| KYM003 | FALSE | 5.36 | 5.38 | 5.46 | 5.52 | 5.5 | 5.52 | 5.61 | 5.74 | 5.71 | 5.71 | 5.71 | 5.71 | 5.71 | 5.71 | 5.71 | 5.71 | 5.71 | 5.71 | 5.71 | 5.71
| KYM004 | FALSE | 5.41 | 5.46 | 5.56 | 5.63 | 5.61 | 5.63 | 5.74 | 5.86 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85
| KYM005 | FALSE | 5.59 | 5.6 | 5.62 | 5.63 | 5.6 | 5.58 | 5.59 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61
| KYM006 | FALSE | 6.56 | 6.55 | 6.54 | 6.54 | 6.51 | 6.49 | 6.51 | 6.56 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53
| L001 | FALSE | 4.18 | 4.23 | 4.3 | 4.37 | 4.4 | 4.45 | 4.52 | 4.62 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68
| L002 | FALSE | 5.04 | 5.06 | 5.13 | 5.14 | 5.14 | 5.17 | 5.2 | 5.26 | 5.24 | 5.24 | 5.24 | 5.24 | 5.24 | 5.24 | 5.24 | 5.24 | 5.24 | 5.24 | 5.24 | 5.24
| L004 | FALSE | 2.14 | 2.17 | 2.2 | 2.23 | 2.25 | 2.27 | 2.3 | 2.34 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37
| L005 | FALSE | 4.9 | 4.93 | 4.99 | 5.02 | 5.03 | 5.06 | 5.09 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16
| L006 | FALSE | 2.53 | 2.47 | 2.44 | 2.42 | 2.38 | 2.36 | 2.34 | 2.33 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31
| L009 | FALSE | 2.99 | 3.04 | 3.09 | 3.14 | 3.17 | 3.21 | 3.26 | 3.34 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
| L010 | FALSE | 4.52 | 4.56 | 4.63 | 4.69 | 4.72 | 4.77 | 4.85 | 4.92 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
| L013 | FALSE | 2.36 | 2.33 | 2.32 | 2.31 | 2.3 | 2.29 | 2.3 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33
| L014 | FALSE | 4.08 | 4.08 | 4.1 | 4.13 | 4.13 | 4.13 | 4.16 | 4.2 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21
| L015 | FALSE | 2.53 | 2.53 | 2.55 | 2.56 | 2.56 | 2.57 | 2.58 | 2.62 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63
| L018 | FALSE | 2.88 | 2.92 | 2.99 | 3.03 | 3.07 | 3.11 | 3.17 | 3.23 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28
| L019 | FALSE | 4.61 | 4.65 | 4.72 | 4.79 | 4.83 | 4.88 | 4.96 | 5.05 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12
| L020 | FALSE | 2.67 | 2.69 | 2.72 | 2.74 | 2.75 | 2.76 | 2.78 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81
| L022 | FALSE | 4.65 | 4.71 | 4.78 | 4.82 | 4.83 | 4.86 | 4.92 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
| L023 | FALSE | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
| LFSF | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LQ001 | FALSE | 3.97 | 4.11 | 4.25 | 4.38 | 4.5 | 4.62 | 4.76 | 4.89 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03
| LQ002 | FALSE | 2.16 | 2.23 | 2.3 | 2.36 | 2.42 | 2.48 | 2.55 | 2.62 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.69
| LQ003 | FALSE | 2.91 | 3.01 | 3.11 | 3.21 | 3.29 | 3.37 | 3.47 | 3.58 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66
| LQ004 | FALSE | 4.23 | 4.3 | 4.37 | 4.43 | 4.49 | 4.55 | 4.61 | 4.7 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
| LQ007 | FALSE | 0.53 | 0.54 | 0.56 | 0.57 | 0.58 | 0.58 | 0.6 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63
| LQ008 | FALSE | 0.3 | 0.31 | 0.32 | 0.32 | 0.33 | 0.34 | 0.35 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
| LQ009 | FALSE | 2.12 | 2.18 | 2.26 | 2.32 | 2.36 | 2.41 | 2.49 | 2.57 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
| LQ010 | FALSE | 1.19 | 1.23 | 1.27 | 1.31 | 1.34 | 1.37 | 1.41 | 1.46 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49
| LQ011 | FALSE | 3.44 | 3.56 | 3.69 | 3.81 | 3.92 | 4.03 | 4.14 | 4.27 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39
| LQ012 | FALSE | 4.09 | 4.24 | 4.38 | 4.52 | 4.64 | 4.77 | 4.91 | 5.05 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18
| LQ014 | FALSE | 3.58 | 3.67 | 3.77 | 3.86 | 3.94 | 4.02 | 4.12 | 4.21 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31
| LQ015 | FALSE | 2.26 | 2.35 | 2.44 | 2.53 | 2.6 | 2.68 | 2.77 | 2.86 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94
| LQ016 | FALSE | 2.5 | 2.58 | 2.67 | 2.75 | 2.82 | 2.89 | 2.97 | 3.07 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14
| LQ017 | FALSE | 3.35 | 3.47 | 3.6 | 3.71 | 3.8 | 3.9 | 4.03 | 4.16 | 4.25 | 4.25 | 4.25 | 4.25 | 4.25 | 4.25 | 4.25 | 4.25 | 4.25 | 4.25 | 4.25 | 4.25
| LQ021 | FALSE | 2.75 | 2.85 | 2.95 | 3.04 | 3.13 | 3.22 | 3.32 | 3.42 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52
| LQ022 | FALSE | 2.99 | 3.1 | 3.2 | 3.3 | 3.39 | 3.48 | 3.58 | 3.68 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78
| LQ023 | FALSE | 2.91 | 3.02 | 3.13 | 3.24 | 3.34 | 3.45 | 3.55 | 3.67 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78
| LQ024 | FALSE | 3.21 | 3.33 | 3.44 | 3.55 | 3.66 | 3.75 | 3.87 | 3.99 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09
| LQ027 | FALSE | 0.74 | 0.77 | 0.8 | 0.82 | 0.84 | 0.87 | 0.89 | 0.92 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
| LQ028 | FALSE | 3.77 | 3.89 | 4.01 | 4.13 | 4.23 | 4.34 | 4.45 | 4.58 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69
| LQ029 | FALSE | 2.31 | 2.39 | 2.47 | 2.55 | 2.62 | 2.7 | 2.77 | 2.85 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93
| LQ030 | FALSE | 2.06 | 2.14 | 2.21 | 2.28 | 2.34 | 2.41 | 2.48 | 2.56 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62
| LQ033 | FALSE | 0.81 | 0.83 | 0.86 | 0.89 | 0.91 | 0.93 | 0.96 | 0.99 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01
| LQ034 | FALSE | 3.99 | 4.08 | 4.15 | 4.21 | 4.27 | 4.33 | 4.39 | 4.46 | 4.52 | 4.52 | 4.52 | 4.52 | 4.52 | 4.52 | 4.52 | 4.52 | 4.52 | 4.52 | 4.52 | 4.52
| LQ035 | FALSE | 0.79 | 0.81 | 0.84 | 0.86 | 0.87 | 0.88 | 0.91 | 0.94 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
| LQ040 | FALSE | 2.54 | 2.63 | 2.72 | 2.8 | 2.88 | 2.95 | 3.04 | 3.13 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
| LQ041 | FALSE | 2.5 | 2.54 | 2.59 | 2.63 | 2.64 | 2.66 | 2.7 | 2.76 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77
| LQ042 | FALSE | 2.34 | 2.42 | 2.5 | 2.58 | 2.65 | 2.73 | 2.8 | 2.88 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96
| LQ043 | FALSE | 2.17 | 2.25 | 2.32 | 2.4 | 2.46 | 2.52 | 2.59 | 2.67 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74
| LQ045 | FALSE | 0.98 | 1.01 | 1.05 | 1.08 | 1.11 | 1.14 | 1.17 | 1.21 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24
| LQ046 | FALSE | 2.77 | 2.88 | 2.98 | 3.08 | 3.16 | 3.24 | 3.33 | 3.43 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52
| LQ047 | FALSE | 3.03 | 3.13 | 3.24 | 3.34 | 3.44 | 3.53 | 3.63 | 3.74 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84
| LQ048 | FALSE | 3.11 | 3.22 | 3.33 | 3.43 | 3.52 | 3.62 | 3.72 | 3.83 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93
| LQ049 | FALSE | 2.93 | 3.03 | 3.14 | 3.24 | 3.33 | 3.42 | 3.52 | 3.62 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72
| LQ050 | FALSE | 1.77 | 1.83 | 1.89 | 1.95 | 2 | 2.05 | 2.11 | 2.17 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23
| LQ052 | FALSE | 3.92 | 4.05 | 4.19 | 4.32 | 4.44 | 4.55 | 4.68 | 4.82 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
| LQ054 | FALSE | 2.54 | 2.64 | 2.73 | 2.82 | 2.91 | 2.99 | 3.08 | 3.17 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26
| LQ055 | FALSE | 3.84 | 3.98 | 4.12 | 4.25 | 4.37 | 4.49 | 4.63 | 4.77 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9
| LQ056 | FALSE | 3.64 | 3.77 | 3.9 | 4.02 | 4.14 | 4.25 | 4.38 | 4.51 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63
| LV001 | FALSE | 13.12 | 9.27 | 9.41 | 9.54 | 9.65 | 9.71 | 9.87 | 10.06 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21
| LV002 | FALSE | 15.53 | 15.66 | 16.05 | 16.36 | 16.59 | 16.86 | 17.27 | 17.77 | 18.04 | 18.04 | 18.04 | 18.04 | 18.04 | 18.04 | 18.04 | 18.04 | 18.04 | 18.04 | 18.04 | 18.04
| LV003 | FALSE | 11.21 | 7.77 | 8.1 | 8.39 | 8.65 | 8.95 | 9.26 | 9.6 | 9.86 | 9.86 | 9.86 | 9.86 | 9.86 | 9.86 | 9.86 | 9.86 | 9.86 | 9.86 | 9.86 | 9.86
| LV004 | FALSE | 15.49 | 15.88 | 16.35 | 16.76 | 17.13 | 17.52 | 18.04 | 18.55 | 19.01 | 19.01 | 19.01 | 19.01 | 19.01 | 19.01 | 19.01 | 19.01 | 19.01 | 19.01 | 19.01 | 19.01
| LV005 | FALSE | 14.85 | 15.38 | 15.97 | 16.54 | 17.01 | 17.47 | 18.1 | 18.79 | 19.32 | 19.32 | 19.32 | 19.32 | 19.32 | 19.32 | 19.32 | 19.32 | 19.32 | 19.32 | 19.32 | 19.32
| LV006 | FALSE | 6 | 6.21 | 6.46 | 6.68 | 6.86 | 7.04 | 7.28 | 7.54 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73
| LV007 | FALSE | 9.81 | 10.28 | 10.77 | 11.23 | 11.66 | 12.09 | 12.73 | 13.26 | 13.66 | 13.66 | 13.66 | 13.66 | 13.66 | 13.66 | 13.66 | 13.66 | 13.66 | 13.66 | 13.66 | 13.66
| LV008 | FALSE | 14.76 | 15 | 15.34 | 15.64 | 15.83 | 16.05 | 16.35 | 16.75 | 17.04 | 17.04 | 17.04 | 17.04 | 17.04 | 17.04 | 17.04 | 17.04 | 17.04 | 17.04 | 17.04 | 17.04
| LV009 | FALSE | 7.77 | 7.71 | 7.69 | 7.66 | 7.57 | 7.5 | 7.46 | 7.47 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41
| LV010 | FALSE | 6.8 | 6.82 | 6.88 | 6.91 | 6.94 | 6.99 | 7.04 | 7.14 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17
| LVN001 | FALSE | 24.85 | 25.69 | 26.48 | 27.25 | 27.97 | 28.66 | 29.37 | 30.12 | 30.85 | 30.85 | 30.85 | 30.85 | 30.85 | 30.85 | 30.85 | 30.85 | 30.85 | 30.85 | 30.85 | 30.85
| LVN021 | FALSE | 19.07 | 20.12 | 21.22 | 22.22 | 23.08 | 23.98 | 25 | 26.06 | 26.84 | 26.84 | 26.84 | 26.84 | 26.84 | 26.84 | 26.84 | 26.84 | 26.84 | 26.84 | 26.84 | 26.84
| LVN022 | FALSE | 14.23 | 14.42 | 14.67 | 14.88 | 15.01 | 15.18 | 15.46 | 15.84 | 15.98 | 15.98 | 15.98 | 15.98 | 15.98 | 15.98 | 15.98 | 15.98 | 15.98 | 15.98 | 15.98 | 15.98
| LVN023 | FALSE | 12.98 | 13.38 | 13.8 | 14.2 | 14.54 | 14.88 | 15.28 | 15.71 | 16.05 | 16.05 | 16.05 | 16.05 | 16.05 | 16.05 | 16.05 | 16.05 | 16.05 | 16.05 | 16.05 | 16.05
| LVN024 | FALSE | 11.26 | 11.98 | 12.69 | 13.38 | 14 | 14.59 | 15.22 | 15.89 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5
| LVN031 | FALSE | 18.06 | 18.45 | 18.82 | 19.17 | 19.5 | 19.82 | 20.15 | 20.5 | 20.84 | 20.84 | 20.84 | 20.84 | 20.84 | 20.84 | 20.84 | 20.84 | 20.84 | 20.84 | 20.84 | 20.84
| LVN032 | FALSE | 15.8 | 16.26 | 16.72 | 17.17 | 17.57 | 17.96 | 18.37 | 18.81 | 19.22 | 19.22 | 19.22 | 19.22 | 19.22 | 19.22 | 19.22 | 19.22 | 19.22 | 19.22 | 19.22 | 19.22
| LVN033 | FALSE | 12.88 | 13.18 | 13.61 | 13.93 | 14.11 | 14.29 | 14.71 | 15.21 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36
| LVN034 | FALSE | 10.47 | 10.72 | 11 | 11.25 | 11.46 | 11.67 | 11.93 | 12.21 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43
| MBN012 | FALSE | 9.85 | 10 | 10.18 | 10.34 | 10.46 | 10.6 | 10.78 | 10.99 | 11.14 | 11.14 | 11.14 | 11.14 | 11.14 | 11.14 | 11.14 | 11.14 | 11.14 | 11.14 | 11.14 | 11.14
| MBN013 | FALSE | 4.03 | 4.04 | 4.09 | 4.13 | 4.14 | 4.15 | 4.2 | 4.27 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28 | 4.28
| MBN014 | FALSE | 6.75 | 6.83 | 6.95 | 7.03 | 7.05 | 7.1 | 7.21 | 7.35 | 7.36 | 7.36 | 7.36 | 7.36 | 7.36 | 7.36 | 7.36 | 7.36 | 7.36 | 7.36 | 7.36 | 7.36
| MBN023 | FALSE | 13.63 | 13.65 | 13.73 | 13.78 | 13.74 | 13.72 | 13.79 | 13.88 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
| MBN031 | FALSE | 5.85 | 5.9 | 6.01 | 6.09 | 6.1 | 6.13 | 6.24 | 6.37 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38
| MBN032 | FALSE | 12.9 | 13.16 | 13.46 | 13.7 | 13.84 | 14.02 | 14.33 | 14.69 | 14.81 | 14.81 | 14.81 | 14.81 | 14.81 | 14.81 | 14.81 | 14.81 | 14.81 | 14.81 | 14.81 | 14.81
| MDA022 | FALSE | 8.82 | 8.68 | 8.62 | 8.58 | 8.48 | 8.4 | 8.38 | 8.39 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34
| MDA023 | FALSE | 17.42 | 17.57 | 17.82 | 17.99 | 18.06 | 18.17 | 18.41 | 18.7 | 18.78 | 18.78 | 18.78 | 18.78 | 18.78 | 18.78 | 18.78 | 18.78 | 18.78 | 18.78 | 18.78 | 18.78
| MDA024 | FALSE | 7.86 | 7.81 | 7.84 | 7.85 | 7.82 | 7.81 | 7.85 | 7.9 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88
| MDA031 | FALSE | 5.7 | 5.65 | 5.62 | 5.6 | 5.53 | 5.49 | 5.49 | 5.51 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46
| MDA032 | FALSE | 7.57 | 7.6 | 7.65 | 7.66 | 7.63 | 7.63 | 7.69 | 7.77 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75
| MDA033 | FALSE | 4.61 | 4.68 | 4.75 | 4.82 | 4.87 | 4.92 | 4.99 | 5.08 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13
| MDA034 | FALSE | 6.41 | 6.51 | 6.63 | 6.72 | 6.77 | 6.84 | 6.95 | 7.09 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17
| MG001 | FALSE | 4.05 | 4.09 | 4.13 | 4.15 | 4.15 | 4.16 | 4.22 | 4.29 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32
| MG002 | FALSE | 1.8 | 1.81 | 1.82 | 1.84 | 1.85 | 1.86 | 1.89 | 1.92 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95
| MG004 | FALSE | 4.49 | 4.6 | 4.68 | 4.77 | 4.84 | 4.95 | 5.13 | 5.3 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44
| MG006 | FALSE | 3.53 | 3.59 | 3.65 | 3.71 | 3.75 | 3.79 | 3.84 | 3.91 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95
| MG009 | FALSE | 1.44 | 1.51 | 1.57 | 1.62 | 1.68 | 1.75 | 1.87 | 2.01 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13
| MG013 | FALSE | 1.81 | 1.82 | 1.83 | 1.83 | 1.83 | 1.83 | 1.84 | 1.85 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86
| MG014 | FALSE | 3.86 | 3.87 | 3.87 | 3.88 | 3.88 | 3.89 | 3.91 | 3.96 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94
| MG015 | FALSE | 1.76 | 1.79 | 1.8 | 1.81 | 1.81 | 1.81 | 1.82 | 1.85 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84
| MG018 | FALSE | 3.73 | 4.14 | 4.57 | 4.99 | 5.4 | 5.82 | 6.27 | 6.73 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17
| MG019 | FALSE | 9.03 | 9.22 | 9.31 | 9.4 | 9.46 | 9.52 | 9.68 | 9.86 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01
| MG020 | FALSE | 6.04 | 6.04 | 6.05 | 6.06 | 6.06 | 6.06 | 6.09 | 6.12 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16
| MG022 | FALSE | 2.16 | 2.4 | 2.65 | 2.9 | 3.14 | 3.38 | 3.64 | 3.91 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16
| MG023 | FALSE | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.19 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
| MG024 | FALSE | 1.39 | 1.51 | 1.64 | 1.77 | 1.89 | 2.01 | 2.14 | 2.27 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
| MLN011 | FALSE | 13.09 | 13.73 | 14.47 | 15.14 | 15.74 | 16.37 | 17.13 | 18.09 | 18.68 | 18.68 | 18.68 | 18.68 | 18.68 | 18.68 | 18.68 | 18.68 | 18.68 | 18.68 | 18.68 | 18.68
| MLN012 | FALSE | 8.25 | 8.5 | 8.79 | 9.07 | 9.28 | 9.51 | 9.79 | 10.14 | 10.37 | 10.37 | 10.37 | 10.37 | 10.37 | 10.37 | 10.37 | 10.37 | 10.37 | 10.37 | 10.37 | 10.37
| MLN013 | FALSE | 14 | 14.58 | 15.22 | 15.77 | 16.32 | 16.9 | 17.55 | 18.34 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83
| MLN014 | FALSE | 10.64 | 11.05 | 11.53 | 11.97 | 12.35 | 12.76 | 13.26 | 13.82 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28
| MLN021 | FALSE | 18.67 | 19.95 | 21.45 | 23.08 | 24.31 | 25.91 | 27.61 | 29.46 | 30.99 | 30.99 | 30.99 | 30.99 | 30.99 | 30.99 | 30.99 | 30.99 | 30.99 | 30.99 | 30.99 | 30.99
| MLN022 | FALSE | 9.86 | 10.02 | 10.34 | 10.64 | 10.89 | 11.12 | 11.47 | 11.92 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21
| MLN023 | FALSE | 8.73 | 9.11 | 9.55 | 9.95 | 10.31 | 10.69 | 11.14 | 11.66 | 12.09 | 12.09 | 12.09 | 12.09 | 12.09 | 12.09 | 12.09 | 12.09 | 12.09 | 12.09 | 12.09 | 12.09
| MLN024 | FALSE | 9.1 | 9.3 | 9.55 | 9.78 | 9.98 | 10.2 | 10.42 | 10.7 | 10.94 | 10.94 | 10.94 | 10.94 | 10.94 | 10.94 | 10.94 | 10.94 | 10.94 | 10.94 | 10.94 | 10.94
| MLN031 | FALSE | 2 | 2 | 9.36 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
| MLN032 | FALSE | 9.17 | 9.52 | 9.92 | 10.28 | 10.59 | 10.93 | 11.34 | 11.81 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17
| MLN033 | FALSE | 20.66 | 16.79 | 18.15 | 19.45 | 20.67 | 21.91 | 23.33 | 24.99 | 26.25 | 26.25 | 26.25 | 26.25 | 26.25 | 26.25 | 26.25 | 26.25 | 26.25 | 26.25 | 26.25 | 26.25
| MNA013 | FALSE | 9.18 | 9.18 | 9.18 | 9.21 | 9.2 | 9.18 | 9.19 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
| MNA014 | FALSE | 12.15 | 12.26 | 12.45 | 12.58 | 12.59 | 12.65 | 12.9 | 13.18 | 13.14 | 13.14 | 13.14 | 13.14 | 13.14 | 13.14 | 13.14 | 13.14 | 13.14 | 13.14 | 13.14 | 13.14
| MNA021 | FALSE | 8.82 | 8.82 | 8.85 | 8.86 | 8.83 | 8.81 | 8.86 | 8.92 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89 | 8.89
| MNA022 | FALSE | 5.89 | 5.91 | 5.97 | 5.98 | 6 | 6.02 | 6.07 | 6.13 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15
| MNA024 | FALSE | 7.87 | 8.03 | 8.19 | 8.37 | 8.49 | 8.63 | 8.83 | 9.03 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2
| MNA034 | FALSE | 6.59 | 6.65 | 6.73 | 6.78 | 6.78 | 6.8 | 6.89 | 6.99 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97
| MP001 | FALSE | 3.34 | 3.29 | 3.24 | 3.19 | 3.15 | 3.1 | 3.06 | 3.03 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| MP005 | FALSE | 4.14 | 4.26 | 4.38 | 4.49 | 4.58 | 4.67 | 4.8 | 4.94 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02
| MP006 | FALSE | 4.69 | 4.57 | 4.46 | 4.35 | 4.24 | 4.14 | 4.05 | 3.98 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91
| MP007 | FALSE | 7.17 | 7.21 | 7.26 | 7.31 | 7.35 | 7.39 | 7.46 | 7.54 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61
| MP008 | FALSE | 2.61 | 2.63 | 2.67 | 2.7 | 2.71 | 2.74 | 2.78 | 2.83 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85
| MP009 | FALSE | 2.47 | 2.41 | 2.35 | 2.3 | 2.24 | 2.19 | 2.14 | 2.1 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06
| MP015 | FALSE | 3.08 | 3.01 | 2.94 | 2.87 | 2.8 | 2.74 | 2.69 | 2.64 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59
| MP016 | FALSE | 1.37 | 1.36 | 1.36 | 1.36 | 1.35 | 1.35 | 1.35 | 1.35 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34
| MP018 | FALSE | 3.87 | 3.91 | 3.94 | 3.97 | 3.99 | 4.01 | 4.04 | 4.09 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13
| MP020 | FALSE | 2.36 | 2.4 | 2.45 | 2.49 | 2.5 | 2.53 | 2.58 | 2.65 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
| MP021 | FALSE | 4.71 | 4.7 | 4.71 | 4.72 | 4.72 | 4.72 | 4.74 | 4.76 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77
| MP029 | FALSE | 2.71 | 2.73 | 2.76 | 2.78 | 2.8 | 2.82 | 2.85 | 2.89 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92 | 2.92
| MP030 | FALSE | 4.01 | 4.03 | 4.07 | 4.1 | 4.12 | 4.15 | 4.19 | 4.26 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
| MP031 | FALSE | 3.1 | 3.13 | 3.18 | 3.22 | 3.24 | 3.27 | 3.32 | 3.39 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41
| MP032 | FALSE | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
| MP033 | FALSE | 3.39 | 3.46 | 3.49 | 3.5 | 3.51 | 3.53 | 3.53 | 3.55 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56
| MP035 | FALSE | 2.03 | 2.04 | 2.06 | 2.08 | 2.09 | 2.1 | 2.12 | 2.15 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17
| MP036 | FALSE | 3.16 | 3.17 | 3.18 | 3.19 | 3.2 | 3.2 | 3.22 | 3.25 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27
| MP037 | FALSE | 4.55 | 4.58 | 4.62 | 4.65 | 4.67 | 4.7 | 4.74 | 4.79 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84
| MP038 | FALSE | 4.25 | 4.22 | 4.16 | 4.1 | 4.05 | 3.99 | 3.95 | 3.9 | 3.87 | 3.87 | 3.87 | 3.87 | 3.87 | 3.87 | 3.87 | 3.87 | 3.87 | 3.87 | 3.87 | 3.87
| MP040 | FALSE | 3.25 | 3.17 | 3.09 | 3.02 | 2.94 | 2.87 | 2.81 | 2.76 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71
| MP044 | FALSE | 3.05 | 2.98 | 2.93 | 2.87 | 2.81 | 2.75 | 2.71 | 2.68 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64
| MP047 | FALSE | 3.3 | 3.35 | 3.42 | 3.47 | 3.5 | 3.53 | 3.61 | 3.69 | 3.71 | 3.71 | 3.71 | 3.71 | 3.71 | 3.71 | 3.71 | 3.71 | 3.71 | 3.71 | 3.71 | 3.71
| MP048 | FALSE | 5.03 | 5.2 | 5.37 | 5.53 | 5.68 | 5.82 | 5.98 | 6.14 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31
| MP049 | FALSE | 1.99 | 1.94 | 1.9 | 1.86 | 1.82 | 1.78 | 1.75 | 1.72 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69
| MP050 | FALSE | 3.65 | 3.65 | 3.6 | 3.55 | 3.48 | 3.42 | 3.37 | 3.33 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28
| MP051 | FALSE | 1.61 | 1.62 | 1.64 | 1.65 | 1.67 | 1.68 | 1.7 | 1.72 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74
| MP053 | FALSE | 4.88 | 4.91 | 4.94 | 4.98 | 5 | 5.03 | 5.07 | 5.12 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17 | 5.17
| MP054 | FALSE | 2.41 | 2.43 | 2.45 | 2.46 | 2.48 | 2.49 | 2.51 | 2.54 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56
| MP055 | FALSE | 3.72 | 3.61 | 3.49 | 3.38 | 3.28 | 3.2 | 3.15 | 3.09 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03
| MP058 | FALSE | 3.81 | 3.79 | 3.77 | 3.76 | 3.74 | 3.73 | 3.73 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74
| MP062 | FALSE | 3.52 | 3.56 | 3.6 | 3.64 | 3.66 | 3.69 | 3.74 | 3.79 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84
| MP064 | FALSE | 3.38 | 3.4 | 3.43 | 3.45 | 3.47 | 3.49 | 3.52 | 3.56 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59
| MP067 | FALSE | 3.68 | 3.71 | 3.75 | 3.79 | 3.8 | 3.82 | 3.87 | 3.93 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96
| MRO002 | FALSE | 1.12 | 1.11 | 1.11 | 1.11 | 1.11 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
| MRO004 | FALSE | 3.99 | 4 | 4.03 | 4.04 | 4.03 | 4.02 | 4.04 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07
| MRO005 | FALSE | 5.91 | 5.94 | 5.98 | 6.01 | 6.01 | 6.02 | 6.05 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08
| MRO006 | FALSE | 3.43 | 3.42 | 3.43 | 3.42 | 3.41 | 3.39 | 3.39 | 3.4 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
| MRO007 | FALSE | 5.56 | 5.61 | 5.69 | 5.77 | 5.8 | 5.82 | 5.91 | 6.01 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04
| MRO008 | FALSE | 6.5 | 6.52 | 6.56 | 6.59 | 6.59 | 6.6 | 6.65 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
| MTC011 | FALSE | 0 | 17.49 | 18.43 | 19.09 | 19.72 | 20.34 | 21.1 | 21.87 | 22.46 | 22.46 | 22.46 | 22.46 | 22.46 | 22.46 | 22.46 | 22.46 | 22.46 | 22.46 | 22.46 | 22.46
| MTC012 | FALSE | 0 | 17.09 | 17.95 | 18.52 | 19.05 | 19.58 | 20.23 | 20.91 | 21.41 | 21.41 | 21.41 | 21.41 | 21.41 | 21.41 | 21.41 | 21.41 | 21.41 | 21.41 | 21.41 | 21.41
| MTC013 | FALSE | 0 | 13.15 | 13.51 | 13.8 | 13.88 | 14.03 | 14.24 | 14.48 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 14.6
| MTC014 | FALSE | 0 | 18.2 | 18.97 | 19.7 | 20.32 | 20.95 | 21.72 | 22.64 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28
| MTC015 | FALSE | 0 | 13.59 | 14.52 | 15.42 | 16.25 | 17.08 | 18.05 | 19.17 | 20.03 | 20.03 | 20.03 | 20.03 | 20.03 | 20.03 | 20.03 | 20.03 | 20.03 | 20.03 | 20.03 | 20.03
| MTC016 | FALSE | 0 | 8.34 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75
| MTC017 | FALSE | 0 | 11.19 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
| NC001 | FALSE | 4.12 | 4.26 | 4.32 | 4.37 | 4.4 | 4.45 | 4.5 | 4.58 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62 | 4.62
| NC002 | FALSE | 4.55 | 4.66 | 4.78 | 4.89 | 4.99 | 5.11 | 5.27 | 5.37 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46
| NC004 | FALSE | 4.82 | 4.92 | 4.98 | 5.07 | 5.14 | 5.22 | 5.36 | 5.49 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55
| NC005 | FALSE | 3.84 | 3.94 | 4.05 | 4.13 | 4.2 | 4.3 | 4.42 | 4.56 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63 | 4.63
| NC006 | FALSE | 3.91 | 4.01 | 4.1 | 4.2 | 4.26 | 4.33 | 4.43 | 4.53 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61
| NC009 | FALSE | 3.07 | 3.15 | 3.26 | 3.35 | 3.42 | 3.5 | 3.59 | 3.71 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78
| NC010 | FALSE | 2.59 | 2.66 | 2.74 | 2.82 | 2.87 | 2.93 | 3.01 | 3.12 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
| NC013 | FALSE | 3.83 | 3.91 | 4.01 | 4.09 | 4.16 | 4.22 | 4.31 | 4.43 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
| NC014 | FALSE | 3.54 | 3.5 | 3.51 | 3.56 | 3.6 | 3.66 | 3.7 | 3.79 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84
| NC015 | FALSE | 5.43 | 5.57 | 5.72 | 5.84 | 5.95 | 6.04 | 6.2 | 6.36 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46
| NHL015 | FALSE | 3.37 | 3.36 | 3.37 | 3.36 | 3.33 | 3.3 | 3.3 | 3.3 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27
| NHL016 | FALSE | 3.49 | 3.45 | 3.44 | 3.41 | 3.36 | 3.32 | 3.3 | 3.29 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24
| NHL031 | FALSE | 9.33 | 9.17 | 9.09 | 9.08 | 8.97 | 8.84 | 8.73 | 8.73 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66
| NKA001 | FALSE | 2.58 | 2.61 | 2.66 | 2.69 | 2.69 | 2.71 | 2.76 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83
| NKA002 | FALSE | 5.94 | 5.95 | 6.02 | 6.07 | 6.07 | 6.07 | 6.14 | 6.24 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23
| NKA003 | FALSE | 4.57 | 4.56 | 4.56 | 4.55 | 4.53 | 4.51 | 4.51 | 4.52 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
| NKA004 | FALSE | 10.52 | 10.68 | 10.9 | 11.09 | 11.11 | 11.17 | 11.43 | 11.75 | 11.75 | 11.75 | 11.75 | 11.75 | 11.75 | 11.75 | 11.75 | 11.75 | 11.75 | 11.75 | 11.75 | 11.75
| NKA005 | FALSE | 4.46 | 4.52 | 4.61 | 4.67 | 4.68 | 4.71 | 4.8 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92
| NKA006 | FALSE | 8.49 | 9.81 | 9.94 | 10.03 | 10.01 | 10.03 | 10.16 | 10.3 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29
| NR002 | FALSE | 7.5 | 7.62 | 7.77 | 7.87 | 7.98 | 8.12 | 8.3 | 8.49 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6
| NR003 | FALSE | 5.28 | 5.34 | 5.38 | 5.41 | 5.41 | 5.42 | 5.46 | 5.48 | 5.53 | 5.53 | 5.53 | 5.53 | 5.53 | 5.53 | 5.53 | 5.53 | 5.53 | 5.53 | 5.53 | 5.53
| NR004 | FALSE | 3.72 | 3.84 | 3.97 | 4.09 | 4.2 | 4.32 | 4.44 | 4.58 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7
| NR006 | FALSE | 8.97 | 9.1 | 9.28 | 9.45 | 9.59 | 9.74 | 9.92 | 10.08 | 10.25 | 10.25 | 10.25 | 10.25 | 10.25 | 10.25 | 10.25 | 10.25 | 10.25 | 10.25 | 10.25 | 10.25
| NR007 | FALSE | 6.21 | 6.32 | 6.45 | 6.56 | 6.65 | 6.73 | 6.86 | 6.98 | 7.06 | 7.06 | 7.06 | 7.06 | 7.06 | 7.06 | 7.06 | 7.06 | 7.06 | 7.06 | 7.06 | 7.06
| NR011_NR012 | FALSE | 4.33 | 4.43 | 4.59 | 4.7 | 4.73 | 4.8 | 4.97 | 5.16 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15
| NR013 | FALSE | 2.78 | 2.84 | 2.91 | 2.97 | 3.03 | 3.09 | 3.15 | 3.22 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28
| NR015 | FALSE | 4.77 | 4.86 | 4.99 | 5.11 | 5.22 | 5.32 | 5.46 | 5.63 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72
| NR016 | FALSE | 5.54 | 5.67 | 5.82 | 5.96 | 6.07 | 6.18 | 6.33 | 6.52 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63
| NR021 | FALSE | 2.77 | 2.84 | 2.92 | 2.99 | 3.05 | 3.11 | 3.2 | 3.28 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34
| NR022 | FALSE | 6.55 | 6.68 | 6.83 | 6.95 | 7.02 | 7.11 | 7.23 | 7.34 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41
| NR024 | FALSE | 2.61 | 2.65 | 2.71 | 2.76 | 2.81 | 2.86 | 2.92 | 3 | 3.06 | 3.06 | 3.06 | 3.06 | 3.06 | 3.06 | 3.06 | 3.06 | 3.06 | 3.06 | 3.06 | 3.06
| NR025 | FALSE | 3.28 | 3.34 | 3.42 | 3.49 | 3.53 | 3.58 | 3.67 | 3.76 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79
| NR042 | FALSE | 9.76 | 9.91 | 10.05 | 10.19 | 10.3 | 10.45 | 10.63 | 10.84 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02
| NS010 | FALSE | 0.88 | 0.9 | 0.92 | 0.94 | 0.95 | 0.97 | 0.99 | 1.01 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03
| NS013 | FALSE | 3.21 | 3.25 | 3.28 | 3.3 | 3.31 | 3.33 | 3.36 | 3.39 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| OYN001 | FALSE | 1.76 | 1.75 | 1.76 | 1.77 | 1.75 | 1.74 | 1.75 | 1.76 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74
| OYN003 | FALSE | 0.67 | 0.67 | 0.67 | 0.67 | 0.66 | 0.66 | 0.66 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67
| OYN005 | FALSE | 3.28 | 3.29 | 3.3 | 3.31 | 3.29 | 3.27 | 3.28 | 3.3 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27
| OYN007 | FALSE | 2.15 | 2.13 | 2.12 | 2.11 | 2.09 | 2.06 | 2.05 | 2.04 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01
| PLD001 | FALSE | 4.28 | 4.27 | 4.27 | 4.27 | 4.24 | 4.23 | 4.25 | 4.28 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26
| PLD002 | FALSE | 1.76 | 1.76 | 1.77 | 1.78 | 1.77 | 1.77 | 1.78 | 1.79 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
| PLD003 | FALSE | 2.11 | 2.11 | 2.13 | 2.14 | 2.14 | 2.13 | 2.14 | 2.16 | 2.16 | 2.16 | 2.16 | 2.16 | 2.16 | 2.16 | 2.16 | 2.16 | 2.16 | 2.16 | 2.16 | 2.16
| PLD004 | FALSE | 5.31 | 5.16 | 5.07 | 5.03 | 4.99 | 4.97 | 4.97 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99
| PLD005 | FALSE | 2.37 | 2.35 | 2.33 | 2.31 | 2.3 | 2.28 | 2.27 | 2.26 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25
| PLD006 | FALSE | 4.33 | 4.26 | 4.25 | 4.24 | 4.18 | 4.14 | 4.14 | 4.16 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14
| PM001 | FALSE | 1.98 | 2.07 | 2.19 | 2.31 | 2.4 | 2.5 | 2.64 | 2.79 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89
| PM002 | FALSE | 1.77 | 1.77 | 1.74 | 1.7 | 1.65 | 1.6 | 1.57 | 1.54 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48
| PM003 | FALSE | 2.37 | 2.4 | 2.46 | 2.51 | 2.54 | 2.58 | 2.63 | 2.7 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73
| PM004 | FALSE | 3.38 | 3.67 | 3.96 | 4.25 | 4.52 | 4.78 | 5.06 | 5.34 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61
| PM005 | FALSE | 2.38 | 2.41 | 2.45 | 2.48 | 2.51 | 2.54 | 2.57 | 2.61 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64
| PM006 | FALSE | 1.56 | 1.57 | 1.58 | 1.59 | 1.59 | 1.6 | 1.61 | 1.62 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63
| PM007 | FALSE | 0.85 | 0.9 | 0.96 | 1.02 | 1.07 | 1.11 | 1.18 | 1.25 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29
| PM008 | FALSE | 2.31 | 2.57 | 2.83 | 3.1 | 3.37 | 3.63 | 3.91 | 4.19 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48
| PM009 | FALSE | 2.52 | 2.56 | 2.6 | 2.64 | 2.67 | 2.7 | 2.74 | 2.79 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81
| PM010 | FALSE | 1.07 | 1.19 | 1.32 | 1.45 | 1.57 | 1.7 | 1.84 | 1.97 | 2.11 | 2.11 | 2.11 | 2.11 | 2.11 | 2.11 | 2.11 | 2.11 | 2.11 | 2.11 | 2.11 | 2.11
| PM011 | FALSE | 0.17 | 0.18 | 0.2 | 0.22 | 0.24 | 0.26 | 0.28 | 0.3 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
| PM012 | FALSE | 1.64 | 1.65 | 1.67 | 1.68 | 1.68 | 1.68 | 1.7 | 1.72 | 1.72 | 1.72 | 1.72 | 1.72 | 1.72 | 1.72 | 1.72 | 1.72 | 1.72 | 1.72 | 1.72 | 1.72
| Q001 | FALSE | 2.93 | 2.88 | 2.83 | 2.8 | 2.76 | 2.73 | 2.7 | 2.66 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63
| Q002 | FALSE | 6.32 | 6.41 | 6.51 | 6.6 | 6.63 | 6.68 | 6.79 | 6.91 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96
| Q004 | FALSE | 3.38 | 3.33 | 3.29 | 3.25 | 3.22 | 3.2 | 3.16 | 3.16 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
| Q005 | FALSE | 3.22 | 3.2 | 3.22 | 3.23 | 3.24 | 3.25 | 3.27 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
| Q006 | FALSE | 4.62 | 4.56 | 4.51 | 4.45 | 4.34 | 4.34 | 4.38 | 4.38 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35 | 4.35
| Q009 | FALSE | 4.29 | 4.27 | 4.29 | 4.28 | 4.26 | 4.27 | 4.27 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29
| Q010 | FALSE | 4.21 | 4.14 | 4.1 | 4.06 | 4.02 | 3.98 | 3.97 | 3.96 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92
| Q013 | FALSE | 2.88 | 2.9 | 2.93 | 2.95 | 2.96 | 2.99 | 3.02 | 3.06 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07
| Q014 | FALSE | 4.94 | 5 | 5.07 | 5.11 | 5.12 | 5.15 | 5.23 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3
| Q015 | FALSE | 1.58 | 1.59 | 1.6 | 1.6 | 1.6 | 1.61 | 1.62 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64
| Q019 | FALSE | 5.7 | 5.74 | 5.79 | 5.86 | 5.88 | 5.87 | 5.92 | 5.98 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| R021 | FALSE | 2.75 | 2.83 | 2.93 | 3 | 3.08 | 3.15 | 3.23 | 3.31 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
| R022 | FALSE | 3.22 | 3.29 | 3.36 | 3.42 | 3.46 | 3.5 | 3.56 | 3.63 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| R023 | FALSE | 6.46 | 6.65 | 6.86 | 7.06 | 7.22 | 7.38 | 7.58 | 7.81 | 7.95 | 7.95 | 7.95 | 7.95 | 7.95 | 7.95 | 7.95 | 7.95 | 7.95 | 7.95 | 7.95 | 7.95
| R024 | FALSE | 4.91 | 4.97 | 5.01 | 5.03 | 5.04 | 5.03 | 5.06 | 5.11 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09
| R031 | FALSE | 5.91 | 7.76 | 7.98 | 8 | 7.9 | 7.87 | 7.88 | 7.98 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96 | 7.96
| R032 | FALSE | 5.01 | 5.11 | 5.25 | 5.37 | 5.47 | 5.6 | 5.75 | 5.91 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01 | 6.01
| R033 | FALSE | 10.75 | 10.79 | 10.88 | 10.98 | 11.04 | 11.11 | 11.21 | 11.34 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4
| R035 | FALSE | 4.8 | 6.63 | 6.98 | 7.01 | 7.01 | 7.01 | 7.05 | 7.11 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09
| RCT011 | FALSE | 3.94 | 4 | 4.07 | 4.14 | 4.16 | 4.2 | 4.28 | 4.37 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
| RCT012 | FALSE | 3.69 | 3.69 | 3.69 | 3.69 | 3.68 | 3.67 | 3.67 | 3.67 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68
| RCT013 | FALSE | 11.26 | 11.28 | 11.39 | 11.43 | 11.38 | 11.37 | 11.5 | 11.67 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6
| RCT014 | FALSE | 9.89 | 9.91 | 9.95 | 9.96 | 9.92 | 9.91 | 9.97 | 10.03 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01
| RCT015 | FALSE | 3.34 | 3.35 | 3.36 | 3.37 | 3.38 | 3.39 | 3.4 | 3.41 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43
| RCT021 | FALSE | 5.54 | 5.6 | 5.7 | 5.75 | 5.77 | 5.8 | 5.9 | 6 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02
| RCT022 | FALSE | 7.71 | 7.84 | 8.06 | 8.22 | 8.24 | 8.33 | 8.59 | 8.87 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84
| RCT023 | FALSE | 10.21 | 10.29 | 10.49 | 10.64 | 10.69 | 10.75 | 10.94 | 11.19 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23
| RD001 | FALSE | 4.08 | 4.12 | 4.2 | 4.25 | 4.29 | 4.31 | 4.38 | 4.45 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47
| RD002 | FALSE | 4.47 | 4.52 | 4.58 | 4.63 | 4.65 | 4.69 | 4.75 | 4.84 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87
| RD004 | FALSE | 4.77 | 4.83 | 4.92 | 4.99 | 5.01 | 5.04 | 5.13 | 5.22 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23
| RD005 | FALSE | 4.01 | 4.04 | 4.1 | 4.14 | 4.15 | 4.17 | 4.22 | 4.29 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31
| RD006 | FALSE | 4.18 | 4.03 | 4 | 3.98 | 3.99 | 4 | 4.04 | 4.07 | 4.08 | 4.08 | 4.08 | 4.08 | 4.08 | 4.08 | 4.08 | 4.08 | 4.08 | 4.08 | 4.08 | 4.08
| RD009 | FALSE | 3.72 | 3.75 | 3.8 | 3.83 | 3.85 | 3.88 | 3.92 | 3.99 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| RD010 | FALSE | 3.38 | 3.42 | 3.48 | 3.52 | 3.54 | 3.56 | 3.61 | 3.66 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69
| RD013 | FALSE | 4.16 | 4.18 | 4.23 | 4.27 | 4.28 | 4.3 | 4.34 | 4.4 | 4.42 | 4.42 | 4.42 | 4.42 | 4.42 | 4.42 | 4.42 | 4.42 | 4.42 | 4.42 | 4.42 | 4.42
| RD014 | FALSE | 6.59 | 6.66 | 6.76 | 6.85 | 6.88 | 6.92 | 7 | 7.14 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23
| RD015 | FALSE | 2.67 | 2.71 | 2.75 | 2.79 | 2.82 | 2.85 | 2.88 | 2.95 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97
| RTS-MTMSY | FALSE | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
| RVL001 | FALSE | 6.65 | 7.45 | 7.55 | 7.62 | 7.62 | 7.66 | 7.77 | 7.88 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87 | 7.87
| RVL004 | FALSE | 12.2 | 12.42 | 12.72 | 12.98 | 13.08 | 13.2 | 13.52 | 13.91 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97
| RVL006 | FALSE | 7.11 | 7.16 | 7.28 | 7.37 | 7.41 | 7.46 | 7.55 | 7.66 | 7.72 | 7.72 | 7.72 | 7.72 | 7.72 | 7.72 | 7.72 | 7.72 | 7.72 | 7.72 | 7.72 | 7.72
| RVL008 | FALSE | 5.42 | 6.54 | 6.72 | 6.84 | 6.88 | 6.95 | 7.13 | 7.34 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35
| SA001 | FALSE | 5.22 | 5.3 | 5.4 | 5.43 | 5.5 | 5.58 | 5.67 | 5.8 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88
| SA002 | FALSE | 7.58 | 7.63 | 7.7 | 7.76 | 7.77 | 7.79 | 7.86 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94
| SA003 | FALSE | 8.95 | 9.05 | 9.19 | 9.28 | 9.3 | 9.34 | 9.51 | 9.71 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78
| SA004 | FALSE | 5.25 | 5.33 | 5.44 | 5.52 | 5.59 | 5.67 | 5.77 | 5.91 | 5.99 | 5.99 | 5.99 | 5.99 | 5.99 | 5.99 | 5.99 | 5.99 | 5.99 | 5.99 | 5.99 | 5.99
| SA005 | FALSE | 8.8 | 8.91 | 9.03 | 9.12 | 9.18 | 9.29 | 9.42 | 9.56 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67
| SA006 | FALSE | 6.38 | 6.38 | 6.41 | 6.43 | 6.41 | 6.42 | 6.45 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53
| SA007 | FALSE | 17.51 | 17.89 | 18.32 | 18.72 | 19 | 19.31 | 19.76 | 20.21 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6
| SA009 | FALSE | 12.72 | 13.27 | 13.87 | 14.47 | 15.02 | 15.61 | 16.32 | 17.05 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62
| SA010 | FALSE | 7.21 | 7.25 | 7.32 | 7.36 | 7.36 | 7.38 | 7.46 | 7.58 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57
| SA011 | FALSE | 11.37 | 11.55 | 11.82 | 12.07 | 12.23 | 12.45 | 12.74 | 13.05 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29
| SA012 | FALSE | 9.88 | 9.82 | 9.78 | 9.72 | 9.64 | 9.57 | 9.53 | 9.5 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45
| SB011 | FALSE | 2.72 | 2.82 | 2.94 | 3.05 | 3.14 | 3.23 | 3.34 | 3.47 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56
| SB012 | FALSE | 3.68 | 3.85 | 4.01 | 4.17 | 4.31 | 4.47 | 4.65 | 4.84 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99
| SB013 | FALSE | 2.81 | 2.9 | 3 | 3.1 | 3.17 | 3.24 | 3.34 | 3.46 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55
| SB015 | FALSE | 3.03 | 3.07 | 3.16 | 3.25 | 3.32 | 3.41 | 3.54 | 3.68 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77
| SB016 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SB021 | FALSE | 3.98 | 4.1 | 4.25 | 4.37 | 4.46 | 4.56 | 4.71 | 4.87 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94
| SB022 | FALSE | 1.64 | 1.7 | 1.76 | 1.82 | 1.88 | 1.93 | 1.98 | 2.04 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1
| SB023 | FALSE | 2.33 | 2.42 | 2.52 | 2.61 | 2.7 | 2.8 | 2.91 | 3.01 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1
| SB025 | FALSE | 1.8 | 1.81 | 1.82 | 1.84 | 1.85 | 1.86 | 1.87 | 1.89 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91
| SB026 | FALSE | 6.45 | 6.46 | 6.47 | 6.47 | 6.48 | 6.48 | 6.5 | 6.54 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57 | 6.57
| SB041 | FALSE | 4.3 | 5.14 | 5.34 | 5.36 | 5.36 | 5.37 | 5.39 | 5.43 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45
| SB042 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SB043 | FALSE | 8.65 | 8.66 | 8.67 | 8.68 | 8.68 | 8.69 | 8.72 | 8.77 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82
| SB045 | FALSE | 3.38 | 3.39 | 3.41 | 3.43 | 3.44 | 3.45 | 3.47 | 3.5 | 3.53 | 3.53 | 3.53 | 3.53 | 3.53 | 3.53 | 3.53 | 3.53 | 3.53 | 3.53 | 3.53 | 3.53
| SB046 | FALSE | 0.22 | 0.23 | 0.24 | 0.25 | 0.25 | 0.26 | 0.27 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
| SB051 | FALSE | 3.32 | 3.35 | 3.41 | 3.46 | 3.48 | 3.5 | 3.57 | 3.65 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| SB052 | FALSE | 2.03 | 2.08 | 2.14 | 2.19 | 2.22 | 2.25 | 2.32 | 2.4 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42
| SB053 | FALSE | 3.45 | 3.47 | 3.48 | 3.49 | 3.48 | 3.49 | 3.51 | 3.53 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54
| SB055 | FALSE | 2.86 | 2.97 | 3.08 | 3.18 | 3.28 | 3.37 | 3.48 | 3.58 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68 | 3.68
| SB056 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001 | FALSE | 4.89 | 4.84 | 4.78 | 4.74 | 4.66 | 4.59 | 4.56 | 4.51 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44 | 4.44
| SHL002 | FALSE | 13.92 | 13.73 | 13.71 | 13.57 | 13.33 | 13.21 | 13.22 | 13.34 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1
| SHL004 | FALSE | 7.98 | 7.97 | 7.99 | 8.01 | 7.95 | 7.91 | 7.95 | 8.01 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97
| SHL005 | FALSE | 3.98 | 3.98 | 3.98 | 3.98 | 3.94 | 3.92 | 3.94 | 3.97 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95
| SHL007 | FALSE | 8.67 | 8.62 | 8.59 | 8.55 | 8.47 | 8.37 | 8.35 | 8.34 | 8.25 | 8.25 | 8.25 | 8.25 | 8.25 | 8.25 | 8.25 | 8.25 | 8.25 | 8.25 | 8.25 | 8.25
| SHL008 | FALSE | 9.75 | 9.73 | 9.76 | 9.74 | 9.65 | 9.59 | 9.6 | 9.62 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56
| SHN011 | FALSE | 7.85 | 7.94 | 8.07 | 8.17 | 8.18 | 8.24 | 8.4 | 8.59 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62
| SHN012 | FALSE | 6.88 | 6.99 | 7.13 | 7.24 | 7.31 | 7.39 | 7.53 | 7.71 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8
| SHN014 | FALSE | 6.92 | 6.95 | 7.01 | 7.04 | 7.05 | 7.06 | 7.12 | 7.19 | 7.21 | 7.21 | 7.21 | 7.21 | 7.21 | 7.21 | 7.21 | 7.21 | 7.21 | 7.21 | 7.21 | 7.21
| SHN021 | FALSE | 7.08 | 7.18 | 7.31 | 7.42 | 7.48 | 7.56 | 7.71 | 7.88 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97 | 7.97
| SHN022 | FALSE | 4.34 | 4.33 | 4.34 | 4.36 | 4.37 | 4.38 | 4.4 | 4.44 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46 | 4.46
| SHN023 | FALSE | 4.31 | 4.26 | 4.26 | 4.26 | 4.22 | 4.22 | 4.23 | 4.26 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27
| SHN024 | FALSE | 7.66 | 7.78 | 7.97 | 8.1 | 8.15 | 8.22 | 8.41 | 8.64 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66
| SHP011 | FALSE | 9.5 | 9.42 | 9.4 | 9.41 | 9.36 | 9.29 | 9.27 | 9.29 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27
| SHP012 | FALSE | 7.32 | 7.4 | 7.56 | 7.68 | 7.68 | 7.74 | 7.88 | 8.07 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
| SHP014 | FALSE | 5.57 | 5.6 | 5.66 | 5.69 | 5.67 | 5.68 | 5.73 | 5.79 | 5.78 | 5.78 | 5.78 | 5.78 | 5.78 | 5.78 | 5.78 | 5.78 | 5.78 | 5.78 | 5.78 | 5.78
| SHP021 | FALSE | 7.08 | 7.03 | 6.99 | 6.94 | 6.69 | 6.68 | 6.69 | 6.71 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58
| SK001 | FALSE | 5.04 | 5.19 | 5.36 | 5.53 | 5.67 | 5.82 | 6.01 | 6.2 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34
| SK002 | FALSE | 3.99 | 3.99 | 4 | 4 | 4 | 4.01 | 4.02 | 4.04 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06
| SK004 | FALSE | 2.39 | 2.46 | 2.54 | 2.61 | 2.67 | 2.74 | 2.82 | 2.91 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97
| SK005 | FALSE | 5.73 | 5.91 | 6.12 | 6.3 | 6.49 | 6.69 | 6.9 | 7.15 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31
| SK006 | FALSE | 2.98 | 3.02 | 3.03 | 3.04 | 3.05 | 3.06 | 3.08 | 3.1 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11
| SK009 | FALSE | 2.14 | 2.22 | 2.3 | 2.38 | 2.45 | 2.52 | 2.62 | 2.73 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| SK010 | FALSE | 6.67 | 6.67 | 6.68 | 6.69 | 6.69 | 6.7 | 6.72 | 6.76 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
| SK013 | FALSE | 3.25 | 3.36 | 3.49 | 3.6 | 3.69 | 3.8 | 3.92 | 4.06 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15
| SK014 | FALSE | 3.06 | 3.15 | 3.23 | 3.31 | 3.39 | 3.47 | 3.57 | 3.65 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74 | 3.74
| SK015 | FALSE | 2.52 | 2.59 | 2.67 | 2.75 | 2.83 | 2.9 | 2.98 | 3.06 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14
| SK018 | FALSE | 5.15 | 5.16 | 5.17 | 5.18 | 5.18 | 5.18 | 5.2 | 5.23 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25
| SK019 | FALSE | 2.16 | 2.36 | 2.67 | 2.68 | 2.7 | 2.71 | 2.73 | 2.76 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77 | 2.77
| SK020 | FALSE | 4.23 | 4.33 | 4.44 | 4.54 | 4.63 | 4.73 | 4.84 | 4.95 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06
| SK022 | FALSE | 3.32 | 3.41 | 3.5 | 3.59 | 3.66 | 3.73 | 3.82 | 3.93 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| SK023 | FALSE | 1.75 | 1.81 | 1.88 | 1.94 | 1.99 | 2.05 | 2.11 | 2.18 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23
| SK024 | FALSE | 4.1 | 4.18 | 4.26 | 4.33 | 4.4 | 4.47 | 4.56 | 4.65 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72
| SK025 | FALSE | 3.57 | 3.63 | 3.7 | 3.75 | 3.77 | 3.8 | 3.84 | 3.88 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89 | 3.89
| SO001 | FALSE | 3.46 | 3.59 | 3.73 | 3.86 | 3.98 | 4.1 | 4.24 | 4.38 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51
| SO002 | FALSE | 1.85 | 1.91 | 1.98 | 2.04 | 2.09 | 2.15 | 2.21 | 2.27 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34
| SO005 | FALSE | 2.52 | 2.59 | 2.67 | 2.74 | 2.81 | 2.88 | 2.96 | 3.05 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12
| SO006 | FALSE | 2.39 | 2.48 | 2.57 | 2.66 | 2.74 | 2.83 | 2.91 | 3.01 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09
| SO009 | FALSE | 4.43 | 4.6 | 4.76 | 4.92 | 5.07 | 5.22 | 5.38 | 5.54 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
| SO010 | FALSE | 4.32 | 4.4 | 4.49 | 4.59 | 4.66 | 4.74 | 4.84 | 4.95 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03 | 5.03
| SO013 | FALSE | 4.58 | 4.75 | 4.93 | 5.1 | 5.25 | 5.4 | 5.57 | 5.76 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92
| SO014 | FALSE | 5.05 | 5.17 | 5.26 | 5.36 | 5.44 | 5.52 | 5.62 | 5.72 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83
| SO015 | FALSE | 1.24 | 1.28 | 1.32 | 1.37 | 1.4 | 1.44 | 1.49 | 1.54 | 1.57 | 1.57 | 1.57 | 1.57 | 1.57 | 1.57 | 1.57 | 1.57 | 1.57 | 1.57 | 1.57 | 1.57
| SO018 | FALSE | 2.44 | 2.51 | 2.58 | 2.65 | 2.71 | 2.78 | 2.86 | 2.94 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02
| SO019 | FALSE | 0.8 | 0.84 | 0.88 | 0.92 | 0.95 | 0.98 | 1.02 | 1.07 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11
| SO020 | FALSE | 2.64 | 2.71 | 2.77 | 2.84 | 2.9 | 2.96 | 3.04 | 3.11 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17
| SO022 | FALSE | 4.86 | 5 | 5.14 | 5.27 | 5.39 | 5.51 | 5.66 | 5.8 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94
| SO023 | FALSE | 2.79 | 2.9 | 3.01 | 3.12 | 3.22 | 3.32 | 3.43 | 3.54 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64 | 3.64
| SO024 | FALSE | 4.39 | 4.51 | 4.59 | 4.66 | 4.72 | 4.79 | 4.87 | 4.94 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02
| SSE011 | FALSE | 11.7 | 11.71 | 11.75 | 11.79 | 11.81 | 11.86 | 11.91 | 11.98 | 12.03 | 12.03 | 12.03 | 12.03 | 12.03 | 12.03 | 12.03 | 12.03 | 12.03 | 12.03 | 12.03 | 12.03
| SSE012 | FALSE | 6.01 | 6.05 | 6.12 | 6.22 | 6.28 | 6.34 | 6.46 | 6.64 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71
| SSE013 | FALSE | 8.15 | 8.05 | 8.06 | 8.06 | 8.02 | 7.96 | 7.95 | 7.95 | 7.92 | 7.92 | 7.92 | 7.92 | 7.92 | 7.92 | 7.92 | 7.92 | 7.92 | 7.92 | 7.92 | 7.92
| SSE014 | FALSE | 12.47 | 12.68 | 12.94 | 13.1 | 13.21 | 13.36 | 13.61 | 13.99 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
| SSE031 | FALSE | 10.76 | 10.92 | 11.08 | 11.27 | 11.34 | 11.44 | 11.66 | 11.88 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08
| SSE032 | FALSE | 9.51 | 9.48 | 9.47 | 9.52 | 9.53 | 9.6 | 9.74 | 9.91 | 9.94 | 9.94 | 9.94 | 9.94 | 9.94 | 9.94 | 9.94 | 9.94 | 9.94 | 9.94 | 9.94 | 9.94
| SSE033 | FALSE | 10.16 | 10.3 | 10.52 | 10.68 | 10.79 | 10.94 | 11.17 | 11.41 | 11.52 | 11.52 | 11.52 | 11.52 | 11.52 | 11.52 | 11.52 | 11.52 | 11.52 | 11.52 | 11.52 | 11.52
| SSE034 | FALSE | 11.86 | 12.07 | 12.36 | 12.66 | 12.78 | 12.88 | 13.25 | 13.68 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84 | 13.84
| STL004 | FALSE | 8.11 | 8.04 | 7.97 | 7.91 | 7.86 | 7.78 | 7.73 | 7.69 | 7.66 | 7.66 | 7.66 | 7.66 | 7.66 | 7.66 | 7.66 | 7.66 | 7.66 | 7.66 | 7.66 | 7.66
| STL005 | FALSE | 8.77 | 8.74 | 8.75 | 8.74 | 8.68 | 8.62 | 8.6 | 8.61 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55
| STL006 | FALSE | 3.34 | 3.3 | 3.31 | 3.31 | 3.29 | 3.26 | 3.28 | 3.29 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27
| STL007 | FALSE | 6.56 | 6.43 | 6.35 | 6.28 | 6.2 | 6.09 | 6.13 | 6.07 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08
| STN011 | FALSE | 7.29 | 7.32 | 7.39 | 7.43 | 7.44 | 7.46 | 7.54 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65
| STN012 | FALSE | 10.53 | 10.73 | 10.97 | 11.19 | 11.35 | 11.53 | 11.82 | 12.11 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27
| STN013 | FALSE | 6.32 | 6.35 | 6.38 | 6.41 | 6.43 | 6.44 | 6.47 | 6.51 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55
| STN014 | FALSE | 6.98 | 6.95 | 6.95 | 6.97 | 6.98 | 6.99 | 7.03 | 7.09 | 7.12 | 7.12 | 7.12 | 7.12 | 7.12 | 7.12 | 7.12 | 7.12 | 7.12 | 7.12 | 7.12 | 7.12
| STN021 | FALSE | 6.1 | 6.18 | 6.29 | 6.37 | 6.44 | 6.52 | 6.63 | 6.76 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82
| STN022 | FALSE | 8.01 | 8.03 | 8.07 | 8.1 | 8.07 | 8.04 | 8.12 | 8.15 | 8.13 | 8.13 | 8.13 | 8.13 | 8.13 | 8.13 | 8.13 | 8.13 | 8.13 | 8.13 | 8.13 | 8.13
| STN023 | FALSE | 3.55 | 3.52 | 3.49 | 3.48 | 3.45 | 3.43 | 3.42 | 3.4 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
| STN024 | FALSE | 12.05 | 12.17 | 12.43 | 12.61 | 12.65 | 12.73 | 13.02 | 13.37 | 13.38 | 13.38 | 13.38 | 13.38 | 13.38 | 13.38 | 13.38 | 13.38 | 13.38 | 13.38 | 13.38 | 13.38
| STN031 | FALSE | 7.04 | 6.95 | 6.9 | 6.87 | 6.8 | 6.76 | 6.74 | 6.74 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71
| SU012 | FALSE | 14.17 | 14.29 | 14.48 | 14.65 | 14.8 | 14.92 | 15.16 | 15.48 | 15.62 | 15.62 | 15.62 | 15.62 | 15.62 | 15.62 | 15.62 | 15.62 | 15.62 | 15.62 | 15.62 | 15.62
| SU013 | FALSE | 9.57 | 9.7 | 9.87 | 10.03 | 10.14 | 10.25 | 10.42 | 10.61 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76
| SU015 | FALSE | 10.81 | 11.25 | 11.77 | 12.23 | 12.65 | 13.06 | 13.66 | 14.28 | 14.66 | 14.66 | 14.66 | 14.66 | 14.66 | 14.66 | 14.66 | 14.66 | 14.66 | 14.66 | 14.66 | 14.66
| SU021 | FALSE | 11.26 | 11.39 | 11.53 | 11.65 | 11.73 | 11.84 | 11.99 | 12.15 | 12.25 | 12.25 | 12.25 | 12.25 | 12.25 | 12.25 | 12.25 | 12.25 | 12.25 | 12.25 | 12.25 | 12.25
| SU022 | FALSE | 12.59 | 12.91 | 13.28 | 13.57 | 13.83 | 14.16 | 14.48 | 14.93 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2
| SU023 | FALSE | 13.6 | 13.84 | 14.09 | 14.33 | 14.52 | 14.7 | 14.96 | 15.28 | 15.52 | 15.52 | 15.52 | 15.52 | 15.52 | 15.52 | 15.52 | 15.52 | 15.52 | 15.52 | 15.52 | 15.52
| SU024 | FALSE | 3.47 | 3.52 | 3.58 | 3.63 | 3.67 | 3.71 | 3.77 | 3.83 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88
| SU032 | FALSE | 5.24 | 7.58 | 8.26 | 8.33 | 8.39 | 8.45 | 8.51 | 8.58 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66
| SU034 | FALSE | 8.99 | 9.12 | 9.28 | 9.44 | 9.54 | 9.67 | 9.82 | 10 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13
| SU035 | FALSE | 16.84 | 17.24 | 17.72 | 18.2 | 18.47 | 18.79 | 19.27 | 19.86 | 20.27 | 20.27 | 20.27 | 20.27 | 20.27 | 20.27 | 20.27 | 20.27 | 20.27 | 20.27 | 20.27 | 20.27
| TK001 | FALSE | 3.61 | 3.66 | 3.72 | 3.76 | 3.79 | 3.83 | 3.88 | 3.94 | 3.97 | 3.97 | 3.97 | 3.97 | 3.97 | 3.97 | 3.97 | 3.97 | 3.97 | 3.97 | 3.97 | 3.97
| TK002 | FALSE | 4.03 | 4.1 | 4.17 | 4.22 | 4.24 | 4.25 | 4.31 | 4.38 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
| TK004 | FALSE | 4.03 | 4.02 | 4.02 | 4.03 | 4.02 | 4.02 | 4.06 | 4.1 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11
| TK005 | FALSE | 2.6 | 2.65 | 2.7 | 2.75 | 2.79 | 2.83 | 2.9 | 2.96 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| TK006 | FALSE | 5.1 | 5.1 | 5.13 | 5.13 | 5.13 | 5.13 | 5.15 | 5.2 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18
| TK009 | FALSE | 2.86 | 2.97 | 3.09 | 3.19 | 3.29 | 3.4 | 3.52 | 3.66 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75
| TK010 | FALSE | 2.95 | 2.94 | 2.95 | 2.96 | 2.95 | 2.97 | 2.99 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01
| TK011 | FALSE | 4.61 | 4.6 | 4.6 | 4.58 | 4.55 | 4.52 | 4.5 | 4.49 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45
| TK013 | FALSE | 3.38 | 3.47 | 3.58 | 3.68 | 3.76 | 3.83 | 3.94 | 4.06 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14
| TK014 | FALSE | 3.98 | 3.98 | 4 | 4.01 | 4 | 4.01 | 4.05 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1
| TK015 | FALSE | 3.65 | 3.67 | 3.71 | 3.73 | 3.74 | 3.77 | 3.79 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84
| TK017 | FALSE | 3.26 | 3.34 | 3.43 | 3.5 | 3.56 | 3.62 | 3.7 | 3.81 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85
| TK019 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TK020 | FALSE | 1.74 | 1.79 | 1.84 | 1.88 | 1.93 | 1.97 | 2.02 | 2.07 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12
| TK022 | FALSE | 4.27 | 4.32 | 4.39 | 4.49 | 4.54 | 4.59 | 4.66 | 4.74 | 4.81 | 4.81 | 4.81 | 4.81 | 4.81 | 4.81 | 4.81 | 4.81 | 4.81 | 4.81 | 4.81 | 4.81
| TK023 | FALSE | 3.79 | 3.91 | 4.04 | 4.17 | 4.26 | 4.38 | 4.51 | 4.66 | 4.78 | 4.78 | 4.78 | 4.78 | 4.78 | 4.78 | 4.78 | 4.78 | 4.78 | 4.78 | 4.78 | 4.78
| TK024 | FALSE | 2.29 | 2.35 | 2.41 | 2.47 | 2.52 | 2.58 | 2.64 | 2.7 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75
| TK025 | FALSE | 3.89 | 3.89 | 3.91 | 3.93 | 3.93 | 3.94 | 3.97 | 4.01 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| TNA011 | FALSE | 19.06 | 12.06 | 12.77 | 13.48 | 14.06 | 14.67 | 15.41 | 16.26 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92 | 16.92
| TNA012 | FALSE | 15.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA013 | FALSE | 9.79 | 10.28 | 10.82 | 11.35 | 11.76 | 12.17 | 12.69 | 13.25 | 13.58 | 13.58 | 13.58 | 13.58 | 13.58 | 13.58 | 13.58 | 13.58 | 13.58 | 13.58 | 13.58 | 13.58
| TNA014 | FALSE | 9.02 | 9.47 | 9.96 | 10.41 | 10.77 | 11.14 | 11.61 | 12.1 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43 | 12.43
| TNA021 | FALSE | 16.41 | 16.58 | 16.76 | 16.94 | 17.09 | 17.23 | 17.48 | 17.68 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8
| TNA022 | FALSE | 15.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA023 | FALSE | 15.08 | 21.1 | 22.26 | 23.35 | 24.33 | 25.34 | 26.43 | 27.56 | 28.51 | 28.51 | 28.51 | 28.51 | 28.51 | 28.51 | 28.51 | 28.51 | 28.51 | 28.51 | 28.51 | 28.51
| TNA024 | FALSE | 18.59 | 19.6 | 20.7 | 21.73 | 22.63 | 23.49 | 24.53 | 25.65 | 26.51 | 26.51 | 26.51 | 26.51 | 26.51 | 26.51 | 26.51 | 26.51 | 26.51 | 26.51 | 26.51 | 26.51
| TNA031 | FALSE | 20.19 | 18.29 | 18.98 | 19.54 | 20.03 | 20.49 | 21.09 | 21.82 | 22.33 | 22.33 | 22.33 | 22.33 | 22.33 | 22.33 | 22.33 | 22.33 | 22.33 | 22.33 | 22.33 | 22.33
| TNA033 | FALSE | 19.09 | 19.8 | 20.58 | 21.42 | 22.05 | 22.67 | 23.47 | 24.42 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2
| TQY021 | FALSE | 12.05 | 12.2 | 12.39 | 12.63 | 12.75 | 12.9 | 12.94 | 13.01 | 13.04 | 13.04 | 13.04 | 13.04 | 13.04 | 13.04 | 13.04 | 13.04 | 13.04 | 13.04 | 13.04 | 13.04
| TQY022 | FALSE | 11.73 | 12.06 | 12.42 | 12.71 | 12.97 | 13.27 | 13.57 | 13.96 | 14.04 | 14.04 | 14.04 | 14.04 | 14.04 | 14.04 | 14.04 | 14.04 | 14.04 | 14.04 | 14.04 | 14.04
| TQY031 | FALSE | 13.84 | 13.99 | 14.36 | 14.64 | 14.89 | 15.13 | 15.46 | 15.93 | 16.22 | 16.22 | 16.22 | 16.22 | 16.22 | 16.22 | 16.22 | 16.22 | 16.22 | 16.22 | 16.22 | 16.22
| TQY032 | FALSE | 14.77 | 15.04 | 15.4 | 15.76 | 16.01 | 16.25 | 16.45 | 16.83 | 17.12 | 17.12 | 17.12 | 17.12 | 17.12 | 17.12 | 17.12 | 17.12 | 17.12 | 17.12 | 17.12 | 17.12
| TRG011 | FALSE | 1.41 | 1.42 | 1.45 | 1.48 | 1.48 | 1.48 | 1.51 | 1.55 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56
| TRG013 | FALSE | 5.62 | 5.64 | 5.72 | 5.77 | 5.75 | 5.76 | 5.83 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94
| TRG014 | FALSE | 3.76 | 3.76 | 3.77 | 3.78 | 3.76 | 3.76 | 3.79 | 3.84 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82
| TRG022 | FALSE | 4.87 | 4.92 | 5 | 5.06 | 5.06 | 5.08 | 5.17 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28
| TRG024 | FALSE | 8.22 | 8.36 | 8.58 | 8.76 | 8.8 | 8.87 | 9.11 | 9.38 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4
| VM003 | FALSE | 1 | 1.02 | 1.05 | 1.08 | 1.09 | 1.1 | 1.14 | 1.18 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19
| VM004 | FALSE | 3.73 | 3.73 | 3.74 | 3.75 | 3.75 | 3.74 | 3.77 | 3.81 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82
| VM005 | FALSE | 1.94 | 1.99 | 2.05 | 2.11 | 2.16 | 2.21 | 2.27 | 2.32 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
| VM006 | FALSE | 1.01 | 1.04 | 1.08 | 1.11 | 1.13 | 1.16 | 1.19 | 1.23 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25
| VM007 | FALSE | 3.08 | 3.07 | 3.07 | 3.06 | 3.05 | 3.05 | 3.05 | 3.07 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08
| VM008 | FALSE | 3.46 | 3.5 | 3.54 | 3.58 | 3.6 | 3.63 | 3.68 | 3.74 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77
| VM009 | FALSE | 1.44 | 1.48 | 1.53 | 1.58 | 1.6 | 1.63 | 1.69 | 1.75 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77 | 1.77
| VM010 | FALSE | 2.01 | 2.08 | 2.15 | 2.21 | 2.28 | 2.35 | 2.42 | 2.49 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55
| VM011 | FALSE | 2.53 | 2.63 | 2.74 | 2.84 | 2.93 | 3.02 | 3.13 | 3.23 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34
| VM014 | FALSE | 3.27 | 3.3 | 3.34 | 3.37 | 3.4 | 3.44 | 3.48 | 3.52 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56
| VM018 | FALSE | 2.75 | 2.76 | 2.78 | 2.8 | 2.81 | 2.83 | 2.85 | 2.88 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91
| VM020 | FALSE | 2.72 | 2.75 | 2.76 | 2.75 | 2.74 | 2.72 | 2.73 | 2.74 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72
| VM022 | FALSE | 2.85 | 2.92 | 3 | 3.07 | 3.12 | 3.18 | 3.26 | 3.34 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| VM025 | FALSE | 3.21 | 3.29 | 3.4 | 3.51 | 3.55 | 3.62 | 3.73 | 3.88 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93 | 3.93
| VM026 | FALSE | 3.69 | 3.76 | 3.8 | 3.85 | 3.87 | 3.9 | 3.95 | 4.02 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06
| VM027 | FALSE | 2.01 | 2.08 | 2.16 | 2.24 | 2.31 | 2.37 | 2.44 | 2.52 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
| VM028 | FALSE | 2.72 | 2.78 | 2.88 | 2.96 | 2.98 | 3.02 | 3.11 | 3.24 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26 | 3.26
| VM029 | FALSE | 0.98 | 1.01 | 1.04 | 1.06 | 1.09 | 1.11 | 1.14 | 1.16 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19
| VM030 | FALSE | 4.82 | 4.82 | 4.83 | 4.84 | 4.83 | 4.82 | 4.83 | 4.85 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83
| VM034 | FALSE | 4.29 | 4.31 | 4.34 | 4.37 | 4.39 | 4.4 | 4.45 | 4.52 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55
| VM035 | FALSE | 4.71 | 4.76 | 4.85 | 4.9 | 4.91 | 4.94 | 5.04 | 5.15 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14
| VM037 | FALSE | 4.18 | 4.15 | 4.12 | 4.1 | 4.07 | 4.05 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04
| VM038 | FALSE | 3.01 | 3.05 | 3.07 | 3.11 | 3.12 | 3.13 | 3.16 | 3.21 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25
| VM039 | FALSE | 3.43 | 3.41 | 3.39 | 3.37 | 3.35 | 3.33 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32
| VM040 | FALSE | 1.77 | 1.8 | 1.82 | 1.86 | 1.89 | 1.92 | 1.97 | 2.02 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07
| VM041 | FALSE | 3.18 | 3.28 | 3.39 | 3.48 | 3.57 | 3.66 | 3.76 | 3.86 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96 | 3.96
| VM042 | FALSE | 2.46 | 2.54 | 2.61 | 2.69 | 2.75 | 2.82 | 2.89 | 2.97 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05
| WA003 | FALSE | 2.78 | 2.83 | 2.88 | 2.93 | 2.97 | 3.01 | 3.06 | 3.12 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17
| WA005 | FALSE | 5.49 | 5.58 | 5.67 | 5.76 | 5.83 | 5.9 | 6 | 6.11 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2
| WA006 | FALSE | 1.96 | 1.98 | 2 | 2.02 | 2.04 | 2.06 | 2.08 | 2.11 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13
| WA008 | FALSE | 3.28 | 3.32 | 3.36 | 3.39 | 3.41 | 3.44 | 3.49 | 3.54 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57
| WA009 | FALSE | 4.56 | 4.71 | 4.87 | 5.02 | 5.15 | 5.28 | 5.43 | 5.59 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73
| WA011 | FALSE | 1.58 | 1.59 | 1.6 | 1.62 | 1.63 | 1.64 | 1.65 | 1.67 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69
| WA020 | FALSE | 5.36 | 5.5 | 5.63 | 5.77 | 5.88 | 5.99 | 6.12 | 6.26 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
| WA021 | FALSE | 3.2 | 3.23 | 3.27 | 3.32 | 3.35 | 3.38 | 3.44 | 3.49 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54
| WA022 | FALSE | 2.85 | 2.88 | 2.9 | 2.93 | 2.95 | 2.97 | 3 | 3.04 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07
| WA023 | FALSE | 2.93 | 2.92 | 2.91 | 2.89 | 2.88 | 2.88 | 2.88 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89
| WA024 | FALSE | 2.2 | 2.21 | 2.23 | 2.25 | 2.26 | 2.27 | 2.3 | 2.32 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34
| WA027 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WA030 | FALSE | 1.61 | 1.68 | 1.74 | 1.8 | 1.85 | 1.9 | 1.97 | 2.03 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09
| WA031 | FALSE | 3.1 | 3.13 | 3.16 | 3.19 | 3.21 | 3.23 | 3.27 | 3.31 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34
| WA032 | FALSE | 1.48 | 1.54 | 1.6 | 1.66 | 1.72 | 1.77 | 1.83 | 1.9 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95
| WA033 | FALSE | 4.25 | 4.3 | 4.35 | 4.41 | 4.44 | 4.47 | 4.53 | 4.61 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65
| WA035 | FALSE | 2.52 | 2.54 | 2.56 | 2.58 | 2.6 | 2.62 | 2.64 | 2.67 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7
| WB001 | FALSE | 1.87 | 1.9 | 1.94 | 1.98 | 2 | 2.03 | 2.07 | 2.12 | 2.14 | 2.14 | 2.14 | 2.14 | 2.14 | 2.14 | 2.14 | 2.14 | 2.14 | 2.14 | 2.14 | 2.14
| WB002 | FALSE | 6.25 | 6.39 | 6.56 | 6.73 | 6.82 | 6.96 | 7.12 | 7.31 | 7.49 | 7.49 | 7.49 | 7.49 | 7.49 | 7.49 | 7.49 | 7.49 | 7.49 | 7.49 | 7.49 | 7.49
| WB004 | FALSE | 2.68 | 2.69 | 2.69 | 2.69 | 2.68 | 2.66 | 2.66 | 2.66 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64
| WB005 | FALSE | 2.49 | 2.52 | 2.57 | 2.62 | 2.66 | 2.7 | 2.75 | 2.81 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86
| WB009 | FALSE | 2.96 | 3.02 | 3.1 | 3.15 | 3.2 | 3.27 | 3.33 | 3.43 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48 | 3.48
| WB010 | FALSE | 2.62 | 2.66 | 2.72 | 2.77 | 2.8 | 2.84 | 2.91 | 2.98 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01
| WB011 | FALSE | 4.59 | 4.9 | 4.96 | 5.01 | 5.04 | 5.06 | 5.12 | 5.19 | 5.22 | 5.22 | 5.22 | 5.22 | 5.22 | 5.22 | 5.22 | 5.22 | 5.22 | 5.22 | 5.22 | 5.22
| WB013 | FALSE | 3.88 | 3.96 | 4.07 | 4.15 | 4.21 | 4.28 | 4.4 | 4.52 | 4.57 | 4.57 | 4.57 | 4.57 | 4.57 | 4.57 | 4.57 | 4.57 | 4.57 | 4.57 | 4.57 | 4.57
| WB014 | FALSE | 1.7 | 1.71 | 1.73 | 1.75 | 1.76 | 1.78 | 1.8 | 1.82 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83
| WB015 | FALSE | 2.29 | 2.32 | 2.36 | 2.39 | 2.41 | 2.44 | 2.48 | 2.52 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54
| WB032 | FALSE | 4.29 | 4.4 | 6.95 | 7.11 | 7.25 | 7.4 | 7.6 | 7.85 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98
| WB033 | FALSE | 3.32 | 3.39 | 3.46 | 3.52 | 3.56 | 3.59 | 3.65 | 3.69 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75
| WB034 | FALSE | 3.94 | 4.04 | 4.15 | 4.24 | 4.32 | 4.39 | 4.49 | 4.62 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7
| WB035 | FALSE | 0 | 0 | 4.32 | 4.36 | 4.39 | 4.44 | 4.51 | 4.63 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64 | 4.64
| WB036 | FALSE | 0 | 0 | 8.32 | 8.5 | 8.64 | 8.79 | 9.03 | 9.33 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44 | 9.44
| WB037 | FALSE | 0 | 0 | 5.7 | 5.81 | 5.91 | 6.04 | 6.18 | 6.37 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45
| WBE011 | FALSE | 7.2 | 7.17 | 7.2 | 7.2 | 7.17 | 7.18 | 7.22 | 7.33 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29
| WBE012 | FALSE | 4.97 | 5.02 | 5.09 | 5.16 | 5.2 | 5.23 | 5.29 | 5.39 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43
| WBE013 | FALSE | 13.04 | 13.54 | 14.15 | 14.72 | 15.19 | 15.7 | 16.33 | 17.04 | 17.64 | 17.64 | 17.64 | 17.64 | 17.64 | 17.64 | 17.64 | 17.64 | 17.64 | 17.64 | 17.64 | 17.64
| WBE014 | FALSE | 12.44 | 6.52 | 6.83 | 7.15 | 7.45 | 7.75 | 8.11 | 8.46 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75
| WBE021 | FALSE | 11.46 | 3.35 | 3.28 | 3.25 | 3.21 | 3.19 | 3.17 | 3.16 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
| WBE022 | FALSE | 8.92 | 8.97 | 9.07 | 9.13 | 9.19 | 9.31 | 9.53 | 9.78 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98 | 9.98
| WBE023 | FALSE | 13.91 | 14.21 | 14.58 | 14.92 | 15.24 | 15.68 | 16.15 | 16.68 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05
| WBE024 | FALSE | 15.25 | 15.62 | 15.99 | 16.4 | 16.76 | 17.17 | 17.63 | 18.11 | 18.37 | 18.37 | 18.37 | 18.37 | 18.37 | 18.37 | 18.37 | 18.37 | 18.37 | 18.37 | 18.37 | 18.37
| WBE031 | FALSE | 11.13 | 11.55 | 12.01 | 12.45 | 12.79 | 13.16 | 13.62 | 14.19 | 14.59 | 14.59 | 14.59 | 14.59 | 14.59 | 14.59 | 14.59 | 14.59 | 14.59 | 14.59 | 14.59 | 14.59
| WBE032 | FALSE | 10.82 | 7.51 | 7.68 | 7.83 | 7.95 | 8.11 | 8.29 | 8.52 | 8.65 | 8.65 | 8.65 | 8.65 | 8.65 | 8.65 | 8.65 | 8.65 | 8.65 | 8.65 | 8.65 | 8.65
| WBE033 | FALSE | 13.88 | 14.42 | 14.98 | 15.52 | 15.96 | 16.43 | 17.03 | 17.72 | 18.22 | 18.22 | 18.22 | 18.22 | 18.22 | 18.22 | 18.22 | 18.22 | 18.22 | 18.22 | 18.22 | 18.22
| WBE034 | FALSE | 12.94 | 13.4 | 13.99 | 14.52 | 14.95 | 15.45 | 16 | 16.66 | 17.17 | 17.17 | 17.17 | 17.17 | 17.17 | 17.17 | 17.17 | 17.17 | 17.17 | 17.17 | 17.17 | 17.17
| WBL002 | FALSE | 15.75 | 15.74 | 15.86 | 15.96 | 15.98 | 15.99 | 16.1 | 16.28 | 16.34 | 16.34 | 16.34 | 16.34 | 16.34 | 16.34 | 16.34 | 16.34 | 16.34 | 16.34 | 16.34 | 16.34
| WBL003 | FALSE | 7.38 | 7.31 | 7.26 | 7.23 | 7.16 | 7.11 | 7.08 | 7.06 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01 | 7.01
| WBL004 | FALSE | 9.5 | 9.46 | 9.46 | 9.45 | 9.42 | 9.42 | 9.44 | 9.5 | 9.49 | 9.49 | 9.49 | 9.49 | 9.49 | 9.49 | 9.49 | 9.49 | 9.49 | 9.49 | 9.49 | 9.49
| WBL005 | FALSE | 6.09 | 6.15 | 6.26 | 6.36 | 6.4 | 6.46 | 6.57 | 6.71 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76
| WBL006 | FALSE | 4.56 | 4.61 | 4.68 | 4.75 | 4.8 | 4.85 | 4.93 | 5.03 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09
| WBL008 | FALSE | 5.04 | 4.93 | 4.86 | 4.83 | 4.81 | 4.82 | 4.85 | 4.91 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96
| WBL010 | FALSE | 6.56 | 6.41 | 6.32 | 6.24 | 6.14 | 6.02 | 5.94 | 5.84 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75
| WBL012 | FALSE | 9.09 | 9.17 | 9.32 | 9.43 | 9.45 | 9.5 | 9.68 | 9.87 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
| WD011 | FALSE | 4.36 | 4.43 | 4.52 | 4.59 | 4.63 | 4.68 | 4.76 | 4.85 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9
| WD013 | FALSE | 5.83 | 5.91 | 6.02 | 6.1 | 6.17 | 6.24 | 6.35 | 6.46 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51
| WD021 | FALSE | 2.91 | 2.96 | 3.01 | 3.05 | 3.09 | 3.11 | 3.16 | 3.23 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27 | 3.27
| WD022 | FALSE | 4.9 | 4.97 | 5.06 | 5.14 | 5.18 | 5.23 | 5.32 | 5.42 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48
| WD031 | FALSE | 5.45 | 5.53 | 5.63 | 5.72 | 5.78 | 5.85 | 5.97 | 6.06 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12
| WD032 | FALSE | 4.83 | 4.9 | 4.99 | 5.06 | 5.13 | 5.18 | 5.24 | 5.31 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36
| WG012 | FALSE | 6.52 | 6.83 | 7.13 | 7.42 | 7.68 | 7.95 | 8.23 | 8.52 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
| WG013 | FALSE | 5.56 | 5.82 | 6.05 | 6.27 | 6.48 | 6.68 | 6.9 | 7.13 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34 | 7.34
| WG014 | FALSE | 2.58 | 2.79 | 2.99 | 3.18 | 3.36 | 3.54 | 3.72 | 3.92 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09
| WG016 | FALSE | 7.68 | 8.35 | 9.03 | 9.59 | 10.16 | 10.71 | 11.27 | 11.87 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41
| WG021 | FALSE | 6.75 | 6.95 | 7.16 | 7.35 | 7.53 | 7.7 | 7.9 | 8.1 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28
| WG022 | FALSE | 2.44 | 2.55 | 2.66 | 2.76 | 2.86 | 2.95 | 3.05 | 3.15 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25
| WG024 | FALSE | 7 | 7.65 | 8.35 | 9.06 | 9.75 | 10.45 | 11.18 | 11.93 | 12.65 | 12.65 | 12.65 | 12.65 | 12.65 | 12.65 | 12.65 | 12.65 | 12.65 | 12.65 | 12.65 | 12.65
| WG028 | FALSE | 2.18 | 2.25 | 2.35 | 2.42 | 2.46 | 2.51 | 2.61 | 2.72 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75 | 2.75
| WG032 | FALSE | 6.41 | 6.74 | 7.05 | 7.34 | 7.62 | 7.89 | 8.18 | 8.47 | 8.78 | 8.78 | 8.78 | 8.78 | 8.78 | 8.78 | 8.78 | 8.78 | 8.78 | 8.78 | 8.78 | 8.78
| WG033 | FALSE | 6.38 | 6.93 | 7.45 | 7.95 | 8.42 | 8.87 | 9.34 | 9.81 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28
| WG034 | FALSE | 5.13 | 5.56 | 5.98 | 6.37 | 6.74 | 7.11 | 7.48 | 7.85 | 8.22 | 8.22 | 8.22 | 8.22 | 8.22 | 8.22 | 8.22 | 8.22 | 8.22 | 8.22 | 8.22 | 8.22
| WG036 | FALSE | 5.05 | 5.46 | 5.85 | 6.23 | 6.59 | 6.94 | 7.3 | 7.66 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02
| WG037 | FALSE | 5.01 | 5.17 | 5.38 | 5.54 | 5.63 | 5.72 | 5.93 | 6.18 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27
| WG038 | FALSE | 4.24 | 4.42 | 4.61 | 4.78 | 4.94 | 5.1 | 5.27 | 5.46 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62
| WIN011 | FALSE | 4.43 | 4.44 | 4.5 | 4.54 | 4.56 | 4.57 | 4.62 | 4.69 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71
| WIN022 | FALSE | 2.42 | 2.44 | 2.48 | 2.5 | 2.51 | 2.53 | 2.55 | 2.59 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
| WIN023 | FALSE | 2.47 | 2.51 | 2.56 | 2.6 | 2.63 | 2.66 | 2.73 | 2.79 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83
| WMN013 | FALSE | 7.1 | 7.12 | 7.19 | 7.23 | 7.21 | 7.2 | 7.28 | 7.4 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37
| WMN014 | FALSE | 10.22 | 10.39 | 10.66 | 10.87 | 10.9 | 11.02 | 11.27 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6
| WMN021 | FALSE | 12.41 | 12.41 | 12.48 | 12.53 | 12.47 | 12.41 | 12.5 | 12.65 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62
| WND011 | FALSE | 0.7 | 0.71 | 0.72 | 0.74 | 0.75 | 0.77 | 0.79 | 0.81 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
| WND012 | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013 | FALSE | 6.7 | 6.93 | 7.19 | 7.41 | 7.59 | 7.79 | 8.1 | 8.45 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68
| WND014 | FALSE | 5.8 | 5.83 | 5.92 | 5.99 | 6.05 | 6.13 | 6.26 | 6.42 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
| WND021 | FALSE | 1.62 | 1.66 | 1.71 | 1.77 | 1.8 | 1.84 | 1.9 | 1.97 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03
| WND022 | FALSE | 1.31 | 1.35 | 1.38 | 1.42 | 1.45 | 1.48 | 1.51 | 1.56 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59
| WND023 | FALSE | 8.07 | 8.22 | 8.41 | 8.62 | 8.71 | 8.81 | 8.99 | 9.28 | 9.42 | 9.42 | 9.42 | 9.42 | 9.42 | 9.42 | 9.42 | 9.42 | 9.42 | 9.42 | 9.42 | 9.42
| WND024 | FALSE | 4.18 | 4.22 | 4.3 | 4.4 | 4.46 | 4.52 | 4.64 | 4.75 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83 | 4.83
| WP012 | FALSE | 2.27 | 2.28 | 2.3 | 2.31 | 2.33 | 2.34 | 2.36 | 2.38 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41 | 2.41
| WP014 | FALSE | 3.87 | 3.9 | 3.93 | 3.96 | 3.99 | 4.01 | 4.05 | 4.1 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14
| WP021 | FALSE | 4.15 | 4.18 | 4.22 | 4.26 | 4.29 | 4.32 | 4.37 | 4.42 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47 | 4.47
| WP022 | FALSE | 3.04 | 3.15 | 3.25 | 3.36 | 3.45 | 3.55 | 3.66 | 3.75 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86
| WP025 | FALSE | 4.7 | 4.85 | 5.01 | 5.16 | 5.29 | 5.43 | 5.58 | 5.73 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88
| WP032 | FALSE | 3.73 | 3.76 | 3.8 | 3.83 | 3.86 | 3.89 | 3.94 | 3.99 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03
| WP033 | FALSE | 2.66 | 2.69 | 2.71 | 2.74 | 2.75 | 2.77 | 2.8 | 2.83 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86
| WP034 | FALSE | 2.3 | 2.32 | 2.34 | 2.36 | 2.37 | 2.38 | 2.41 | 2.44 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46 | 2.46
| WP041 | FALSE | 2.83 | 2.85 | 2.88 | 2.9 | 2.92 | 2.93 | 2.96 | 3 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03
| WP042 | FALSE | 2.45 | 2.47 | 2.48 | 2.5 | 2.52 | 2.53 | 2.55 | 2.58 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
| WP045 | FALSE | 3.37 | 3.48 | 3.57 | 3.67 | 3.75 | 3.83 | 3.92 | 4.02 | 4.12 | 4.12 | 4.12 | 4.12 | 4.12 | 4.12 | 4.12 | 4.12 | 4.12 | 4.12 | 4.12 | 4.12
| WPD011 | FALSE | 7.24 | 7.14 | 7.07 | 7.11 | 7.18 | 7.28 | 7.42 | 7.59 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61 | 7.61
| WPD012 | FALSE | 15.2 | 15.96 | 16.8 | 17.58 | 18.29 | 19.1 | 19.92 | 20.85 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66
| WPD013 | FALSE | 10.97 | 11.15 | 11.34 | 11.52 | 11.68 | 11.84 | 12.03 | 12.23 | 12.42 | 12.42 | 12.42 | 12.42 | 12.42 | 12.42 | 12.42 | 12.42 | 12.42 | 12.42 | 12.42 | 12.42
| WPD014 | FALSE | 0.1 | 0.1 | 0.1 | 0.1 | 0.11 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
| WPD022 | FALSE | 11.65 | 12.19 | 12.76 | 13.31 | 13.8 | 14.32 | 14.88 | 15.51 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06 | 16.06
| WPD024 | FALSE | 9.14 | 9.46 | 9.83 | 10.16 | 10.46 | 10.78 | 11.17 | 11.58 | 11.89 | 11.89 | 11.89 | 11.89 | 11.89 | 11.89 | 11.89 | 11.89 | 11.89 | 11.89 | 11.89 | 11.89
| WPD031 | FALSE | 6.18 | 6.41 | 6.65 | 6.88 | 7.09 | 7.29 | 7.6 | 8.03 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21
| WPD033 | FALSE | 9.15 | 9.36 | 9.62 | 9.84 | 10.01 | 10.2 | 10.45 | 10.79 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92
| BAS | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BATS | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BATSBAS1 | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BETSMRO | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BSP | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BBD | FALSE | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388
| BSPBBD | FALSE | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388
| KGT | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSF | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGTSGSF | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGTSHL | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHTS | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHTSKYM1 | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHTSMNA | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHTSNKA | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHTSSHP | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WSF | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WMN | FALSE | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223
| WSFWMN | FALSE | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223
| STN | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNASTN | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Span data
Powercor
Lines flood resilience program
FLOOD FORECAST
[13 empty] | 2050 RCP 4.5 | [6 empty] | 2050 RCP 8.5 | [6 empty] | Probability of flood occuring | [20 empty] | Safety risk ($)
| Span ID | Feeder | ZSS | Pole 1 ID | Pole 2 ID | Lifting height (m) | Longtitude | Latitude | Historical 1% AEP rainfall depth (mm) | Historical 2% AEP rainfall depth (mm) | 2050 RCP 4.5 | 2050 RCP 8.5 | 1% AEP rainfall depth for 2050 RCP 4.5, Y1 (mm) | 2% AEP rainfall depth for 2050 RCP 4.5, Y2 (mm) | 1% AEP, X1 | 2% AEP, X2 | Slope from 2% to 1% AEP | Intercept from 2% to 1% AEP | 2050 RCP 4.5 AEP using historical 1% AEP depth | 1% AEP rainfall depth for 2050 RCP 8.5, Y1 (mm) | 2% AEP rainfall depth for 2050 RCP 8.5, Y2 (mm) | 1% AEP, X1 | 2% AEP, X2 | Slope from 2% to 1% AEP | Intercept from 2% to 1% AEP | 2050 RCP 8.5 AEP using historical 1% AEP depth | RCP4.5 2050 flood forecast | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
| 10058538 | BAS033 | BAS | 191121971 | 15804479 | 0.15139 | 143.6655 | -37.6501 | 120 | 106 | 5.4% | 7.3% | 126.48 | 111.724 | 0.01 | 0.02 | -1475.6 | 141.236 | 1.439% | 128.76 | 113.738 | 0.01 | 0.02 | -1502.2 | 143.782 | 1.583% | 143.9% | 0.9631% | 0.978% | 0.993% | 1.008% | 1.023% | 1.038% | 1.053% | 1.068% | 1.083% | 1.097% | 1.112% | 1.127% | 1.142% | 1.157% | 1.172% | 1.187% | 1.202% | 1.217% | 1.232% | 1.247% | 0.00039003 | 0.00039608 | 0.00040212 | 0.00040817 | 0.00041422 | 0.00042027 | 0.00042632 | 0.00043237 | 0.00043842 | 0.00044446 | 0.00045051 | 0.00045656 | 0.00046261 | 0.00046866 | 0.00047471 | 0.00048075 | 0.0004868 | 0.00049285 | 0.0004989 | 0.00050495
| 10060242 | HTN032 | KGTS | 15479056 | 15479123 | 1.4396 | 142.0161 | -37.7506 | 114 | 97.2 | 5.4% | 7.3% | 120.156 | 102.4488 | 0.01 | 0.02 | -1770.72 | 137.8632 | 1.348% | 122.322 | 104.2956 | 0.01 | 0.02 | -1802.64 | 140.3484 | 1.462% | 134.8% | 0.9537% | 0.9656% | 0.9774% | 0.9892% | 1.001% | 1.013% | 1.025% | 1.037% | 1.048% | 1.06% | 1.072% | 1.084% | 1.096% | 1.107% | 1.119% | 1.131% | 1.143% | 1.155% | 1.167% | 1.178% | 0.00038625 | 0.00039104 | 0.00039582 | 0.00040061 | 0.0004054 | 0.00041019 | 0.00041498 | 0.00041977 | 0.00042455 | 0.00042934 | 0.00043413 | 0.00043892 | 0.00044371 | 0.0004485 | 0.00045328 | 0.00045807 | 0.00046286 | 0.00046765 | 0.00047244 | 0.00047723
| 10069507 | WND014 | WND | 15516218 | 15516233 | 0.87569 | 144.428 | -37.2341 | 130 | 116 | 6.3% | 8.8% | 138.19 | 123.308 | 0.01 | 0.02 | -1488.2 | 153.072 | 1.55% | 139.49 | 126.208 | 0.01 | 0.02 | -1328.2 | 152.772 | 1.715% | 155% | 0.9744% | 0.9931% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.105% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.236% | 1.255% | 1.274% | 1.293% | 1.311% | 1.33% | 0.00039462 | 0.0004022 | 0.00040978 | 0.00041736 | 0.00042494 | 0.00043252 | 0.0004401 | 0.00044768 | 0.00045526 | 0.00046284 | 0.00047042 | 0.000478 | 0.00048558 | 0.00049316 | 0.00050074 | 0.00050832 | 0.0005159 | 0.00052348 | 0.00053106 | 0.00053864
| 10084145 | MDA032 | MDA | 15577055 | 15577086 | 2.9681 | 142.1668 | -34.1841 | 112 | 97.6 | 6.3% | 8.8% | 119.056 | 103.7488 | 0.01 | 0.02 | -1530.72 | 134.3632 | 1.461% | 120.176 | 106.1888 | 0.01 | 0.02 | -1398.72 | 134.1632 | 1.585% | 146.1% | 0.9653% | 0.981% | 0.9967% | 1.012% | 1.028% | 1.044% | 1.059% | 1.075% | 1.091% | 1.106% | 1.122% | 1.138% | 1.153% | 1.169% | 1.185% | 1.2% | 1.216% | 1.232% | 1.247% | 1.263% | 0.00039093 | 0.00039728 | 0.00040363 | 0.00040998 | 0.00041632 | 0.00042267 | 0.00042902 | 0.00043537 | 0.00044172 | 0.00044807 | 0.00045442 | 0.00046077 | 0.00046712 | 0.00047347 | 0.00047981 | 0.00048616 | 0.00049251 | 0.00049886 | 0.00050521 | 0.00051156
| 10093224 | EHK022 | EHK | 15616100 | 15616125 | 4.0115 | 144.2886 | -36.7539 | 115 | 104 | 6.3% | 8.8% | 122.245 | 110.552 | 0.01 | 0.02 | -1169.3 | 133.938 | 1.62% | 123.395 | 113.152 | 0.01 | 0.02 | -1024.3 | 133.638 | 1.82% | 162% | 0.9815% | 1.003% | 1.024% | 1.045% | 1.066% | 1.087% | 1.108% | 1.129% | 1.15% | 1.171% | 1.192% | 1.213% | 1.234% | 1.255% | 1.277% | 1.298% | 1.319% | 1.34% | 1.361% | 1.382% | 0.00039748 | 0.00040602 | 0.00041455 | 0.00042309 | 0.00043162 | 0.00044015 | 0.00044869 | 0.00045722 | 0.00046576 | 0.00047429 | 0.00048282 | 0.00049136 | 0.00049989 | 0.00050843 | 0.00051696 | 0.00052549 | 0.00053403 | 0.00054256 | 0.0005511 | 0.00055963
| 10097205 | BAS022 | BAS | 15635128 | 17355103 | 1.5562 | 143.8309 | -37.6641 | 120 | 106 | 5.4% | 7.3% | 126.48 | 111.724 | 0.01 | 0.02 | -1475.6 | 141.236 | 1.439% | 128.76 | 113.738 | 0.01 | 0.02 | -1502.2 | 143.782 | 1.583% | 143.9% | 0.9631% | 0.978% | 0.993% | 1.008% | 1.023% | 1.038% | 1.053% | 1.068% | 1.083% | 1.097% | 1.112% | 1.127% | 1.142% | 1.157% | 1.172% | 1.187% | 1.202% | 1.217% | 1.232% | 1.247% | 0.00039003 | 0.00039608 | 0.00040212 | 0.00040817 | 0.00041422 | 0.00042027 | 0.00042632 | 0.00043237 | 0.00043842 | 0.00044446 | 0.00045051 | 0.00045656 | 0.00046261 | 0.00046866 | 0.00047471 | 0.00048075 | 0.0004868 | 0.00049285 | 0.0004989 | 0.00050495
| 10137677 | BAS033 | BAS | 15804458 | 15804352 | 2.9582 | 143.6572 | -37.6542 | 120 | 106 | 5.4% | 7.3% | 126.48 | 111.724 | 0.01 | 0.02 | -1475.6 | 141.236 | 1.439% | 128.76 | 113.738 | 0.01 | 0.02 | -1502.2 | 143.782 | 1.583% | 143.9% | 0.9631% | 0.978% | 0.993% | 1.008% | 1.023% | 1.038% | 1.053% | 1.068% | 1.083% | 1.097% | 1.112% | 1.127% | 1.142% | 1.157% | 1.172% | 1.187% | 1.202% | 1.217% | 1.232% | 1.247% | 0.00039003 | 0.00039608 | 0.00040212 | 0.00040817 | 0.00041422 | 0.00042027 | 0.00042632 | 0.00043237 | 0.00043842 | 0.00044446 | 0.00045051 | 0.00045656 | 0.00046261 | 0.00046866 | 0.00047471 | 0.00048075 | 0.0004868 | 0.00049285 | 0.0004989 | 0.00050495
| 10154574 | CMN005 | CMN | 16982227 | 15877050 | 0.19972 | 144.2094 | -37.0713 | 121 | 108 | 6.3% | 8.8% | 128.623 | 114.804 | 0.01 | 0.02 | -1381.9 | 142.442 | 1.552% | 129.833 | 117.504 | 0.01 | 0.02 | -1232.9 | 142.162 | 1.716% | 155.2% | 0.9746% | 0.9933% | 1.012% | 1.031% | 1.05% | 1.068% | 1.087% | 1.106% | 1.125% | 1.143% | 1.162% | 1.181% | 1.2% | 1.218% | 1.237% | 1.256% | 1.275% | 1.293% | 1.312% | 1.331% | 0.00039468 | 0.00040227 | 0.00040987 | 0.00041747 | 0.00042507 | 0.00043266 | 0.00044026 | 0.00044786 | 0.00045546 | 0.00046306 | 0.00047065 | 0.00047825 | 0.00048585 | 0.00049345 | 0.00050104 | 0.00050864 | 0.00051624 | 0.00052384 | 0.00053144 | 0.00053903
| 10156754 | STL005 | STL | 15886686 | 16631215 | 0.62543 | 142.5312 | -37.0176 | 119 | 105 | 6.3% | 8.8% | 126.497 | 111.615 | 0.01 | 0.02 | -1488.2 | 141.379 | 1.504% | 127.687 | 114.24 | 0.01 | 0.02 | -1344.7 | 141.134 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.21% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.0003927 | 0.00039964 | 0.00040657 | 0.00041351 | 0.00042045 | 0.00042739 | 0.00043433 | 0.00044127 | 0.00044821 | 0.00045514 | 0.00046208 | 0.00046902 | 0.00047596 | 0.0004829 | 0.00048984 | 0.00049678 | 0.00050371 | 0.00051065 | 0.00051759 | 0.00052453
| 10156772 | STL005 | STL | 16631756 | 15886734 | 0.23155 | 142.5804 | -37.0255 | 121 | 106 | 6.3% | 8.8% | 128.623 | 112.678 | 0.01 | 0.02 | -1594.5 | 144.568 | 1.478% | 129.833 | 115.328 | 0.01 | 0.02 | -1450.5 | 144.338 | 1.609% | 147.8% | 0.9671% | 0.9833% | 0.9996% | 1.016% | 1.032% | 1.048% | 1.065% | 1.081% | 1.097% | 1.113% | 1.13% | 1.146% | 1.162% | 1.178% | 1.195% | 1.211% | 1.227% | 1.243% | 1.26% | 1.276% | 0.00039164 | 0.00039822 | 0.00040481 | 0.00041139 | 0.00041798 | 0.00042456 | 0.00043114 | 0.00043773 | 0.00044431 | 0.0004509 | 0.00045748 | 0.00046407 | 0.00047065 | 0.00047724 | 0.00048382 | 0.00049041 | 0.00049699 | 0.00050358 | 0.00051016 | 0.00051675
| 10156819 | STL006 | STL | 16631150 | 15886907 | 0.86376 | 142.5148 | -36.9697 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10158895 | CMN002 | CMN | 15893802 | 15893851 | 0.62245 | 144.0882 | -37.1752 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10158902 | CMN002 | CMN | 15893813 | 17398204 | 3.3632 | 144.0895 | -37.1602 | 113 | 101 | 6.3% | 8.8% | 120.119 | 107.363 | 0.01 | 0.02 | -1275.6 | 132.875 | 1.558% | 121.249 | 109.888 | 0.01 | 0.02 | -1136.1 | 132.61 | 1.726% | 155.8% | 0.9752% | 0.9942% | 1.013% | 1.032% | 1.051% | 1.07% | 1.089% | 1.108% | 1.127% | 1.146% | 1.165% | 1.184% | 1.203% | 1.222% | 1.241% | 1.26% | 1.279% | 1.298% | 1.317% | 1.336% | 0.00039494 | 0.00040263 | 0.00041032 | 0.000418 | 0.00042569 | 0.00043338 | 0.00044106 | 0.00044875 | 0.00045644 | 0.00046412 | 0.00047181 | 0.0004795 | 0.00048718 | 0.00049487 | 0.00050256 | 0.00051024 | 0.00051793 | 0.00052562 | 0.0005333 | 0.00054099
| 10159643 | STL007 | STL | 17331465 | 15896848 | 0.67778 | 143.1404 | -36.9104 | 116 | 102 | 6.3% | 8.8% | 123.308 | 108.426 | 0.01 | 0.02 | -1488.2 | 138.19 | 1.491% | 124.468 | 110.976 | 0.01 | 0.02 | -1349.2 | 137.96 | 1.628% | 149.1% | 0.9684% | 0.9851% | 1.002% | 1.018% | 1.035% | 1.052% | 1.069% | 1.085% | 1.102% | 1.119% | 1.135% | 1.152% | 1.169% | 1.185% | 1.202% | 1.219% | 1.236% | 1.252% | 1.269% | 1.286% | 0.00039217 | 0.00039894 | 0.0004057 | 0.00041246 | 0.00041923 | 0.00042599 | 0.00043275 | 0.00043952 | 0.00044628 | 0.00045304 | 0.00045981 | 0.00046657 | 0.00047334 | 0.0004801 | 0.00048686 | 0.00049363 | 0.00050039 | 0.00050715 | 0.00051392 | 0.00052068
| 10159700 | STL007 | STL | 17334189 | 15897021 | 0.87962 | 143.1747 | -36.9592 | 124 | 110 | 6.3% | 8.8% | 131.812 | 116.93 | 0.01 | 0.02 | -1488.2 | 146.694 | 1.525% | 133.052 | 119.68 | 0.01 | 0.02 | -1337.2 | 146.424 | 1.677% | 152.5% | 0.9718% | 0.9897% | 1.008% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.115% | 1.133% | 1.15% | 1.168% | 1.186% | 1.204% | 1.222% | 1.24% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039357 | 0.0004008 | 0.00040803 | 0.00041526 | 0.00042249 | 0.00042972 | 0.00043695 | 0.00044418 | 0.00045141 | 0.00045864 | 0.00046587 | 0.0004731 | 0.00048033 | 0.00048756 | 0.00049479 | 0.00050202 | 0.00050925 | 0.00051648 | 0.00052371 | 0.00053094
| 10159749 | STL007 | STL | 17333796 | 15897168 | 1.8068 | 143.1262 | -36.9994 | 123 | 108 | 6.3% | 8.8% | 130.749 | 114.804 | 0.01 | 0.02 | -1594.5 | 146.694 | 1.486% | 131.979 | 117.504 | 0.01 | 0.02 | -1447.5 | 146.454 | 1.62% | 148.6% | 0.9679% | 0.9844% | 1.001% | 1.017% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.133% | 1.15% | 1.166% | 1.183% | 1.199% | 1.216% | 1.232% | 1.249% | 1.265% | 1.282% | 0.00039196 | 0.00039866 | 0.00040535 | 0.00041204 | 0.00041874 | 0.00042543 | 0.00043212 | 0.00043882 | 0.00044551 | 0.00045221 | 0.0004589 | 0.00046559 | 0.00047229 | 0.00047898 | 0.00048567 | 0.00049237 | 0.00049906 | 0.00050575 | 0.00051245 | 0.00051914
| 10159758 | STL007 | STL | 17334121 | 15897205 | 1.1786 | 143.1416 | -37.0128 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10159822 | STL006 | STL | 16308068 | 15897428 | 1.444 | 142.7489 | -36.9064 | 112 | 98.6 | 6.3% | 8.8% | 119.056 | 104.8118 | 0.01 | 0.02 | -1424.42 | 133.3002 | 1.495% | 120.176 | 107.2768 | 0.01 | 0.02 | -1289.92 | 133.0752 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.003% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.222% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.000406 | 0.00041282 | 0.00041964 | 0.00042646 | 0.00043329 | 0.00044011 | 0.00044693 | 0.00045375 | 0.00046058 | 0.0004674 | 0.00047422 | 0.00048105 | 0.00048787 | 0.00049469 | 0.00050151 | 0.00050834 | 0.00051516 | 0.00052198
| 10159823 | STL006 | STL | 15897428 | 16308320 | 2.3405 | 142.7477 | -36.904 | 112 | 98.6 | 6.3% | 8.8% | 119.056 | 104.8118 | 0.01 | 0.02 | -1424.42 | 133.3002 | 1.495% | 120.176 | 107.2768 | 0.01 | 0.02 | -1289.92 | 133.0752 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.003% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.222% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.000406 | 0.00041282 | 0.00041964 | 0.00042646 | 0.00043329 | 0.00044011 | 0.00044693 | 0.00045375 | 0.00046058 | 0.0004674 | 0.00047422 | 0.00048105 | 0.00048787 | 0.00049469 | 0.00050151 | 0.00050834 | 0.00051516 | 0.00052198
| 10159824 | STL006 | STL | 15897428 | 16308072 | 2.2138 | 142.7508 | -36.9048 | 111 | 98 | 6.3% | 8.8% | 117.993 | 104.174 | 0.01 | 0.02 | -1381.9 | 131.812 | 1.506% | 119.103 | 106.624 | 0.01 | 0.02 | -1247.9 | 131.582 | 1.649% | 150.6% | 0.9699% | 0.9871% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.09% | 1.108% | 1.125% | 1.142% | 1.159% | 1.176% | 1.194% | 1.211% | 1.228% | 1.245% | 1.262% | 1.28% | 1.297% | 0.00039279 | 0.00039976 | 0.00040673 | 0.0004137 | 0.00042067 | 0.00042764 | 0.00043461 | 0.00044158 | 0.00044855 | 0.00045552 | 0.00046249 | 0.00046946 | 0.00047643 | 0.0004834 | 0.00049037 | 0.00049734 | 0.00050431 | 0.00051128 | 0.00051825 | 0.00052522
| 10159833 | STL006 | STL | 16308173 | 15897463 | 0.1372 | 142.785 | -36.9189 | 111 | 97.8 | 6.3% | 8.8% | 117.993 | 103.9614 | 0.01 | 0.02 | -1403.16 | 132.0246 | 1.498% | 119.103 | 106.4064 | 0.01 | 0.02 | -1269.66 | 131.7996 | 1.638% | 149.8% | 0.9691% | 0.9861% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.189% | 1.206% | 1.223% | 1.24% | 1.257% | 1.274% | 1.291% | 0.00039247 | 0.00039934 | 0.0004062 | 0.00041307 | 0.00041993 | 0.0004268 | 0.00043366 | 0.00044052 | 0.00044739 | 0.00045425 | 0.00046112 | 0.00046798 | 0.00047485 | 0.00048171 | 0.00048857 | 0.00049544 | 0.0005023 | 0.00050917 | 0.00051603 | 0.0005229
| 10160457 | STL006 | STL | 16308120 | 15900054 | 0.72881 | 142.7683 | -36.9159 | 111 | 98 | 6.3% | 8.8% | 117.993 | 104.174 | 0.01 | 0.02 | -1381.9 | 131.812 | 1.506% | 119.103 | 106.624 | 0.01 | 0.02 | -1247.9 | 131.582 | 1.649% | 150.6% | 0.9699% | 0.9871% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.09% | 1.108% | 1.125% | 1.142% | 1.159% | 1.176% | 1.194% | 1.211% | 1.228% | 1.245% | 1.262% | 1.28% | 1.297% | 0.00039279 | 0.00039976 | 0.00040673 | 0.0004137 | 0.00042067 | 0.00042764 | 0.00043461 | 0.00044158 | 0.00044855 | 0.00045552 | 0.00046249 | 0.00046946 | 0.00047643 | 0.0004834 | 0.00049037 | 0.00049734 | 0.00050431 | 0.00051128 | 0.00051825 | 0.00052522
| 10160458 | STL006 | STL | 15900054 | 16308108 | 0.57852 | 142.7668 | -36.9158 | 111 | 98 | 6.3% | 8.8% | 117.993 | 104.174 | 0.01 | 0.02 | -1381.9 | 131.812 | 1.506% | 119.103 | 106.624 | 0.01 | 0.02 | -1247.9 | 131.582 | 1.649% | 150.6% | 0.9699% | 0.9871% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.09% | 1.108% | 1.125% | 1.142% | 1.159% | 1.176% | 1.194% | 1.211% | 1.228% | 1.245% | 1.262% | 1.28% | 1.297% | 0.00039279 | 0.00039976 | 0.00040673 | 0.0004137 | 0.00042067 | 0.00042764 | 0.00043461 | 0.00044158 | 0.00044855 | 0.00045552 | 0.00046249 | 0.00046946 | 0.00047643 | 0.0004834 | 0.00049037 | 0.00049734 | 0.00050431 | 0.00051128 | 0.00051825 | 0.00052522
| 10160460 | STL006 | STL | 16308152 | 15900060 | 0.43462 | 142.785 | -36.9153 | 111 | 97.8 | 6.3% | 8.8% | 117.993 | 103.9614 | 0.01 | 0.02 | -1403.16 | 132.0246 | 1.498% | 119.103 | 106.4064 | 0.01 | 0.02 | -1269.66 | 131.7996 | 1.638% | 149.8% | 0.9691% | 0.9861% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.189% | 1.206% | 1.223% | 1.24% | 1.257% | 1.274% | 1.291% | 0.00039247 | 0.00039934 | 0.0004062 | 0.00041307 | 0.00041993 | 0.0004268 | 0.00043366 | 0.00044052 | 0.00044739 | 0.00045425 | 0.00046112 | 0.00046798 | 0.00047485 | 0.00048171 | 0.00048857 | 0.00049544 | 0.0005023 | 0.00050917 | 0.00051603 | 0.0005229
| 10162366 | STL006 | STL | 15908649 | 16308424 | 0.76169 | 142.7897 | -36.9116 | 111 | 97.8 | 6.3% | 8.8% | 117.993 | 103.9614 | 0.01 | 0.02 | -1403.16 | 132.0246 | 1.498% | 119.103 | 106.4064 | 0.01 | 0.02 | -1269.66 | 131.7996 | 1.638% | 149.8% | 0.9691% | 0.9861% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.189% | 1.206% | 1.223% | 1.24% | 1.257% | 1.274% | 1.291% | 0.00039247 | 0.00039934 | 0.0004062 | 0.00041307 | 0.00041993 | 0.0004268 | 0.00043366 | 0.00044052 | 0.00044739 | 0.00045425 | 0.00046112 | 0.00046798 | 0.00047485 | 0.00048171 | 0.00048857 | 0.00049544 | 0.0005023 | 0.00050917 | 0.00051603 | 0.0005229
| 10162370 | STL006 | STL | 16308424 | 15908654 | 0.718 | 142.7864 | -36.9118 | 111 | 97.8 | 6.3% | 8.8% | 117.993 | 103.9614 | 0.01 | 0.02 | -1403.16 | 132.0246 | 1.498% | 119.103 | 106.4064 | 0.01 | 0.02 | -1269.66 | 131.7996 | 1.638% | 149.8% | 0.9691% | 0.9861% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.189% | 1.206% | 1.223% | 1.24% | 1.257% | 1.274% | 1.291% | 0.00039247 | 0.00039934 | 0.0004062 | 0.00041307 | 0.00041993 | 0.0004268 | 0.00043366 | 0.00044052 | 0.00044739 | 0.00045425 | 0.00046112 | 0.00046798 | 0.00047485 | 0.00048171 | 0.00048857 | 0.00049544 | 0.0005023 | 0.00050917 | 0.00051603 | 0.0005229
| 10162417 | STL007 | STL | 17332888 | 15908812 | 0.22211 | 142.9912 | -37.0075 | 110 | 97.2 | 6.3% | 8.8% | 116.93 | 103.3236 | 0.01 | 0.02 | -1360.64 | 130.5364 | 1.509% | 118.03 | 105.7536 | 0.01 | 0.02 | -1227.64 | 130.3064 | 1.654% | 150.9% | 0.9702% | 0.9876% | 1.005% | 1.022% | 1.04% | 1.057% | 1.074% | 1.091% | 1.109% | 1.126% | 1.143% | 1.161% | 1.178% | 1.195% | 1.213% | 1.23% | 1.247% | 1.265% | 1.282% | 1.299% | 0.00039293 | 0.00039994 | 0.00040696 | 0.00041397 | 0.00042099 | 0.000428 | 0.00043502 | 0.00044203 | 0.00044905 | 0.00045606 | 0.00046308 | 0.00047009 | 0.00047711 | 0.00048412 | 0.00049114 | 0.00049815 | 0.00050517 | 0.00051218 | 0.0005192 | 0.00052621
| 10162477 | STL007 | STL | 17332953 | 15909004 | 0.21541 | 142.9794 | -37.0146 | 110 | 97.2 | 6.3% | 8.8% | 116.93 | 103.3236 | 0.01 | 0.02 | -1360.64 | 130.5364 | 1.509% | 118.03 | 105.7536 | 0.01 | 0.02 | -1227.64 | 130.3064 | 1.654% | 150.9% | 0.9702% | 0.9876% | 1.005% | 1.022% | 1.04% | 1.057% | 1.074% | 1.091% | 1.109% | 1.126% | 1.143% | 1.161% | 1.178% | 1.195% | 1.213% | 1.23% | 1.247% | 1.265% | 1.282% | 1.299% | 0.00039293 | 0.00039994 | 0.00040696 | 0.00041397 | 0.00042099 | 0.000428 | 0.00043502 | 0.00044203 | 0.00044905 | 0.00045606 | 0.00046308 | 0.00047009 | 0.00047711 | 0.00048412 | 0.00049114 | 0.00049815 | 0.00050517 | 0.00051218 | 0.0005192 | 0.00052621
| 10165961 | HSM004 | HSM | 16327487 | 15926046 | 1.0046 | 142.1185 | -36.7558 | 117 | 99.8 | 6.3% | 8.8% | 124.371 | 106.0874 | 0.01 | 0.02 | -1828.36 | 142.6546 | 1.403% | 125.541 | 108.5824 | 0.01 | 0.02 | -1695.86 | 142.4996 | 1.504% | 140.3% | 0.9594% | 0.9731% | 0.9868% | 1.001% | 1.014% | 1.028% | 1.042% | 1.055% | 1.069% | 1.083% | 1.097% | 1.11% | 1.124% | 1.138% | 1.151% | 1.165% | 1.179% | 1.192% | 1.206% | 1.22% | 0.00038854 | 0.00039409 | 0.00039965 | 0.0004052 | 0.00041075 | 0.0004163 | 0.00042186 | 0.00042741 | 0.00043296 | 0.00043851 | 0.00044407 | 0.00044962 | 0.00045517 | 0.00046073 | 0.00046628 | 0.00047183 | 0.00047738 | 0.00048294 | 0.00048849 | 0.00049404
| 10167756 | CTN006 | CTN | 15932906 | 16818243 | 0.77584 | 143.1481 | -36.6644 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10167757 | CTN006 | CTN | 15932911 | 16818211 | 0.46124 | 143.1399 | -36.6566 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10167767 | CTN006 | CTN | 15932947 | 15932952 | 0.14322 | 143.1531 | -36.6742 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10170532 | CTN006 | CTN | 193504963 | 15944528 | 0.83504 | 143.1545 | -36.6334 | 106 | 94.1 | 6.3% | 8.8% | 112.678 | 100.0283 | 0.01 | 0.02 | -1264.97 | 125.3277 | 1.528% | 113.738 | 102.3808 | 0.01 | 0.02 | -1135.72 | 125.0952 | 1.681% | 152.8% | 0.9721% | 0.9901% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.241% | 1.259% | 1.277% | 1.295% | 1.313% | 0.0003937 | 0.00040097 | 0.00040824 | 0.00041551 | 0.00042278 | 0.00043005 | 0.00043732 | 0.00044459 | 0.00045186 | 0.00045914 | 0.00046641 | 0.00047368 | 0.00048095 | 0.00048822 | 0.00049549 | 0.00050276 | 0.00051003 | 0.00051731 | 0.00052458 | 0.00053185
| 10173413 | BATSBAS1 | BAS | 15962778 | 17742437 | 0.3681 | 143.8617 | -37.566 | 119 | 105 | 5.4% | 7.3% | 125.426 | 110.67 | 0.01 | 0.02 | -1475.6 | 140.182 | 1.435% | 127.687 | 112.665 | 0.01 | 0.02 | -1502.2 | 142.709 | 1.578% | 143.5% | 0.9627% | 0.9775% | 0.9923% | 1.007% | 1.022% | 1.037% | 1.052% | 1.066% | 1.081% | 1.096% | 1.111% | 1.126% | 1.14% | 1.155% | 1.17% | 1.185% | 1.2% | 1.214% | 1.229% | 1.244% | 0.00038988 | 0.00039587 | 0.00040187 | 0.00040787 | 0.00041387 | 0.00041987 | 0.00042586 | 0.00043186 | 0.00043786 | 0.00044386 | 0.00044986 | 0.00045585 | 0.00046185 | 0.00046785 | 0.00047385 | 0.00047985 | 0.00048585 | 0.00049184 | 0.00049784 | 0.00050384
| 10173503 | CHM011 | CHM | 41075546 | 15964427 | 1.8126 | 141.4992 | -36.9041 | 115 | 98.4 | 6.3% | 8.8% | 122.245 | 104.5992 | 0.01 | 0.02 | -1764.58 | 139.8908 | 1.411% | 123.395 | 107.0592 | 0.01 | 0.02 | -1633.58 | 139.7308 | 1.514% | 141.1% | 0.9602% | 0.9741% | 0.9881% | 1.002% | 1.016% | 1.03% | 1.044% | 1.058% | 1.072% | 1.086% | 1.1% | 1.114% | 1.128% | 1.142% | 1.156% | 1.17% | 1.184% | 1.198% | 1.212% | 1.225% | 0.00038885 | 0.0003945 | 0.00040016 | 0.00040581 | 0.00041147 | 0.00041712 | 0.00042278 | 0.00042843 | 0.00043409 | 0.00043974 | 0.0004454 | 0.00045105 | 0.00045671 | 0.00046236 | 0.00046802 | 0.00047367 | 0.00047933 | 0.00048498 | 0.00049064 | 0.00049629
| 10182107 | BET005 | BETS | 16001148 | 16001158 | 0.62829 | 144.5457 | -36.9192 | 111 | 99.8 | 6.3% | 8.8% | 117.993 | 106.0874 | 0.01 | 0.02 | -1190.56 | 129.8986 | 1.587% | 119.103 | 108.5824 | 0.01 | 0.02 | -1052.06 | 129.6236 | 1.77% | 158.7% | 0.9782% | 0.9982% | 1.018% | 1.038% | 1.058% | 1.078% | 1.098% | 1.118% | 1.138% | 1.158% | 1.178% | 1.198% | 1.218% | 1.238% | 1.258% | 1.278% | 1.298% | 1.318% | 1.338% | 1.358% | 0.00039615 | 0.00040424 | 0.00041233 | 0.00042042 | 0.00042851 | 0.0004366 | 0.00044469 | 0.00045278 | 0.00046087 | 0.00046896 | 0.00047705 | 0.00048514 | 0.00049323 | 0.00050132 | 0.00050941 | 0.0005175 | 0.00052559 | 0.00053368 | 0.00054177 | 0.00054986
| 10182494 | HSM004 | HSM | 16002428 | 16457665 | 0.49055 | 141.5339 | -36.9666 | 117 | 99.8 | 6.3% | 8.8% | 124.371 | 106.0874 | 0.01 | 0.02 | -1828.36 | 142.6546 | 1.403% | 125.541 | 108.5824 | 0.01 | 0.02 | -1695.86 | 142.4996 | 1.504% | 140.3% | 0.9594% | 0.9731% | 0.9868% | 1.001% | 1.014% | 1.028% | 1.042% | 1.055% | 1.069% | 1.083% | 1.097% | 1.11% | 1.124% | 1.138% | 1.151% | 1.165% | 1.179% | 1.192% | 1.206% | 1.22% | 0.00038854 | 0.00039409 | 0.00039965 | 0.0004052 | 0.00041075 | 0.0004163 | 0.00042186 | 0.00042741 | 0.00043296 | 0.00043851 | 0.00044407 | 0.00044962 | 0.00045517 | 0.00046073 | 0.00046628 | 0.00047183 | 0.00047738 | 0.00048294 | 0.00048849 | 0.00049404
| 10183243 | NHL016 | NHL | 16489273 | 181448759 | 1.2625 | 141.8421 | -35.9764 | 141 | 117 | 6.3% | 8.8% | 149.883 | 124.371 | 0.01 | 0.02 | -2551.2 | 175.395 | 1.348% | 151.293 | 127.296 | 0.01 | 0.02 | -2399.7 | 175.29 | 1.429% | 134.8% | 0.9538% | 0.9656% | 0.9775% | 0.9893% | 1.001% | 1.013% | 1.025% | 1.037% | 1.049% | 1.06% | 1.072% | 1.084% | 1.096% | 1.108% | 1.12% | 1.131% | 1.143% | 1.155% | 1.167% | 1.179% | 0.00038627 | 0.00039106 | 0.00039586 | 0.00040066 | 0.00040545 | 0.00041025 | 0.00041504 | 0.00041984 | 0.00042463 | 0.00042943 | 0.00043423 | 0.00043902 | 0.00044382 | 0.00044861 | 0.00045341 | 0.00045821 | 0.000463 | 0.0004678 | 0.00047259 | 0.00047739
| 10184457 | EHK031 | EHK | 16009501 | 16643367 | 0.91069 | 144.5175 | -36.7175 | 106 | 95.9 | 6.3% | 8.8% | 112.678 | 101.9417 | 0.01 | 0.02 | -1073.63 | 123.4143 | 1.622% | 113.738 | 104.3392 | 0.01 | 0.02 | -939.88 | 123.1368 | 1.823% | 162.2% | 0.9817% | 1.003% | 1.024% | 1.045% | 1.066% | 1.088% | 1.109% | 1.13% | 1.151% | 1.172% | 1.193% | 1.214% | 1.236% | 1.257% | 1.278% | 1.299% | 1.32% | 1.341% | 1.363% | 1.384% | 0.00039758 | 0.00040615 | 0.00041472 | 0.00042328 | 0.00043185 | 0.00044042 | 0.00044899 | 0.00045755 | 0.00046612 | 0.00047469 | 0.00048325 | 0.00049182 | 0.00050039 | 0.00050895 | 0.00051752 | 0.00052609 | 0.00053466 | 0.00054322 | 0.00055179 | 0.00056036
| 10186354 | EHK024 | EHK | 16016653 | 16932664 | 0.88841 | 143.8618 | -36.3272 | 103 | 92.4 | 6.3% | 8.8% | 109.489 | 98.2212 | 0.01 | 0.02 | -1126.78 | 120.7568 | 1.576% | 110.519 | 100.5312 | 0.01 | 0.02 | -998.78 | 120.5068 | 1.753% | 157.6% | 0.977% | 0.9966% | 1.016% | 1.036% | 1.055% | 1.075% | 1.095% | 1.114% | 1.134% | 1.153% | 1.173% | 1.192% | 1.212% | 1.232% | 1.251% | 1.271% | 1.29% | 1.31% | 1.33% | 1.349% | 0.00039568 | 0.00040361 | 0.00041154 | 0.00041947 | 0.00042741 | 0.00043534 | 0.00044327 | 0.0004512 | 0.00045913 | 0.00046706 | 0.000475 | 0.00048293 | 0.00049086 | 0.00049879 | 0.00050672 | 0.00051466 | 0.00052259 | 0.00053052 | 0.00053845 | 0.00054638
| 10186356 | EHK024 | EHK | 16932668 | 16016653 | 0.42163 | 143.8639 | -36.3276 | 103 | 92.4 | 6.3% | 8.8% | 109.489 | 98.2212 | 0.01 | 0.02 | -1126.78 | 120.7568 | 1.576% | 110.519 | 100.5312 | 0.01 | 0.02 | -998.78 | 120.5068 | 1.753% | 157.6% | 0.977% | 0.9966% | 1.016% | 1.036% | 1.055% | 1.075% | 1.095% | 1.114% | 1.134% | 1.153% | 1.173% | 1.192% | 1.212% | 1.232% | 1.251% | 1.271% | 1.29% | 1.31% | 1.33% | 1.349% | 0.00039568 | 0.00040361 | 0.00041154 | 0.00041947 | 0.00042741 | 0.00043534 | 0.00044327 | 0.0004512 | 0.00045913 | 0.00046706 | 0.000475 | 0.00048293 | 0.00049086 | 0.00049879 | 0.00050672 | 0.00051466 | 0.00052259 | 0.00053052 | 0.00053845 | 0.00054638
| 10186359 | EHK024 | EHK | 16932664 | 16016663 | 1.0065 | 143.8588 | -36.3286 | 103 | 92.4 | 6.3% | 8.8% | 109.489 | 98.2212 | 0.01 | 0.02 | -1126.78 | 120.7568 | 1.576% | 110.519 | 100.5312 | 0.01 | 0.02 | -998.78 | 120.5068 | 1.753% | 157.6% | 0.977% | 0.9966% | 1.016% | 1.036% | 1.055% | 1.075% | 1.095% | 1.114% | 1.134% | 1.153% | 1.173% | 1.192% | 1.212% | 1.232% | 1.251% | 1.271% | 1.29% | 1.31% | 1.33% | 1.349% | 0.00039568 | 0.00040361 | 0.00041154 | 0.00041947 | 0.00042741 | 0.00043534 | 0.00044327 | 0.0004512 | 0.00045913 | 0.00046706 | 0.000475 | 0.00048293 | 0.00049086 | 0.00049879 | 0.00050672 | 0.00051466 | 0.00052259 | 0.00053052 | 0.00053845 | 0.00054638
| 10186730 | BET006 | BETS | 16017903 | 17383889 | 0.31302 | 143.8956 | -36.6672 | 102 | 92.6 | 6.3% | 8.8% | 108.426 | 98.4338 | 0.01 | 0.02 | -999.22 | 118.4182 | 1.643% | 109.446 | 100.7488 | 0.01 | 0.02 | -869.72 | 118.1432 | 1.856% | 164.3% | 0.9839% | 1.006% | 1.028% | 1.05% | 1.071% | 1.093% | 1.115% | 1.137% | 1.159% | 1.181% | 1.203% | 1.224% | 1.246% | 1.268% | 1.29% | 1.312% | 1.334% | 1.356% | 1.378% | 1.399% | 0.00039845 | 0.00040731 | 0.00041617 | 0.00042503 | 0.00043389 | 0.00044274 | 0.0004516 | 0.00046046 | 0.00046932 | 0.00047817 | 0.00048703 | 0.00049589 | 0.00050475 | 0.0005136 | 0.00052246 | 0.00053132 | 0.00054018 | 0.00054904 | 0.00055789 | 0.00056675
| 10187532 | BET006 | BETS | 16021939 | 16021924 | 3.0575 | 143.9025 | -36.7616 | 102 | 92.7 | 6.3% | 8.8% | 108.426 | 98.5401 | 0.01 | 0.02 | -988.59 | 118.3119 | 1.65% | 109.446 | 100.8576 | 0.01 | 0.02 | -858.84 | 118.0344 | 1.867% | 165% | 0.9846% | 1.007% | 1.029% | 1.051% | 1.073% | 1.095% | 1.117% | 1.139% | 1.161% | 1.184% | 1.206% | 1.228% | 1.25% | 1.272% | 1.294% | 1.316% | 1.338% | 1.36% | 1.383% | 1.405% | 0.00039874 | 0.00040769 | 0.00041665 | 0.0004256 | 0.00043455 | 0.00044351 | 0.00045246 | 0.00046141 | 0.00047036 | 0.00047932 | 0.00048827 | 0.00049722 | 0.00050618 | 0.00051513 | 0.00052408 | 0.00053303 | 0.00054199 | 0.00055094 | 0.00055989 | 0.00056885
| 10187618 | BET006 | BETS | 16022176 | 17247437 | 0.2134 | 143.795 | -36.7305 | 103 | 92.9 | 6.3% | 8.8% | 109.489 | 98.7527 | 0.01 | 0.02 | -1073.63 | 120.2253 | 1.604% | 110.519 | 101.0752 | 0.01 | 0.02 | -944.38 | 119.9628 | 1.796% | 160.4% | 0.9799% | 1% | 1.021% | 1.042% | 1.062% | 1.083% | 1.103% | 1.124% | 1.144% | 1.165% | 1.185% | 1.206% | 1.227% | 1.247% | 1.268% | 1.288% | 1.309% | 1.329% | 1.35% | 1.37% | 0.00039686 | 0.00040518 | 0.0004135 | 0.00042183 | 0.00043015 | 0.00043848 | 0.0004468 | 0.00045513 | 0.00046345 | 0.00047178 | 0.0004801 | 0.00048843 | 0.00049675 | 0.00050508 | 0.0005134 | 0.00052172 | 0.00053005 | 0.00053837 | 0.0005467 | 0.00055502
| 10187619 | BET006 | BETS | 17247437 | 16022182 | 0.44065 | 143.7914 | -36.7305 | 103 | 92.9 | 6.3% | 8.8% | 109.489 | 98.7527 | 0.01 | 0.02 | -1073.63 | 120.2253 | 1.604% | 110.519 | 101.0752 | 0.01 | 0.02 | -944.38 | 119.9628 | 1.796% | 160.4% | 0.9799% | 1% | 1.021% | 1.042% | 1.062% | 1.083% | 1.103% | 1.124% | 1.144% | 1.165% | 1.185% | 1.206% | 1.227% | 1.247% | 1.268% | 1.288% | 1.309% | 1.329% | 1.35% | 1.37% | 0.00039686 | 0.00040518 | 0.0004135 | 0.00042183 | 0.00043015 | 0.00043848 | 0.0004468 | 0.00045513 | 0.00046345 | 0.00047178 | 0.0004801 | 0.00048843 | 0.00049675 | 0.00050508 | 0.0005134 | 0.00052172 | 0.00053005 | 0.00053837 | 0.0005467 | 0.00055502
| 10190219 | NHL015 | NHL | 16030921 | 16202696 | 2.9044 | 142.0158 | -36.3974 | 128 | 108 | 6.3% | 8.8% | 136.064 | 114.804 | 0.01 | 0.02 | -2126 | 157.324 | 1.379% | 137.344 | 117.504 | 0.01 | 0.02 | -1984 | 157.184 | 1.471% | 137.9% | 0.957% | 0.9699% | 0.9828% | 0.9957% | 1.009% | 1.021% | 1.034% | 1.047% | 1.06% | 1.073% | 1.086% | 1.099% | 1.112% | 1.125% | 1.138% | 1.15% | 1.163% | 1.176% | 1.189% | 1.202% | 0.00038755 | 0.00039278 | 0.000398 | 0.00040323 | 0.00040845 | 0.00041368 | 0.0004189 | 0.00042412 | 0.00042935 | 0.00043457 | 0.0004398 | 0.00044502 | 0.00045025 | 0.00045547 | 0.00046069 | 0.00046592 | 0.00047114 | 0.00047637 | 0.00048159 | 0.00048682
| 10191201 | NKA006 | RCTS | 16034379 | 17124734 | 0.53437 | 145.4101 | -35.8659 | 117 | 104 | 6.3% | 8.8% | 124.371 | 110.552 | 0.01 | 0.02 | -1381.9 | 138.19 | 1.533% | 125.541 | 113.152 | 0.01 | 0.02 | -1238.9 | 137.93 | 1.689% | 153.3% | 0.9727% | 0.9908% | 1.009% | 1.027% | 1.045% | 1.063% | 1.082% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.19% | 1.209% | 1.227% | 1.245% | 1.263% | 1.281% | 1.299% | 1.317% | 0.00039392 | 0.00040127 | 0.00040861 | 0.00041596 | 0.00042331 | 0.00043065 | 0.000438 | 0.00044535 | 0.0004527 | 0.00046004 | 0.00046739 | 0.00047474 | 0.00048208 | 0.00048943 | 0.00049678 | 0.00050412 | 0.00051147 | 0.00051882 | 0.00052616 | 0.00053351
| 10191767 | BAN003 | BAN | 16036408 | 17490974 | 0.67995 | 144.2214 | -37.3141 | 139 | 123 | 6.3% | 8.8% | 147.757 | 130.749 | 0.01 | 0.02 | -1700.8 | 164.765 | 1.515% | 149.147 | 133.824 | 0.01 | 0.02 | -1532.3 | 164.47 | 1.662% | 151.5% | 0.9708% | 0.9883% | 1.006% | 1.023% | 1.041% | 1.058% | 1.076% | 1.093% | 1.111% | 1.128% | 1.146% | 1.163% | 1.181% | 1.198% | 1.216% | 1.233% | 1.251% | 1.268% | 1.286% | 1.304% | 0.00039316 | 0.00040025 | 0.00040734 | 0.00041443 | 0.00042152 | 0.00042861 | 0.00043571 | 0.0004428 | 0.00044989 | 0.00045698 | 0.00046407 | 0.00047116 | 0.00047826 | 0.00048535 | 0.00049244 | 0.00049953 | 0.00050662 | 0.00051371 | 0.0005208 | 0.0005279
| 10196439 | MRO007 | MRO | 17389512 | 16052586 | 2.4998 | 144.003 | -36.876 | 110 | 98.5 | 6.3% | 8.8% | 116.93 | 104.7055 | 0.01 | 0.02 | -1222.45 | 129.1545 | 1.567% | 118.03 | 107.168 | 0.01 | 0.02 | -1086.2 | 128.892 | 1.739% | 156.7% | 0.9761% | 0.9954% | 1.015% | 1.034% | 1.053% | 1.073% | 1.092% | 1.111% | 1.13% | 1.15% | 1.169% | 1.188% | 1.207% | 1.227% | 1.246% | 1.265% | 1.285% | 1.304% | 1.323% | 1.342% | 0.00039531 | 0.00040311 | 0.00041092 | 0.00041873 | 0.00042654 | 0.00043435 | 0.00044215 | 0.00044996 | 0.00045777 | 0.00046558 | 0.00047339 | 0.00048119 | 0.000489 | 0.00049681 | 0.00050462 | 0.00051243 | 0.00052023 | 0.00052804 | 0.00053585 | 0.00054366
| 10196454 | MRO007 | MRO | 16052634 | 17389617 | 1.4816 | 144.0218 | -36.8778 | 110 | 98.5 | 6.3% | 8.8% | 116.93 | 104.7055 | 0.01 | 0.02 | -1222.45 | 129.1545 | 1.567% | 118.03 | 107.168 | 0.01 | 0.02 | -1086.2 | 128.892 | 1.739% | 156.7% | 0.9761% | 0.9954% | 1.015% | 1.034% | 1.053% | 1.073% | 1.092% | 1.111% | 1.13% | 1.15% | 1.169% | 1.188% | 1.207% | 1.227% | 1.246% | 1.265% | 1.285% | 1.304% | 1.323% | 1.342% | 0.00039531 | 0.00040311 | 0.00041092 | 0.00041873 | 0.00042654 | 0.00043435 | 0.00044215 | 0.00044996 | 0.00045777 | 0.00046558 | 0.00047339 | 0.00048119 | 0.000489 | 0.00049681 | 0.00050462 | 0.00051243 | 0.00052023 | 0.00052804 | 0.00053585 | 0.00054366
| 10196456 | MRO007 | MRO | 16052645 | 17389613 | 3.8358 | 144.0198 | -36.8756 | 110 | 98.5 | 6.3% | 8.8% | 116.93 | 104.7055 | 0.01 | 0.02 | -1222.45 | 129.1545 | 1.567% | 118.03 | 107.168 | 0.01 | 0.02 | -1086.2 | 128.892 | 1.739% | 156.7% | 0.9761% | 0.9954% | 1.015% | 1.034% | 1.053% | 1.073% | 1.092% | 1.111% | 1.13% | 1.15% | 1.169% | 1.188% | 1.207% | 1.227% | 1.246% | 1.265% | 1.285% | 1.304% | 1.323% | 1.342% | 0.00039531 | 0.00040311 | 0.00041092 | 0.00041873 | 0.00042654 | 0.00043435 | 0.00044215 | 0.00044996 | 0.00045777 | 0.00046558 | 0.00047339 | 0.00048119 | 0.000489 | 0.00049681 | 0.00050462 | 0.00051243 | 0.00052023 | 0.00052804 | 0.00053585 | 0.00054366
| 10198480 | MRO008 | MRO | 17094171 | 16059468 | 1.8216 | 143.6843 | -37.0522 | 111 | 99.1 | 6.3% | 8.8% | 117.993 | 105.3433 | 0.01 | 0.02 | -1264.97 | 130.6427 | 1.553% | 119.103 | 107.8208 | 0.01 | 0.02 | -1128.22 | 130.3852 | 1.718% | 155.3% | 0.9747% | 0.9935% | 1.012% | 1.031% | 1.05% | 1.069% | 1.087% | 1.106% | 1.125% | 1.144% | 1.163% | 1.181% | 1.2% | 1.219% | 1.238% | 1.257% | 1.276% | 1.294% | 1.313% | 1.332% | 0.00039472 | 0.00040234 | 0.00040995 | 0.00041757 | 0.00042518 | 0.0004328 | 0.00044041 | 0.00044802 | 0.00045564 | 0.00046325 | 0.00047087 | 0.00047848 | 0.00048609 | 0.00049371 | 0.00050132 | 0.00050894 | 0.00051655 | 0.00052417 | 0.00053178 | 0.00053939
| 10203381 | SHN011 | SHN | 16084593 | 16935750 | 0.49768 | 145.43 | -36.2991 | 113 | 99.5 | 6.3% | 8.8% | 120.119 | 105.7685 | 0.01 | 0.02 | -1435.05 | 134.4695 | 1.496% | 121.249 | 108.256 | 0.01 | 0.02 | -1299.3 | 134.242 | 1.635% | 149.6% | 0.9689% | 0.9858% | 1.003% | 1.02% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.121% | 1.138% | 1.154% | 1.171% | 1.188% | 1.205% | 1.222% | 1.239% | 1.256% | 1.273% | 1.289% | 0.00039238 | 0.00039921 | 0.00040605 | 0.00041288 | 0.00041971 | 0.00042654 | 0.00043338 | 0.00044021 | 0.00044704 | 0.00045387 | 0.00046071 | 0.00046754 | 0.00047437 | 0.0004812 | 0.00048804 | 0.00049487 | 0.0005017 | 0.00050854 | 0.00051537 | 0.0005222
| 10205049 | NHL015 | NHL | 200211340 | 16090552 | 0.80968 | 141.9738 | -36.4142 | 129 | 109 | 6.3% | 8.8% | 137.127 | 115.867 | 0.01 | 0.02 | -2126 | 158.387 | 1.382% | 138.417 | 118.592 | 0.01 | 0.02 | -1982.5 | 158.242 | 1.475% | 138.2% | 0.9573% | 0.9703% | 0.9833% | 0.9963% | 1.009% | 1.022% | 1.035% | 1.048% | 1.061% | 1.074% | 1.087% | 1.1% | 1.113% | 1.126% | 1.139% | 1.152% | 1.165% | 1.178% | 1.191% | 1.204% | 0.00038768 | 0.00039294 | 0.00039821 | 0.00040347 | 0.00040874 | 0.000414 | 0.00041927 | 0.00042453 | 0.0004298 | 0.00043506 | 0.00044033 | 0.00044559 | 0.00045086 | 0.00045612 | 0.00046139 | 0.00046665 | 0.00047192 | 0.00047718 | 0.00048245 | 0.00048771
| 10206645 | KGT004 | KGTS | 16737748 | 16096464 | 0.1035 | 143.7602 | -35.5829 | 105 | 93.1 | 6.3% | 8.8% | 111.615 | 98.9653 | 0.01 | 0.02 | -1264.97 | 124.2647 | 1.523% | 112.665 | 101.2928 | 0.01 | 0.02 | -1137.22 | 124.0372 | 1.674% | 152.3% | 0.9716% | 0.9894% | 1.007% | 1.025% | 1.043% | 1.061% | 1.078% | 1.096% | 1.114% | 1.132% | 1.149% | 1.167% | 1.185% | 1.203% | 1.221% | 1.238% | 1.256% | 1.274% | 1.292% | 1.31% | 0.00039349 | 0.00040069 | 0.00040789 | 0.0004151 | 0.0004223 | 0.0004295 | 0.00043671 | 0.00044391 | 0.00045111 | 0.00045831 | 0.00046552 | 0.00047272 | 0.00047992 | 0.00048712 | 0.00049433 | 0.00050153 | 0.00050873 | 0.00051593 | 0.00052314 | 0.00053034
| 10207652 | KGT004 | KGTS | 16100942 | 203163382 | 0.19835 | 143.8368 | -35.6003 | 107 | 94.8 | 6.3% | 8.8% | 113.741 | 100.7724 | 0.01 | 0.02 | -1296.86 | 126.7096 | 1.52% | 114.811 | 103.1424 | 0.01 | 0.02 | -1166.86 | 126.4796 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.29% | 1.307% | 0.00039336 | 0.00040052 | 0.00040768 | 0.00041484 | 0.000422 | 0.00042916 | 0.00043632 | 0.00044347 | 0.00045063 | 0.00045779 | 0.00046495 | 0.00047211 | 0.00047927 | 0.00048643 | 0.00049359 | 0.00050075 | 0.00050791 | 0.00051507 | 0.00052223 | 0.00052939
| 10207676 | HTN011 | HTN | 16101049 | 16450195 | 1.0461 | 142.0033 | -38.0371 | 129 | 109 | 5.4% | 7.3% | 135.966 | 114.886 | 0.01 | 0.02 | -2108 | 157.046 | 1.33% | 138.417 | 116.957 | 0.01 | 0.02 | -2146 | 159.877 | 1.439% | 133% | 0.952% | 0.9632% | 0.9745% | 0.9857% | 0.9969% | 1.008% | 1.019% | 1.031% | 1.042% | 1.053% | 1.064% | 1.076% | 1.087% | 1.098% | 1.109% | 1.121% | 1.132% | 1.143% | 1.154% | 1.166% | 0.00038554 | 0.00039009 | 0.00039464 | 0.00039919 | 0.00040374 | 0.00040829 | 0.00041285 | 0.0004174 | 0.00042195 | 0.0004265 | 0.00043105 | 0.0004356 | 0.00044015 | 0.00044471 | 0.00044926 | 0.00045381 | 0.00045836 | 0.00046291 | 0.00046746 | 0.00047201
| 10208645 | HTN011 | HTN | 16104486 | 16104481 | 0.25496 | 141.8576 | -37.9988 | 128 | 108 | 5.4% | 7.3% | 134.912 | 113.832 | 0.01 | 0.02 | -2108 | 155.992 | 1.328% | 137.344 | 115.884 | 0.01 | 0.02 | -2146 | 158.804 | 1.435% | 132.8% | 0.9517% | 0.9629% | 0.974% | 0.9852% | 0.9963% | 1.007% | 1.019% | 1.03% | 1.041% | 1.052% | 1.063% | 1.074% | 1.086% | 1.097% | 1.108% | 1.119% | 1.13% | 1.141% | 1.152% | 1.164% | 0.00038543 | 0.00038995 | 0.00039446 | 0.00039898 | 0.0004035 | 0.00040801 | 0.00041253 | 0.00041704 | 0.00042156 | 0.00042608 | 0.00043059 | 0.00043511 | 0.00043962 | 0.00044414 | 0.00044866 | 0.00045317 | 0.00045769 | 0.00046221 | 0.00046672 | 0.00047124
| 10208648 | HTN011 | HTN | 16104486 | 16449707 | 1.2519 | 141.8565 | -37.9999 | 128 | 108 | 5.4% | 7.3% | 134.912 | 113.832 | 0.01 | 0.02 | -2108 | 155.992 | 1.328% | 137.344 | 115.884 | 0.01 | 0.02 | -2146 | 158.804 | 1.435% | 132.8% | 0.9517% | 0.9629% | 0.974% | 0.9852% | 0.9963% | 1.007% | 1.019% | 1.03% | 1.041% | 1.052% | 1.063% | 1.074% | 1.086% | 1.097% | 1.108% | 1.119% | 1.13% | 1.141% | 1.152% | 1.164% | 0.00038543 | 0.00038995 | 0.00039446 | 0.00039898 | 0.0004035 | 0.00040801 | 0.00041253 | 0.00041704 | 0.00042156 | 0.00042608 | 0.00043059 | 0.00043511 | 0.00043962 | 0.00044414 | 0.00044866 | 0.00045317 | 0.00045769 | 0.00046221 | 0.00046672 | 0.00047124
| 10209776 | HTN011 | HTN | 16449686 | 16108208 | 0.39084 | 141.8459 | -37.9968 | 126 | 107 | 5.4% | 7.3% | 132.804 | 112.778 | 0.01 | 0.02 | -2002.6 | 152.83 | 1.34% | 135.198 | 114.811 | 0.01 | 0.02 | -2038.7 | 155.585 | 1.451% | 134% | 0.9529% | 0.9645% | 0.976% | 0.9876% | 0.9992% | 1.011% | 1.022% | 1.034% | 1.045% | 1.057% | 1.068% | 1.08% | 1.092% | 1.103% | 1.115% | 1.126% | 1.138% | 1.149% | 1.161% | 1.172% | 0.00038592 | 0.0003906 | 0.00039528 | 0.00039996 | 0.00040464 | 0.00040932 | 0.000414 | 0.00041868 | 0.00042336 | 0.00042804 | 0.00043272 | 0.0004374 | 0.00044208 | 0.00044676 | 0.00045144 | 0.00045611 | 0.00046079 | 0.00046547 | 0.00047015 | 0.00047483
| 10209778 | HTN011 | HTN | 16108208 | 16449836 | 1.4509 | 141.8425 | -37.9969 | 126 | 107 | 5.4% | 7.3% | 132.804 | 112.778 | 0.01 | 0.02 | -2002.6 | 152.83 | 1.34% | 135.198 | 114.811 | 0.01 | 0.02 | -2038.7 | 155.585 | 1.451% | 134% | 0.9529% | 0.9645% | 0.976% | 0.9876% | 0.9992% | 1.011% | 1.022% | 1.034% | 1.045% | 1.057% | 1.068% | 1.08% | 1.092% | 1.103% | 1.115% | 1.126% | 1.138% | 1.149% | 1.161% | 1.172% | 0.00038592 | 0.0003906 | 0.00039528 | 0.00039996 | 0.00040464 | 0.00040932 | 0.000414 | 0.00041868 | 0.00042336 | 0.00042804 | 0.00043272 | 0.0004374 | 0.00044208 | 0.00044676 | 0.00045144 | 0.00045611 | 0.00046079 | 0.00046547 | 0.00047015 | 0.00047483
| 10210955 | BAS011 | BAS | 16113809 | 16113801 | 0.38225 | 143.3683 | -37.5154 | 111 | 98.1 | 5.4% | 7.3% | 116.994 | 103.3974 | 0.01 | 0.02 | -1359.66 | 130.5906 | 1.441% | 119.103 | 105.2613 | 0.01 | 0.02 | -1384.17 | 132.9447 | 1.585% | 144.1% | 0.9633% | 0.9782% | 0.9932% | 1.008% | 1.023% | 1.038% | 1.053% | 1.068% | 1.083% | 1.098% | 1.113% | 1.128% | 1.143% | 1.158% | 1.173% | 1.188% | 1.203% | 1.218% | 1.233% | 1.248% | 0.0003901 | 0.00039617 | 0.00040224 | 0.00040831 | 0.00041439 | 0.00042046 | 0.00042653 | 0.0004326 | 0.00043867 | 0.00044474 | 0.00045082 | 0.00045689 | 0.00046296 | 0.00046903 | 0.0004751 | 0.00048118 | 0.00048725 | 0.00049332 | 0.00049939 | 0.00050546
| 10213821 | SHN021 | SHN | 16126616 | 16126621 | 1.4637 | 145.3814 | -36.3261 | 113 | 99.7 | 6.3% | 8.8% | 120.119 | 105.9811 | 0.01 | 0.02 | -1413.79 | 134.2569 | 1.504% | 121.249 | 108.4736 | 0.01 | 0.02 | -1277.54 | 134.0244 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039269 | 0.00039962 | 0.00040656 | 0.00041349 | 0.00042043 | 0.00042737 | 0.0004343 | 0.00044124 | 0.00044817 | 0.00045511 | 0.00046204 | 0.00046898 | 0.00047591 | 0.00048285 | 0.00048978 | 0.00049672 | 0.00050366 | 0.00051059 | 0.00051753 | 0.00052446
| 10214005 | EHK024 | EHK | 16127451 | 63214950 | 0.43575 | 144.2964 | -36.3765 | 103 | 93 | 6.3% | 8.8% | 109.489 | 98.859 | 0.01 | 0.02 | -1063 | 120.119 | 1.61% | 110.519 | 101.184 | 0.01 | 0.02 | -933.5 | 119.854 | 1.805% | 161% | 0.9806% | 1.001% | 1.022% | 1.043% | 1.064% | 1.084% | 1.105% | 1.126% | 1.147% | 1.167% | 1.188% | 1.209% | 1.23% | 1.25% | 1.271% | 1.292% | 1.313% | 1.333% | 1.354% | 1.375% | 0.00039711 | 0.00040551 | 0.00041392 | 0.00042233 | 0.00043074 | 0.00043914 | 0.00044755 | 0.00045596 | 0.00046437 | 0.00047278 | 0.00048118 | 0.00048959 | 0.000498 | 0.00050641 | 0.00051482 | 0.00052322 | 0.00053163 | 0.00054004 | 0.00054845 | 0.00055685
| 10214006 | EHK024 | EHK | 16127472 | 16127459 | 1.7741 | 144.2901 | -36.3697 | 103 | 92.9 | 6.3% | 8.8% | 109.489 | 98.7527 | 0.01 | 0.02 | -1073.63 | 120.2253 | 1.604% | 110.519 | 101.0752 | 0.01 | 0.02 | -944.38 | 119.9628 | 1.796% | 160.4% | 0.9799% | 1% | 1.021% | 1.042% | 1.062% | 1.083% | 1.103% | 1.124% | 1.144% | 1.165% | 1.185% | 1.206% | 1.227% | 1.247% | 1.268% | 1.288% | 1.309% | 1.329% | 1.35% | 1.37% | 0.00039686 | 0.00040518 | 0.0004135 | 0.00042183 | 0.00043015 | 0.00043848 | 0.0004468 | 0.00045513 | 0.00046345 | 0.00047178 | 0.0004801 | 0.00048843 | 0.00049675 | 0.00050508 | 0.0005134 | 0.00052172 | 0.00053005 | 0.00053837 | 0.0005467 | 0.00055502
| 10214007 | EHK024 | EHK | 16127459 | 137370486 | 0.18106 | 144.2927 | -36.3719 | 103 | 92.9 | 6.3% | 8.8% | 109.489 | 98.7527 | 0.01 | 0.02 | -1073.63 | 120.2253 | 1.604% | 110.519 | 101.0752 | 0.01 | 0.02 | -944.38 | 119.9628 | 1.796% | 160.4% | 0.9799% | 1% | 1.021% | 1.042% | 1.062% | 1.083% | 1.103% | 1.124% | 1.144% | 1.165% | 1.185% | 1.206% | 1.227% | 1.247% | 1.268% | 1.288% | 1.309% | 1.329% | 1.35% | 1.37% | 0.00039686 | 0.00040518 | 0.0004135 | 0.00042183 | 0.00043015 | 0.00043848 | 0.0004468 | 0.00045513 | 0.00046345 | 0.00047178 | 0.0004801 | 0.00048843 | 0.00049675 | 0.00050508 | 0.0005134 | 0.00052172 | 0.00053005 | 0.00053837 | 0.0005467 | 0.00055502
| 10218050 | ART023 | ART | 16146780 | 16146776 | 2.008 | 143.1074 | -37.156 | 111 | 98.5 | 6.3% | 8.8% | 117.993 | 104.7055 | 0.01 | 0.02 | -1328.75 | 131.2805 | 1.526% | 119.103 | 107.168 | 0.01 | 0.02 | -1193.5 | 131.038 | 1.679% | 152.6% | 0.972% | 0.9899% | 1.008% | 1.026% | 1.044% | 1.061% | 1.079% | 1.097% | 1.115% | 1.133% | 1.151% | 1.169% | 1.187% | 1.205% | 1.223% | 1.24% | 1.258% | 1.276% | 1.294% | 1.312% | 0.00039363 | 0.00040088 | 0.00040813 | 0.00041537 | 0.00042262 | 0.00042987 | 0.00043712 | 0.00044437 | 0.00045162 | 0.00045887 | 0.00046611 | 0.00047336 | 0.00048061 | 0.00048786 | 0.00049511 | 0.00050236 | 0.00050961 | 0.00051686 | 0.0005241 | 0.00053135
| 10219401 | MRO008 | MRO | 16152893 | 16152903 | 1.7234 | 143.4142 | -37.1565 | 120 | 107 | 6.3% | 8.8% | 127.56 | 113.741 | 0.01 | 0.02 | -1381.9 | 141.379 | 1.547% | 128.76 | 116.416 | 0.01 | 0.02 | -1234.4 | 141.104 | 1.71% | 154.7% | 0.9741% | 0.9927% | 1.011% | 1.03% | 1.049% | 1.067% | 1.086% | 1.104% | 1.123% | 1.142% | 1.16% | 1.179% | 1.197% | 1.216% | 1.235% | 1.253% | 1.272% | 1.29% | 1.309% | 1.328% | 0.00039449 | 0.00040202 | 0.00040956 | 0.00041709 | 0.00042463 | 0.00043216 | 0.0004397 | 0.00044723 | 0.00045477 | 0.0004623 | 0.00046984 | 0.00047737 | 0.00048491 | 0.00049244 | 0.00049998 | 0.00050751 | 0.00051505 | 0.00052258 | 0.00053012 | 0.00053765
| 10224712 | KYM001 | KYM | 16178998 | 16179043 | 1.4566 | 144.8318 | -36.4008 | 108 | 96.2 | 6.3% | 8.8% | 114.804 | 102.2606 | 0.01 | 0.02 | -1254.34 | 127.3474 | 1.542% | 115.884 | 104.6656 | 0.01 | 0.02 | -1121.84 | 127.1024 | 1.703% | 154.2% | 0.9736% | 0.9921% | 1.011% | 1.029% | 1.047% | 1.066% | 1.084% | 1.103% | 1.121% | 1.14% | 1.158% | 1.177% | 1.195% | 1.213% | 1.232% | 1.25% | 1.269% | 1.287% | 1.306% | 1.324% | 0.0003943 | 0.00040177 | 0.00040924 | 0.00041671 | 0.00042418 | 0.00043165 | 0.00043912 | 0.00044659 | 0.00045406 | 0.00046154 | 0.00046901 | 0.00047648 | 0.00048395 | 0.00049142 | 0.00049889 | 0.00050636 | 0.00051383 | 0.00052131 | 0.00052878 | 0.00053625
| 10224713 | KYM001 | KYM | 16179002 | 203298942 | 1.3384 | 144.8285 | -36.399 | 108 | 96 | 6.3% | 8.8% | 114.804 | 102.048 | 0.01 | 0.02 | -1275.6 | 127.56 | 1.533% | 115.884 | 104.448 | 0.01 | 0.02 | -1143.6 | 127.32 | 1.689% | 153.3% | 0.9727% | 0.9908% | 1.009% | 1.027% | 1.045% | 1.063% | 1.082% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.19% | 1.209% | 1.227% | 1.245% | 1.263% | 1.281% | 1.299% | 1.317% | 0.00039392 | 0.00040127 | 0.00040861 | 0.00041596 | 0.00042331 | 0.00043065 | 0.000438 | 0.00044535 | 0.0004527 | 0.00046004 | 0.00046739 | 0.00047474 | 0.00048208 | 0.00048943 | 0.00049678 | 0.00050412 | 0.00051147 | 0.00051882 | 0.00052616 | 0.00053351
| 10224837 | ECA007 | ECA | 42237248 | 200550261 | 0.18771 | 144.6385 | -36.4854 | 106 | 94.9 | 6.3% | 8.8% | 112.678 | 100.8787 | 0.01 | 0.02 | -1179.93 | 124.4773 | 1.566% | 113.738 | 103.2512 | 0.01 | 0.02 | -1048.68 | 124.2248 | 1.738% | 156.6% | 0.976% | 0.9953% | 1.015% | 1.034% | 1.053% | 1.072% | 1.092% | 1.111% | 1.13% | 1.149% | 1.169% | 1.188% | 1.207% | 1.226% | 1.245% | 1.265% | 1.284% | 1.303% | 1.322% | 1.342% | 0.00039527 | 0.00040306 | 0.00041086 | 0.00041865 | 0.00042645 | 0.00043424 | 0.00044204 | 0.00044983 | 0.00045763 | 0.00046542 | 0.00047322 | 0.00048102 | 0.00048881 | 0.00049661 | 0.0005044 | 0.0005122 | 0.00051999 | 0.00052779 | 0.00053558 | 0.00054338
| 10224838 | ECA007 | ECA | 200550261 | 16179827 | 0.70951 | 144.6396 | -36.4834 | 106 | 94.9 | 6.3% | 8.8% | 112.678 | 100.8787 | 0.01 | 0.02 | -1179.93 | 124.4773 | 1.566% | 113.738 | 103.2512 | 0.01 | 0.02 | -1048.68 | 124.2248 | 1.738% | 156.6% | 0.976% | 0.9953% | 1.015% | 1.034% | 1.053% | 1.072% | 1.092% | 1.111% | 1.13% | 1.149% | 1.169% | 1.188% | 1.207% | 1.226% | 1.245% | 1.265% | 1.284% | 1.303% | 1.322% | 1.342% | 0.00039527 | 0.00040306 | 0.00041086 | 0.00041865 | 0.00042645 | 0.00043424 | 0.00044204 | 0.00044983 | 0.00045763 | 0.00046542 | 0.00047322 | 0.00048102 | 0.00048881 | 0.00049661 | 0.0005044 | 0.0005122 | 0.00051999 | 0.00052779 | 0.00053558 | 0.00054338
| 10224869 | ECA007 | ECA | 16179889 | 17666097 | 0.24748 | 144.6538 | -36.4733 | 106 | 95.1 | 6.3% | 8.8% | 112.678 | 101.0913 | 0.01 | 0.02 | -1158.67 | 124.2647 | 1.576% | 113.738 | 103.4688 | 0.01 | 0.02 | -1026.92 | 124.0072 | 1.754% | 157.6% | 0.9771% | 0.9967% | 1.016% | 1.036% | 1.055% | 1.075% | 1.095% | 1.114% | 1.134% | 1.153% | 1.173% | 1.193% | 1.212% | 1.232% | 1.252% | 1.271% | 1.291% | 1.31% | 1.33% | 1.35% | 0.0003957 | 0.00040363 | 0.00041157 | 0.00041951 | 0.00042745 | 0.00043539 | 0.00044333 | 0.00045126 | 0.0004592 | 0.00046714 | 0.00047508 | 0.00048302 | 0.00049096 | 0.00049889 | 0.00050683 | 0.00051477 | 0.00052271 | 0.00053065 | 0.00053859 | 0.00054652
| 10224870 | ECA007 | ECA | 16179894 | 16180329 | 1.6213 | 144.652 | -36.4742 | 106 | 95.1 | 6.3% | 8.8% | 112.678 | 101.0913 | 0.01 | 0.02 | -1158.67 | 124.2647 | 1.576% | 113.738 | 103.4688 | 0.01 | 0.02 | -1026.92 | 124.0072 | 1.754% | 157.6% | 0.9771% | 0.9967% | 1.016% | 1.036% | 1.055% | 1.075% | 1.095% | 1.114% | 1.134% | 1.153% | 1.173% | 1.193% | 1.212% | 1.232% | 1.252% | 1.271% | 1.291% | 1.31% | 1.33% | 1.35% | 0.0003957 | 0.00040363 | 0.00041157 | 0.00041951 | 0.00042745 | 0.00043539 | 0.00044333 | 0.00045126 | 0.0004592 | 0.00046714 | 0.00047508 | 0.00048302 | 0.00049096 | 0.00049889 | 0.00050683 | 0.00051477 | 0.00052271 | 0.00053065 | 0.00053859 | 0.00054652
| 10225122 | ECA007 | ECA | 16180942 | 16180937 | 0.84353 | 144.6712 | -36.459 | 106 | 95.1 | 6.3% | 8.8% | 112.678 | 101.0913 | 0.01 | 0.02 | -1158.67 | 124.2647 | 1.576% | 113.738 | 103.4688 | 0.01 | 0.02 | -1026.92 | 124.0072 | 1.754% | 157.6% | 0.9771% | 0.9967% | 1.016% | 1.036% | 1.055% | 1.075% | 1.095% | 1.114% | 1.134% | 1.153% | 1.173% | 1.193% | 1.212% | 1.232% | 1.252% | 1.271% | 1.291% | 1.31% | 1.33% | 1.35% | 0.0003957 | 0.00040363 | 0.00041157 | 0.00041951 | 0.00042745 | 0.00043539 | 0.00044333 | 0.00045126 | 0.0004592 | 0.00046714 | 0.00047508 | 0.00048302 | 0.00049096 | 0.00049889 | 0.00050683 | 0.00051477 | 0.00052271 | 0.00053065 | 0.00053859 | 0.00054652
| 10225129 | ECA007 | ECA | 16180965 | 16181123 | 1.1427 | 144.6736 | -36.4553 | 106 | 95.1 | 6.3% | 8.8% | 112.678 | 101.0913 | 0.01 | 0.02 | -1158.67 | 124.2647 | 1.576% | 113.738 | 103.4688 | 0.01 | 0.02 | -1026.92 | 124.0072 | 1.754% | 157.6% | 0.9771% | 0.9967% | 1.016% | 1.036% | 1.055% | 1.075% | 1.095% | 1.114% | 1.134% | 1.153% | 1.173% | 1.193% | 1.212% | 1.232% | 1.252% | 1.271% | 1.291% | 1.31% | 1.33% | 1.35% | 0.0003957 | 0.00040363 | 0.00041157 | 0.00041951 | 0.00042745 | 0.00043539 | 0.00044333 | 0.00045126 | 0.0004592 | 0.00046714 | 0.00047508 | 0.00048302 | 0.00049096 | 0.00049889 | 0.00050683 | 0.00051477 | 0.00052271 | 0.00053065 | 0.00053859 | 0.00054652
| 10225165 | ECA007 | ECA | 16181113 | 16181198 | 1.6398 | 144.6649 | -36.461 | 106 | 95.1 | 6.3% | 8.8% | 112.678 | 101.0913 | 0.01 | 0.02 | -1158.67 | 124.2647 | 1.576% | 113.738 | 103.4688 | 0.01 | 0.02 | -1026.92 | 124.0072 | 1.754% | 157.6% | 0.9771% | 0.9967% | 1.016% | 1.036% | 1.055% | 1.075% | 1.095% | 1.114% | 1.134% | 1.153% | 1.173% | 1.193% | 1.212% | 1.232% | 1.252% | 1.271% | 1.291% | 1.31% | 1.33% | 1.35% | 0.0003957 | 0.00040363 | 0.00041157 | 0.00041951 | 0.00042745 | 0.00043539 | 0.00044333 | 0.00045126 | 0.0004592 | 0.00046714 | 0.00047508 | 0.00048302 | 0.00049096 | 0.00049889 | 0.00050683 | 0.00051477 | 0.00052271 | 0.00053065 | 0.00053859 | 0.00054652
| 10228259 | STN024 | STN | 17110265 | 16194445 | 1.1484 | 145.5889 | -36.3663 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10229034 | NHL015 | NHL | 16198449 | 16198445 | 0.21748 | 141.9898 | -36.4186 | 128 | 108 | 6.3% | 8.8% | 136.064 | 114.804 | 0.01 | 0.02 | -2126 | 157.324 | 1.379% | 137.344 | 117.504 | 0.01 | 0.02 | -1984 | 157.184 | 1.471% | 137.9% | 0.957% | 0.9699% | 0.9828% | 0.9957% | 1.009% | 1.021% | 1.034% | 1.047% | 1.06% | 1.073% | 1.086% | 1.099% | 1.112% | 1.125% | 1.138% | 1.15% | 1.163% | 1.176% | 1.189% | 1.202% | 0.00038755 | 0.00039278 | 0.000398 | 0.00040323 | 0.00040845 | 0.00041368 | 0.0004189 | 0.00042412 | 0.00042935 | 0.00043457 | 0.0004398 | 0.00044502 | 0.00045025 | 0.00045547 | 0.00046069 | 0.00046592 | 0.00047114 | 0.00047637 | 0.00048159 | 0.00048682
| 10229043 | NHL015 | NHL | 16198489 | 16198481 | 1.1104 | 141.9842 | -36.4185 | 128 | 108 | 6.3% | 8.8% | 136.064 | 114.804 | 0.01 | 0.02 | -2126 | 157.324 | 1.379% | 137.344 | 117.504 | 0.01 | 0.02 | -1984 | 157.184 | 1.471% | 137.9% | 0.957% | 0.9699% | 0.9828% | 0.9957% | 1.009% | 1.021% | 1.034% | 1.047% | 1.06% | 1.073% | 1.086% | 1.099% | 1.112% | 1.125% | 1.138% | 1.15% | 1.163% | 1.176% | 1.189% | 1.202% | 0.00038755 | 0.00039278 | 0.000398 | 0.00040323 | 0.00040845 | 0.00041368 | 0.0004189 | 0.00042412 | 0.00042935 | 0.00043457 | 0.0004398 | 0.00044502 | 0.00045025 | 0.00045547 | 0.00046069 | 0.00046592 | 0.00047114 | 0.00047637 | 0.00048159 | 0.00048682
| 10229105 | NHL015 | NHL | 16198772 | 17656329 | 0.4562 | 141.9755 | -36.4159 | 128 | 108 | 6.3% | 8.8% | 136.064 | 114.804 | 0.01 | 0.02 | -2126 | 157.324 | 1.379% | 137.344 | 117.504 | 0.01 | 0.02 | -1984 | 157.184 | 1.471% | 137.9% | 0.957% | 0.9699% | 0.9828% | 0.9957% | 1.009% | 1.021% | 1.034% | 1.047% | 1.06% | 1.073% | 1.086% | 1.099% | 1.112% | 1.125% | 1.138% | 1.15% | 1.163% | 1.176% | 1.189% | 1.202% | 0.00038755 | 0.00039278 | 0.000398 | 0.00040323 | 0.00040845 | 0.00041368 | 0.0004189 | 0.00042412 | 0.00042935 | 0.00043457 | 0.0004398 | 0.00044502 | 0.00045025 | 0.00045547 | 0.00046069 | 0.00046592 | 0.00047114 | 0.00047637 | 0.00048159 | 0.00048682
| 10229268 | KYM004 | KYM | 16206861 | 16199482 | 0.21124 | 145.0319 | -36.304 | 108 | 95.8 | 6.3% | 8.8% | 114.804 | 101.8354 | 0.01 | 0.02 | -1296.86 | 127.7726 | 1.525% | 115.884 | 104.2304 | 0.01 | 0.02 | -1165.36 | 127.5376 | 1.677% | 152.5% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.115% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.222% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039356 | 0.00040079 | 0.00040801 | 0.00041524 | 0.00042247 | 0.00042969 | 0.00043692 | 0.00044414 | 0.00045137 | 0.0004586 | 0.00046582 | 0.00047305 | 0.00048028 | 0.0004875 | 0.00049473 | 0.00050195 | 0.00050918 | 0.00051641 | 0.00052363 | 0.00053086
| 10229636 | KYM004 | KYM | 16200932 | 200798882 | 1.1397 | 145.0325 | -36.286 | 108 | 95.6 | 6.3% | 8.8% | 114.804 | 101.6228 | 0.01 | 0.02 | -1318.12 | 127.9852 | 1.516% | 115.884 | 104.0128 | 0.01 | 0.02 | -1187.12 | 127.7552 | 1.664% | 151.6% | 0.9709% | 0.9885% | 1.006% | 1.024% | 1.041% | 1.059% | 1.076% | 1.094% | 1.111% | 1.129% | 1.146% | 1.164% | 1.182% | 1.199% | 1.217% | 1.234% | 1.252% | 1.269% | 1.287% | 1.304% | 0.00039321 | 0.00040032 | 0.00040743 | 0.00041454 | 0.00042165 | 0.00042876 | 0.00043587 | 0.00044298 | 0.00045009 | 0.0004572 | 0.00046431 | 0.00047142 | 0.00047853 | 0.00048564 | 0.00049275 | 0.00049986 | 0.00050697 | 0.00051408 | 0.00052118 | 0.00052829
| 10229638 | KYM004 | KYM | 200798889 | 200798894 | 1.0083 | 145.0337 | -36.2863 | 108 | 95.6 | 6.3% | 8.8% | 114.804 | 101.6228 | 0.01 | 0.02 | -1318.12 | 127.9852 | 1.516% | 115.884 | 104.0128 | 0.01 | 0.02 | -1187.12 | 127.7552 | 1.664% | 151.6% | 0.9709% | 0.9885% | 1.006% | 1.024% | 1.041% | 1.059% | 1.076% | 1.094% | 1.111% | 1.129% | 1.146% | 1.164% | 1.182% | 1.199% | 1.217% | 1.234% | 1.252% | 1.269% | 1.287% | 1.304% | 0.00039321 | 0.00040032 | 0.00040743 | 0.00041454 | 0.00042165 | 0.00042876 | 0.00043587 | 0.00044298 | 0.00045009 | 0.0004572 | 0.00046431 | 0.00047142 | 0.00047853 | 0.00048564 | 0.00049275 | 0.00049986 | 0.00050697 | 0.00051408 | 0.00052118 | 0.00052829
| 10229671 | KYM006 | KYM | 16201084 | 16201080 | 0.41269 | 145.0057 | -36.2811 | 108 | 95.3 | 6.3% | 8.8% | 114.804 | 101.3039 | 0.01 | 0.02 | -1350.01 | 128.3041 | 1.504% | 115.884 | 103.6864 | 0.01 | 0.02 | -1219.76 | 128.0816 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.073% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.193% | 1.21% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039271 | 0.00039965 | 0.00040659 | 0.00041353 | 0.00042047 | 0.00042742 | 0.00043436 | 0.0004413 | 0.00044824 | 0.00045518 | 0.00046212 | 0.00046907 | 0.00047601 | 0.00048295 | 0.00048989 | 0.00049683 | 0.00050377 | 0.00051072 | 0.00051766 | 0.0005246
| 10229688 | KYM006 | KYM | 16201154 | 16201159 | 1.871 | 145.0021 | -36.2922 | 108 | 95.3 | 6.3% | 8.8% | 114.804 | 101.3039 | 0.01 | 0.02 | -1350.01 | 128.3041 | 1.504% | 115.884 | 103.6864 | 0.01 | 0.02 | -1219.76 | 128.0816 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.073% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.193% | 1.21% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039271 | 0.00039965 | 0.00040659 | 0.00041353 | 0.00042047 | 0.00042742 | 0.00043436 | 0.0004413 | 0.00044824 | 0.00045518 | 0.00046212 | 0.00046907 | 0.00047601 | 0.00048295 | 0.00048989 | 0.00049683 | 0.00050377 | 0.00051072 | 0.00051766 | 0.0005246
| 10229690 | KYM006 | KYM | 16201163 | 16201159 | 1.136 | 145.0035 | -36.2927 | 108 | 95.3 | 6.3% | 8.8% | 114.804 | 101.3039 | 0.01 | 0.02 | -1350.01 | 128.3041 | 1.504% | 115.884 | 103.6864 | 0.01 | 0.02 | -1219.76 | 128.0816 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.073% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.193% | 1.21% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039271 | 0.00039965 | 0.00040659 | 0.00041353 | 0.00042047 | 0.00042742 | 0.00043436 | 0.0004413 | 0.00044824 | 0.00045518 | 0.00046212 | 0.00046907 | 0.00047601 | 0.00048295 | 0.00048989 | 0.00049683 | 0.00050377 | 0.00051072 | 0.00051766 | 0.0005246
| 10229741 | KYM006 | KYM | 16201365 | 16201361 | 0.43374 | 145.0007 | -36.2842 | 108 | 95.3 | 6.3% | 8.8% | 114.804 | 101.3039 | 0.01 | 0.02 | -1350.01 | 128.3041 | 1.504% | 115.884 | 103.6864 | 0.01 | 0.02 | -1219.76 | 128.0816 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.073% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.193% | 1.21% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039271 | 0.00039965 | 0.00040659 | 0.00041353 | 0.00042047 | 0.00042742 | 0.00043436 | 0.0004413 | 0.00044824 | 0.00045518 | 0.00046212 | 0.00046907 | 0.00047601 | 0.00048295 | 0.00048989 | 0.00049683 | 0.00050377 | 0.00051072 | 0.00051766 | 0.0005246
| 10229744 | KYM006 | KYM | 16201373 | 41022367 | 0.68092 | 144.9972 | -36.2842 | 107 | 95 | 6.3% | 8.8% | 113.741 | 100.985 | 0.01 | 0.02 | -1275.6 | 126.497 | 1.528% | 114.811 | 103.36 | 0.01 | 0.02 | -1145.1 | 126.262 | 1.682% | 152.8% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039372 | 0.000401 | 0.00040827 | 0.00041555 | 0.00042283 | 0.00043011 | 0.00043739 | 0.00044467 | 0.00045195 | 0.00045923 | 0.0004665 | 0.00047378 | 0.00048106 | 0.00048834 | 0.00049562 | 0.0005029 | 0.00051018 | 0.00051745 | 0.00052473 | 0.00053201
| 10229786 | KYM004 | KYM | 63617487 | 16201538 | 1.3946 | 145.0311 | -36.262 | 108 | 95.3 | 6.3% | 8.8% | 114.804 | 101.3039 | 0.01 | 0.02 | -1350.01 | 128.3041 | 1.504% | 115.884 | 103.6864 | 0.01 | 0.02 | -1219.76 | 128.0816 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.073% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.193% | 1.21% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039271 | 0.00039965 | 0.00040659 | 0.00041353 | 0.00042047 | 0.00042742 | 0.00043436 | 0.0004413 | 0.00044824 | 0.00045518 | 0.00046212 | 0.00046907 | 0.00047601 | 0.00048295 | 0.00048989 | 0.00049683 | 0.00050377 | 0.00051072 | 0.00051766 | 0.0005246
| 10229796 | KYM004 | KYM | 16201570 | 17723454 | 0.90155 | 145.0286 | -36.2554 | 108 | 95.3 | 6.3% | 8.8% | 114.804 | 101.3039 | 0.01 | 0.02 | -1350.01 | 128.3041 | 1.504% | 115.884 | 103.6864 | 0.01 | 0.02 | -1219.76 | 128.0816 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.073% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.193% | 1.21% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039271 | 0.00039965 | 0.00040659 | 0.00041353 | 0.00042047 | 0.00042742 | 0.00043436 | 0.0004413 | 0.00044824 | 0.00045518 | 0.00046212 | 0.00046907 | 0.00047601 | 0.00048295 | 0.00048989 | 0.00049683 | 0.00050377 | 0.00051072 | 0.00051766 | 0.0005246
| 10229864 | KYM004 | KYM | 16201841 | 16349094 | 0.33111 | 145.109 | -36.2695 | 109 | 96.4 | 6.3% | 8.8% | 115.867 | 102.4732 | 0.01 | 0.02 | -1339.38 | 129.2608 | 1.513% | 116.957 | 104.8832 | 0.01 | 0.02 | -1207.38 | 129.0308 | 1.659% | 151.3% | 0.9706% | 0.988% | 1.005% | 1.023% | 1.04% | 1.058% | 1.075% | 1.093% | 1.11% | 1.128% | 1.145% | 1.162% | 1.18% | 1.197% | 1.215% | 1.232% | 1.25% | 1.267% | 1.284% | 1.302% | 0.00039307 | 0.00040013 | 0.00040719 | 0.00041425 | 0.00042131 | 0.00042837 | 0.00043544 | 0.0004425 | 0.00044956 | 0.00045662 | 0.00046368 | 0.00047074 | 0.00047781 | 0.00048487 | 0.00049193 | 0.00049899 | 0.00050605 | 0.00051311 | 0.00052018 | 0.00052724
| 10229887 | KYM004 | KYM | 16201941 | 16201946 | 0.80311 | 145.0518 | -36.2547 | 108 | 95.6 | 6.3% | 8.8% | 114.804 | 101.6228 | 0.01 | 0.02 | -1318.12 | 127.9852 | 1.516% | 115.884 | 104.0128 | 0.01 | 0.02 | -1187.12 | 127.7552 | 1.664% | 151.6% | 0.9709% | 0.9885% | 1.006% | 1.024% | 1.041% | 1.059% | 1.076% | 1.094% | 1.111% | 1.129% | 1.146% | 1.164% | 1.182% | 1.199% | 1.217% | 1.234% | 1.252% | 1.269% | 1.287% | 1.304% | 0.00039321 | 0.00040032 | 0.00040743 | 0.00041454 | 0.00042165 | 0.00042876 | 0.00043587 | 0.00044298 | 0.00045009 | 0.0004572 | 0.00046431 | 0.00047142 | 0.00047853 | 0.00048564 | 0.00049275 | 0.00049986 | 0.00050697 | 0.00051408 | 0.00052118 | 0.00052829
| 10229924 | KYM004 | KYM | 16202115 | 16202110 | 0.14911 | 145.0481 | -36.284 | 108 | 95.6 | 6.3% | 8.8% | 114.804 | 101.6228 | 0.01 | 0.02 | -1318.12 | 127.9852 | 1.516% | 115.884 | 104.0128 | 0.01 | 0.02 | -1187.12 | 127.7552 | 1.664% | 151.6% | 0.9709% | 0.9885% | 1.006% | 1.024% | 1.041% | 1.059% | 1.076% | 1.094% | 1.111% | 1.129% | 1.146% | 1.164% | 1.182% | 1.199% | 1.217% | 1.234% | 1.252% | 1.269% | 1.287% | 1.304% | 0.00039321 | 0.00040032 | 0.00040743 | 0.00041454 | 0.00042165 | 0.00042876 | 0.00043587 | 0.00044298 | 0.00045009 | 0.0004572 | 0.00046431 | 0.00047142 | 0.00047853 | 0.00048564 | 0.00049275 | 0.00049986 | 0.00050697 | 0.00051408 | 0.00052118 | 0.00052829
| 10229929 | KYM004 | KYM | 16202123 | 16202132 | 0.55574 | 145.0409 | -36.2835 | 108 | 95.6 | 6.3% | 8.8% | 114.804 | 101.6228 | 0.01 | 0.02 | -1318.12 | 127.9852 | 1.516% | 115.884 | 104.0128 | 0.01 | 0.02 | -1187.12 | 127.7552 | 1.664% | 151.6% | 0.9709% | 0.9885% | 1.006% | 1.024% | 1.041% | 1.059% | 1.076% | 1.094% | 1.111% | 1.129% | 1.146% | 1.164% | 1.182% | 1.199% | 1.217% | 1.234% | 1.252% | 1.269% | 1.287% | 1.304% | 0.00039321 | 0.00040032 | 0.00040743 | 0.00041454 | 0.00042165 | 0.00042876 | 0.00043587 | 0.00044298 | 0.00045009 | 0.0004572 | 0.00046431 | 0.00047142 | 0.00047853 | 0.00048564 | 0.00049275 | 0.00049986 | 0.00050697 | 0.00051408 | 0.00052118 | 0.00052829
| 10229934 | KYM004 | KYM | 16202140 | 16202144 | 0.25149 | 145.0409 | -36.2797 | 108 | 95.6 | 6.3% | 8.8% | 114.804 | 101.6228 | 0.01 | 0.02 | -1318.12 | 127.9852 | 1.516% | 115.884 | 104.0128 | 0.01 | 0.02 | -1187.12 | 127.7552 | 1.664% | 151.6% | 0.9709% | 0.9885% | 1.006% | 1.024% | 1.041% | 1.059% | 1.076% | 1.094% | 1.111% | 1.129% | 1.146% | 1.164% | 1.182% | 1.199% | 1.217% | 1.234% | 1.252% | 1.269% | 1.287% | 1.304% | 0.00039321 | 0.00040032 | 0.00040743 | 0.00041454 | 0.00042165 | 0.00042876 | 0.00043587 | 0.00044298 | 0.00045009 | 0.0004572 | 0.00046431 | 0.00047142 | 0.00047853 | 0.00048564 | 0.00049275 | 0.00049986 | 0.00050697 | 0.00051408 | 0.00052118 | 0.00052829
| 10229935 | KYM004 | KYM | 16202144 | 16202148 | 0.22783 | 145.0409 | -36.2785 | 108 | 95.6 | 6.3% | 8.8% | 114.804 | 101.6228 | 0.01 | 0.02 | -1318.12 | 127.9852 | 1.516% | 115.884 | 104.0128 | 0.01 | 0.02 | -1187.12 | 127.7552 | 1.664% | 151.6% | 0.9709% | 0.9885% | 1.006% | 1.024% | 1.041% | 1.059% | 1.076% | 1.094% | 1.111% | 1.129% | 1.146% | 1.164% | 1.182% | 1.199% | 1.217% | 1.234% | 1.252% | 1.269% | 1.287% | 1.304% | 0.00039321 | 0.00040032 | 0.00040743 | 0.00041454 | 0.00042165 | 0.00042876 | 0.00043587 | 0.00044298 | 0.00045009 | 0.0004572 | 0.00046431 | 0.00047142 | 0.00047853 | 0.00048564 | 0.00049275 | 0.00049986 | 0.00050697 | 0.00051408 | 0.00052118 | 0.00052829
| 10229987 | KYM004 | KYM | 16202387 | 16202391 | 0.18836 | 145.0497 | -36.2565 | 108 | 95.3 | 6.3% | 8.8% | 114.804 | 101.3039 | 0.01 | 0.02 | -1350.01 | 128.3041 | 1.504% | 115.884 | 103.6864 | 0.01 | 0.02 | -1219.76 | 128.0816 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.073% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.193% | 1.21% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039271 | 0.00039965 | 0.00040659 | 0.00041353 | 0.00042047 | 0.00042742 | 0.00043436 | 0.0004413 | 0.00044824 | 0.00045518 | 0.00046212 | 0.00046907 | 0.00047601 | 0.00048295 | 0.00048989 | 0.00049683 | 0.00050377 | 0.00051072 | 0.00051766 | 0.0005246
| 10230057 | NHL015 | NHL | 16202692 | 16202688 | 0.38871 | 142.01 | -36.3974 | 128 | 108 | 6.3% | 8.8% | 136.064 | 114.804 | 0.01 | 0.02 | -2126 | 157.324 | 1.379% | 137.344 | 117.504 | 0.01 | 0.02 | -1984 | 157.184 | 1.471% | 137.9% | 0.957% | 0.9699% | 0.9828% | 0.9957% | 1.009% | 1.021% | 1.034% | 1.047% | 1.06% | 1.073% | 1.086% | 1.099% | 1.112% | 1.125% | 1.138% | 1.15% | 1.163% | 1.176% | 1.189% | 1.202% | 0.00038755 | 0.00039278 | 0.000398 | 0.00040323 | 0.00040845 | 0.00041368 | 0.0004189 | 0.00042412 | 0.00042935 | 0.00043457 | 0.0004398 | 0.00044502 | 0.00045025 | 0.00045547 | 0.00046069 | 0.00046592 | 0.00047114 | 0.00047637 | 0.00048159 | 0.00048682
| 10230058 | NHL015 | NHL | 16202696 | 16202692 | 1.3131 | 142.0128 | -36.3974 | 128 | 108 | 6.3% | 8.8% | 136.064 | 114.804 | 0.01 | 0.02 | -2126 | 157.324 | 1.379% | 137.344 | 117.504 | 0.01 | 0.02 | -1984 | 157.184 | 1.471% | 137.9% | 0.957% | 0.9699% | 0.9828% | 0.9957% | 1.009% | 1.021% | 1.034% | 1.047% | 1.06% | 1.073% | 1.086% | 1.099% | 1.112% | 1.125% | 1.138% | 1.15% | 1.163% | 1.176% | 1.189% | 1.202% | 0.00038755 | 0.00039278 | 0.000398 | 0.00040323 | 0.00040845 | 0.00041368 | 0.0004189 | 0.00042412 | 0.00042935 | 0.00043457 | 0.0004398 | 0.00044502 | 0.00045025 | 0.00045547 | 0.00046069 | 0.00046592 | 0.00047114 | 0.00047637 | 0.00048159 | 0.00048682
| 10230280 | KYM004 | KYM | 16203690 | 16203695 | 0.53933 | 145.0481 | -36.2467 | 107 | 94.9 | 6.3% | 8.8% | 113.741 | 100.8787 | 0.01 | 0.02 | -1286.23 | 126.6033 | 1.524% | 114.811 | 103.2512 | 0.01 | 0.02 | -1155.98 | 126.3708 | 1.676% | 152.4% | 0.9717% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.203% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.31% | 0.00039354 | 0.00040076 | 0.00040797 | 0.00041519 | 0.00042241 | 0.00042963 | 0.00043685 | 0.00044407 | 0.00045129 | 0.0004585 | 0.00046572 | 0.00047294 | 0.00048016 | 0.00048738 | 0.0004946 | 0.00050181 | 0.00050903 | 0.00051625 | 0.00052347 | 0.00053069
| 10231029 | KYM003 | KYM | 16206760 | 17582062 | 0.68329 | 145.0782 | -36.2747 | 109 | 96 | 6.3% | 8.8% | 115.867 | 102.048 | 0.01 | 0.02 | -1381.9 | 129.686 | 1.497% | 116.957 | 104.448 | 0.01 | 0.02 | -1250.9 | 129.466 | 1.636% | 149.7% | 0.969% | 0.9859% | 1.003% | 1.02% | 1.037% | 1.053% | 1.07% | 1.087% | 1.104% | 1.121% | 1.138% | 1.155% | 1.172% | 1.189% | 1.206% | 1.222% | 1.239% | 1.256% | 1.273% | 1.29% | 0.00039241 | 0.00039926 | 0.0004061 | 0.00041295 | 0.00041979 | 0.00042664 | 0.00043348 | 0.00044032 | 0.00044717 | 0.00045401 | 0.00046086 | 0.0004677 | 0.00047455 | 0.00048139 | 0.00048824 | 0.00049508 | 0.00050192 | 0.00050877 | 0.00051561 | 0.00052246
| 10231053 | KYM004 | KYM | 16206856 | 16206861 | 0.8809 | 145.0319 | -36.3048 | 108 | 95.8 | 6.3% | 8.8% | 114.804 | 101.8354 | 0.01 | 0.02 | -1296.86 | 127.7726 | 1.525% | 115.884 | 104.2304 | 0.01 | 0.02 | -1165.36 | 127.5376 | 1.677% | 152.5% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.115% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.222% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039356 | 0.00040079 | 0.00040801 | 0.00041524 | 0.00042247 | 0.00042969 | 0.00043692 | 0.00044414 | 0.00045137 | 0.0004586 | 0.00046582 | 0.00047305 | 0.00048028 | 0.0004875 | 0.00049473 | 0.00050195 | 0.00050918 | 0.00051641 | 0.00052363 | 0.00053086
| 10231059 | KYM004 | KYM | 16206978 | 16206881 | 0.23778 | 145.0327 | -36.306 | 108 | 95.8 | 6.3% | 8.8% | 114.804 | 101.8354 | 0.01 | 0.02 | -1296.86 | 127.7726 | 1.525% | 115.884 | 104.2304 | 0.01 | 0.02 | -1165.36 | 127.5376 | 1.677% | 152.5% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.115% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.222% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039356 | 0.00040079 | 0.00040801 | 0.00041524 | 0.00042247 | 0.00042969 | 0.00043692 | 0.00044414 | 0.00045137 | 0.0004586 | 0.00046582 | 0.00047305 | 0.00048028 | 0.0004875 | 0.00049473 | 0.00050195 | 0.00050918 | 0.00051641 | 0.00052363 | 0.00053086
| 10231086 | KYM002 | KYM | 16207036 | 16207032 | 1.5438 | 145.0385 | -36.3075 | 108 | 95.8 | 6.3% | 8.8% | 114.804 | 101.8354 | 0.01 | 0.02 | -1296.86 | 127.7726 | 1.525% | 115.884 | 104.2304 | 0.01 | 0.02 | -1165.36 | 127.5376 | 1.677% | 152.5% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.115% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.222% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039356 | 0.00040079 | 0.00040801 | 0.00041524 | 0.00042247 | 0.00042969 | 0.00043692 | 0.00044414 | 0.00045137 | 0.0004586 | 0.00046582 | 0.00047305 | 0.00048028 | 0.0004875 | 0.00049473 | 0.00050195 | 0.00050918 | 0.00051641 | 0.00052363 | 0.00053086
| 10232140 | SHP014 | SHP | 16211311 | 16211316 | 1.9853 | 145.0586 | -36.4265 | 111 | 98.4 | 6.3% | 8.8% | 117.993 | 104.5992 | 0.01 | 0.02 | -1339.38 | 131.3868 | 1.522% | 119.103 | 107.0592 | 0.01 | 0.02 | -1204.38 | 131.1468 | 1.673% | 152.2% | 0.9715% | 0.9893% | 1.007% | 1.025% | 1.043% | 1.06% | 1.078% | 1.096% | 1.114% | 1.131% | 1.149% | 1.167% | 1.185% | 1.202% | 1.22% | 1.238% | 1.256% | 1.273% | 1.291% | 1.309% | 0.00039346 | 0.00040065 | 0.00040784 | 0.00041503 | 0.00042222 | 0.00042941 | 0.0004366 | 0.00044379 | 0.00045098 | 0.00045818 | 0.00046537 | 0.00047256 | 0.00047975 | 0.00048694 | 0.00049413 | 0.00050132 | 0.00050851 | 0.00051571 | 0.0005229 | 0.00053009
| 10232141 | SHP014 | SHP | 16211311 | 17686420 | 0.34196 | 145.0599 | -36.4274 | 111 | 98.4 | 6.3% | 8.8% | 117.993 | 104.5992 | 0.01 | 0.02 | -1339.38 | 131.3868 | 1.522% | 119.103 | 107.0592 | 0.01 | 0.02 | -1204.38 | 131.1468 | 1.673% | 152.2% | 0.9715% | 0.9893% | 1.007% | 1.025% | 1.043% | 1.06% | 1.078% | 1.096% | 1.114% | 1.131% | 1.149% | 1.167% | 1.185% | 1.202% | 1.22% | 1.238% | 1.256% | 1.273% | 1.291% | 1.309% | 0.00039346 | 0.00040065 | 0.00040784 | 0.00041503 | 0.00042222 | 0.00042941 | 0.0004366 | 0.00044379 | 0.00045098 | 0.00045818 | 0.00046537 | 0.00047256 | 0.00047975 | 0.00048694 | 0.00049413 | 0.00050132 | 0.00050851 | 0.00051571 | 0.0005229 | 0.00053009
| 10232159 | SHP011 | SHP | 16211386 | 16211391 | 1.3548 | 145.0145 | -36.4214 | 109 | 96.8 | 6.3% | 8.8% | 115.867 | 102.8984 | 0.01 | 0.02 | -1296.86 | 128.8356 | 1.53% | 116.957 | 105.3184 | 0.01 | 0.02 | -1163.86 | 128.5956 | 1.684% | 153% | 0.9723% | 0.9903% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039376 | 0.00040105 | 0.00040835 | 0.00041564 | 0.00042293 | 0.00043023 | 0.00043752 | 0.00044481 | 0.00045211 | 0.0004594 | 0.00046669 | 0.00047399 | 0.00048128 | 0.00048857 | 0.00049587 | 0.00050316 | 0.00051045 | 0.00051774 | 0.00052504 | 0.00053233
| 10232252 | SHP014 | SHP | 16211791 | 16211796 | 0.65992 | 145.0928 | -36.4697 | 113 | 99.5 | 6.3% | 8.8% | 120.119 | 105.7685 | 0.01 | 0.02 | -1435.05 | 134.4695 | 1.496% | 121.249 | 108.256 | 0.01 | 0.02 | -1299.3 | 134.242 | 1.635% | 149.6% | 0.9689% | 0.9858% | 1.003% | 1.02% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.121% | 1.138% | 1.154% | 1.171% | 1.188% | 1.205% | 1.222% | 1.239% | 1.256% | 1.273% | 1.289% | 0.00039238 | 0.00039921 | 0.00040605 | 0.00041288 | 0.00041971 | 0.00042654 | 0.00043338 | 0.00044021 | 0.00044704 | 0.00045387 | 0.00046071 | 0.00046754 | 0.00047437 | 0.0004812 | 0.00048804 | 0.00049487 | 0.0005017 | 0.00050854 | 0.00051537 | 0.0005222
| 10232276 | SHP014 | SHP | 16211892 | 187582390 | 0.26235 | 145.0369 | -36.47 | 112 | 98.9 | 6.3% | 8.8% | 119.056 | 105.1307 | 0.01 | 0.02 | -1392.53 | 132.9813 | 1.507% | 120.176 | 107.6032 | 0.01 | 0.02 | -1257.28 | 132.7488 | 1.65% | 150.7% | 0.97% | 0.9872% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.091% | 1.108% | 1.125% | 1.142% | 1.16% | 1.177% | 1.194% | 1.211% | 1.228% | 1.246% | 1.263% | 1.28% | 1.297% | 0.00039282 | 0.0003998 | 0.00040678 | 0.00041376 | 0.00042073 | 0.00042771 | 0.00043469 | 0.00044167 | 0.00044865 | 0.00045563 | 0.00046261 | 0.00046959 | 0.00047657 | 0.00048355 | 0.00049053 | 0.0004975 | 0.00050448 | 0.00051146 | 0.00051844 | 0.00052542
| 10232278 | SHP014 | SHP | 16211896 | 16212671 | 0.93795 | 145.0318 | -36.4689 | 112 | 98.9 | 6.3% | 8.8% | 119.056 | 105.1307 | 0.01 | 0.02 | -1392.53 | 132.9813 | 1.507% | 120.176 | 107.6032 | 0.01 | 0.02 | -1257.28 | 132.7488 | 1.65% | 150.7% | 0.97% | 0.9872% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.091% | 1.108% | 1.125% | 1.142% | 1.16% | 1.177% | 1.194% | 1.211% | 1.228% | 1.246% | 1.263% | 1.28% | 1.297% | 0.00039282 | 0.0003998 | 0.00040678 | 0.00041376 | 0.00042073 | 0.00042771 | 0.00043469 | 0.00044167 | 0.00044865 | 0.00045563 | 0.00046261 | 0.00046959 | 0.00047657 | 0.00048355 | 0.00049053 | 0.0004975 | 0.00050448 | 0.00051146 | 0.00051844 | 0.00052542
| 10232347 | SHP014 | SHP | 16212109 | 17772277 | 1.0841 | 145.1021 | -36.4825 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10232355 | SHP014 | SHP | 16212152 | 16212148 | 0.86032 | 145.0956 | -36.5015 | 116 | 102 | 6.3% | 8.8% | 123.308 | 108.426 | 0.01 | 0.02 | -1488.2 | 138.19 | 1.491% | 124.468 | 110.976 | 0.01 | 0.02 | -1349.2 | 137.96 | 1.628% | 149.1% | 0.9684% | 0.9851% | 1.002% | 1.018% | 1.035% | 1.052% | 1.069% | 1.085% | 1.102% | 1.119% | 1.135% | 1.152% | 1.169% | 1.185% | 1.202% | 1.219% | 1.236% | 1.252% | 1.269% | 1.286% | 0.00039217 | 0.00039894 | 0.0004057 | 0.00041246 | 0.00041923 | 0.00042599 | 0.00043275 | 0.00043952 | 0.00044628 | 0.00045304 | 0.00045981 | 0.00046657 | 0.00047334 | 0.0004801 | 0.00048686 | 0.00049363 | 0.00050039 | 0.00050715 | 0.00051392 | 0.00052068
| 10232383 | SHP014 | SHP | 16212246 | 188038927 | 1.6418 | 145.0227 | -36.4404 | 110 | 97.5 | 6.3% | 8.8% | 116.93 | 103.6425 | 0.01 | 0.02 | -1328.75 | 130.2175 | 1.522% | 118.03 | 106.08 | 0.01 | 0.02 | -1195 | 129.98 | 1.672% | 152.2% | 0.9715% | 0.9892% | 1.007% | 1.025% | 1.042% | 1.06% | 1.078% | 1.096% | 1.113% | 1.131% | 1.149% | 1.167% | 1.184% | 1.202% | 1.22% | 1.238% | 1.255% | 1.273% | 1.291% | 1.309% | 0.00039343 | 0.00040062 | 0.0004078 | 0.00041498 | 0.00042217 | 0.00042935 | 0.00043653 | 0.00044372 | 0.0004509 | 0.00045808 | 0.00046527 | 0.00047245 | 0.00047963 | 0.00048682 | 0.000494 | 0.00050118 | 0.00050837 | 0.00051555 | 0.00052273 | 0.00052992
| 10232388 | SHTSSHP | KYM | 17154049 | 16212263 | 0.67631 | 145.0952 | -36.433 | 112 | 98.7 | 6.3% | 8.8% | 119.056 | 104.9181 | 0.01 | 0.02 | -1413.79 | 133.1939 | 1.499% | 120.176 | 107.3856 | 0.01 | 0.02 | -1279.04 | 132.9664 | 1.639% | 149.9% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.0003925 | 0.00039938 | 0.00040625 | 0.00041313 | 0.00042 | 0.00042687 | 0.00043375 | 0.00044062 | 0.0004475 | 0.00045437 | 0.00046124 | 0.00046812 | 0.00047499 | 0.00048187 | 0.00048874 | 0.00049562 | 0.00050249 | 0.00050936 | 0.00051624 | 0.00052311
| 10232390 | SHP014 | SHP | 16212272 | 16212268 | 0.54224 | 145.0865 | -36.4349 | 112 | 98.7 | 6.3% | 8.8% | 119.056 | 104.9181 | 0.01 | 0.02 | -1413.79 | 133.1939 | 1.499% | 120.176 | 107.3856 | 0.01 | 0.02 | -1279.04 | 132.9664 | 1.639% | 149.9% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.0003925 | 0.00039938 | 0.00040625 | 0.00041313 | 0.00042 | 0.00042687 | 0.00043375 | 0.00044062 | 0.0004475 | 0.00045437 | 0.00046124 | 0.00046812 | 0.00047499 | 0.00048187 | 0.00048874 | 0.00049562 | 0.00050249 | 0.00050936 | 0.00051624 | 0.00052311
| 10232400 | SHP014 | SHP | 16212314 | 16212309 | 1.6712 | 145.0685 | -36.4771 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10232401 | SHP014 | SHP | 16212318 | 16212314 | 2.1902 | 145.0685 | -36.4747 | 112 | 99.2 | 6.3% | 8.8% | 119.056 | 105.4496 | 0.01 | 0.02 | -1360.64 | 132.6624 | 1.519% | 120.176 | 107.9296 | 0.01 | 0.02 | -1224.64 | 132.4224 | 1.668% | 151.9% | 0.9712% | 0.9888% | 1.006% | 1.024% | 1.042% | 1.059% | 1.077% | 1.095% | 1.112% | 1.13% | 1.148% | 1.165% | 1.183% | 1.2% | 1.218% | 1.236% | 1.253% | 1.271% | 1.289% | 1.306% | 0.00039331 | 0.00040045 | 0.00040759 | 0.00041474 | 0.00042188 | 0.00042902 | 0.00043616 | 0.00044331 | 0.00045045 | 0.00045759 | 0.00046474 | 0.00047188 | 0.00047902 | 0.00048616 | 0.00049331 | 0.00050045 | 0.00050759 | 0.00051473 | 0.00052188 | 0.00052902
| 10232488 | SHP014 | SHP | 16212663 | 16212658 | 1.1418 | 145.0319 | -36.4618 | 112 | 98.9 | 6.3% | 8.8% | 119.056 | 105.1307 | 0.01 | 0.02 | -1392.53 | 132.9813 | 1.507% | 120.176 | 107.6032 | 0.01 | 0.02 | -1257.28 | 132.7488 | 1.65% | 150.7% | 0.97% | 0.9872% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.091% | 1.108% | 1.125% | 1.142% | 1.16% | 1.177% | 1.194% | 1.211% | 1.228% | 1.246% | 1.263% | 1.28% | 1.297% | 0.00039282 | 0.0003998 | 0.00040678 | 0.00041376 | 0.00042073 | 0.00042771 | 0.00043469 | 0.00044167 | 0.00044865 | 0.00045563 | 0.00046261 | 0.00046959 | 0.00047657 | 0.00048355 | 0.00049053 | 0.0004975 | 0.00050448 | 0.00051146 | 0.00051844 | 0.00052542
| 10232489 | SHP014 | SHP | 16212658 | 16212937 | 0.57115 | 145.031 | -36.4604 | 112 | 98.9 | 6.3% | 8.8% | 119.056 | 105.1307 | 0.01 | 0.02 | -1392.53 | 132.9813 | 1.507% | 120.176 | 107.6032 | 0.01 | 0.02 | -1257.28 | 132.7488 | 1.65% | 150.7% | 0.97% | 0.9872% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.091% | 1.108% | 1.125% | 1.142% | 1.16% | 1.177% | 1.194% | 1.211% | 1.228% | 1.246% | 1.263% | 1.28% | 1.297% | 0.00039282 | 0.0003998 | 0.00040678 | 0.00041376 | 0.00042073 | 0.00042771 | 0.00043469 | 0.00044167 | 0.00044865 | 0.00045563 | 0.00046261 | 0.00046959 | 0.00047657 | 0.00048355 | 0.00049053 | 0.0004975 | 0.00050448 | 0.00051146 | 0.00051844 | 0.00052542
| 10232490 | SHP014 | SHP | 16212667 | 16212663 | 1.1488 | 145.0319 | -36.4645 | 112 | 98.9 | 6.3% | 8.8% | 119.056 | 105.1307 | 0.01 | 0.02 | -1392.53 | 132.9813 | 1.507% | 120.176 | 107.6032 | 0.01 | 0.02 | -1257.28 | 132.7488 | 1.65% | 150.7% | 0.97% | 0.9872% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.091% | 1.108% | 1.125% | 1.142% | 1.16% | 1.177% | 1.194% | 1.211% | 1.228% | 1.246% | 1.263% | 1.28% | 1.297% | 0.00039282 | 0.0003998 | 0.00040678 | 0.00041376 | 0.00042073 | 0.00042771 | 0.00043469 | 0.00044167 | 0.00044865 | 0.00045563 | 0.00046261 | 0.00046959 | 0.00047657 | 0.00048355 | 0.00049053 | 0.0004975 | 0.00050448 | 0.00051146 | 0.00051844 | 0.00052542
| 10232493 | SHP014 | SHP | 16212675 | 17529371 | 0.97324 | 145.0312 | -36.472 | 112 | 98.9 | 6.3% | 8.8% | 119.056 | 105.1307 | 0.01 | 0.02 | -1392.53 | 132.9813 | 1.507% | 120.176 | 107.6032 | 0.01 | 0.02 | -1257.28 | 132.7488 | 1.65% | 150.7% | 0.97% | 0.9872% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.091% | 1.108% | 1.125% | 1.142% | 1.16% | 1.177% | 1.194% | 1.211% | 1.228% | 1.246% | 1.263% | 1.28% | 1.297% | 0.00039282 | 0.0003998 | 0.00040678 | 0.00041376 | 0.00042073 | 0.00042771 | 0.00043469 | 0.00044167 | 0.00044865 | 0.00045563 | 0.00046261 | 0.00046959 | 0.00047657 | 0.00048355 | 0.00049053 | 0.0004975 | 0.00050448 | 0.00051146 | 0.00051844 | 0.00052542
| 10233610 | KYM006 | KYM | 16217428 | 17598255 | 0.95671 | 144.941 | -36.2955 | 106 | 94 | 6.3% | 8.8% | 112.678 | 99.922 | 0.01 | 0.02 | -1275.6 | 125.434 | 1.524% | 113.738 | 102.272 | 0.01 | 0.02 | -1146.6 | 125.204 | 1.675% | 152.4% | 0.9717% | 0.9895% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.096% | 1.114% | 1.132% | 1.15% | 1.168% | 1.185% | 1.203% | 1.221% | 1.239% | 1.257% | 1.274% | 1.292% | 1.31% | 0.00039351 | 0.00040072 | 0.00040793 | 0.00041515 | 0.00042236 | 0.00042957 | 0.00043678 | 0.00044399 | 0.0004512 | 0.00045841 | 0.00046562 | 0.00047283 | 0.00048004 | 0.00048725 | 0.00049446 | 0.00050167 | 0.00050888 | 0.00051609 | 0.0005233 | 0.00053052
| 10233711 | KYM001 | KYM | 16217882 | 16217877 | 1.7137 | 144.9777 | -36.3553 | 108 | 95.9 | 6.3% | 8.8% | 114.804 | 101.9417 | 0.01 | 0.02 | -1286.23 | 127.6663 | 1.529% | 115.884 | 104.3392 | 0.01 | 0.02 | -1154.48 | 127.4288 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039374 | 0.00040103 | 0.00040831 | 0.0004156 | 0.00042288 | 0.00043017 | 0.00043746 | 0.00044474 | 0.00045203 | 0.00045931 | 0.0004666 | 0.00047389 | 0.00048117 | 0.00048846 | 0.00049574 | 0.00050303 | 0.00051031 | 0.0005176 | 0.00052489 | 0.00053217
| 10233712 | KYM001 | KYM | 16217887 | 16217882 | 1.4313 | 144.9792 | -36.3553 | 108 | 95.9 | 6.3% | 8.8% | 114.804 | 101.9417 | 0.01 | 0.02 | -1286.23 | 127.6663 | 1.529% | 115.884 | 104.3392 | 0.01 | 0.02 | -1154.48 | 127.4288 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039374 | 0.00040103 | 0.00040831 | 0.0004156 | 0.00042288 | 0.00043017 | 0.00043746 | 0.00044474 | 0.00045203 | 0.00045931 | 0.0004666 | 0.00047389 | 0.00048117 | 0.00048846 | 0.00049574 | 0.00050303 | 0.00051031 | 0.0005176 | 0.00052489 | 0.00053217
| 10233713 | KYM001 | KYM | 178510194 | 16217887 | 1.0337 | 144.9807 | -36.3553 | 108 | 95.9 | 6.3% | 8.8% | 114.804 | 101.9417 | 0.01 | 0.02 | -1286.23 | 127.6663 | 1.529% | 115.884 | 104.3392 | 0.01 | 0.02 | -1154.48 | 127.4288 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039374 | 0.00040103 | 0.00040831 | 0.0004156 | 0.00042288 | 0.00043017 | 0.00043746 | 0.00044474 | 0.00045203 | 0.00045931 | 0.0004666 | 0.00047389 | 0.00048117 | 0.00048846 | 0.00049574 | 0.00050303 | 0.00051031 | 0.0005176 | 0.00052489 | 0.00053217
| 10233714 | KYM001 | KYM | 16217896 | 178510194 | 0.24967 | 144.9815 | -36.3551 | 108 | 95.9 | 6.3% | 8.8% | 114.804 | 101.9417 | 0.01 | 0.02 | -1286.23 | 127.6663 | 1.529% | 115.884 | 104.3392 | 0.01 | 0.02 | -1154.48 | 127.4288 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039374 | 0.00040103 | 0.00040831 | 0.0004156 | 0.00042288 | 0.00043017 | 0.00043746 | 0.00044474 | 0.00045203 | 0.00045931 | 0.0004666 | 0.00047389 | 0.00048117 | 0.00048846 | 0.00049574 | 0.00050303 | 0.00051031 | 0.0005176 | 0.00052489 | 0.00053217
| 10233715 | KYM001 | KYM | 16217896 | 16218147 | 2.4293 | 144.9815 | -36.3537 | 108 | 95.9 | 6.3% | 8.8% | 114.804 | 101.9417 | 0.01 | 0.02 | -1286.23 | 127.6663 | 1.529% | 115.884 | 104.3392 | 0.01 | 0.02 | -1154.48 | 127.4288 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039374 | 0.00040103 | 0.00040831 | 0.0004156 | 0.00042288 | 0.00043017 | 0.00043746 | 0.00044474 | 0.00045203 | 0.00045931 | 0.0004666 | 0.00047389 | 0.00048117 | 0.00048846 | 0.00049574 | 0.00050303 | 0.00051031 | 0.0005176 | 0.00052489 | 0.00053217
| 10233717 | KYM001 | KYM | 16217901 | 178510194 | 0.69954 | 144.9822 | -36.3553 | 108 | 95.9 | 6.3% | 8.8% | 114.804 | 101.9417 | 0.01 | 0.02 | -1286.23 | 127.6663 | 1.529% | 115.884 | 104.3392 | 0.01 | 0.02 | -1154.48 | 127.4288 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039374 | 0.00040103 | 0.00040831 | 0.0004156 | 0.00042288 | 0.00043017 | 0.00043746 | 0.00044474 | 0.00045203 | 0.00045931 | 0.0004666 | 0.00047389 | 0.00048117 | 0.00048846 | 0.00049574 | 0.00050303 | 0.00051031 | 0.0005176 | 0.00052489 | 0.00053217
| 10234489 | SHP011 | SHP | 192176367 | 111130653 | 0.11378 | 144.9845 | -36.4531 | 111 | 98 | 6.3% | 8.8% | 117.993 | 104.174 | 0.01 | 0.02 | -1381.9 | 131.812 | 1.506% | 119.103 | 106.624 | 0.01 | 0.02 | -1247.9 | 131.582 | 1.649% | 150.6% | 0.9699% | 0.9871% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.09% | 1.108% | 1.125% | 1.142% | 1.159% | 1.176% | 1.194% | 1.211% | 1.228% | 1.245% | 1.262% | 1.28% | 1.297% | 0.00039279 | 0.00039976 | 0.00040673 | 0.0004137 | 0.00042067 | 0.00042764 | 0.00043461 | 0.00044158 | 0.00044855 | 0.00045552 | 0.00046249 | 0.00046946 | 0.00047643 | 0.0004834 | 0.00049037 | 0.00049734 | 0.00050431 | 0.00051128 | 0.00051825 | 0.00052522
| 10240137 | MRO007 | MRO | 16246859 | 16246863 | 2.0027 | 143.6463 | -37.1418 | 115 | 103 | 6.3% | 8.8% | 122.245 | 109.489 | 0.01 | 0.02 | -1275.6 | 135.001 | 1.568% | 123.395 | 112.064 | 0.01 | 0.02 | -1133.1 | 134.726 | 1.741% | 156.8% | 0.9762% | 0.9955% | 1.015% | 1.034% | 1.053% | 1.073% | 1.092% | 1.111% | 1.131% | 1.15% | 1.169% | 1.189% | 1.208% | 1.227% | 1.247% | 1.266% | 1.285% | 1.305% | 1.324% | 1.343% | 0.00039535 | 0.00040317 | 0.000411 | 0.00041882 | 0.00042664 | 0.00043446 | 0.00044229 | 0.00045011 | 0.00045793 | 0.00046576 | 0.00047358 | 0.0004814 | 0.00048922 | 0.00049705 | 0.00050487 | 0.00051269 | 0.00052052 | 0.00052834 | 0.00053616 | 0.00054398
| 10240291 | MRO007 | MRO | 16247565 | 16247569 | 0.23647 | 143.748 | -37.1598 | 109 | 96.9 | 6.3% | 8.8% | 115.867 | 103.0047 | 0.01 | 0.02 | -1286.23 | 128.7293 | 1.534% | 116.957 | 105.4272 | 0.01 | 0.02 | -1152.98 | 128.4868 | 1.69% | 153.4% | 0.9727% | 0.9909% | 1.009% | 1.027% | 1.045% | 1.064% | 1.082% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.191% | 1.209% | 1.227% | 1.245% | 1.263% | 1.281% | 1.3% | 1.318% | 0.00039394 | 0.0004013 | 0.00040865 | 0.000416 | 0.00042336 | 0.00043071 | 0.00043806 | 0.00044542 | 0.00045277 | 0.00046012 | 0.00046748 | 0.00047483 | 0.00048218 | 0.00048954 | 0.00049689 | 0.00050424 | 0.0005116 | 0.00051895 | 0.0005263 | 0.00053366
| 10240307 | MRO007 | MRO | 16247633 | 16247642 | 0.45537 | 143.76 | -37.1495 | 108 | 95.9 | 6.3% | 8.8% | 114.804 | 101.9417 | 0.01 | 0.02 | -1286.23 | 127.6663 | 1.529% | 115.884 | 104.3392 | 0.01 | 0.02 | -1154.48 | 127.4288 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039374 | 0.00040103 | 0.00040831 | 0.0004156 | 0.00042288 | 0.00043017 | 0.00043746 | 0.00044474 | 0.00045203 | 0.00045931 | 0.0004666 | 0.00047389 | 0.00048117 | 0.00048846 | 0.00049574 | 0.00050303 | 0.00051031 | 0.0005176 | 0.00052489 | 0.00053217
| 10240313 | MRO007 | MRO | 16247669 | 16247664 | 0.12826 | 143.764 | -37.1435 | 108 | 95.9 | 6.3% | 8.8% | 114.804 | 101.9417 | 0.01 | 0.02 | -1286.23 | 127.6663 | 1.529% | 115.884 | 104.3392 | 0.01 | 0.02 | -1154.48 | 127.4288 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039374 | 0.00040103 | 0.00040831 | 0.0004156 | 0.00042288 | 0.00043017 | 0.00043746 | 0.00044474 | 0.00045203 | 0.00045931 | 0.0004666 | 0.00047389 | 0.00048117 | 0.00048846 | 0.00049574 | 0.00050303 | 0.00051031 | 0.0005176 | 0.00052489 | 0.00053217
| 10240609 | MRO007 | MRO | 16249077 | 16249100 | 1.2287 | 143.7455 | -37.1702 | 109 | 96.9 | 6.3% | 8.8% | 115.867 | 103.0047 | 0.01 | 0.02 | -1286.23 | 128.7293 | 1.534% | 116.957 | 105.4272 | 0.01 | 0.02 | -1152.98 | 128.4868 | 1.69% | 153.4% | 0.9727% | 0.9909% | 1.009% | 1.027% | 1.045% | 1.064% | 1.082% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.191% | 1.209% | 1.227% | 1.245% | 1.263% | 1.281% | 1.3% | 1.318% | 0.00039394 | 0.0004013 | 0.00040865 | 0.000416 | 0.00042336 | 0.00043071 | 0.00043806 | 0.00044542 | 0.00045277 | 0.00046012 | 0.00046748 | 0.00047483 | 0.00048218 | 0.00048954 | 0.00049689 | 0.00050424 | 0.0005116 | 0.00051895 | 0.0005263 | 0.00053366
| 10243207 | STN024 | STN | 16263191 | 16263196 | 0.75854 | 145.5879 | -36.3627 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10243209 | STN024 | STN | 16263196 | 16263200 | 0.36819 | 145.5894 | -36.3628 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10243244 | SHL004 | SHL | 16694612 | 16263321 | 2.087 | 143.522 | -35.2264 | 106 | 94.5 | 6.3% | 8.8% | 112.678 | 100.4535 | 0.01 | 0.02 | -1222.45 | 124.9025 | 1.546% | 113.738 | 102.816 | 0.01 | 0.02 | -1092.2 | 124.66 | 1.708% | 154.6% | 0.974% | 0.9926% | 1.011% | 1.03% | 1.048% | 1.067% | 1.085% | 1.104% | 1.123% | 1.141% | 1.16% | 1.178% | 1.197% | 1.216% | 1.234% | 1.253% | 1.271% | 1.29% | 1.308% | 1.327% | 0.00039445 | 0.00040198 | 0.0004095 | 0.00041703 | 0.00042455 | 0.00043207 | 0.0004396 | 0.00044712 | 0.00045465 | 0.00046217 | 0.0004697 | 0.00047722 | 0.00048474 | 0.00049227 | 0.00049979 | 0.00050732 | 0.00051484 | 0.00052236 | 0.00052989 | 0.00053741
| 10243245 | SHL004 | SHL | 16263321 | 17800142 | 0.72258 | 143.5239 | -35.2259 | 106 | 94.5 | 6.3% | 8.8% | 112.678 | 100.4535 | 0.01 | 0.02 | -1222.45 | 124.9025 | 1.546% | 113.738 | 102.816 | 0.01 | 0.02 | -1092.2 | 124.66 | 1.708% | 154.6% | 0.974% | 0.9926% | 1.011% | 1.03% | 1.048% | 1.067% | 1.085% | 1.104% | 1.123% | 1.141% | 1.16% | 1.178% | 1.197% | 1.216% | 1.234% | 1.253% | 1.271% | 1.29% | 1.308% | 1.327% | 0.00039445 | 0.00040198 | 0.0004095 | 0.00041703 | 0.00042455 | 0.00043207 | 0.0004396 | 0.00044712 | 0.00045465 | 0.00046217 | 0.0004697 | 0.00047722 | 0.00048474 | 0.00049227 | 0.00049979 | 0.00050732 | 0.00051484 | 0.00052236 | 0.00052989 | 0.00053741
| 10244130 | TNA022 | TNA | 16268438 | 16268447 | 0.21355 | 144.6264 | -37.8538 | 123 | 107 | 5.4% | 7.3% | 129.642 | 112.778 | 0.01 | 0.02 | -1686.4 | 146.506 | 1.394% | 131.979 | 114.811 | 0.01 | 0.02 | -1716.8 | 149.147 | 1.523% | 139.4% | 0.9585% | 0.9719% | 0.9852% | 0.9986% | 1.012% | 1.025% | 1.039% | 1.052% | 1.066% | 1.079% | 1.092% | 1.106% | 1.119% | 1.133% | 1.146% | 1.159% | 1.173% | 1.186% | 1.2% | 1.213% | 0.00038816 | 0.00039358 | 0.00039901 | 0.00040443 | 0.00040985 | 0.00041528 | 0.0004207 | 0.00042613 | 0.00043155 | 0.00043698 | 0.0004424 | 0.00044783 | 0.00045325 | 0.00045868 | 0.0004641 | 0.00046953 | 0.00047495 | 0.00048038 | 0.0004858 | 0.00049123
| 10244137 | TNA022 | TNA | 16268463 | 16359907 | 0.56147 | 144.6233 | -37.8541 | 121 | 106 | 5.4% | 7.3% | 127.534 | 111.724 | 0.01 | 0.02 | -1581 | 143.344 | 1.413% | 129.833 | 113.738 | 0.01 | 0.02 | -1609.5 | 145.928 | 1.549% | 141.3% | 0.9604% | 0.9745% | 0.9886% | 1.003% | 1.017% | 1.031% | 1.045% | 1.059% | 1.073% | 1.087% | 1.101% | 1.115% | 1.129% | 1.143% | 1.157% | 1.171% | 1.185% | 1.199% | 1.213% | 1.228% | 0.00038896 | 0.00039465 | 0.00040034 | 0.00040604 | 0.00041173 | 0.00041742 | 0.00042311 | 0.0004288 | 0.0004345 | 0.00044019 | 0.00044588 | 0.00045157 | 0.00045727 | 0.00046296 | 0.00046865 | 0.00047434 | 0.00048004 | 0.00048573 | 0.00049142 | 0.00049711
| 10246348 | WBL006 | WBL | 16278377 | 16278628 | 0.133 | 142.4746 | -38.3577 | 121 | 103 | 5.4% | 7.3% | 127.534 | 108.562 | 0.01 | 0.02 | -1897.2 | 146.506 | 1.344% | 129.833 | 110.519 | 0.01 | 0.02 | -1931.4 | 149.147 | 1.457% | 134.4% | 0.9534% | 0.9651% | 0.9768% | 0.9886% | 1% | 1.012% | 1.024% | 1.035% | 1.047% | 1.059% | 1.071% | 1.082% | 1.094% | 1.106% | 1.117% | 1.129% | 1.141% | 1.153% | 1.164% | 1.176% | 0.00038611 | 0.00039086 | 0.0003956 | 0.00040034 | 0.00040509 | 0.00040983 | 0.00041457 | 0.00041932 | 0.00042406 | 0.0004288 | 0.00043355 | 0.00043829 | 0.00044304 | 0.00044778 | 0.00045252 | 0.00045727 | 0.00046201 | 0.00046675 | 0.0004715 | 0.00047624
| 10251564 | SHN021 | SHN | 16301504 | 16967698 | 0.13826 | 145.3853 | -36.3446 | 113 | 99.7 | 6.3% | 8.8% | 120.119 | 105.9811 | 0.01 | 0.02 | -1413.79 | 134.2569 | 1.504% | 121.249 | 108.4736 | 0.01 | 0.02 | -1277.54 | 134.0244 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039269 | 0.00039962 | 0.00040656 | 0.00041349 | 0.00042043 | 0.00042737 | 0.0004343 | 0.00044124 | 0.00044817 | 0.00045511 | 0.00046204 | 0.00046898 | 0.00047591 | 0.00048285 | 0.00048978 | 0.00049672 | 0.00050366 | 0.00051059 | 0.00051753 | 0.00052446
| 10253006 | STL006 | STL | 16308072 | 17567260 | 1.5516 | 142.7545 | -36.9043 | 111 | 98 | 6.3% | 8.8% | 117.993 | 104.174 | 0.01 | 0.02 | -1381.9 | 131.812 | 1.506% | 119.103 | 106.624 | 0.01 | 0.02 | -1247.9 | 131.582 | 1.649% | 150.6% | 0.9699% | 0.9871% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.09% | 1.108% | 1.125% | 1.142% | 1.159% | 1.176% | 1.194% | 1.211% | 1.228% | 1.245% | 1.262% | 1.28% | 1.297% | 0.00039279 | 0.00039976 | 0.00040673 | 0.0004137 | 0.00042067 | 0.00042764 | 0.00043461 | 0.00044158 | 0.00044855 | 0.00045552 | 0.00046249 | 0.00046946 | 0.00047643 | 0.0004834 | 0.00049037 | 0.00049734 | 0.00050431 | 0.00051128 | 0.00051825 | 0.00052522
| 10253013 | STL006 | STL | 16308104 | 16308100 | 0.7074 | 142.7631 | -36.9158 | 111 | 98 | 6.3% | 8.8% | 117.993 | 104.174 | 0.01 | 0.02 | -1381.9 | 131.812 | 1.506% | 119.103 | 106.624 | 0.01 | 0.02 | -1247.9 | 131.582 | 1.649% | 150.6% | 0.9699% | 0.9871% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.09% | 1.108% | 1.125% | 1.142% | 1.159% | 1.176% | 1.194% | 1.211% | 1.228% | 1.245% | 1.262% | 1.28% | 1.297% | 0.00039279 | 0.00039976 | 0.00040673 | 0.0004137 | 0.00042067 | 0.00042764 | 0.00043461 | 0.00044158 | 0.00044855 | 0.00045552 | 0.00046249 | 0.00046946 | 0.00047643 | 0.0004834 | 0.00049037 | 0.00049734 | 0.00050431 | 0.00051128 | 0.00051825 | 0.00052522
| 10253014 | STL006 | STL | 16308108 | 16308104 | 0.29321 | 142.765 | -36.9158 | 111 | 98 | 6.3% | 8.8% | 117.993 | 104.174 | 0.01 | 0.02 | -1381.9 | 131.812 | 1.506% | 119.103 | 106.624 | 0.01 | 0.02 | -1247.9 | 131.582 | 1.649% | 150.6% | 0.9699% | 0.9871% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.09% | 1.108% | 1.125% | 1.142% | 1.159% | 1.176% | 1.194% | 1.211% | 1.228% | 1.245% | 1.262% | 1.28% | 1.297% | 0.00039279 | 0.00039976 | 0.00040673 | 0.0004137 | 0.00042067 | 0.00042764 | 0.00043461 | 0.00044158 | 0.00044855 | 0.00045552 | 0.00046249 | 0.00046946 | 0.00047643 | 0.0004834 | 0.00049037 | 0.00049734 | 0.00050431 | 0.00051128 | 0.00051825 | 0.00052522
| 10253028 | STL006 | STL | 146132464 | 16308173 | 1.0738 | 142.7847 | -36.9202 | 111 | 97.8 | 6.3% | 8.8% | 117.993 | 103.9614 | 0.01 | 0.02 | -1403.16 | 132.0246 | 1.498% | 119.103 | 106.4064 | 0.01 | 0.02 | -1269.66 | 131.7996 | 1.638% | 149.8% | 0.9691% | 0.9861% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.189% | 1.206% | 1.223% | 1.24% | 1.257% | 1.274% | 1.291% | 0.00039247 | 0.00039934 | 0.0004062 | 0.00041307 | 0.00041993 | 0.0004268 | 0.00043366 | 0.00044052 | 0.00044739 | 0.00045425 | 0.00046112 | 0.00046798 | 0.00047485 | 0.00048171 | 0.00048857 | 0.00049544 | 0.0005023 | 0.00050917 | 0.00051603 | 0.0005229
| 10253030 | STL006 | STL | 16308181 | 146132464 | 0.17721 | 142.7842 | -36.9216 | 111 | 97.8 | 6.3% | 8.8% | 117.993 | 103.9614 | 0.01 | 0.02 | -1403.16 | 132.0246 | 1.498% | 119.103 | 106.4064 | 0.01 | 0.02 | -1269.66 | 131.7996 | 1.638% | 149.8% | 0.9691% | 0.9861% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.189% | 1.206% | 1.223% | 1.24% | 1.257% | 1.274% | 1.291% | 0.00039247 | 0.00039934 | 0.0004062 | 0.00041307 | 0.00041993 | 0.0004268 | 0.00043366 | 0.00044052 | 0.00044739 | 0.00045425 | 0.00046112 | 0.00046798 | 0.00047485 | 0.00048171 | 0.00048857 | 0.00049544 | 0.0005023 | 0.00050917 | 0.00051603 | 0.0005229
| 10253061 | STL006 | STL | 17567260 | 16308329 | 1.3167 | 142.7579 | -36.9038 | 111 | 98 | 6.3% | 8.8% | 117.993 | 104.174 | 0.01 | 0.02 | -1381.9 | 131.812 | 1.506% | 119.103 | 106.624 | 0.01 | 0.02 | -1247.9 | 131.582 | 1.649% | 150.6% | 0.9699% | 0.9871% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.09% | 1.108% | 1.125% | 1.142% | 1.159% | 1.176% | 1.194% | 1.211% | 1.228% | 1.245% | 1.262% | 1.28% | 1.297% | 0.00039279 | 0.00039976 | 0.00040673 | 0.0004137 | 0.00042067 | 0.00042764 | 0.00043461 | 0.00044158 | 0.00044855 | 0.00045552 | 0.00046249 | 0.00046946 | 0.00047643 | 0.0004834 | 0.00049037 | 0.00049734 | 0.00050431 | 0.00051128 | 0.00051825 | 0.00052522
| 10256915 | HSM004 | HSM | 16327475 | 16327470 | 0.52829 | 142.09 | -36.7704 | 117 | 100 | 6.3% | 8.8% | 124.371 | 106.3 | 0.01 | 0.02 | -1807.1 | 142.442 | 1.408% | 125.541 | 108.8 | 0.01 | 0.02 | -1674.1 | 142.282 | 1.51% | 140.8% | 0.9599% | 0.9738% | 0.9876% | 1.002% | 1.015% | 1.029% | 1.043% | 1.057% | 1.071% | 1.085% | 1.099% | 1.112% | 1.126% | 1.14% | 1.154% | 1.168% | 1.182% | 1.196% | 1.21% | 1.223% | 0.00038874 | 0.00039435 | 0.00039997 | 0.00040559 | 0.00041121 | 0.00041683 | 0.00042244 | 0.00042806 | 0.00043368 | 0.0004393 | 0.00044492 | 0.00045053 | 0.00045615 | 0.00046177 | 0.00046739 | 0.00047301 | 0.00047862 | 0.00048424 | 0.00048986 | 0.00049548
| 10261741 | KYM003 | KYM | 16348864 | 16348869 | 0.41289 | 145.1303 | -36.284 | 110 | 96.8 | 6.3% | 8.8% | 116.93 | 102.8984 | 0.01 | 0.02 | -1403.16 | 130.9616 | 1.494% | 118.03 | 105.3184 | 0.01 | 0.02 | -1271.16 | 130.7416 | 1.632% | 149.4% | 0.9687% | 0.9855% | 1.002% | 1.019% | 1.036% | 1.053% | 1.069% | 1.086% | 1.103% | 1.12% | 1.137% | 1.153% | 1.17% | 1.187% | 1.204% | 1.221% | 1.237% | 1.254% | 1.271% | 1.288% | 0.00039229 | 0.00039909 | 0.00040589 | 0.0004127 | 0.0004195 | 0.0004263 | 0.0004331 | 0.00043991 | 0.00044671 | 0.00045351 | 0.00046031 | 0.00046712 | 0.00047392 | 0.00048072 | 0.00048752 | 0.00049433 | 0.00050113 | 0.00050793 | 0.00051473 | 0.00052154
| 10261832 | KYM003 | KYM | 16349247 | 16349252 | 2.017 | 145.1699 | -36.276 | 110 | 97 | 6.3% | 8.8% | 116.93 | 103.111 | 0.01 | 0.02 | -1381.9 | 130.749 | 1.501% | 118.03 | 105.536 | 0.01 | 0.02 | -1249.4 | 130.524 | 1.643% | 150.1% | 0.9694% | 0.9865% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.089% | 1.106% | 1.123% | 1.14% | 1.157% | 1.174% | 1.191% | 1.208% | 1.225% | 1.242% | 1.259% | 1.276% | 1.293% | 0.0003926 | 0.00039951 | 0.00040642 | 0.00041332 | 0.00042023 | 0.00042714 | 0.00043405 | 0.00044095 | 0.00044786 | 0.00045477 | 0.00046167 | 0.00046858 | 0.00047549 | 0.0004824 | 0.0004893 | 0.00049621 | 0.00050312 | 0.00051002 | 0.00051693 | 0.00052384
| 10261833 | KYM003 | KYM | 16349257 | 16349261 | 1.5404 | 145.1683 | -36.2798 | 110 | 97 | 6.3% | 8.8% | 116.93 | 103.111 | 0.01 | 0.02 | -1381.9 | 130.749 | 1.501% | 118.03 | 105.536 | 0.01 | 0.02 | -1249.4 | 130.524 | 1.643% | 150.1% | 0.9694% | 0.9865% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.089% | 1.106% | 1.123% | 1.14% | 1.157% | 1.174% | 1.191% | 1.208% | 1.225% | 1.242% | 1.259% | 1.276% | 1.293% | 0.0003926 | 0.00039951 | 0.00040642 | 0.00041332 | 0.00042023 | 0.00042714 | 0.00043405 | 0.00044095 | 0.00044786 | 0.00045477 | 0.00046167 | 0.00046858 | 0.00047549 | 0.0004824 | 0.0004893 | 0.00049621 | 0.00050312 | 0.00051002 | 0.00051693 | 0.00052384
| 10262007 | KYM003 | KYM | 16349982 | 110624803 | 0.6175 | 145.1869 | -36.2859 | 110 | 97.3 | 6.3% | 8.8% | 116.93 | 103.4299 | 0.01 | 0.02 | -1350.01 | 130.4301 | 1.513% | 118.03 | 105.8624 | 0.01 | 0.02 | -1216.76 | 130.1976 | 1.66% | 151.3% | 0.9706% | 0.9881% | 1.006% | 1.023% | 1.04% | 1.058% | 1.075% | 1.093% | 1.11% | 1.128% | 1.145% | 1.163% | 1.18% | 1.198% | 1.215% | 1.233% | 1.25% | 1.267% | 1.285% | 1.302% | 0.00039309 | 0.00040016 | 0.00040723 | 0.0004143 | 0.00042137 | 0.00042844 | 0.00043551 | 0.00044258 | 0.00044965 | 0.00045673 | 0.0004638 | 0.00047087 | 0.00047794 | 0.00048501 | 0.00049208 | 0.00049915 | 0.00050622 | 0.00051329 | 0.00052036 | 0.00052743
| 10262050 | KYM003 | KYM | 16350211 | 16350203 | 0.74918 | 145.1836 | -36.2922 | 110 | 97.3 | 6.3% | 8.8% | 116.93 | 103.4299 | 0.01 | 0.02 | -1350.01 | 130.4301 | 1.513% | 118.03 | 105.8624 | 0.01 | 0.02 | -1216.76 | 130.1976 | 1.66% | 151.3% | 0.9706% | 0.9881% | 1.006% | 1.023% | 1.04% | 1.058% | 1.075% | 1.093% | 1.11% | 1.128% | 1.145% | 1.163% | 1.18% | 1.198% | 1.215% | 1.233% | 1.25% | 1.267% | 1.285% | 1.302% | 0.00039309 | 0.00040016 | 0.00040723 | 0.0004143 | 0.00042137 | 0.00042844 | 0.00043551 | 0.00044258 | 0.00044965 | 0.00045673 | 0.0004638 | 0.00047087 | 0.00047794 | 0.00048501 | 0.00049208 | 0.00049915 | 0.00050622 | 0.00051329 | 0.00052036 | 0.00052743
| 10262851 | SHP014 | SHP | 16353438 | 63936327 | 0.16236 | 145.1062 | -36.4855 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10262865 | SHP014 | SHP | 16353514 | 16353518 | 2.0269 | 145.1306 | -36.5036 | 116 | 102 | 6.3% | 8.8% | 123.308 | 108.426 | 0.01 | 0.02 | -1488.2 | 138.19 | 1.491% | 124.468 | 110.976 | 0.01 | 0.02 | -1349.2 | 137.96 | 1.628% | 149.1% | 0.9684% | 0.9851% | 1.002% | 1.018% | 1.035% | 1.052% | 1.069% | 1.085% | 1.102% | 1.119% | 1.135% | 1.152% | 1.169% | 1.185% | 1.202% | 1.219% | 1.236% | 1.252% | 1.269% | 1.286% | 0.00039217 | 0.00039894 | 0.0004057 | 0.00041246 | 0.00041923 | 0.00042599 | 0.00043275 | 0.00043952 | 0.00044628 | 0.00045304 | 0.00045981 | 0.00046657 | 0.00047334 | 0.0004801 | 0.00048686 | 0.00049363 | 0.00050039 | 0.00050715 | 0.00051392 | 0.00052068
| 10262868 | SHP014 | SHP | 17711821 | 16353531 | 1.1153 | 145.1334 | -36.4999 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10263212 | SHP014 | SHP | 16354950 | 16355000 | 0.14823 | 145.1222 | -36.4762 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10263224 | MNA034 | MNA | 16355014 | 16355009 | 0.77613 | 145.211 | -36.5911 | 123 | 108 | 6.3% | 8.8% | 130.749 | 114.804 | 0.01 | 0.02 | -1594.5 | 146.694 | 1.486% | 131.979 | 117.504 | 0.01 | 0.02 | -1447.5 | 146.454 | 1.62% | 148.6% | 0.9679% | 0.9844% | 1.001% | 1.017% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.133% | 1.15% | 1.166% | 1.183% | 1.199% | 1.216% | 1.232% | 1.249% | 1.265% | 1.282% | 0.00039196 | 0.00039866 | 0.00040535 | 0.00041204 | 0.00041874 | 0.00042543 | 0.00043212 | 0.00043882 | 0.00044551 | 0.00045221 | 0.0004589 | 0.00046559 | 0.00047229 | 0.00047898 | 0.00048567 | 0.00049237 | 0.00049906 | 0.00050575 | 0.00051245 | 0.00051914
| 10263226 | MNA034 | MNA | 16355014 | 17676939 | 1.2381 | 145.2113 | -36.5892 | 123 | 108 | 6.3% | 8.8% | 130.749 | 114.804 | 0.01 | 0.02 | -1594.5 | 146.694 | 1.486% | 131.979 | 117.504 | 0.01 | 0.02 | -1447.5 | 146.454 | 1.62% | 148.6% | 0.9679% | 0.9844% | 1.001% | 1.017% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.133% | 1.15% | 1.166% | 1.183% | 1.199% | 1.216% | 1.232% | 1.249% | 1.265% | 1.282% | 0.00039196 | 0.00039866 | 0.00040535 | 0.00041204 | 0.00041874 | 0.00042543 | 0.00043212 | 0.00043882 | 0.00044551 | 0.00045221 | 0.0004589 | 0.00046559 | 0.00047229 | 0.00047898 | 0.00048567 | 0.00049237 | 0.00049906 | 0.00050575 | 0.00051245 | 0.00051914
| 10263303 | MNA034 | MNA | 16355351 | 16355347 | 1.9546 | 145.1976 | -36.5883 | 123 | 108 | 6.3% | 8.8% | 130.749 | 114.804 | 0.01 | 0.02 | -1594.5 | 146.694 | 1.486% | 131.979 | 117.504 | 0.01 | 0.02 | -1447.5 | 146.454 | 1.62% | 148.6% | 0.9679% | 0.9844% | 1.001% | 1.017% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.133% | 1.15% | 1.166% | 1.183% | 1.199% | 1.216% | 1.232% | 1.249% | 1.265% | 1.282% | 0.00039196 | 0.00039866 | 0.00040535 | 0.00041204 | 0.00041874 | 0.00042543 | 0.00043212 | 0.00043882 | 0.00044551 | 0.00045221 | 0.0004589 | 0.00046559 | 0.00047229 | 0.00047898 | 0.00048567 | 0.00049237 | 0.00049906 | 0.00050575 | 0.00051245 | 0.00051914
| 10263304 | MNA034 | MNA | 16355347 | 16355375 | 1.1277 | 145.1976 | -36.5907 | 123 | 108 | 6.3% | 8.8% | 130.749 | 114.804 | 0.01 | 0.02 | -1594.5 | 146.694 | 1.486% | 131.979 | 117.504 | 0.01 | 0.02 | -1447.5 | 146.454 | 1.62% | 148.6% | 0.9679% | 0.9844% | 1.001% | 1.017% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.133% | 1.15% | 1.166% | 1.183% | 1.199% | 1.216% | 1.232% | 1.249% | 1.265% | 1.282% | 0.00039196 | 0.00039866 | 0.00040535 | 0.00041204 | 0.00041874 | 0.00042543 | 0.00043212 | 0.00043882 | 0.00044551 | 0.00045221 | 0.0004589 | 0.00046559 | 0.00047229 | 0.00047898 | 0.00048567 | 0.00049237 | 0.00049906 | 0.00050575 | 0.00051245 | 0.00051914
| 10263307 | MNA034 | MNA | 16355363 | 16355359 | 1.5226 | 145.2023 | -36.5871 | 123 | 108 | 6.3% | 8.8% | 130.749 | 114.804 | 0.01 | 0.02 | -1594.5 | 146.694 | 1.486% | 131.979 | 117.504 | 0.01 | 0.02 | -1447.5 | 146.454 | 1.62% | 148.6% | 0.9679% | 0.9844% | 1.001% | 1.017% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.133% | 1.15% | 1.166% | 1.183% | 1.199% | 1.216% | 1.232% | 1.249% | 1.265% | 1.282% | 0.00039196 | 0.00039866 | 0.00040535 | 0.00041204 | 0.00041874 | 0.00042543 | 0.00043212 | 0.00043882 | 0.00044551 | 0.00045221 | 0.0004589 | 0.00046559 | 0.00047229 | 0.00047898 | 0.00048567 | 0.00049237 | 0.00049906 | 0.00050575 | 0.00051245 | 0.00051914
| 10263308 | MNA034 | MNA | 16355367 | 16355363 | 1.0812 | 145.2043 | -36.5871 | 123 | 108 | 6.3% | 8.8% | 130.749 | 114.804 | 0.01 | 0.02 | -1594.5 | 146.694 | 1.486% | 131.979 | 117.504 | 0.01 | 0.02 | -1447.5 | 146.454 | 1.62% | 148.6% | 0.9679% | 0.9844% | 1.001% | 1.017% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.133% | 1.15% | 1.166% | 1.183% | 1.199% | 1.216% | 1.232% | 1.249% | 1.265% | 1.282% | 0.00039196 | 0.00039866 | 0.00040535 | 0.00041204 | 0.00041874 | 0.00042543 | 0.00043212 | 0.00043882 | 0.00044551 | 0.00045221 | 0.0004589 | 0.00046559 | 0.00047229 | 0.00047898 | 0.00048567 | 0.00049237 | 0.00049906 | 0.00050575 | 0.00051245 | 0.00051914
| 10263310 | MNA034 | MNA | 16355375 | 16355379 | 1.6436 | 145.1974 | -36.593 | 123 | 108 | 6.3% | 8.8% | 130.749 | 114.804 | 0.01 | 0.02 | -1594.5 | 146.694 | 1.486% | 131.979 | 117.504 | 0.01 | 0.02 | -1447.5 | 146.454 | 1.62% | 148.6% | 0.9679% | 0.9844% | 1.001% | 1.017% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.133% | 1.15% | 1.166% | 1.183% | 1.199% | 1.216% | 1.232% | 1.249% | 1.265% | 1.282% | 0.00039196 | 0.00039866 | 0.00040535 | 0.00041204 | 0.00041874 | 0.00042543 | 0.00043212 | 0.00043882 | 0.00044551 | 0.00045221 | 0.0004589 | 0.00046559 | 0.00047229 | 0.00047898 | 0.00048567 | 0.00049237 | 0.00049906 | 0.00050575 | 0.00051245 | 0.00051914
| 10263393 | MNA034 | MNA | 16355695 | 16355699 | 1.4552 | 145.2003 | -36.6077 | 125 | 109 | 6.3% | 8.8% | 132.875 | 115.867 | 0.01 | 0.02 | -1700.8 | 149.883 | 1.463% | 134.125 | 118.592 | 0.01 | 0.02 | -1553.3 | 149.658 | 1.587% | 146.3% | 0.9655% | 0.9813% | 0.997% | 1.013% | 1.029% | 1.044% | 1.06% | 1.076% | 1.091% | 1.107% | 1.123% | 1.139% | 1.154% | 1.17% | 1.186% | 1.202% | 1.217% | 1.233% | 1.249% | 1.265% | 0.00039101 | 0.00039739 | 0.00040377 | 0.00041015 | 0.00041652 | 0.0004229 | 0.00042928 | 0.00043565 | 0.00044203 | 0.00044841 | 0.00045479 | 0.00046116 | 0.00046754 | 0.00047392 | 0.0004803 | 0.00048667 | 0.00049305 | 0.00049943 | 0.00050581 | 0.00051218
| 10263844 | EHK031 | EHK | 16358262 | 16358266 | 0.57511 | 144.5458 | -36.6316 | 105 | 94.9 | 6.3% | 8.8% | 111.615 | 100.8787 | 0.01 | 0.02 | -1073.63 | 122.3513 | 1.616% | 112.665 | 103.2512 | 0.01 | 0.02 | -941.38 | 122.0788 | 1.814% | 161.6% | 0.9811% | 1.002% | 1.023% | 1.044% | 1.065% | 1.086% | 1.107% | 1.128% | 1.149% | 1.17% | 1.191% | 1.212% | 1.233% | 1.254% | 1.275% | 1.295% | 1.316% | 1.337% | 1.358% | 1.379% | 0.00039734 | 0.00040583 | 0.00041431 | 0.0004228 | 0.00043129 | 0.00043977 | 0.00044826 | 0.00045674 | 0.00046523 | 0.00047372 | 0.0004822 | 0.00049069 | 0.00049918 | 0.00050766 | 0.00051615 | 0.00052463 | 0.00053312 | 0.00054161 | 0.00055009 | 0.00055858
| 10263847 | EHK031 | EHK | 16358271 | 16358281 | 3.8628 | 144.5491 | -36.631 | 105 | 94.9 | 6.3% | 8.8% | 111.615 | 100.8787 | 0.01 | 0.02 | -1073.63 | 122.3513 | 1.616% | 112.665 | 103.2512 | 0.01 | 0.02 | -941.38 | 122.0788 | 1.814% | 161.6% | 0.9811% | 1.002% | 1.023% | 1.044% | 1.065% | 1.086% | 1.107% | 1.128% | 1.149% | 1.17% | 1.191% | 1.212% | 1.233% | 1.254% | 1.275% | 1.295% | 1.316% | 1.337% | 1.358% | 1.379% | 0.00039734 | 0.00040583 | 0.00041431 | 0.0004228 | 0.00043129 | 0.00043977 | 0.00044826 | 0.00045674 | 0.00046523 | 0.00047372 | 0.0004822 | 0.00049069 | 0.00049918 | 0.00050766 | 0.00051615 | 0.00052463 | 0.00053312 | 0.00054161 | 0.00055009 | 0.00055858
| 10264152 | MBN031 | MBN | 16359518 | 16359523 | 0.10619 | 141.5939 | -34.2431 | 101 | 87.5 | 6.3% | 8.8% | 107.363 | 93.0125 | 0.01 | 0.02 | -1435.05 | 121.7135 | 1.443% | 108.373 | 95.2 | 0.01 | 0.02 | -1317.3 | 121.546 | 1.56% | 144.3% | 0.9635% | 0.9786% | 0.9937% | 1.009% | 1.024% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.129% | 1.144% | 1.16% | 1.175% | 1.19% | 1.205% | 1.22% | 1.235% | 1.25% | 0.0003902 | 0.00039631 | 0.00040242 | 0.00040852 | 0.00041463 | 0.00042074 | 0.00042685 | 0.00043295 | 0.00043906 | 0.00044517 | 0.00045127 | 0.00045738 | 0.00046349 | 0.0004696 | 0.0004757 | 0.00048181 | 0.00048792 | 0.00049402 | 0.00050013 | 0.00050624
| 10264167 | MBN031 | MBN | 154645699 | 16359608 | 0.47668 | 141.6189 | -34.2519 | 101 | 87.8 | 6.3% | 8.8% | 107.363 | 93.3314 | 0.01 | 0.02 | -1403.16 | 121.3946 | 1.453% | 108.373 | 95.5264 | 0.01 | 0.02 | -1284.66 | 121.2196 | 1.574% | 145.3% | 0.9645% | 0.98% | 0.9954% | 1.011% | 1.026% | 1.042% | 1.057% | 1.073% | 1.088% | 1.103% | 1.119% | 1.134% | 1.15% | 1.165% | 1.18% | 1.196% | 1.211% | 1.227% | 1.242% | 1.258% | 0.00039062 | 0.00039687 | 0.00040311 | 0.00040936 | 0.0004156 | 0.00042185 | 0.00042809 | 0.00043434 | 0.00044059 | 0.00044683 | 0.00045308 | 0.00045932 | 0.00046557 | 0.00047182 | 0.00047806 | 0.00048431 | 0.00049055 | 0.0004968 | 0.00050305 | 0.00050929
| 10264169 | MBN031 | MBN | 16359613 | 16359618 | 0.20696 | 141.6217 | -34.2529 | 101 | 87.8 | 6.3% | 8.8% | 107.363 | 93.3314 | 0.01 | 0.02 | -1403.16 | 121.3946 | 1.453% | 108.373 | 95.5264 | 0.01 | 0.02 | -1284.66 | 121.2196 | 1.574% | 145.3% | 0.9645% | 0.98% | 0.9954% | 1.011% | 1.026% | 1.042% | 1.057% | 1.073% | 1.088% | 1.103% | 1.119% | 1.134% | 1.15% | 1.165% | 1.18% | 1.196% | 1.211% | 1.227% | 1.242% | 1.258% | 0.00039062 | 0.00039687 | 0.00040311 | 0.00040936 | 0.0004156 | 0.00042185 | 0.00042809 | 0.00043434 | 0.00044059 | 0.00044683 | 0.00045308 | 0.00045932 | 0.00046557 | 0.00047182 | 0.00047806 | 0.00048431 | 0.00049055 | 0.0004968 | 0.00050305 | 0.00050929
| 10264170 | MBN031 | MBN | 16359618 | 16359623 | 0.59014 | 141.6232 | -34.2534 | 101 | 87.8 | 6.3% | 8.8% | 107.363 | 93.3314 | 0.01 | 0.02 | -1403.16 | 121.3946 | 1.453% | 108.373 | 95.5264 | 0.01 | 0.02 | -1284.66 | 121.2196 | 1.574% | 145.3% | 0.9645% | 0.98% | 0.9954% | 1.011% | 1.026% | 1.042% | 1.057% | 1.073% | 1.088% | 1.103% | 1.119% | 1.134% | 1.15% | 1.165% | 1.18% | 1.196% | 1.211% | 1.227% | 1.242% | 1.258% | 0.00039062 | 0.00039687 | 0.00040311 | 0.00040936 | 0.0004156 | 0.00042185 | 0.00042809 | 0.00043434 | 0.00044059 | 0.00044683 | 0.00045308 | 0.00045932 | 0.00046557 | 0.00047182 | 0.00047806 | 0.00048431 | 0.00049055 | 0.0004968 | 0.00050305 | 0.00050929
| 10264171 | MBN031 | MBN | 16359623 | 16359628 | 1.561 | 141.6246 | -34.2539 | 101 | 87.8 | 6.3% | 8.8% | 107.363 | 93.3314 | 0.01 | 0.02 | -1403.16 | 121.3946 | 1.453% | 108.373 | 95.5264 | 0.01 | 0.02 | -1284.66 | 121.2196 | 1.574% | 145.3% | 0.9645% | 0.98% | 0.9954% | 1.011% | 1.026% | 1.042% | 1.057% | 1.073% | 1.088% | 1.103% | 1.119% | 1.134% | 1.15% | 1.165% | 1.18% | 1.196% | 1.211% | 1.227% | 1.242% | 1.258% | 0.00039062 | 0.00039687 | 0.00040311 | 0.00040936 | 0.0004156 | 0.00042185 | 0.00042809 | 0.00043434 | 0.00044059 | 0.00044683 | 0.00045308 | 0.00045932 | 0.00046557 | 0.00047182 | 0.00047806 | 0.00048431 | 0.00049055 | 0.0004968 | 0.00050305 | 0.00050929
| 10269387 | STL006 | STL | 16388908 | 16388912 | 0.13363 | 142.8058 | -36.9137 | 111 | 98.1 | 6.3% | 8.8% | 117.993 | 104.2803 | 0.01 | 0.02 | -1371.27 | 131.7057 | 1.51% | 119.103 | 106.7328 | 0.01 | 0.02 | -1237.02 | 131.4732 | 1.655% | 151% | 0.9703% | 0.9876% | 1.005% | 1.022% | 1.04% | 1.057% | 1.074% | 1.092% | 1.109% | 1.126% | 1.144% | 1.161% | 1.178% | 1.196% | 1.213% | 1.23% | 1.248% | 1.265% | 1.282% | 1.3% | 0.00039295 | 0.00039998 | 0.000407 | 0.00041403 | 0.00042105 | 0.00042807 | 0.0004351 | 0.00044212 | 0.00044915 | 0.00045617 | 0.00046319 | 0.00047022 | 0.00047724 | 0.00048426 | 0.00049129 | 0.00049831 | 0.00050534 | 0.00051236 | 0.00051938 | 0.00052641
| 10273779 | BAN003 | BAN | 16409390 | 16409385 | 0.4659 | 144.1734 | -37.5771 | 130 | 115 | 5.4% | 7.3% | 137.02 | 121.21 | 0.01 | 0.02 | -1581 | 152.83 | 1.444% | 139.49 | 123.395 | 0.01 | 0.02 | -1609.5 | 155.585 | 1.59% | 144.4% | 0.9636% | 0.9787% | 0.9938% | 1.009% | 1.024% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.115% | 1.13% | 1.145% | 1.16% | 1.175% | 1.19% | 1.205% | 1.22% | 1.235% | 1.251% | 0.00039023 | 0.00039634 | 0.00040246 | 0.00040858 | 0.00041469 | 0.00042081 | 0.00042692 | 0.00043304 | 0.00043915 | 0.00044527 | 0.00045139 | 0.0004575 | 0.00046362 | 0.00046973 | 0.00047585 | 0.00048196 | 0.00048808 | 0.0004942 | 0.00050031 | 0.00050643
| 10274498 | BMH003 | BMH | 16412404 | 17531788 | 0.21186 | 144.3894 | -37.6879 | 128 | 113 | 5.4% | 7.3% | 134.912 | 119.102 | 0.01 | 0.02 | -1581 | 150.722 | 1.437% | 137.344 | 121.249 | 0.01 | 0.02 | -1609.5 | 153.439 | 1.581% | 143.7% | 0.9629% | 0.9777% | 0.9926% | 1.007% | 1.022% | 1.037% | 1.052% | 1.067% | 1.082% | 1.097% | 1.112% | 1.126% | 1.141% | 1.156% | 1.171% | 1.186% | 1.201% | 1.216% | 1.231% | 1.245% | 0.00038995 | 0.00039597 | 0.00040199 | 0.00040801 | 0.00041403 | 0.00042005 | 0.00042608 | 0.0004321 | 0.00043812 | 0.00044414 | 0.00045016 | 0.00045618 | 0.00046221 | 0.00046823 | 0.00047425 | 0.00048027 | 0.00048629 | 0.00049231 | 0.00049834 | 0.00050436
| 10274507 | BMH003 | BMH | 16412436 | 17603718 | 0.39244 | 144.379 | -37.6813 | 128 | 113 | 5.4% | 7.3% | 134.912 | 119.102 | 0.01 | 0.02 | -1581 | 150.722 | 1.437% | 137.344 | 121.249 | 0.01 | 0.02 | -1609.5 | 153.439 | 1.581% | 143.7% | 0.9629% | 0.9777% | 0.9926% | 1.007% | 1.022% | 1.037% | 1.052% | 1.067% | 1.082% | 1.097% | 1.112% | 1.126% | 1.141% | 1.156% | 1.171% | 1.186% | 1.201% | 1.216% | 1.231% | 1.245% | 0.00038995 | 0.00039597 | 0.00040199 | 0.00040801 | 0.00041403 | 0.00042005 | 0.00042608 | 0.0004321 | 0.00043812 | 0.00044414 | 0.00045016 | 0.00045618 | 0.00046221 | 0.00046823 | 0.00047425 | 0.00048027 | 0.00048629 | 0.00049231 | 0.00049834 | 0.00050436
| 10274517 | BMH003 | BMH | 17603718 | 16412470 | 0.32385 | 144.3794 | -37.6805 | 128 | 113 | 5.4% | 7.3% | 134.912 | 119.102 | 0.01 | 0.02 | -1581 | 150.722 | 1.437% | 137.344 | 121.249 | 0.01 | 0.02 | -1609.5 | 153.439 | 1.581% | 143.7% | 0.9629% | 0.9777% | 0.9926% | 1.007% | 1.022% | 1.037% | 1.052% | 1.067% | 1.082% | 1.097% | 1.112% | 1.126% | 1.141% | 1.156% | 1.171% | 1.186% | 1.201% | 1.216% | 1.231% | 1.245% | 0.00038995 | 0.00039597 | 0.00040199 | 0.00040801 | 0.00041403 | 0.00042005 | 0.00042608 | 0.0004321 | 0.00043812 | 0.00044414 | 0.00045016 | 0.00045618 | 0.00046221 | 0.00046823 | 0.00047425 | 0.00048027 | 0.00048629 | 0.00049231 | 0.00049834 | 0.00050436
| 10274874 | BMH006 | BMH | 16414852 | 16414860 | 2.703 | 144.45 | -37.6983 | 120 | 105 | 5.4% | 7.3% | 126.48 | 110.67 | 0.01 | 0.02 | -1581 | 142.29 | 1.41% | 128.76 | 112.665 | 0.01 | 0.02 | -1609.5 | 144.855 | 1.544% | 141% | 0.9601% | 0.974% | 0.988% | 1.002% | 1.016% | 1.03% | 1.044% | 1.058% | 1.072% | 1.086% | 1.099% | 1.113% | 1.127% | 1.141% | 1.155% | 1.169% | 1.183% | 1.197% | 1.211% | 1.225% | 0.00038882 | 0.00039446 | 0.00040011 | 0.00040575 | 0.0004114 | 0.00041704 | 0.00042269 | 0.00042833 | 0.00043398 | 0.00043962 | 0.00044527 | 0.00045092 | 0.00045656 | 0.00046221 | 0.00046785 | 0.0004735 | 0.00047914 | 0.00048479 | 0.00049043 | 0.00049608
| 10275122 | BMH006 | BMH | 16415902 | 16415897 | 0.74768 | 144.4684 | -37.6965 | 117 | 103 | 5.4% | 7.3% | 123.318 | 108.562 | 0.01 | 0.02 | -1475.6 | 138.074 | 1.428% | 125.541 | 110.519 | 0.01 | 0.02 | -1502.2 | 140.563 | 1.569% | 142.8% | 0.962% | 0.9765% | 0.9911% | 1.006% | 1.02% | 1.035% | 1.049% | 1.064% | 1.078% | 1.093% | 1.108% | 1.122% | 1.137% | 1.151% | 1.166% | 1.18% | 1.195% | 1.21% | 1.224% | 1.239% | 0.00038957 | 0.00039547 | 0.00040137 | 0.00040727 | 0.00041316 | 0.00041906 | 0.00042496 | 0.00043085 | 0.00043675 | 0.00044265 | 0.00044855 | 0.00045444 | 0.00046034 | 0.00046624 | 0.00047214 | 0.00047803 | 0.00048393 | 0.00048983 | 0.00049572 | 0.00050162
| 10275306 | BMH006 | BMH | 16416625 | 118639387 | 0.69406 | 144.4447 | -37.7109 | 120 | 105 | 5.4% | 7.3% | 126.48 | 110.67 | 0.01 | 0.02 | -1581 | 142.29 | 1.41% | 128.76 | 112.665 | 0.01 | 0.02 | -1609.5 | 144.855 | 1.544% | 141% | 0.9601% | 0.974% | 0.988% | 1.002% | 1.016% | 1.03% | 1.044% | 1.058% | 1.072% | 1.086% | 1.099% | 1.113% | 1.127% | 1.141% | 1.155% | 1.169% | 1.183% | 1.197% | 1.211% | 1.225% | 0.00038882 | 0.00039446 | 0.00040011 | 0.00040575 | 0.0004114 | 0.00041704 | 0.00042269 | 0.00042833 | 0.00043398 | 0.00043962 | 0.00044527 | 0.00045092 | 0.00045656 | 0.00046221 | 0.00046785 | 0.0004735 | 0.00047914 | 0.00048479 | 0.00049043 | 0.00049608
| 10275360 | BMH006 | BMH | 16416861 | 16416857 | 1.1513 | 144.459 | -37.6774 | 117 | 103 | 5.4% | 7.3% | 123.318 | 108.562 | 0.01 | 0.02 | -1475.6 | 138.074 | 1.428% | 125.541 | 110.519 | 0.01 | 0.02 | -1502.2 | 140.563 | 1.569% | 142.8% | 0.962% | 0.9765% | 0.9911% | 1.006% | 1.02% | 1.035% | 1.049% | 1.064% | 1.078% | 1.093% | 1.108% | 1.122% | 1.137% | 1.151% | 1.166% | 1.18% | 1.195% | 1.21% | 1.224% | 1.239% | 0.00038957 | 0.00039547 | 0.00040137 | 0.00040727 | 0.00041316 | 0.00041906 | 0.00042496 | 0.00043085 | 0.00043675 | 0.00044265 | 0.00044855 | 0.00045444 | 0.00046034 | 0.00046624 | 0.00047214 | 0.00047803 | 0.00048393 | 0.00048983 | 0.00049572 | 0.00050162
| 10275362 | BMH006 | BMH | 16416861 | 16416928 | 0.92962 | 144.4578 | -37.6771 | 117 | 103 | 5.4% | 7.3% | 123.318 | 108.562 | 0.01 | 0.02 | -1475.6 | 138.074 | 1.428% | 125.541 | 110.519 | 0.01 | 0.02 | -1502.2 | 140.563 | 1.569% | 142.8% | 0.962% | 0.9765% | 0.9911% | 1.006% | 1.02% | 1.035% | 1.049% | 1.064% | 1.078% | 1.093% | 1.108% | 1.122% | 1.137% | 1.151% | 1.166% | 1.18% | 1.195% | 1.21% | 1.224% | 1.239% | 0.00038957 | 0.00039547 | 0.00040137 | 0.00040727 | 0.00041316 | 0.00041906 | 0.00042496 | 0.00043085 | 0.00043675 | 0.00044265 | 0.00044855 | 0.00045444 | 0.00046034 | 0.00046624 | 0.00047214 | 0.00047803 | 0.00048393 | 0.00048983 | 0.00049572 | 0.00050162
| 10278483 | SHP012 | SHP | 16430774 | 193649572 | 0.21817 | 144.6842 | -36.3179 | 105 | 93.6 | 6.3% | 8.8% | 111.615 | 99.4968 | 0.01 | 0.02 | -1211.82 | 123.7332 | 1.546% | 112.665 | 101.8368 | 0.01 | 0.02 | -1082.82 | 123.4932 | 1.708% | 154.6% | 0.974% | 0.9925% | 1.011% | 1.03% | 1.048% | 1.067% | 1.085% | 1.104% | 1.122% | 1.141% | 1.16% | 1.178% | 1.197% | 1.215% | 1.234% | 1.252% | 1.271% | 1.29% | 1.308% | 1.327% | 0.00039444 | 0.00040196 | 0.00040947 | 0.00041699 | 0.00042451 | 0.00043203 | 0.00043955 | 0.00044707 | 0.00045459 | 0.0004621 | 0.00046962 | 0.00047714 | 0.00048466 | 0.00049218 | 0.0004997 | 0.00050722 | 0.00051473 | 0.00052225 | 0.00052977 | 0.00053729
| 10281761 | KYM004 | KYM | 16445287 | 16445292 | 1.3887 | 145.1857 | -36.1566 | 112 | 98.5 | 6.3% | 8.8% | 119.056 | 104.7055 | 0.01 | 0.02 | -1435.05 | 133.4065 | 1.492% | 120.176 | 107.168 | 0.01 | 0.02 | -1300.8 | 133.184 | 1.629% | 149.2% | 0.9684% | 0.9852% | 1.002% | 1.019% | 1.035% | 1.052% | 1.069% | 1.085% | 1.102% | 1.119% | 1.136% | 1.152% | 1.169% | 1.186% | 1.203% | 1.219% | 1.236% | 1.253% | 1.269% | 1.286% | 0.0003922 | 0.00039897 | 0.00040574 | 0.00041252 | 0.00041929 | 0.00042606 | 0.00043283 | 0.0004396 | 0.00044638 | 0.00045315 | 0.00045992 | 0.00046669 | 0.00047347 | 0.00048024 | 0.00048701 | 0.00049378 | 0.00050055 | 0.00050733 | 0.0005141 | 0.00052087
| 10281764 | KYM004 | KYM | 16445296 | 17220480 | 0.64392 | 145.1855 | -36.1531 | 112 | 98.5 | 6.3% | 8.8% | 119.056 | 104.7055 | 0.01 | 0.02 | -1435.05 | 133.4065 | 1.492% | 120.176 | 107.168 | 0.01 | 0.02 | -1300.8 | 133.184 | 1.629% | 149.2% | 0.9684% | 0.9852% | 1.002% | 1.019% | 1.035% | 1.052% | 1.069% | 1.085% | 1.102% | 1.119% | 1.136% | 1.152% | 1.169% | 1.186% | 1.203% | 1.219% | 1.236% | 1.253% | 1.269% | 1.286% | 0.0003922 | 0.00039897 | 0.00040574 | 0.00041252 | 0.00041929 | 0.00042606 | 0.00043283 | 0.0004396 | 0.00044638 | 0.00045315 | 0.00045992 | 0.00046669 | 0.00047347 | 0.00048024 | 0.00048701 | 0.00049378 | 0.00050055 | 0.00050733 | 0.0005141 | 0.00052087
| 10281798 | KYM004 | KYM | 16445448 | 16445452 | 0.15159 | 145.1927 | -36.157 | 112 | 98.5 | 6.3% | 8.8% | 119.056 | 104.7055 | 0.01 | 0.02 | -1435.05 | 133.4065 | 1.492% | 120.176 | 107.168 | 0.01 | 0.02 | -1300.8 | 133.184 | 1.629% | 149.2% | 0.9684% | 0.9852% | 1.002% | 1.019% | 1.035% | 1.052% | 1.069% | 1.085% | 1.102% | 1.119% | 1.136% | 1.152% | 1.169% | 1.186% | 1.203% | 1.219% | 1.236% | 1.253% | 1.269% | 1.286% | 0.0003922 | 0.00039897 | 0.00040574 | 0.00041252 | 0.00041929 | 0.00042606 | 0.00043283 | 0.0004396 | 0.00044638 | 0.00045315 | 0.00045992 | 0.00046669 | 0.00047347 | 0.00048024 | 0.00048701 | 0.00049378 | 0.00050055 | 0.00050733 | 0.0005141 | 0.00052087
| 10282283 | BMH003 | BMH | 16448149 | 16448136 | 0.38187 | 144.2176 | -37.7366 | 140 | 123 | 5.4% | 7.3% | 147.56 | 129.642 | 0.01 | 0.02 | -1791.8 | 165.478 | 1.422% | 150.22 | 131.979 | 0.01 | 0.02 | -1824.1 | 168.461 | 1.56% | 142.2% | 0.9613% | 0.9757% | 0.99% | 1.004% | 1.019% | 1.033% | 1.047% | 1.062% | 1.076% | 1.09% | 1.105% | 1.119% | 1.134% | 1.148% | 1.162% | 1.177% | 1.191% | 1.205% | 1.22% | 1.234% | 0.00038932 | 0.00039513 | 0.00040094 | 0.00040675 | 0.00041256 | 0.00041837 | 0.00042418 | 0.00042999 | 0.00043581 | 0.00044162 | 0.00044743 | 0.00045324 | 0.00045905 | 0.00046486 | 0.00047067 | 0.00047648 | 0.0004823 | 0.00048811 | 0.00049392 | 0.00049973
| 10282315 | BMH003 | BMH | 16448262 | 16448258 | 0.34198 | 144.2211 | -37.7151 | 138 | 122 | 5.4% | 7.3% | 145.452 | 128.588 | 0.01 | 0.02 | -1686.4 | 162.316 | 1.442% | 148.074 | 130.906 | 0.01 | 0.02 | -1716.8 | 165.242 | 1.587% | 144.2% | 0.9634% | 0.9784% | 0.9934% | 1.008% | 1.023% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.129% | 1.144% | 1.159% | 1.174% | 1.189% | 1.204% | 1.219% | 1.234% | 1.249% | 0.00039014 | 0.00039623 | 0.00040231 | 0.0004084 | 0.00041449 | 0.00042057 | 0.00042666 | 0.00043274 | 0.00043883 | 0.00044492 | 0.000451 | 0.00045709 | 0.00046318 | 0.00046926 | 0.00047535 | 0.00048143 | 0.00048752 | 0.00049361 | 0.00049969 | 0.00050578
| 10282316 | BMH003 | BMH | 16448266 | 16448262 | 0.47123 | 144.2213 | -37.7141 | 138 | 122 | 5.4% | 7.3% | 145.452 | 128.588 | 0.01 | 0.02 | -1686.4 | 162.316 | 1.442% | 148.074 | 130.906 | 0.01 | 0.02 | -1716.8 | 165.242 | 1.587% | 144.2% | 0.9634% | 0.9784% | 0.9934% | 1.008% | 1.023% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.129% | 1.144% | 1.159% | 1.174% | 1.189% | 1.204% | 1.219% | 1.234% | 1.249% | 0.00039014 | 0.00039623 | 0.00040231 | 0.0004084 | 0.00041449 | 0.00042057 | 0.00042666 | 0.00043274 | 0.00043883 | 0.00044492 | 0.000451 | 0.00045709 | 0.00046318 | 0.00046926 | 0.00047535 | 0.00048143 | 0.00048752 | 0.00049361 | 0.00049969 | 0.00050578
| 10282317 | BMH003 | BMH | 16448270 | 16448266 | 0.64506 | 144.2215 | -37.7129 | 138 | 122 | 5.4% | 7.3% | 145.452 | 128.588 | 0.01 | 0.02 | -1686.4 | 162.316 | 1.442% | 148.074 | 130.906 | 0.01 | 0.02 | -1716.8 | 165.242 | 1.587% | 144.2% | 0.9634% | 0.9784% | 0.9934% | 1.008% | 1.023% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.129% | 1.144% | 1.159% | 1.174% | 1.189% | 1.204% | 1.219% | 1.234% | 1.249% | 0.00039014 | 0.00039623 | 0.00040231 | 0.0004084 | 0.00041449 | 0.00042057 | 0.00042666 | 0.00043274 | 0.00043883 | 0.00044492 | 0.000451 | 0.00045709 | 0.00046318 | 0.00046926 | 0.00047535 | 0.00048143 | 0.00048752 | 0.00049361 | 0.00049969 | 0.00050578
| 10282347 | BMH003 | BMH | 16448385 | 16448389 | 1.177 | 144.1974 | -37.7374 | 138 | 121 | 5.4% | 7.3% | 145.452 | 127.534 | 0.01 | 0.02 | -1791.8 | 163.37 | 1.416% | 148.074 | 129.833 | 0.01 | 0.02 | -1824.1 | 166.315 | 1.552% | 141.6% | 0.9607% | 0.9749% | 0.989% | 1.003% | 1.017% | 1.031% | 1.046% | 1.06% | 1.074% | 1.088% | 1.102% | 1.116% | 1.13% | 1.145% | 1.159% | 1.173% | 1.187% | 1.201% | 1.215% | 1.229% | 0.00038907 | 0.00039479 | 0.00040052 | 0.00040625 | 0.00041198 | 0.00041771 | 0.00042344 | 0.00042916 | 0.00043489 | 0.00044062 | 0.00044635 | 0.00045208 | 0.00045781 | 0.00046353 | 0.00046926 | 0.00047499 | 0.00048072 | 0.00048645 | 0.00049218 | 0.0004979
| 10282348 | BMH003 | BMH | 161364370 | 16448385 | 0.23945 | 144.1977 | -37.7348 | 138 | 121 | 5.4% | 7.3% | 145.452 | 127.534 | 0.01 | 0.02 | -1791.8 | 163.37 | 1.416% | 148.074 | 129.833 | 0.01 | 0.02 | -1824.1 | 166.315 | 1.552% | 141.6% | 0.9607% | 0.9749% | 0.989% | 1.003% | 1.017% | 1.031% | 1.046% | 1.06% | 1.074% | 1.088% | 1.102% | 1.116% | 1.13% | 1.145% | 1.159% | 1.173% | 1.187% | 1.201% | 1.215% | 1.229% | 0.00038907 | 0.00039479 | 0.00040052 | 0.00040625 | 0.00041198 | 0.00041771 | 0.00042344 | 0.00042916 | 0.00043489 | 0.00044062 | 0.00044635 | 0.00045208 | 0.00045781 | 0.00046353 | 0.00046926 | 0.00047499 | 0.00048072 | 0.00048645 | 0.00049218 | 0.0004979
| 10283440 | HSM002 | HSM | 16453504 | 16453508 | 1.5734 | 141.8416 | -36.9041 | 123 | 104 | 6.3% | 8.8% | 130.749 | 110.552 | 0.01 | 0.02 | -2019.7 | 150.946 | 1.384% | 131.979 | 113.152 | 0.01 | 0.02 | -1882.7 | 150.806 | 1.477% | 138.4% | 0.9574% | 0.9705% | 0.9835% | 0.9966% | 1.01% | 1.023% | 1.036% | 1.049% | 1.062% | 1.075% | 1.088% | 1.101% | 1.114% | 1.127% | 1.14% | 1.153% | 1.166% | 1.179% | 1.192% | 1.205% | 0.00038773 | 0.00039302 | 0.0003983 | 0.00040359 | 0.00040887 | 0.00041416 | 0.00041944 | 0.00042473 | 0.00043001 | 0.00043529 | 0.00044058 | 0.00044586 | 0.00045115 | 0.00045643 | 0.00046172 | 0.000467 | 0.00047229 | 0.00047757 | 0.00048286 | 0.00048814
| 10284224 | HSM004 | HSM | 16457214 | 16457218 | 2.5767 | 141.4985 | -36.8887 | 116 | 99.2 | 6.3% | 8.8% | 123.308 | 105.4496 | 0.01 | 0.02 | -1785.84 | 141.1664 | 1.409% | 124.468 | 107.9296 | 0.01 | 0.02 | -1653.84 | 141.0064 | 1.512% | 140.9% | 0.96% | 0.9739% | 0.9879% | 1.002% | 1.016% | 1.03% | 1.044% | 1.057% | 1.071% | 1.085% | 1.099% | 1.113% | 1.127% | 1.141% | 1.155% | 1.169% | 1.183% | 1.197% | 1.211% | 1.224% | 0.00038879 | 0.00039443 | 0.00040006 | 0.0004057 | 0.00041134 | 0.00041697 | 0.00042261 | 0.00042824 | 0.00043388 | 0.00043952 | 0.00044515 | 0.00045079 | 0.00045643 | 0.00046206 | 0.0004677 | 0.00047334 | 0.00047897 | 0.00048461 | 0.00049024 | 0.00049588
| 10284360 | HSM004 | HSM | 16457873 | 162940897 | 0.493 | 141.601 | -36.9073 | 120 | 102 | 6.3% | 8.8% | 127.56 | 108.426 | 0.01 | 0.02 | -1913.4 | 146.694 | 1.395% | 128.76 | 110.976 | 0.01 | 0.02 | -1778.4 | 146.544 | 1.493% | 139.5% | 0.9586% | 0.972% | 0.9855% | 0.9989% | 1.012% | 1.026% | 1.039% | 1.053% | 1.066% | 1.08% | 1.093% | 1.106% | 1.12% | 1.133% | 1.147% | 1.16% | 1.174% | 1.187% | 1.2% | 1.214% | 0.00038821 | 0.00039365 | 0.00039909 | 0.00040453 | 0.00040998 | 0.00041542 | 0.00042086 | 0.0004263 | 0.00043174 | 0.00043719 | 0.00044263 | 0.00044807 | 0.00045351 | 0.00045895 | 0.0004644 | 0.00046984 | 0.00047528 | 0.00048072 | 0.00048616 | 0.00049161
| 10290339 | NHL015 | NHL | 89524255 | 16489052 | 0.3822 | 141.9399 | -35.8272 | 137 | 114 | 6.3% | 8.8% | 145.631 | 121.182 | 0.01 | 0.02 | -2444.9 | 170.08 | 1.353% | 147.001 | 124.032 | 0.01 | 0.02 | -2296.9 | 169.97 | 1.435% | 135.3% | 0.9543% | 0.9663% | 0.9783% | 0.9903% | 1.002% | 1.014% | 1.026% | 1.038% | 1.05% | 1.062% | 1.074% | 1.086% | 1.098% | 1.11% | 1.122% | 1.134% | 1.146% | 1.158% | 1.17% | 1.182% | 0.00038647 | 0.00039133 | 0.00039619 | 0.00040106 | 0.00040592 | 0.00041078 | 0.00041564 | 0.0004205 | 0.00042537 | 0.00043023 | 0.00043509 | 0.00043995 | 0.00044482 | 0.00044968 | 0.00045454 | 0.0004594 | 0.00046427 | 0.00046913 | 0.00047399 | 0.00047885
| 10298697 | HSM004 | HSM | 16529615 | 16529611 | 0.59231 | 141.5428 | -36.9845 | 117 | 99.6 | 6.3% | 8.8% | 124.371 | 105.8748 | 0.01 | 0.02 | -1849.62 | 142.8672 | 1.399% | 125.541 | 108.3648 | 0.01 | 0.02 | -1717.62 | 142.7172 | 1.497% | 139.9% | 0.9589% | 0.9725% | 0.986% | 0.9996% | 1.013% | 1.027% | 1.04% | 1.054% | 1.067% | 1.081% | 1.094% | 1.108% | 1.122% | 1.135% | 1.149% | 1.162% | 1.176% | 1.189% | 1.203% | 1.216% | 0.00038835 | 0.00039384 | 0.00039933 | 0.00040481 | 0.0004103 | 0.00041579 | 0.00042128 | 0.00042677 | 0.00043226 | 0.00043775 | 0.00044324 | 0.00044873 | 0.00045422 | 0.0004597 | 0.00046519 | 0.00047068 | 0.00047617 | 0.00048166 | 0.00048715 | 0.00049264
| 10298698 | HSM004 | HSM | 108127045 | 16529615 | 0.50779 | 141.542 | -36.9827 | 117 | 99.6 | 6.3% | 8.8% | 124.371 | 105.8748 | 0.01 | 0.02 | -1849.62 | 142.8672 | 1.399% | 125.541 | 108.3648 | 0.01 | 0.02 | -1717.62 | 142.7172 | 1.497% | 139.9% | 0.9589% | 0.9725% | 0.986% | 0.9996% | 1.013% | 1.027% | 1.04% | 1.054% | 1.067% | 1.081% | 1.094% | 1.108% | 1.122% | 1.135% | 1.149% | 1.162% | 1.176% | 1.189% | 1.203% | 1.216% | 0.00038835 | 0.00039384 | 0.00039933 | 0.00040481 | 0.0004103 | 0.00041579 | 0.00042128 | 0.00042677 | 0.00043226 | 0.00043775 | 0.00044324 | 0.00044873 | 0.00045422 | 0.0004597 | 0.00046519 | 0.00047068 | 0.00047617 | 0.00048166 | 0.00048715 | 0.00049264
| 10308414 | BBD014 | BBD | 16574318 | 178575460 | 0.31211 | 143.3267 | -34.9308 | 108 | 95.9 | 6.3% | 8.8% | 114.804 | 101.9417 | 0.01 | 0.02 | -1286.23 | 127.6663 | 1.529% | 115.884 | 104.3392 | 0.01 | 0.02 | -1154.48 | 127.4288 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039374 | 0.00040103 | 0.00040831 | 0.0004156 | 0.00042288 | 0.00043017 | 0.00043746 | 0.00044474 | 0.00045203 | 0.00045931 | 0.0004666 | 0.00047389 | 0.00048117 | 0.00048846 | 0.00049574 | 0.00050303 | 0.00051031 | 0.0005176 | 0.00052489 | 0.00053217
| 10315838 | CTN003 | CTN | 88030204 | 16609194 | 0.26079 | 143.5364 | -35.9036 | 104 | 92.8 | 6.3% | 8.8% | 110.552 | 98.6464 | 0.01 | 0.02 | -1190.56 | 122.4576 | 1.55% | 111.592 | 100.9664 | 0.01 | 0.02 | -1062.56 | 122.2176 | 1.715% | 155% | 0.9744% | 0.9931% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.105% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.236% | 1.255% | 1.274% | 1.293% | 1.311% | 1.33% | 0.00039462 | 0.0004022 | 0.00040978 | 0.00041736 | 0.00042494 | 0.00043252 | 0.0004401 | 0.00044768 | 0.00045526 | 0.00046284 | 0.00047042 | 0.000478 | 0.00048558 | 0.00049316 | 0.00050074 | 0.00050832 | 0.0005159 | 0.00052348 | 0.00053106 | 0.00053864
| 10315839 | CTN003 | CTN | 16609194 | 16609279 | 2.4505 | 143.5391 | -35.9039 | 104 | 92.8 | 6.3% | 8.8% | 110.552 | 98.6464 | 0.01 | 0.02 | -1190.56 | 122.4576 | 1.55% | 111.592 | 100.9664 | 0.01 | 0.02 | -1062.56 | 122.2176 | 1.715% | 155% | 0.9744% | 0.9931% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.105% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.236% | 1.255% | 1.274% | 1.293% | 1.311% | 1.33% | 0.00039462 | 0.0004022 | 0.00040978 | 0.00041736 | 0.00042494 | 0.00043252 | 0.0004401 | 0.00044768 | 0.00045526 | 0.00046284 | 0.00047042 | 0.000478 | 0.00048558 | 0.00049316 | 0.00050074 | 0.00050832 | 0.0005159 | 0.00052348 | 0.00053106 | 0.00053864
| 10315842 | CTN003 | CTN | 88030204 | 16609212 | 0.6905 | 143.5342 | -35.9045 | 104 | 92.8 | 6.3% | 8.8% | 110.552 | 98.6464 | 0.01 | 0.02 | -1190.56 | 122.4576 | 1.55% | 111.592 | 100.9664 | 0.01 | 0.02 | -1062.56 | 122.2176 | 1.715% | 155% | 0.9744% | 0.9931% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.105% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.236% | 1.255% | 1.274% | 1.293% | 1.311% | 1.33% | 0.00039462 | 0.0004022 | 0.00040978 | 0.00041736 | 0.00042494 | 0.00043252 | 0.0004401 | 0.00044768 | 0.00045526 | 0.00046284 | 0.00047042 | 0.000478 | 0.00048558 | 0.00049316 | 0.00050074 | 0.00050832 | 0.0005159 | 0.00052348 | 0.00053106 | 0.00053864
| 10315843 | CTN003 | CTN | 16609212 | 16609216 | 1.9907 | 143.5322 | -35.9065 | 104 | 92.8 | 6.3% | 8.8% | 110.552 | 98.6464 | 0.01 | 0.02 | -1190.56 | 122.4576 | 1.55% | 111.592 | 100.9664 | 0.01 | 0.02 | -1062.56 | 122.2176 | 1.715% | 155% | 0.9744% | 0.9931% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.105% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.236% | 1.255% | 1.274% | 1.293% | 1.311% | 1.33% | 0.00039462 | 0.0004022 | 0.00040978 | 0.00041736 | 0.00042494 | 0.00043252 | 0.0004401 | 0.00044768 | 0.00045526 | 0.00046284 | 0.00047042 | 0.000478 | 0.00048558 | 0.00049316 | 0.00050074 | 0.00050832 | 0.0005159 | 0.00052348 | 0.00053106 | 0.00053864
| 10315857 | CTN003 | CTN | 16609279 | 16609275 | 2.2068 | 143.5425 | -35.9042 | 104 | 92.8 | 6.3% | 8.8% | 110.552 | 98.6464 | 0.01 | 0.02 | -1190.56 | 122.4576 | 1.55% | 111.592 | 100.9664 | 0.01 | 0.02 | -1062.56 | 122.2176 | 1.715% | 155% | 0.9744% | 0.9931% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.105% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.236% | 1.255% | 1.274% | 1.293% | 1.311% | 1.33% | 0.00039462 | 0.0004022 | 0.00040978 | 0.00041736 | 0.00042494 | 0.00043252 | 0.0004401 | 0.00044768 | 0.00045526 | 0.00046284 | 0.00047042 | 0.000478 | 0.00048558 | 0.00049316 | 0.00050074 | 0.00050832 | 0.0005159 | 0.00052348 | 0.00053106 | 0.00053864
| 10315858 | CTN003 | CTN | 16609275 | 16609283 | 0.74259 | 143.546 | -35.9046 | 104 | 92.8 | 6.3% | 8.8% | 110.552 | 98.6464 | 0.01 | 0.02 | -1190.56 | 122.4576 | 1.55% | 111.592 | 100.9664 | 0.01 | 0.02 | -1062.56 | 122.2176 | 1.715% | 155% | 0.9744% | 0.9931% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.105% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.236% | 1.255% | 1.274% | 1.293% | 1.311% | 1.33% | 0.00039462 | 0.0004022 | 0.00040978 | 0.00041736 | 0.00042494 | 0.00043252 | 0.0004401 | 0.00044768 | 0.00045526 | 0.00046284 | 0.00047042 | 0.000478 | 0.00048558 | 0.00049316 | 0.00050074 | 0.00050832 | 0.0005159 | 0.00052348 | 0.00053106 | 0.00053864
| 10315859 | CTN003 | CTN | 16609283 | 192401945 | 0.61345 | 143.549 | -35.9049 | 104 | 92.8 | 6.3% | 8.8% | 110.552 | 98.6464 | 0.01 | 0.02 | -1190.56 | 122.4576 | 1.55% | 111.592 | 100.9664 | 0.01 | 0.02 | -1062.56 | 122.2176 | 1.715% | 155% | 0.9744% | 0.9931% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.105% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.236% | 1.255% | 1.274% | 1.293% | 1.311% | 1.33% | 0.00039462 | 0.0004022 | 0.00040978 | 0.00041736 | 0.00042494 | 0.00043252 | 0.0004401 | 0.00044768 | 0.00045526 | 0.00046284 | 0.00047042 | 0.000478 | 0.00048558 | 0.00049316 | 0.00050074 | 0.00050832 | 0.0005159 | 0.00052348 | 0.00053106 | 0.00053864
| 10318791 | MRO005 | MRO | 16623798 | 17095780 | 2.1576 | 143.5125 | -36.8116 | 109 | 97.8 | 6.3% | 8.8% | 115.867 | 103.9614 | 0.01 | 0.02 | -1190.56 | 127.7726 | 1.577% | 116.957 | 106.4064 | 0.01 | 0.02 | -1055.06 | 127.5076 | 1.754% | 157.7% | 0.9771% | 0.9967% | 1.016% | 1.036% | 1.056% | 1.075% | 1.095% | 1.114% | 1.134% | 1.154% | 1.173% | 1.193% | 1.213% | 1.232% | 1.252% | 1.271% | 1.291% | 1.311% | 1.33% | 1.35% | 0.00039571 | 0.00040366 | 0.0004116 | 0.00041955 | 0.00042749 | 0.00043544 | 0.00044338 | 0.00045132 | 0.00045927 | 0.00046721 | 0.00047516 | 0.0004831 | 0.00049105 | 0.00049899 | 0.00050694 | 0.00051488 | 0.00052282 | 0.00053077 | 0.00053871 | 0.00054666
| 10320316 | STL006 | STL | 16631138 | 191393374 | 0.52084 | 142.5251 | -36.968 | 118 | 103 | 6.3% | 8.8% | 125.434 | 109.489 | 0.01 | 0.02 | -1594.5 | 141.379 | 1.466% | 126.614 | 112.064 | 0.01 | 0.02 | -1455 | 141.164 | 1.592% | 146.6% | 0.9658% | 0.9817% | 0.9976% | 1.013% | 1.029% | 1.045% | 1.061% | 1.077% | 1.093% | 1.109% | 1.124% | 1.14% | 1.156% | 1.172% | 1.188% | 1.204% | 1.22% | 1.235% | 1.251% | 1.267% | 0.00039115 | 0.00039757 | 0.00040399 | 0.00041041 | 0.00041683 | 0.00042325 | 0.00042968 | 0.0004361 | 0.00044252 | 0.00044894 | 0.00045536 | 0.00046178 | 0.0004682 | 0.00047463 | 0.00048105 | 0.00048747 | 0.00049389 | 0.00050031 | 0.00050673 | 0.00051316
| 10320317 | STL006 | STL | 16631142 | 16631138 | 1.5809 | 142.5215 | -36.968 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10320318 | STL006 | STL | 190993655 | 16631142 | 2.2343 | 142.5175 | -36.968 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10320465 | STL005 | STL | 16631768 | 16631760 | 0.19019 | 142.5763 | -37.0294 | 121 | 106 | 6.3% | 8.8% | 128.623 | 112.678 | 0.01 | 0.02 | -1594.5 | 144.568 | 1.478% | 129.833 | 115.328 | 0.01 | 0.02 | -1450.5 | 144.338 | 1.609% | 147.8% | 0.9671% | 0.9833% | 0.9996% | 1.016% | 1.032% | 1.048% | 1.065% | 1.081% | 1.097% | 1.113% | 1.13% | 1.146% | 1.162% | 1.178% | 1.195% | 1.211% | 1.227% | 1.243% | 1.26% | 1.276% | 0.00039164 | 0.00039822 | 0.00040481 | 0.00041139 | 0.00041798 | 0.00042456 | 0.00043114 | 0.00043773 | 0.00044431 | 0.0004509 | 0.00045748 | 0.00046407 | 0.00047065 | 0.00047724 | 0.00048382 | 0.00049041 | 0.00049699 | 0.00050358 | 0.00051016 | 0.00051675
| 10327284 | WSFWMN | WMN | 16664059 | 16664055 | 1.2657 | 142.6631 | -34.7629 | 112 | 97.8 | 6.3% | 8.8% | 119.056 | 103.9614 | 0.01 | 0.02 | -1509.46 | 134.1506 | 1.467% | 120.176 | 106.4064 | 0.01 | 0.02 | -1376.96 | 133.9456 | 1.594% | 146.7% | 0.966% | 0.9819% | 0.9978% | 1.014% | 1.03% | 1.045% | 1.061% | 1.077% | 1.093% | 1.109% | 1.125% | 1.141% | 1.157% | 1.173% | 1.189% | 1.204% | 1.22% | 1.236% | 1.252% | 1.268% | 0.0003912 | 0.00039764 | 0.00040407 | 0.00041051 | 0.00041695 | 0.00042339 | 0.00042983 | 0.00043627 | 0.0004427 | 0.00044914 | 0.00045558 | 0.00046202 | 0.00046846 | 0.0004749 | 0.00048133 | 0.00048777 | 0.00049421 | 0.00050065 | 0.00050709 | 0.00051353
| 10327285 | WSFWMN | WMN | 16664063 | 16664059 | 0.65492 | 142.6624 | -34.7641 | 112 | 97.8 | 6.3% | 8.8% | 119.056 | 103.9614 | 0.01 | 0.02 | -1509.46 | 134.1506 | 1.467% | 120.176 | 106.4064 | 0.01 | 0.02 | -1376.96 | 133.9456 | 1.594% | 146.7% | 0.966% | 0.9819% | 0.9978% | 1.014% | 1.03% | 1.045% | 1.061% | 1.077% | 1.093% | 1.109% | 1.125% | 1.141% | 1.157% | 1.173% | 1.189% | 1.204% | 1.22% | 1.236% | 1.252% | 1.268% | 0.0003912 | 0.00039764 | 0.00040407 | 0.00041051 | 0.00041695 | 0.00042339 | 0.00042983 | 0.00043627 | 0.0004427 | 0.00044914 | 0.00045558 | 0.00046202 | 0.00046846 | 0.0004749 | 0.00048133 | 0.00048777 | 0.00049421 | 0.00050065 | 0.00050709 | 0.00051353
| 10327294 | WSFWMN | WMN | 16664107 | 16664103 | 0.74261 | 142.6542 | -34.7692 | 112 | 97.8 | 6.3% | 8.8% | 119.056 | 103.9614 | 0.01 | 0.02 | -1509.46 | 134.1506 | 1.467% | 120.176 | 106.4064 | 0.01 | 0.02 | -1376.96 | 133.9456 | 1.594% | 146.7% | 0.966% | 0.9819% | 0.9978% | 1.014% | 1.03% | 1.045% | 1.061% | 1.077% | 1.093% | 1.109% | 1.125% | 1.141% | 1.157% | 1.173% | 1.189% | 1.204% | 1.22% | 1.236% | 1.252% | 1.268% | 0.0003912 | 0.00039764 | 0.00040407 | 0.00041051 | 0.00041695 | 0.00042339 | 0.00042983 | 0.00043627 | 0.0004427 | 0.00044914 | 0.00045558 | 0.00046202 | 0.00046846 | 0.0004749 | 0.00048133 | 0.00048777 | 0.00049421 | 0.00050065 | 0.00050709 | 0.00051353
| 10327298 | WSFWMN | WMN | 16664107 | 16664112 | 0.45456 | 142.6535 | -34.7692 | 112 | 97.8 | 6.3% | 8.8% | 119.056 | 103.9614 | 0.01 | 0.02 | -1509.46 | 134.1506 | 1.467% | 120.176 | 106.4064 | 0.01 | 0.02 | -1376.96 | 133.9456 | 1.594% | 146.7% | 0.966% | 0.9819% | 0.9978% | 1.014% | 1.03% | 1.045% | 1.061% | 1.077% | 1.093% | 1.109% | 1.125% | 1.141% | 1.157% | 1.173% | 1.189% | 1.204% | 1.22% | 1.236% | 1.252% | 1.268% | 0.0003912 | 0.00039764 | 0.00040407 | 0.00041051 | 0.00041695 | 0.00042339 | 0.00042983 | 0.00043627 | 0.0004427 | 0.00044914 | 0.00045558 | 0.00046202 | 0.00046846 | 0.0004749 | 0.00048133 | 0.00048777 | 0.00049421 | 0.00050065 | 0.00050709 | 0.00051353
| 10327338 | WSFWMN | WMN | 161751526 | 162603213 | 0.34811 | 142.647 | -34.7715 | 110 | 96.4 | 6.3% | 8.8% | 116.93 | 102.4732 | 0.01 | 0.02 | -1445.68 | 131.3868 | 1.479% | 118.03 | 104.8832 | 0.01 | 0.02 | -1314.68 | 131.1768 | 1.611% | 147.9% | 0.9672% | 0.9835% | 0.9998% | 1.016% | 1.032% | 1.049% | 1.065% | 1.081% | 1.098% | 1.114% | 1.13% | 1.147% | 1.163% | 1.179% | 1.195% | 1.212% | 1.228% | 1.244% | 1.261% | 1.277% | 0.00039169 | 0.00039829 | 0.00040489 | 0.0004115 | 0.0004181 | 0.0004247 | 0.0004313 | 0.00043791 | 0.00044451 | 0.00045111 | 0.00045771 | 0.00046432 | 0.00047092 | 0.00047752 | 0.00048412 | 0.00049072 | 0.00049733 | 0.00050393 | 0.00051053 | 0.00051713
| 10328372 | HTN034 | KGTS | 16670768 | 16670764 | 0.51239 | 141.2386 | -37.7004 | 108 | 92.3 | 5.4% | 7.3% | 113.832 | 97.2842 | 0.01 | 0.02 | -1654.78 | 130.3798 | 1.352% | 115.884 | 99.0379 | 0.01 | 0.02 | -1684.61 | 132.7301 | 1.468% | 135.2% | 0.9542% | 0.9662% | 0.9782% | 0.9902% | 1.002% | 1.014% | 1.026% | 1.038% | 1.05% | 1.062% | 1.074% | 1.086% | 1.098% | 1.11% | 1.122% | 1.134% | 1.146% | 1.158% | 1.17% | 1.182% | 0.00038644 | 0.0003913 | 0.00039615 | 0.00040101 | 0.00040586 | 0.00041072 | 0.00041557 | 0.00042042 | 0.00042528 | 0.00043013 | 0.00043499 | 0.00043984 | 0.00044469 | 0.00044955 | 0.0004544 | 0.00045926 | 0.00046411 | 0.00046897 | 0.00047382 | 0.00047867
| 10328909 | TNA022 | TNA | 16672897 | 16672964 | 2.2651 | 144.5871 | -37.8155 | 121 | 106 | 5.4% | 7.3% | 127.534 | 111.724 | 0.01 | 0.02 | -1581 | 143.344 | 1.413% | 129.833 | 113.738 | 0.01 | 0.02 | -1609.5 | 145.928 | 1.549% | 141.3% | 0.9604% | 0.9745% | 0.9886% | 1.003% | 1.017% | 1.031% | 1.045% | 1.059% | 1.073% | 1.087% | 1.101% | 1.115% | 1.129% | 1.143% | 1.157% | 1.171% | 1.185% | 1.199% | 1.213% | 1.228% | 0.00038896 | 0.00039465 | 0.00040034 | 0.00040604 | 0.00041173 | 0.00041742 | 0.00042311 | 0.0004288 | 0.0004345 | 0.00044019 | 0.00044588 | 0.00045157 | 0.00045727 | 0.00046296 | 0.00046865 | 0.00047434 | 0.00048004 | 0.00048573 | 0.00049142 | 0.00049711
| 10329039 | TNA022 | TNA | 16673484 | 16673480 | 0.10366 | 144.6108 | -37.8353 | 122 | 106 | 5.4% | 7.3% | 128.588 | 111.724 | 0.01 | 0.02 | -1686.4 | 145.452 | 1.391% | 130.906 | 113.738 | 0.01 | 0.02 | -1716.8 | 148.074 | 1.519% | 139.1% | 0.9581% | 0.9714% | 0.9847% | 0.998% | 1.011% | 1.025% | 1.038% | 1.051% | 1.064% | 1.078% | 1.091% | 1.104% | 1.118% | 1.131% | 1.144% | 1.157% | 1.171% | 1.184% | 1.197% | 1.211% | 0.00038802 | 0.0003934 | 0.00039878 | 0.00040417 | 0.00040955 | 0.00041493 | 0.00042031 | 0.00042569 | 0.00043107 | 0.00043645 | 0.00044183 | 0.00044721 | 0.00045259 | 0.00045797 | 0.00046335 | 0.00046873 | 0.00047411 | 0.00047949 | 0.00048488 | 0.00049026
| 10331635 | CTN006 | CTN | 16684456 | 193221987 | 0.31692 | 143.3179 | -36.3297 | 98 | 88.7 | 6.3% | 8.8% | 104.174 | 94.2881 | 0.01 | 0.02 | -988.59 | 114.0599 | 1.625% | 105.154 | 96.5056 | 0.01 | 0.02 | -864.84 | 113.8024 | 1.827% | 162.5% | 0.982% | 1.003% | 1.024% | 1.046% | 1.067% | 1.088% | 1.109% | 1.131% | 1.152% | 1.173% | 1.194% | 1.216% | 1.237% | 1.258% | 1.279% | 1.301% | 1.322% | 1.343% | 1.364% | 1.386% | 0.00039769 | 0.00040629 | 0.00041489 | 0.00042349 | 0.00043209 | 0.0004407 | 0.0004493 | 0.0004579 | 0.0004665 | 0.0004751 | 0.00048371 | 0.00049231 | 0.00050091 | 0.00050951 | 0.00051811 | 0.00052671 | 0.00053532 | 0.00054392 | 0.00055252 | 0.00056112
| 10331638 | CTN006 | CTN | 16684460 | 16684478 | 0.35151 | 143.3184 | -36.3321 | 98 | 88.7 | 6.3% | 8.8% | 104.174 | 94.2881 | 0.01 | 0.02 | -988.59 | 114.0599 | 1.625% | 105.154 | 96.5056 | 0.01 | 0.02 | -864.84 | 113.8024 | 1.827% | 162.5% | 0.982% | 1.003% | 1.024% | 1.046% | 1.067% | 1.088% | 1.109% | 1.131% | 1.152% | 1.173% | 1.194% | 1.216% | 1.237% | 1.258% | 1.279% | 1.301% | 1.322% | 1.343% | 1.364% | 1.386% | 0.00039769 | 0.00040629 | 0.00041489 | 0.00042349 | 0.00043209 | 0.0004407 | 0.0004493 | 0.0004579 | 0.0004665 | 0.0004751 | 0.00048371 | 0.00049231 | 0.00050091 | 0.00050951 | 0.00051811 | 0.00052671 | 0.00053532 | 0.00054392 | 0.00055252 | 0.00056112
| 10331644 | CTN006 | CTN | 16684486 | 16684490 | 0.31501 | 143.3272 | -36.3359 | 98.6 | 89.3 | 6.3% | 8.8% | 104.8118 | 94.9259 | 0.01 | 0.02 | -988.59 | 114.6977 | 1.628% | 105.7978 | 97.1584 | 0.01 | 0.02 | -863.94 | 114.4372 | 1.833% | 162.8% | 0.9824% | 1.004% | 1.025% | 1.046% | 1.068% | 1.089% | 1.111% | 1.132% | 1.153% | 1.175% | 1.196% | 1.217% | 1.239% | 1.26% | 1.282% | 1.303% | 1.324% | 1.346% | 1.367% | 1.388% | 0.00039785 | 0.0004065 | 0.00041515 | 0.00042381 | 0.00043246 | 0.00044112 | 0.00044977 | 0.00045843 | 0.00046708 | 0.00047574 | 0.00048439 | 0.00049304 | 0.0005017 | 0.00051035 | 0.00051901 | 0.00052766 | 0.00053632 | 0.00054497 | 0.00055363 | 0.00056228
| 10331648 | CTN006 | CTN | 16684506 | 16684510 | 0.45865 | 143.3129 | -36.3393 | 98 | 88.7 | 6.3% | 8.8% | 104.174 | 94.2881 | 0.01 | 0.02 | -988.59 | 114.0599 | 1.625% | 105.154 | 96.5056 | 0.01 | 0.02 | -864.84 | 113.8024 | 1.827% | 162.5% | 0.982% | 1.003% | 1.024% | 1.046% | 1.067% | 1.088% | 1.109% | 1.131% | 1.152% | 1.173% | 1.194% | 1.216% | 1.237% | 1.258% | 1.279% | 1.301% | 1.322% | 1.343% | 1.364% | 1.386% | 0.00039769 | 0.00040629 | 0.00041489 | 0.00042349 | 0.00043209 | 0.0004407 | 0.0004493 | 0.0004579 | 0.0004665 | 0.0004751 | 0.00048371 | 0.00049231 | 0.00050091 | 0.00050951 | 0.00051811 | 0.00052671 | 0.00053532 | 0.00054392 | 0.00055252 | 0.00056112
| 10334019 | SHL004 | SHL | 16694594 | 16694590 | 0.15815 | 143.5144 | -35.2243 | 107 | 94.9 | 6.3% | 8.8% | 113.741 | 100.8787 | 0.01 | 0.02 | -1286.23 | 126.6033 | 1.524% | 114.811 | 103.2512 | 0.01 | 0.02 | -1155.98 | 126.3708 | 1.676% | 152.4% | 0.9717% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.203% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.31% | 0.00039354 | 0.00040076 | 0.00040797 | 0.00041519 | 0.00042241 | 0.00042963 | 0.00043685 | 0.00044407 | 0.00045129 | 0.0004585 | 0.00046572 | 0.00047294 | 0.00048016 | 0.00048738 | 0.0004946 | 0.00050181 | 0.00050903 | 0.00051625 | 0.00052347 | 0.00053069
| 10334157 | SHL004 | SHL | 16695129 | 157074000 | 1.1452 | 143.4463 | -35.2195 | 107 | 95.1 | 6.3% | 8.8% | 113.741 | 101.0913 | 0.01 | 0.02 | -1264.97 | 126.3907 | 1.533% | 114.811 | 103.4688 | 0.01 | 0.02 | -1134.22 | 126.1532 | 1.689% | 153.3% | 0.9726% | 0.9908% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.19% | 1.208% | 1.226% | 1.245% | 1.263% | 1.281% | 1.299% | 1.317% | 0.0003939 | 0.00040124 | 0.00040858 | 0.00041592 | 0.00042326 | 0.0004306 | 0.00043794 | 0.00044528 | 0.00045262 | 0.00045996 | 0.0004673 | 0.00047464 | 0.00048198 | 0.00048932 | 0.00049666 | 0.000504 | 0.00051134 | 0.00051868 | 0.00052602 | 0.00053336
| 10334179 | SHL004 | SHL | 17655415 | 16695225 | 1.7415 | 143.4398 | -35.2186 | 107 | 95.1 | 6.3% | 8.8% | 113.741 | 101.0913 | 0.01 | 0.02 | -1264.97 | 126.3907 | 1.533% | 114.811 | 103.4688 | 0.01 | 0.02 | -1134.22 | 126.1532 | 1.689% | 153.3% | 0.9726% | 0.9908% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.19% | 1.208% | 1.226% | 1.245% | 1.263% | 1.281% | 1.299% | 1.317% | 0.0003939 | 0.00040124 | 0.00040858 | 0.00041592 | 0.00042326 | 0.0004306 | 0.00043794 | 0.00044528 | 0.00045262 | 0.00045996 | 0.0004673 | 0.00047464 | 0.00048198 | 0.00048932 | 0.00049666 | 0.000504 | 0.00051134 | 0.00051868 | 0.00052602 | 0.00053336
| 10334194 | SHL004 | SHL | 16695286 | 17693693 | 0.28456 | 143.4376 | -35.2175 | 107 | 95.1 | 6.3% | 8.8% | 113.741 | 101.0913 | 0.01 | 0.02 | -1264.97 | 126.3907 | 1.533% | 114.811 | 103.4688 | 0.01 | 0.02 | -1134.22 | 126.1532 | 1.689% | 153.3% | 0.9726% | 0.9908% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.19% | 1.208% | 1.226% | 1.245% | 1.263% | 1.281% | 1.299% | 1.317% | 0.0003939 | 0.00040124 | 0.00040858 | 0.00041592 | 0.00042326 | 0.0004306 | 0.00043794 | 0.00044528 | 0.00045262 | 0.00045996 | 0.0004673 | 0.00047464 | 0.00048198 | 0.00048932 | 0.00049666 | 0.000504 | 0.00051134 | 0.00051868 | 0.00052602 | 0.00053336
| 10334197 | SHL004 | SHL | 162602829 | 16695294 | 0.41603 | 143.4431 | -35.2195 | 107 | 95.1 | 6.3% | 8.8% | 113.741 | 101.0913 | 0.01 | 0.02 | -1264.97 | 126.3907 | 1.533% | 114.811 | 103.4688 | 0.01 | 0.02 | -1134.22 | 126.1532 | 1.689% | 153.3% | 0.9726% | 0.9908% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.19% | 1.208% | 1.226% | 1.245% | 1.263% | 1.281% | 1.299% | 1.317% | 0.0003939 | 0.00040124 | 0.00040858 | 0.00041592 | 0.00042326 | 0.0004306 | 0.00043794 | 0.00044528 | 0.00045262 | 0.00045996 | 0.0004673 | 0.00047464 | 0.00048198 | 0.00048932 | 0.00049666 | 0.000504 | 0.00051134 | 0.00051868 | 0.00052602 | 0.00053336
| 10334198 | SHL004 | SHL | 190233603 | 157074000 | 1.1439 | 143.4457 | -35.2204 | 107 | 95.1 | 6.3% | 8.8% | 113.741 | 101.0913 | 0.01 | 0.02 | -1264.97 | 126.3907 | 1.533% | 114.811 | 103.4688 | 0.01 | 0.02 | -1134.22 | 126.1532 | 1.689% | 153.3% | 0.9726% | 0.9908% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.19% | 1.208% | 1.226% | 1.245% | 1.263% | 1.281% | 1.299% | 1.317% | 0.0003939 | 0.00040124 | 0.00040858 | 0.00041592 | 0.00042326 | 0.0004306 | 0.00043794 | 0.00044528 | 0.00045262 | 0.00045996 | 0.0004673 | 0.00047464 | 0.00048198 | 0.00048932 | 0.00049666 | 0.000504 | 0.00051134 | 0.00051868 | 0.00052602 | 0.00053336
| 10334199 | SHL004 | SHL | 162602829 | 190233603 | 0.21796 | 143.4444 | -35.22 | 107 | 95.1 | 6.3% | 8.8% | 113.741 | 101.0913 | 0.01 | 0.02 | -1264.97 | 126.3907 | 1.533% | 114.811 | 103.4688 | 0.01 | 0.02 | -1134.22 | 126.1532 | 1.689% | 153.3% | 0.9726% | 0.9908% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.19% | 1.208% | 1.226% | 1.245% | 1.263% | 1.281% | 1.299% | 1.317% | 0.0003939 | 0.00040124 | 0.00040858 | 0.00041592 | 0.00042326 | 0.0004306 | 0.00043794 | 0.00044528 | 0.00045262 | 0.00045996 | 0.0004673 | 0.00047464 | 0.00048198 | 0.00048932 | 0.00049666 | 0.000504 | 0.00051134 | 0.00051868 | 0.00052602 | 0.00053336
| 10334201 | SHL004 | SHL | 42236359 | 190233596 | 0.29008 | 143.4483 | -35.2206 | 107 | 95.1 | 6.3% | 8.8% | 113.741 | 101.0913 | 0.01 | 0.02 | -1264.97 | 126.3907 | 1.533% | 114.811 | 103.4688 | 0.01 | 0.02 | -1134.22 | 126.1532 | 1.689% | 153.3% | 0.9726% | 0.9908% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.19% | 1.208% | 1.226% | 1.245% | 1.263% | 1.281% | 1.299% | 1.317% | 0.0003939 | 0.00040124 | 0.00040858 | 0.00041592 | 0.00042326 | 0.0004306 | 0.00043794 | 0.00044528 | 0.00045262 | 0.00045996 | 0.0004673 | 0.00047464 | 0.00048198 | 0.00048932 | 0.00049666 | 0.000504 | 0.00051134 | 0.00051868 | 0.00052602 | 0.00053336
| 10334243 | SHL004 | SHL | 16695481 | 16695467 | 3.0264 | 143.4503 | -35.2079 | 107 | 95 | 6.3% | 8.8% | 113.741 | 100.985 | 0.01 | 0.02 | -1275.6 | 126.497 | 1.528% | 114.811 | 103.36 | 0.01 | 0.02 | -1145.1 | 126.262 | 1.682% | 152.8% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039372 | 0.000401 | 0.00040827 | 0.00041555 | 0.00042283 | 0.00043011 | 0.00043739 | 0.00044467 | 0.00045195 | 0.00045923 | 0.0004665 | 0.00047378 | 0.00048106 | 0.00048834 | 0.00049562 | 0.0005029 | 0.00051018 | 0.00051745 | 0.00052473 | 0.00053201
| 10334245 | SHL004 | SHL | 16695481 | 16695476 | 1.3144 | 143.4504 | -35.2096 | 107 | 95 | 6.3% | 8.8% | 113.741 | 100.985 | 0.01 | 0.02 | -1275.6 | 126.497 | 1.528% | 114.811 | 103.36 | 0.01 | 0.02 | -1145.1 | 126.262 | 1.682% | 152.8% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039372 | 0.000401 | 0.00040827 | 0.00041555 | 0.00042283 | 0.00043011 | 0.00043739 | 0.00044467 | 0.00045195 | 0.00045923 | 0.0004665 | 0.00047378 | 0.00048106 | 0.00048834 | 0.00049562 | 0.0005029 | 0.00051018 | 0.00051745 | 0.00052473 | 0.00053201
| 10334849 | SHL004 | SHL | 16698074 | 16698078 | 0.21534 | 143.481 | -35.2808 | 105 | 93.3 | 6.3% | 8.8% | 111.615 | 99.1779 | 0.01 | 0.02 | -1243.71 | 124.0521 | 1.532% | 112.665 | 101.5104 | 0.01 | 0.02 | -1115.46 | 123.8196 | 1.687% | 153.2% | 0.9725% | 0.9906% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.099% | 1.117% | 1.135% | 1.153% | 1.172% | 1.19% | 1.208% | 1.226% | 1.244% | 1.262% | 1.28% | 1.298% | 1.316% | 0.00039386 | 0.00040118 | 0.00040851 | 0.00041584 | 0.00042316 | 0.00043049 | 0.00043781 | 0.00044514 | 0.00045246 | 0.00045979 | 0.00046712 | 0.00047444 | 0.00048177 | 0.00048909 | 0.00049642 | 0.00050374 | 0.00051107 | 0.0005184 | 0.00052572 | 0.00053305
| 10334851 | SHL004 | SHL | 190233546 | 16698082 | 0.48094 | 143.4794 | -35.2804 | 105 | 93.3 | 6.3% | 8.8% | 111.615 | 99.1779 | 0.01 | 0.02 | -1243.71 | 124.0521 | 1.532% | 112.665 | 101.5104 | 0.01 | 0.02 | -1115.46 | 123.8196 | 1.687% | 153.2% | 0.9725% | 0.9906% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.099% | 1.117% | 1.135% | 1.153% | 1.172% | 1.19% | 1.208% | 1.226% | 1.244% | 1.262% | 1.28% | 1.298% | 1.316% | 0.00039386 | 0.00040118 | 0.00040851 | 0.00041584 | 0.00042316 | 0.00043049 | 0.00043781 | 0.00044514 | 0.00045246 | 0.00045979 | 0.00046712 | 0.00047444 | 0.00048177 | 0.00048909 | 0.00049642 | 0.00050374 | 0.00051107 | 0.0005184 | 0.00052572 | 0.00053305
| 10334853 | SHL004 | SHL | 16698094 | 16698090 | 0.61497 | 143.4779 | -35.2807 | 105 | 93.3 | 6.3% | 8.8% | 111.615 | 99.1779 | 0.01 | 0.02 | -1243.71 | 124.0521 | 1.532% | 112.665 | 101.5104 | 0.01 | 0.02 | -1115.46 | 123.8196 | 1.687% | 153.2% | 0.9725% | 0.9906% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.099% | 1.117% | 1.135% | 1.153% | 1.172% | 1.19% | 1.208% | 1.226% | 1.244% | 1.262% | 1.28% | 1.298% | 1.316% | 0.00039386 | 0.00040118 | 0.00040851 | 0.00041584 | 0.00042316 | 0.00043049 | 0.00043781 | 0.00044514 | 0.00045246 | 0.00045979 | 0.00046712 | 0.00047444 | 0.00048177 | 0.00048909 | 0.00049642 | 0.00050374 | 0.00051107 | 0.0005184 | 0.00052572 | 0.00053305
| 10334854 | SHL004 | SHL | 16698094 | 16698098 | 0.55742 | 143.4771 | -35.2808 | 105 | 93.3 | 6.3% | 8.8% | 111.615 | 99.1779 | 0.01 | 0.02 | -1243.71 | 124.0521 | 1.532% | 112.665 | 101.5104 | 0.01 | 0.02 | -1115.46 | 123.8196 | 1.687% | 153.2% | 0.9725% | 0.9906% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.099% | 1.117% | 1.135% | 1.153% | 1.172% | 1.19% | 1.208% | 1.226% | 1.244% | 1.262% | 1.28% | 1.298% | 1.316% | 0.00039386 | 0.00040118 | 0.00040851 | 0.00041584 | 0.00042316 | 0.00043049 | 0.00043781 | 0.00044514 | 0.00045246 | 0.00045979 | 0.00046712 | 0.00047444 | 0.00048177 | 0.00048909 | 0.00049642 | 0.00050374 | 0.00051107 | 0.0005184 | 0.00052572 | 0.00053305
| 10334855 | SHL004 | SHL | 16698098 | 16698103 | 1.9833 | 143.476 | -35.2809 | 105 | 93.3 | 6.3% | 8.8% | 111.615 | 99.1779 | 0.01 | 0.02 | -1243.71 | 124.0521 | 1.532% | 112.665 | 101.5104 | 0.01 | 0.02 | -1115.46 | 123.8196 | 1.687% | 153.2% | 0.9725% | 0.9906% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.099% | 1.117% | 1.135% | 1.153% | 1.172% | 1.19% | 1.208% | 1.226% | 1.244% | 1.262% | 1.28% | 1.298% | 1.316% | 0.00039386 | 0.00040118 | 0.00040851 | 0.00041584 | 0.00042316 | 0.00043049 | 0.00043781 | 0.00044514 | 0.00045246 | 0.00045979 | 0.00046712 | 0.00047444 | 0.00048177 | 0.00048909 | 0.00049642 | 0.00050374 | 0.00051107 | 0.0005184 | 0.00052572 | 0.00053305
| 10334857 | SHL004 | SHL | 16698103 | 16698107 | 1.062 | 143.4749 | -35.2808 | 105 | 93.6 | 6.3% | 8.8% | 111.615 | 99.4968 | 0.01 | 0.02 | -1211.82 | 123.7332 | 1.546% | 112.665 | 101.8368 | 0.01 | 0.02 | -1082.82 | 123.4932 | 1.708% | 154.6% | 0.974% | 0.9925% | 1.011% | 1.03% | 1.048% | 1.067% | 1.085% | 1.104% | 1.122% | 1.141% | 1.16% | 1.178% | 1.197% | 1.215% | 1.234% | 1.252% | 1.271% | 1.29% | 1.308% | 1.327% | 0.00039444 | 0.00040196 | 0.00040947 | 0.00041699 | 0.00042451 | 0.00043203 | 0.00043955 | 0.00044707 | 0.00045459 | 0.0004621 | 0.00046962 | 0.00047714 | 0.00048466 | 0.00049218 | 0.0004997 | 0.00050722 | 0.00051473 | 0.00052225 | 0.00052977 | 0.00053729
| 10334858 | SHL004 | SHL | 16698111 | 16698107 | 0.40838 | 143.4741 | -35.2807 | 105 | 93.6 | 6.3% | 8.8% | 111.615 | 99.4968 | 0.01 | 0.02 | -1211.82 | 123.7332 | 1.546% | 112.665 | 101.8368 | 0.01 | 0.02 | -1082.82 | 123.4932 | 1.708% | 154.6% | 0.974% | 0.9925% | 1.011% | 1.03% | 1.048% | 1.067% | 1.085% | 1.104% | 1.122% | 1.141% | 1.16% | 1.178% | 1.197% | 1.215% | 1.234% | 1.252% | 1.271% | 1.29% | 1.308% | 1.327% | 0.00039444 | 0.00040196 | 0.00040947 | 0.00041699 | 0.00042451 | 0.00043203 | 0.00043955 | 0.00044707 | 0.00045459 | 0.0004621 | 0.00046962 | 0.00047714 | 0.00048466 | 0.00049218 | 0.0004997 | 0.00050722 | 0.00051473 | 0.00052225 | 0.00052977 | 0.00053729
| 10334859 | SHL004 | SHL | 16698111 | 162612642 | 0.29582 | 143.4741 | -35.2816 | 105 | 93.6 | 6.3% | 8.8% | 111.615 | 99.4968 | 0.01 | 0.02 | -1211.82 | 123.7332 | 1.546% | 112.665 | 101.8368 | 0.01 | 0.02 | -1082.82 | 123.4932 | 1.708% | 154.6% | 0.974% | 0.9925% | 1.011% | 1.03% | 1.048% | 1.067% | 1.085% | 1.104% | 1.122% | 1.141% | 1.16% | 1.178% | 1.197% | 1.215% | 1.234% | 1.252% | 1.271% | 1.29% | 1.308% | 1.327% | 0.00039444 | 0.00040196 | 0.00040947 | 0.00041699 | 0.00042451 | 0.00043203 | 0.00043955 | 0.00044707 | 0.00045459 | 0.0004621 | 0.00046962 | 0.00047714 | 0.00048466 | 0.00049218 | 0.0004997 | 0.00050722 | 0.00051473 | 0.00052225 | 0.00052977 | 0.00053729
| 10334929 | SHL004 | SHL | 16698421 | 17795910 | 0.30051 | 143.4735 | -35.2675 | 106 | 94.1 | 6.3% | 8.8% | 112.678 | 100.0283 | 0.01 | 0.02 | -1264.97 | 125.3277 | 1.528% | 113.738 | 102.3808 | 0.01 | 0.02 | -1135.72 | 125.0952 | 1.681% | 152.8% | 0.9721% | 0.9901% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.241% | 1.259% | 1.277% | 1.295% | 1.313% | 0.0003937 | 0.00040097 | 0.00040824 | 0.00041551 | 0.00042278 | 0.00043005 | 0.00043732 | 0.00044459 | 0.00045186 | 0.00045914 | 0.00046641 | 0.00047368 | 0.00048095 | 0.00048822 | 0.00049549 | 0.00050276 | 0.00051003 | 0.00051731 | 0.00052458 | 0.00053185
| 10334930 | SHL004 | SHL | 16698430 | 163047249 | 0.99208 | 143.4766 | -35.2667 | 106 | 93.9 | 6.3% | 8.8% | 112.678 | 99.8157 | 0.01 | 0.02 | -1286.23 | 125.5403 | 1.519% | 113.738 | 102.1632 | 0.01 | 0.02 | -1157.48 | 125.3128 | 1.669% | 151.9% | 0.9712% | 0.9889% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.165% | 1.183% | 1.201% | 1.218% | 1.236% | 1.254% | 1.271% | 1.289% | 1.307% | 0.00039333 | 0.00040049 | 0.00040764 | 0.00041479 | 0.00042194 | 0.00042909 | 0.00043624 | 0.00044339 | 0.00045054 | 0.00045769 | 0.00046485 | 0.000472 | 0.00047915 | 0.0004863 | 0.00049345 | 0.0005006 | 0.00050775 | 0.0005149 | 0.00052205 | 0.0005292
| 10334955 | SHL004 | SHL | 16698527 | 190273136 | 1.1892 | 143.4712 | -35.262 | 106 | 94.1 | 6.3% | 8.8% | 112.678 | 100.0283 | 0.01 | 0.02 | -1264.97 | 125.3277 | 1.528% | 113.738 | 102.3808 | 0.01 | 0.02 | -1135.72 | 125.0952 | 1.681% | 152.8% | 0.9721% | 0.9901% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.241% | 1.259% | 1.277% | 1.295% | 1.313% | 0.0003937 | 0.00040097 | 0.00040824 | 0.00041551 | 0.00042278 | 0.00043005 | 0.00043732 | 0.00044459 | 0.00045186 | 0.00045914 | 0.00046641 | 0.00047368 | 0.00048095 | 0.00048822 | 0.00049549 | 0.00050276 | 0.00051003 | 0.00051731 | 0.00052458 | 0.00053185
| 10335111 | SHL004 | SHL | 16699209 | 16699205 | 0.86088 | 143.4863 | -35.2476 | 106 | 94.4 | 6.3% | 8.8% | 112.678 | 100.3472 | 0.01 | 0.02 | -1233.08 | 125.0088 | 1.542% | 113.738 | 102.7072 | 0.01 | 0.02 | -1103.08 | 124.7688 | 1.701% | 154.2% | 0.9735% | 0.9919% | 1.01% | 1.029% | 1.047% | 1.066% | 1.084% | 1.102% | 1.121% | 1.139% | 1.158% | 1.176% | 1.195% | 1.213% | 1.231% | 1.25% | 1.268% | 1.287% | 1.305% | 1.323% | 0.00039426 | 0.00040172 | 0.00040918 | 0.00041664 | 0.0004241 | 0.00043156 | 0.00043902 | 0.00044647 | 0.00045393 | 0.00046139 | 0.00046885 | 0.00047631 | 0.00048377 | 0.00049123 | 0.00049869 | 0.00050615 | 0.00051361 | 0.00052107 | 0.00052853 | 0.00053599
| 10335133 | SHL004 | SHL | 16699307 | 16699298 | 0.53188 | 143.4821 | -35.2482 | 106 | 94.4 | 6.3% | 8.8% | 112.678 | 100.3472 | 0.01 | 0.02 | -1233.08 | 125.0088 | 1.542% | 113.738 | 102.7072 | 0.01 | 0.02 | -1103.08 | 124.7688 | 1.701% | 154.2% | 0.9735% | 0.9919% | 1.01% | 1.029% | 1.047% | 1.066% | 1.084% | 1.102% | 1.121% | 1.139% | 1.158% | 1.176% | 1.195% | 1.213% | 1.231% | 1.25% | 1.268% | 1.287% | 1.305% | 1.323% | 0.00039426 | 0.00040172 | 0.00040918 | 0.00041664 | 0.0004241 | 0.00043156 | 0.00043902 | 0.00044647 | 0.00045393 | 0.00046139 | 0.00046885 | 0.00047631 | 0.00048377 | 0.00049123 | 0.00049869 | 0.00050615 | 0.00051361 | 0.00052107 | 0.00052853 | 0.00053599
| 10335134 | SHL004 | SHL | 190233662 | 16699298 | 1.2917 | 143.4808 | -35.2488 | 106 | 94.4 | 6.3% | 8.8% | 112.678 | 100.3472 | 0.01 | 0.02 | -1233.08 | 125.0088 | 1.542% | 113.738 | 102.7072 | 0.01 | 0.02 | -1103.08 | 124.7688 | 1.701% | 154.2% | 0.9735% | 0.9919% | 1.01% | 1.029% | 1.047% | 1.066% | 1.084% | 1.102% | 1.121% | 1.139% | 1.158% | 1.176% | 1.195% | 1.213% | 1.231% | 1.25% | 1.268% | 1.287% | 1.305% | 1.323% | 0.00039426 | 0.00040172 | 0.00040918 | 0.00041664 | 0.0004241 | 0.00043156 | 0.00043902 | 0.00044647 | 0.00045393 | 0.00046139 | 0.00046885 | 0.00047631 | 0.00048377 | 0.00049123 | 0.00049869 | 0.00050615 | 0.00051361 | 0.00052107 | 0.00052853 | 0.00053599
| 10335163 | SHL004 | SHL | 16699425 | 16699421 | 0.21906 | 143.4698 | -35.2575 | 106 | 94.1 | 6.3% | 8.8% | 112.678 | 100.0283 | 0.01 | 0.02 | -1264.97 | 125.3277 | 1.528% | 113.738 | 102.3808 | 0.01 | 0.02 | -1135.72 | 125.0952 | 1.681% | 152.8% | 0.9721% | 0.9901% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.241% | 1.259% | 1.277% | 1.295% | 1.313% | 0.0003937 | 0.00040097 | 0.00040824 | 0.00041551 | 0.00042278 | 0.00043005 | 0.00043732 | 0.00044459 | 0.00045186 | 0.00045914 | 0.00046641 | 0.00047368 | 0.00048095 | 0.00048822 | 0.00049549 | 0.00050276 | 0.00051003 | 0.00051731 | 0.00052458 | 0.00053185
| 10335335 | SHL004 | SHL | 16791619 | 16700182 | 0.14228 | 143.4713 | -35.2455 | 106 | 94.6 | 6.3% | 8.8% | 112.678 | 100.5598 | 0.01 | 0.02 | -1211.82 | 124.7962 | 1.551% | 113.738 | 102.9248 | 0.01 | 0.02 | -1081.32 | 124.5512 | 1.716% | 155.1% | 0.9745% | 0.9932% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.106% | 1.124% | 1.143% | 1.162% | 1.181% | 1.199% | 1.218% | 1.237% | 1.256% | 1.274% | 1.293% | 1.312% | 1.331% | 0.00039465 | 0.00040224 | 0.00040983 | 0.00041742 | 0.00042501 | 0.0004326 | 0.00044019 | 0.00044778 | 0.00045537 | 0.00046296 | 0.00047055 | 0.00047814 | 0.00048573 | 0.00049332 | 0.00050091 | 0.0005085 | 0.00051609 | 0.00052368 | 0.00053127 | 0.00053886
| 10335353 | SHL004 | SHL | 16700272 | 16818500 | 0.10252 | 143.4707 | -35.2538 | 106 | 94.1 | 6.3% | 8.8% | 112.678 | 100.0283 | 0.01 | 0.02 | -1264.97 | 125.3277 | 1.528% | 113.738 | 102.3808 | 0.01 | 0.02 | -1135.72 | 125.0952 | 1.681% | 152.8% | 0.9721% | 0.9901% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.241% | 1.259% | 1.277% | 1.295% | 1.313% | 0.0003937 | 0.00040097 | 0.00040824 | 0.00041551 | 0.00042278 | 0.00043005 | 0.00043732 | 0.00044459 | 0.00045186 | 0.00045914 | 0.00046641 | 0.00047368 | 0.00048095 | 0.00048822 | 0.00049549 | 0.00050276 | 0.00051003 | 0.00051731 | 0.00052458 | 0.00053185
| 10335473 | SHL004 | SHL | 16700900 | 16700905 | 0.61995 | 143.5322 | -35.2877 | 105 | 93.7 | 6.3% | 8.8% | 111.615 | 99.6031 | 0.01 | 0.02 | -1201.19 | 123.6269 | 1.551% | 112.665 | 101.9456 | 0.01 | 0.02 | -1071.94 | 123.3844 | 1.715% | 155.1% | 0.9745% | 0.9932% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.106% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.237% | 1.255% | 1.274% | 1.293% | 1.312% | 1.33% | 0.00039464 | 0.00040222 | 0.00040981 | 0.00041739 | 0.00042498 | 0.00043256 | 0.00044015 | 0.00044773 | 0.00045532 | 0.0004629 | 0.00047049 | 0.00047807 | 0.00048566 | 0.00049324 | 0.00050083 | 0.00050841 | 0.000516 | 0.00052358 | 0.00053117 | 0.00053875
| 10335478 | SHL004 | SHL | 16700935 | 190346299 | 0.77817 | 143.5315 | -35.2844 | 105 | 93.7 | 6.3% | 8.8% | 111.615 | 99.6031 | 0.01 | 0.02 | -1201.19 | 123.6269 | 1.551% | 112.665 | 101.9456 | 0.01 | 0.02 | -1071.94 | 123.3844 | 1.715% | 155.1% | 0.9745% | 0.9932% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.106% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.237% | 1.255% | 1.274% | 1.293% | 1.312% | 1.33% | 0.00039464 | 0.00040222 | 0.00040981 | 0.00041739 | 0.00042498 | 0.00043256 | 0.00044015 | 0.00044773 | 0.00045532 | 0.0004629 | 0.00047049 | 0.00047807 | 0.00048566 | 0.00049324 | 0.00050083 | 0.00050841 | 0.000516 | 0.00052358 | 0.00053117 | 0.00053875
| 10335641 | SHL004 | SHL | 16701588 | 16701592 | 1.1729 | 143.5335 | -35.2774 | 105 | 93.7 | 6.3% | 8.8% | 111.615 | 99.6031 | 0.01 | 0.02 | -1201.19 | 123.6269 | 1.551% | 112.665 | 101.9456 | 0.01 | 0.02 | -1071.94 | 123.3844 | 1.715% | 155.1% | 0.9745% | 0.9932% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.106% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.237% | 1.255% | 1.274% | 1.293% | 1.312% | 1.33% | 0.00039464 | 0.00040222 | 0.00040981 | 0.00041739 | 0.00042498 | 0.00043256 | 0.00044015 | 0.00044773 | 0.00045532 | 0.0004629 | 0.00047049 | 0.00047807 | 0.00048566 | 0.00049324 | 0.00050083 | 0.00050841 | 0.000516 | 0.00052358 | 0.00053117 | 0.00053875
| 10335642 | SHL004 | SHL | 16701592 | 16701596 | 0.82758 | 143.5335 | -35.2764 | 105 | 93.7 | 6.3% | 8.8% | 111.615 | 99.6031 | 0.01 | 0.02 | -1201.19 | 123.6269 | 1.551% | 112.665 | 101.9456 | 0.01 | 0.02 | -1071.94 | 123.3844 | 1.715% | 155.1% | 0.9745% | 0.9932% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.106% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.237% | 1.255% | 1.274% | 1.293% | 1.312% | 1.33% | 0.00039464 | 0.00040222 | 0.00040981 | 0.00041739 | 0.00042498 | 0.00043256 | 0.00044015 | 0.00044773 | 0.00045532 | 0.0004629 | 0.00047049 | 0.00047807 | 0.00048566 | 0.00049324 | 0.00050083 | 0.00050841 | 0.000516 | 0.00052358 | 0.00053117 | 0.00053875
| 10335643 | SHL004 | SHL | 16701596 | 16701600 | 1.5639 | 143.5335 | -35.2753 | 105 | 93.7 | 6.3% | 8.8% | 111.615 | 99.6031 | 0.01 | 0.02 | -1201.19 | 123.6269 | 1.551% | 112.665 | 101.9456 | 0.01 | 0.02 | -1071.94 | 123.3844 | 1.715% | 155.1% | 0.9745% | 0.9932% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.106% | 1.124% | 1.143% | 1.162% | 1.18% | 1.199% | 1.218% | 1.237% | 1.255% | 1.274% | 1.293% | 1.312% | 1.33% | 0.00039464 | 0.00040222 | 0.00040981 | 0.00041739 | 0.00042498 | 0.00043256 | 0.00044015 | 0.00044773 | 0.00045532 | 0.0004629 | 0.00047049 | 0.00047807 | 0.00048566 | 0.00049324 | 0.00050083 | 0.00050841 | 0.000516 | 0.00052358 | 0.00053117 | 0.00053875
| 10335708 | SHL004 | SHL | 16701852 | 16701857 | 0.26248 | 143.5593 | -35.2461 | 106 | 94.4 | 6.3% | 8.8% | 112.678 | 100.3472 | 0.01 | 0.02 | -1233.08 | 125.0088 | 1.542% | 113.738 | 102.7072 | 0.01 | 0.02 | -1103.08 | 124.7688 | 1.701% | 154.2% | 0.9735% | 0.9919% | 1.01% | 1.029% | 1.047% | 1.066% | 1.084% | 1.102% | 1.121% | 1.139% | 1.158% | 1.176% | 1.195% | 1.213% | 1.231% | 1.25% | 1.268% | 1.287% | 1.305% | 1.323% | 0.00039426 | 0.00040172 | 0.00040918 | 0.00041664 | 0.0004241 | 0.00043156 | 0.00043902 | 0.00044647 | 0.00045393 | 0.00046139 | 0.00046885 | 0.00047631 | 0.00048377 | 0.00049123 | 0.00049869 | 0.00050615 | 0.00051361 | 0.00052107 | 0.00052853 | 0.00053599
| 10337277 | FNS013 | FNS | 16708580 | 16708572 | 0.80719 | 144.4038 | -38.0233 | 109 | 95.7 | 5.4% | 7.3% | 114.886 | 100.8678 | 0.01 | 0.02 | -1401.82 | 128.9042 | 1.42% | 116.957 | 102.6861 | 0.01 | 0.02 | -1427.09 | 131.2279 | 1.558% | 142% | 0.9611% | 0.9754% | 0.9897% | 1.004% | 1.018% | 1.033% | 1.047% | 1.061% | 1.075% | 1.09% | 1.104% | 1.118% | 1.132% | 1.147% | 1.161% | 1.175% | 1.19% | 1.204% | 1.218% | 1.232% | 0.00038923 | 0.00039501 | 0.0004008 | 0.00040658 | 0.00041236 | 0.00041815 | 0.00042393 | 0.00042971 | 0.0004355 | 0.00044128 | 0.00044706 | 0.00045285 | 0.00045863 | 0.00046441 | 0.0004702 | 0.00047598 | 0.00048176 | 0.00048755 | 0.00049333 | 0.00049911
| 10337280 | FNS013 | FNS | 77733390 | 16708580 | 0.82735 | 144.403 | -38.0233 | 109 | 95.7 | 5.4% | 7.3% | 114.886 | 100.8678 | 0.01 | 0.02 | -1401.82 | 128.9042 | 1.42% | 116.957 | 102.6861 | 0.01 | 0.02 | -1427.09 | 131.2279 | 1.558% | 142% | 0.9611% | 0.9754% | 0.9897% | 1.004% | 1.018% | 1.033% | 1.047% | 1.061% | 1.075% | 1.09% | 1.104% | 1.118% | 1.132% | 1.147% | 1.161% | 1.175% | 1.19% | 1.204% | 1.218% | 1.232% | 0.00038923 | 0.00039501 | 0.0004008 | 0.00040658 | 0.00041236 | 0.00041815 | 0.00042393 | 0.00042971 | 0.0004355 | 0.00044128 | 0.00044706 | 0.00045285 | 0.00045863 | 0.00046441 | 0.0004702 | 0.00047598 | 0.00048176 | 0.00048755 | 0.00049333 | 0.00049911
| 10337583 | FNS022 | FNS | 16710331 | 16710335 | 0.7669 | 144.5137 | -37.9816 | 113 | 99.5 | 5.4% | 7.3% | 119.102 | 104.873 | 0.01 | 0.02 | -1422.9 | 133.331 | 1.429% | 121.249 | 106.7635 | 0.01 | 0.02 | -1448.55 | 135.7345 | 1.569% | 142.9% | 0.962% | 0.9766% | 0.9912% | 1.006% | 1.02% | 1.035% | 1.05% | 1.064% | 1.079% | 1.093% | 1.108% | 1.122% | 1.137% | 1.152% | 1.166% | 1.181% | 1.195% | 1.21% | 1.225% | 1.239% | 0.0003896 | 0.00039551 | 0.00040141 | 0.00040732 | 0.00041323 | 0.00041913 | 0.00042504 | 0.00043095 | 0.00043685 | 0.00044276 | 0.00044867 | 0.00045457 | 0.00046048 | 0.00046639 | 0.00047229 | 0.0004782 | 0.00048411 | 0.00049001 | 0.00049592 | 0.00050183
| 10337585 | FNS022 | FNS | 16710335 | 16710345 | 0.37936 | 144.513 | -37.9812 | 113 | 99.5 | 5.4% | 7.3% | 119.102 | 104.873 | 0.01 | 0.02 | -1422.9 | 133.331 | 1.429% | 121.249 | 106.7635 | 0.01 | 0.02 | -1448.55 | 135.7345 | 1.569% | 142.9% | 0.962% | 0.9766% | 0.9912% | 1.006% | 1.02% | 1.035% | 1.05% | 1.064% | 1.079% | 1.093% | 1.108% | 1.122% | 1.137% | 1.152% | 1.166% | 1.181% | 1.195% | 1.21% | 1.225% | 1.239% | 0.0003896 | 0.00039551 | 0.00040141 | 0.00040732 | 0.00041323 | 0.00041913 | 0.00042504 | 0.00043095 | 0.00043685 | 0.00044276 | 0.00044867 | 0.00045457 | 0.00046048 | 0.00046639 | 0.00047229 | 0.0004782 | 0.00048411 | 0.00049001 | 0.00049592 | 0.00050183
| 10337818 | GHP022 | GHP | 16711324 | 16711329 | 1.3046 | 144.2804 | -37.856 | 124 | 109 | 5.4% | 7.3% | 130.696 | 114.886 | 0.01 | 0.02 | -1581 | 146.506 | 1.424% | 133.052 | 116.957 | 0.01 | 0.02 | -1609.5 | 149.147 | 1.562% | 142.4% | 0.9615% | 0.9759% | 0.9903% | 1.005% | 1.019% | 1.034% | 1.048% | 1.062% | 1.077% | 1.091% | 1.106% | 1.12% | 1.134% | 1.149% | 1.163% | 1.178% | 1.192% | 1.206% | 1.221% | 1.235% | 0.00038938 | 0.00039522 | 0.00040105 | 0.00040688 | 0.00041272 | 0.00041855 | 0.00042438 | 0.00043022 | 0.00043605 | 0.00044188 | 0.00044772 | 0.00045355 | 0.00045938 | 0.00046522 | 0.00047105 | 0.00047688 | 0.00048272 | 0.00048855 | 0.00049438 | 0.00050022
| 10338170 | WBE023 | WBE | 16712817 | 187561466 | 2.5778 | 144.5703 | -37.919 | 118 | 103 | 5.4% | 7.3% | 124.372 | 108.562 | 0.01 | 0.02 | -1581 | 140.182 | 1.403% | 126.614 | 110.519 | 0.01 | 0.02 | -1609.5 | 142.709 | 1.535% | 140.3% | 0.9594% | 0.9731% | 0.9868% | 1.001% | 1.014% | 1.028% | 1.042% | 1.055% | 1.069% | 1.083% | 1.096% | 1.11% | 1.124% | 1.138% | 1.151% | 1.165% | 1.179% | 1.192% | 1.206% | 1.22% | 0.00038854 | 0.00039409 | 0.00039964 | 0.00040519 | 0.00041074 | 0.00041629 | 0.00042184 | 0.00042739 | 0.00043294 | 0.0004385 | 0.00044405 | 0.0004496 | 0.00045515 | 0.0004607 | 0.00046625 | 0.0004718 | 0.00047735 | 0.00048291 | 0.00048846 | 0.00049401
| 10338172 | WBE023 | WBE | 16712825 | 190921372 | 0.88753 | 144.5713 | -37.9135 | 118 | 103 | 5.4% | 7.3% | 124.372 | 108.562 | 0.01 | 0.02 | -1581 | 140.182 | 1.403% | 126.614 | 110.519 | 0.01 | 0.02 | -1609.5 | 142.709 | 1.535% | 140.3% | 0.9594% | 0.9731% | 0.9868% | 1.001% | 1.014% | 1.028% | 1.042% | 1.055% | 1.069% | 1.083% | 1.096% | 1.11% | 1.124% | 1.138% | 1.151% | 1.165% | 1.179% | 1.192% | 1.206% | 1.22% | 0.00038854 | 0.00039409 | 0.00039964 | 0.00040519 | 0.00041074 | 0.00041629 | 0.00042184 | 0.00042739 | 0.00043294 | 0.0004385 | 0.00044405 | 0.0004496 | 0.00045515 | 0.0004607 | 0.00046625 | 0.0004718 | 0.00047735 | 0.00048291 | 0.00048846 | 0.00049401
| 10339279 | STN011 | STN | 16721236 | 16721232 | 0.67173 | 145.4535 | -36.3991 | 116 | 102 | 6.3% | 8.8% | 123.308 | 108.426 | 0.01 | 0.02 | -1488.2 | 138.19 | 1.491% | 124.468 | 110.976 | 0.01 | 0.02 | -1349.2 | 137.96 | 1.628% | 149.1% | 0.9684% | 0.9851% | 1.002% | 1.018% | 1.035% | 1.052% | 1.069% | 1.085% | 1.102% | 1.119% | 1.135% | 1.152% | 1.169% | 1.185% | 1.202% | 1.219% | 1.236% | 1.252% | 1.269% | 1.286% | 0.00039217 | 0.00039894 | 0.0004057 | 0.00041246 | 0.00041923 | 0.00042599 | 0.00043275 | 0.00043952 | 0.00044628 | 0.00045304 | 0.00045981 | 0.00046657 | 0.00047334 | 0.0004801 | 0.00048686 | 0.00049363 | 0.00050039 | 0.00050715 | 0.00051392 | 0.00052068
| 10341919 | SHL005 | SHL | 16735480 | 16735472 | 0.30008 | 143.6704 | -35.4206 | 104 | 92 | 6.3% | 8.8% | 110.552 | 97.796 | 0.01 | 0.02 | -1275.6 | 123.308 | 1.514% | 111.592 | 100.096 | 0.01 | 0.02 | -1149.6 | 123.088 | 1.66% | 151.4% | 0.9707% | 0.9881% | 1.006% | 1.023% | 1.041% | 1.058% | 1.075% | 1.093% | 1.11% | 1.128% | 1.145% | 1.163% | 1.18% | 1.198% | 1.215% | 1.233% | 1.25% | 1.268% | 1.285% | 1.303% | 0.00039311 | 0.00040018 | 0.00040725 | 0.00041433 | 0.0004214 | 0.00042848 | 0.00043555 | 0.00044263 | 0.0004497 | 0.00045678 | 0.00046385 | 0.00047093 | 0.000478 | 0.00048507 | 0.00049215 | 0.00049922 | 0.0005063 | 0.00051337 | 0.00052045 | 0.00052752
| 10341923 | SHL005 | SHL | 16735480 | 113626491 | 1.1653 | 143.6692 | -35.4199 | 104 | 92 | 6.3% | 8.8% | 110.552 | 97.796 | 0.01 | 0.02 | -1275.6 | 123.308 | 1.514% | 111.592 | 100.096 | 0.01 | 0.02 | -1149.6 | 123.088 | 1.66% | 151.4% | 0.9707% | 0.9881% | 1.006% | 1.023% | 1.041% | 1.058% | 1.075% | 1.093% | 1.11% | 1.128% | 1.145% | 1.163% | 1.18% | 1.198% | 1.215% | 1.233% | 1.25% | 1.268% | 1.285% | 1.303% | 0.00039311 | 0.00040018 | 0.00040725 | 0.00041433 | 0.0004214 | 0.00042848 | 0.00043555 | 0.00044263 | 0.0004497 | 0.00045678 | 0.00046385 | 0.00047093 | 0.000478 | 0.00048507 | 0.00049215 | 0.00049922 | 0.0005063 | 0.00051337 | 0.00052045 | 0.00052752
| 10342346 | KGT004 | KGTS | 96123213 | 16737245 | 0.66004 | 143.7593 | -35.5798 | 105 | 93.1 | 6.3% | 8.8% | 111.615 | 98.9653 | 0.01 | 0.02 | -1264.97 | 124.2647 | 1.523% | 112.665 | 101.2928 | 0.01 | 0.02 | -1137.22 | 124.0372 | 1.674% | 152.3% | 0.9716% | 0.9894% | 1.007% | 1.025% | 1.043% | 1.061% | 1.078% | 1.096% | 1.114% | 1.132% | 1.149% | 1.167% | 1.185% | 1.203% | 1.221% | 1.238% | 1.256% | 1.274% | 1.292% | 1.31% | 0.00039349 | 0.00040069 | 0.00040789 | 0.0004151 | 0.0004223 | 0.0004295 | 0.00043671 | 0.00044391 | 0.00045111 | 0.00045831 | 0.00046552 | 0.00047272 | 0.00047992 | 0.00048712 | 0.00049433 | 0.00050153 | 0.00050873 | 0.00051593 | 0.00052314 | 0.00053034
| 10342482 | KGT004 | KGTS | 128246808 | 16737773 | 0.4189 | 143.7623 | -35.5863 | 105 | 93.1 | 6.3% | 8.8% | 111.615 | 98.9653 | 0.01 | 0.02 | -1264.97 | 124.2647 | 1.523% | 112.665 | 101.2928 | 0.01 | 0.02 | -1137.22 | 124.0372 | 1.674% | 152.3% | 0.9716% | 0.9894% | 1.007% | 1.025% | 1.043% | 1.061% | 1.078% | 1.096% | 1.114% | 1.132% | 1.149% | 1.167% | 1.185% | 1.203% | 1.221% | 1.238% | 1.256% | 1.274% | 1.292% | 1.31% | 0.00039349 | 0.00040069 | 0.00040789 | 0.0004151 | 0.0004223 | 0.0004295 | 0.00043671 | 0.00044391 | 0.00045111 | 0.00045831 | 0.00046552 | 0.00047272 | 0.00047992 | 0.00048712 | 0.00049433 | 0.00050153 | 0.00050873 | 0.00051593 | 0.00052314 | 0.00053034
| 10342495 | KGT004 | KGTS | 16737820 | 16737816 | 0.43533 | 143.765 | -35.5921 | 105 | 93.1 | 6.3% | 8.8% | 111.615 | 98.9653 | 0.01 | 0.02 | -1264.97 | 124.2647 | 1.523% | 112.665 | 101.2928 | 0.01 | 0.02 | -1137.22 | 124.0372 | 1.674% | 152.3% | 0.9716% | 0.9894% | 1.007% | 1.025% | 1.043% | 1.061% | 1.078% | 1.096% | 1.114% | 1.132% | 1.149% | 1.167% | 1.185% | 1.203% | 1.221% | 1.238% | 1.256% | 1.274% | 1.292% | 1.31% | 0.00039349 | 0.00040069 | 0.00040789 | 0.0004151 | 0.0004223 | 0.0004295 | 0.00043671 | 0.00044391 | 0.00045111 | 0.00045831 | 0.00046552 | 0.00047272 | 0.00047992 | 0.00048712 | 0.00049433 | 0.00050153 | 0.00050873 | 0.00051593 | 0.00052314 | 0.00053034
| 10342875 | KGT004 | KGTS | 16739370 | 16739366 | 0.21446 | 143.8572 | -35.6547 | 108 | 95.1 | 6.3% | 8.8% | 114.804 | 101.0913 | 0.01 | 0.02 | -1371.27 | 128.5167 | 1.496% | 115.884 | 103.4688 | 0.01 | 0.02 | -1241.52 | 128.2992 | 1.635% | 149.6% | 0.9689% | 0.9858% | 1.003% | 1.02% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.121% | 1.138% | 1.155% | 1.171% | 1.188% | 1.205% | 1.222% | 1.239% | 1.256% | 1.273% | 1.29% | 0.00039238 | 0.00039922 | 0.00040605 | 0.00041289 | 0.00041972 | 0.00042655 | 0.00043339 | 0.00044022 | 0.00044706 | 0.00045389 | 0.00046073 | 0.00046756 | 0.00047439 | 0.00048123 | 0.00048806 | 0.0004949 | 0.00050173 | 0.00050856 | 0.0005154 | 0.00052223
| 10342881 | KGT004 | KGTS | 16739390 | 16739403 | 1.2536 | 143.8475 | -35.6556 | 107 | 94.8 | 6.3% | 8.8% | 113.741 | 100.7724 | 0.01 | 0.02 | -1296.86 | 126.7096 | 1.52% | 114.811 | 103.1424 | 0.01 | 0.02 | -1166.86 | 126.4796 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.29% | 1.307% | 0.00039336 | 0.00040052 | 0.00040768 | 0.00041484 | 0.000422 | 0.00042916 | 0.00043632 | 0.00044347 | 0.00045063 | 0.00045779 | 0.00046495 | 0.00047211 | 0.00047927 | 0.00048643 | 0.00049359 | 0.00050075 | 0.00050791 | 0.00051507 | 0.00052223 | 0.00052939
| 10343245 | KGTSGSF | KGTS | 16740921 | 16740925 | 0.32884 | 143.8719 | -35.7355 | 109 | 95.6 | 6.3% | 8.8% | 115.867 | 101.6228 | 0.01 | 0.02 | -1424.42 | 130.1112 | 1.482% | 116.957 | 104.0128 | 0.01 | 0.02 | -1294.42 | 129.9012 | 1.615% | 148.2% | 0.9675% | 0.9839% | 1% | 1.017% | 1.033% | 1.049% | 1.066% | 1.082% | 1.099% | 1.115% | 1.131% | 1.148% | 1.164% | 1.181% | 1.197% | 1.213% | 1.23% | 1.246% | 1.263% | 1.279% | 0.0003918 | 0.00039844 | 0.00040508 | 0.00041172 | 0.00041836 | 0.000425 | 0.00043164 | 0.00043828 | 0.00044492 | 0.00045156 | 0.0004582 | 0.00046484 | 0.00047148 | 0.00047812 | 0.00048476 | 0.0004914 | 0.00049804 | 0.00050468 | 0.00051132 | 0.00051796
| 10343246 | KGTSGSF | KGTS | 16740925 | 16740929 | 0.75662 | 143.8703 | -35.7355 | 109 | 95.6 | 6.3% | 8.8% | 115.867 | 101.6228 | 0.01 | 0.02 | -1424.42 | 130.1112 | 1.482% | 116.957 | 104.0128 | 0.01 | 0.02 | -1294.42 | 129.9012 | 1.615% | 148.2% | 0.9675% | 0.9839% | 1% | 1.017% | 1.033% | 1.049% | 1.066% | 1.082% | 1.099% | 1.115% | 1.131% | 1.148% | 1.164% | 1.181% | 1.197% | 1.213% | 1.23% | 1.246% | 1.263% | 1.279% | 0.0003918 | 0.00039844 | 0.00040508 | 0.00041172 | 0.00041836 | 0.000425 | 0.00043164 | 0.00043828 | 0.00044492 | 0.00045156 | 0.0004582 | 0.00046484 | 0.00047148 | 0.00047812 | 0.00048476 | 0.0004914 | 0.00049804 | 0.00050468 | 0.00051132 | 0.00051796
| 10343647 | KGT004 | KGTS | 192864584 | 16742676 | 0.33271 | 143.8634 | -35.7973 | 110 | 96.7 | 6.3% | 8.8% | 116.93 | 102.7921 | 0.01 | 0.02 | -1413.79 | 131.0679 | 1.49% | 118.03 | 105.2096 | 0.01 | 0.02 | -1282.04 | 130.8504 | 1.626% | 149% | 0.9683% | 0.985% | 1.002% | 1.018% | 1.035% | 1.052% | 1.068% | 1.085% | 1.102% | 1.118% | 1.135% | 1.152% | 1.168% | 1.185% | 1.202% | 1.218% | 1.235% | 1.252% | 1.268% | 1.285% | 0.00039214 | 0.00039889 | 0.00040564 | 0.00041239 | 0.00041914 | 0.00042589 | 0.00043264 | 0.00043939 | 0.00044615 | 0.0004529 | 0.00045965 | 0.0004664 | 0.00047315 | 0.0004799 | 0.00048665 | 0.00049341 | 0.00050016 | 0.00050691 | 0.00051366 | 0.00052041
| 10343727 | KGT004 | KGTS | 194544165 | 16742978 | 0.48573 | 143.8571 | -35.7991 | 110 | 96.7 | 6.3% | 8.8% | 116.93 | 102.7921 | 0.01 | 0.02 | -1413.79 | 131.0679 | 1.49% | 118.03 | 105.2096 | 0.01 | 0.02 | -1282.04 | 130.8504 | 1.626% | 149% | 0.9683% | 0.985% | 1.002% | 1.018% | 1.035% | 1.052% | 1.068% | 1.085% | 1.102% | 1.118% | 1.135% | 1.152% | 1.168% | 1.185% | 1.202% | 1.218% | 1.235% | 1.252% | 1.268% | 1.285% | 0.00039214 | 0.00039889 | 0.00040564 | 0.00041239 | 0.00041914 | 0.00042589 | 0.00043264 | 0.00043939 | 0.00044615 | 0.0004529 | 0.00045965 | 0.0004664 | 0.00047315 | 0.0004799 | 0.00048665 | 0.00049341 | 0.00050016 | 0.00050691 | 0.00051366 | 0.00052041
| 10352910 | SHL005 | SHL | 16783079 | 16783089 | 1.4467 | 143.6151 | -35.3859 | 103 | 91.4 | 6.3% | 8.8% | 109.489 | 97.1582 | 0.01 | 0.02 | -1233.08 | 121.8198 | 1.526% | 110.519 | 99.4432 | 0.01 | 0.02 | -1107.58 | 121.5948 | 1.679% | 152.6% | 0.972% | 0.9899% | 1.008% | 1.026% | 1.044% | 1.061% | 1.079% | 1.097% | 1.115% | 1.133% | 1.151% | 1.169% | 1.187% | 1.205% | 1.223% | 1.24% | 1.258% | 1.276% | 1.294% | 1.312% | 0.00039363 | 0.00040087 | 0.00040812 | 0.00041537 | 0.00042262 | 0.00042987 | 0.00043711 | 0.00044436 | 0.00045161 | 0.00045886 | 0.00046611 | 0.00047336 | 0.0004806 | 0.00048785 | 0.0004951 | 0.00050235 | 0.0005096 | 0.00051684 | 0.00052409 | 0.00053134
| 10360536 | CTN006 | CTN | 16818219 | 16817841 | 0.57246 | 143.1321 | -36.6614 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10360621 | CTN006 | CTN | 16818207 | 17700753 | 0.21537 | 143.1445 | -36.6621 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10360625 | CTN006 | CTN | 16818231 | 16818235 | 0.55725 | 143.1414 | -36.6529 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10360626 | CTN006 | CTN | 16818243 | 16818239 | 0.68925 | 143.1511 | -36.6638 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10360627 | CTN006 | CTN | 16818239 | 16818247 | 2.1778 | 143.154 | -36.6629 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10360628 | CTN006 | CTN | 16818247 | 16818251 | 2.1169 | 143.1569 | -36.6616 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10363777 | OYN005 | RCTS | 16832691 | 16832784 | 0.23069 | 142.3788 | -35.1823 | 108 | 94.6 | 6.3% | 8.8% | 114.804 | 100.5598 | 0.01 | 0.02 | -1424.42 | 129.0482 | 1.478% | 115.884 | 102.9248 | 0.01 | 0.02 | -1295.92 | 128.8432 | 1.608% | 147.8% | 0.967% | 0.9833% | 0.9995% | 1.016% | 1.032% | 1.048% | 1.064% | 1.081% | 1.097% | 1.113% | 1.129% | 1.146% | 1.162% | 1.178% | 1.194% | 1.211% | 1.227% | 1.243% | 1.259% | 1.276% | 0.00039162 | 0.0003982 | 0.00040478 | 0.00041136 | 0.00041794 | 0.00042451 | 0.00043109 | 0.00043767 | 0.00044425 | 0.00045083 | 0.00045741 | 0.00046399 | 0.00047057 | 0.00047715 | 0.00048373 | 0.00049031 | 0.00049688 | 0.00050346 | 0.00051004 | 0.00051662
| 10364607 | CTN003 | CTN | 16836200 | 16836205 | 0.38977 | 143.1205 | -35.7586 | 104 | 93.5 | 6.3% | 8.8% | 110.552 | 99.3905 | 0.01 | 0.02 | -1116.15 | 121.7135 | 1.587% | 111.592 | 101.728 | 0.01 | 0.02 | -986.4 | 121.456 | 1.77% | 158.7% | 0.9782% | 0.9981% | 1.018% | 1.038% | 1.058% | 1.078% | 1.098% | 1.118% | 1.138% | 1.158% | 1.178% | 1.198% | 1.218% | 1.238% | 1.258% | 1.278% | 1.298% | 1.318% | 1.338% | 1.357% | 0.00039614 | 0.00040422 | 0.00041231 | 0.00042039 | 0.00042848 | 0.00043656 | 0.00044465 | 0.00045273 | 0.00046082 | 0.0004689 | 0.00047699 | 0.00048507 | 0.00049316 | 0.00050125 | 0.00050933 | 0.00051742 | 0.0005255 | 0.00053359 | 0.00054167 | 0.00054976
| 10366996 | MBN031 | MBN | 86136122 | 16845946 | 0.59303 | 141.5833 | -34.2637 | 101 | 87.2 | 6.3% | 8.8% | 107.363 | 92.6936 | 0.01 | 0.02 | -1466.94 | 122.0324 | 1.434% | 108.373 | 94.8736 | 0.01 | 0.02 | -1349.94 | 121.8724 | 1.546% | 143.4% | 0.9625% | 0.9773% | 0.992% | 1.007% | 1.022% | 1.036% | 1.051% | 1.066% | 1.081% | 1.095% | 1.11% | 1.125% | 1.14% | 1.154% | 1.169% | 1.184% | 1.199% | 1.213% | 1.228% | 1.243% | 0.0003898 | 0.00039578 | 0.00040175 | 0.00040773 | 0.0004137 | 0.00041968 | 0.00042565 | 0.00043163 | 0.0004376 | 0.00044357 | 0.00044955 | 0.00045552 | 0.0004615 | 0.00046747 | 0.00047345 | 0.00047942 | 0.00048539 | 0.00049137 | 0.00049734 | 0.00050332
| 10366997 | MBN031 | MBN | 16845946 | 86136126 | 0.843 | 141.5825 | -34.2649 | 101 | 87.2 | 6.3% | 8.8% | 107.363 | 92.6936 | 0.01 | 0.02 | -1466.94 | 122.0324 | 1.434% | 108.373 | 94.8736 | 0.01 | 0.02 | -1349.94 | 121.8724 | 1.546% | 143.4% | 0.9625% | 0.9773% | 0.992% | 1.007% | 1.022% | 1.036% | 1.051% | 1.066% | 1.081% | 1.095% | 1.11% | 1.125% | 1.14% | 1.154% | 1.169% | 1.184% | 1.199% | 1.213% | 1.228% | 1.243% | 0.0003898 | 0.00039578 | 0.00040175 | 0.00040773 | 0.0004137 | 0.00041968 | 0.00042565 | 0.00043163 | 0.0004376 | 0.00044357 | 0.00044955 | 0.00045552 | 0.0004615 | 0.00046747 | 0.00047345 | 0.00047942 | 0.00048539 | 0.00049137 | 0.00049734 | 0.00050332
| 10367014 | MBN031 | MBN | 86136046 | 16846009 | 0.12488 | 141.5965 | -34.2284 | 101 | 87.5 | 6.3% | 8.8% | 107.363 | 93.0125 | 0.01 | 0.02 | -1435.05 | 121.7135 | 1.443% | 108.373 | 95.2 | 0.01 | 0.02 | -1317.3 | 121.546 | 1.56% | 144.3% | 0.9635% | 0.9786% | 0.9937% | 1.009% | 1.024% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.129% | 1.144% | 1.16% | 1.175% | 1.19% | 1.205% | 1.22% | 1.235% | 1.25% | 0.0003902 | 0.00039631 | 0.00040242 | 0.00040852 | 0.00041463 | 0.00042074 | 0.00042685 | 0.00043295 | 0.00043906 | 0.00044517 | 0.00045127 | 0.00045738 | 0.00046349 | 0.0004696 | 0.0004757 | 0.00048181 | 0.00048792 | 0.00049402 | 0.00050013 | 0.00050624
| 10367015 | MBN031 | MBN | 16846009 | 86136050 | 0.17468 | 141.5961 | -34.2296 | 101 | 87.5 | 6.3% | 8.8% | 107.363 | 93.0125 | 0.01 | 0.02 | -1435.05 | 121.7135 | 1.443% | 108.373 | 95.2 | 0.01 | 0.02 | -1317.3 | 121.546 | 1.56% | 144.3% | 0.9635% | 0.9786% | 0.9937% | 1.009% | 1.024% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.129% | 1.144% | 1.16% | 1.175% | 1.19% | 1.205% | 1.22% | 1.235% | 1.25% | 0.0003902 | 0.00039631 | 0.00040242 | 0.00040852 | 0.00041463 | 0.00042074 | 0.00042685 | 0.00043295 | 0.00043906 | 0.00044517 | 0.00045127 | 0.00045738 | 0.00046349 | 0.0004696 | 0.0004757 | 0.00048181 | 0.00048792 | 0.00049402 | 0.00050013 | 0.00050624
| 10367016 | MBN031 | MBN | 77828966 | 16846017 | 1.0538 | 141.5977 | -34.2238 | 101 | 87.8 | 6.3% | 8.8% | 107.363 | 93.3314 | 0.01 | 0.02 | -1403.16 | 121.3946 | 1.453% | 108.373 | 95.5264 | 0.01 | 0.02 | -1284.66 | 121.2196 | 1.574% | 145.3% | 0.9645% | 0.98% | 0.9954% | 1.011% | 1.026% | 1.042% | 1.057% | 1.073% | 1.088% | 1.103% | 1.119% | 1.134% | 1.15% | 1.165% | 1.18% | 1.196% | 1.211% | 1.227% | 1.242% | 1.258% | 0.00039062 | 0.00039687 | 0.00040311 | 0.00040936 | 0.0004156 | 0.00042185 | 0.00042809 | 0.00043434 | 0.00044059 | 0.00044683 | 0.00045308 | 0.00045932 | 0.00046557 | 0.00047182 | 0.00047806 | 0.00048431 | 0.00049055 | 0.0004968 | 0.00050305 | 0.00050929
| 10367017 | MBN031 | MBN | 16846017 | 77828972 | 1.0552 | 141.5976 | -34.2251 | 101 | 87.5 | 6.3% | 8.8% | 107.363 | 93.0125 | 0.01 | 0.02 | -1435.05 | 121.7135 | 1.443% | 108.373 | 95.2 | 0.01 | 0.02 | -1317.3 | 121.546 | 1.56% | 144.3% | 0.9635% | 0.9786% | 0.9937% | 1.009% | 1.024% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.129% | 1.144% | 1.16% | 1.175% | 1.19% | 1.205% | 1.22% | 1.235% | 1.25% | 0.0003902 | 0.00039631 | 0.00040242 | 0.00040852 | 0.00041463 | 0.00042074 | 0.00042685 | 0.00043295 | 0.00043906 | 0.00044517 | 0.00045127 | 0.00045738 | 0.00046349 | 0.0004696 | 0.0004757 | 0.00048181 | 0.00048792 | 0.00049402 | 0.00050013 | 0.00050624
| 10367019 | MBN031 | MBN | 16846021 | 77828966 | 1.0819 | 141.5976 | -34.2226 | 101 | 87.8 | 6.3% | 8.8% | 107.363 | 93.3314 | 0.01 | 0.02 | -1403.16 | 121.3946 | 1.453% | 108.373 | 95.5264 | 0.01 | 0.02 | -1284.66 | 121.2196 | 1.574% | 145.3% | 0.9645% | 0.98% | 0.9954% | 1.011% | 1.026% | 1.042% | 1.057% | 1.073% | 1.088% | 1.103% | 1.119% | 1.134% | 1.15% | 1.165% | 1.18% | 1.196% | 1.211% | 1.227% | 1.242% | 1.258% | 0.00039062 | 0.00039687 | 0.00040311 | 0.00040936 | 0.0004156 | 0.00042185 | 0.00042809 | 0.00043434 | 0.00044059 | 0.00044683 | 0.00045308 | 0.00045932 | 0.00046557 | 0.00047182 | 0.00047806 | 0.00048431 | 0.00049055 | 0.0004968 | 0.00050305 | 0.00050929
| 10367159 | MBN031 | MBN | 52301636 | 16846375 | 1.7192 | 141.655 | -34.1985 | 104 | 90.4 | 6.3% | 8.8% | 110.552 | 96.0952 | 0.01 | 0.02 | -1445.68 | 125.0088 | 1.453% | 111.592 | 98.3552 | 0.01 | 0.02 | -1323.68 | 124.8288 | 1.574% | 145.3% | 0.9645% | 0.9799% | 0.9953% | 1.011% | 1.026% | 1.042% | 1.057% | 1.072% | 1.088% | 1.103% | 1.119% | 1.134% | 1.149% | 1.165% | 1.18% | 1.196% | 1.211% | 1.227% | 1.242% | 1.257% | 0.00039061 | 0.00039685 | 0.00040309 | 0.00040934 | 0.00041558 | 0.00042182 | 0.00042806 | 0.0004343 | 0.00044055 | 0.00044679 | 0.00045303 | 0.00045927 | 0.00046552 | 0.00047176 | 0.000478 | 0.00048424 | 0.00049048 | 0.00049673 | 0.00050297 | 0.00050921
| 10367160 | MBN031 | MBN | 16846375 | 52301643 | 0.94402 | 141.6531 | -34.1987 | 104 | 90.4 | 6.3% | 8.8% | 110.552 | 96.0952 | 0.01 | 0.02 | -1445.68 | 125.0088 | 1.453% | 111.592 | 98.3552 | 0.01 | 0.02 | -1323.68 | 124.8288 | 1.574% | 145.3% | 0.9645% | 0.9799% | 0.9953% | 1.011% | 1.026% | 1.042% | 1.057% | 1.072% | 1.088% | 1.103% | 1.119% | 1.134% | 1.149% | 1.165% | 1.18% | 1.196% | 1.211% | 1.227% | 1.242% | 1.257% | 0.00039061 | 0.00039685 | 0.00040309 | 0.00040934 | 0.00041558 | 0.00042182 | 0.00042806 | 0.0004343 | 0.00044055 | 0.00044679 | 0.00045303 | 0.00045927 | 0.00046552 | 0.00047176 | 0.000478 | 0.00048424 | 0.00049048 | 0.00049673 | 0.00050297 | 0.00050921
| 10367815 | HTN034 | KGTS | 16849113 | 16850805 | 1.6847 | 141.4426 | -37.6058 | 117 | 99.2 | 5.4% | 7.3% | 123.318 | 104.5568 | 0.01 | 0.02 | -1876.12 | 142.0792 | 1.337% | 125.541 | 106.4416 | 0.01 | 0.02 | -1909.94 | 144.6404 | 1.447% | 133.7% | 0.9526% | 0.9641% | 0.9755% | 0.987% | 0.9984% | 1.01% | 1.021% | 1.033% | 1.044% | 1.056% | 1.067% | 1.079% | 1.09% | 1.102% | 1.113% | 1.124% | 1.136% | 1.147% | 1.159% | 1.17% | 0.0003858 | 0.00039043 | 0.00039507 | 0.00039971 | 0.00040435 | 0.00040899 | 0.00041363 | 0.00041826 | 0.0004229 | 0.00042754 | 0.00043218 | 0.00043682 | 0.00044146 | 0.00044609 | 0.00045073 | 0.00045537 | 0.00046001 | 0.00046465 | 0.00046929 | 0.00047392
| 10367829 | HTN034 | KGTS | 16849174 | 16849169 | 0.10024 | 141.4341 | -37.595 | 118 | 100 | 5.4% | 7.3% | 124.372 | 105.4 | 0.01 | 0.02 | -1897.2 | 143.344 | 1.336% | 126.614 | 107.3 | 0.01 | 0.02 | -1931.4 | 145.928 | 1.446% | 133.6% | 0.9525% | 0.964% | 0.9754% | 0.9868% | 0.9982% | 1.01% | 1.021% | 1.033% | 1.044% | 1.055% | 1.067% | 1.078% | 1.09% | 1.101% | 1.112% | 1.124% | 1.135% | 1.147% | 1.158% | 1.17% | 0.00038576 | 0.00039039 | 0.00039501 | 0.00039964 | 0.00040426 | 0.00040889 | 0.00041352 | 0.00041814 | 0.00042277 | 0.00042739 | 0.00043202 | 0.00043665 | 0.00044127 | 0.0004459 | 0.00045052 | 0.00045515 | 0.00045978 | 0.0004644 | 0.00046903 | 0.00047365
| 10367836 | HTN034 | KGTS | 16849195 | 16849199 | 0.56677 | 141.4283 | -37.5903 | 118 | 100 | 5.4% | 7.3% | 124.372 | 105.4 | 0.01 | 0.02 | -1897.2 | 143.344 | 1.336% | 126.614 | 107.3 | 0.01 | 0.02 | -1931.4 | 145.928 | 1.446% | 133.6% | 0.9525% | 0.964% | 0.9754% | 0.9868% | 0.9982% | 1.01% | 1.021% | 1.033% | 1.044% | 1.055% | 1.067% | 1.078% | 1.09% | 1.101% | 1.112% | 1.124% | 1.135% | 1.147% | 1.158% | 1.17% | 0.00038576 | 0.00039039 | 0.00039501 | 0.00039964 | 0.00040426 | 0.00040889 | 0.00041352 | 0.00041814 | 0.00042277 | 0.00042739 | 0.00043202 | 0.00043665 | 0.00044127 | 0.0004459 | 0.00045052 | 0.00045515 | 0.00045978 | 0.0004644 | 0.00046903 | 0.00047365
| 10367934 | HTN034 | KGTS | 193885923 | 16849636 | 0.37713 | 141.3752 | -37.5591 | 117 | 99.2 | 5.4% | 7.3% | 123.318 | 104.5568 | 0.01 | 0.02 | -1876.12 | 142.0792 | 1.337% | 125.541 | 106.4416 | 0.01 | 0.02 | -1909.94 | 144.6404 | 1.447% | 133.7% | 0.9526% | 0.9641% | 0.9755% | 0.987% | 0.9984% | 1.01% | 1.021% | 1.033% | 1.044% | 1.056% | 1.067% | 1.079% | 1.09% | 1.102% | 1.113% | 1.124% | 1.136% | 1.147% | 1.159% | 1.17% | 0.0003858 | 0.00039043 | 0.00039507 | 0.00039971 | 0.00040435 | 0.00040899 | 0.00041363 | 0.00041826 | 0.0004229 | 0.00042754 | 0.00043218 | 0.00043682 | 0.00044146 | 0.00044609 | 0.00045073 | 0.00045537 | 0.00046001 | 0.00046465 | 0.00046929 | 0.00047392
| 10367937 | HTN034 | KGTS | 16849654 | 16849649 | 0.10386 | 141.3763 | -37.5575 | 117 | 99.2 | 5.4% | 7.3% | 123.318 | 104.5568 | 0.01 | 0.02 | -1876.12 | 142.0792 | 1.337% | 125.541 | 106.4416 | 0.01 | 0.02 | -1909.94 | 144.6404 | 1.447% | 133.7% | 0.9526% | 0.9641% | 0.9755% | 0.987% | 0.9984% | 1.01% | 1.021% | 1.033% | 1.044% | 1.056% | 1.067% | 1.079% | 1.09% | 1.102% | 1.113% | 1.124% | 1.136% | 1.147% | 1.159% | 1.17% | 0.0003858 | 0.00039043 | 0.00039507 | 0.00039971 | 0.00040435 | 0.00040899 | 0.00041363 | 0.00041826 | 0.0004229 | 0.00042754 | 0.00043218 | 0.00043682 | 0.00044146 | 0.00044609 | 0.00045073 | 0.00045537 | 0.00046001 | 0.00046465 | 0.00046929 | 0.00047392
| 10367938 | HTN034 | KGTS | 16849654 | 16849659 | 0.49167 | 141.3758 | -37.5568 | 117 | 99.2 | 5.4% | 7.3% | 123.318 | 104.5568 | 0.01 | 0.02 | -1876.12 | 142.0792 | 1.337% | 125.541 | 106.4416 | 0.01 | 0.02 | -1909.94 | 144.6404 | 1.447% | 133.7% | 0.9526% | 0.9641% | 0.9755% | 0.987% | 0.9984% | 1.01% | 1.021% | 1.033% | 1.044% | 1.056% | 1.067% | 1.079% | 1.09% | 1.102% | 1.113% | 1.124% | 1.136% | 1.147% | 1.159% | 1.17% | 0.0003858 | 0.00039043 | 0.00039507 | 0.00039971 | 0.00040435 | 0.00040899 | 0.00041363 | 0.00041826 | 0.0004229 | 0.00042754 | 0.00043218 | 0.00043682 | 0.00044146 | 0.00044609 | 0.00045073 | 0.00045537 | 0.00046001 | 0.00046465 | 0.00046929 | 0.00047392
| 10367939 | HTN034 | KGTS | 16849654 | 16849663 | 2.5509 | 141.377 | -37.5565 | 117 | 99.2 | 5.4% | 7.3% | 123.318 | 104.5568 | 0.01 | 0.02 | -1876.12 | 142.0792 | 1.337% | 125.541 | 106.4416 | 0.01 | 0.02 | -1909.94 | 144.6404 | 1.447% | 133.7% | 0.9526% | 0.9641% | 0.9755% | 0.987% | 0.9984% | 1.01% | 1.021% | 1.033% | 1.044% | 1.056% | 1.067% | 1.079% | 1.09% | 1.102% | 1.113% | 1.124% | 1.136% | 1.147% | 1.159% | 1.17% | 0.0003858 | 0.00039043 | 0.00039507 | 0.00039971 | 0.00040435 | 0.00040899 | 0.00041363 | 0.00041826 | 0.0004229 | 0.00042754 | 0.00043218 | 0.00043682 | 0.00044146 | 0.00044609 | 0.00045073 | 0.00045537 | 0.00046001 | 0.00046465 | 0.00046929 | 0.00047392
| 10367947 | HTN034 | KGTS | 16849693 | 16849697 | 1.5862 | 141.3817 | -37.5494 | 116 | 98.3 | 5.4% | 7.3% | 122.264 | 103.6082 | 0.01 | 0.02 | -1865.58 | 140.9198 | 1.336% | 124.468 | 105.4759 | 0.01 | 0.02 | -1899.21 | 143.4601 | 1.446% | 133.6% | 0.9525% | 0.964% | 0.9754% | 0.9868% | 0.9982% | 1.01% | 1.021% | 1.032% | 1.044% | 1.055% | 1.067% | 1.078% | 1.09% | 1.101% | 1.112% | 1.124% | 1.135% | 1.147% | 1.158% | 1.17% | 0.00038576 | 0.00039038 | 0.000395 | 0.00039963 | 0.00040425 | 0.00040888 | 0.0004135 | 0.00041813 | 0.00042275 | 0.00042738 | 0.000432 | 0.00043663 | 0.00044125 | 0.00044588 | 0.0004505 | 0.00045513 | 0.00045975 | 0.00046437 | 0.000469 | 0.00047362
| 10367948 | HTN034 | KGTS | 16849697 | 16849702 | 3.1602 | 141.3822 | -37.5482 | 116 | 98.3 | 5.4% | 7.3% | 122.264 | 103.6082 | 0.01 | 0.02 | -1865.58 | 140.9198 | 1.336% | 124.468 | 105.4759 | 0.01 | 0.02 | -1899.21 | 143.4601 | 1.446% | 133.6% | 0.9525% | 0.964% | 0.9754% | 0.9868% | 0.9982% | 1.01% | 1.021% | 1.032% | 1.044% | 1.055% | 1.067% | 1.078% | 1.09% | 1.101% | 1.112% | 1.124% | 1.135% | 1.147% | 1.158% | 1.17% | 0.00038576 | 0.00039038 | 0.000395 | 0.00039963 | 0.00040425 | 0.00040888 | 0.0004135 | 0.00041813 | 0.00042275 | 0.00042738 | 0.000432 | 0.00043663 | 0.00044125 | 0.00044588 | 0.0004505 | 0.00045513 | 0.00045975 | 0.00046437 | 0.000469 | 0.00047362
| 10367952 | HTN034 | KGTS | 16849714 | 16849718 | 0.74949 | 141.3844 | -37.5427 | 116 | 98.3 | 5.4% | 7.3% | 122.264 | 103.6082 | 0.01 | 0.02 | -1865.58 | 140.9198 | 1.336% | 124.468 | 105.4759 | 0.01 | 0.02 | -1899.21 | 143.4601 | 1.446% | 133.6% | 0.9525% | 0.964% | 0.9754% | 0.9868% | 0.9982% | 1.01% | 1.021% | 1.032% | 1.044% | 1.055% | 1.067% | 1.078% | 1.09% | 1.101% | 1.112% | 1.124% | 1.135% | 1.147% | 1.158% | 1.17% | 0.00038576 | 0.00039038 | 0.000395 | 0.00039963 | 0.00040425 | 0.00040888 | 0.0004135 | 0.00041813 | 0.00042275 | 0.00042738 | 0.000432 | 0.00043663 | 0.00044125 | 0.00044588 | 0.0004505 | 0.00045513 | 0.00045975 | 0.00046437 | 0.000469 | 0.00047362
| 10368011 | HTN013 | HTN | 16849935 | 16849939 | 1.6265 | 141.4503 | -37.5186 | 117 | 99.5 | 5.4% | 7.3% | 123.318 | 104.873 | 0.01 | 0.02 | -1844.5 | 141.763 | 1.343% | 125.541 | 106.7635 | 0.01 | 0.02 | -1877.75 | 144.3185 | 1.455% | 134.3% | 0.9532% | 0.9649% | 0.9765% | 0.9882% | 0.9998% | 1.011% | 1.023% | 1.035% | 1.046% | 1.058% | 1.07% | 1.081% | 1.093% | 1.105% | 1.116% | 1.128% | 1.14% | 1.151% | 1.163% | 1.175% | 0.00038604 | 0.00039075 | 0.00039547 | 0.00040019 | 0.00040491 | 0.00040962 | 0.00041434 | 0.00041906 | 0.00042378 | 0.0004285 | 0.00043321 | 0.00043793 | 0.00044265 | 0.00044737 | 0.00045208 | 0.0004568 | 0.00046152 | 0.00046624 | 0.00047096 | 0.00047567
| 10368178 | HTN013 | HTN | 193212832 | 176990314 | 0.89976 | 141.4546 | -37.5209 | 117 | 99.5 | 5.4% | 7.3% | 123.318 | 104.873 | 0.01 | 0.02 | -1844.5 | 141.763 | 1.343% | 125.541 | 106.7635 | 0.01 | 0.02 | -1877.75 | 144.3185 | 1.455% | 134.3% | 0.9532% | 0.9649% | 0.9765% | 0.9882% | 0.9998% | 1.011% | 1.023% | 1.035% | 1.046% | 1.058% | 1.07% | 1.081% | 1.093% | 1.105% | 1.116% | 1.128% | 1.14% | 1.151% | 1.163% | 1.175% | 0.00038604 | 0.00039075 | 0.00039547 | 0.00040019 | 0.00040491 | 0.00040962 | 0.00041434 | 0.00041906 | 0.00042378 | 0.0004285 | 0.00043321 | 0.00043793 | 0.00044265 | 0.00044737 | 0.00045208 | 0.0004568 | 0.00046152 | 0.00046624 | 0.00047096 | 0.00047567
| 10369081 | HTN034 | KGTS | 16854453 | 16854441 | 0.92079 | 141.4738 | -37.6457 | 117 | 99.3 | 5.4% | 7.3% | 123.318 | 104.6622 | 0.01 | 0.02 | -1865.58 | 141.9738 | 1.339% | 125.541 | 106.5489 | 0.01 | 0.02 | -1899.21 | 144.5331 | 1.45% | 133.9% | 0.9528% | 0.9643% | 0.9759% | 0.9874% | 0.9989% | 1.01% | 1.022% | 1.033% | 1.045% | 1.056% | 1.068% | 1.08% | 1.091% | 1.103% | 1.114% | 1.126% | 1.137% | 1.149% | 1.16% | 1.172% | 0.00038588 | 0.00039054 | 0.0003952 | 0.00039987 | 0.00040453 | 0.0004092 | 0.00041386 | 0.00041853 | 0.00042319 | 0.00042786 | 0.00043252 | 0.00043718 | 0.00044185 | 0.00044651 | 0.00045118 | 0.00045584 | 0.00046051 | 0.00046517 | 0.00046984 | 0.0004745
| 10369082 | HTN034 | KGTS | 16854441 | 16854445 | 0.33734 | 141.4729 | -37.6447 | 117 | 99.3 | 5.4% | 7.3% | 123.318 | 104.6622 | 0.01 | 0.02 | -1865.58 | 141.9738 | 1.339% | 125.541 | 106.5489 | 0.01 | 0.02 | -1899.21 | 144.5331 | 1.45% | 133.9% | 0.9528% | 0.9643% | 0.9759% | 0.9874% | 0.9989% | 1.01% | 1.022% | 1.033% | 1.045% | 1.056% | 1.068% | 1.08% | 1.091% | 1.103% | 1.114% | 1.126% | 1.137% | 1.149% | 1.16% | 1.172% | 0.00038588 | 0.00039054 | 0.0003952 | 0.00039987 | 0.00040453 | 0.0004092 | 0.00041386 | 0.00041853 | 0.00042319 | 0.00042786 | 0.00043252 | 0.00043718 | 0.00044185 | 0.00044651 | 0.00045118 | 0.00045584 | 0.00046051 | 0.00046517 | 0.00046984 | 0.0004745
| 10369084 | HTN034 | KGTS | 16854457 | 16854453 | 0.9944 | 141.4748 | -37.6467 | 117 | 99.3 | 5.4% | 7.3% | 123.318 | 104.6622 | 0.01 | 0.02 | -1865.58 | 141.9738 | 1.339% | 125.541 | 106.5489 | 0.01 | 0.02 | -1899.21 | 144.5331 | 1.45% | 133.9% | 0.9528% | 0.9643% | 0.9759% | 0.9874% | 0.9989% | 1.01% | 1.022% | 1.033% | 1.045% | 1.056% | 1.068% | 1.08% | 1.091% | 1.103% | 1.114% | 1.126% | 1.137% | 1.149% | 1.16% | 1.172% | 0.00038588 | 0.00039054 | 0.0003952 | 0.00039987 | 0.00040453 | 0.0004092 | 0.00041386 | 0.00041853 | 0.00042319 | 0.00042786 | 0.00043252 | 0.00043718 | 0.00044185 | 0.00044651 | 0.00045118 | 0.00045584 | 0.00046051 | 0.00046517 | 0.00046984 | 0.0004745
| 10369089 | HTN034 | KGTS | 16854493 | 16854473 | 0.85177 | 141.4793 | -37.6517 | 119 | 101 | 5.4% | 7.3% | 125.426 | 106.454 | 0.01 | 0.02 | -1897.2 | 144.398 | 1.339% | 127.687 | 108.373 | 0.01 | 0.02 | -1931.4 | 147.001 | 1.45% | 133.9% | 0.9528% | 0.9644% | 0.9759% | 0.9874% | 0.9989% | 1.01% | 1.022% | 1.033% | 1.045% | 1.057% | 1.068% | 1.08% | 1.091% | 1.103% | 1.114% | 1.126% | 1.137% | 1.149% | 1.16% | 1.172% | 0.00038588 | 0.00039054 | 0.00039521 | 0.00039987 | 0.00040454 | 0.0004092 | 0.00041387 | 0.00041853 | 0.0004232 | 0.00042786 | 0.00043253 | 0.00043719 | 0.00044186 | 0.00044652 | 0.00045119 | 0.00045585 | 0.00046052 | 0.00046519 | 0.00046985 | 0.00047452
| 10369091 | HTN034 | KGTS | 16854477 | 16854485 | 0.52504 | 141.4816 | -37.6537 | 119 | 101 | 5.4% | 7.3% | 125.426 | 106.454 | 0.01 | 0.02 | -1897.2 | 144.398 | 1.339% | 127.687 | 108.373 | 0.01 | 0.02 | -1931.4 | 147.001 | 1.45% | 133.9% | 0.9528% | 0.9644% | 0.9759% | 0.9874% | 0.9989% | 1.01% | 1.022% | 1.033% | 1.045% | 1.057% | 1.068% | 1.08% | 1.091% | 1.103% | 1.114% | 1.126% | 1.137% | 1.149% | 1.16% | 1.172% | 0.00038588 | 0.00039054 | 0.00039521 | 0.00039987 | 0.00040454 | 0.0004092 | 0.00041387 | 0.00041853 | 0.0004232 | 0.00042786 | 0.00043253 | 0.00043719 | 0.00044186 | 0.00044652 | 0.00045119 | 0.00045585 | 0.00046052 | 0.00046519 | 0.00046985 | 0.00047452
| 10369646 | HTN013 | HTN | 16856858 | 16856853 | 0.53957 | 141.5835 | -37.6146 | 117 | 99.9 | 5.4% | 7.3% | 123.318 | 105.2946 | 0.01 | 0.02 | -1802.34 | 141.3414 | 1.351% | 125.541 | 107.1927 | 0.01 | 0.02 | -1834.83 | 143.8893 | 1.465% | 135.1% | 0.954% | 0.966% | 0.9779% | 0.9898% | 1.002% | 1.014% | 1.026% | 1.037% | 1.049% | 1.061% | 1.073% | 1.085% | 1.097% | 1.109% | 1.121% | 1.133% | 1.145% | 1.157% | 1.169% | 1.181% | 0.00038637 | 0.00039119 | 0.00039602 | 0.00040085 | 0.00040568 | 0.00041051 | 0.00041534 | 0.00042016 | 0.00042499 | 0.00042982 | 0.00043465 | 0.00043948 | 0.0004443 | 0.00044913 | 0.00045396 | 0.00045879 | 0.00046362 | 0.00046845 | 0.00047327 | 0.0004781
| 10369837 | HTN034 | KGTS | 16857621 | 16857625 | 1.6414 | 141.2191 | -37.3617 | 117 | 99.4 | 5.4% | 7.3% | 123.318 | 104.7676 | 0.01 | 0.02 | -1855.04 | 141.8684 | 1.341% | 125.541 | 106.6562 | 0.01 | 0.02 | -1888.48 | 144.4258 | 1.452% | 134.1% | 0.953% | 0.9646% | 0.9762% | 0.9878% | 0.9994% | 1.011% | 1.023% | 1.034% | 1.046% | 1.057% | 1.069% | 1.08% | 1.092% | 1.104% | 1.115% | 1.127% | 1.138% | 1.15% | 1.162% | 1.173% | 0.00038595 | 0.00039065 | 0.00039534 | 0.00040003 | 0.00040472 | 0.00040941 | 0.0004141 | 0.00041879 | 0.00042348 | 0.00042817 | 0.00043286 | 0.00043756 | 0.00044225 | 0.00044694 | 0.00045163 | 0.00045632 | 0.00046101 | 0.0004657 | 0.00047039 | 0.00047508
| 10369838 | HTN034 | KGTS | 16857625 | 16857630 | 0.28844 | 141.2183 | -37.3602 | 117 | 99.4 | 5.4% | 7.3% | 123.318 | 104.7676 | 0.01 | 0.02 | -1855.04 | 141.8684 | 1.341% | 125.541 | 106.6562 | 0.01 | 0.02 | -1888.48 | 144.4258 | 1.452% | 134.1% | 0.953% | 0.9646% | 0.9762% | 0.9878% | 0.9994% | 1.011% | 1.023% | 1.034% | 1.046% | 1.057% | 1.069% | 1.08% | 1.092% | 1.104% | 1.115% | 1.127% | 1.138% | 1.15% | 1.162% | 1.173% | 0.00038595 | 0.00039065 | 0.00039534 | 0.00040003 | 0.00040472 | 0.00040941 | 0.0004141 | 0.00041879 | 0.00042348 | 0.00042817 | 0.00043286 | 0.00043756 | 0.00044225 | 0.00044694 | 0.00045163 | 0.00045632 | 0.00046101 | 0.0004657 | 0.00047039 | 0.00047508
| 10369839 | HTN034 | KGTS | 16857625 | 16857648 | 0.4508 | 141.2205 | -37.3613 | 117 | 99.4 | 5.4% | 7.3% | 123.318 | 104.7676 | 0.01 | 0.02 | -1855.04 | 141.8684 | 1.341% | 125.541 | 106.6562 | 0.01 | 0.02 | -1888.48 | 144.4258 | 1.452% | 134.1% | 0.953% | 0.9646% | 0.9762% | 0.9878% | 0.9994% | 1.011% | 1.023% | 1.034% | 1.046% | 1.057% | 1.069% | 1.08% | 1.092% | 1.104% | 1.115% | 1.127% | 1.138% | 1.15% | 1.162% | 1.173% | 0.00038595 | 0.00039065 | 0.00039534 | 0.00040003 | 0.00040472 | 0.00040941 | 0.0004141 | 0.00041879 | 0.00042348 | 0.00042817 | 0.00043286 | 0.00043756 | 0.00044225 | 0.00044694 | 0.00045163 | 0.00045632 | 0.00046101 | 0.0004657 | 0.00047039 | 0.00047508
| 10369847 | HTN034 | KGTS | 16857648 | 16857644 | 0.97503 | 141.2234 | -37.3624 | 117 | 99.4 | 5.4% | 7.3% | 123.318 | 104.7676 | 0.01 | 0.02 | -1855.04 | 141.8684 | 1.341% | 125.541 | 106.6562 | 0.01 | 0.02 | -1888.48 | 144.4258 | 1.452% | 134.1% | 0.953% | 0.9646% | 0.9762% | 0.9878% | 0.9994% | 1.011% | 1.023% | 1.034% | 1.046% | 1.057% | 1.069% | 1.08% | 1.092% | 1.104% | 1.115% | 1.127% | 1.138% | 1.15% | 1.162% | 1.173% | 0.00038595 | 0.00039065 | 0.00039534 | 0.00040003 | 0.00040472 | 0.00040941 | 0.0004141 | 0.00041879 | 0.00042348 | 0.00042817 | 0.00043286 | 0.00043756 | 0.00044225 | 0.00044694 | 0.00045163 | 0.00045632 | 0.00046101 | 0.0004657 | 0.00047039 | 0.00047508
| 10369863 | HTN034 | KGTS | 16857733 | 203323006 | 1.3473 | 141.2448 | -37.3656 | 117 | 99.6 | 5.4% | 7.3% | 123.318 | 104.9784 | 0.01 | 0.02 | -1833.96 | 141.6576 | 1.345% | 125.541 | 106.8708 | 0.01 | 0.02 | -1867.02 | 144.2112 | 1.457% | 134.5% | 0.9534% | 0.9651% | 0.9769% | 0.9886% | 1% | 1.012% | 1.024% | 1.035% | 1.047% | 1.059% | 1.071% | 1.082% | 1.094% | 1.106% | 1.117% | 1.129% | 1.141% | 1.153% | 1.164% | 1.176% | 0.00038612 | 0.00039086 | 0.00039561 | 0.00040035 | 0.0004051 | 0.00040984 | 0.00041459 | 0.00041933 | 0.00042408 | 0.00042882 | 0.00043357 | 0.00043831 | 0.00044306 | 0.0004478 | 0.00045255 | 0.00045729 | 0.00046204 | 0.00046678 | 0.00047153 | 0.00047627
| 10369865 | HTN034 | KGTS | 16857737 | 16857733 | 2.4143 | 141.2412 | -37.3653 | 117 | 99.6 | 5.4% | 7.3% | 123.318 | 104.9784 | 0.01 | 0.02 | -1833.96 | 141.6576 | 1.345% | 125.541 | 106.8708 | 0.01 | 0.02 | -1867.02 | 144.2112 | 1.457% | 134.5% | 0.9534% | 0.9651% | 0.9769% | 0.9886% | 1% | 1.012% | 1.024% | 1.035% | 1.047% | 1.059% | 1.071% | 1.082% | 1.094% | 1.106% | 1.117% | 1.129% | 1.141% | 1.153% | 1.164% | 1.176% | 0.00038612 | 0.00039086 | 0.00039561 | 0.00040035 | 0.0004051 | 0.00040984 | 0.00041459 | 0.00041933 | 0.00042408 | 0.00042882 | 0.00043357 | 0.00043831 | 0.00044306 | 0.0004478 | 0.00045255 | 0.00045729 | 0.00046204 | 0.00046678 | 0.00047153 | 0.00047627
| 10370437 | HTN013 | HTN | 16860189 | 16860176 | 2.1042 | 141.4355 | -37.5016 | 117 | 99.5 | 5.4% | 7.3% | 123.318 | 104.873 | 0.01 | 0.02 | -1844.5 | 141.763 | 1.343% | 125.541 | 106.7635 | 0.01 | 0.02 | -1877.75 | 144.3185 | 1.455% | 134.3% | 0.9532% | 0.9649% | 0.9765% | 0.9882% | 0.9998% | 1.011% | 1.023% | 1.035% | 1.046% | 1.058% | 1.07% | 1.081% | 1.093% | 1.105% | 1.116% | 1.128% | 1.14% | 1.151% | 1.163% | 1.175% | 0.00038604 | 0.00039075 | 0.00039547 | 0.00040019 | 0.00040491 | 0.00040962 | 0.00041434 | 0.00041906 | 0.00042378 | 0.0004285 | 0.00043321 | 0.00043793 | 0.00044265 | 0.00044737 | 0.00045208 | 0.0004568 | 0.00046152 | 0.00046624 | 0.00047096 | 0.00047567
| 10370496 | HTN013 | HTN | 16860428 | 16860488 | 1.95 | 141.4307 | -37.4841 | 117 | 99.7 | 5.4% | 7.3% | 123.318 | 105.0838 | 0.01 | 0.02 | -1823.42 | 141.5522 | 1.346% | 125.541 | 106.9781 | 0.01 | 0.02 | -1856.29 | 144.1039 | 1.46% | 134.6% | 0.9536% | 0.9654% | 0.9772% | 0.989% | 1.001% | 1.013% | 1.024% | 1.036% | 1.048% | 1.06% | 1.071% | 1.083% | 1.095% | 1.107% | 1.119% | 1.13% | 1.142% | 1.154% | 1.166% | 1.178% | 0.0003862 | 0.00039097 | 0.00039574 | 0.00040052 | 0.00040529 | 0.00041006 | 0.00041483 | 0.00041961 | 0.00042438 | 0.00042915 | 0.00043392 | 0.00043869 | 0.00044347 | 0.00044824 | 0.00045301 | 0.00045778 | 0.00046256 | 0.00046733 | 0.0004721 | 0.00047687
| 10370722 | HTN013 | HTN | 16861421 | 117437873 | 0.99474 | 141.4638 | -37.5043 | 117 | 99.5 | 5.4% | 7.3% | 123.318 | 104.873 | 0.01 | 0.02 | -1844.5 | 141.763 | 1.343% | 125.541 | 106.7635 | 0.01 | 0.02 | -1877.75 | 144.3185 | 1.455% | 134.3% | 0.9532% | 0.9649% | 0.9765% | 0.9882% | 0.9998% | 1.011% | 1.023% | 1.035% | 1.046% | 1.058% | 1.07% | 1.081% | 1.093% | 1.105% | 1.116% | 1.128% | 1.14% | 1.151% | 1.163% | 1.175% | 0.00038604 | 0.00039075 | 0.00039547 | 0.00040019 | 0.00040491 | 0.00040962 | 0.00041434 | 0.00041906 | 0.00042378 | 0.0004285 | 0.00043321 | 0.00043793 | 0.00044265 | 0.00044737 | 0.00045208 | 0.0004568 | 0.00046152 | 0.00046624 | 0.00047096 | 0.00047567
| 10373068 | MNA034 | MNA | 16871117 | 16871113 | 0.55645 | 145.2346 | -36.5816 | 122 | 107 | 6.3% | 8.8% | 129.686 | 113.741 | 0.01 | 0.02 | -1594.5 | 145.631 | 1.482% | 130.906 | 116.416 | 0.01 | 0.02 | -1449 | 145.396 | 1.615% | 148.2% | 0.9675% | 0.9838% | 1% | 1.017% | 1.033% | 1.049% | 1.066% | 1.082% | 1.099% | 1.115% | 1.131% | 1.148% | 1.164% | 1.181% | 1.197% | 1.213% | 1.23% | 1.246% | 1.263% | 1.279% | 0.0003918 | 0.00039844 | 0.00040508 | 0.00041172 | 0.00041836 | 0.000425 | 0.00043163 | 0.00043827 | 0.00044491 | 0.00045155 | 0.00045819 | 0.00046483 | 0.00047147 | 0.00047811 | 0.00048475 | 0.00049139 | 0.00049803 | 0.00050467 | 0.00051131 | 0.00051794
| 10373078 | MNA034 | MNA | 16871147 | 16871152 | 1.0743 | 145.2491 | -36.5746 | 121 | 106 | 6.3% | 8.8% | 128.623 | 112.678 | 0.01 | 0.02 | -1594.5 | 144.568 | 1.478% | 129.833 | 115.328 | 0.01 | 0.02 | -1450.5 | 144.338 | 1.609% | 147.8% | 0.9671% | 0.9833% | 0.9996% | 1.016% | 1.032% | 1.048% | 1.065% | 1.081% | 1.097% | 1.113% | 1.13% | 1.146% | 1.162% | 1.178% | 1.195% | 1.211% | 1.227% | 1.243% | 1.26% | 1.276% | 0.00039164 | 0.00039822 | 0.00040481 | 0.00041139 | 0.00041798 | 0.00042456 | 0.00043114 | 0.00043773 | 0.00044431 | 0.0004509 | 0.00045748 | 0.00046407 | 0.00047065 | 0.00047724 | 0.00048382 | 0.00049041 | 0.00049699 | 0.00050358 | 0.00051016 | 0.00051675
| 10373097 | MNA034 | MNA | 16871223 | 16871228 | 0.75526 | 145.2776 | -36.5501 | 120 | 105 | 6.3% | 8.8% | 127.56 | 111.615 | 0.01 | 0.02 | -1594.5 | 143.505 | 1.474% | 128.76 | 114.24 | 0.01 | 0.02 | -1452 | 143.28 | 1.603% | 147.4% | 0.9666% | 0.9828% | 0.9989% | 1.015% | 1.031% | 1.047% | 1.063% | 1.08% | 1.096% | 1.112% | 1.128% | 1.144% | 1.16% | 1.176% | 1.192% | 1.209% | 1.225% | 1.241% | 1.257% | 1.273% | 0.00039147 | 0.000398 | 0.00040453 | 0.00041106 | 0.00041759 | 0.00042412 | 0.00043065 | 0.00043719 | 0.00044372 | 0.00045025 | 0.00045678 | 0.00046331 | 0.00046984 | 0.00047637 | 0.0004829 | 0.00048943 | 0.00049596 | 0.00050249 | 0.00050902 | 0.00051555
| 10373098 | MNA034 | MNA | 16871223 | 16872419 | 1.83 | 145.2786 | -36.5504 | 120 | 105 | 6.3% | 8.8% | 127.56 | 111.615 | 0.01 | 0.02 | -1594.5 | 143.505 | 1.474% | 128.76 | 114.24 | 0.01 | 0.02 | -1452 | 143.28 | 1.603% | 147.4% | 0.9666% | 0.9828% | 0.9989% | 1.015% | 1.031% | 1.047% | 1.063% | 1.08% | 1.096% | 1.112% | 1.128% | 1.144% | 1.16% | 1.176% | 1.192% | 1.209% | 1.225% | 1.241% | 1.257% | 1.273% | 0.00039147 | 0.000398 | 0.00040453 | 0.00041106 | 0.00041759 | 0.00042412 | 0.00043065 | 0.00043719 | 0.00044372 | 0.00045025 | 0.00045678 | 0.00046331 | 0.00046984 | 0.00047637 | 0.0004829 | 0.00048943 | 0.00049596 | 0.00050249 | 0.00050902 | 0.00051555
| 10373099 | MNA034 | MNA | 16871228 | 16871232 | 0.76258 | 145.277 | -36.5478 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10373102 | MNA034 | MNA | 16871241 | 16871245 | 1.369 | 145.2772 | -36.5439 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10373201 | MNA034 | MNA | 16871666 | 17277028 | 0.29839 | 145.2779 | -36.5124 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10373265 | MNA034 | MNA | 16871944 | 16871940 | 1.3874 | 145.3232 | -36.5594 | 120 | 105 | 6.3% | 8.8% | 127.56 | 111.615 | 0.01 | 0.02 | -1594.5 | 143.505 | 1.474% | 128.76 | 114.24 | 0.01 | 0.02 | -1452 | 143.28 | 1.603% | 147.4% | 0.9666% | 0.9828% | 0.9989% | 1.015% | 1.031% | 1.047% | 1.063% | 1.08% | 1.096% | 1.112% | 1.128% | 1.144% | 1.16% | 1.176% | 1.192% | 1.209% | 1.225% | 1.241% | 1.257% | 1.273% | 0.00039147 | 0.000398 | 0.00040453 | 0.00041106 | 0.00041759 | 0.00042412 | 0.00043065 | 0.00043719 | 0.00044372 | 0.00045025 | 0.00045678 | 0.00046331 | 0.00046984 | 0.00047637 | 0.0004829 | 0.00048943 | 0.00049596 | 0.00050249 | 0.00050902 | 0.00051555
| 10373267 | MNA034 | MNA | 153141897 | 16871944 | 0.71746 | 145.3202 | -36.5581 | 120 | 105 | 6.3% | 8.8% | 127.56 | 111.615 | 0.01 | 0.02 | -1594.5 | 143.505 | 1.474% | 128.76 | 114.24 | 0.01 | 0.02 | -1452 | 143.28 | 1.603% | 147.4% | 0.9666% | 0.9828% | 0.9989% | 1.015% | 1.031% | 1.047% | 1.063% | 1.08% | 1.096% | 1.112% | 1.128% | 1.144% | 1.16% | 1.176% | 1.192% | 1.209% | 1.225% | 1.241% | 1.257% | 1.273% | 0.00039147 | 0.000398 | 0.00040453 | 0.00041106 | 0.00041759 | 0.00042412 | 0.00043065 | 0.00043719 | 0.00044372 | 0.00045025 | 0.00045678 | 0.00046331 | 0.00046984 | 0.00047637 | 0.0004829 | 0.00048943 | 0.00049596 | 0.00050249 | 0.00050902 | 0.00051555
| 10373268 | MNA034 | MNA | 16871944 | 17529724 | 1.0517 | 145.3208 | -36.5601 | 120 | 105 | 6.3% | 8.8% | 127.56 | 111.615 | 0.01 | 0.02 | -1594.5 | 143.505 | 1.474% | 128.76 | 114.24 | 0.01 | 0.02 | -1452 | 143.28 | 1.603% | 147.4% | 0.9666% | 0.9828% | 0.9989% | 1.015% | 1.031% | 1.047% | 1.063% | 1.08% | 1.096% | 1.112% | 1.128% | 1.144% | 1.16% | 1.176% | 1.192% | 1.209% | 1.225% | 1.241% | 1.257% | 1.273% | 0.00039147 | 0.000398 | 0.00040453 | 0.00041106 | 0.00041759 | 0.00042412 | 0.00043065 | 0.00043719 | 0.00044372 | 0.00045025 | 0.00045678 | 0.00046331 | 0.00046984 | 0.00047637 | 0.0004829 | 0.00048943 | 0.00049596 | 0.00050249 | 0.00050902 | 0.00051555
| 10373284 | MNA034 | MNA | 16872037 | 16872326 | 0.92463 | 145.2951 | -36.544 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10373345 | MNA034 | MNA | 16872326 | 16872321 | 1.5224 | 145.2933 | -36.5456 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10373712 | MNA034 | MNA | 16873776 | 16875251 | 1.4869 | 145.226 | -36.6185 | 124 | 109 | 6.3% | 8.8% | 131.812 | 115.867 | 0.01 | 0.02 | -1594.5 | 147.757 | 1.49% | 133.052 | 118.592 | 0.01 | 0.02 | -1446 | 147.512 | 1.626% | 149% | 0.9683% | 0.9849% | 1.002% | 1.018% | 1.035% | 1.052% | 1.068% | 1.085% | 1.102% | 1.118% | 1.135% | 1.152% | 1.168% | 1.185% | 1.202% | 1.218% | 1.235% | 1.252% | 1.268% | 1.285% | 0.00039213 | 0.00039887 | 0.00040562 | 0.00041237 | 0.00041912 | 0.00042587 | 0.00043261 | 0.00043936 | 0.00044611 | 0.00045286 | 0.00045961 | 0.00046635 | 0.0004731 | 0.00047985 | 0.0004866 | 0.00049335 | 0.00050009 | 0.00050684 | 0.00051359 | 0.00052034
| 10374056 | MNA034 | MNA | 16875251 | 16875255 | 1.69 | 145.2271 | -36.6178 | 124 | 109 | 6.3% | 8.8% | 131.812 | 115.867 | 0.01 | 0.02 | -1594.5 | 147.757 | 1.49% | 133.052 | 118.592 | 0.01 | 0.02 | -1446 | 147.512 | 1.626% | 149% | 0.9683% | 0.9849% | 1.002% | 1.018% | 1.035% | 1.052% | 1.068% | 1.085% | 1.102% | 1.118% | 1.135% | 1.152% | 1.168% | 1.185% | 1.202% | 1.218% | 1.235% | 1.252% | 1.268% | 1.285% | 0.00039213 | 0.00039887 | 0.00040562 | 0.00041237 | 0.00041912 | 0.00042587 | 0.00043261 | 0.00043936 | 0.00044611 | 0.00045286 | 0.00045961 | 0.00046635 | 0.0004731 | 0.00047985 | 0.0004866 | 0.00049335 | 0.00050009 | 0.00050684 | 0.00051359 | 0.00052034
| 10376361 | MNA034 | MNA | 16885145 | 16885150 | 1.6675 | 145.2957 | -36.5269 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10376367 | MNA034 | MNA | 16885167 | 16885176 | 0.34151 | 145.2897 | -36.527 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10376369 | MNA034 | MNA | 16885181 | 16885185 | 0.142 | 145.2975 | -36.5305 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10376370 | MNA034 | MNA | 16885189 | 16885193 | 0.32439 | 145.2878 | -36.5279 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10376373 | MNA034 | MNA | 16885202 | 16885198 | 1.093 | 145.2754 | -36.5283 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10376473 | MNA034 | MNA | 16885636 | 16885626 | 0.91831 | 145.2232 | -36.5659 | 121 | 107 | 6.3% | 8.8% | 128.623 | 113.741 | 0.01 | 0.02 | -1488.2 | 143.505 | 1.512% | 129.833 | 116.416 | 0.01 | 0.02 | -1341.7 | 143.25 | 1.658% | 151.2% | 0.9705% | 0.988% | 1.005% | 1.023% | 1.04% | 1.058% | 1.075% | 1.092% | 1.11% | 1.127% | 1.145% | 1.162% | 1.18% | 1.197% | 1.214% | 1.232% | 1.249% | 1.267% | 1.284% | 1.302% | 0.00039305 | 0.0004001 | 0.00040716 | 0.00041421 | 0.00042127 | 0.00042832 | 0.00043538 | 0.00044243 | 0.00044949 | 0.00045654 | 0.0004636 | 0.00047065 | 0.00047771 | 0.00048476 | 0.00049182 | 0.00049887 | 0.00050593 | 0.00051298 | 0.00052004 | 0.00052709
| 10376557 | RCT014 | RCTS | 16886209 | 16886205 | 1.1194 | 142.3203 | -34.345 | 110 | 95.8 | 6.3% | 8.8% | 116.93 | 101.8354 | 0.01 | 0.02 | -1509.46 | 132.0246 | 1.459% | 118.03 | 104.2304 | 0.01 | 0.02 | -1379.96 | 131.8296 | 1.582% | 145.9% | 0.9651% | 0.9807% | 0.9963% | 1.012% | 1.028% | 1.043% | 1.059% | 1.074% | 1.09% | 1.106% | 1.121% | 1.137% | 1.152% | 1.168% | 1.184% | 1.199% | 1.215% | 1.231% | 1.246% | 1.262% | 0.00039085 | 0.00039718 | 0.0004035 | 0.00040982 | 0.00041615 | 0.00042247 | 0.00042879 | 0.00043512 | 0.00044144 | 0.00044776 | 0.00045409 | 0.00046041 | 0.00046673 | 0.00047306 | 0.00047938 | 0.0004857 | 0.00049203 | 0.00049835 | 0.00050467 | 0.000511
| 10376558 | RCT014 | RCTS | 16886209 | 16886213 | 2.1105 | 142.3218 | -34.3427 | 110 | 95.8 | 6.3% | 8.8% | 116.93 | 101.8354 | 0.01 | 0.02 | -1509.46 | 132.0246 | 1.459% | 118.03 | 104.2304 | 0.01 | 0.02 | -1379.96 | 131.8296 | 1.582% | 145.9% | 0.9651% | 0.9807% | 0.9963% | 1.012% | 1.028% | 1.043% | 1.059% | 1.074% | 1.09% | 1.106% | 1.121% | 1.137% | 1.152% | 1.168% | 1.184% | 1.199% | 1.215% | 1.231% | 1.246% | 1.262% | 0.00039085 | 0.00039718 | 0.0004035 | 0.00040982 | 0.00041615 | 0.00042247 | 0.00042879 | 0.00043512 | 0.00044144 | 0.00044776 | 0.00045409 | 0.00046041 | 0.00046673 | 0.00047306 | 0.00047938 | 0.0004857 | 0.00049203 | 0.00049835 | 0.00050467 | 0.000511
| 10378233 | RCT013 | RCTS | 16893203 | 16893186 | 0.80535 | 142.3629 | -34.4846 | 108 | 93.8 | 6.3% | 8.8% | 114.804 | 99.7094 | 0.01 | 0.02 | -1509.46 | 129.8986 | 1.451% | 115.884 | 102.0544 | 0.01 | 0.02 | -1382.96 | 129.7136 | 1.57% | 145.1% | 0.9643% | 0.9796% | 0.9949% | 1.01% | 1.026% | 1.041% | 1.056% | 1.072% | 1.087% | 1.102% | 1.118% | 1.133% | 1.148% | 1.164% | 1.179% | 1.194% | 1.21% | 1.225% | 1.24% | 1.256% | 0.00039051 | 0.00039672 | 0.00040292 | 0.00040913 | 0.00041534 | 0.00042155 | 0.00042776 | 0.00043397 | 0.00044017 | 0.00044638 | 0.00045259 | 0.0004588 | 0.00046501 | 0.00047122 | 0.00047743 | 0.00048363 | 0.00048984 | 0.00049605 | 0.00050226 | 0.00050847
| 10378430 | RCT013 | RCTS | 16893988 | 16893992 | 0.1239 | 142.3655 | -34.5036 | 107 | 93.4 | 6.3% | 8.8% | 113.741 | 99.2842 | 0.01 | 0.02 | -1445.68 | 128.1978 | 1.466% | 114.811 | 101.6192 | 0.01 | 0.02 | -1319.18 | 128.0028 | 1.592% | 146.6% | 0.9658% | 0.9817% | 0.9976% | 1.013% | 1.029% | 1.045% | 1.061% | 1.077% | 1.093% | 1.109% | 1.124% | 1.14% | 1.156% | 1.172% | 1.188% | 1.204% | 1.22% | 1.235% | 1.251% | 1.267% | 0.00039115 | 0.00039757 | 0.00040399 | 0.00041042 | 0.00041684 | 0.00042326 | 0.00042968 | 0.0004361 | 0.00044253 | 0.00044895 | 0.00045537 | 0.00046179 | 0.00046822 | 0.00047464 | 0.00048106 | 0.00048748 | 0.00049391 | 0.00050033 | 0.00050675 | 0.00051317
| 10378796 | RCT013 | RCTS | 16895487 | 16895492 | 1.5847 | 142.3839 | -34.5581 | 106 | 92.8 | 6.3% | 8.8% | 112.678 | 98.6464 | 0.01 | 0.02 | -1403.16 | 126.7096 | 1.476% | 113.738 | 100.9664 | 0.01 | 0.02 | -1277.16 | 126.5096 | 1.606% | 147.6% | 0.9668% | 0.983% | 0.9992% | 1.015% | 1.032% | 1.048% | 1.064% | 1.08% | 1.096% | 1.113% | 1.129% | 1.145% | 1.161% | 1.177% | 1.193% | 1.21% | 1.226% | 1.242% | 1.258% | 1.274% | 0.00039155 | 0.0003981 | 0.00040466 | 0.00041121 | 0.00041777 | 0.00042432 | 0.00043088 | 0.00043743 | 0.00044399 | 0.00045054 | 0.0004571 | 0.00046365 | 0.00047021 | 0.00047676 | 0.00048332 | 0.00048987 | 0.00049643 | 0.00050298 | 0.00050954 | 0.00051609
| 10378807 | RCT013 | RCTS | 16895528 | 16895611 | 1.4618 | 142.3885 | -34.5675 | 106 | 92.8 | 6.3% | 8.8% | 112.678 | 98.6464 | 0.01 | 0.02 | -1403.16 | 126.7096 | 1.476% | 113.738 | 100.9664 | 0.01 | 0.02 | -1277.16 | 126.5096 | 1.606% | 147.6% | 0.9668% | 0.983% | 0.9992% | 1.015% | 1.032% | 1.048% | 1.064% | 1.08% | 1.096% | 1.113% | 1.129% | 1.145% | 1.161% | 1.177% | 1.193% | 1.21% | 1.226% | 1.242% | 1.258% | 1.274% | 0.00039155 | 0.0003981 | 0.00040466 | 0.00041121 | 0.00041777 | 0.00042432 | 0.00043088 | 0.00043743 | 0.00044399 | 0.00045054 | 0.0004571 | 0.00046365 | 0.00047021 | 0.00047676 | 0.00048332 | 0.00048987 | 0.00049643 | 0.00050298 | 0.00050954 | 0.00051609
| 10378828 | RCT013 | RCTS | 16895632 | 16895636 | 0.18984 | 142.3972 | -34.569 | 106 | 92.8 | 6.3% | 8.8% | 112.678 | 98.6464 | 0.01 | 0.02 | -1403.16 | 126.7096 | 1.476% | 113.738 | 100.9664 | 0.01 | 0.02 | -1277.16 | 126.5096 | 1.606% | 147.6% | 0.9668% | 0.983% | 0.9992% | 1.015% | 1.032% | 1.048% | 1.064% | 1.08% | 1.096% | 1.113% | 1.129% | 1.145% | 1.161% | 1.177% | 1.193% | 1.21% | 1.226% | 1.242% | 1.258% | 1.274% | 0.00039155 | 0.0003981 | 0.00040466 | 0.00041121 | 0.00041777 | 0.00042432 | 0.00043088 | 0.00043743 | 0.00044399 | 0.00045054 | 0.0004571 | 0.00046365 | 0.00047021 | 0.00047676 | 0.00048332 | 0.00048987 | 0.00049643 | 0.00050298 | 0.00050954 | 0.00051609
| 10378830 | RCT013 | RCTS | 16895640 | 100123866 | 0.36861 | 142.4022 | -34.5684 | 106 | 92.1 | 6.3% | 8.8% | 112.678 | 97.9023 | 0.01 | 0.02 | -1477.57 | 127.4537 | 1.452% | 113.738 | 100.2048 | 0.01 | 0.02 | -1353.32 | 127.2712 | 1.572% | 145.2% | 0.9644% | 0.9798% | 0.9951% | 1.011% | 1.026% | 1.041% | 1.057% | 1.072% | 1.087% | 1.103% | 1.118% | 1.133% | 1.149% | 1.164% | 1.18% | 1.195% | 1.21% | 1.226% | 1.241% | 1.256% | 0.00039056 | 0.00039678 | 0.00040301 | 0.00040923 | 0.00041546 | 0.00042168 | 0.00042791 | 0.00043413 | 0.00044036 | 0.00044658 | 0.00045281 | 0.00045903 | 0.00046526 | 0.00047148 | 0.00047771 | 0.00048393 | 0.00049016 | 0.00049638 | 0.00050261 | 0.00050883
| 10378852 | RCT013 | RCTS | 16895725 | 16895735 | 0.89295 | 142.396 | -34.562 | 106 | 92.8 | 6.3% | 8.8% | 112.678 | 98.6464 | 0.01 | 0.02 | -1403.16 | 126.7096 | 1.476% | 113.738 | 100.9664 | 0.01 | 0.02 | -1277.16 | 126.5096 | 1.606% | 147.6% | 0.9668% | 0.983% | 0.9992% | 1.015% | 1.032% | 1.048% | 1.064% | 1.08% | 1.096% | 1.113% | 1.129% | 1.145% | 1.161% | 1.177% | 1.193% | 1.21% | 1.226% | 1.242% | 1.258% | 1.274% | 0.00039155 | 0.0003981 | 0.00040466 | 0.00041121 | 0.00041777 | 0.00042432 | 0.00043088 | 0.00043743 | 0.00044399 | 0.00045054 | 0.0004571 | 0.00046365 | 0.00047021 | 0.00047676 | 0.00048332 | 0.00048987 | 0.00049643 | 0.00050298 | 0.00050954 | 0.00051609
| 10378869 | RCT013 | RCTS | 16895808 | 16895812 | 1.0106 | 142.4107 | -34.5733 | 106 | 92.1 | 6.3% | 8.8% | 112.678 | 97.9023 | 0.01 | 0.02 | -1477.57 | 127.4537 | 1.452% | 113.738 | 100.2048 | 0.01 | 0.02 | -1353.32 | 127.2712 | 1.572% | 145.2% | 0.9644% | 0.9798% | 0.9951% | 1.011% | 1.026% | 1.041% | 1.057% | 1.072% | 1.087% | 1.103% | 1.118% | 1.133% | 1.149% | 1.164% | 1.18% | 1.195% | 1.21% | 1.226% | 1.241% | 1.256% | 0.00039056 | 0.00039678 | 0.00040301 | 0.00040923 | 0.00041546 | 0.00042168 | 0.00042791 | 0.00043413 | 0.00044036 | 0.00044658 | 0.00045281 | 0.00045903 | 0.00046526 | 0.00047148 | 0.00047771 | 0.00048393 | 0.00049016 | 0.00049638 | 0.00050261 | 0.00050883
| 10378872 | RCT013 | RCTS | 16895816 | 16895820 | 0.88077 | 142.4134 | -34.5778 | 105 | 91.9 | 6.3% | 8.8% | 111.615 | 97.6897 | 0.01 | 0.02 | -1392.53 | 125.5403 | 1.475% | 112.665 | 99.9872 | 0.01 | 0.02 | -1267.78 | 125.3428 | 1.605% | 147.5% | 0.9667% | 0.9829% | 0.9991% | 1.015% | 1.031% | 1.048% | 1.064% | 1.08% | 1.096% | 1.112% | 1.128% | 1.144% | 1.161% | 1.177% | 1.193% | 1.209% | 1.225% | 1.241% | 1.258% | 1.274% | 0.00039151 | 0.00039805 | 0.0004046 | 0.00041114 | 0.00041768 | 0.00042422 | 0.00043077 | 0.00043731 | 0.00044385 | 0.0004504 | 0.00045694 | 0.00046348 | 0.00047002 | 0.00047657 | 0.00048311 | 0.00048965 | 0.0004962 | 0.00050274 | 0.00050928 | 0.00051582
| 10378875 | RCT013 | RCTS | 16895824 | 16895828 | 0.50915 | 142.4178 | -34.5794 | 105 | 91.9 | 6.3% | 8.8% | 111.615 | 97.6897 | 0.01 | 0.02 | -1392.53 | 125.5403 | 1.475% | 112.665 | 99.9872 | 0.01 | 0.02 | -1267.78 | 125.3428 | 1.605% | 147.5% | 0.9667% | 0.9829% | 0.9991% | 1.015% | 1.031% | 1.048% | 1.064% | 1.08% | 1.096% | 1.112% | 1.128% | 1.144% | 1.161% | 1.177% | 1.193% | 1.209% | 1.225% | 1.241% | 1.258% | 1.274% | 0.00039151 | 0.00039805 | 0.0004046 | 0.00041114 | 0.00041768 | 0.00042422 | 0.00043077 | 0.00043731 | 0.00044385 | 0.0004504 | 0.00045694 | 0.00046348 | 0.00047002 | 0.00047657 | 0.00048311 | 0.00048965 | 0.0004962 | 0.00050274 | 0.00050928 | 0.00051582
| 10378881 | RCT013 | RCTS | 16895844 | 16895848 | 2.3081 | 142.4239 | -34.5849 | 105 | 91.9 | 6.3% | 8.8% | 111.615 | 97.6897 | 0.01 | 0.02 | -1392.53 | 125.5403 | 1.475% | 112.665 | 99.9872 | 0.01 | 0.02 | -1267.78 | 125.3428 | 1.605% | 147.5% | 0.9667% | 0.9829% | 0.9991% | 1.015% | 1.031% | 1.048% | 1.064% | 1.08% | 1.096% | 1.112% | 1.128% | 1.144% | 1.161% | 1.177% | 1.193% | 1.209% | 1.225% | 1.241% | 1.258% | 1.274% | 0.00039151 | 0.00039805 | 0.0004046 | 0.00041114 | 0.00041768 | 0.00042422 | 0.00043077 | 0.00043731 | 0.00044385 | 0.0004504 | 0.00045694 | 0.00046348 | 0.00047002 | 0.00047657 | 0.00048311 | 0.00048965 | 0.0004962 | 0.00050274 | 0.00050928 | 0.00051582
| 10378887 | RCT013 | RCTS | 16895860 | 16895864 | 2.0754 | 142.4274 | -34.5931 | 105 | 91.7 | 6.3% | 8.8% | 111.615 | 97.4771 | 0.01 | 0.02 | -1413.79 | 125.7529 | 1.468% | 112.665 | 99.7696 | 0.01 | 0.02 | -1289.54 | 125.5604 | 1.594% | 146.8% | 0.966% | 0.9819% | 0.9978% | 1.014% | 1.03% | 1.046% | 1.061% | 1.077% | 1.093% | 1.109% | 1.125% | 1.141% | 1.157% | 1.173% | 1.189% | 1.205% | 1.221% | 1.237% | 1.252% | 1.268% | 0.00039121 | 0.00039766 | 0.0004041 | 0.00041055 | 0.00041699 | 0.00042344 | 0.00042988 | 0.00043633 | 0.00044277 | 0.00044922 | 0.00045566 | 0.0004621 | 0.00046855 | 0.00047499 | 0.00048144 | 0.00048788 | 0.00049433 | 0.00050077 | 0.00050722 | 0.00051366
| 10378888 | RCT013 | RCTS | 16895864 | 16895868 | 1.9746 | 142.4284 | -34.5953 | 105 | 91.7 | 6.3% | 8.8% | 111.615 | 97.4771 | 0.01 | 0.02 | -1413.79 | 125.7529 | 1.468% | 112.665 | 99.7696 | 0.01 | 0.02 | -1289.54 | 125.5604 | 1.594% | 146.8% | 0.966% | 0.9819% | 0.9978% | 1.014% | 1.03% | 1.046% | 1.061% | 1.077% | 1.093% | 1.109% | 1.125% | 1.141% | 1.157% | 1.173% | 1.189% | 1.205% | 1.221% | 1.237% | 1.252% | 1.268% | 0.00039121 | 0.00039766 | 0.0004041 | 0.00041055 | 0.00041699 | 0.00042344 | 0.00042988 | 0.00043633 | 0.00044277 | 0.00044922 | 0.00045566 | 0.0004621 | 0.00046855 | 0.00047499 | 0.00048144 | 0.00048788 | 0.00049433 | 0.00050077 | 0.00050722 | 0.00051366
| 10378889 | RCT013 | RCTS | 16895868 | 200455728 | 1.1128 | 142.4295 | -34.5971 | 105 | 91.7 | 6.3% | 8.8% | 111.615 | 97.4771 | 0.01 | 0.02 | -1413.79 | 125.7529 | 1.468% | 112.665 | 99.7696 | 0.01 | 0.02 | -1289.54 | 125.5604 | 1.594% | 146.8% | 0.966% | 0.9819% | 0.9978% | 1.014% | 1.03% | 1.046% | 1.061% | 1.077% | 1.093% | 1.109% | 1.125% | 1.141% | 1.157% | 1.173% | 1.189% | 1.205% | 1.221% | 1.237% | 1.252% | 1.268% | 0.00039121 | 0.00039766 | 0.0004041 | 0.00041055 | 0.00041699 | 0.00042344 | 0.00042988 | 0.00043633 | 0.00044277 | 0.00044922 | 0.00045566 | 0.0004621 | 0.00046855 | 0.00047499 | 0.00048144 | 0.00048788 | 0.00049433 | 0.00050077 | 0.00050722 | 0.00051366
| 10378892 | RCT013 | RCTS | 16895880 | 200455761 | 1.4702 | 142.4331 | -34.6004 | 105 | 91.7 | 6.3% | 8.8% | 111.615 | 97.4771 | 0.01 | 0.02 | -1413.79 | 125.7529 | 1.468% | 112.665 | 99.7696 | 0.01 | 0.02 | -1289.54 | 125.5604 | 1.594% | 146.8% | 0.966% | 0.9819% | 0.9978% | 1.014% | 1.03% | 1.046% | 1.061% | 1.077% | 1.093% | 1.109% | 1.125% | 1.141% | 1.157% | 1.173% | 1.189% | 1.205% | 1.221% | 1.237% | 1.252% | 1.268% | 0.00039121 | 0.00039766 | 0.0004041 | 0.00041055 | 0.00041699 | 0.00042344 | 0.00042988 | 0.00043633 | 0.00044277 | 0.00044922 | 0.00045566 | 0.0004621 | 0.00046855 | 0.00047499 | 0.00048144 | 0.00048788 | 0.00049433 | 0.00050077 | 0.00050722 | 0.00051366
| 10379177 | RCT014 | RCTS | 16897032 | 66714729 | 0.28832 | 142.3536 | -34.3601 | 110 | 95.6 | 6.3% | 8.8% | 116.93 | 101.6228 | 0.01 | 0.02 | -1530.72 | 132.2372 | 1.453% | 118.03 | 104.0128 | 0.01 | 0.02 | -1401.72 | 132.0472 | 1.573% | 145.3% | 0.9645% | 0.9799% | 0.9953% | 1.011% | 1.026% | 1.041% | 1.057% | 1.072% | 1.088% | 1.103% | 1.118% | 1.134% | 1.149% | 1.165% | 1.18% | 1.195% | 1.211% | 1.226% | 1.242% | 1.257% | 0.00039059 | 0.00039682 | 0.00040306 | 0.0004093 | 0.00041553 | 0.00042177 | 0.000428 | 0.00043424 | 0.00044047 | 0.00044671 | 0.00045294 | 0.00045918 | 0.00046542 | 0.00047165 | 0.00047789 | 0.00048412 | 0.00049036 | 0.00049659 | 0.00050283 | 0.00050906
| 10379178 | RCT014 | RCTS | 16897032 | 16897054 | 0.63689 | 142.3515 | -34.3613 | 110 | 95.6 | 6.3% | 8.8% | 116.93 | 101.6228 | 0.01 | 0.02 | -1530.72 | 132.2372 | 1.453% | 118.03 | 104.0128 | 0.01 | 0.02 | -1401.72 | 132.0472 | 1.573% | 145.3% | 0.9645% | 0.9799% | 0.9953% | 1.011% | 1.026% | 1.041% | 1.057% | 1.072% | 1.088% | 1.103% | 1.118% | 1.134% | 1.149% | 1.165% | 1.18% | 1.195% | 1.211% | 1.226% | 1.242% | 1.257% | 0.00039059 | 0.00039682 | 0.00040306 | 0.0004093 | 0.00041553 | 0.00042177 | 0.000428 | 0.00043424 | 0.00044047 | 0.00044671 | 0.00045294 | 0.00045918 | 0.00046542 | 0.00047165 | 0.00047789 | 0.00048412 | 0.00049036 | 0.00049659 | 0.00050283 | 0.00050906
| 10379182 | RCT014 | RCTS | 16897054 | 16897063 | 0.441 | 142.3508 | -34.3639 | 110 | 95.6 | 6.3% | 8.8% | 116.93 | 101.6228 | 0.01 | 0.02 | -1530.72 | 132.2372 | 1.453% | 118.03 | 104.0128 | 0.01 | 0.02 | -1401.72 | 132.0472 | 1.573% | 145.3% | 0.9645% | 0.9799% | 0.9953% | 1.011% | 1.026% | 1.041% | 1.057% | 1.072% | 1.088% | 1.103% | 1.118% | 1.134% | 1.149% | 1.165% | 1.18% | 1.195% | 1.211% | 1.226% | 1.242% | 1.257% | 0.00039059 | 0.00039682 | 0.00040306 | 0.0004093 | 0.00041553 | 0.00042177 | 0.000428 | 0.00043424 | 0.00044047 | 0.00044671 | 0.00045294 | 0.00045918 | 0.00046542 | 0.00047165 | 0.00047789 | 0.00048412 | 0.00049036 | 0.00049659 | 0.00050283 | 0.00050906
| 10382614 | SHTSNKA | KYM | 16915965 | 16915913 | 0.39916 | 145.4151 | -36.3242 | 113 | 99.6 | 6.3% | 8.8% | 120.119 | 105.8748 | 0.01 | 0.02 | -1424.42 | 134.3632 | 1.5% | 121.249 | 108.3648 | 0.01 | 0.02 | -1288.42 | 134.1332 | 1.64% | 150% | 0.9693% | 0.9863% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039253 | 0.00039942 | 0.0004063 | 0.00041318 | 0.00042007 | 0.00042695 | 0.00043383 | 0.00044072 | 0.0004476 | 0.00045449 | 0.00046137 | 0.00046825 | 0.00047514 | 0.00048202 | 0.0004889 | 0.00049579 | 0.00050267 | 0.00050956 | 0.00051644 | 0.00052332
| 10382624 | SHTSNKA | KYM | 16915960 | 16915965 | 0.41906 | 145.4143 | -36.3242 | 113 | 99.6 | 6.3% | 8.8% | 120.119 | 105.8748 | 0.01 | 0.02 | -1424.42 | 134.3632 | 1.5% | 121.249 | 108.3648 | 0.01 | 0.02 | -1288.42 | 134.1332 | 1.64% | 150% | 0.9693% | 0.9863% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039253 | 0.00039942 | 0.0004063 | 0.00041318 | 0.00042007 | 0.00042695 | 0.00043383 | 0.00044072 | 0.0004476 | 0.00045449 | 0.00046137 | 0.00046825 | 0.00047514 | 0.00048202 | 0.0004889 | 0.00049579 | 0.00050267 | 0.00050956 | 0.00051644 | 0.00052332
| 10382634 | SHTSNKA | KYM | 16916011 | 16916015 | 0.44715 | 145.404 | -36.3233 | 113 | 99.6 | 6.3% | 8.8% | 120.119 | 105.8748 | 0.01 | 0.02 | -1424.42 | 134.3632 | 1.5% | 121.249 | 108.3648 | 0.01 | 0.02 | -1288.42 | 134.1332 | 1.64% | 150% | 0.9693% | 0.9863% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039253 | 0.00039942 | 0.0004063 | 0.00041318 | 0.00042007 | 0.00042695 | 0.00043383 | 0.00044072 | 0.0004476 | 0.00045449 | 0.00046137 | 0.00046825 | 0.00047514 | 0.00048202 | 0.0004889 | 0.00049579 | 0.00050267 | 0.00050956 | 0.00051644 | 0.00052332
| 10382635 | SHTSNKA | KYM | 16916015 | 16916019 | 0.41807 | 145.4029 | -36.3233 | 113 | 99.6 | 6.3% | 8.8% | 120.119 | 105.8748 | 0.01 | 0.02 | -1424.42 | 134.3632 | 1.5% | 121.249 | 108.3648 | 0.01 | 0.02 | -1288.42 | 134.1332 | 1.64% | 150% | 0.9693% | 0.9863% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039253 | 0.00039942 | 0.0004063 | 0.00041318 | 0.00042007 | 0.00042695 | 0.00043383 | 0.00044072 | 0.0004476 | 0.00045449 | 0.00046137 | 0.00046825 | 0.00047514 | 0.00048202 | 0.0004889 | 0.00049579 | 0.00050267 | 0.00050956 | 0.00051644 | 0.00052332
| 10382636 | SHTSNKA | KYM | 16916019 | 16916023 | 0.38138 | 145.4018 | -36.3234 | 113 | 99.6 | 6.3% | 8.8% | 120.119 | 105.8748 | 0.01 | 0.02 | -1424.42 | 134.3632 | 1.5% | 121.249 | 108.3648 | 0.01 | 0.02 | -1288.42 | 134.1332 | 1.64% | 150% | 0.9693% | 0.9863% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039253 | 0.00039942 | 0.0004063 | 0.00041318 | 0.00042007 | 0.00042695 | 0.00043383 | 0.00044072 | 0.0004476 | 0.00045449 | 0.00046137 | 0.00046825 | 0.00047514 | 0.00048202 | 0.0004889 | 0.00049579 | 0.00050267 | 0.00050956 | 0.00051644 | 0.00052332
| 10382650 | SHN011 | SHN | 16916077 | 182753570 | 0.91735 | 145.3982 | -36.3246 | 113 | 99.5 | 6.3% | 8.8% | 120.119 | 105.7685 | 0.01 | 0.02 | -1435.05 | 134.4695 | 1.496% | 121.249 | 108.256 | 0.01 | 0.02 | -1299.3 | 134.242 | 1.635% | 149.6% | 0.9689% | 0.9858% | 1.003% | 1.02% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.121% | 1.138% | 1.154% | 1.171% | 1.188% | 1.205% | 1.222% | 1.239% | 1.256% | 1.273% | 1.289% | 0.00039238 | 0.00039921 | 0.00040605 | 0.00041288 | 0.00041971 | 0.00042654 | 0.00043338 | 0.00044021 | 0.00044704 | 0.00045387 | 0.00046071 | 0.00046754 | 0.00047437 | 0.0004812 | 0.00048804 | 0.00049487 | 0.0005017 | 0.00050854 | 0.00051537 | 0.0005222
| 10382652 | SHN011 | SHN | 16916086 | 16916091 | 1.4937 | 145.3986 | -36.3224 | 113 | 99.5 | 6.3% | 8.8% | 120.119 | 105.7685 | 0.01 | 0.02 | -1435.05 | 134.4695 | 1.496% | 121.249 | 108.256 | 0.01 | 0.02 | -1299.3 | 134.242 | 1.635% | 149.6% | 0.9689% | 0.9858% | 1.003% | 1.02% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.121% | 1.138% | 1.154% | 1.171% | 1.188% | 1.205% | 1.222% | 1.239% | 1.256% | 1.273% | 1.289% | 0.00039238 | 0.00039921 | 0.00040605 | 0.00041288 | 0.00041971 | 0.00042654 | 0.00043338 | 0.00044021 | 0.00044704 | 0.00045387 | 0.00046071 | 0.00046754 | 0.00047437 | 0.0004812 | 0.00048804 | 0.00049487 | 0.0005017 | 0.00050854 | 0.00051537 | 0.0005222
| 10382708 | SHN011 | SHN | 16916314 | 16916309 | 0.28771 | 145.3952 | -36.2816 | 113 | 99.4 | 6.3% | 8.8% | 120.119 | 105.6622 | 0.01 | 0.02 | -1445.68 | 134.5758 | 1.492% | 121.249 | 108.1472 | 0.01 | 0.02 | -1310.18 | 134.3508 | 1.63% | 149.2% | 0.9685% | 0.9853% | 1.002% | 1.019% | 1.036% | 1.052% | 1.069% | 1.086% | 1.102% | 1.119% | 1.136% | 1.153% | 1.169% | 1.186% | 1.203% | 1.22% | 1.236% | 1.253% | 1.27% | 1.287% | 0.00039223 | 0.00039901 | 0.00040579 | 0.00041258 | 0.00041936 | 0.00042614 | 0.00043292 | 0.00043971 | 0.00044649 | 0.00045327 | 0.00046005 | 0.00046684 | 0.00047362 | 0.0004804 | 0.00048718 | 0.00049397 | 0.00050075 | 0.00050753 | 0.00051431 | 0.0005211
| 10383250 | MBN032 | MBN | 16919055 | 16919050 | 1.2467 | 142.1076 | -34.2468 | 112 | 97.5 | 6.3% | 8.8% | 119.056 | 103.6425 | 0.01 | 0.02 | -1541.35 | 134.4695 | 1.458% | 120.176 | 106.08 | 0.01 | 0.02 | -1409.6 | 134.272 | 1.58% | 145.8% | 0.965% | 0.9806% | 0.9961% | 1.012% | 1.027% | 1.043% | 1.058% | 1.074% | 1.09% | 1.105% | 1.121% | 1.136% | 1.152% | 1.167% | 1.183% | 1.199% | 1.214% | 1.23% | 1.245% | 1.261% | 0.0003908 | 0.0003971 | 0.00040341 | 0.00040971 | 0.00041602 | 0.00042232 | 0.00042863 | 0.00043493 | 0.00044124 | 0.00044754 | 0.00045385 | 0.00046015 | 0.00046646 | 0.00047276 | 0.00047907 | 0.00048538 | 0.00049168 | 0.00049799 | 0.00050429 | 0.0005106
| 10383467 | MBN032 | MBN | 16919942 | 16919951 | 0.17236 | 142.0889 | -34.245 | 112 | 97.2 | 6.3% | 8.8% | 119.056 | 103.3236 | 0.01 | 0.02 | -1573.24 | 134.7884 | 1.449% | 120.176 | 105.7536 | 0.01 | 0.02 | -1442.24 | 134.5984 | 1.567% | 144.9% | 0.964% | 0.9793% | 0.9945% | 1.01% | 1.025% | 1.04% | 1.056% | 1.071% | 1.086% | 1.101% | 1.117% | 1.132% | 1.147% | 1.162% | 1.178% | 1.193% | 1.208% | 1.223% | 1.239% | 1.254% | 0.00039041 | 0.00039659 | 0.00040277 | 0.00040895 | 0.00041512 | 0.0004213 | 0.00042748 | 0.00043366 | 0.00043983 | 0.00044601 | 0.00045219 | 0.00045836 | 0.00046454 | 0.00047072 | 0.0004769 | 0.00048307 | 0.00048925 | 0.00049543 | 0.00050161 | 0.00050778
| 10383807 | HTN034 | KGTS | 16921430 | 198357412 | 0.28727 | 141.0376 | -37.5333 | 110 | 94.5 | 5.4% | 7.3% | 115.94 | 99.603 | 0.01 | 0.02 | -1633.7 | 132.277 | 1.364% | 118.03 | 101.3985 | 0.01 | 0.02 | -1663.15 | 134.6615 | 1.483% | 136.4% | 0.9554% | 0.9677% | 0.9801% | 0.9925% | 1.005% | 1.017% | 1.03% | 1.042% | 1.054% | 1.067% | 1.079% | 1.091% | 1.104% | 1.116% | 1.128% | 1.141% | 1.153% | 1.166% | 1.178% | 1.19% | 0.00038691 | 0.00039191 | 0.00039692 | 0.00040193 | 0.00040694 | 0.00041194 | 0.00041695 | 0.00042196 | 0.00042697 | 0.00043198 | 0.00043698 | 0.00044199 | 0.000447 | 0.00045201 | 0.00045702 | 0.00046202 | 0.00046703 | 0.00047204 | 0.00047705 | 0.00048206
| 10383946 | CTN006 | CTN | 16921998 | 16921994 | 0.7128 | 143.3148 | -36.4673 | 97.9 | 88.3 | 6.3% | 8.8% | 104.0677 | 93.8629 | 0.01 | 0.02 | -1020.48 | 114.2725 | 1.604% | 105.0467 | 96.0704 | 0.01 | 0.02 | -897.63 | 114.023 | 1.796% | 160.4% | 0.9799% | 1% | 1.021% | 1.042% | 1.062% | 1.083% | 1.103% | 1.124% | 1.144% | 1.165% | 1.185% | 1.206% | 1.227% | 1.247% | 1.268% | 1.288% | 1.309% | 1.329% | 1.35% | 1.37% | 0.00039686 | 0.00040518 | 0.0004135 | 0.00042183 | 0.00043015 | 0.00043848 | 0.0004468 | 0.00045513 | 0.00046345 | 0.00047178 | 0.0004801 | 0.00048843 | 0.00049675 | 0.00050507 | 0.0005134 | 0.00052172 | 0.00053005 | 0.00053837 | 0.0005467 | 0.00055502
| 10383947 | CTN006 | CTN | 191736049 | 16921998 | 0.20949 | 143.3149 | -36.4687 | 97.9 | 88.3 | 6.3% | 8.8% | 104.0677 | 93.8629 | 0.01 | 0.02 | -1020.48 | 114.2725 | 1.604% | 105.0467 | 96.0704 | 0.01 | 0.02 | -897.63 | 114.023 | 1.796% | 160.4% | 0.9799% | 1% | 1.021% | 1.042% | 1.062% | 1.083% | 1.103% | 1.124% | 1.144% | 1.165% | 1.185% | 1.206% | 1.227% | 1.247% | 1.268% | 1.288% | 1.309% | 1.329% | 1.35% | 1.37% | 0.00039686 | 0.00040518 | 0.0004135 | 0.00042183 | 0.00043015 | 0.00043848 | 0.0004468 | 0.00045513 | 0.00046345 | 0.00047178 | 0.0004801 | 0.00048843 | 0.00049675 | 0.00050507 | 0.0005134 | 0.00052172 | 0.00053005 | 0.00053837 | 0.0005467 | 0.00055502
| 10385402 | CTN004 | CTN | 16928027 | 16928031 | 0.5689 | 143.4137 | -36.6224 | 105 | 94.6 | 6.3% | 8.8% | 111.615 | 100.5598 | 0.01 | 0.02 | -1105.52 | 122.6702 | 1.598% | 112.665 | 102.9248 | 0.01 | 0.02 | -974.02 | 122.4052 | 1.787% | 159.8% | 0.9793% | 0.9997% | 1.02% | 1.04% | 1.061% | 1.081% | 1.101% | 1.122% | 1.142% | 1.162% | 1.183% | 1.203% | 1.224% | 1.244% | 1.264% | 1.285% | 1.305% | 1.325% | 1.346% | 1.366% | 0.00039661 | 0.00040485 | 0.00041309 | 0.00042133 | 0.00042957 | 0.00043781 | 0.00044605 | 0.0004543 | 0.00046254 | 0.00047078 | 0.00047902 | 0.00048726 | 0.0004955 | 0.00050374 | 0.00051199 | 0.00052023 | 0.00052847 | 0.00053671 | 0.00054495 | 0.00055319
| 10385403 | CTN004 | CTN | 16928031 | 162642465 | 1.3263 | 143.4155 | -36.6198 | 105 | 94.6 | 6.3% | 8.8% | 111.615 | 100.5598 | 0.01 | 0.02 | -1105.52 | 122.6702 | 1.598% | 112.665 | 102.9248 | 0.01 | 0.02 | -974.02 | 122.4052 | 1.787% | 159.8% | 0.9793% | 0.9997% | 1.02% | 1.04% | 1.061% | 1.081% | 1.101% | 1.122% | 1.142% | 1.162% | 1.183% | 1.203% | 1.224% | 1.244% | 1.264% | 1.285% | 1.305% | 1.325% | 1.346% | 1.366% | 0.00039661 | 0.00040485 | 0.00041309 | 0.00042133 | 0.00042957 | 0.00043781 | 0.00044605 | 0.0004543 | 0.00046254 | 0.00047078 | 0.00047902 | 0.00048726 | 0.0004955 | 0.00050374 | 0.00051199 | 0.00052023 | 0.00052847 | 0.00053671 | 0.00054495 | 0.00055319
| 10386137 | CTN002 | CTN | 16931047 | 16931051 | 0.68465 | 143.8573 | -36.2263 | 105 | 93.6 | 6.3% | 8.8% | 111.615 | 99.4968 | 0.01 | 0.02 | -1211.82 | 123.7332 | 1.546% | 112.665 | 101.8368 | 0.01 | 0.02 | -1082.82 | 123.4932 | 1.708% | 154.6% | 0.974% | 0.9925% | 1.011% | 1.03% | 1.048% | 1.067% | 1.085% | 1.104% | 1.122% | 1.141% | 1.16% | 1.178% | 1.197% | 1.215% | 1.234% | 1.252% | 1.271% | 1.29% | 1.308% | 1.327% | 0.00039444 | 0.00040196 | 0.00040947 | 0.00041699 | 0.00042451 | 0.00043203 | 0.00043955 | 0.00044707 | 0.00045459 | 0.0004621 | 0.00046962 | 0.00047714 | 0.00048466 | 0.00049218 | 0.0004997 | 0.00050722 | 0.00051473 | 0.00052225 | 0.00052977 | 0.00053729
| 10386152 | CTN002 | CTN | 16931105 | 16987567 | 0.67138 | 143.8674 | -36.2216 | 105 | 94 | 6.3% | 8.8% | 111.615 | 99.922 | 0.01 | 0.02 | -1169.3 | 123.308 | 1.566% | 112.665 | 102.272 | 0.01 | 0.02 | -1039.3 | 123.058 | 1.738% | 156.6% | 0.976% | 0.9952% | 1.014% | 1.034% | 1.053% | 1.072% | 1.091% | 1.111% | 1.13% | 1.149% | 1.168% | 1.188% | 1.207% | 1.226% | 1.245% | 1.265% | 1.284% | 1.303% | 1.322% | 1.342% | 0.00039526 | 0.00040305 | 0.00041084 | 0.00041863 | 0.00042643 | 0.00043422 | 0.00044201 | 0.0004498 | 0.00045759 | 0.00046538 | 0.00047318 | 0.00048097 | 0.00048876 | 0.00049655 | 0.00050434 | 0.00051214 | 0.00051993 | 0.00052772 | 0.00053551 | 0.0005433
| 10386978 | SHN024 | SHN | 16934601 | 16934606 | 0.45794 | 145.434 | -36.3045 | 114 | 99.7 | 6.3% | 8.8% | 121.182 | 105.9811 | 0.01 | 0.02 | -1520.09 | 136.3829 | 1.472% | 122.322 | 108.4736 | 0.01 | 0.02 | -1384.84 | 136.1704 | 1.601% | 147.2% | 0.9665% | 0.9825% | 0.9986% | 1.015% | 1.031% | 1.047% | 1.063% | 1.079% | 1.095% | 1.111% | 1.127% | 1.143% | 1.159% | 1.175% | 1.191% | 1.208% | 1.224% | 1.24% | 1.256% | 1.272% | 0.0003914 | 0.00039791 | 0.00040442 | 0.00041093 | 0.00041743 | 0.00042394 | 0.00043045 | 0.00043696 | 0.00044346 | 0.00044997 | 0.00045648 | 0.00046299 | 0.00046949 | 0.000476 | 0.00048251 | 0.00048902 | 0.00049552 | 0.00050203 | 0.00050854 | 0.00051505
| 10386985 | SHN024 | SHN | 202715724 | 16934631 | 0.18084 | 145.4312 | -36.3088 | 114 | 99.7 | 6.3% | 8.8% | 121.182 | 105.9811 | 0.01 | 0.02 | -1520.09 | 136.3829 | 1.472% | 122.322 | 108.4736 | 0.01 | 0.02 | -1384.84 | 136.1704 | 1.601% | 147.2% | 0.9665% | 0.9825% | 0.9986% | 1.015% | 1.031% | 1.047% | 1.063% | 1.079% | 1.095% | 1.111% | 1.127% | 1.143% | 1.159% | 1.175% | 1.191% | 1.208% | 1.224% | 1.24% | 1.256% | 1.272% | 0.0003914 | 0.00039791 | 0.00040442 | 0.00041093 | 0.00041743 | 0.00042394 | 0.00043045 | 0.00043696 | 0.00044346 | 0.00044997 | 0.00045648 | 0.00046299 | 0.00046949 | 0.000476 | 0.00048251 | 0.00048902 | 0.00049552 | 0.00050203 | 0.00050854 | 0.00051505
| 10387051 | SHN011 | SHN | 16934885 | 16934889 | 0.96426 | 145.4371 | -36.2992 | 113 | 99.5 | 6.3% | 8.8% | 120.119 | 105.7685 | 0.01 | 0.02 | -1435.05 | 134.4695 | 1.496% | 121.249 | 108.256 | 0.01 | 0.02 | -1299.3 | 134.242 | 1.635% | 149.6% | 0.9689% | 0.9858% | 1.003% | 1.02% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.121% | 1.138% | 1.154% | 1.171% | 1.188% | 1.205% | 1.222% | 1.239% | 1.256% | 1.273% | 1.289% | 0.00039238 | 0.00039921 | 0.00040605 | 0.00041288 | 0.00041971 | 0.00042654 | 0.00043338 | 0.00044021 | 0.00044704 | 0.00045387 | 0.00046071 | 0.00046754 | 0.00047437 | 0.0004812 | 0.00048804 | 0.00049487 | 0.0005017 | 0.00050854 | 0.00051537 | 0.0005222
| 10387092 | SHN021 | SHN | 16935070 | 16935066 | 0.43027 | 145.3722 | -36.3234 | 112 | 98.9 | 6.3% | 8.8% | 119.056 | 105.1307 | 0.01 | 0.02 | -1392.53 | 132.9813 | 1.507% | 120.176 | 107.6032 | 0.01 | 0.02 | -1257.28 | 132.7488 | 1.65% | 150.7% | 0.97% | 0.9872% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.091% | 1.108% | 1.125% | 1.142% | 1.16% | 1.177% | 1.194% | 1.211% | 1.228% | 1.246% | 1.263% | 1.28% | 1.297% | 0.00039282 | 0.0003998 | 0.00040678 | 0.00041376 | 0.00042073 | 0.00042771 | 0.00043469 | 0.00044167 | 0.00044865 | 0.00045563 | 0.00046261 | 0.00046959 | 0.00047657 | 0.00048355 | 0.00049053 | 0.0004975 | 0.00050448 | 0.00051146 | 0.00051844 | 0.00052542
| 10387109 | SHN021 | SHN | 16935117 | 16935121 | 0.11031 | 145.3687 | -36.3119 | 112 | 98.9 | 6.3% | 8.8% | 119.056 | 105.1307 | 0.01 | 0.02 | -1392.53 | 132.9813 | 1.507% | 120.176 | 107.6032 | 0.01 | 0.02 | -1257.28 | 132.7488 | 1.65% | 150.7% | 0.97% | 0.9872% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.091% | 1.108% | 1.125% | 1.142% | 1.16% | 1.177% | 1.194% | 1.211% | 1.228% | 1.246% | 1.263% | 1.28% | 1.297% | 0.00039282 | 0.0003998 | 0.00040678 | 0.00041376 | 0.00042073 | 0.00042771 | 0.00043469 | 0.00044167 | 0.00044865 | 0.00045563 | 0.00046261 | 0.00046959 | 0.00047657 | 0.00048355 | 0.00049053 | 0.0004975 | 0.00050448 | 0.00051146 | 0.00051844 | 0.00052542
| 10387129 | SHN011 | SHN | 16935201 | 16935205 | 1.038 | 145.3897 | -36.2993 | 113 | 99.4 | 6.3% | 8.8% | 120.119 | 105.6622 | 0.01 | 0.02 | -1445.68 | 134.5758 | 1.492% | 121.249 | 108.1472 | 0.01 | 0.02 | -1310.18 | 134.3508 | 1.63% | 149.2% | 0.9685% | 0.9853% | 1.002% | 1.019% | 1.036% | 1.052% | 1.069% | 1.086% | 1.102% | 1.119% | 1.136% | 1.153% | 1.169% | 1.186% | 1.203% | 1.22% | 1.236% | 1.253% | 1.27% | 1.287% | 0.00039223 | 0.00039901 | 0.00040579 | 0.00041258 | 0.00041936 | 0.00042614 | 0.00043292 | 0.00043971 | 0.00044649 | 0.00045327 | 0.00046005 | 0.00046684 | 0.00047362 | 0.0004804 | 0.00048718 | 0.00049397 | 0.00050075 | 0.00050753 | 0.00051431 | 0.0005211
| 10387271 | SHN011 | SHN | 16935750 | 16935745 | 0.54118 | 145.4267 | -36.2991 | 113 | 99.5 | 6.3% | 8.8% | 120.119 | 105.7685 | 0.01 | 0.02 | -1435.05 | 134.4695 | 1.496% | 121.249 | 108.256 | 0.01 | 0.02 | -1299.3 | 134.242 | 1.635% | 149.6% | 0.9689% | 0.9858% | 1.003% | 1.02% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.121% | 1.138% | 1.154% | 1.171% | 1.188% | 1.205% | 1.222% | 1.239% | 1.256% | 1.273% | 1.289% | 0.00039238 | 0.00039921 | 0.00040605 | 0.00041288 | 0.00041971 | 0.00042654 | 0.00043338 | 0.00044021 | 0.00044704 | 0.00045387 | 0.00046071 | 0.00046754 | 0.00047437 | 0.0004812 | 0.00048804 | 0.00049487 | 0.0005017 | 0.00050854 | 0.00051537 | 0.0005222
| 10388106 | MNA021 | MNA | 17273722 | 16939299 | 0.20645 | 145.3253 | -36.4243 | 113 | 99.4 | 6.3% | 8.8% | 120.119 | 105.6622 | 0.01 | 0.02 | -1445.68 | 134.5758 | 1.492% | 121.249 | 108.1472 | 0.01 | 0.02 | -1310.18 | 134.3508 | 1.63% | 149.2% | 0.9685% | 0.9853% | 1.002% | 1.019% | 1.036% | 1.052% | 1.069% | 1.086% | 1.102% | 1.119% | 1.136% | 1.153% | 1.169% | 1.186% | 1.203% | 1.22% | 1.236% | 1.253% | 1.27% | 1.287% | 0.00039223 | 0.00039901 | 0.00040579 | 0.00041258 | 0.00041936 | 0.00042614 | 0.00043292 | 0.00043971 | 0.00044649 | 0.00045327 | 0.00046005 | 0.00046684 | 0.00047362 | 0.0004804 | 0.00048718 | 0.00049397 | 0.00050075 | 0.00050753 | 0.00051431 | 0.0005211
| 10388760 | HTN034 | KGTS | 16942167 | 16942171 | 1.3142 | 141.2426 | -37.6772 | 108 | 92.5 | 5.4% | 7.3% | 113.832 | 97.495 | 0.01 | 0.02 | -1633.7 | 130.169 | 1.357% | 115.884 | 99.2525 | 0.01 | 0.02 | -1663.15 | 132.5155 | 1.474% | 135.7% | 0.9547% | 0.9668% | 0.979% | 0.9911% | 1.003% | 1.015% | 1.028% | 1.04% | 1.052% | 1.064% | 1.076% | 1.088% | 1.1% | 1.113% | 1.125% | 1.137% | 1.149% | 1.161% | 1.173% | 1.185% | 0.00038663 | 0.00039155 | 0.00039647 | 0.00040138 | 0.0004063 | 0.00041122 | 0.00041613 | 0.00042105 | 0.00042597 | 0.00043088 | 0.0004358 | 0.00044072 | 0.00044563 | 0.00045055 | 0.00045547 | 0.00046038 | 0.0004653 | 0.00047022 | 0.00047514 | 0.00048005
| 10389372 | GHP022 | GHP | 16944725 | 16944734 | 1.2261 | 144.2615 | -38.0429 | 109 | 95.7 | 5.4% | 7.3% | 114.886 | 100.8678 | 0.01 | 0.02 | -1401.82 | 128.9042 | 1.42% | 116.957 | 102.6861 | 0.01 | 0.02 | -1427.09 | 131.2279 | 1.558% | 142% | 0.9611% | 0.9754% | 0.9897% | 1.004% | 1.018% | 1.033% | 1.047% | 1.061% | 1.075% | 1.09% | 1.104% | 1.118% | 1.132% | 1.147% | 1.161% | 1.175% | 1.19% | 1.204% | 1.218% | 1.232% | 0.00038923 | 0.00039501 | 0.0004008 | 0.00040658 | 0.00041236 | 0.00041815 | 0.00042393 | 0.00042971 | 0.0004355 | 0.00044128 | 0.00044706 | 0.00045285 | 0.00045863 | 0.00046441 | 0.0004702 | 0.00047598 | 0.00048176 | 0.00048755 | 0.00049333 | 0.00049911
| 10389980 | GHP021 | GHP | 16947256 | 17339656 | 1.0462 | 144.1506 | -38.1088 | 104 | 91.7 | 5.4% | 7.3% | 109.616 | 96.6518 | 0.01 | 0.02 | -1296.42 | 122.5802 | 1.433% | 111.592 | 98.3941 | 0.01 | 0.02 | -1319.79 | 124.7899 | 1.575% | 143.3% | 0.9625% | 0.9772% | 0.9919% | 1.007% | 1.021% | 1.036% | 1.051% | 1.066% | 1.08% | 1.095% | 1.11% | 1.125% | 1.139% | 1.154% | 1.169% | 1.183% | 1.198% | 1.213% | 1.228% | 1.242% | 0.00038978 | 0.00039575 | 0.00040171 | 0.00040768 | 0.00041365 | 0.00041961 | 0.00042558 | 0.00043155 | 0.00043751 | 0.00044348 | 0.00044945 | 0.00045541 | 0.00046138 | 0.00046735 | 0.00047331 | 0.00047928 | 0.00048525 | 0.00049121 | 0.00049718 | 0.00050315
| 10390524 | BMH005 | BBD | 16949674 | 16949628 | 1.675 | 144.275 | -37.704 | 134 | 118 | 5.4% | 7.3% | 141.236 | 124.372 | 0.01 | 0.02 | -1686.4 | 158.1 | 1.429% | 143.782 | 126.614 | 0.01 | 0.02 | -1716.8 | 160.95 | 1.57% | 142.9% | 0.9621% | 0.9766% | 0.9912% | 1.006% | 1.02% | 1.035% | 1.05% | 1.064% | 1.079% | 1.093% | 1.108% | 1.123% | 1.137% | 1.152% | 1.166% | 1.181% | 1.196% | 1.21% | 1.225% | 1.239% | 0.00038961 | 0.00039552 | 0.00040143 | 0.00040734 | 0.00041325 | 0.00041916 | 0.00042507 | 0.00043098 | 0.00043689 | 0.0004428 | 0.00044871 | 0.00045462 | 0.00046053 | 0.00046644 | 0.00047235 | 0.00047826 | 0.00048417 | 0.00049008 | 0.00049599 | 0.0005019
| 10391055 | CHM011 | CHM | 16951907 | 153909862 | 0.74887 | 141.0027 | -37.1703 | 111 | 95.1 | 6.3% | 8.8% | 117.993 | 101.0913 | 0.01 | 0.02 | -1690.17 | 134.8947 | 1.414% | 119.103 | 103.4688 | 0.01 | 0.02 | -1563.42 | 134.7372 | 1.518% | 141.4% | 0.9605% | 0.9746% | 0.9886% | 1.003% | 1.017% | 1.031% | 1.045% | 1.059% | 1.073% | 1.087% | 1.101% | 1.115% | 1.129% | 1.143% | 1.157% | 1.172% | 1.186% | 1.2% | 1.214% | 1.228% | 0.00038898 | 0.00039468 | 0.00040037 | 0.00040607 | 0.00041177 | 0.00041747 | 0.00042317 | 0.00042887 | 0.00043457 | 0.00044027 | 0.00044596 | 0.00045166 | 0.00045736 | 0.00046306 | 0.00046876 | 0.00047446 | 0.00048016 | 0.00048586 | 0.00049155 | 0.00049725
| 10391593 | CHM011 | CHM | 16954636 | 16954664 | 0.10304 | 141.38 | -37.2602 | 117 | 99.9 | 5.4% | 7.3% | 123.318 | 105.2946 | 0.01 | 0.02 | -1802.34 | 141.3414 | 1.351% | 125.541 | 107.1927 | 0.01 | 0.02 | -1834.83 | 143.8893 | 1.465% | 135.1% | 0.954% | 0.966% | 0.9779% | 0.9898% | 1.002% | 1.014% | 1.026% | 1.037% | 1.049% | 1.061% | 1.073% | 1.085% | 1.097% | 1.109% | 1.121% | 1.133% | 1.145% | 1.157% | 1.169% | 1.181% | 0.00038637 | 0.00039119 | 0.00039602 | 0.00040085 | 0.00040568 | 0.00041051 | 0.00041534 | 0.00042016 | 0.00042499 | 0.00042982 | 0.00043465 | 0.00043948 | 0.0004443 | 0.00044913 | 0.00045396 | 0.00045879 | 0.00046362 | 0.00046845 | 0.00047327 | 0.0004781
| 10394458 | SHTSKYM1 | KYM | 183080865 | 16967385 | 1.1839 | 145.3818 | -36.3476 | 113 | 99.7 | 6.3% | 8.8% | 120.119 | 105.9811 | 0.01 | 0.02 | -1413.79 | 134.2569 | 1.504% | 121.249 | 108.4736 | 0.01 | 0.02 | -1277.54 | 134.0244 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039269 | 0.00039962 | 0.00040656 | 0.00041349 | 0.00042043 | 0.00042737 | 0.0004343 | 0.00044124 | 0.00044817 | 0.00045511 | 0.00046204 | 0.00046898 | 0.00047591 | 0.00048285 | 0.00048978 | 0.00049672 | 0.00050366 | 0.00051059 | 0.00051753 | 0.00052446
| 10394464 | SHTSKYM1 | KYM | 16967385 | 202105573 | 1.2999 | 145.3808 | -36.3478 | 113 | 99.7 | 6.3% | 8.8% | 120.119 | 105.9811 | 0.01 | 0.02 | -1413.79 | 134.2569 | 1.504% | 121.249 | 108.4736 | 0.01 | 0.02 | -1277.54 | 134.0244 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039269 | 0.00039962 | 0.00040656 | 0.00041349 | 0.00042043 | 0.00042737 | 0.0004343 | 0.00044124 | 0.00044817 | 0.00045511 | 0.00046204 | 0.00046898 | 0.00047591 | 0.00048285 | 0.00048978 | 0.00049672 | 0.00050366 | 0.00051059 | 0.00051753 | 0.00052446
| 10394473 | SHTSMNA | KYM | 16967418 | 17551293 | 0.4802 | 145.3766 | -36.3477 | 113 | 99.7 | 6.3% | 8.8% | 120.119 | 105.9811 | 0.01 | 0.02 | -1413.79 | 134.2569 | 1.504% | 121.249 | 108.4736 | 0.01 | 0.02 | -1277.54 | 134.0244 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039269 | 0.00039962 | 0.00040656 | 0.00041349 | 0.00042043 | 0.00042737 | 0.0004343 | 0.00044124 | 0.00044817 | 0.00045511 | 0.00046204 | 0.00046898 | 0.00047591 | 0.00048285 | 0.00048978 | 0.00049672 | 0.00050366 | 0.00051059 | 0.00051753 | 0.00052446
| 10395561 | RCT015 | RCTS | 16973059 | 16973063 | 0.60705 | 142.2191 | -34.2478 | 112 | 97.4 | 6.3% | 8.8% | 119.056 | 103.5362 | 0.01 | 0.02 | -1551.98 | 134.5758 | 1.455% | 120.176 | 105.9712 | 0.01 | 0.02 | -1420.48 | 134.3808 | 1.576% | 145.5% | 0.9647% | 0.9801% | 0.9956% | 1.011% | 1.027% | 1.042% | 1.057% | 1.073% | 1.088% | 1.104% | 1.119% | 1.135% | 1.15% | 1.166% | 1.181% | 1.197% | 1.212% | 1.228% | 1.243% | 1.258% | 0.00039067 | 0.00039693 | 0.00040319 | 0.00040945 | 0.00041572 | 0.00042198 | 0.00042824 | 0.0004345 | 0.00044076 | 0.00044703 | 0.00045329 | 0.00045955 | 0.00046581 | 0.00047207 | 0.00047834 | 0.0004846 | 0.00049086 | 0.00049712 | 0.00050338 | 0.00050965
| 10395563 | RCT015 | RCTS | 17659083 | 16973072 | 0.6836 | 142.2194 | -34.2495 | 112 | 97.4 | 6.3% | 8.8% | 119.056 | 103.5362 | 0.01 | 0.02 | -1551.98 | 134.5758 | 1.455% | 120.176 | 105.9712 | 0.01 | 0.02 | -1420.48 | 134.3808 | 1.576% | 145.5% | 0.9647% | 0.9801% | 0.9956% | 1.011% | 1.027% | 1.042% | 1.057% | 1.073% | 1.088% | 1.104% | 1.119% | 1.135% | 1.15% | 1.166% | 1.181% | 1.197% | 1.212% | 1.228% | 1.243% | 1.258% | 0.00039067 | 0.00039693 | 0.00040319 | 0.00040945 | 0.00041572 | 0.00042198 | 0.00042824 | 0.0004345 | 0.00044076 | 0.00044703 | 0.00045329 | 0.00045955 | 0.00046581 | 0.00047207 | 0.00047834 | 0.0004846 | 0.00049086 | 0.00049712 | 0.00050338 | 0.00050965
| 10395566 | RCT015 | RCTS | 16973081 | 16973085 | 1.5986 | 142.2241 | -34.2516 | 112 | 97.3 | 6.3% | 8.8% | 119.056 | 103.4299 | 0.01 | 0.02 | -1562.61 | 134.6821 | 1.452% | 120.176 | 105.8624 | 0.01 | 0.02 | -1431.36 | 134.4896 | 1.571% | 145.2% | 0.9643% | 0.9797% | 0.9951% | 1.01% | 1.026% | 1.041% | 1.056% | 1.072% | 1.087% | 1.103% | 1.118% | 1.133% | 1.149% | 1.164% | 1.179% | 1.195% | 1.21% | 1.225% | 1.241% | 1.256% | 0.00039054 | 0.00039676 | 0.00040298 | 0.0004092 | 0.00041542 | 0.00042164 | 0.00042786 | 0.00043408 | 0.0004403 | 0.00044651 | 0.00045273 | 0.00045895 | 0.00046517 | 0.00047139 | 0.00047761 | 0.00048383 | 0.00049005 | 0.00049627 | 0.00050249 | 0.00050871
| 10395712 | RCT011 | RCTS | 16973711 | 16973715 | 0.35516 | 142.2201 | -34.2632 | 112 | 97.3 | 6.3% | 8.8% | 119.056 | 103.4299 | 0.01 | 0.02 | -1562.61 | 134.6821 | 1.452% | 120.176 | 105.8624 | 0.01 | 0.02 | -1431.36 | 134.4896 | 1.571% | 145.2% | 0.9643% | 0.9797% | 0.9951% | 1.01% | 1.026% | 1.041% | 1.056% | 1.072% | 1.087% | 1.103% | 1.118% | 1.133% | 1.149% | 1.164% | 1.179% | 1.195% | 1.21% | 1.225% | 1.241% | 1.256% | 0.00039054 | 0.00039676 | 0.00040298 | 0.0004092 | 0.00041542 | 0.00042164 | 0.00042786 | 0.00043408 | 0.0004403 | 0.00044651 | 0.00045273 | 0.00045895 | 0.00046517 | 0.00047139 | 0.00047761 | 0.00048383 | 0.00049005 | 0.00049627 | 0.00050249 | 0.00050871
| 10395713 | RCT011 | RCTS | 16973715 | 95332489 | 0.61433 | 142.2199 | -34.2621 | 112 | 97.3 | 6.3% | 8.8% | 119.056 | 103.4299 | 0.01 | 0.02 | -1562.61 | 134.6821 | 1.452% | 120.176 | 105.8624 | 0.01 | 0.02 | -1431.36 | 134.4896 | 1.571% | 145.2% | 0.9643% | 0.9797% | 0.9951% | 1.01% | 1.026% | 1.041% | 1.056% | 1.072% | 1.087% | 1.103% | 1.118% | 1.133% | 1.149% | 1.164% | 1.179% | 1.195% | 1.21% | 1.225% | 1.241% | 1.256% | 0.00039054 | 0.00039676 | 0.00040298 | 0.0004092 | 0.00041542 | 0.00042164 | 0.00042786 | 0.00043408 | 0.0004403 | 0.00044651 | 0.00045273 | 0.00045895 | 0.00046517 | 0.00047139 | 0.00047761 | 0.00048383 | 0.00049005 | 0.00049627 | 0.00050249 | 0.00050871
| 10395714 | RCT011 | RCTS | 17780241 | 16973723 | 0.24016 | 142.2191 | -34.2576 | 112 | 97.3 | 6.3% | 8.8% | 119.056 | 103.4299 | 0.01 | 0.02 | -1562.61 | 134.6821 | 1.452% | 120.176 | 105.8624 | 0.01 | 0.02 | -1431.36 | 134.4896 | 1.571% | 145.2% | 0.9643% | 0.9797% | 0.9951% | 1.01% | 1.026% | 1.041% | 1.056% | 1.072% | 1.087% | 1.103% | 1.118% | 1.133% | 1.149% | 1.164% | 1.179% | 1.195% | 1.21% | 1.225% | 1.241% | 1.256% | 0.00039054 | 0.00039676 | 0.00040298 | 0.0004092 | 0.00041542 | 0.00042164 | 0.00042786 | 0.00043408 | 0.0004403 | 0.00044651 | 0.00045273 | 0.00045895 | 0.00046517 | 0.00047139 | 0.00047761 | 0.00048383 | 0.00049005 | 0.00049627 | 0.00050249 | 0.00050871
| 10400226 | MDA023 | MDA | 16994150 | 41847294 | 0.53619 | 142.1045 | -34.2706 | 112 | 97.3 | 6.3% | 8.8% | 119.056 | 103.4299 | 0.01 | 0.02 | -1562.61 | 134.6821 | 1.452% | 120.176 | 105.8624 | 0.01 | 0.02 | -1431.36 | 134.4896 | 1.571% | 145.2% | 0.9643% | 0.9797% | 0.9951% | 1.01% | 1.026% | 1.041% | 1.056% | 1.072% | 1.087% | 1.103% | 1.118% | 1.133% | 1.149% | 1.164% | 1.179% | 1.195% | 1.21% | 1.225% | 1.241% | 1.256% | 0.00039054 | 0.00039676 | 0.00040298 | 0.0004092 | 0.00041542 | 0.00042164 | 0.00042786 | 0.00043408 | 0.0004403 | 0.00044651 | 0.00045273 | 0.00045895 | 0.00046517 | 0.00047139 | 0.00047761 | 0.00048383 | 0.00049005 | 0.00049627 | 0.00050249 | 0.00050871
| 10400310 | MDA023 | MDA | 16994529 | 16994534 | 0.21709 | 142.09 | -34.2697 | 111 | 96.5 | 6.3% | 8.8% | 117.993 | 102.5795 | 0.01 | 0.02 | -1541.35 | 133.4065 | 1.454% | 119.103 | 104.992 | 0.01 | 0.02 | -1411.1 | 133.214 | 1.574% | 145.4% | 0.9646% | 0.98% | 0.9954% | 1.011% | 1.026% | 1.042% | 1.057% | 1.073% | 1.088% | 1.103% | 1.119% | 1.134% | 1.15% | 1.165% | 1.181% | 1.196% | 1.211% | 1.227% | 1.242% | 1.258% | 0.00039063 | 0.00039688 | 0.00040313 | 0.00040937 | 0.00041562 | 0.00042187 | 0.00042812 | 0.00043437 | 0.00044062 | 0.00044687 | 0.00045312 | 0.00045937 | 0.00046562 | 0.00047186 | 0.00047811 | 0.00048436 | 0.00049061 | 0.00049686 | 0.00050311 | 0.00050936
| 10400311 | MDA023 | MDA | 16994534 | 16994548 | 2.0357 | 142.089 | -34.2706 | 111 | 96.5 | 6.3% | 8.8% | 117.993 | 102.5795 | 0.01 | 0.02 | -1541.35 | 133.4065 | 1.454% | 119.103 | 104.992 | 0.01 | 0.02 | -1411.1 | 133.214 | 1.574% | 145.4% | 0.9646% | 0.98% | 0.9954% | 1.011% | 1.026% | 1.042% | 1.057% | 1.073% | 1.088% | 1.103% | 1.119% | 1.134% | 1.15% | 1.165% | 1.181% | 1.196% | 1.211% | 1.227% | 1.242% | 1.258% | 0.00039063 | 0.00039688 | 0.00040313 | 0.00040937 | 0.00041562 | 0.00042187 | 0.00042812 | 0.00043437 | 0.00044062 | 0.00044687 | 0.00045312 | 0.00045937 | 0.00046562 | 0.00047186 | 0.00047811 | 0.00048436 | 0.00049061 | 0.00049686 | 0.00050311 | 0.00050936
| 10400312 | MDA023 | MDA | 16994548 | 16994539 | 0.57829 | 142.0882 | -34.2712 | 111 | 96.5 | 6.3% | 8.8% | 117.993 | 102.5795 | 0.01 | 0.02 | -1541.35 | 133.4065 | 1.454% | 119.103 | 104.992 | 0.01 | 0.02 | -1411.1 | 133.214 | 1.574% | 145.4% | 0.9646% | 0.98% | 0.9954% | 1.011% | 1.026% | 1.042% | 1.057% | 1.073% | 1.088% | 1.103% | 1.119% | 1.134% | 1.15% | 1.165% | 1.181% | 1.196% | 1.211% | 1.227% | 1.242% | 1.258% | 0.00039063 | 0.00039688 | 0.00040313 | 0.00040937 | 0.00041562 | 0.00042187 | 0.00042812 | 0.00043437 | 0.00044062 | 0.00044687 | 0.00045312 | 0.00045937 | 0.00046562 | 0.00047186 | 0.00047811 | 0.00048436 | 0.00049061 | 0.00049686 | 0.00050311 | 0.00050936
| 10402508 | RCT011 | RCTS | 41070651 | 17003430 | 0.50916 | 142.228 | -34.2803 | 111 | 96.6 | 6.3% | 8.8% | 117.993 | 102.6858 | 0.01 | 0.02 | -1530.72 | 133.3002 | 1.457% | 119.103 | 105.1008 | 0.01 | 0.02 | -1400.22 | 133.1052 | 1.579% | 145.7% | 0.9649% | 0.9804% | 0.996% | 1.011% | 1.027% | 1.043% | 1.058% | 1.074% | 1.089% | 1.105% | 1.12% | 1.136% | 1.151% | 1.167% | 1.182% | 1.198% | 1.213% | 1.229% | 1.245% | 1.26% | 0.00039076 | 0.00039705 | 0.00040334 | 0.00040964 | 0.00041593 | 0.00042222 | 0.00042851 | 0.0004348 | 0.0004411 | 0.00044739 | 0.00045368 | 0.00045997 | 0.00046627 | 0.00047256 | 0.00047885 | 0.00048514 | 0.00049144 | 0.00049773 | 0.00050402 | 0.00051031
| 10402528 | RCT011 | RCTS | 17003510 | 17780249 | 0.39323 | 142.2233 | -34.271 | 112 | 97.3 | 6.3% | 8.8% | 119.056 | 103.4299 | 0.01 | 0.02 | -1562.61 | 134.6821 | 1.452% | 120.176 | 105.8624 | 0.01 | 0.02 | -1431.36 | 134.4896 | 1.571% | 145.2% | 0.9643% | 0.9797% | 0.9951% | 1.01% | 1.026% | 1.041% | 1.056% | 1.072% | 1.087% | 1.103% | 1.118% | 1.133% | 1.149% | 1.164% | 1.179% | 1.195% | 1.21% | 1.225% | 1.241% | 1.256% | 0.00039054 | 0.00039676 | 0.00040298 | 0.0004092 | 0.00041542 | 0.00042164 | 0.00042786 | 0.00043408 | 0.0004403 | 0.00044651 | 0.00045273 | 0.00045895 | 0.00046517 | 0.00047139 | 0.00047761 | 0.00048383 | 0.00049005 | 0.00049627 | 0.00050249 | 0.00050871
| 10403961 | CLC003 | CLC | 17009631 | 17009626 | 0.49352 | 143.3807 | -38.555 | 106 | 92.3 | 5.4% | 7.3% | 111.724 | 97.2842 | 0.01 | 0.02 | -1443.98 | 126.1638 | 1.396% | 113.738 | 99.0379 | 0.01 | 0.02 | -1470.01 | 128.4381 | 1.526% | 139.6% | 0.9587% | 0.9722% | 0.9857% | 0.9992% | 1.013% | 1.026% | 1.04% | 1.053% | 1.067% | 1.08% | 1.094% | 1.107% | 1.121% | 1.134% | 1.147% | 1.161% | 1.174% | 1.188% | 1.201% | 1.215% | 0.00038826 | 0.00039372 | 0.00039918 | 0.00040464 | 0.0004101 | 0.00041556 | 0.00042102 | 0.00042648 | 0.00043194 | 0.0004374 | 0.00044286 | 0.00044832 | 0.00045378 | 0.00045924 | 0.0004647 | 0.00047016 | 0.00047562 | 0.00048108 | 0.00048654 | 0.000492
| 10403963 | CLC003 | CLC | 17563229 | 17009626 | 0.26822 | 143.3809 | -38.5539 | 106 | 92.3 | 5.4% | 7.3% | 111.724 | 97.2842 | 0.01 | 0.02 | -1443.98 | 126.1638 | 1.396% | 113.738 | 99.0379 | 0.01 | 0.02 | -1470.01 | 128.4381 | 1.526% | 139.6% | 0.9587% | 0.9722% | 0.9857% | 0.9992% | 1.013% | 1.026% | 1.04% | 1.053% | 1.067% | 1.08% | 1.094% | 1.107% | 1.121% | 1.134% | 1.147% | 1.161% | 1.174% | 1.188% | 1.201% | 1.215% | 0.00038826 | 0.00039372 | 0.00039918 | 0.00040464 | 0.0004101 | 0.00041556 | 0.00042102 | 0.00042648 | 0.00043194 | 0.0004374 | 0.00044286 | 0.00044832 | 0.00045378 | 0.00045924 | 0.0004647 | 0.00047016 | 0.00047562 | 0.00048108 | 0.00048654 | 0.000492
| 10403984 | CLC003 | CLC | 17009705 | 17009722 | 1.3513 | 143.395 | -38.5563 | 106 | 92.3 | 5.4% | 7.3% | 111.724 | 97.2842 | 0.01 | 0.02 | -1443.98 | 126.1638 | 1.396% | 113.738 | 99.0379 | 0.01 | 0.02 | -1470.01 | 128.4381 | 1.526% | 139.6% | 0.9587% | 0.9722% | 0.9857% | 0.9992% | 1.013% | 1.026% | 1.04% | 1.053% | 1.067% | 1.08% | 1.094% | 1.107% | 1.121% | 1.134% | 1.147% | 1.161% | 1.174% | 1.188% | 1.201% | 1.215% | 0.00038826 | 0.00039372 | 0.00039918 | 0.00040464 | 0.0004101 | 0.00041556 | 0.00042102 | 0.00042648 | 0.00043194 | 0.0004374 | 0.00044286 | 0.00044832 | 0.00045378 | 0.00045924 | 0.0004647 | 0.00047016 | 0.00047562 | 0.00048108 | 0.00048654 | 0.000492
| 10404053 | CLC003 | CLC | 17010016 | 17563233 | 0.76169 | 143.4078 | -38.5105 | 106 | 92.5 | 5.4% | 7.3% | 111.724 | 97.495 | 0.01 | 0.02 | -1422.9 | 125.953 | 1.402% | 113.738 | 99.2525 | 0.01 | 0.02 | -1448.55 | 128.2235 | 1.534% | 140.2% | 0.9593% | 0.973% | 0.9867% | 1% | 1.014% | 1.028% | 1.041% | 1.055% | 1.069% | 1.082% | 1.096% | 1.11% | 1.123% | 1.137% | 1.151% | 1.165% | 1.178% | 1.192% | 1.206% | 1.219% | 0.0003885 | 0.00039404 | 0.00039959 | 0.00040513 | 0.00041067 | 0.00041621 | 0.00042175 | 0.00042729 | 0.00043283 | 0.00043837 | 0.00044391 | 0.00044945 | 0.00045499 | 0.00046053 | 0.00046607 | 0.00047161 | 0.00047716 | 0.0004827 | 0.00048824 | 0.00049378
| 10404054 | CLC003 | CLC | 17010024 | 17010028 | 1.2291 | 143.4032 | -38.5188 | 106 | 92.5 | 5.4% | 7.3% | 111.724 | 97.495 | 0.01 | 0.02 | -1422.9 | 125.953 | 1.402% | 113.738 | 99.2525 | 0.01 | 0.02 | -1448.55 | 128.2235 | 1.534% | 140.2% | 0.9593% | 0.973% | 0.9867% | 1% | 1.014% | 1.028% | 1.041% | 1.055% | 1.069% | 1.082% | 1.096% | 1.11% | 1.123% | 1.137% | 1.151% | 1.165% | 1.178% | 1.192% | 1.206% | 1.219% | 0.0003885 | 0.00039404 | 0.00039959 | 0.00040513 | 0.00041067 | 0.00041621 | 0.00042175 | 0.00042729 | 0.00043283 | 0.00043837 | 0.00044391 | 0.00044945 | 0.00045499 | 0.00046053 | 0.00046607 | 0.00047161 | 0.00047716 | 0.0004827 | 0.00048824 | 0.00049378
| 10404060 | CLC003 | CLC | 17563233 | 17010042 | 0.39772 | 143.4098 | -38.5095 | 106 | 92.5 | 5.4% | 7.3% | 111.724 | 97.495 | 0.01 | 0.02 | -1422.9 | 125.953 | 1.402% | 113.738 | 99.2525 | 0.01 | 0.02 | -1448.55 | 128.2235 | 1.534% | 140.2% | 0.9593% | 0.973% | 0.9867% | 1% | 1.014% | 1.028% | 1.041% | 1.055% | 1.069% | 1.082% | 1.096% | 1.11% | 1.123% | 1.137% | 1.151% | 1.165% | 1.178% | 1.192% | 1.206% | 1.219% | 0.0003885 | 0.00039404 | 0.00039959 | 0.00040513 | 0.00041067 | 0.00041621 | 0.00042175 | 0.00042729 | 0.00043283 | 0.00043837 | 0.00044391 | 0.00044945 | 0.00045499 | 0.00046053 | 0.00046607 | 0.00047161 | 0.00047716 | 0.0004827 | 0.00048824 | 0.00049378
| 10408207 | SHTSKYM1 | KYM | 17027777 | 17027791 | 0.93246 | 145.3894 | -36.3475 | 113 | 99.7 | 6.3% | 8.8% | 120.119 | 105.9811 | 0.01 | 0.02 | -1413.79 | 134.2569 | 1.504% | 121.249 | 108.4736 | 0.01 | 0.02 | -1277.54 | 134.0244 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039269 | 0.00039962 | 0.00040656 | 0.00041349 | 0.00042043 | 0.00042737 | 0.0004343 | 0.00044124 | 0.00044817 | 0.00045511 | 0.00046204 | 0.00046898 | 0.00047591 | 0.00048285 | 0.00048978 | 0.00049672 | 0.00050366 | 0.00051059 | 0.00051753 | 0.00052446
| 10408211 | SHN021 | SHN | 17027915 | 17027786 | 0.11946 | 145.3902 | -36.3501 | 113 | 99.6 | 6.3% | 8.8% | 120.119 | 105.8748 | 0.01 | 0.02 | -1424.42 | 134.3632 | 1.5% | 121.249 | 108.3648 | 0.01 | 0.02 | -1288.42 | 134.1332 | 1.64% | 150% | 0.9693% | 0.9863% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039253 | 0.00039942 | 0.0004063 | 0.00041318 | 0.00042007 | 0.00042695 | 0.00043383 | 0.00044072 | 0.0004476 | 0.00045449 | 0.00046137 | 0.00046825 | 0.00047514 | 0.00048202 | 0.0004889 | 0.00049579 | 0.00050267 | 0.00050956 | 0.00051644 | 0.00052332
| 10408220 | SHN021 | SHN | 17028667 | 17027824 | 0.83149 | 145.3945 | -36.3506 | 113 | 99.6 | 6.3% | 8.8% | 120.119 | 105.8748 | 0.01 | 0.02 | -1424.42 | 134.3632 | 1.5% | 121.249 | 108.3648 | 0.01 | 0.02 | -1288.42 | 134.1332 | 1.64% | 150% | 0.9693% | 0.9863% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039253 | 0.00039942 | 0.0004063 | 0.00041318 | 0.00042007 | 0.00042695 | 0.00043383 | 0.00044072 | 0.0004476 | 0.00045449 | 0.00046137 | 0.00046825 | 0.00047514 | 0.00048202 | 0.0004889 | 0.00049579 | 0.00050267 | 0.00050956 | 0.00051644 | 0.00052332
| 10408238 | SHN021 | SHN | 17027911 | 17027920 | 0.31986 | 145.3864 | -36.3505 | 113 | 99.6 | 6.3% | 8.8% | 120.119 | 105.8748 | 0.01 | 0.02 | -1424.42 | 134.3632 | 1.5% | 121.249 | 108.3648 | 0.01 | 0.02 | -1288.42 | 134.1332 | 1.64% | 150% | 0.9693% | 0.9863% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039253 | 0.00039942 | 0.0004063 | 0.00041318 | 0.00042007 | 0.00042695 | 0.00043383 | 0.00044072 | 0.0004476 | 0.00045449 | 0.00046137 | 0.00046825 | 0.00047514 | 0.00048202 | 0.0004889 | 0.00049579 | 0.00050267 | 0.00050956 | 0.00051644 | 0.00052332
| 10408241 | SHN021 | SHN | 17028667 | 17027915 | 0.27215 | 145.3916 | -36.3508 | 113 | 99.6 | 6.3% | 8.8% | 120.119 | 105.8748 | 0.01 | 0.02 | -1424.42 | 134.3632 | 1.5% | 121.249 | 108.3648 | 0.01 | 0.02 | -1288.42 | 134.1332 | 1.64% | 150% | 0.9693% | 0.9863% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039253 | 0.00039942 | 0.0004063 | 0.00041318 | 0.00042007 | 0.00042695 | 0.00043383 | 0.00044072 | 0.0004476 | 0.00045449 | 0.00046137 | 0.00046825 | 0.00047514 | 0.00048202 | 0.0004889 | 0.00049579 | 0.00050267 | 0.00050956 | 0.00051644 | 0.00052332
| 10408242 | SHN021 | SHN | 17598251 | 17027915 | 0.1108 | 145.3895 | -36.3507 | 113 | 99.6 | 6.3% | 8.8% | 120.119 | 105.8748 | 0.01 | 0.02 | -1424.42 | 134.3632 | 1.5% | 121.249 | 108.3648 | 0.01 | 0.02 | -1288.42 | 134.1332 | 1.64% | 150% | 0.9693% | 0.9863% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039253 | 0.00039942 | 0.0004063 | 0.00041318 | 0.00042007 | 0.00042695 | 0.00043383 | 0.00044072 | 0.0004476 | 0.00045449 | 0.00046137 | 0.00046825 | 0.00047514 | 0.00048202 | 0.0004889 | 0.00049579 | 0.00050267 | 0.00050956 | 0.00051644 | 0.00052332
| 10408420 | SHN021 | SHN | 17028917 | 17028913 | 1.1087 | 145.3908 | -36.3532 | 113 | 99.6 | 6.3% | 8.8% | 120.119 | 105.8748 | 0.01 | 0.02 | -1424.42 | 134.3632 | 1.5% | 121.249 | 108.3648 | 0.01 | 0.02 | -1288.42 | 134.1332 | 1.64% | 150% | 0.9693% | 0.9863% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039253 | 0.00039942 | 0.0004063 | 0.00041318 | 0.00042007 | 0.00042695 | 0.00043383 | 0.00044072 | 0.0004476 | 0.00045449 | 0.00046137 | 0.00046825 | 0.00047514 | 0.00048202 | 0.0004889 | 0.00049579 | 0.00050267 | 0.00050956 | 0.00051644 | 0.00052332
| 10408427 | STN011 | STN | 17028963 | 17028967 | 0.16581 | 145.4481 | -36.414 | 116 | 102 | 6.3% | 8.8% | 123.308 | 108.426 | 0.01 | 0.02 | -1488.2 | 138.19 | 1.491% | 124.468 | 110.976 | 0.01 | 0.02 | -1349.2 | 137.96 | 1.628% | 149.1% | 0.9684% | 0.9851% | 1.002% | 1.018% | 1.035% | 1.052% | 1.069% | 1.085% | 1.102% | 1.119% | 1.135% | 1.152% | 1.169% | 1.185% | 1.202% | 1.219% | 1.236% | 1.252% | 1.269% | 1.286% | 0.00039217 | 0.00039894 | 0.0004057 | 0.00041246 | 0.00041923 | 0.00042599 | 0.00043275 | 0.00043952 | 0.00044628 | 0.00045304 | 0.00045981 | 0.00046657 | 0.00047334 | 0.0004801 | 0.00048686 | 0.00049363 | 0.00050039 | 0.00050715 | 0.00051392 | 0.00052068
| 10408436 | STN011 | STN | 17029006 | 17029011 | 0.79918 | 145.4543 | -36.4092 | 117 | 102 | 6.3% | 8.8% | 124.371 | 108.426 | 0.01 | 0.02 | -1594.5 | 140.316 | 1.462% | 125.541 | 110.976 | 0.01 | 0.02 | -1456.5 | 140.106 | 1.586% | 146.2% | 0.9654% | 0.9812% | 0.9969% | 1.013% | 1.028% | 1.044% | 1.06% | 1.075% | 1.091% | 1.107% | 1.123% | 1.138% | 1.154% | 1.17% | 1.186% | 1.201% | 1.217% | 1.233% | 1.248% | 1.264% | 0.00039098 | 0.00039735 | 0.00040372 | 0.00041008 | 0.00041645 | 0.00042282 | 0.00042919 | 0.00043555 | 0.00044192 | 0.00044829 | 0.00045465 | 0.00046102 | 0.00046739 | 0.00047376 | 0.00048012 | 0.00048649 | 0.00049286 | 0.00049922 | 0.00050559 | 0.00051196
| 10409274 | STN024 | STN | 203095893 | 17032634 | 0.13753 | 145.527 | -36.3681 | 116 | 101 | 6.3% | 8.8% | 123.308 | 107.363 | 0.01 | 0.02 | -1594.5 | 139.253 | 1.458% | 124.468 | 109.888 | 0.01 | 0.02 | -1458 | 139.048 | 1.581% | 145.8% | 0.965% | 0.9806% | 0.9962% | 1.012% | 1.027% | 1.043% | 1.059% | 1.074% | 1.09% | 1.105% | 1.121% | 1.137% | 1.152% | 1.168% | 1.183% | 1.199% | 1.214% | 1.23% | 1.246% | 1.261% | 0.00039082 | 0.00039713 | 0.00040345 | 0.00040976 | 0.00041607 | 0.00042238 | 0.0004287 | 0.00043501 | 0.00044132 | 0.00044763 | 0.00045395 | 0.00046026 | 0.00046657 | 0.00047288 | 0.0004792 | 0.00048551 | 0.00049182 | 0.00049814 | 0.00050445 | 0.00051076
| 10411123 | KGT004 | KGTS | 17039557 | 17039561 | 2.0596 | 143.8862 | -35.6872 | 108 | 95.3 | 6.3% | 8.8% | 114.804 | 101.3039 | 0.01 | 0.02 | -1350.01 | 128.3041 | 1.504% | 115.884 | 103.6864 | 0.01 | 0.02 | -1219.76 | 128.0816 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.073% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.193% | 1.21% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039271 | 0.00039965 | 0.00040659 | 0.00041353 | 0.00042047 | 0.00042742 | 0.00043436 | 0.0004413 | 0.00044824 | 0.00045518 | 0.00046212 | 0.00046907 | 0.00047601 | 0.00048295 | 0.00048989 | 0.00049683 | 0.00050377 | 0.00051072 | 0.00051766 | 0.0005246
| 10411149 | KGT004 | KGTS | 17039678 | 17039683 | 0.70209 | 143.8841 | -35.7246 | 108 | 95.4 | 6.3% | 8.8% | 114.804 | 101.4102 | 0.01 | 0.02 | -1339.38 | 128.1978 | 1.508% | 115.884 | 103.7952 | 0.01 | 0.02 | -1208.88 | 127.9728 | 1.652% | 150.8% | 0.9701% | 0.9874% | 1.005% | 1.022% | 1.039% | 1.056% | 1.074% | 1.091% | 1.108% | 1.126% | 1.143% | 1.16% | 1.177% | 1.195% | 1.212% | 1.229% | 1.247% | 1.264% | 1.281% | 1.298% | 0.00039287 | 0.00039987 | 0.00040687 | 0.00041386 | 0.00042086 | 0.00042786 | 0.00043485 | 0.00044185 | 0.00044885 | 0.00045584 | 0.00046284 | 0.00046984 | 0.00047683 | 0.00048383 | 0.00049083 | 0.00049782 | 0.00050482 | 0.00051182 | 0.00051882 | 0.00052581
| 10411734 | GHP022 | GHP | 17042081 | 17042085 | 0.81256 | 144.2678 | -38.0466 | 109 | 95.7 | 5.4% | 7.3% | 114.886 | 100.8678 | 0.01 | 0.02 | -1401.82 | 128.9042 | 1.42% | 116.957 | 102.6861 | 0.01 | 0.02 | -1427.09 | 131.2279 | 1.558% | 142% | 0.9611% | 0.9754% | 0.9897% | 1.004% | 1.018% | 1.033% | 1.047% | 1.061% | 1.075% | 1.09% | 1.104% | 1.118% | 1.132% | 1.147% | 1.161% | 1.175% | 1.19% | 1.204% | 1.218% | 1.232% | 0.00038923 | 0.00039501 | 0.0004008 | 0.00040658 | 0.00041236 | 0.00041815 | 0.00042393 | 0.00042971 | 0.0004355 | 0.00044128 | 0.00044706 | 0.00045285 | 0.00045863 | 0.00046441 | 0.0004702 | 0.00047598 | 0.00048176 | 0.00048755 | 0.00049333 | 0.00049911
| 10414656 | FNS012 | FNS | 17053568 | 17053560 | 0.78253 | 144.3609 | -38.0815 | 107 | 94.1 | 5.4% | 7.3% | 112.778 | 99.1814 | 0.01 | 0.02 | -1359.66 | 126.3746 | 1.425% | 114.811 | 100.9693 | 0.01 | 0.02 | -1384.17 | 128.6527 | 1.564% | 142.5% | 0.9616% | 0.9761% | 0.9905% | 1.005% | 1.019% | 1.034% | 1.048% | 1.063% | 1.077% | 1.092% | 1.106% | 1.121% | 1.135% | 1.15% | 1.164% | 1.178% | 1.193% | 1.207% | 1.222% | 1.236% | 0.00038944 | 0.00039529 | 0.00040115 | 0.000407 | 0.00041285 | 0.00041871 | 0.00042456 | 0.00043041 | 0.00043627 | 0.00044212 | 0.00044797 | 0.00045383 | 0.00045968 | 0.00046553 | 0.00047138 | 0.00047724 | 0.00048309 | 0.00048894 | 0.0004948 | 0.00050065
| 10419901 | CLC003 | CLC | 17076706 | 140237344 | 0.80049 | 143.4513 | -38.7751 | 125 | 108 | 5.4% | 7.3% | 131.75 | 113.832 | 0.01 | 0.02 | -1791.8 | 149.668 | 1.377% | 134.125 | 115.884 | 0.01 | 0.02 | -1824.1 | 152.366 | 1.5% | 137.7% | 0.9567% | 0.9695% | 0.9823% | 0.9951% | 1.008% | 1.021% | 1.034% | 1.046% | 1.059% | 1.072% | 1.085% | 1.098% | 1.11% | 1.123% | 1.136% | 1.149% | 1.162% | 1.175% | 1.187% | 1.2% | 0.00038745 | 0.00039264 | 0.00039782 | 0.00040301 | 0.0004082 | 0.00041339 | 0.00041858 | 0.00042377 | 0.00042896 | 0.00043415 | 0.00043933 | 0.00044452 | 0.00044971 | 0.0004549 | 0.00046009 | 0.00046528 | 0.00047047 | 0.00047565 | 0.00048084 | 0.00048603
| 10419913 | CLC003 | CLC | 17076767 | 17076785 | 0.31311 | 143.4818 | -38.7637 | 130 | 113 | 5.4% | 7.3% | 137.02 | 119.102 | 0.01 | 0.02 | -1791.8 | 154.938 | 1.392% | 139.49 | 121.249 | 0.01 | 0.02 | -1824.1 | 157.731 | 1.52% | 139.2% | 0.9582% | 0.9716% | 0.9849% | 0.9982% | 1.012% | 1.025% | 1.038% | 1.052% | 1.065% | 1.078% | 1.091% | 1.105% | 1.118% | 1.131% | 1.145% | 1.158% | 1.171% | 1.185% | 1.198% | 1.211% | 0.00038807 | 0.00039347 | 0.00039886 | 0.00040426 | 0.00040966 | 0.00041505 | 0.00042045 | 0.00042584 | 0.00043124 | 0.00043664 | 0.00044203 | 0.00044743 | 0.00045282 | 0.00045822 | 0.00046362 | 0.00046901 | 0.00047441 | 0.00047981 | 0.0004852 | 0.0004906
| 10423140 | NKA001 | NKA | 17090284 | 17090288 | 1.7141 | 145.7411 | -36.1998 | 112 | 99 | 6.3% | 8.8% | 119.056 | 105.237 | 0.01 | 0.02 | -1381.9 | 132.875 | 1.511% | 120.176 | 107.712 | 0.01 | 0.02 | -1246.4 | 132.64 | 1.656% | 151.1% | 0.9704% | 0.9877% | 1.005% | 1.022% | 1.04% | 1.057% | 1.075% | 1.092% | 1.109% | 1.127% | 1.144% | 1.161% | 1.179% | 1.196% | 1.213% | 1.231% | 1.248% | 1.266% | 1.283% | 1.3% | 0.00039298 | 0.00040001 | 0.00040705 | 0.00041408 | 0.00042111 | 0.00042814 | 0.00043518 | 0.00044221 | 0.00044924 | 0.00045627 | 0.00046331 | 0.00047034 | 0.00047737 | 0.00048441 | 0.00049144 | 0.00049847 | 0.0005055 | 0.00051254 | 0.00051957 | 0.0005266
| 10423219 | NKA001 | NKA | 17090689 | 183316117 | 0.76253 | 145.7451 | -36.2129 | 112 | 98.9 | 6.3% | 8.8% | 119.056 | 105.1307 | 0.01 | 0.02 | -1392.53 | 132.9813 | 1.507% | 120.176 | 107.6032 | 0.01 | 0.02 | -1257.28 | 132.7488 | 1.65% | 150.7% | 0.97% | 0.9872% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.091% | 1.108% | 1.125% | 1.142% | 1.16% | 1.177% | 1.194% | 1.211% | 1.228% | 1.246% | 1.263% | 1.28% | 1.297% | 0.00039282 | 0.0003998 | 0.00040678 | 0.00041376 | 0.00042073 | 0.00042771 | 0.00043469 | 0.00044167 | 0.00044865 | 0.00045563 | 0.00046261 | 0.00046959 | 0.00047657 | 0.00048355 | 0.00049053 | 0.0004975 | 0.00050448 | 0.00051146 | 0.00051844 | 0.00052542
| 10423495 | NKA001 | NKA | 17091731 | 17091727 | 0.15916 | 145.7892 | -36.2375 | 113 | 99.2 | 6.3% | 8.8% | 120.119 | 105.4496 | 0.01 | 0.02 | -1466.94 | 134.7884 | 1.485% | 121.249 | 107.9296 | 0.01 | 0.02 | -1331.94 | 134.5684 | 1.619% | 148.5% | 0.9678% | 0.9843% | 1.001% | 1.017% | 1.034% | 1.05% | 1.067% | 1.083% | 1.1% | 1.116% | 1.133% | 1.149% | 1.166% | 1.182% | 1.199% | 1.215% | 1.232% | 1.248% | 1.265% | 1.281% | 0.00039193 | 0.00039862 | 0.0004053 | 0.00041199 | 0.00041867 | 0.00042535 | 0.00043204 | 0.00043872 | 0.00044541 | 0.00045209 | 0.00045878 | 0.00046546 | 0.00047214 | 0.00047883 | 0.00048551 | 0.0004922 | 0.00049888 | 0.00050557 | 0.00051225 | 0.00051893
| 10423534 | NKA001 | NKA | 17091916 | 17091920 | 0.1453 | 145.8003 | -36.2346 | 113 | 99 | 6.3% | 8.8% | 120.119 | 105.237 | 0.01 | 0.02 | -1488.2 | 135.001 | 1.478% | 121.249 | 107.712 | 0.01 | 0.02 | -1353.7 | 134.786 | 1.609% | 147.8% | 0.9671% | 0.9834% | 0.9996% | 1.016% | 1.032% | 1.048% | 1.065% | 1.081% | 1.097% | 1.114% | 1.13% | 1.146% | 1.162% | 1.179% | 1.195% | 1.211% | 1.227% | 1.244% | 1.26% | 1.276% | 0.00039165 | 0.00039824 | 0.00040483 | 0.00041141 | 0.000418 | 0.00042459 | 0.00043118 | 0.00043777 | 0.00044436 | 0.00045095 | 0.00045753 | 0.00046412 | 0.00047071 | 0.0004773 | 0.00048389 | 0.00049048 | 0.00049707 | 0.00050366 | 0.00051024 | 0.00051683
| 10423865 | MRO005 | MRO | 17093341 | 17093333 | 1.2064 | 143.5295 | -37.0448 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10423867 | MRO005 | MRO | 17093337 | 17093341 | 0.55402 | 143.5277 | -37.0422 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10423890 | MRO008 | MRO | 17093448 | 17093444 | 0.68373 | 143.6776 | -37.0883 | 113 | 100 | 6.3% | 8.8% | 120.119 | 106.3 | 0.01 | 0.02 | -1381.9 | 133.938 | 1.515% | 121.249 | 108.8 | 0.01 | 0.02 | -1244.9 | 133.698 | 1.663% | 151.5% | 0.9708% | 0.9884% | 1.006% | 1.023% | 1.041% | 1.058% | 1.076% | 1.093% | 1.111% | 1.129% | 1.146% | 1.164% | 1.181% | 1.199% | 1.216% | 1.234% | 1.251% | 1.269% | 1.286% | 1.304% | 0.00039317 | 0.00040026 | 0.00040736 | 0.00041445 | 0.00042155 | 0.00042865 | 0.00043574 | 0.00044284 | 0.00044993 | 0.00045703 | 0.00046412 | 0.00047122 | 0.00047831 | 0.00048541 | 0.00049251 | 0.0004996 | 0.0005067 | 0.00051379 | 0.00052089 | 0.00052798
| 10423949 | MRO008 | MRO | 140831952 | 17093700 | 0.89608 | 143.6008 | -37.0575 | 113 | 101 | 6.3% | 8.8% | 120.119 | 107.363 | 0.01 | 0.02 | -1275.6 | 132.875 | 1.558% | 121.249 | 109.888 | 0.01 | 0.02 | -1136.1 | 132.61 | 1.726% | 155.8% | 0.9752% | 0.9942% | 1.013% | 1.032% | 1.051% | 1.07% | 1.089% | 1.108% | 1.127% | 1.146% | 1.165% | 1.184% | 1.203% | 1.222% | 1.241% | 1.26% | 1.279% | 1.298% | 1.317% | 1.336% | 0.00039494 | 0.00040263 | 0.00041032 | 0.000418 | 0.00042569 | 0.00043338 | 0.00044106 | 0.00044875 | 0.00045644 | 0.00046412 | 0.00047181 | 0.0004795 | 0.00048718 | 0.00049487 | 0.00050256 | 0.00051024 | 0.00051793 | 0.00052562 | 0.0005333 | 0.00054099
| 10424032 | MRO008 | MRO | 17094039 | 17094043 | 0.93749 | 143.6234 | -37.0989 | 114 | 102 | 6.3% | 8.8% | 121.182 | 108.426 | 0.01 | 0.02 | -1275.6 | 133.938 | 1.563% | 122.322 | 110.976 | 0.01 | 0.02 | -1134.6 | 133.668 | 1.733% | 156.3% | 0.9757% | 0.9949% | 1.014% | 1.033% | 1.052% | 1.071% | 1.091% | 1.11% | 1.129% | 1.148% | 1.167% | 1.186% | 1.206% | 1.225% | 1.244% | 1.263% | 1.282% | 1.301% | 1.32% | 1.34% | 0.00039515 | 0.0004029 | 0.00041066 | 0.00041841 | 0.00042617 | 0.00043392 | 0.00044168 | 0.00044943 | 0.00045718 | 0.00046494 | 0.00047269 | 0.00048045 | 0.0004882 | 0.00049596 | 0.00050371 | 0.00051147 | 0.00051922 | 0.00052698 | 0.00053473 | 0.00054249
| 10424065 | MRO008 | MRO | 17094194 | 17094198 | 2.6578 | 143.6879 | -37.0466 | 109 | 97.6 | 6.3% | 8.8% | 115.867 | 103.7488 | 0.01 | 0.02 | -1211.82 | 127.9852 | 1.567% | 116.957 | 106.1888 | 0.01 | 0.02 | -1076.82 | 127.7252 | 1.739% | 156.7% | 0.9761% | 0.9954% | 1.015% | 1.034% | 1.053% | 1.072% | 1.092% | 1.111% | 1.13% | 1.15% | 1.169% | 1.188% | 1.207% | 1.227% | 1.246% | 1.265% | 1.284% | 1.304% | 1.323% | 1.342% | 0.0003953 | 0.0004031 | 0.00041091 | 0.00041871 | 0.00042652 | 0.00043432 | 0.00044213 | 0.00044993 | 0.00045774 | 0.00046554 | 0.00047335 | 0.00048115 | 0.00048896 | 0.00049676 | 0.00050457 | 0.00051237 | 0.00052018 | 0.00052798 | 0.00053579 | 0.00054359
| 10424522 | MRO005 | MRO | 17096284 | 17096280 | 1.5679 | 143.6784 | -36.8036 | 107 | 96.4 | 6.3% | 8.8% | 113.741 | 102.4732 | 0.01 | 0.02 | -1126.78 | 125.0088 | 1.598% | 114.811 | 104.8832 | 0.01 | 0.02 | -992.78 | 124.7388 | 1.787% | 159.8% | 0.9793% | 0.9997% | 1.02% | 1.04% | 1.061% | 1.081% | 1.101% | 1.122% | 1.142% | 1.162% | 1.183% | 1.203% | 1.223% | 1.244% | 1.264% | 1.285% | 1.305% | 1.325% | 1.346% | 1.366% | 0.0003966 | 0.00040484 | 0.00041308 | 0.00042132 | 0.00042956 | 0.0004378 | 0.00044604 | 0.00045428 | 0.00046252 | 0.00047076 | 0.000479 | 0.00048724 | 0.00049548 | 0.00050372 | 0.00051196 | 0.0005202 | 0.00052844 | 0.00053668 | 0.00054492 | 0.00055316
| 10424523 | MRO005 | MRO | 17096288 | 17096284 | 1.715 | 143.6778 | -36.806 | 107 | 96.4 | 6.3% | 8.8% | 113.741 | 102.4732 | 0.01 | 0.02 | -1126.78 | 125.0088 | 1.598% | 114.811 | 104.8832 | 0.01 | 0.02 | -992.78 | 124.7388 | 1.787% | 159.8% | 0.9793% | 0.9997% | 1.02% | 1.04% | 1.061% | 1.081% | 1.101% | 1.122% | 1.142% | 1.162% | 1.183% | 1.203% | 1.223% | 1.244% | 1.264% | 1.285% | 1.305% | 1.325% | 1.346% | 1.366% | 0.0003966 | 0.00040484 | 0.00041308 | 0.00042132 | 0.00042956 | 0.0004378 | 0.00044604 | 0.00045428 | 0.00046252 | 0.00047076 | 0.000479 | 0.00048724 | 0.00049548 | 0.00050372 | 0.00051196 | 0.0005202 | 0.00052844 | 0.00053668 | 0.00054492 | 0.00055316
| 10424698 | MRO005 | MRO | 17096999 | 17097004 | 0.96738 | 143.5197 | -36.8651 | 109 | 97.7 | 6.3% | 8.8% | 115.867 | 103.8551 | 0.01 | 0.02 | -1201.19 | 127.8789 | 1.572% | 116.957 | 106.2976 | 0.01 | 0.02 | -1065.94 | 127.6164 | 1.746% | 157.2% | 0.9766% | 0.996% | 1.015% | 1.035% | 1.054% | 1.074% | 1.093% | 1.113% | 1.132% | 1.152% | 1.171% | 1.19% | 1.21% | 1.229% | 1.249% | 1.268% | 1.288% | 1.307% | 1.327% | 1.346% | 0.0003955 | 0.00040338 | 0.00041125 | 0.00041913 | 0.000427 | 0.00043487 | 0.00044275 | 0.00045062 | 0.0004585 | 0.00046637 | 0.00047424 | 0.00048212 | 0.00048999 | 0.00049787 | 0.00050574 | 0.00051361 | 0.00052149 | 0.00052936 | 0.00053724 | 0.00054511
| 10424827 | MRO005 | MRO | 17248058 | 17097550 | 1.131 | 143.6952 | -36.9171 | 107 | 95.7 | 6.3% | 8.8% | 113.741 | 101.7291 | 0.01 | 0.02 | -1201.19 | 125.7529 | 1.561% | 114.811 | 104.1216 | 0.01 | 0.02 | -1068.94 | 125.5004 | 1.731% | 156.1% | 0.9755% | 0.9946% | 1.014% | 1.033% | 1.052% | 1.071% | 1.09% | 1.109% | 1.128% | 1.147% | 1.166% | 1.185% | 1.205% | 1.224% | 1.243% | 1.262% | 1.281% | 1.3% | 1.319% | 1.338% | 0.00039507 | 0.0004028 | 0.00041053 | 0.00041826 | 0.00042599 | 0.00043372 | 0.00044145 | 0.00044918 | 0.00045691 | 0.00046464 | 0.00047237 | 0.0004801 | 0.00048782 | 0.00049555 | 0.00050328 | 0.00051101 | 0.00051874 | 0.00052647 | 0.0005342 | 0.00054193
| 10424852 | MRO008 | MRO | 17097656 | 17097660 | 2.0474 | 143.4839 | -36.9989 | 113 | 100 | 6.3% | 8.8% | 120.119 | 106.3 | 0.01 | 0.02 | -1381.9 | 133.938 | 1.515% | 121.249 | 108.8 | 0.01 | 0.02 | -1244.9 | 133.698 | 1.663% | 151.5% | 0.9708% | 0.9884% | 1.006% | 1.023% | 1.041% | 1.058% | 1.076% | 1.093% | 1.111% | 1.129% | 1.146% | 1.164% | 1.181% | 1.199% | 1.216% | 1.234% | 1.251% | 1.269% | 1.286% | 1.304% | 0.00039317 | 0.00040026 | 0.00040736 | 0.00041445 | 0.00042155 | 0.00042865 | 0.00043574 | 0.00044284 | 0.00044993 | 0.00045703 | 0.00046412 | 0.00047122 | 0.00047831 | 0.00048541 | 0.00049251 | 0.0004996 | 0.0005067 | 0.00051379 | 0.00052089 | 0.00052798
| 10424853 | MRO008 | MRO | 17097660 | 17097665 | 1.9379 | 143.4807 | -36.9986 | 113 | 100 | 6.3% | 8.8% | 120.119 | 106.3 | 0.01 | 0.02 | -1381.9 | 133.938 | 1.515% | 121.249 | 108.8 | 0.01 | 0.02 | -1244.9 | 133.698 | 1.663% | 151.5% | 0.9708% | 0.9884% | 1.006% | 1.023% | 1.041% | 1.058% | 1.076% | 1.093% | 1.111% | 1.129% | 1.146% | 1.164% | 1.181% | 1.199% | 1.216% | 1.234% | 1.251% | 1.269% | 1.286% | 1.304% | 0.00039317 | 0.00040026 | 0.00040736 | 0.00041445 | 0.00042155 | 0.00042865 | 0.00043574 | 0.00044284 | 0.00044993 | 0.00045703 | 0.00046412 | 0.00047122 | 0.00047831 | 0.00048541 | 0.00049251 | 0.0004996 | 0.0005067 | 0.00051379 | 0.00052089 | 0.00052798
| 10424854 | MRO008 | MRO | 17097665 | 17097669 | 1.7145 | 143.4775 | -36.9982 | 113 | 100 | 6.3% | 8.8% | 120.119 | 106.3 | 0.01 | 0.02 | -1381.9 | 133.938 | 1.515% | 121.249 | 108.8 | 0.01 | 0.02 | -1244.9 | 133.698 | 1.663% | 151.5% | 0.9708% | 0.9884% | 1.006% | 1.023% | 1.041% | 1.058% | 1.076% | 1.093% | 1.111% | 1.129% | 1.146% | 1.164% | 1.181% | 1.199% | 1.216% | 1.234% | 1.251% | 1.269% | 1.286% | 1.304% | 0.00039317 | 0.00040026 | 0.00040736 | 0.00041445 | 0.00042155 | 0.00042865 | 0.00043574 | 0.00044284 | 0.00044993 | 0.00045703 | 0.00046412 | 0.00047122 | 0.00047831 | 0.00048541 | 0.00049251 | 0.0004996 | 0.0005067 | 0.00051379 | 0.00052089 | 0.00052798
| 10424855 | MRO008 | MRO | 17097669 | 17335631 | 1.2806 | 143.4743 | -36.9978 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10424858 | MRO008 | MRO | 17097677 | 17097682 | 2.7168 | 143.4865 | -37.0034 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10424860 | MRO008 | MRO | 17097690 | 191199022 | 0.31873 | 143.4841 | -37.0067 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10424875 | MRO008 | MRO | 17097754 | 17097750 | 2.4873 | 143.479 | -37.0339 | 115 | 103 | 6.3% | 8.8% | 122.245 | 109.489 | 0.01 | 0.02 | -1275.6 | 135.001 | 1.568% | 123.395 | 112.064 | 0.01 | 0.02 | -1133.1 | 134.726 | 1.741% | 156.8% | 0.9762% | 0.9955% | 1.015% | 1.034% | 1.053% | 1.073% | 1.092% | 1.111% | 1.131% | 1.15% | 1.169% | 1.189% | 1.208% | 1.227% | 1.247% | 1.266% | 1.285% | 1.305% | 1.324% | 1.343% | 0.00039535 | 0.00040317 | 0.000411 | 0.00041882 | 0.00042664 | 0.00043446 | 0.00044229 | 0.00045011 | 0.00045793 | 0.00046576 | 0.00047358 | 0.0004814 | 0.00048922 | 0.00049705 | 0.00050487 | 0.00051269 | 0.00052052 | 0.00052834 | 0.00053616 | 0.00054398
| 10424888 | MRO008 | MRO | 17097805 | 17097809 | 0.1302 | 143.5015 | -37.0053 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10424889 | MRO008 | MRO | 17097809 | 17097813 | 0.81184 | 143.5045 | -37.0057 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10424893 | MRO005 | MRO | 17097860 | 17097828 | 0.15799 | 143.5277 | -37.0273 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10424936 | MRO005 | MRO | 17098002 | 17097998 | 0.76582 | 143.5219 | -36.9698 | 112 | 99.5 | 6.3% | 8.8% | 119.056 | 105.7685 | 0.01 | 0.02 | -1328.75 | 132.3435 | 1.531% | 120.176 | 108.256 | 0.01 | 0.02 | -1192 | 132.096 | 1.686% | 153.1% | 0.9725% | 0.9905% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.099% | 1.117% | 1.135% | 1.153% | 1.171% | 1.189% | 1.207% | 1.225% | 1.243% | 1.261% | 1.279% | 1.298% | 1.316% | 0.00039382 | 0.00040114 | 0.00040845 | 0.00041577 | 0.00042308 | 0.00043039 | 0.00043771 | 0.00044502 | 0.00045234 | 0.00045965 | 0.00046696 | 0.00047428 | 0.00048159 | 0.00048891 | 0.00049622 | 0.00050353 | 0.00051085 | 0.00051816 | 0.00052548 | 0.00053279
| 10424937 | MRO005 | MRO | 17098006 | 17098002 | 0.61873 | 143.5232 | -36.9702 | 112 | 99.5 | 6.3% | 8.8% | 119.056 | 105.7685 | 0.01 | 0.02 | -1328.75 | 132.3435 | 1.531% | 120.176 | 108.256 | 0.01 | 0.02 | -1192 | 132.096 | 1.686% | 153.1% | 0.9725% | 0.9905% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.099% | 1.117% | 1.135% | 1.153% | 1.171% | 1.189% | 1.207% | 1.225% | 1.243% | 1.261% | 1.279% | 1.298% | 1.316% | 0.00039382 | 0.00040114 | 0.00040845 | 0.00041577 | 0.00042308 | 0.00043039 | 0.00043771 | 0.00044502 | 0.00045234 | 0.00045965 | 0.00046696 | 0.00047428 | 0.00048159 | 0.00048891 | 0.00049622 | 0.00050353 | 0.00051085 | 0.00051816 | 0.00052548 | 0.00053279
| 10424938 | MRO005 | MRO | 17098010 | 17098006 | 0.4967 | 143.5244 | -36.9705 | 112 | 99.5 | 6.3% | 8.8% | 119.056 | 105.7685 | 0.01 | 0.02 | -1328.75 | 132.3435 | 1.531% | 120.176 | 108.256 | 0.01 | 0.02 | -1192 | 132.096 | 1.686% | 153.1% | 0.9725% | 0.9905% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.099% | 1.117% | 1.135% | 1.153% | 1.171% | 1.189% | 1.207% | 1.225% | 1.243% | 1.261% | 1.279% | 1.298% | 1.316% | 0.00039382 | 0.00040114 | 0.00040845 | 0.00041577 | 0.00042308 | 0.00043039 | 0.00043771 | 0.00044502 | 0.00045234 | 0.00045965 | 0.00046696 | 0.00047428 | 0.00048159 | 0.00048891 | 0.00049622 | 0.00050353 | 0.00051085 | 0.00051816 | 0.00052548 | 0.00053279
| 10424939 | MRO005 | MRO | 17098015 | 17098010 | 0.47336 | 143.5257 | -36.9709 | 114 | 102 | 6.3% | 8.8% | 121.182 | 108.426 | 0.01 | 0.02 | -1275.6 | 133.938 | 1.563% | 122.322 | 110.976 | 0.01 | 0.02 | -1134.6 | 133.668 | 1.733% | 156.3% | 0.9757% | 0.9949% | 1.014% | 1.033% | 1.052% | 1.071% | 1.091% | 1.11% | 1.129% | 1.148% | 1.167% | 1.186% | 1.206% | 1.225% | 1.244% | 1.263% | 1.282% | 1.301% | 1.32% | 1.34% | 0.00039515 | 0.0004029 | 0.00041066 | 0.00041841 | 0.00042617 | 0.00043392 | 0.00044168 | 0.00044943 | 0.00045718 | 0.00046494 | 0.00047269 | 0.00048045 | 0.0004882 | 0.00049596 | 0.00050371 | 0.00051147 | 0.00051922 | 0.00052698 | 0.00053473 | 0.00054249
| 10424955 | MRO005 | MRO | 163160733 | 203618533 | 2.254 | 143.5297 | -36.9695 | 114 | 102 | 6.3% | 8.8% | 121.182 | 108.426 | 0.01 | 0.02 | -1275.6 | 133.938 | 1.563% | 122.322 | 110.976 | 0.01 | 0.02 | -1134.6 | 133.668 | 1.733% | 156.3% | 0.9757% | 0.9949% | 1.014% | 1.033% | 1.052% | 1.071% | 1.091% | 1.11% | 1.129% | 1.148% | 1.167% | 1.186% | 1.206% | 1.225% | 1.244% | 1.263% | 1.282% | 1.301% | 1.32% | 1.34% | 0.00039515 | 0.0004029 | 0.00041066 | 0.00041841 | 0.00042617 | 0.00043392 | 0.00044168 | 0.00044943 | 0.00045718 | 0.00046494 | 0.00047269 | 0.00048045 | 0.0004882 | 0.00049596 | 0.00050371 | 0.00051147 | 0.00051922 | 0.00052698 | 0.00053473 | 0.00054249
| 10424956 | MRO005 | MRO | 203618533 | 129134824 | 0.22287 | 143.5304 | -36.9671 | 114 | 102 | 6.3% | 8.8% | 121.182 | 108.426 | 0.01 | 0.02 | -1275.6 | 133.938 | 1.563% | 122.322 | 110.976 | 0.01 | 0.02 | -1134.6 | 133.668 | 1.733% | 156.3% | 0.9757% | 0.9949% | 1.014% | 1.033% | 1.052% | 1.071% | 1.091% | 1.11% | 1.129% | 1.148% | 1.167% | 1.186% | 1.206% | 1.225% | 1.244% | 1.263% | 1.282% | 1.301% | 1.32% | 1.34% | 0.00039515 | 0.0004029 | 0.00041066 | 0.00041841 | 0.00042617 | 0.00043392 | 0.00044168 | 0.00044943 | 0.00045718 | 0.00046494 | 0.00047269 | 0.00048045 | 0.0004882 | 0.00049596 | 0.00050371 | 0.00051147 | 0.00051922 | 0.00052698 | 0.00053473 | 0.00054249
| 10425007 | MRO005 | MRO | 17098347 | 17098303 | 0.30756 | 143.5663 | -37.0201 | 113 | 100 | 6.3% | 8.8% | 120.119 | 106.3 | 0.01 | 0.02 | -1381.9 | 133.938 | 1.515% | 121.249 | 108.8 | 0.01 | 0.02 | -1244.9 | 133.698 | 1.663% | 151.5% | 0.9708% | 0.9884% | 1.006% | 1.023% | 1.041% | 1.058% | 1.076% | 1.093% | 1.111% | 1.129% | 1.146% | 1.164% | 1.181% | 1.199% | 1.216% | 1.234% | 1.251% | 1.269% | 1.286% | 1.304% | 0.00039317 | 0.00040026 | 0.00040736 | 0.00041445 | 0.00042155 | 0.00042865 | 0.00043574 | 0.00044284 | 0.00044993 | 0.00045703 | 0.00046412 | 0.00047122 | 0.00047831 | 0.00048541 | 0.00049251 | 0.0004996 | 0.0005067 | 0.00051379 | 0.00052089 | 0.00052798
| 10425014 | MRO005 | MRO | 17098347 | 17098327 | 0.30753 | 143.5695 | -37.0199 | 113 | 100 | 6.3% | 8.8% | 120.119 | 106.3 | 0.01 | 0.02 | -1381.9 | 133.938 | 1.515% | 121.249 | 108.8 | 0.01 | 0.02 | -1244.9 | 133.698 | 1.663% | 151.5% | 0.9708% | 0.9884% | 1.006% | 1.023% | 1.041% | 1.058% | 1.076% | 1.093% | 1.111% | 1.129% | 1.146% | 1.164% | 1.181% | 1.199% | 1.216% | 1.234% | 1.251% | 1.269% | 1.286% | 1.304% | 0.00039317 | 0.00040026 | 0.00040736 | 0.00041445 | 0.00042155 | 0.00042865 | 0.00043574 | 0.00044284 | 0.00044993 | 0.00045703 | 0.00046412 | 0.00047122 | 0.00047831 | 0.00048541 | 0.00049251 | 0.0004996 | 0.0005067 | 0.00051379 | 0.00052089 | 0.00052798
| 10425042 | MRO005 | MRO | 17098434 | 17098438 | 0.70665 | 143.6163 | -36.992 | 111 | 99.5 | 6.3% | 8.8% | 117.993 | 105.7685 | 0.01 | 0.02 | -1222.45 | 130.2175 | 1.572% | 119.103 | 108.256 | 0.01 | 0.02 | -1084.7 | 129.95 | 1.747% | 157.2% | 0.9766% | 0.9961% | 1.016% | 1.035% | 1.054% | 1.074% | 1.093% | 1.113% | 1.132% | 1.152% | 1.171% | 1.191% | 1.21% | 1.23% | 1.249% | 1.268% | 1.288% | 1.307% | 1.327% | 1.346% | 0.00039552 | 0.0004034 | 0.00041128 | 0.00041916 | 0.00042703 | 0.00043491 | 0.00044279 | 0.00045067 | 0.00045855 | 0.00046643 | 0.00047431 | 0.00048219 | 0.00049007 | 0.00049795 | 0.00050583 | 0.0005137 | 0.00052158 | 0.00052946 | 0.00053734 | 0.00054522
| 10425088 | MRO005 | MRO | 17098647 | 17098643 | 1.3488 | 143.6111 | -37.0118 | 111 | 98.7 | 6.3% | 8.8% | 117.993 | 104.9181 | 0.01 | 0.02 | -1307.49 | 131.0679 | 1.535% | 119.103 | 107.3856 | 0.01 | 0.02 | -1171.74 | 130.8204 | 1.692% | 153.5% | 0.9728% | 0.991% | 1.009% | 1.027% | 1.046% | 1.064% | 1.082% | 1.1% | 1.118% | 1.137% | 1.155% | 1.173% | 1.191% | 1.209% | 1.228% | 1.246% | 1.264% | 1.282% | 1.3% | 1.318% | 0.00039398 | 0.00040135 | 0.00040871 | 0.00041608 | 0.00042345 | 0.00043081 | 0.00043818 | 0.00044555 | 0.00045291 | 0.00046028 | 0.00046765 | 0.00047501 | 0.00048238 | 0.00048975 | 0.00049711 | 0.00050448 | 0.00051185 | 0.00051921 | 0.00052658 | 0.00053395
| 10425089 | MRO005 | MRO | 17098647 | 17098672 | 0.68548 | 143.61 | -37.0124 | 111 | 98.7 | 6.3% | 8.8% | 117.993 | 104.9181 | 0.01 | 0.02 | -1307.49 | 131.0679 | 1.535% | 119.103 | 107.3856 | 0.01 | 0.02 | -1171.74 | 130.8204 | 1.692% | 153.5% | 0.9728% | 0.991% | 1.009% | 1.027% | 1.046% | 1.064% | 1.082% | 1.1% | 1.118% | 1.137% | 1.155% | 1.173% | 1.191% | 1.209% | 1.228% | 1.246% | 1.264% | 1.282% | 1.3% | 1.318% | 0.00039398 | 0.00040135 | 0.00040871 | 0.00041608 | 0.00042345 | 0.00043081 | 0.00043818 | 0.00044555 | 0.00045291 | 0.00046028 | 0.00046765 | 0.00047501 | 0.00048238 | 0.00048975 | 0.00049711 | 0.00050448 | 0.00051185 | 0.00051921 | 0.00052658 | 0.00053395
| 10425120 | MRO005 | MRO | 17098801 | 17098788 | 2.3274 | 143.6318 | -36.9672 | 108 | 96.7 | 6.3% | 8.8% | 114.804 | 102.7921 | 0.01 | 0.02 | -1201.19 | 126.8159 | 1.566% | 115.884 | 105.2096 | 0.01 | 0.02 | -1067.44 | 126.5584 | 1.739% | 156.6% | 0.9761% | 0.9953% | 1.015% | 1.034% | 1.053% | 1.072% | 1.092% | 1.111% | 1.13% | 1.149% | 1.169% | 1.188% | 1.207% | 1.227% | 1.246% | 1.265% | 1.284% | 1.304% | 1.323% | 1.342% | 0.00039529 | 0.00040309 | 0.00041089 | 0.00041869 | 0.00042649 | 0.0004343 | 0.0004421 | 0.0004499 | 0.0004577 | 0.0004655 | 0.0004733 | 0.00048111 | 0.00048891 | 0.00049671 | 0.00050451 | 0.00051231 | 0.00052012 | 0.00052792 | 0.00053572 | 0.00054352
| 10425132 | MRO005 | MRO | 17098831 | 17098843 | 0.90292 | 143.6252 | -36.9495 | 108 | 97 | 6.3% | 8.8% | 114.804 | 103.111 | 0.01 | 0.02 | -1169.3 | 126.497 | 1.582% | 115.884 | 105.536 | 0.01 | 0.02 | -1034.8 | 126.232 | 1.762% | 158.2% | 0.9776% | 0.9974% | 1.017% | 1.037% | 1.057% | 1.077% | 1.096% | 1.116% | 1.136% | 1.156% | 1.176% | 1.195% | 1.215% | 1.235% | 1.255% | 1.274% | 1.294% | 1.314% | 1.334% | 1.354% | 0.00039593 | 0.00040394 | 0.00041195 | 0.00041997 | 0.00042798 | 0.000436 | 0.00044401 | 0.00045203 | 0.00046004 | 0.00046806 | 0.00047607 | 0.00048409 | 0.0004921 | 0.00050011 | 0.00050813 | 0.00051614 | 0.00052416 | 0.00053217 | 0.00054019 | 0.0005482
| 10425165 | MRO005 | MRO | 17099092 | 17098977 | 1.9712 | 143.6523 | -37.0016 | 109 | 97.6 | 6.3% | 8.8% | 115.867 | 103.7488 | 0.01 | 0.02 | -1211.82 | 127.9852 | 1.567% | 116.957 | 106.1888 | 0.01 | 0.02 | -1076.82 | 127.7252 | 1.739% | 156.7% | 0.9761% | 0.9954% | 1.015% | 1.034% | 1.053% | 1.072% | 1.092% | 1.111% | 1.13% | 1.15% | 1.169% | 1.188% | 1.207% | 1.227% | 1.246% | 1.265% | 1.284% | 1.304% | 1.323% | 1.342% | 0.0003953 | 0.0004031 | 0.00041091 | 0.00041871 | 0.00042652 | 0.00043432 | 0.00044213 | 0.00044993 | 0.00045774 | 0.00046554 | 0.00047335 | 0.00048115 | 0.00048896 | 0.00049676 | 0.00050457 | 0.00051237 | 0.00052018 | 0.00052798 | 0.00053579 | 0.00054359
| 10425193 | MRO005 | MRO | 17099084 | 17099092 | 0.24851 | 143.6534 | -37.0022 | 109 | 97.6 | 6.3% | 8.8% | 115.867 | 103.7488 | 0.01 | 0.02 | -1211.82 | 127.9852 | 1.567% | 116.957 | 106.1888 | 0.01 | 0.02 | -1076.82 | 127.7252 | 1.739% | 156.7% | 0.9761% | 0.9954% | 1.015% | 1.034% | 1.053% | 1.072% | 1.092% | 1.111% | 1.13% | 1.15% | 1.169% | 1.188% | 1.207% | 1.227% | 1.246% | 1.265% | 1.284% | 1.304% | 1.323% | 1.342% | 0.0003953 | 0.0004031 | 0.00041091 | 0.00041871 | 0.00042652 | 0.00043432 | 0.00044213 | 0.00044993 | 0.00045774 | 0.00046554 | 0.00047335 | 0.00048115 | 0.00048896 | 0.00049676 | 0.00050457 | 0.00051237 | 0.00052018 | 0.00052798 | 0.00053579 | 0.00054359
| 10425308 | GHP021 | GHP | 17099661 | 17099657 | 1.5775 | 144.313 | -38.1421 | 109 | 95.6 | 5.4% | 7.3% | 114.886 | 100.7624 | 0.01 | 0.02 | -1412.36 | 129.0096 | 1.417% | 116.957 | 102.5788 | 0.01 | 0.02 | -1437.82 | 131.3352 | 1.553% | 141.7% | 0.9608% | 0.975% | 0.9891% | 1.003% | 1.017% | 1.032% | 1.046% | 1.06% | 1.074% | 1.088% | 1.103% | 1.117% | 1.131% | 1.145% | 1.159% | 1.173% | 1.188% | 1.202% | 1.216% | 1.23% | 0.0003891 | 0.00039484 | 0.00040058 | 0.00040632 | 0.00041206 | 0.0004178 | 0.00042354 | 0.00042928 | 0.00043502 | 0.00044076 | 0.0004465 | 0.00045224 | 0.00045798 | 0.00046372 | 0.00046946 | 0.0004752 | 0.00048094 | 0.00048668 | 0.00049242 | 0.00049816
| 10425309 | GHP021 | GHP | 17099735 | 17099661 | 0.30489 | 144.314 | -38.1428 | 109 | 95.6 | 5.4% | 7.3% | 114.886 | 100.7624 | 0.01 | 0.02 | -1412.36 | 129.0096 | 1.417% | 116.957 | 102.5788 | 0.01 | 0.02 | -1437.82 | 131.3352 | 1.553% | 141.7% | 0.9608% | 0.975% | 0.9891% | 1.003% | 1.017% | 1.032% | 1.046% | 1.06% | 1.074% | 1.088% | 1.103% | 1.117% | 1.131% | 1.145% | 1.159% | 1.173% | 1.188% | 1.202% | 1.216% | 1.23% | 0.0003891 | 0.00039484 | 0.00040058 | 0.00040632 | 0.00041206 | 0.0004178 | 0.00042354 | 0.00042928 | 0.00043502 | 0.00044076 | 0.0004465 | 0.00045224 | 0.00045798 | 0.00046372 | 0.00046946 | 0.0004752 | 0.00048094 | 0.00048668 | 0.00049242 | 0.00049816
| 10427665 | STN024 | STN | 187875867 | 17110034 | 0.75783 | 145.5956 | -36.3551 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10427689 | STN024 | STN | 17110122 | 17110127 | 0.93582 | 145.6133 | -36.3662 | 116 | 101 | 6.3% | 8.8% | 123.308 | 107.363 | 0.01 | 0.02 | -1594.5 | 139.253 | 1.458% | 124.468 | 109.888 | 0.01 | 0.02 | -1458 | 139.048 | 1.581% | 145.8% | 0.965% | 0.9806% | 0.9962% | 1.012% | 1.027% | 1.043% | 1.059% | 1.074% | 1.09% | 1.105% | 1.121% | 1.137% | 1.152% | 1.168% | 1.183% | 1.199% | 1.214% | 1.23% | 1.246% | 1.261% | 0.00039082 | 0.00039713 | 0.00040345 | 0.00040976 | 0.00041607 | 0.00042238 | 0.0004287 | 0.00043501 | 0.00044132 | 0.00044763 | 0.00045395 | 0.00046026 | 0.00046657 | 0.00047288 | 0.0004792 | 0.00048551 | 0.00049182 | 0.00049814 | 0.00050445 | 0.00051076
| 10427723 | STN024 | STN | 17110273 | 17110278 | 0.36281 | 145.5883 | -36.3682 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10427805 | STN024 | STN | 17110622 | 17110626 | 1.1411 | 145.637 | -36.3645 | 118 | 103 | 6.3% | 8.8% | 125.434 | 109.489 | 0.01 | 0.02 | -1594.5 | 141.379 | 1.466% | 126.614 | 112.064 | 0.01 | 0.02 | -1455 | 141.164 | 1.592% | 146.6% | 0.9658% | 0.9817% | 0.9976% | 1.013% | 1.029% | 1.045% | 1.061% | 1.077% | 1.093% | 1.109% | 1.124% | 1.14% | 1.156% | 1.172% | 1.188% | 1.204% | 1.22% | 1.235% | 1.251% | 1.267% | 0.00039115 | 0.00039757 | 0.00040399 | 0.00041041 | 0.00041683 | 0.00042325 | 0.00042968 | 0.0004361 | 0.00044252 | 0.00044894 | 0.00045536 | 0.00046178 | 0.0004682 | 0.00047463 | 0.00048105 | 0.00048747 | 0.00049389 | 0.00050031 | 0.00050673 | 0.00051316
| 10427869 | STN011 | STN | 17110950 | 17110912 | 0.16649 | 145.6307 | -36.4006 | 118 | 103 | 6.3% | 8.8% | 125.434 | 109.489 | 0.01 | 0.02 | -1594.5 | 141.379 | 1.466% | 126.614 | 112.064 | 0.01 | 0.02 | -1455 | 141.164 | 1.592% | 146.6% | 0.9658% | 0.9817% | 0.9976% | 1.013% | 1.029% | 1.045% | 1.061% | 1.077% | 1.093% | 1.109% | 1.124% | 1.14% | 1.156% | 1.172% | 1.188% | 1.204% | 1.22% | 1.235% | 1.251% | 1.267% | 0.00039115 | 0.00039757 | 0.00040399 | 0.00041041 | 0.00041683 | 0.00042325 | 0.00042968 | 0.0004361 | 0.00044252 | 0.00044894 | 0.00045536 | 0.00046178 | 0.0004682 | 0.00047463 | 0.00048105 | 0.00048747 | 0.00049389 | 0.00050031 | 0.00050673 | 0.00051316
| 10427995 | STN011 | STN | 17111475 | 17111467 | 0.1989 | 145.6339 | -36.4439 | 119 | 104 | 6.3% | 8.8% | 126.497 | 110.552 | 0.01 | 0.02 | -1594.5 | 142.442 | 1.47% | 127.687 | 113.152 | 0.01 | 0.02 | -1453.5 | 142.222 | 1.598% | 147% | 0.9662% | 0.9822% | 0.9982% | 1.014% | 1.03% | 1.046% | 1.062% | 1.078% | 1.094% | 1.11% | 1.126% | 1.142% | 1.158% | 1.174% | 1.19% | 1.206% | 1.222% | 1.238% | 1.254% | 1.27% | 0.00039131 | 0.00039779 | 0.00040426 | 0.00041074 | 0.00041721 | 0.00042369 | 0.00043017 | 0.00043664 | 0.00044312 | 0.00044959 | 0.00045607 | 0.00046254 | 0.00046902 | 0.0004755 | 0.00048197 | 0.00048845 | 0.00049492 | 0.0005014 | 0.00050788 | 0.00051435
| 10428001 | STN011 | STN | 17111557 | 17111488 | 0.76026 | 145.6274 | -36.4417 | 119 | 104 | 6.3% | 8.8% | 126.497 | 110.552 | 0.01 | 0.02 | -1594.5 | 142.442 | 1.47% | 127.687 | 113.152 | 0.01 | 0.02 | -1453.5 | 142.222 | 1.598% | 147% | 0.9662% | 0.9822% | 0.9982% | 1.014% | 1.03% | 1.046% | 1.062% | 1.078% | 1.094% | 1.11% | 1.126% | 1.142% | 1.158% | 1.174% | 1.19% | 1.206% | 1.222% | 1.238% | 1.254% | 1.27% | 0.00039131 | 0.00039779 | 0.00040426 | 0.00041074 | 0.00041721 | 0.00042369 | 0.00043017 | 0.00043664 | 0.00044312 | 0.00044959 | 0.00045607 | 0.00046254 | 0.00046902 | 0.0004755 | 0.00048197 | 0.00048845 | 0.00049492 | 0.0005014 | 0.00050788 | 0.00051435
| 10428002 | STN011 | STN | 17111488 | 17111553 | 1.449 | 145.6246 | -36.4399 | 119 | 104 | 6.3% | 8.8% | 126.497 | 110.552 | 0.01 | 0.02 | -1594.5 | 142.442 | 1.47% | 127.687 | 113.152 | 0.01 | 0.02 | -1453.5 | 142.222 | 1.598% | 147% | 0.9662% | 0.9822% | 0.9982% | 1.014% | 1.03% | 1.046% | 1.062% | 1.078% | 1.094% | 1.11% | 1.126% | 1.142% | 1.158% | 1.174% | 1.19% | 1.206% | 1.222% | 1.238% | 1.254% | 1.27% | 0.00039131 | 0.00039779 | 0.00040426 | 0.00041074 | 0.00041721 | 0.00042369 | 0.00043017 | 0.00043664 | 0.00044312 | 0.00044959 | 0.00045607 | 0.00046254 | 0.00046902 | 0.0004755 | 0.00048197 | 0.00048845 | 0.00049492 | 0.0005014 | 0.00050788 | 0.00051435
| 10428050 | STN011 | STN | 17111697 | 17696775 | 0.64453 | 145.6508 | -36.4356 | 119 | 104 | 6.3% | 8.8% | 126.497 | 110.552 | 0.01 | 0.02 | -1594.5 | 142.442 | 1.47% | 127.687 | 113.152 | 0.01 | 0.02 | -1453.5 | 142.222 | 1.598% | 147% | 0.9662% | 0.9822% | 0.9982% | 1.014% | 1.03% | 1.046% | 1.062% | 1.078% | 1.094% | 1.11% | 1.126% | 1.142% | 1.158% | 1.174% | 1.19% | 1.206% | 1.222% | 1.238% | 1.254% | 1.27% | 0.00039131 | 0.00039779 | 0.00040426 | 0.00041074 | 0.00041721 | 0.00042369 | 0.00043017 | 0.00043664 | 0.00044312 | 0.00044959 | 0.00045607 | 0.00046254 | 0.00046902 | 0.0004755 | 0.00048197 | 0.00048845 | 0.00049492 | 0.0005014 | 0.00050788 | 0.00051435
| 10428821 | KGT002 | KGTS | 17115016 | 17115007 | 0.99785 | 143.9452 | -35.6633 | 108 | 95.3 | 6.3% | 8.8% | 114.804 | 101.3039 | 0.01 | 0.02 | -1350.01 | 128.3041 | 1.504% | 115.884 | 103.6864 | 0.01 | 0.02 | -1219.76 | 128.0816 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.073% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.193% | 1.21% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039271 | 0.00039965 | 0.00040659 | 0.00041353 | 0.00042047 | 0.00042742 | 0.00043436 | 0.0004413 | 0.00044824 | 0.00045518 | 0.00046212 | 0.00046907 | 0.00047601 | 0.00048295 | 0.00048989 | 0.00049683 | 0.00050377 | 0.00051072 | 0.00051766 | 0.0005246
| 10429014 | CME016 | CME | 17137416 | 17115789 | 0.23816 | 146.0665 | -36.0643 | 120 | 106 | 6.3% | 8.8% | 127.56 | 112.678 | 0.01 | 0.02 | -1488.2 | 142.442 | 1.508% | 128.76 | 115.328 | 0.01 | 0.02 | -1343.2 | 142.192 | 1.652% | 150.8% | 0.9701% | 0.9874% | 1.005% | 1.022% | 1.039% | 1.056% | 1.074% | 1.091% | 1.108% | 1.126% | 1.143% | 1.16% | 1.177% | 1.195% | 1.212% | 1.229% | 1.247% | 1.264% | 1.281% | 1.298% | 0.00039287 | 0.00039987 | 0.00040687 | 0.00041386 | 0.00042086 | 0.00042786 | 0.00043485 | 0.00044185 | 0.00044885 | 0.00045584 | 0.00046284 | 0.00046984 | 0.00047683 | 0.00048383 | 0.00049083 | 0.00049782 | 0.00050482 | 0.00051182 | 0.00051882 | 0.00052581
| 10431269 | NKA005 | RCTS | 17125683 | 186965822 | 1.3899 | 145.5613 | -35.8499 | 117 | 104 | 6.3% | 8.8% | 124.371 | 110.552 | 0.01 | 0.02 | -1381.9 | 138.19 | 1.533% | 125.541 | 113.152 | 0.01 | 0.02 | -1238.9 | 137.93 | 1.689% | 153.3% | 0.9727% | 0.9908% | 1.009% | 1.027% | 1.045% | 1.063% | 1.082% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.19% | 1.209% | 1.227% | 1.245% | 1.263% | 1.281% | 1.299% | 1.317% | 0.00039392 | 0.00040127 | 0.00040861 | 0.00041596 | 0.00042331 | 0.00043065 | 0.000438 | 0.00044535 | 0.0004527 | 0.00046004 | 0.00046739 | 0.00047474 | 0.00048208 | 0.00048943 | 0.00049678 | 0.00050412 | 0.00051147 | 0.00051882 | 0.00052616 | 0.00053351
| 10431301 | NKA005 | RCTS | 17125538 | 17125543 | 1.7107 | 145.5696 | -35.875 | 116 | 103 | 6.3% | 8.8% | 123.308 | 109.489 | 0.01 | 0.02 | -1381.9 | 137.127 | 1.529% | 124.468 | 112.064 | 0.01 | 0.02 | -1240.4 | 136.872 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039373 | 0.00040102 | 0.0004083 | 0.00041558 | 0.00042287 | 0.00043015 | 0.00043744 | 0.00044472 | 0.000452 | 0.00045929 | 0.00046657 | 0.00047386 | 0.00048114 | 0.00048842 | 0.00049571 | 0.00050299 | 0.00051028 | 0.00051756 | 0.00052484 | 0.00053213
| 10431302 | NKA005 | RCTS | 17125543 | 17125547 | 0.32404 | 145.5689 | -35.8737 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10431333 | NKA005 | RCTS | 17125665 | 17125669 | 0.69972 | 145.5864 | -35.8624 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10431335 | NKA005 | RCTS | 17125688 | 17125683 | 0.96229 | 145.5645 | -35.8502 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10431408 | NKA005 | RCTS | 17343746 | 17125996 | 1.7352 | 145.5768 | -35.8875 | 116 | 103 | 6.3% | 8.8% | 123.308 | 109.489 | 0.01 | 0.02 | -1381.9 | 137.127 | 1.529% | 124.468 | 112.064 | 0.01 | 0.02 | -1240.4 | 136.872 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039373 | 0.00040102 | 0.0004083 | 0.00041558 | 0.00042287 | 0.00043015 | 0.00043744 | 0.00044472 | 0.000452 | 0.00045929 | 0.00046657 | 0.00047386 | 0.00048114 | 0.00048842 | 0.00049571 | 0.00050299 | 0.00051028 | 0.00051756 | 0.00052484 | 0.00053213
| 10434063 | CME016 | CME | 17137391 | 17137400 | 1.1797 | 146.0536 | -36.0596 | 120 | 106 | 6.3% | 8.8% | 127.56 | 112.678 | 0.01 | 0.02 | -1488.2 | 142.442 | 1.508% | 128.76 | 115.328 | 0.01 | 0.02 | -1343.2 | 142.192 | 1.652% | 150.8% | 0.9701% | 0.9874% | 1.005% | 1.022% | 1.039% | 1.056% | 1.074% | 1.091% | 1.108% | 1.126% | 1.143% | 1.16% | 1.177% | 1.195% | 1.212% | 1.229% | 1.247% | 1.264% | 1.281% | 1.298% | 0.00039287 | 0.00039987 | 0.00040687 | 0.00041386 | 0.00042086 | 0.00042786 | 0.00043485 | 0.00044185 | 0.00044885 | 0.00045584 | 0.00046284 | 0.00046984 | 0.00047683 | 0.00048383 | 0.00049083 | 0.00049782 | 0.00050482 | 0.00051182 | 0.00051882 | 0.00052581
| 10434065 | CME016 | CME | 17137400 | 17137404 | 1.3273 | 146.0564 | -36.0606 | 120 | 106 | 6.3% | 8.8% | 127.56 | 112.678 | 0.01 | 0.02 | -1488.2 | 142.442 | 1.508% | 128.76 | 115.328 | 0.01 | 0.02 | -1343.2 | 142.192 | 1.652% | 150.8% | 0.9701% | 0.9874% | 1.005% | 1.022% | 1.039% | 1.056% | 1.074% | 1.091% | 1.108% | 1.126% | 1.143% | 1.16% | 1.177% | 1.195% | 1.212% | 1.229% | 1.247% | 1.264% | 1.281% | 1.298% | 0.00039287 | 0.00039987 | 0.00040687 | 0.00041386 | 0.00042086 | 0.00042786 | 0.00043485 | 0.00044185 | 0.00044885 | 0.00045584 | 0.00046284 | 0.00046984 | 0.00047683 | 0.00048383 | 0.00049083 | 0.00049782 | 0.00050482 | 0.00051182 | 0.00051882 | 0.00052581
| 10434066 | CME016 | CME | 17137404 | 17137408 | 1.928 | 146.0592 | -36.0616 | 120 | 106 | 6.3% | 8.8% | 127.56 | 112.678 | 0.01 | 0.02 | -1488.2 | 142.442 | 1.508% | 128.76 | 115.328 | 0.01 | 0.02 | -1343.2 | 142.192 | 1.652% | 150.8% | 0.9701% | 0.9874% | 1.005% | 1.022% | 1.039% | 1.056% | 1.074% | 1.091% | 1.108% | 1.126% | 1.143% | 1.16% | 1.177% | 1.195% | 1.212% | 1.229% | 1.247% | 1.264% | 1.281% | 1.298% | 0.00039287 | 0.00039987 | 0.00040687 | 0.00041386 | 0.00042086 | 0.00042786 | 0.00043485 | 0.00044185 | 0.00044885 | 0.00045584 | 0.00046284 | 0.00046984 | 0.00047683 | 0.00048383 | 0.00049083 | 0.00049782 | 0.00050482 | 0.00051182 | 0.00051882 | 0.00052581
| 10434067 | CME016 | CME | 17137408 | 17137412 | 2.4232 | 146.062 | -36.0627 | 120 | 106 | 6.3% | 8.8% | 127.56 | 112.678 | 0.01 | 0.02 | -1488.2 | 142.442 | 1.508% | 128.76 | 115.328 | 0.01 | 0.02 | -1343.2 | 142.192 | 1.652% | 150.8% | 0.9701% | 0.9874% | 1.005% | 1.022% | 1.039% | 1.056% | 1.074% | 1.091% | 1.108% | 1.126% | 1.143% | 1.16% | 1.177% | 1.195% | 1.212% | 1.229% | 1.247% | 1.264% | 1.281% | 1.298% | 0.00039287 | 0.00039987 | 0.00040687 | 0.00041386 | 0.00042086 | 0.00042786 | 0.00043485 | 0.00044185 | 0.00044885 | 0.00045584 | 0.00046284 | 0.00046984 | 0.00047683 | 0.00048383 | 0.00049083 | 0.00049782 | 0.00050482 | 0.00051182 | 0.00051882 | 0.00052581
| 10434068 | CME016 | CME | 17137412 | 17137416 | 1.9687 | 146.0648 | -36.0637 | 120 | 106 | 6.3% | 8.8% | 127.56 | 112.678 | 0.01 | 0.02 | -1488.2 | 142.442 | 1.508% | 128.76 | 115.328 | 0.01 | 0.02 | -1343.2 | 142.192 | 1.652% | 150.8% | 0.9701% | 0.9874% | 1.005% | 1.022% | 1.039% | 1.056% | 1.074% | 1.091% | 1.108% | 1.126% | 1.143% | 1.16% | 1.177% | 1.195% | 1.212% | 1.229% | 1.247% | 1.264% | 1.281% | 1.298% | 0.00039287 | 0.00039987 | 0.00040687 | 0.00041386 | 0.00042086 | 0.00042786 | 0.00043485 | 0.00044185 | 0.00044885 | 0.00045584 | 0.00046284 | 0.00046984 | 0.00047683 | 0.00048383 | 0.00049083 | 0.00049782 | 0.00050482 | 0.00051182 | 0.00051882 | 0.00052581
| 10434345 | CME016 | CME | 17138621 | 17138625 | 0.60373 | 145.9327 | -36.0969 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10434431 | CME016 | CME | 17138939 | 17138935 | 0.37535 | 145.9626 | -36.147 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10434583 | CME016 | CME | 17139689 | 17139693 | 0.24782 | 146.1422 | -36.0779 | 122 | 107 | 6.3% | 8.8% | 129.686 | 113.741 | 0.01 | 0.02 | -1594.5 | 145.631 | 1.482% | 130.906 | 116.416 | 0.01 | 0.02 | -1449 | 145.396 | 1.615% | 148.2% | 0.9675% | 0.9838% | 1% | 1.017% | 1.033% | 1.049% | 1.066% | 1.082% | 1.099% | 1.115% | 1.131% | 1.148% | 1.164% | 1.181% | 1.197% | 1.213% | 1.23% | 1.246% | 1.263% | 1.279% | 0.0003918 | 0.00039844 | 0.00040508 | 0.00041172 | 0.00041836 | 0.000425 | 0.00043163 | 0.00043827 | 0.00044491 | 0.00045155 | 0.00045819 | 0.00046483 | 0.00047147 | 0.00047811 | 0.00048475 | 0.00049139 | 0.00049803 | 0.00050467 | 0.00051131 | 0.00051794
| 10438628 | GCY011 | GCY | 17157079 | 17158082 | 0.38731 | 144.3501 | -38.1714 | 108 | 95.2 | 5.4% | 7.3% | 113.832 | 100.3408 | 0.01 | 0.02 | -1349.12 | 127.3232 | 1.432% | 115.884 | 102.1496 | 0.01 | 0.02 | -1373.44 | 129.6184 | 1.574% | 143.2% | 0.9624% | 0.9771% | 0.9918% | 1.006% | 1.021% | 1.036% | 1.051% | 1.065% | 1.08% | 1.095% | 1.109% | 1.124% | 1.139% | 1.154% | 1.168% | 1.183% | 1.198% | 1.212% | 1.227% | 1.242% | 0.00038974 | 0.0003957 | 0.00040165 | 0.00040761 | 0.00041356 | 0.00041951 | 0.00042547 | 0.00043142 | 0.00043738 | 0.00044333 | 0.00044928 | 0.00045524 | 0.00046119 | 0.00046715 | 0.0004731 | 0.00047905 | 0.00048501 | 0.00049096 | 0.00049692 | 0.00050287
| 10438867 | GCY011 | GCY | 17158082 | 17577205 | 0.42675 | 144.3502 | -38.171 | 108 | 95.2 | 5.4% | 7.3% | 113.832 | 100.3408 | 0.01 | 0.02 | -1349.12 | 127.3232 | 1.432% | 115.884 | 102.1496 | 0.01 | 0.02 | -1373.44 | 129.6184 | 1.574% | 143.2% | 0.9624% | 0.9771% | 0.9918% | 1.006% | 1.021% | 1.036% | 1.051% | 1.065% | 1.08% | 1.095% | 1.109% | 1.124% | 1.139% | 1.154% | 1.168% | 1.183% | 1.198% | 1.212% | 1.227% | 1.242% | 0.00038974 | 0.0003957 | 0.00040165 | 0.00040761 | 0.00041356 | 0.00041951 | 0.00042547 | 0.00043142 | 0.00043738 | 0.00044333 | 0.00044928 | 0.00045524 | 0.00046119 | 0.00046715 | 0.0004731 | 0.00047905 | 0.00048501 | 0.00049096 | 0.00049692 | 0.00050287
| 10439185 | GCY014 | GCY | 17159307 | 17159303 | 1.8197 | 144.3317 | -38.1647 | 108 | 94.9 | 5.4% | 7.3% | 113.832 | 100.0246 | 0.01 | 0.02 | -1380.74 | 127.6394 | 1.422% | 115.884 | 101.8277 | 0.01 | 0.02 | -1405.63 | 129.9403 | 1.561% | 142.2% | 0.9614% | 0.9757% | 0.9901% | 1.004% | 1.019% | 1.033% | 1.048% | 1.062% | 1.076% | 1.091% | 1.105% | 1.119% | 1.134% | 1.148% | 1.162% | 1.177% | 1.191% | 1.206% | 1.22% | 1.234% | 0.00038933 | 0.00039515 | 0.00040097 | 0.00040679 | 0.00041261 | 0.00041842 | 0.00042424 | 0.00043006 | 0.00043588 | 0.00044169 | 0.00044751 | 0.00045333 | 0.00045915 | 0.00046496 | 0.00047078 | 0.0004766 | 0.00048242 | 0.00048823 | 0.00049405 | 0.00049987
| 10439186 | GCY014 | GCY | 17159312 | 17159307 | 2.5553 | 144.3318 | -38.1642 | 108 | 94.9 | 5.4% | 7.3% | 113.832 | 100.0246 | 0.01 | 0.02 | -1380.74 | 127.6394 | 1.422% | 115.884 | 101.8277 | 0.01 | 0.02 | -1405.63 | 129.9403 | 1.561% | 142.2% | 0.9614% | 0.9757% | 0.9901% | 1.004% | 1.019% | 1.033% | 1.048% | 1.062% | 1.076% | 1.091% | 1.105% | 1.119% | 1.134% | 1.148% | 1.162% | 1.177% | 1.191% | 1.206% | 1.22% | 1.234% | 0.00038933 | 0.00039515 | 0.00040097 | 0.00040679 | 0.00041261 | 0.00041842 | 0.00042424 | 0.00043006 | 0.00043588 | 0.00044169 | 0.00044751 | 0.00045333 | 0.00045915 | 0.00046496 | 0.00047078 | 0.0004766 | 0.00048242 | 0.00048823 | 0.00049405 | 0.00049987
| 10439593 | GCY011 | GCY | 17161208 | 17809505 | 1.16 | 144.3541 | -38.1751 | 107 | 94.4 | 5.4% | 7.3% | 112.778 | 99.4976 | 0.01 | 0.02 | -1328.04 | 126.0584 | 1.435% | 114.811 | 101.2912 | 0.01 | 0.02 | -1351.98 | 128.3308 | 1.578% | 143.5% | 0.9627% | 0.9775% | 0.9923% | 1.007% | 1.022% | 1.037% | 1.051% | 1.066% | 1.081% | 1.096% | 1.111% | 1.125% | 1.14% | 1.155% | 1.17% | 1.185% | 1.199% | 1.214% | 1.229% | 1.244% | 0.00038986 | 0.00039585 | 0.00040184 | 0.00040784 | 0.00041383 | 0.00041982 | 0.00042581 | 0.00043181 | 0.0004378 | 0.00044379 | 0.00044978 | 0.00045578 | 0.00046177 | 0.00046776 | 0.00047375 | 0.00047975 | 0.00048574 | 0.00049173 | 0.00049772 | 0.00050372
| 10441147 | GCY014 | GCY | 17167460 | 17167455 | 0.594 | 144.3322 | -38.1632 | 108 | 94.9 | 5.4% | 7.3% | 113.832 | 100.0246 | 0.01 | 0.02 | -1380.74 | 127.6394 | 1.422% | 115.884 | 101.8277 | 0.01 | 0.02 | -1405.63 | 129.9403 | 1.561% | 142.2% | 0.9614% | 0.9757% | 0.9901% | 1.004% | 1.019% | 1.033% | 1.048% | 1.062% | 1.076% | 1.091% | 1.105% | 1.119% | 1.134% | 1.148% | 1.162% | 1.177% | 1.191% | 1.206% | 1.22% | 1.234% | 0.00038933 | 0.00039515 | 0.00040097 | 0.00040679 | 0.00041261 | 0.00041842 | 0.00042424 | 0.00043006 | 0.00043588 | 0.00044169 | 0.00044751 | 0.00045333 | 0.00045915 | 0.00046496 | 0.00047078 | 0.0004766 | 0.00048242 | 0.00048823 | 0.00049405 | 0.00049987
| 10441152 | GCY014 | GCY | 17167477 | 83048490 | 0.21174 | 144.334 | -38.1629 | 108 | 94.9 | 5.4% | 7.3% | 113.832 | 100.0246 | 0.01 | 0.02 | -1380.74 | 127.6394 | 1.422% | 115.884 | 101.8277 | 0.01 | 0.02 | -1405.63 | 129.9403 | 1.561% | 142.2% | 0.9614% | 0.9757% | 0.9901% | 1.004% | 1.019% | 1.033% | 1.048% | 1.062% | 1.076% | 1.091% | 1.105% | 1.119% | 1.134% | 1.148% | 1.162% | 1.177% | 1.191% | 1.206% | 1.22% | 1.234% | 0.00038933 | 0.00039515 | 0.00040097 | 0.00040679 | 0.00041261 | 0.00041842 | 0.00042424 | 0.00043006 | 0.00043588 | 0.00044169 | 0.00044751 | 0.00045333 | 0.00045915 | 0.00046496 | 0.00047078 | 0.0004766 | 0.00048242 | 0.00048823 | 0.00049405 | 0.00049987
| 10441153 | GCY014 | GCY | 17167477 | 17577196 | 0.36132 | 144.3343 | -38.1628 | 108 | 94.9 | 5.4% | 7.3% | 113.832 | 100.0246 | 0.01 | 0.02 | -1380.74 | 127.6394 | 1.422% | 115.884 | 101.8277 | 0.01 | 0.02 | -1405.63 | 129.9403 | 1.561% | 142.2% | 0.9614% | 0.9757% | 0.9901% | 1.004% | 1.019% | 1.033% | 1.048% | 1.062% | 1.076% | 1.091% | 1.105% | 1.119% | 1.134% | 1.148% | 1.162% | 1.177% | 1.191% | 1.206% | 1.22% | 1.234% | 0.00038933 | 0.00039515 | 0.00040097 | 0.00040679 | 0.00041261 | 0.00041842 | 0.00042424 | 0.00043006 | 0.00043588 | 0.00044169 | 0.00044751 | 0.00045333 | 0.00045915 | 0.00046496 | 0.00047078 | 0.0004766 | 0.00048242 | 0.00048823 | 0.00049405 | 0.00049987
| 10441155 | GCY014 | GCY | 17167485 | 17167489 | 0.52051 | 144.3352 | -38.1626 | 108 | 94.9 | 5.4% | 7.3% | 113.832 | 100.0246 | 0.01 | 0.02 | -1380.74 | 127.6394 | 1.422% | 115.884 | 101.8277 | 0.01 | 0.02 | -1405.63 | 129.9403 | 1.561% | 142.2% | 0.9614% | 0.9757% | 0.9901% | 1.004% | 1.019% | 1.033% | 1.048% | 1.062% | 1.076% | 1.091% | 1.105% | 1.119% | 1.134% | 1.148% | 1.162% | 1.177% | 1.191% | 1.206% | 1.22% | 1.234% | 0.00038933 | 0.00039515 | 0.00040097 | 0.00040679 | 0.00041261 | 0.00041842 | 0.00042424 | 0.00043006 | 0.00043588 | 0.00044169 | 0.00044751 | 0.00045333 | 0.00045915 | 0.00046496 | 0.00047078 | 0.0004766 | 0.00048242 | 0.00048823 | 0.00049405 | 0.00049987
| 10441156 | GCY014 | GCY | 17167489 | 17167493 | 0.16084 | 144.3356 | -38.1625 | 108 | 94.9 | 5.4% | 7.3% | 113.832 | 100.0246 | 0.01 | 0.02 | -1380.74 | 127.6394 | 1.422% | 115.884 | 101.8277 | 0.01 | 0.02 | -1405.63 | 129.9403 | 1.561% | 142.2% | 0.9614% | 0.9757% | 0.9901% | 1.004% | 1.019% | 1.033% | 1.048% | 1.062% | 1.076% | 1.091% | 1.105% | 1.119% | 1.134% | 1.148% | 1.162% | 1.177% | 1.191% | 1.206% | 1.22% | 1.234% | 0.00038933 | 0.00039515 | 0.00040097 | 0.00040679 | 0.00041261 | 0.00041842 | 0.00042424 | 0.00043006 | 0.00043588 | 0.00044169 | 0.00044751 | 0.00045333 | 0.00045915 | 0.00046496 | 0.00047078 | 0.0004766 | 0.00048242 | 0.00048823 | 0.00049405 | 0.00049987
| 10444738 | CME016 | CME | 17181974 | 17181969 | 1.93 | 145.6887 | -35.9913 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10444739 | CME016 | CME | 17181983 | 17181974 | 0.49284 | 145.6894 | -35.9926 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10444742 | CME016 | CME | 17182006 | 17181998 | 0.54896 | 145.699 | -36.0028 | 113 | 100 | 6.3% | 8.8% | 120.119 | 106.3 | 0.01 | 0.02 | -1381.9 | 133.938 | 1.515% | 121.249 | 108.8 | 0.01 | 0.02 | -1244.9 | 133.698 | 1.663% | 151.5% | 0.9708% | 0.9884% | 1.006% | 1.023% | 1.041% | 1.058% | 1.076% | 1.093% | 1.111% | 1.129% | 1.146% | 1.164% | 1.181% | 1.199% | 1.216% | 1.234% | 1.251% | 1.269% | 1.286% | 1.304% | 0.00039317 | 0.00040026 | 0.00040736 | 0.00041445 | 0.00042155 | 0.00042865 | 0.00043574 | 0.00044284 | 0.00044993 | 0.00045703 | 0.00046412 | 0.00047122 | 0.00047831 | 0.00048541 | 0.00049251 | 0.0004996 | 0.0005067 | 0.00051379 | 0.00052089 | 0.00052798
| 10444771 | CME014 | CME | 17182161 | 17182165 | 0.16924 | 145.7287 | -35.9846 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10444772 | CME014 | CME | 17182165 | 17182169 | 1.0384 | 145.726 | -35.9846 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10444773 | CME014 | CME | 17182169 | 17182173 | 0.86503 | 145.7233 | -35.9846 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10445669 | GHP012 | GHP | 17186432 | 17186391 | 2.9457 | 144.2854 | -38.0889 | 109 | 95.8 | 5.4% | 7.3% | 114.886 | 100.9732 | 0.01 | 0.02 | -1391.28 | 128.7988 | 1.423% | 116.957 | 102.7934 | 0.01 | 0.02 | -1416.36 | 131.1206 | 1.562% | 142.3% | 0.9614% | 0.9758% | 0.9902% | 1.005% | 1.019% | 1.033% | 1.048% | 1.062% | 1.077% | 1.091% | 1.105% | 1.12% | 1.134% | 1.148% | 1.163% | 1.177% | 1.192% | 1.206% | 1.22% | 1.235% | 0.00038936 | 0.00039519 | 0.00040102 | 0.00040684 | 0.00041267 | 0.0004185 | 0.00042432 | 0.00043015 | 0.00043598 | 0.00044181 | 0.00044763 | 0.00045346 | 0.00045929 | 0.00046511 | 0.00047094 | 0.00047677 | 0.0004826 | 0.00048842 | 0.00049425 | 0.00050008
| 10449773 | CDN004 | CDN | 17205509 | 17205505 | 1.0559 | 143.2191 | -38.0596 | 116 | 101 | 5.4% | 7.3% | 122.264 | 106.454 | 0.01 | 0.02 | -1581 | 138.074 | 1.396% | 124.468 | 108.373 | 0.01 | 0.02 | -1609.5 | 140.563 | 1.526% | 139.6% | 0.9587% | 0.9722% | 0.9856% | 0.9991% | 1.013% | 1.026% | 1.04% | 1.053% | 1.066% | 1.08% | 1.093% | 1.107% | 1.12% | 1.134% | 1.147% | 1.161% | 1.174% | 1.188% | 1.201% | 1.215% | 0.00038825 | 0.00039371 | 0.00039917 | 0.00040462 | 0.00041008 | 0.00041554 | 0.000421 | 0.00042645 | 0.00043191 | 0.00043737 | 0.00044282 | 0.00044828 | 0.00045374 | 0.00045919 | 0.00046465 | 0.00047011 | 0.00047557 | 0.00048102 | 0.00048648 | 0.00049194
| 10449775 | CDN004 | CDN | 17205517 | 17205513 | 2.03 | 143.2245 | -38.0588 | 116 | 101 | 5.4% | 7.3% | 122.264 | 106.454 | 0.01 | 0.02 | -1581 | 138.074 | 1.396% | 124.468 | 108.373 | 0.01 | 0.02 | -1609.5 | 140.563 | 1.526% | 139.6% | 0.9587% | 0.9722% | 0.9856% | 0.9991% | 1.013% | 1.026% | 1.04% | 1.053% | 1.066% | 1.08% | 1.093% | 1.107% | 1.12% | 1.134% | 1.147% | 1.161% | 1.174% | 1.188% | 1.201% | 1.215% | 0.00038825 | 0.00039371 | 0.00039917 | 0.00040462 | 0.00041008 | 0.00041554 | 0.000421 | 0.00042645 | 0.00043191 | 0.00043737 | 0.00044282 | 0.00044828 | 0.00045374 | 0.00045919 | 0.00046465 | 0.00047011 | 0.00047557 | 0.00048102 | 0.00048648 | 0.00049194
| 10449921 | CDN004 | CDN | 17206120 | 17206124 | 0.22841 | 143.4066 | -38.0797 | 106 | 93.3 | 5.4% | 7.3% | 111.724 | 98.3382 | 0.01 | 0.02 | -1338.58 | 125.1098 | 1.428% | 113.738 | 100.1109 | 0.01 | 0.02 | -1362.71 | 127.3651 | 1.568% | 142.8% | 0.9619% | 0.9764% | 0.991% | 1.006% | 1.02% | 1.035% | 1.049% | 1.064% | 1.078% | 1.093% | 1.107% | 1.122% | 1.136% | 1.151% | 1.166% | 1.18% | 1.195% | 1.209% | 1.224% | 1.238% | 0.00038955 | 0.00039544 | 0.00040133 | 0.00040722 | 0.00041311 | 0.000419 | 0.00042489 | 0.00043078 | 0.00043667 | 0.00044256 | 0.00044845 | 0.00045434 | 0.00046023 | 0.00046612 | 0.00047201 | 0.0004779 | 0.00048379 | 0.00048968 | 0.00049557 | 0.00050146
| 10451873 | NKA002 | RCTS | 17366698 | 17215357 | 0.38653 | 145.0308 | -35.9701 | 110 | 97.6 | 6.3% | 8.8% | 116.93 | 103.7488 | 0.01 | 0.02 | -1318.12 | 130.1112 | 1.526% | 118.03 | 106.1888 | 0.01 | 0.02 | -1184.12 | 129.8712 | 1.678% | 152.6% | 0.9719% | 0.9898% | 1.008% | 1.026% | 1.043% | 1.061% | 1.079% | 1.097% | 1.115% | 1.133% | 1.151% | 1.169% | 1.186% | 1.204% | 1.222% | 1.24% | 1.258% | 1.276% | 1.294% | 1.312% | 0.00039361 | 0.00040085 | 0.00040809 | 0.00041533 | 0.00042257 | 0.00042981 | 0.00043705 | 0.0004443 | 0.00045154 | 0.00045878 | 0.00046602 | 0.00047326 | 0.0004805 | 0.00048774 | 0.00049498 | 0.00050223 | 0.00050947 | 0.00051671 | 0.00052395 | 0.00053119
| 10451874 | NKA002 | RCTS | 17215357 | 17215361 | 0.60441 | 145.0309 | -35.9723 | 110 | 97.6 | 6.3% | 8.8% | 116.93 | 103.7488 | 0.01 | 0.02 | -1318.12 | 130.1112 | 1.526% | 118.03 | 106.1888 | 0.01 | 0.02 | -1184.12 | 129.8712 | 1.678% | 152.6% | 0.9719% | 0.9898% | 1.008% | 1.026% | 1.043% | 1.061% | 1.079% | 1.097% | 1.115% | 1.133% | 1.151% | 1.169% | 1.186% | 1.204% | 1.222% | 1.24% | 1.258% | 1.276% | 1.294% | 1.312% | 0.00039361 | 0.00040085 | 0.00040809 | 0.00041533 | 0.00042257 | 0.00042981 | 0.00043705 | 0.0004443 | 0.00045154 | 0.00045878 | 0.00046602 | 0.00047326 | 0.0004805 | 0.00048774 | 0.00049498 | 0.00050223 | 0.00050947 | 0.00051671 | 0.00052395 | 0.00053119
| 10451880 | NKA002 | RCTS | 17215377 | 17215381 | 0.16216 | 145.0311 | -35.984 | 109 | 97 | 6.3% | 8.8% | 115.867 | 103.111 | 0.01 | 0.02 | -1275.6 | 128.623 | 1.538% | 116.957 | 105.536 | 0.01 | 0.02 | -1142.1 | 128.378 | 1.697% | 153.8% | 0.9732% | 0.9915% | 1.01% | 1.028% | 1.046% | 1.065% | 1.083% | 1.101% | 1.12% | 1.138% | 1.156% | 1.175% | 1.193% | 1.211% | 1.23% | 1.248% | 1.266% | 1.284% | 1.303% | 1.321% | 0.00039413 | 0.00040154 | 0.00040896 | 0.00041637 | 0.00042378 | 0.0004312 | 0.00043861 | 0.00044603 | 0.00045344 | 0.00046086 | 0.00046827 | 0.00047569 | 0.0004831 | 0.00049052 | 0.00049793 | 0.00050535 | 0.00051276 | 0.00052018 | 0.00052759 | 0.000535
| 10452431 | NKA002 | RCTS | 17218764 | 17217714 | 1.2798 | 145.2051 | -36.0335 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10453092 | KYM004 | KYM | 17220480 | 17221031 | 1.8217 | 145.1871 | -36.15 | 112 | 98.5 | 6.3% | 8.8% | 119.056 | 104.7055 | 0.01 | 0.02 | -1435.05 | 133.4065 | 1.492% | 120.176 | 107.168 | 0.01 | 0.02 | -1300.8 | 133.184 | 1.629% | 149.2% | 0.9684% | 0.9852% | 1.002% | 1.019% | 1.035% | 1.052% | 1.069% | 1.085% | 1.102% | 1.119% | 1.136% | 1.152% | 1.169% | 1.186% | 1.203% | 1.219% | 1.236% | 1.253% | 1.269% | 1.286% | 0.0003922 | 0.00039897 | 0.00040574 | 0.00041252 | 0.00041929 | 0.00042606 | 0.00043283 | 0.0004396 | 0.00044638 | 0.00045315 | 0.00045992 | 0.00046669 | 0.00047347 | 0.00048024 | 0.00048701 | 0.00049378 | 0.00050055 | 0.00050733 | 0.0005141 | 0.00052087
| 10453231 | KYM004 | KYM | 17221031 | 17221039 | 0.92026 | 145.1887 | -36.147 | 112 | 98.8 | 6.3% | 8.8% | 119.056 | 105.0244 | 0.01 | 0.02 | -1403.16 | 133.0876 | 1.503% | 120.176 | 107.4944 | 0.01 | 0.02 | -1268.16 | 132.8576 | 1.645% | 150.3% | 0.9696% | 0.9867% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.089% | 1.106% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.226% | 1.243% | 1.26% | 1.277% | 1.295% | 0.00039266 | 0.00039959 | 0.00040651 | 0.00041344 | 0.00042036 | 0.00042729 | 0.00043422 | 0.00044114 | 0.00044807 | 0.000455 | 0.00046192 | 0.00046885 | 0.00047577 | 0.0004827 | 0.00048963 | 0.00049655 | 0.00050348 | 0.0005104 | 0.00051733 | 0.00052426
| 10457145 | SHN024 | SHN | 17624062 | 17238617 | 0.53302 | 145.469 | -36.3249 | 114 | 99.8 | 6.3% | 8.8% | 121.182 | 106.0874 | 0.01 | 0.02 | -1509.46 | 136.2766 | 1.476% | 122.322 | 108.5824 | 0.01 | 0.02 | -1373.96 | 136.0616 | 1.606% | 147.6% | 0.9668% | 0.983% | 0.9992% | 1.015% | 1.032% | 1.048% | 1.064% | 1.08% | 1.096% | 1.112% | 1.129% | 1.145% | 1.161% | 1.177% | 1.193% | 1.21% | 1.226% | 1.242% | 1.258% | 1.274% | 0.00039154 | 0.0003981 | 0.00040465 | 0.0004112 | 0.00041776 | 0.00042431 | 0.00043086 | 0.00043742 | 0.00044397 | 0.00045052 | 0.00045708 | 0.00046363 | 0.00047018 | 0.00047674 | 0.00048329 | 0.00048984 | 0.0004964 | 0.00050295 | 0.0005095 | 0.00051606
| 10457656 | STN024 | STN | 188526749 | 17240796 | 1.0631 | 145.6316 | -36.313 | 114 | 99.5 | 6.3% | 8.8% | 121.182 | 105.7685 | 0.01 | 0.02 | -1541.35 | 136.5955 | 1.466% | 122.322 | 108.256 | 0.01 | 0.02 | -1406.6 | 136.388 | 1.592% | 146.6% | 0.9658% | 0.9817% | 0.9975% | 1.013% | 1.029% | 1.045% | 1.061% | 1.077% | 1.093% | 1.108% | 1.124% | 1.14% | 1.156% | 1.172% | 1.188% | 1.204% | 1.219% | 1.235% | 1.251% | 1.267% | 0.00039113 | 0.00039755 | 0.00040397 | 0.00041039 | 0.00041681 | 0.00042322 | 0.00042964 | 0.00043606 | 0.00044248 | 0.0004489 | 0.00045531 | 0.00046173 | 0.00046815 | 0.00047457 | 0.00048098 | 0.0004874 | 0.00049382 | 0.00050024 | 0.00050666 | 0.00051307
| 10457822 | STN024 | STN | 17241512 | 17241508 | 1.6335 | 145.733 | -36.299 | 113 | 99.7 | 6.3% | 8.8% | 120.119 | 105.9811 | 0.01 | 0.02 | -1413.79 | 134.2569 | 1.504% | 121.249 | 108.4736 | 0.01 | 0.02 | -1277.54 | 134.0244 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039269 | 0.00039962 | 0.00040656 | 0.00041349 | 0.00042043 | 0.00042737 | 0.0004343 | 0.00044124 | 0.00044817 | 0.00045511 | 0.00046204 | 0.00046898 | 0.00047591 | 0.00048285 | 0.00048978 | 0.00049672 | 0.00050366 | 0.00051059 | 0.00051753 | 0.00052446
| 10457823 | STN024 | STN | 17241508 | 17241555 | 2.3687 | 145.7315 | -36.2976 | 113 | 99.7 | 6.3% | 8.8% | 120.119 | 105.9811 | 0.01 | 0.02 | -1413.79 | 134.2569 | 1.504% | 121.249 | 108.4736 | 0.01 | 0.02 | -1277.54 | 134.0244 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039269 | 0.00039962 | 0.00040656 | 0.00041349 | 0.00042043 | 0.00042737 | 0.0004343 | 0.00044124 | 0.00044817 | 0.00045511 | 0.00046204 | 0.00046898 | 0.00047591 | 0.00048285 | 0.00048978 | 0.00049672 | 0.00050366 | 0.00051059 | 0.00051753 | 0.00052446
| 10457824 | STN024 | STN | 17241516 | 17241512 | 0.27461 | 145.7362 | -36.299 | 113 | 99.7 | 6.3% | 8.8% | 120.119 | 105.9811 | 0.01 | 0.02 | -1413.79 | 134.2569 | 1.504% | 121.249 | 108.4736 | 0.01 | 0.02 | -1277.54 | 134.0244 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039269 | 0.00039962 | 0.00040656 | 0.00041349 | 0.00042043 | 0.00042737 | 0.0004343 | 0.00044124 | 0.00044817 | 0.00045511 | 0.00046204 | 0.00046898 | 0.00047591 | 0.00048285 | 0.00048978 | 0.00049672 | 0.00050366 | 0.00051059 | 0.00051753 | 0.00052446
| 10457825 | STN024 | STN | 17241520 | 17241516 | 0.23459 | 145.7393 | -36.299 | 113 | 99.7 | 6.3% | 8.8% | 120.119 | 105.9811 | 0.01 | 0.02 | -1413.79 | 134.2569 | 1.504% | 121.249 | 108.4736 | 0.01 | 0.02 | -1277.54 | 134.0244 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039269 | 0.00039962 | 0.00040656 | 0.00041349 | 0.00042043 | 0.00042737 | 0.0004343 | 0.00044124 | 0.00044817 | 0.00045511 | 0.00046204 | 0.00046898 | 0.00047591 | 0.00048285 | 0.00048978 | 0.00049672 | 0.00050366 | 0.00051059 | 0.00051753 | 0.00052446
| 10457879 | STN024 | STN | 17241749 | 188526679 | 0.88101 | 145.6904 | -36.324 | 118 | 103 | 6.3% | 8.8% | 125.434 | 109.489 | 0.01 | 0.02 | -1594.5 | 141.379 | 1.466% | 126.614 | 112.064 | 0.01 | 0.02 | -1455 | 141.164 | 1.592% | 146.6% | 0.9658% | 0.9817% | 0.9976% | 1.013% | 1.029% | 1.045% | 1.061% | 1.077% | 1.093% | 1.109% | 1.124% | 1.14% | 1.156% | 1.172% | 1.188% | 1.204% | 1.22% | 1.235% | 1.251% | 1.267% | 0.00039115 | 0.00039757 | 0.00040399 | 0.00041041 | 0.00041683 | 0.00042325 | 0.00042968 | 0.0004361 | 0.00044252 | 0.00044894 | 0.00045536 | 0.00046178 | 0.0004682 | 0.00047463 | 0.00048105 | 0.00048747 | 0.00049389 | 0.00050031 | 0.00050673 | 0.00051316
| 10457889 | STN024 | STN | 17241783 | 17241774 | 1.7897 | 145.7095 | -36.3302 | 120 | 105 | 6.3% | 8.8% | 127.56 | 111.615 | 0.01 | 0.02 | -1594.5 | 143.505 | 1.474% | 128.76 | 114.24 | 0.01 | 0.02 | -1452 | 143.28 | 1.603% | 147.4% | 0.9666% | 0.9828% | 0.9989% | 1.015% | 1.031% | 1.047% | 1.063% | 1.08% | 1.096% | 1.112% | 1.128% | 1.144% | 1.16% | 1.176% | 1.192% | 1.209% | 1.225% | 1.241% | 1.257% | 1.273% | 0.00039147 | 0.000398 | 0.00040453 | 0.00041106 | 0.00041759 | 0.00042412 | 0.00043065 | 0.00043719 | 0.00044372 | 0.00045025 | 0.00045678 | 0.00046331 | 0.00046984 | 0.00047637 | 0.0004829 | 0.00048943 | 0.00049596 | 0.00050249 | 0.00050902 | 0.00051555
| 10457891 | STN024 | STN | 188526559 | 17241783 | 2.7161 | 145.7079 | -36.3286 | 120 | 105 | 6.3% | 8.8% | 127.56 | 111.615 | 0.01 | 0.02 | -1594.5 | 143.505 | 1.474% | 128.76 | 114.24 | 0.01 | 0.02 | -1452 | 143.28 | 1.603% | 147.4% | 0.9666% | 0.9828% | 0.9989% | 1.015% | 1.031% | 1.047% | 1.063% | 1.08% | 1.096% | 1.112% | 1.128% | 1.144% | 1.16% | 1.176% | 1.192% | 1.209% | 1.225% | 1.241% | 1.257% | 1.273% | 0.00039147 | 0.000398 | 0.00040453 | 0.00041106 | 0.00041759 | 0.00042412 | 0.00043065 | 0.00043719 | 0.00044372 | 0.00045025 | 0.00045678 | 0.00046331 | 0.00046984 | 0.00047637 | 0.0004829 | 0.00048943 | 0.00049596 | 0.00050249 | 0.00050902 | 0.00051555
| 10458007 | STN024 | STN | 17242286 | 17577887 | 0.74315 | 145.6903 | -36.2963 | 113 | 99.4 | 6.3% | 8.8% | 120.119 | 105.6622 | 0.01 | 0.02 | -1445.68 | 134.5758 | 1.492% | 121.249 | 108.1472 | 0.01 | 0.02 | -1310.18 | 134.3508 | 1.63% | 149.2% | 0.9685% | 0.9853% | 1.002% | 1.019% | 1.036% | 1.052% | 1.069% | 1.086% | 1.102% | 1.119% | 1.136% | 1.153% | 1.169% | 1.186% | 1.203% | 1.22% | 1.236% | 1.253% | 1.27% | 1.287% | 0.00039223 | 0.00039901 | 0.00040579 | 0.00041258 | 0.00041936 | 0.00042614 | 0.00043292 | 0.00043971 | 0.00044649 | 0.00045327 | 0.00046005 | 0.00046684 | 0.00047362 | 0.0004804 | 0.00048718 | 0.00049397 | 0.00050075 | 0.00050753 | 0.00051431 | 0.0005211
| 10458226 | STN011 | STN | 17243318 | 123231361 | 1.6695 | 145.668 | -36.4273 | 119 | 104 | 6.3% | 8.8% | 126.497 | 110.552 | 0.01 | 0.02 | -1594.5 | 142.442 | 1.47% | 127.687 | 113.152 | 0.01 | 0.02 | -1453.5 | 142.222 | 1.598% | 147% | 0.9662% | 0.9822% | 0.9982% | 1.014% | 1.03% | 1.046% | 1.062% | 1.078% | 1.094% | 1.11% | 1.126% | 1.142% | 1.158% | 1.174% | 1.19% | 1.206% | 1.222% | 1.238% | 1.254% | 1.27% | 0.00039131 | 0.00039779 | 0.00040426 | 0.00041074 | 0.00041721 | 0.00042369 | 0.00043017 | 0.00043664 | 0.00044312 | 0.00044959 | 0.00045607 | 0.00046254 | 0.00046902 | 0.0004755 | 0.00048197 | 0.00048845 | 0.00049492 | 0.0005014 | 0.00050788 | 0.00051435
| 10458228 | STN011 | STN | 123231361 | 17243331 | 0.46262 | 145.67 | -36.4277 | 119 | 104 | 6.3% | 8.8% | 126.497 | 110.552 | 0.01 | 0.02 | -1594.5 | 142.442 | 1.47% | 127.687 | 113.152 | 0.01 | 0.02 | -1453.5 | 142.222 | 1.598% | 147% | 0.9662% | 0.9822% | 0.9982% | 1.014% | 1.03% | 1.046% | 1.062% | 1.078% | 1.094% | 1.11% | 1.126% | 1.142% | 1.158% | 1.174% | 1.19% | 1.206% | 1.222% | 1.238% | 1.254% | 1.27% | 0.00039131 | 0.00039779 | 0.00040426 | 0.00041074 | 0.00041721 | 0.00042369 | 0.00043017 | 0.00043664 | 0.00044312 | 0.00044959 | 0.00045607 | 0.00046254 | 0.00046902 | 0.0004755 | 0.00048197 | 0.00048845 | 0.00049492 | 0.0005014 | 0.00050788 | 0.00051435
| 10458278 | STN024 | STN | 17243539 | 17243535 | 2.5966 | 145.7491 | -36.3855 | 118 | 103 | 6.3% | 8.8% | 125.434 | 109.489 | 0.01 | 0.02 | -1594.5 | 141.379 | 1.466% | 126.614 | 112.064 | 0.01 | 0.02 | -1455 | 141.164 | 1.592% | 146.6% | 0.9658% | 0.9817% | 0.9976% | 1.013% | 1.029% | 1.045% | 1.061% | 1.077% | 1.093% | 1.109% | 1.124% | 1.14% | 1.156% | 1.172% | 1.188% | 1.204% | 1.22% | 1.235% | 1.251% | 1.267% | 0.00039115 | 0.00039757 | 0.00040399 | 0.00041041 | 0.00041683 | 0.00042325 | 0.00042968 | 0.0004361 | 0.00044252 | 0.00044894 | 0.00045536 | 0.00046178 | 0.0004682 | 0.00047463 | 0.00048105 | 0.00048747 | 0.00049389 | 0.00050031 | 0.00050673 | 0.00051316
| 10458309 | STN024 | STN | 17243757 | 17243665 | 0.13549 | 145.783 | -36.4038 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10458332 | STN024 | STN | 17243762 | 17785417 | 1.22 | 145.7791 | -36.4032 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10458955 | MRO005 | MRO | 17246512 | 17246517 | 0.72515 | 143.7496 | -37.0355 | 110 | 98.1 | 6.3% | 8.8% | 116.93 | 104.2803 | 0.01 | 0.02 | -1264.97 | 129.5797 | 1.548% | 118.03 | 106.7328 | 0.01 | 0.02 | -1129.72 | 129.3272 | 1.711% | 154.8% | 0.9742% | 0.9928% | 1.011% | 1.03% | 1.049% | 1.067% | 1.086% | 1.105% | 1.123% | 1.142% | 1.16% | 1.179% | 1.198% | 1.216% | 1.235% | 1.254% | 1.272% | 1.291% | 1.31% | 1.328% | 0.00039452 | 0.00040206 | 0.00040961 | 0.00041716 | 0.0004247 | 0.00043225 | 0.00043979 | 0.00044734 | 0.00045488 | 0.00046243 | 0.00046997 | 0.00047752 | 0.00048507 | 0.00049261 | 0.00050016 | 0.0005077 | 0.00051525 | 0.00052279 | 0.00053034 | 0.00053788
| 10459329 | MRO005 | MRO | 17248196 | 17248192 | 0.9444 | 143.7441 | -36.8735 | 105 | 94.5 | 6.3% | 8.8% | 111.615 | 100.4535 | 0.01 | 0.02 | -1116.15 | 122.7765 | 1.593% | 112.665 | 102.816 | 0.01 | 0.02 | -984.9 | 122.514 | 1.778% | 159.3% | 0.9787% | 0.9989% | 1.019% | 1.039% | 1.059% | 1.08% | 1.1% | 1.12% | 1.14% | 1.16% | 1.18% | 1.2% | 1.221% | 1.241% | 1.261% | 1.281% | 1.301% | 1.321% | 1.342% | 1.362% | 0.00039637 | 0.00040453 | 0.0004127 | 0.00042086 | 0.00042902 | 0.00043719 | 0.00044535 | 0.00045351 | 0.00046167 | 0.00046984 | 0.000478 | 0.00048616 | 0.00049433 | 0.00050249 | 0.00051065 | 0.00051882 | 0.00052698 | 0.00053514 | 0.0005433 | 0.00055147
| 10459384 | MRO005 | MRO | 17248416 | 17248420 | 0.97623 | 143.7664 | -36.9161 | 105 | 93.9 | 6.3% | 8.8% | 111.615 | 99.8157 | 0.01 | 0.02 | -1179.93 | 123.4143 | 1.561% | 112.665 | 102.1632 | 0.01 | 0.02 | -1050.18 | 123.1668 | 1.73% | 156.1% | 0.9755% | 0.9945% | 1.014% | 1.033% | 1.052% | 1.071% | 1.09% | 1.109% | 1.128% | 1.147% | 1.166% | 1.185% | 1.204% | 1.223% | 1.242% | 1.261% | 1.281% | 1.3% | 1.319% | 1.338% | 0.00039505 | 0.00040277 | 0.00041049 | 0.00041821 | 0.00042593 | 0.00043366 | 0.00044138 | 0.0004491 | 0.00045682 | 0.00046454 | 0.00047226 | 0.00047999 | 0.00048771 | 0.00049543 | 0.00050315 | 0.00051087 | 0.00051859 | 0.00052632 | 0.00053404 | 0.00054176
| 10459436 | MRO005 | MRO | 17250584 | 17248652 | 0.63899 | 143.7327 | -36.946 | 105 | 93.9 | 6.3% | 8.8% | 111.615 | 99.8157 | 0.01 | 0.02 | -1179.93 | 123.4143 | 1.561% | 112.665 | 102.1632 | 0.01 | 0.02 | -1050.18 | 123.1668 | 1.73% | 156.1% | 0.9755% | 0.9945% | 1.014% | 1.033% | 1.052% | 1.071% | 1.09% | 1.109% | 1.128% | 1.147% | 1.166% | 1.185% | 1.204% | 1.223% | 1.242% | 1.261% | 1.281% | 1.3% | 1.319% | 1.338% | 0.00039505 | 0.00040277 | 0.00041049 | 0.00041821 | 0.00042593 | 0.00043366 | 0.00044138 | 0.0004491 | 0.00045682 | 0.00046454 | 0.00047226 | 0.00047999 | 0.00048771 | 0.00049543 | 0.00050315 | 0.00051087 | 0.00051859 | 0.00052632 | 0.00053404 | 0.00054176
| 10459437 | MRO005 | MRO | 17248652 | 64828988 | 0.48736 | 143.7334 | -36.9451 | 105 | 93.9 | 6.3% | 8.8% | 111.615 | 99.8157 | 0.01 | 0.02 | -1179.93 | 123.4143 | 1.561% | 112.665 | 102.1632 | 0.01 | 0.02 | -1050.18 | 123.1668 | 1.73% | 156.1% | 0.9755% | 0.9945% | 1.014% | 1.033% | 1.052% | 1.071% | 1.09% | 1.109% | 1.128% | 1.147% | 1.166% | 1.185% | 1.204% | 1.223% | 1.242% | 1.261% | 1.281% | 1.3% | 1.319% | 1.338% | 0.00039505 | 0.00040277 | 0.00041049 | 0.00041821 | 0.00042593 | 0.00043366 | 0.00044138 | 0.0004491 | 0.00045682 | 0.00046454 | 0.00047226 | 0.00047999 | 0.00048771 | 0.00049543 | 0.00050315 | 0.00051087 | 0.00051859 | 0.00052632 | 0.00053404 | 0.00054176
| 10459605 | MRO005 | MRO | 17249320 | 17249351 | 2.2484 | 143.7851 | -36.9012 | 104 | 93.1 | 6.3% | 8.8% | 110.552 | 98.9653 | 0.01 | 0.02 | -1158.67 | 122.1387 | 1.565% | 111.592 | 101.2928 | 0.01 | 0.02 | -1029.92 | 121.8912 | 1.737% | 156.5% | 0.976% | 0.9952% | 1.014% | 1.034% | 1.053% | 1.072% | 1.091% | 1.111% | 1.13% | 1.149% | 1.168% | 1.188% | 1.207% | 1.226% | 1.245% | 1.264% | 1.284% | 1.303% | 1.322% | 1.341% | 0.00039525 | 0.00040304 | 0.00041082 | 0.00041861 | 0.0004264 | 0.00043419 | 0.00044198 | 0.00044977 | 0.00045756 | 0.00046534 | 0.00047313 | 0.00048092 | 0.00048871 | 0.0004965 | 0.00050429 | 0.00051208 | 0.00051986 | 0.00052765 | 0.00053544 | 0.00054323
| 10459607 | MRO005 | MRO | 17249324 | 17249329 | 3.2024 | 143.7833 | -36.8992 | 104 | 93.6 | 6.3% | 8.8% | 110.552 | 99.4968 | 0.01 | 0.02 | -1105.52 | 121.6072 | 1.593% | 111.592 | 101.8368 | 0.01 | 0.02 | -975.52 | 121.3472 | 1.778% | 159.3% | 0.9787% | 0.9989% | 1.019% | 1.039% | 1.059% | 1.08% | 1.1% | 1.12% | 1.14% | 1.16% | 1.18% | 1.2% | 1.221% | 1.241% | 1.261% | 1.281% | 1.301% | 1.321% | 1.342% | 1.362% | 0.00039637 | 0.00040453 | 0.0004127 | 0.00042086 | 0.00042902 | 0.00043719 | 0.00044535 | 0.00045351 | 0.00046167 | 0.00046984 | 0.000478 | 0.00048616 | 0.00049433 | 0.00050249 | 0.00051065 | 0.00051882 | 0.00052698 | 0.00053514 | 0.0005433 | 0.00055147
| 10459611 | MRO005 | MRO | 17249351 | 17249342 | 2.2185 | 143.7875 | -36.9029 | 104 | 93.1 | 6.3% | 8.8% | 110.552 | 98.9653 | 0.01 | 0.02 | -1158.67 | 122.1387 | 1.565% | 111.592 | 101.2928 | 0.01 | 0.02 | -1029.92 | 121.8912 | 1.737% | 156.5% | 0.976% | 0.9952% | 1.014% | 1.034% | 1.053% | 1.072% | 1.091% | 1.111% | 1.13% | 1.149% | 1.168% | 1.188% | 1.207% | 1.226% | 1.245% | 1.264% | 1.284% | 1.303% | 1.322% | 1.341% | 0.00039525 | 0.00040304 | 0.00041082 | 0.00041861 | 0.0004264 | 0.00043419 | 0.00044198 | 0.00044977 | 0.00045756 | 0.00046534 | 0.00047313 | 0.00048092 | 0.00048871 | 0.0004965 | 0.00050429 | 0.00051208 | 0.00051986 | 0.00052765 | 0.00053544 | 0.00054323
| 10459612 | MRO005 | MRO | 17249355 | 17249342 | 1.7848 | 143.79 | -36.9045 | 104 | 93.1 | 6.3% | 8.8% | 110.552 | 98.9653 | 0.01 | 0.02 | -1158.67 | 122.1387 | 1.565% | 111.592 | 101.2928 | 0.01 | 0.02 | -1029.92 | 121.8912 | 1.737% | 156.5% | 0.976% | 0.9952% | 1.014% | 1.034% | 1.053% | 1.072% | 1.091% | 1.111% | 1.13% | 1.149% | 1.168% | 1.188% | 1.207% | 1.226% | 1.245% | 1.264% | 1.284% | 1.303% | 1.322% | 1.341% | 0.00039525 | 0.00040304 | 0.00041082 | 0.00041861 | 0.0004264 | 0.00043419 | 0.00044198 | 0.00044977 | 0.00045756 | 0.00046534 | 0.00047313 | 0.00048092 | 0.00048871 | 0.0004965 | 0.00050429 | 0.00051208 | 0.00051986 | 0.00052765 | 0.00053544 | 0.00054323
| 10459677 | MRO005 | MRO | 17249599 | 17249613 | 0.72126 | 143.7885 | -36.9258 | 104 | 93.6 | 6.3% | 8.8% | 110.552 | 99.4968 | 0.01 | 0.02 | -1105.52 | 121.6072 | 1.593% | 111.592 | 101.8368 | 0.01 | 0.02 | -975.52 | 121.3472 | 1.778% | 159.3% | 0.9787% | 0.9989% | 1.019% | 1.039% | 1.059% | 1.08% | 1.1% | 1.12% | 1.14% | 1.16% | 1.18% | 1.2% | 1.221% | 1.241% | 1.261% | 1.281% | 1.301% | 1.321% | 1.342% | 1.362% | 0.00039637 | 0.00040453 | 0.0004127 | 0.00042086 | 0.00042902 | 0.00043719 | 0.00044535 | 0.00045351 | 0.00046167 | 0.00046984 | 0.000478 | 0.00048616 | 0.00049433 | 0.00050249 | 0.00051065 | 0.00051882 | 0.00052698 | 0.00053514 | 0.0005433 | 0.00055147
| 10459745 | MRO005 | MRO | 17249909 | 17249914 | 0.99462 | 143.7199 | -36.8645 | 105 | 94.8 | 6.3% | 8.8% | 111.615 | 100.7724 | 0.01 | 0.02 | -1084.26 | 122.4576 | 1.61% | 112.665 | 103.1424 | 0.01 | 0.02 | -952.26 | 122.1876 | 1.805% | 161% | 0.9805% | 1.001% | 1.022% | 1.043% | 1.064% | 1.084% | 1.105% | 1.126% | 1.147% | 1.167% | 1.188% | 1.209% | 1.23% | 1.25% | 1.271% | 1.292% | 1.313% | 1.333% | 1.354% | 1.375% | 0.00039709 | 0.00040549 | 0.0004139 | 0.0004223 | 0.0004307 | 0.00043911 | 0.00044751 | 0.00045591 | 0.00046432 | 0.00047272 | 0.00048112 | 0.00048952 | 0.00049793 | 0.00050633 | 0.00051473 | 0.00052314 | 0.00053154 | 0.00053994 | 0.00054835 | 0.00055675
| 10459909 | MRO005 | MRO | 17250588 | 17250584 | 0.41118 | 143.732 | -36.947 | 105 | 93.9 | 6.3% | 8.8% | 111.615 | 99.8157 | 0.01 | 0.02 | -1179.93 | 123.4143 | 1.561% | 112.665 | 102.1632 | 0.01 | 0.02 | -1050.18 | 123.1668 | 1.73% | 156.1% | 0.9755% | 0.9945% | 1.014% | 1.033% | 1.052% | 1.071% | 1.09% | 1.109% | 1.128% | 1.147% | 1.166% | 1.185% | 1.204% | 1.223% | 1.242% | 1.261% | 1.281% | 1.3% | 1.319% | 1.338% | 0.00039505 | 0.00040277 | 0.00041049 | 0.00041821 | 0.00042593 | 0.00043366 | 0.00044138 | 0.0004491 | 0.00045682 | 0.00046454 | 0.00047226 | 0.00047999 | 0.00048771 | 0.00049543 | 0.00050315 | 0.00051087 | 0.00051859 | 0.00052632 | 0.00053404 | 0.00054176
| 10459910 | MRO005 | MRO | 17250592 | 17250588 | 1.0537 | 143.7313 | -36.9479 | 105 | 93.9 | 6.3% | 8.8% | 111.615 | 99.8157 | 0.01 | 0.02 | -1179.93 | 123.4143 | 1.561% | 112.665 | 102.1632 | 0.01 | 0.02 | -1050.18 | 123.1668 | 1.73% | 156.1% | 0.9755% | 0.9945% | 1.014% | 1.033% | 1.052% | 1.071% | 1.09% | 1.109% | 1.128% | 1.147% | 1.166% | 1.185% | 1.204% | 1.223% | 1.242% | 1.261% | 1.281% | 1.3% | 1.319% | 1.338% | 0.00039505 | 0.00040277 | 0.00041049 | 0.00041821 | 0.00042593 | 0.00043366 | 0.00044138 | 0.0004491 | 0.00045682 | 0.00046454 | 0.00047226 | 0.00047999 | 0.00048771 | 0.00049543 | 0.00050315 | 0.00051087 | 0.00051859 | 0.00052632 | 0.00053404 | 0.00054176
| 10459911 | MRO005 | MRO | 17250596 | 17250592 | 2.1642 | 143.7306 | -36.9489 | 105 | 93.9 | 6.3% | 8.8% | 111.615 | 99.8157 | 0.01 | 0.02 | -1179.93 | 123.4143 | 1.561% | 112.665 | 102.1632 | 0.01 | 0.02 | -1050.18 | 123.1668 | 1.73% | 156.1% | 0.9755% | 0.9945% | 1.014% | 1.033% | 1.052% | 1.071% | 1.09% | 1.109% | 1.128% | 1.147% | 1.166% | 1.185% | 1.204% | 1.223% | 1.242% | 1.261% | 1.281% | 1.3% | 1.319% | 1.338% | 0.00039505 | 0.00040277 | 0.00041049 | 0.00041821 | 0.00042593 | 0.00043366 | 0.00044138 | 0.0004491 | 0.00045682 | 0.00046454 | 0.00047226 | 0.00047999 | 0.00048771 | 0.00049543 | 0.00050315 | 0.00051087 | 0.00051859 | 0.00052632 | 0.00053404 | 0.00054176
| 10459916 | MRO005 | MRO | 17250620 | 17250616 | 0.23347 | 143.7265 | -36.9545 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10459918 | MRO005 | MRO | 202768325 | 17250620 | 0.83681 | 143.7258 | -36.9553 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10459919 | MRO005 | MRO | 17250629 | 202768325 | 1.392 | 143.7252 | -36.9562 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10459924 | MRO005 | MRO | 17250650 | 17250646 | 1.4539 | 143.7232 | -36.9588 | 106 | 94.6 | 6.3% | 8.8% | 112.678 | 100.5598 | 0.01 | 0.02 | -1211.82 | 124.7962 | 1.551% | 113.738 | 102.9248 | 0.01 | 0.02 | -1081.32 | 124.5512 | 1.716% | 155.1% | 0.9745% | 0.9932% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.106% | 1.124% | 1.143% | 1.162% | 1.181% | 1.199% | 1.218% | 1.237% | 1.256% | 1.274% | 1.293% | 1.312% | 1.331% | 0.00039465 | 0.00040224 | 0.00040983 | 0.00041742 | 0.00042501 | 0.0004326 | 0.00044019 | 0.00044778 | 0.00045537 | 0.00046296 | 0.00047055 | 0.00047814 | 0.00048573 | 0.00049332 | 0.00050091 | 0.0005085 | 0.00051609 | 0.00052368 | 0.00053127 | 0.00053886
| 10459926 | MRO005 | MRO | 17250654 | 17250659 | 1.4967 | 143.7239 | -36.9605 | 106 | 94.6 | 6.3% | 8.8% | 112.678 | 100.5598 | 0.01 | 0.02 | -1211.82 | 124.7962 | 1.551% | 113.738 | 102.9248 | 0.01 | 0.02 | -1081.32 | 124.5512 | 1.716% | 155.1% | 0.9745% | 0.9932% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.106% | 1.124% | 1.143% | 1.162% | 1.181% | 1.199% | 1.218% | 1.237% | 1.256% | 1.274% | 1.293% | 1.312% | 1.331% | 0.00039465 | 0.00040224 | 0.00040983 | 0.00041742 | 0.00042501 | 0.0004326 | 0.00044019 | 0.00044778 | 0.00045537 | 0.00046296 | 0.00047055 | 0.00047814 | 0.00048573 | 0.00049332 | 0.00050091 | 0.0005085 | 0.00051609 | 0.00052368 | 0.00053127 | 0.00053886
| 10460035 | MRO005 | MRO | 17251106 | 17251110 | 3.0518 | 143.7202 | -36.9739 | 106 | 94.6 | 6.3% | 8.8% | 112.678 | 100.5598 | 0.01 | 0.02 | -1211.82 | 124.7962 | 1.551% | 113.738 | 102.9248 | 0.01 | 0.02 | -1081.32 | 124.5512 | 1.716% | 155.1% | 0.9745% | 0.9932% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.106% | 1.124% | 1.143% | 1.162% | 1.181% | 1.199% | 1.218% | 1.237% | 1.256% | 1.274% | 1.293% | 1.312% | 1.331% | 0.00039465 | 0.00040224 | 0.00040983 | 0.00041742 | 0.00042501 | 0.0004326 | 0.00044019 | 0.00044778 | 0.00045537 | 0.00046296 | 0.00047055 | 0.00047814 | 0.00048573 | 0.00049332 | 0.00050091 | 0.0005085 | 0.00051609 | 0.00052368 | 0.00053127 | 0.00053886
| 10460197 | MRO005 | MRO | 17251810 | 17251815 | 0.94052 | 143.7732 | -36.9597 | 106 | 94.9 | 6.3% | 8.8% | 112.678 | 100.8787 | 0.01 | 0.02 | -1179.93 | 124.4773 | 1.566% | 113.738 | 103.2512 | 0.01 | 0.02 | -1048.68 | 124.2248 | 1.738% | 156.6% | 0.976% | 0.9953% | 1.015% | 1.034% | 1.053% | 1.072% | 1.092% | 1.111% | 1.13% | 1.149% | 1.169% | 1.188% | 1.207% | 1.226% | 1.245% | 1.265% | 1.284% | 1.303% | 1.322% | 1.342% | 0.00039527 | 0.00040306 | 0.00041086 | 0.00041865 | 0.00042645 | 0.00043424 | 0.00044204 | 0.00044983 | 0.00045763 | 0.00046542 | 0.00047322 | 0.00048102 | 0.00048881 | 0.00049661 | 0.0005044 | 0.0005122 | 0.00051999 | 0.00052779 | 0.00053558 | 0.00054338
| 10460219 | MRO005 | MRO | 17251921 | 201895755 | 1.1029 | 143.7759 | -36.9778 | 107 | 95.3 | 6.3% | 8.8% | 113.741 | 101.3039 | 0.01 | 0.02 | -1243.71 | 126.1781 | 1.542% | 114.811 | 103.6864 | 0.01 | 0.02 | -1112.46 | 125.9356 | 1.702% | 154.2% | 0.9736% | 0.992% | 1.01% | 1.029% | 1.047% | 1.066% | 1.084% | 1.103% | 1.121% | 1.139% | 1.158% | 1.176% | 1.195% | 1.213% | 1.232% | 1.25% | 1.269% | 1.287% | 1.305% | 1.324% | 0.00039428 | 0.00040174 | 0.00040921 | 0.00041667 | 0.00042414 | 0.0004316 | 0.00043907 | 0.00044653 | 0.000454 | 0.00046146 | 0.00046893 | 0.0004764 | 0.00048386 | 0.00049133 | 0.00049879 | 0.00050626 | 0.00051372 | 0.00052119 | 0.00052865 | 0.00053612
| 10460333 | MRO005 | MRO | 17252413 | 17252409 | 1.2693 | 143.7575 | -37.0072 | 108 | 96.3 | 6.3% | 8.8% | 114.804 | 102.3669 | 0.01 | 0.02 | -1243.71 | 127.2411 | 1.547% | 115.884 | 104.7744 | 0.01 | 0.02 | -1110.96 | 126.9936 | 1.71% | 154.7% | 0.9741% | 0.9927% | 1.011% | 1.03% | 1.049% | 1.067% | 1.086% | 1.104% | 1.123% | 1.142% | 1.16% | 1.179% | 1.197% | 1.216% | 1.235% | 1.253% | 1.272% | 1.29% | 1.309% | 1.328% | 0.00039449 | 0.00040202 | 0.00040956 | 0.00041709 | 0.00042463 | 0.00043216 | 0.0004397 | 0.00044723 | 0.00045477 | 0.0004623 | 0.00046984 | 0.00047737 | 0.00048491 | 0.00049244 | 0.00049998 | 0.00050751 | 0.00051505 | 0.00052258 | 0.00053012 | 0.00053765
| 10460342 | MRO005 | MRO | 17252466 | 17252461 | 0.44964 | 143.749 | -37.0263 | 110 | 98.1 | 6.3% | 8.8% | 116.93 | 104.2803 | 0.01 | 0.02 | -1264.97 | 129.5797 | 1.548% | 118.03 | 106.7328 | 0.01 | 0.02 | -1129.72 | 129.3272 | 1.711% | 154.8% | 0.9742% | 0.9928% | 1.011% | 1.03% | 1.049% | 1.067% | 1.086% | 1.105% | 1.123% | 1.142% | 1.16% | 1.179% | 1.198% | 1.216% | 1.235% | 1.254% | 1.272% | 1.291% | 1.31% | 1.328% | 0.00039452 | 0.00040206 | 0.00040961 | 0.00041716 | 0.0004247 | 0.00043225 | 0.00043979 | 0.00044734 | 0.00045488 | 0.00046243 | 0.00046997 | 0.00047752 | 0.00048507 | 0.00049261 | 0.00050016 | 0.0005077 | 0.00051525 | 0.00052279 | 0.00053034 | 0.00053788
| 10460429 | MRO005 | MRO | 17252852 | 17252856 | 0.52537 | 143.7519 | -37.0302 | 109 | 96.9 | 6.3% | 8.8% | 115.867 | 103.0047 | 0.01 | 0.02 | -1286.23 | 128.7293 | 1.534% | 116.957 | 105.4272 | 0.01 | 0.02 | -1152.98 | 128.4868 | 1.69% | 153.4% | 0.9727% | 0.9909% | 1.009% | 1.027% | 1.045% | 1.064% | 1.082% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.191% | 1.209% | 1.227% | 1.245% | 1.263% | 1.281% | 1.3% | 1.318% | 0.00039394 | 0.0004013 | 0.00040865 | 0.000416 | 0.00042336 | 0.00043071 | 0.00043806 | 0.00044542 | 0.00045277 | 0.00046012 | 0.00046748 | 0.00047483 | 0.00048218 | 0.00048954 | 0.00049689 | 0.00050424 | 0.0005116 | 0.00051895 | 0.0005263 | 0.00053366
| 10460430 | MRO005 | MRO | 17252856 | 17252860 | 1.2951 | 143.7521 | -37.0291 | 109 | 96.9 | 6.3% | 8.8% | 115.867 | 103.0047 | 0.01 | 0.02 | -1286.23 | 128.7293 | 1.534% | 116.957 | 105.4272 | 0.01 | 0.02 | -1152.98 | 128.4868 | 1.69% | 153.4% | 0.9727% | 0.9909% | 1.009% | 1.027% | 1.045% | 1.064% | 1.082% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.191% | 1.209% | 1.227% | 1.245% | 1.263% | 1.281% | 1.3% | 1.318% | 0.00039394 | 0.0004013 | 0.00040865 | 0.000416 | 0.00042336 | 0.00043071 | 0.00043806 | 0.00044542 | 0.00045277 | 0.00046012 | 0.00046748 | 0.00047483 | 0.00048218 | 0.00048954 | 0.00049689 | 0.00050424 | 0.0005116 | 0.00051895 | 0.0005263 | 0.00053366
| 10460433 | MRO005 | MRO | 17252864 | 17252936 | 3.1403 | 143.7533 | -37.0274 | 109 | 96.9 | 6.3% | 8.8% | 115.867 | 103.0047 | 0.01 | 0.02 | -1286.23 | 128.7293 | 1.534% | 116.957 | 105.4272 | 0.01 | 0.02 | -1152.98 | 128.4868 | 1.69% | 153.4% | 0.9727% | 0.9909% | 1.009% | 1.027% | 1.045% | 1.064% | 1.082% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.191% | 1.209% | 1.227% | 1.245% | 1.263% | 1.281% | 1.3% | 1.318% | 0.00039394 | 0.0004013 | 0.00040865 | 0.000416 | 0.00042336 | 0.00043071 | 0.00043806 | 0.00044542 | 0.00045277 | 0.00046012 | 0.00046748 | 0.00047483 | 0.00048218 | 0.00048954 | 0.00049689 | 0.00050424 | 0.0005116 | 0.00051895 | 0.0005263 | 0.00053366
| 10461431 | CHA006 | CHA | 17257018 | 17257022 | 2.0638 | 144.1658 | -36.0859 | 102 | 90.8 | 6.3% | 8.8% | 108.426 | 96.5204 | 0.01 | 0.02 | -1190.56 | 120.3316 | 1.54% | 109.446 | 98.7904 | 0.01 | 0.02 | -1065.56 | 120.1016 | 1.699% | 154% | 0.9733% | 0.9917% | 1.01% | 1.028% | 1.047% | 1.065% | 1.083% | 1.102% | 1.12% | 1.139% | 1.157% | 1.175% | 1.194% | 1.212% | 1.23% | 1.249% | 1.267% | 1.285% | 1.304% | 1.322% | 0.00039418 | 0.00040162 | 0.00040905 | 0.00041649 | 0.00042392 | 0.00043135 | 0.00043879 | 0.00044622 | 0.00045366 | 0.00046109 | 0.00046853 | 0.00047596 | 0.00048339 | 0.00049083 | 0.00049826 | 0.0005057 | 0.00051313 | 0.00052056 | 0.000528 | 0.00053543
| 10462669 | CME015 | CME | 17262858 | 17262863 | 0.48884 | 145.6593 | -35.9784 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10462672 | CME015 | CME | 17262863 | 17262877 | 0.41764 | 145.658 | -35.9784 | 114 | 101 | 6.3% | 8.8% | 121.182 | 107.363 | 0.01 | 0.02 | -1381.9 | 135.001 | 1.52% | 122.322 | 109.888 | 0.01 | 0.02 | -1243.4 | 134.756 | 1.669% | 152% | 0.9713% | 0.989% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.166% | 1.183% | 1.201% | 1.219% | 1.236% | 1.254% | 1.272% | 1.289% | 1.307% | 0.00039336 | 0.00040051 | 0.00040767 | 0.00041483 | 0.00042199 | 0.00042915 | 0.00043631 | 0.00044346 | 0.00045062 | 0.00045778 | 0.00046494 | 0.0004721 | 0.00047926 | 0.00048641 | 0.00049357 | 0.00050073 | 0.00050789 | 0.00051505 | 0.00052221 | 0.00052936
| 10464607 | STN011 | STN | 17271295 | 17271551 | 0.17242 | 145.5301 | -36.4342 | 119 | 104 | 6.3% | 8.8% | 126.497 | 110.552 | 0.01 | 0.02 | -1594.5 | 142.442 | 1.47% | 127.687 | 113.152 | 0.01 | 0.02 | -1453.5 | 142.222 | 1.598% | 147% | 0.9662% | 0.9822% | 0.9982% | 1.014% | 1.03% | 1.046% | 1.062% | 1.078% | 1.094% | 1.11% | 1.126% | 1.142% | 1.158% | 1.174% | 1.19% | 1.206% | 1.222% | 1.238% | 1.254% | 1.27% | 0.00039131 | 0.00039779 | 0.00040426 | 0.00041074 | 0.00041721 | 0.00042369 | 0.00043017 | 0.00043664 | 0.00044312 | 0.00044959 | 0.00045607 | 0.00046254 | 0.00046902 | 0.0004755 | 0.00048197 | 0.00048845 | 0.00049492 | 0.0005014 | 0.00050788 | 0.00051435
| 10464701 | STN011 | STN | 17271745 | 17271741 | 1.1723 | 145.4678 | -36.5561 | 122 | 107 | 6.3% | 8.8% | 129.686 | 113.741 | 0.01 | 0.02 | -1594.5 | 145.631 | 1.482% | 130.906 | 116.416 | 0.01 | 0.02 | -1449 | 145.396 | 1.615% | 148.2% | 0.9675% | 0.9838% | 1% | 1.017% | 1.033% | 1.049% | 1.066% | 1.082% | 1.099% | 1.115% | 1.131% | 1.148% | 1.164% | 1.181% | 1.197% | 1.213% | 1.23% | 1.246% | 1.263% | 1.279% | 0.0003918 | 0.00039844 | 0.00040508 | 0.00041172 | 0.00041836 | 0.000425 | 0.00043163 | 0.00043827 | 0.00044491 | 0.00045155 | 0.00045819 | 0.00046483 | 0.00047147 | 0.00047811 | 0.00048475 | 0.00049139 | 0.00049803 | 0.00050467 | 0.00051131 | 0.00051794
| 10464822 | MNA034 | MNA | 17272260 | 17272264 | 0.25144 | 145.3201 | -36.4756 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10464823 | MNA034 | MNA | 17272264 | 183654742 | 0.6073 | 145.3196 | -36.4767 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10465191 | MNA021 | MNA | 17273761 | 17273765 | 0.12552 | 145.3242 | -36.4379 | 113 | 99.1 | 6.3% | 8.8% | 120.119 | 105.3433 | 0.01 | 0.02 | -1477.57 | 134.8947 | 1.482% | 121.249 | 107.8208 | 0.01 | 0.02 | -1342.82 | 134.6772 | 1.614% | 148.2% | 0.9674% | 0.9838% | 1% | 1.017% | 1.033% | 1.049% | 1.066% | 1.082% | 1.099% | 1.115% | 1.131% | 1.148% | 1.164% | 1.18% | 1.197% | 1.213% | 1.23% | 1.246% | 1.262% | 1.279% | 0.00039179 | 0.00039843 | 0.00040506 | 0.0004117 | 0.00041833 | 0.00042497 | 0.00043161 | 0.00043824 | 0.00044488 | 0.00045151 | 0.00045815 | 0.00046479 | 0.00047142 | 0.00047806 | 0.0004847 | 0.00049133 | 0.00049797 | 0.0005046 | 0.00051124 | 0.00051788
| 10465192 | MNA021 | MNA | 17273765 | 17273769 | 0.78102 | 145.3259 | -36.4379 | 114 | 99.9 | 6.3% | 8.8% | 121.182 | 106.1937 | 0.01 | 0.02 | -1498.83 | 136.1703 | 1.479% | 122.322 | 108.6912 | 0.01 | 0.02 | -1363.08 | 135.9528 | 1.611% | 147.9% | 0.9672% | 0.9835% | 0.9998% | 1.016% | 1.032% | 1.049% | 1.065% | 1.081% | 1.098% | 1.114% | 1.13% | 1.146% | 1.163% | 1.179% | 1.195% | 1.212% | 1.228% | 1.244% | 1.261% | 1.277% | 0.00039168 | 0.00039828 | 0.00040488 | 0.00041148 | 0.00041808 | 0.00042468 | 0.00043128 | 0.00043788 | 0.00044448 | 0.00045108 | 0.00045768 | 0.00046428 | 0.00047088 | 0.00047748 | 0.00048408 | 0.00049068 | 0.00049728 | 0.00050388 | 0.00051048 | 0.00051708
| 10465193 | MNA021 | MNA | 17273769 | 17280628 | 1.4459 | 145.3277 | -36.4379 | 114 | 99.9 | 6.3% | 8.8% | 121.182 | 106.1937 | 0.01 | 0.02 | -1498.83 | 136.1703 | 1.479% | 122.322 | 108.6912 | 0.01 | 0.02 | -1363.08 | 135.9528 | 1.611% | 147.9% | 0.9672% | 0.9835% | 0.9998% | 1.016% | 1.032% | 1.049% | 1.065% | 1.081% | 1.098% | 1.114% | 1.13% | 1.146% | 1.163% | 1.179% | 1.195% | 1.212% | 1.228% | 1.244% | 1.261% | 1.277% | 0.00039168 | 0.00039828 | 0.00040488 | 0.00041148 | 0.00041808 | 0.00042468 | 0.00043128 | 0.00043788 | 0.00044448 | 0.00045108 | 0.00045768 | 0.00046428 | 0.00047088 | 0.00047748 | 0.00048408 | 0.00049068 | 0.00049728 | 0.00050388 | 0.00051048 | 0.00051708
| 10466002 | MNA034 | MNA | 17277313 | 17535770 | 1.2375 | 145.2979 | -36.4995 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10466004 | MNA034 | MNA | 17277313 | 17277327 | 0.72889 | 145.2969 | -36.4992 | 115 | 101 | 6.3% | 8.8% | 122.245 | 107.363 | 0.01 | 0.02 | -1488.2 | 137.127 | 1.487% | 123.395 | 109.888 | 0.01 | 0.02 | -1350.7 | 136.902 | 1.622% | 148.7% | 0.9679% | 0.9845% | 1.001% | 1.018% | 1.034% | 1.051% | 1.067% | 1.084% | 1.1% | 1.117% | 1.134% | 1.15% | 1.167% | 1.183% | 1.2% | 1.216% | 1.233% | 1.249% | 1.266% | 1.283% | 0.000392 | 0.0003987 | 0.00040541 | 0.00041211 | 0.00041882 | 0.00042552 | 0.00043223 | 0.00043893 | 0.00044564 | 0.00045235 | 0.00045905 | 0.00046576 | 0.00047246 | 0.00047917 | 0.00048587 | 0.00049258 | 0.00049928 | 0.00050599 | 0.00051269 | 0.0005194
| 10466061 | MNA021 | MNA | 17277649 | 17277636 | 1.2351 | 145.292 | -36.454 | 113 | 99.4 | 6.3% | 8.8% | 120.119 | 105.6622 | 0.01 | 0.02 | -1445.68 | 134.5758 | 1.492% | 121.249 | 108.1472 | 0.01 | 0.02 | -1310.18 | 134.3508 | 1.63% | 149.2% | 0.9685% | 0.9853% | 1.002% | 1.019% | 1.036% | 1.052% | 1.069% | 1.086% | 1.102% | 1.119% | 1.136% | 1.153% | 1.169% | 1.186% | 1.203% | 1.22% | 1.236% | 1.253% | 1.27% | 1.287% | 0.00039223 | 0.00039901 | 0.00040579 | 0.00041258 | 0.00041936 | 0.00042614 | 0.00043292 | 0.00043971 | 0.00044649 | 0.00045327 | 0.00046005 | 0.00046684 | 0.00047362 | 0.0004804 | 0.00048718 | 0.00049397 | 0.00050075 | 0.00050753 | 0.00051431 | 0.0005211
| 10466179 | STN012 | STN | 17278165 | 17278195 | 2.5003 | 145.4166 | -36.4282 | 117 | 102 | 6.3% | 8.8% | 124.371 | 108.426 | 0.01 | 0.02 | -1594.5 | 140.316 | 1.462% | 125.541 | 110.976 | 0.01 | 0.02 | -1456.5 | 140.106 | 1.586% | 146.2% | 0.9654% | 0.9812% | 0.9969% | 1.013% | 1.028% | 1.044% | 1.06% | 1.075% | 1.091% | 1.107% | 1.123% | 1.138% | 1.154% | 1.17% | 1.186% | 1.201% | 1.217% | 1.233% | 1.248% | 1.264% | 0.00039098 | 0.00039735 | 0.00040372 | 0.00041008 | 0.00041645 | 0.00042282 | 0.00042919 | 0.00043555 | 0.00044192 | 0.00044829 | 0.00045465 | 0.00046102 | 0.00046739 | 0.00047376 | 0.00048012 | 0.00048649 | 0.00049286 | 0.00049922 | 0.00050559 | 0.00051196
| 10466185 | STN012 | STN | 17278195 | 17278199 | 2.3057 | 145.4166 | -36.4295 | 117 | 102 | 6.3% | 8.8% | 124.371 | 108.426 | 0.01 | 0.02 | -1594.5 | 140.316 | 1.462% | 125.541 | 110.976 | 0.01 | 0.02 | -1456.5 | 140.106 | 1.586% | 146.2% | 0.9654% | 0.9812% | 0.9969% | 1.013% | 1.028% | 1.044% | 1.06% | 1.075% | 1.091% | 1.107% | 1.123% | 1.138% | 1.154% | 1.17% | 1.186% | 1.201% | 1.217% | 1.233% | 1.248% | 1.264% | 0.00039098 | 0.00039735 | 0.00040372 | 0.00041008 | 0.00041645 | 0.00042282 | 0.00042919 | 0.00043555 | 0.00044192 | 0.00044829 | 0.00045465 | 0.00046102 | 0.00046739 | 0.00047376 | 0.00048012 | 0.00048649 | 0.00049286 | 0.00049922 | 0.00050559 | 0.00051196
| 10466201 | STN021 | STN | 17278266 | 17278271 | 2.553 | 145.429 | -36.4413 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10466203 | STN021 | STN | 17278271 | 17278275 | 0.28633 | 145.429 | -36.442 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10466206 | STN021 | STN | 17278293 | 17278289 | 0.12444 | 145.4259 | -36.4408 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10466208 | STN021 | STN | 17278302 | 17278297 | 0.43782 | 145.424 | -36.4409 | 117 | 102 | 6.3% | 8.8% | 124.371 | 108.426 | 0.01 | 0.02 | -1594.5 | 140.316 | 1.462% | 125.541 | 110.976 | 0.01 | 0.02 | -1456.5 | 140.106 | 1.586% | 146.2% | 0.9654% | 0.9812% | 0.9969% | 1.013% | 1.028% | 1.044% | 1.06% | 1.075% | 1.091% | 1.107% | 1.123% | 1.138% | 1.154% | 1.17% | 1.186% | 1.201% | 1.217% | 1.233% | 1.248% | 1.264% | 0.00039098 | 0.00039735 | 0.00040372 | 0.00041008 | 0.00041645 | 0.00042282 | 0.00042919 | 0.00043555 | 0.00044192 | 0.00044829 | 0.00045465 | 0.00046102 | 0.00046739 | 0.00047376 | 0.00048012 | 0.00048649 | 0.00049286 | 0.00049922 | 0.00050559 | 0.00051196
| 10466709 | MNA034 | MNA | 17280570 | 17280566 | 0.51497 | 145.3309 | -36.4424 | 114 | 99.9 | 6.3% | 8.8% | 121.182 | 106.1937 | 0.01 | 0.02 | -1498.83 | 136.1703 | 1.479% | 122.322 | 108.6912 | 0.01 | 0.02 | -1363.08 | 135.9528 | 1.611% | 147.9% | 0.9672% | 0.9835% | 0.9998% | 1.016% | 1.032% | 1.049% | 1.065% | 1.081% | 1.098% | 1.114% | 1.13% | 1.146% | 1.163% | 1.179% | 1.195% | 1.212% | 1.228% | 1.244% | 1.261% | 1.277% | 0.00039168 | 0.00039828 | 0.00040488 | 0.00041148 | 0.00041808 | 0.00042468 | 0.00043128 | 0.00043788 | 0.00044448 | 0.00045108 | 0.00045768 | 0.00046428 | 0.00047088 | 0.00047748 | 0.00048408 | 0.00049068 | 0.00049728 | 0.00050388 | 0.00051048 | 0.00051708
| 10466711 | MNA034 | MNA | 17280574 | 17280570 | 0.59903 | 145.3312 | -36.4413 | 114 | 99.9 | 6.3% | 8.8% | 121.182 | 106.1937 | 0.01 | 0.02 | -1498.83 | 136.1703 | 1.479% | 122.322 | 108.6912 | 0.01 | 0.02 | -1363.08 | 135.9528 | 1.611% | 147.9% | 0.9672% | 0.9835% | 0.9998% | 1.016% | 1.032% | 1.049% | 1.065% | 1.081% | 1.098% | 1.114% | 1.13% | 1.146% | 1.163% | 1.179% | 1.195% | 1.212% | 1.228% | 1.244% | 1.261% | 1.277% | 0.00039168 | 0.00039828 | 0.00040488 | 0.00041148 | 0.00041808 | 0.00042468 | 0.00043128 | 0.00043788 | 0.00044448 | 0.00045108 | 0.00045768 | 0.00046428 | 0.00047088 | 0.00047748 | 0.00048408 | 0.00049068 | 0.00049728 | 0.00050388 | 0.00051048 | 0.00051708
| 10466713 | MNA034 | MNA | 17280583 | 17280578 | 0.21977 | 145.3332 | -36.4397 | 114 | 99.9 | 6.3% | 8.8% | 121.182 | 106.1937 | 0.01 | 0.02 | -1498.83 | 136.1703 | 1.479% | 122.322 | 108.6912 | 0.01 | 0.02 | -1363.08 | 135.9528 | 1.611% | 147.9% | 0.9672% | 0.9835% | 0.9998% | 1.016% | 1.032% | 1.049% | 1.065% | 1.081% | 1.098% | 1.114% | 1.13% | 1.146% | 1.163% | 1.179% | 1.195% | 1.212% | 1.228% | 1.244% | 1.261% | 1.277% | 0.00039168 | 0.00039828 | 0.00040488 | 0.00041148 | 0.00041808 | 0.00042468 | 0.00043128 | 0.00043788 | 0.00044448 | 0.00045108 | 0.00045768 | 0.00046428 | 0.00047088 | 0.00047748 | 0.00048408 | 0.00049068 | 0.00049728 | 0.00050388 | 0.00051048 | 0.00051708
| 10466718 | MNA034 | MNA | 17280597 | 17280633 | 0.9073 | 145.3312 | -36.4379 | 114 | 99.9 | 6.3% | 8.8% | 121.182 | 106.1937 | 0.01 | 0.02 | -1498.83 | 136.1703 | 1.479% | 122.322 | 108.6912 | 0.01 | 0.02 | -1363.08 | 135.9528 | 1.611% | 147.9% | 0.9672% | 0.9835% | 0.9998% | 1.016% | 1.032% | 1.049% | 1.065% | 1.081% | 1.098% | 1.114% | 1.13% | 1.146% | 1.163% | 1.179% | 1.195% | 1.212% | 1.228% | 1.244% | 1.261% | 1.277% | 0.00039168 | 0.00039828 | 0.00040488 | 0.00041148 | 0.00041808 | 0.00042468 | 0.00043128 | 0.00043788 | 0.00044448 | 0.00045108 | 0.00045768 | 0.00046428 | 0.00047088 | 0.00047748 | 0.00048408 | 0.00049068 | 0.00049728 | 0.00050388 | 0.00051048 | 0.00051708
| 10466720 | MNA034 | MNA | 17280633 | 17280628 | 0.95644 | 145.3295 | -36.4379 | 114 | 99.9 | 6.3% | 8.8% | 121.182 | 106.1937 | 0.01 | 0.02 | -1498.83 | 136.1703 | 1.479% | 122.322 | 108.6912 | 0.01 | 0.02 | -1363.08 | 135.9528 | 1.611% | 147.9% | 0.9672% | 0.9835% | 0.9998% | 1.016% | 1.032% | 1.049% | 1.065% | 1.081% | 1.098% | 1.114% | 1.13% | 1.146% | 1.163% | 1.179% | 1.195% | 1.212% | 1.228% | 1.244% | 1.261% | 1.277% | 0.00039168 | 0.00039828 | 0.00040488 | 0.00041148 | 0.00041808 | 0.00042468 | 0.00043128 | 0.00043788 | 0.00044448 | 0.00045108 | 0.00045768 | 0.00046428 | 0.00047088 | 0.00047748 | 0.00048408 | 0.00049068 | 0.00049728 | 0.00050388 | 0.00051048 | 0.00051708
| 10467873 | CRO021 | CRO | 17286134 | 17286115 | 2.2428 | 144.3512 | -38.1016 | 106 | 93.7 | 5.4% | 7.3% | 111.724 | 98.7598 | 0.01 | 0.02 | -1296.42 | 124.6882 | 1.442% | 113.738 | 100.5401 | 0.01 | 0.02 | -1319.79 | 126.9359 | 1.586% | 144.2% | 0.9633% | 0.9783% | 0.9934% | 1.008% | 1.023% | 1.038% | 1.053% | 1.068% | 1.083% | 1.098% | 1.113% | 1.129% | 1.144% | 1.159% | 1.174% | 1.189% | 1.204% | 1.219% | 1.234% | 1.249% | 0.00039013 | 0.00039621 | 0.00040229 | 0.00040837 | 0.00041445 | 0.00042053 | 0.00042661 | 0.00043269 | 0.00043878 | 0.00044486 | 0.00045094 | 0.00045702 | 0.0004631 | 0.00046918 | 0.00047526 | 0.00048134 | 0.00048743 | 0.00049351 | 0.00049959 | 0.00050567
| 10470103 | WIN011 | WIN | 17296249 | 17296245 | 0.55681 | 143.9806 | -38.2816 | 116 | 102 | 5.4% | 7.3% | 122.264 | 107.508 | 0.01 | 0.02 | -1475.6 | 137.02 | 1.425% | 124.468 | 109.446 | 0.01 | 0.02 | -1502.2 | 139.49 | 1.564% | 142.5% | 0.9616% | 0.976% | 0.9905% | 1.005% | 1.019% | 1.034% | 1.048% | 1.063% | 1.077% | 1.092% | 1.106% | 1.12% | 1.135% | 1.149% | 1.164% | 1.178% | 1.193% | 1.207% | 1.221% | 1.236% | 0.00038942 | 0.00039527 | 0.00040112 | 0.00040696 | 0.00041281 | 0.00041866 | 0.0004245 | 0.00043035 | 0.0004362 | 0.00044204 | 0.00044789 | 0.00045374 | 0.00045958 | 0.00046543 | 0.00047128 | 0.00047713 | 0.00048297 | 0.00048882 | 0.00049467 | 0.00050051
| 10470105 | WIN011 | WIN | 17296257 | 17296253 | 2.1862 | 143.9794 | -38.2794 | 116 | 102 | 5.4% | 7.3% | 122.264 | 107.508 | 0.01 | 0.02 | -1475.6 | 137.02 | 1.425% | 124.468 | 109.446 | 0.01 | 0.02 | -1502.2 | 139.49 | 1.564% | 142.5% | 0.9616% | 0.976% | 0.9905% | 1.005% | 1.019% | 1.034% | 1.048% | 1.063% | 1.077% | 1.092% | 1.106% | 1.12% | 1.135% | 1.149% | 1.164% | 1.178% | 1.193% | 1.207% | 1.221% | 1.236% | 0.00038942 | 0.00039527 | 0.00040112 | 0.00040696 | 0.00041281 | 0.00041866 | 0.0004245 | 0.00043035 | 0.0004362 | 0.00044204 | 0.00044789 | 0.00045374 | 0.00045958 | 0.00046543 | 0.00047128 | 0.00047713 | 0.00048297 | 0.00048882 | 0.00049467 | 0.00050051
| 10470196 | WIN011 | WIN | 17296910 | 17296920 | 0.15708 | 143.9841 | -38.2608 | 112 | 98.4 | 5.4% | 7.3% | 118.048 | 103.7136 | 0.01 | 0.02 | -1433.44 | 132.3824 | 1.422% | 120.176 | 105.5832 | 0.01 | 0.02 | -1459.28 | 134.7688 | 1.56% | 142.2% | 0.9613% | 0.9757% | 0.99% | 1.004% | 1.019% | 1.033% | 1.047% | 1.062% | 1.076% | 1.09% | 1.105% | 1.119% | 1.134% | 1.148% | 1.162% | 1.177% | 1.191% | 1.205% | 1.22% | 1.234% | 0.00038932 | 0.00039513 | 0.00040094 | 0.00040675 | 0.00041256 | 0.00041837 | 0.00042418 | 0.00042999 | 0.00043581 | 0.00044162 | 0.00044743 | 0.00045324 | 0.00045905 | 0.00046486 | 0.00047067 | 0.00047648 | 0.0004823 | 0.00048811 | 0.00049392 | 0.00049973
| 10470961 | GHP011 | GHP | 17300649 | 17300644 | 1.8709 | 144.1279 | -37.8955 | 126 | 111 | 5.4% | 7.3% | 132.804 | 116.994 | 0.01 | 0.02 | -1581 | 148.614 | 1.43% | 135.198 | 119.103 | 0.01 | 0.02 | -1609.5 | 151.293 | 1.571% | 143% | 0.9622% | 0.9768% | 0.9915% | 1.006% | 1.021% | 1.035% | 1.05% | 1.065% | 1.079% | 1.094% | 1.109% | 1.123% | 1.138% | 1.152% | 1.167% | 1.182% | 1.196% | 1.211% | 1.226% | 1.24% | 0.00038966 | 0.00039559 | 0.00040152 | 0.00040745 | 0.00041337 | 0.0004193 | 0.00042523 | 0.00043116 | 0.00043708 | 0.00044301 | 0.00044894 | 0.00045487 | 0.00046079 | 0.00046672 | 0.00047265 | 0.00047858 | 0.0004845 | 0.00049043 | 0.00049636 | 0.00050229
| 10474297 | SHL004 | SHL | 17314988 | 154846531 | 0.49664 | 143.4781 | -35.2649 | 106 | 93.9 | 6.3% | 8.8% | 112.678 | 99.8157 | 0.01 | 0.02 | -1286.23 | 125.5403 | 1.519% | 113.738 | 102.1632 | 0.01 | 0.02 | -1157.48 | 125.3128 | 1.669% | 151.9% | 0.9712% | 0.9889% | 1.007% | 1.024% | 1.042% | 1.06% | 1.077% | 1.095% | 1.113% | 1.13% | 1.148% | 1.165% | 1.183% | 1.201% | 1.218% | 1.236% | 1.254% | 1.271% | 1.289% | 1.307% | 0.00039333 | 0.00040049 | 0.00040764 | 0.00041479 | 0.00042194 | 0.00042909 | 0.00043624 | 0.00044339 | 0.00045054 | 0.00045769 | 0.00046485 | 0.000472 | 0.00047915 | 0.0004863 | 0.00049345 | 0.0005006 | 0.00050775 | 0.0005149 | 0.00052205 | 0.0005292
| 10475546 | NKA005 | RCTS | 17320648 | 17673142 | 0.63198 | 145.5791 | -35.8893 | 116 | 103 | 6.3% | 8.8% | 123.308 | 109.489 | 0.01 | 0.02 | -1381.9 | 137.127 | 1.529% | 124.468 | 112.064 | 0.01 | 0.02 | -1240.4 | 136.872 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039373 | 0.00040102 | 0.0004083 | 0.00041558 | 0.00042287 | 0.00043015 | 0.00043744 | 0.00044472 | 0.000452 | 0.00045929 | 0.00046657 | 0.00047386 | 0.00048114 | 0.00048842 | 0.00049571 | 0.00050299 | 0.00051028 | 0.00051756 | 0.00052484 | 0.00053213
| 10475590 | CME015 | CME | 203819282 | 17320862 | 0.1131 | 145.6779 | -35.9668 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10475691 | CME014 | CME | 17321284 | 17321289 | 0.4406 | 145.7215 | -35.9724 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10475743 | CME014 | CME | 17321504 | 17321951 | 0.64862 | 145.714 | -35.9713 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10475844 | CME014 | CME | 17321951 | 17321956 | 0.34044 | 145.714 | -35.9726 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10478222 | STL007 | STL | 17332949 | 17332945 | 0.37488 | 142.9842 | -37.0155 | 110 | 97.2 | 6.3% | 8.8% | 116.93 | 103.3236 | 0.01 | 0.02 | -1360.64 | 130.5364 | 1.509% | 118.03 | 105.7536 | 0.01 | 0.02 | -1227.64 | 130.3064 | 1.654% | 150.9% | 0.9702% | 0.9876% | 1.005% | 1.022% | 1.04% | 1.057% | 1.074% | 1.091% | 1.109% | 1.126% | 1.143% | 1.161% | 1.178% | 1.195% | 1.213% | 1.23% | 1.247% | 1.265% | 1.282% | 1.299% | 0.00039293 | 0.00039994 | 0.00040696 | 0.00041397 | 0.00042099 | 0.000428 | 0.00043502 | 0.00044203 | 0.00044905 | 0.00045606 | 0.00046308 | 0.00047009 | 0.00047711 | 0.00048412 | 0.00049114 | 0.00049815 | 0.00050517 | 0.00051218 | 0.0005192 | 0.00052621
| 10478223 | STL007 | STL | 17332977 | 17332953 | 0.74439 | 142.9779 | -37.0143 | 110 | 97.2 | 6.3% | 8.8% | 116.93 | 103.3236 | 0.01 | 0.02 | -1360.64 | 130.5364 | 1.509% | 118.03 | 105.7536 | 0.01 | 0.02 | -1227.64 | 130.3064 | 1.654% | 150.9% | 0.9702% | 0.9876% | 1.005% | 1.022% | 1.04% | 1.057% | 1.074% | 1.091% | 1.109% | 1.126% | 1.143% | 1.161% | 1.178% | 1.195% | 1.213% | 1.23% | 1.247% | 1.265% | 1.282% | 1.299% | 0.00039293 | 0.00039994 | 0.00040696 | 0.00041397 | 0.00042099 | 0.000428 | 0.00043502 | 0.00044203 | 0.00044905 | 0.00045606 | 0.00046308 | 0.00047009 | 0.00047711 | 0.00048412 | 0.00049114 | 0.00049815 | 0.00050517 | 0.00051218 | 0.0005192 | 0.00052621
| 10478419 | STL007 | STL | 17333828 | 17333836 | 0.25048 | 143.1293 | -37.0047 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10478541 | STL007 | STL | 17334378 | 17334374 | 1.8093 | 143.1959 | -36.9636 | 120 | 106 | 6.3% | 8.8% | 127.56 | 112.678 | 0.01 | 0.02 | -1488.2 | 142.442 | 1.508% | 128.76 | 115.328 | 0.01 | 0.02 | -1343.2 | 142.192 | 1.652% | 150.8% | 0.9701% | 0.9874% | 1.005% | 1.022% | 1.039% | 1.056% | 1.074% | 1.091% | 1.108% | 1.126% | 1.143% | 1.16% | 1.177% | 1.195% | 1.212% | 1.229% | 1.247% | 1.264% | 1.281% | 1.298% | 0.00039287 | 0.00039987 | 0.00040687 | 0.00041386 | 0.00042086 | 0.00042786 | 0.00043485 | 0.00044185 | 0.00044885 | 0.00045584 | 0.00046284 | 0.00046984 | 0.00047683 | 0.00048383 | 0.00049083 | 0.00049782 | 0.00050482 | 0.00051182 | 0.00051882 | 0.00052581
| 10478730 | MRO005 | MRO | 17335167 | 17335158 | 0.20127 | 143.3309 | -36.9862 | 124 | 110 | 6.3% | 8.8% | 131.812 | 116.93 | 0.01 | 0.02 | -1488.2 | 146.694 | 1.525% | 133.052 | 119.68 | 0.01 | 0.02 | -1337.2 | 146.424 | 1.677% | 152.5% | 0.9718% | 0.9897% | 1.008% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.115% | 1.133% | 1.15% | 1.168% | 1.186% | 1.204% | 1.222% | 1.24% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039357 | 0.0004008 | 0.00040803 | 0.00041526 | 0.00042249 | 0.00042972 | 0.00043695 | 0.00044418 | 0.00045141 | 0.00045864 | 0.00046587 | 0.0004731 | 0.00048033 | 0.00048756 | 0.00049479 | 0.00050202 | 0.00050925 | 0.00051648 | 0.00052371 | 0.00053094
| 10478733 | MRO005 | MRO | 17335198 | 17335189 | 0.92781 | 143.3417 | -36.9859 | 124 | 110 | 6.3% | 8.8% | 131.812 | 116.93 | 0.01 | 0.02 | -1488.2 | 146.694 | 1.525% | 133.052 | 119.68 | 0.01 | 0.02 | -1337.2 | 146.424 | 1.677% | 152.5% | 0.9718% | 0.9897% | 1.008% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.115% | 1.133% | 1.15% | 1.168% | 1.186% | 1.204% | 1.222% | 1.24% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039357 | 0.0004008 | 0.00040803 | 0.00041526 | 0.00042249 | 0.00042972 | 0.00043695 | 0.00044418 | 0.00045141 | 0.00045864 | 0.00046587 | 0.0004731 | 0.00048033 | 0.00048756 | 0.00049479 | 0.00050202 | 0.00050925 | 0.00051648 | 0.00052371 | 0.00053094
| 10478736 | MRO005 | MRO | 17335198 | 17335212 | 2.0386 | 143.3425 | -36.9856 | 124 | 110 | 6.3% | 8.8% | 131.812 | 116.93 | 0.01 | 0.02 | -1488.2 | 146.694 | 1.525% | 133.052 | 119.68 | 0.01 | 0.02 | -1337.2 | 146.424 | 1.677% | 152.5% | 0.9718% | 0.9897% | 1.008% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.115% | 1.133% | 1.15% | 1.168% | 1.186% | 1.204% | 1.222% | 1.24% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039357 | 0.0004008 | 0.00040803 | 0.00041526 | 0.00042249 | 0.00042972 | 0.00043695 | 0.00044418 | 0.00045141 | 0.00045864 | 0.00046587 | 0.0004731 | 0.00048033 | 0.00048756 | 0.00049479 | 0.00050202 | 0.00050925 | 0.00051648 | 0.00052371 | 0.00053094
| 10478833 | MRO008 | MRO | 17335640 | 17335657 | 0.94718 | 143.4707 | -36.9962 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10478837 | MRO008 | MRO | 17335657 | 17335649 | 0.13233 | 143.4701 | -36.9936 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10478838 | MRO008 | MRO | 17335649 | 17335653 | 2.1009 | 143.4695 | -36.9909 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10478853 | MRO008 | MRO | 17335733 | 17335720 | 0.84799 | 143.4674 | -36.961 | 113 | 101 | 6.3% | 8.8% | 120.119 | 107.363 | 0.01 | 0.02 | -1275.6 | 132.875 | 1.558% | 121.249 | 109.888 | 0.01 | 0.02 | -1136.1 | 132.61 | 1.726% | 155.8% | 0.9752% | 0.9942% | 1.013% | 1.032% | 1.051% | 1.07% | 1.089% | 1.108% | 1.127% | 1.146% | 1.165% | 1.184% | 1.203% | 1.222% | 1.241% | 1.26% | 1.279% | 1.298% | 1.317% | 1.336% | 0.00039494 | 0.00040263 | 0.00041032 | 0.000418 | 0.00042569 | 0.00043338 | 0.00044106 | 0.00044875 | 0.00045644 | 0.00046412 | 0.00047181 | 0.0004795 | 0.00048718 | 0.00049487 | 0.00050256 | 0.00051024 | 0.00051793 | 0.00052562 | 0.0005333 | 0.00054099
| 10478856 | MRO008 | MRO | 17335737 | 17335733 | 2.3628 | 143.4672 | -36.9636 | 113 | 101 | 6.3% | 8.8% | 120.119 | 107.363 | 0.01 | 0.02 | -1275.6 | 132.875 | 1.558% | 121.249 | 109.888 | 0.01 | 0.02 | -1136.1 | 132.61 | 1.726% | 155.8% | 0.9752% | 0.9942% | 1.013% | 1.032% | 1.051% | 1.07% | 1.089% | 1.108% | 1.127% | 1.146% | 1.165% | 1.184% | 1.203% | 1.222% | 1.241% | 1.26% | 1.279% | 1.298% | 1.317% | 1.336% | 0.00039494 | 0.00040263 | 0.00041032 | 0.000418 | 0.00042569 | 0.00043338 | 0.00044106 | 0.00044875 | 0.00045644 | 0.00046412 | 0.00047181 | 0.0004795 | 0.00048718 | 0.00049487 | 0.00050256 | 0.00051024 | 0.00051793 | 0.00052562 | 0.0005333 | 0.00054099
| 10478857 | MRO008 | MRO | 17335737 | 17335742 | 2.253 | 143.4687 | -36.9649 | 113 | 101 | 6.3% | 8.8% | 120.119 | 107.363 | 0.01 | 0.02 | -1275.6 | 132.875 | 1.558% | 121.249 | 109.888 | 0.01 | 0.02 | -1136.1 | 132.61 | 1.726% | 155.8% | 0.9752% | 0.9942% | 1.013% | 1.032% | 1.051% | 1.07% | 1.089% | 1.108% | 1.127% | 1.146% | 1.165% | 1.184% | 1.203% | 1.222% | 1.241% | 1.26% | 1.279% | 1.298% | 1.317% | 1.336% | 0.00039494 | 0.00040263 | 0.00041032 | 0.000418 | 0.00042569 | 0.00043338 | 0.00044106 | 0.00044875 | 0.00045644 | 0.00046412 | 0.00047181 | 0.0004795 | 0.00048718 | 0.00049487 | 0.00050256 | 0.00051024 | 0.00051793 | 0.00052562 | 0.0005333 | 0.00054099
| 10479404 | GHP011 | GHP | 17337942 | 17745357 | 0.77473 | 144.1547 | -37.9453 | 114 | 100 | 5.4% | 7.3% | 120.156 | 105.4 | 0.01 | 0.02 | -1475.6 | 134.912 | 1.417% | 122.322 | 107.3 | 0.01 | 0.02 | -1502.2 | 137.344 | 1.554% | 141.7% | 0.9608% | 0.975% | 0.9892% | 1.003% | 1.018% | 1.032% | 1.046% | 1.06% | 1.074% | 1.089% | 1.103% | 1.117% | 1.131% | 1.145% | 1.159% | 1.174% | 1.188% | 1.202% | 1.216% | 1.23% | 0.00038912 | 0.00039487 | 0.00040061 | 0.00040636 | 0.0004121 | 0.00041785 | 0.0004236 | 0.00042934 | 0.00043509 | 0.00044083 | 0.00044658 | 0.00045233 | 0.00045807 | 0.00046382 | 0.00046956 | 0.00047531 | 0.00048106 | 0.0004868 | 0.00049255 | 0.0004983
| 10480544 | CME021 | CME | 17342954 | 17342949 | 0.7764 | 145.6644 | -35.9408 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10480683 | NKA005 | RCTS | 193655456 | 17343616 | 0.60199 | 145.5754 | -35.9007 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10480701 | NKA005 | RCTS | 17343693 | 17343697 | 1.6717 | 145.574 | -35.8903 | 116 | 103 | 6.3% | 8.8% | 123.308 | 109.489 | 0.01 | 0.02 | -1381.9 | 137.127 | 1.529% | 124.468 | 112.064 | 0.01 | 0.02 | -1240.4 | 136.872 | 1.683% | 152.9% | 0.9722% | 0.9902% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.242% | 1.26% | 1.278% | 1.296% | 1.314% | 0.00039373 | 0.00040102 | 0.0004083 | 0.00041558 | 0.00042287 | 0.00043015 | 0.00043744 | 0.00044472 | 0.000452 | 0.00045929 | 0.00046657 | 0.00047386 | 0.00048114 | 0.00048842 | 0.00049571 | 0.00050299 | 0.00051028 | 0.00051756 | 0.00052484 | 0.00053213
| 10481505 | WND014 | WND | 17347694 | 17347699 | 0.70726 | 144.495 | -37.2789 | 136 | 121 | 6.3% | 8.8% | 144.568 | 128.623 | 0.01 | 0.02 | -1594.5 | 160.513 | 1.537% | 145.928 | 131.648 | 0.01 | 0.02 | -1428 | 160.208 | 1.695% | 153.7% | 0.9731% | 0.9914% | 1.01% | 1.028% | 1.046% | 1.064% | 1.083% | 1.101% | 1.119% | 1.138% | 1.156% | 1.174% | 1.192% | 1.211% | 1.229% | 1.247% | 1.266% | 1.284% | 1.302% | 1.32% | 0.00039408 | 0.00040149 | 0.00040889 | 0.00041629 | 0.00042369 | 0.00043109 | 0.00043849 | 0.00044589 | 0.00045329 | 0.00046069 | 0.0004681 | 0.0004755 | 0.0004829 | 0.0004903 | 0.0004977 | 0.0005051 | 0.0005125 | 0.0005199 | 0.0005273 | 0.00053471
| 10483642 | BAS022 | BAS | 17359780 | 17359776 | 0.30037 | 143.8842 | -37.7249 | 122 | 108 | 5.4% | 7.3% | 128.588 | 113.832 | 0.01 | 0.02 | -1475.6 | 143.344 | 1.446% | 130.906 | 115.884 | 0.01 | 0.02 | -1502.2 | 145.928 | 1.593% | 144.6% | 0.9638% | 0.979% | 0.9942% | 1.009% | 1.025% | 1.04% | 1.055% | 1.07% | 1.085% | 1.1% | 1.116% | 1.131% | 1.146% | 1.161% | 1.176% | 1.192% | 1.207% | 1.222% | 1.237% | 1.252% | 0.00039033 | 0.00039648 | 0.00040263 | 0.00040878 | 0.00041493 | 0.00042108 | 0.00042723 | 0.00043337 | 0.00043952 | 0.00044567 | 0.00045182 | 0.00045797 | 0.00046412 | 0.00047027 | 0.00047642 | 0.00048257 | 0.00048872 | 0.00049487 | 0.00050102 | 0.00050717
| 10484201 | CMN004 | CMN | 17362602 | 17362606 | 0.32297 | 144.1432 | -37.0493 | 118 | 105 | 6.3% | 8.8% | 125.434 | 111.615 | 0.01 | 0.02 | -1381.9 | 139.253 | 1.538% | 126.614 | 114.24 | 0.01 | 0.02 | -1237.4 | 138.988 | 1.696% | 153.8% | 0.9732% | 0.9915% | 1.01% | 1.028% | 1.046% | 1.065% | 1.083% | 1.101% | 1.12% | 1.138% | 1.156% | 1.174% | 1.193% | 1.211% | 1.229% | 1.248% | 1.266% | 1.284% | 1.302% | 1.321% | 0.00039411 | 0.00040152 | 0.00040893 | 0.00041634 | 0.00042375 | 0.00043116 | 0.00043857 | 0.00044598 | 0.00045339 | 0.0004608 | 0.0004682 | 0.00047561 | 0.00048302 | 0.00049043 | 0.00049784 | 0.00050525 | 0.00051266 | 0.00052007 | 0.00052748 | 0.00053489
| 10485104 | NKA002 | RCTS | 17366487 | 66222230 | 0.3776 | 145.0573 | -35.9596 | 111 | 98.5 | 6.3% | 8.8% | 117.993 | 104.7055 | 0.01 | 0.02 | -1328.75 | 131.2805 | 1.526% | 119.103 | 107.168 | 0.01 | 0.02 | -1193.5 | 131.038 | 1.679% | 152.6% | 0.972% | 0.9899% | 1.008% | 1.026% | 1.044% | 1.061% | 1.079% | 1.097% | 1.115% | 1.133% | 1.151% | 1.169% | 1.187% | 1.205% | 1.223% | 1.24% | 1.258% | 1.276% | 1.294% | 1.312% | 0.00039363 | 0.00040088 | 0.00040813 | 0.00041537 | 0.00042262 | 0.00042987 | 0.00043712 | 0.00044437 | 0.00045162 | 0.00045887 | 0.00046611 | 0.00047336 | 0.00048061 | 0.00048786 | 0.00049511 | 0.00050236 | 0.00050961 | 0.00051686 | 0.0005241 | 0.00053135
| 10485105 | NKA002 | RCTS | 66222230 | 17366495 | 0.135 | 145.0573 | -35.9574 | 111 | 98.5 | 6.3% | 8.8% | 117.993 | 104.7055 | 0.01 | 0.02 | -1328.75 | 131.2805 | 1.526% | 119.103 | 107.168 | 0.01 | 0.02 | -1193.5 | 131.038 | 1.679% | 152.6% | 0.972% | 0.9899% | 1.008% | 1.026% | 1.044% | 1.061% | 1.079% | 1.097% | 1.115% | 1.133% | 1.151% | 1.169% | 1.187% | 1.205% | 1.223% | 1.24% | 1.258% | 1.276% | 1.294% | 1.312% | 0.00039363 | 0.00040088 | 0.00040813 | 0.00041537 | 0.00042262 | 0.00042987 | 0.00043712 | 0.00044437 | 0.00045162 | 0.00045887 | 0.00046611 | 0.00047336 | 0.00048061 | 0.00048786 | 0.00049511 | 0.00050236 | 0.00050961 | 0.00051686 | 0.0005241 | 0.00053135
| 10485108 | NKA002 | RCTS | 17366503 | 17366507 | 0.57783 | 145.0572 | -35.9508 | 111 | 98.5 | 6.3% | 8.8% | 117.993 | 104.7055 | 0.01 | 0.02 | -1328.75 | 131.2805 | 1.526% | 119.103 | 107.168 | 0.01 | 0.02 | -1193.5 | 131.038 | 1.679% | 152.6% | 0.972% | 0.9899% | 1.008% | 1.026% | 1.044% | 1.061% | 1.079% | 1.097% | 1.115% | 1.133% | 1.151% | 1.169% | 1.187% | 1.205% | 1.223% | 1.24% | 1.258% | 1.276% | 1.294% | 1.312% | 0.00039363 | 0.00040088 | 0.00040813 | 0.00041537 | 0.00042262 | 0.00042987 | 0.00043712 | 0.00044437 | 0.00045162 | 0.00045887 | 0.00046611 | 0.00047336 | 0.00048061 | 0.00048786 | 0.00049511 | 0.00050236 | 0.00050961 | 0.00051686 | 0.0005241 | 0.00053135
| 10485125 | NKA002 | RCTS | 17366570 | 17366574 | 0.70985 | 145.0314 | -35.9605 | 110 | 97.6 | 6.3% | 8.8% | 116.93 | 103.7488 | 0.01 | 0.02 | -1318.12 | 130.1112 | 1.526% | 118.03 | 106.1888 | 0.01 | 0.02 | -1184.12 | 129.8712 | 1.678% | 152.6% | 0.9719% | 0.9898% | 1.008% | 1.026% | 1.043% | 1.061% | 1.079% | 1.097% | 1.115% | 1.133% | 1.151% | 1.169% | 1.186% | 1.204% | 1.222% | 1.24% | 1.258% | 1.276% | 1.294% | 1.312% | 0.00039361 | 0.00040085 | 0.00040809 | 0.00041533 | 0.00042257 | 0.00042981 | 0.00043705 | 0.0004443 | 0.00045154 | 0.00045878 | 0.00046602 | 0.00047326 | 0.0004805 | 0.00048774 | 0.00049498 | 0.00050223 | 0.00050947 | 0.00051671 | 0.00052395 | 0.00053119
| 10485132 | NKA002 | RCTS | 17366596 | 17366627 | 0.62233 | 145.0786 | -35.9686 | 112 | 99.3 | 6.3% | 8.8% | 119.056 | 105.5559 | 0.01 | 0.02 | -1350.01 | 132.5561 | 1.523% | 120.176 | 108.0384 | 0.01 | 0.02 | -1213.76 | 132.3136 | 1.674% | 152.3% | 0.9716% | 0.9894% | 1.007% | 1.025% | 1.043% | 1.06% | 1.078% | 1.096% | 1.114% | 1.132% | 1.149% | 1.167% | 1.185% | 1.203% | 1.22% | 1.238% | 1.256% | 1.274% | 1.292% | 1.309% | 0.00039348 | 0.00040068 | 0.00040788 | 0.00041507 | 0.00042227 | 0.00042947 | 0.00043667 | 0.00044387 | 0.00045107 | 0.00045827 | 0.00046547 | 0.00047267 | 0.00047986 | 0.00048706 | 0.00049426 | 0.00050146 | 0.00050866 | 0.00051586 | 0.00052306 | 0.00053026
| 10488457 | MRO007 | MRO | 17382273 | 17383091 | 2.1978 | 143.8284 | -37.0528 | 107 | 95.1 | 6.3% | 8.8% | 113.741 | 101.0913 | 0.01 | 0.02 | -1264.97 | 126.3907 | 1.533% | 114.811 | 103.4688 | 0.01 | 0.02 | -1134.22 | 126.1532 | 1.689% | 153.3% | 0.9726% | 0.9908% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.19% | 1.208% | 1.226% | 1.245% | 1.263% | 1.281% | 1.299% | 1.317% | 0.0003939 | 0.00040124 | 0.00040858 | 0.00041592 | 0.00042326 | 0.0004306 | 0.00043794 | 0.00044528 | 0.00045262 | 0.00045996 | 0.0004673 | 0.00047464 | 0.00048198 | 0.00048932 | 0.00049666 | 0.000504 | 0.00051134 | 0.00051868 | 0.00052602 | 0.00053336
| 10488513 | BETSMRO | BETS | 17382500 | 17382496 | 0.10507 | 143.8147 | -37.0368 | 106 | 94.3 | 6.3% | 8.8% | 112.678 | 100.2409 | 0.01 | 0.02 | -1243.71 | 125.1151 | 1.537% | 113.738 | 102.5984 | 0.01 | 0.02 | -1113.96 | 124.8776 | 1.695% | 153.7% | 0.9731% | 0.9913% | 1.01% | 1.028% | 1.046% | 1.064% | 1.083% | 1.101% | 1.119% | 1.137% | 1.156% | 1.174% | 1.192% | 1.21% | 1.229% | 1.247% | 1.265% | 1.284% | 1.302% | 1.32% | 0.00039407 | 0.00040146 | 0.00040886 | 0.00041625 | 0.00042365 | 0.00043105 | 0.00043844 | 0.00044584 | 0.00045323 | 0.00046063 | 0.00046802 | 0.00047542 | 0.00048281 | 0.00049021 | 0.00049761 | 0.000505 | 0.0005124 | 0.00051979 | 0.00052719 | 0.00053458
| 10488844 | BET006 | BETS | 17383950 | 17383946 | 0.31663 | 143.8196 | -36.7298 | 103 | 92.9 | 6.3% | 8.8% | 109.489 | 98.7527 | 0.01 | 0.02 | -1073.63 | 120.2253 | 1.604% | 110.519 | 101.0752 | 0.01 | 0.02 | -944.38 | 119.9628 | 1.796% | 160.4% | 0.9799% | 1% | 1.021% | 1.042% | 1.062% | 1.083% | 1.103% | 1.124% | 1.144% | 1.165% | 1.185% | 1.206% | 1.227% | 1.247% | 1.268% | 1.288% | 1.309% | 1.329% | 1.35% | 1.37% | 0.00039686 | 0.00040518 | 0.0004135 | 0.00042183 | 0.00043015 | 0.00043848 | 0.0004468 | 0.00045513 | 0.00046345 | 0.00047178 | 0.0004801 | 0.00048843 | 0.00049675 | 0.00050508 | 0.0005134 | 0.00052172 | 0.00053005 | 0.00053837 | 0.0005467 | 0.00055502
| 10489049 | MRO007 | MRO | 144835632 | 17385104 | 1.2527 | 143.9061 | -36.7712 | 102 | 92.7 | 6.3% | 8.8% | 108.426 | 98.5401 | 0.01 | 0.02 | -988.59 | 118.3119 | 1.65% | 109.446 | 100.8576 | 0.01 | 0.02 | -858.84 | 118.0344 | 1.867% | 165% | 0.9846% | 1.007% | 1.029% | 1.051% | 1.073% | 1.095% | 1.117% | 1.139% | 1.161% | 1.184% | 1.206% | 1.228% | 1.25% | 1.272% | 1.294% | 1.316% | 1.338% | 1.36% | 1.383% | 1.405% | 0.00039874 | 0.00040769 | 0.00041665 | 0.0004256 | 0.00043455 | 0.00044351 | 0.00045246 | 0.00046141 | 0.00047036 | 0.00047932 | 0.00048827 | 0.00049722 | 0.00050618 | 0.00051513 | 0.00052408 | 0.00053303 | 0.00054199 | 0.00055094 | 0.00055989 | 0.00056885
| 10489273 | MRO007 | MRO | 17386158 | 17386154 | 0.67581 | 143.897 | -36.9374 | 104 | 93.3 | 6.3% | 8.8% | 110.552 | 99.1779 | 0.01 | 0.02 | -1137.41 | 121.9261 | 1.576% | 111.592 | 101.5104 | 0.01 | 0.02 | -1008.16 | 121.6736 | 1.753% | 157.6% | 0.977% | 0.9966% | 1.016% | 1.036% | 1.055% | 1.075% | 1.095% | 1.114% | 1.134% | 1.153% | 1.173% | 1.193% | 1.212% | 1.232% | 1.251% | 1.271% | 1.291% | 1.31% | 1.33% | 1.349% | 0.00039568 | 0.00040362 | 0.00041155 | 0.00041949 | 0.00042742 | 0.00043535 | 0.00044329 | 0.00045122 | 0.00045916 | 0.00046709 | 0.00047502 | 0.00048296 | 0.00049089 | 0.00049883 | 0.00050676 | 0.0005147 | 0.00052263 | 0.00053056 | 0.0005385 | 0.00054643
| 10489291 | MRO007 | MRO | 17386241 | 17386496 | 0.68352 | 143.9006 | -36.9183 | 106 | 94.7 | 6.3% | 8.8% | 112.678 | 100.6661 | 0.01 | 0.02 | -1201.19 | 124.6899 | 1.556% | 113.738 | 103.0336 | 0.01 | 0.02 | -1070.44 | 124.4424 | 1.723% | 155.6% | 0.975% | 0.9939% | 1.013% | 1.032% | 1.051% | 1.07% | 1.088% | 1.107% | 1.126% | 1.145% | 1.164% | 1.183% | 1.202% | 1.221% | 1.24% | 1.259% | 1.278% | 1.296% | 1.315% | 1.334% | 0.00039485 | 0.00040251 | 0.00041017 | 0.00041783 | 0.00042548 | 0.00043314 | 0.0004408 | 0.00044845 | 0.00045611 | 0.00046377 | 0.00047143 | 0.00047908 | 0.00048674 | 0.0004944 | 0.00050206 | 0.00050971 | 0.00051737 | 0.00052503 | 0.00053268 | 0.00054034
| 10489354 | MRO007 | MRO | 17386487 | 73550512 | 0.66195 | 143.888 | -36.8958 | 103 | 92.6 | 6.3% | 8.8% | 109.489 | 98.4338 | 0.01 | 0.02 | -1105.52 | 120.5442 | 1.587% | 110.519 | 100.7488 | 0.01 | 0.02 | -977.02 | 120.2892 | 1.77% | 158.7% | 0.9782% | 0.9981% | 1.018% | 1.038% | 1.058% | 1.078% | 1.098% | 1.118% | 1.138% | 1.158% | 1.178% | 1.198% | 1.218% | 1.238% | 1.258% | 1.278% | 1.298% | 1.318% | 1.337% | 1.357% | 0.00039614 | 0.00040422 | 0.0004123 | 0.00042039 | 0.00042847 | 0.00043656 | 0.00044464 | 0.00045273 | 0.00046081 | 0.0004689 | 0.00047698 | 0.00048506 | 0.00049315 | 0.00050123 | 0.00050932 | 0.0005174 | 0.00052549 | 0.00053357 | 0.00054166 | 0.00054974
| 10489395 | MRO007 | MRO | 73550580 | 17386692 | 0.80237 | 143.8534 | -36.9239 | 103 | 92.5 | 6.3% | 8.8% | 109.489 | 98.3275 | 0.01 | 0.02 | -1116.15 | 120.6505 | 1.581% | 110.519 | 100.64 | 0.01 | 0.02 | -987.9 | 120.398 | 1.761% | 158.1% | 0.9776% | 0.9974% | 1.017% | 1.037% | 1.057% | 1.076% | 1.096% | 1.116% | 1.136% | 1.156% | 1.175% | 1.195% | 1.215% | 1.235% | 1.254% | 1.274% | 1.294% | 1.314% | 1.333% | 1.353% | 0.0003959 | 0.00040391 | 0.00041192 | 0.00041993 | 0.00042793 | 0.00043594 | 0.00044395 | 0.00045196 | 0.00045996 | 0.00046797 | 0.00047598 | 0.00048399 | 0.00049199 | 0.0005 | 0.00050801 | 0.00051602 | 0.00052402 | 0.00053203 | 0.00054004 | 0.00054805
| 10489507 | MRO007 | MRO | 17387223 | 17387173 | 1.188 | 143.8188 | -37.024 | 106 | 94.6 | 6.3% | 8.8% | 112.678 | 100.5598 | 0.01 | 0.02 | -1211.82 | 124.7962 | 1.551% | 113.738 | 102.9248 | 0.01 | 0.02 | -1081.32 | 124.5512 | 1.716% | 155.1% | 0.9745% | 0.9932% | 1.012% | 1.031% | 1.049% | 1.068% | 1.087% | 1.106% | 1.124% | 1.143% | 1.162% | 1.181% | 1.199% | 1.218% | 1.237% | 1.256% | 1.274% | 1.293% | 1.312% | 1.331% | 0.00039465 | 0.00040224 | 0.00040983 | 0.00041742 | 0.00042501 | 0.0004326 | 0.00044019 | 0.00044778 | 0.00045537 | 0.00046296 | 0.00047055 | 0.00047814 | 0.00048573 | 0.00049332 | 0.00050091 | 0.0005085 | 0.00051609 | 0.00052368 | 0.00053127 | 0.00053886
| 10489512 | MRO007 | MRO | 17387190 | 17387186 | 0.85217 | 143.8271 | -37.0038 | 106 | 94.4 | 6.3% | 8.8% | 112.678 | 100.3472 | 0.01 | 0.02 | -1233.08 | 125.0088 | 1.542% | 113.738 | 102.7072 | 0.01 | 0.02 | -1103.08 | 124.7688 | 1.701% | 154.2% | 0.9735% | 0.9919% | 1.01% | 1.029% | 1.047% | 1.066% | 1.084% | 1.102% | 1.121% | 1.139% | 1.158% | 1.176% | 1.195% | 1.213% | 1.231% | 1.25% | 1.268% | 1.287% | 1.305% | 1.323% | 0.00039426 | 0.00040172 | 0.00040918 | 0.00041664 | 0.0004241 | 0.00043156 | 0.00043902 | 0.00044647 | 0.00045393 | 0.00046139 | 0.00046885 | 0.00047631 | 0.00048377 | 0.00049123 | 0.00049869 | 0.00050615 | 0.00051361 | 0.00052107 | 0.00052853 | 0.00053599
| 10489514 | MRO007 | MRO | 17796725 | 17387194 | 1.7806 | 143.8271 | -37.0077 | 106 | 94.4 | 6.3% | 8.8% | 112.678 | 100.3472 | 0.01 | 0.02 | -1233.08 | 125.0088 | 1.542% | 113.738 | 102.7072 | 0.01 | 0.02 | -1103.08 | 124.7688 | 1.701% | 154.2% | 0.9735% | 0.9919% | 1.01% | 1.029% | 1.047% | 1.066% | 1.084% | 1.102% | 1.121% | 1.139% | 1.158% | 1.176% | 1.195% | 1.213% | 1.231% | 1.25% | 1.268% | 1.287% | 1.305% | 1.323% | 0.00039426 | 0.00040172 | 0.00040918 | 0.00041664 | 0.0004241 | 0.00043156 | 0.00043902 | 0.00044647 | 0.00045393 | 0.00046139 | 0.00046885 | 0.00047631 | 0.00048377 | 0.00049123 | 0.00049869 | 0.00050615 | 0.00051361 | 0.00052107 | 0.00052853 | 0.00053599
| 10489526 | MRO007 | MRO | 17387249 | 17387245 | 0.65115 | 143.8534 | -37.0062 | 107 | 95.3 | 6.3% | 8.8% | 113.741 | 101.3039 | 0.01 | 0.02 | -1243.71 | 126.1781 | 1.542% | 114.811 | 103.6864 | 0.01 | 0.02 | -1112.46 | 125.9356 | 1.702% | 154.2% | 0.9736% | 0.992% | 1.01% | 1.029% | 1.047% | 1.066% | 1.084% | 1.103% | 1.121% | 1.139% | 1.158% | 1.176% | 1.195% | 1.213% | 1.232% | 1.25% | 1.269% | 1.287% | 1.305% | 1.324% | 0.00039428 | 0.00040174 | 0.00040921 | 0.00041667 | 0.00042414 | 0.0004316 | 0.00043907 | 0.00044653 | 0.000454 | 0.00046146 | 0.00046893 | 0.0004764 | 0.00048386 | 0.00049133 | 0.00049879 | 0.00050626 | 0.00051372 | 0.00052119 | 0.00052865 | 0.00053612
| 10489528 | MRO007 | MRO | 17387365 | 17387249 | 1.8697 | 143.8567 | -37.0067 | 107 | 95.3 | 6.3% | 8.8% | 113.741 | 101.3039 | 0.01 | 0.02 | -1243.71 | 126.1781 | 1.542% | 114.811 | 103.6864 | 0.01 | 0.02 | -1112.46 | 125.9356 | 1.702% | 154.2% | 0.9736% | 0.992% | 1.01% | 1.029% | 1.047% | 1.066% | 1.084% | 1.103% | 1.121% | 1.139% | 1.158% | 1.176% | 1.195% | 1.213% | 1.232% | 1.25% | 1.269% | 1.287% | 1.305% | 1.324% | 0.00039428 | 0.00040174 | 0.00040921 | 0.00041667 | 0.00042414 | 0.0004316 | 0.00043907 | 0.00044653 | 0.000454 | 0.00046146 | 0.00046893 | 0.0004764 | 0.00048386 | 0.00049133 | 0.00049879 | 0.00050626 | 0.00051372 | 0.00052119 | 0.00052865 | 0.00053612
| 10489555 | MRO007 | MRO | 17387356 | 17387365 | 1.4204 | 143.8602 | -37.0072 | 107 | 95.3 | 6.3% | 8.8% | 113.741 | 101.3039 | 0.01 | 0.02 | -1243.71 | 126.1781 | 1.542% | 114.811 | 103.6864 | 0.01 | 0.02 | -1112.46 | 125.9356 | 1.702% | 154.2% | 0.9736% | 0.992% | 1.01% | 1.029% | 1.047% | 1.066% | 1.084% | 1.103% | 1.121% | 1.139% | 1.158% | 1.176% | 1.195% | 1.213% | 1.232% | 1.25% | 1.269% | 1.287% | 1.305% | 1.324% | 0.00039428 | 0.00040174 | 0.00040921 | 0.00041667 | 0.00042414 | 0.0004316 | 0.00043907 | 0.00044653 | 0.000454 | 0.00046146 | 0.00046893 | 0.0004764 | 0.00048386 | 0.00049133 | 0.00049879 | 0.00050626 | 0.00051372 | 0.00052119 | 0.00052865 | 0.00053612
| 10489942 | MRO007 | MRO | 17389226 | 17389230 | 0.54715 | 144.0111 | -36.8838 | 110 | 98.5 | 6.3% | 8.8% | 116.93 | 104.7055 | 0.01 | 0.02 | -1222.45 | 129.1545 | 1.567% | 118.03 | 107.168 | 0.01 | 0.02 | -1086.2 | 128.892 | 1.739% | 156.7% | 0.9761% | 0.9954% | 1.015% | 1.034% | 1.053% | 1.073% | 1.092% | 1.111% | 1.13% | 1.15% | 1.169% | 1.188% | 1.207% | 1.227% | 1.246% | 1.265% | 1.285% | 1.304% | 1.323% | 1.342% | 0.00039531 | 0.00040311 | 0.00041092 | 0.00041873 | 0.00042654 | 0.00043435 | 0.00044215 | 0.00044996 | 0.00045777 | 0.00046558 | 0.00047339 | 0.00048119 | 0.000489 | 0.00049681 | 0.00050462 | 0.00051243 | 0.00052023 | 0.00052804 | 0.00053585 | 0.00054366
| 10489943 | MRO007 | MRO | 17389234 | 17389230 | 0.76162 | 144.0136 | -36.8843 | 110 | 98.5 | 6.3% | 8.8% | 116.93 | 104.7055 | 0.01 | 0.02 | -1222.45 | 129.1545 | 1.567% | 118.03 | 107.168 | 0.01 | 0.02 | -1086.2 | 128.892 | 1.739% | 156.7% | 0.9761% | 0.9954% | 1.015% | 1.034% | 1.053% | 1.073% | 1.092% | 1.111% | 1.13% | 1.15% | 1.169% | 1.188% | 1.207% | 1.227% | 1.246% | 1.265% | 1.285% | 1.304% | 1.323% | 1.342% | 0.00039531 | 0.00040311 | 0.00041092 | 0.00041873 | 0.00042654 | 0.00043435 | 0.00044215 | 0.00044996 | 0.00045777 | 0.00046558 | 0.00047339 | 0.00048119 | 0.000489 | 0.00049681 | 0.00050462 | 0.00051243 | 0.00052023 | 0.00052804 | 0.00053585 | 0.00054366
| 10490021 | MRO007 | MRO | 17389617 | 17389630 | 2.1773 | 144.0249 | -36.8775 | 110 | 98.5 | 6.3% | 8.8% | 116.93 | 104.7055 | 0.01 | 0.02 | -1222.45 | 129.1545 | 1.567% | 118.03 | 107.168 | 0.01 | 0.02 | -1086.2 | 128.892 | 1.739% | 156.7% | 0.9761% | 0.9954% | 1.015% | 1.034% | 1.053% | 1.073% | 1.092% | 1.111% | 1.13% | 1.15% | 1.169% | 1.188% | 1.207% | 1.227% | 1.246% | 1.265% | 1.285% | 1.304% | 1.323% | 1.342% | 0.00039531 | 0.00040311 | 0.00041092 | 0.00041873 | 0.00042654 | 0.00043435 | 0.00044215 | 0.00044996 | 0.00045777 | 0.00046558 | 0.00047339 | 0.00048119 | 0.000489 | 0.00049681 | 0.00050462 | 0.00051243 | 0.00052023 | 0.00052804 | 0.00053585 | 0.00054366
| 10490026 | MRO007 | MRO | 17389634 | 17448380 | 1.695 | 144.0314 | -36.8769 | 110 | 98.9 | 6.3% | 8.8% | 116.93 | 105.1307 | 0.01 | 0.02 | -1179.93 | 128.7293 | 1.587% | 118.03 | 107.6032 | 0.01 | 0.02 | -1042.68 | 128.4568 | 1.77% | 158.7% | 0.9782% | 0.9982% | 1.018% | 1.038% | 1.058% | 1.078% | 1.098% | 1.118% | 1.138% | 1.158% | 1.178% | 1.198% | 1.218% | 1.238% | 1.258% | 1.278% | 1.298% | 1.318% | 1.338% | 1.358% | 0.00039615 | 0.00040424 | 0.00041233 | 0.00042042 | 0.00042851 | 0.0004366 | 0.00044469 | 0.00045278 | 0.00046087 | 0.00046895 | 0.00047704 | 0.00048513 | 0.00049322 | 0.00050131 | 0.0005094 | 0.00051749 | 0.00052558 | 0.00053367 | 0.00054176 | 0.00054985
| 10490184 | CMN004 | CMN | 17390245 | 17390984 | 0.26743 | 143.967 | -36.9824 | 108 | 96.8 | 6.3% | 8.8% | 114.804 | 102.8984 | 0.01 | 0.02 | -1190.56 | 126.7096 | 1.571% | 115.884 | 105.3184 | 0.01 | 0.02 | -1056.56 | 126.4496 | 1.746% | 157.1% | 0.9766% | 0.996% | 1.015% | 1.035% | 1.054% | 1.074% | 1.093% | 1.113% | 1.132% | 1.152% | 1.171% | 1.19% | 1.21% | 1.229% | 1.249% | 1.268% | 1.288% | 1.307% | 1.326% | 1.346% | 0.0003955 | 0.00040337 | 0.00041124 | 0.00041911 | 0.00042698 | 0.00043485 | 0.00044272 | 0.0004506 | 0.00045847 | 0.00046634 | 0.00047421 | 0.00048208 | 0.00048995 | 0.00049782 | 0.0005057 | 0.00051357 | 0.00052144 | 0.00052931 | 0.00053718 | 0.00054505
| 10490223 | CMN004 | CMN | 17390391 | 17390395 | 0.44 | 143.9699 | -36.988 | 108 | 96.8 | 6.3% | 8.8% | 114.804 | 102.8984 | 0.01 | 0.02 | -1190.56 | 126.7096 | 1.571% | 115.884 | 105.3184 | 0.01 | 0.02 | -1056.56 | 126.4496 | 1.746% | 157.1% | 0.9766% | 0.996% | 1.015% | 1.035% | 1.054% | 1.074% | 1.093% | 1.113% | 1.132% | 1.152% | 1.171% | 1.19% | 1.21% | 1.229% | 1.249% | 1.268% | 1.288% | 1.307% | 1.326% | 1.346% | 0.0003955 | 0.00040337 | 0.00041124 | 0.00041911 | 0.00042698 | 0.00043485 | 0.00044272 | 0.0004506 | 0.00045847 | 0.00046634 | 0.00047421 | 0.00048208 | 0.00048995 | 0.00049782 | 0.0005057 | 0.00051357 | 0.00052144 | 0.00052931 | 0.00053718 | 0.00054505
| 10491306 | CMN002 | CMN | 17864580 | 17398155 | 1.2242 | 144.0787 | -37.1493 | 112 | 100 | 6.3% | 8.8% | 119.056 | 106.3 | 0.01 | 0.02 | -1275.6 | 131.812 | 1.553% | 120.176 | 108.8 | 0.01 | 0.02 | -1137.6 | 131.552 | 1.719% | 155.3% | 0.9747% | 0.9935% | 1.012% | 1.031% | 1.05% | 1.069% | 1.088% | 1.106% | 1.125% | 1.144% | 1.163% | 1.182% | 1.2% | 1.219% | 1.238% | 1.257% | 1.276% | 1.295% | 1.313% | 1.332% | 0.00039474 | 0.00040236 | 0.00040998 | 0.00041759 | 0.00042521 | 0.00043283 | 0.00044045 | 0.00044807 | 0.00045569 | 0.00046331 | 0.00047093 | 0.00047854 | 0.00048616 | 0.00049378 | 0.0005014 | 0.00050902 | 0.00051664 | 0.00052426 | 0.00053188 | 0.00053949
| 10494246 | CMN002 | CMN | 17413611 | 17415615 | 2.7907 | 143.9299 | -37.1628 | 110 | 97.9 | 6.3% | 8.8% | 116.93 | 104.0677 | 0.01 | 0.02 | -1286.23 | 129.7923 | 1.539% | 118.03 | 106.5152 | 0.01 | 0.02 | -1151.48 | 129.5448 | 1.697% | 153.9% | 0.9732% | 0.9916% | 1.01% | 1.028% | 1.047% | 1.065% | 1.083% | 1.102% | 1.12% | 1.138% | 1.156% | 1.175% | 1.193% | 1.211% | 1.23% | 1.248% | 1.266% | 1.285% | 1.303% | 1.321% | 0.00039414 | 0.00040157 | 0.00040899 | 0.00041641 | 0.00042383 | 0.00043125 | 0.00043867 | 0.00044609 | 0.00045351 | 0.00046093 | 0.00046835 | 0.00047577 | 0.00048319 | 0.00049062 | 0.00049804 | 0.00050546 | 0.00051288 | 0.0005203 | 0.00052772 | 0.00053514
| 10495435 | BAN003 | BAN | 17420852 | 17420856 | 0.8977 | 144.2001 | -37.5531 | 136 | 119 | 5.4% | 7.3% | 143.344 | 125.426 | 0.01 | 0.02 | -1791.8 | 161.262 | 1.41% | 145.928 | 127.687 | 0.01 | 0.02 | -1824.1 | 164.169 | 1.544% | 141% | 0.9601% | 0.974% | 0.988% | 1.002% | 1.016% | 1.03% | 1.044% | 1.058% | 1.072% | 1.086% | 1.099% | 1.113% | 1.127% | 1.141% | 1.155% | 1.169% | 1.183% | 1.197% | 1.211% | 1.225% | 0.00038882 | 0.00039446 | 0.00040011 | 0.00040575 | 0.0004114 | 0.00041704 | 0.00042269 | 0.00042833 | 0.00043398 | 0.00043962 | 0.00044527 | 0.00045092 | 0.00045656 | 0.00046221 | 0.00046785 | 0.0004735 | 0.00047914 | 0.00048479 | 0.00049043 | 0.00049608
| 10496492 | GHP021 | GHP | 17425866 | 17425870 | 0.32368 | 143.988 | -38.0317 | 105 | 93 | 5.4% | 7.3% | 110.67 | 98.022 | 0.01 | 0.02 | -1264.8 | 123.318 | 1.448% | 112.665 | 99.789 | 0.01 | 0.02 | -1287.6 | 125.541 | 1.595% | 144.8% | 0.964% | 0.9793% | 0.9945% | 1.01% | 1.025% | 1.04% | 1.055% | 1.071% | 1.086% | 1.101% | 1.116% | 1.132% | 1.147% | 1.162% | 1.177% | 1.193% | 1.208% | 1.223% | 1.238% | 1.254% | 0.00039041 | 0.00039658 | 0.00040275 | 0.00040893 | 0.0004151 | 0.00042128 | 0.00042745 | 0.00043363 | 0.0004398 | 0.00044598 | 0.00045215 | 0.00045832 | 0.0004645 | 0.00047067 | 0.00047685 | 0.00048302 | 0.0004892 | 0.00049537 | 0.00050155 | 0.00050772
| 10496504 | GHP021 | GHP | 17425917 | 17425925 | 2.263 | 144.0013 | -38.05 | 106 | 93.5 | 5.4% | 7.3% | 111.724 | 98.549 | 0.01 | 0.02 | -1317.5 | 124.899 | 1.434% | 113.738 | 100.3255 | 0.01 | 0.02 | -1341.25 | 127.1505 | 1.577% | 143.4% | 0.9626% | 0.9774% | 0.9922% | 1.007% | 1.022% | 1.036% | 1.051% | 1.066% | 1.081% | 1.096% | 1.11% | 1.125% | 1.14% | 1.155% | 1.169% | 1.184% | 1.199% | 1.214% | 1.229% | 1.243% | 0.00038983 | 0.00039582 | 0.0004018 | 0.00040779 | 0.00041377 | 0.00041975 | 0.00042574 | 0.00043172 | 0.00043771 | 0.00044369 | 0.00044967 | 0.00045566 | 0.00046164 | 0.00046763 | 0.00047361 | 0.00047959 | 0.00048558 | 0.00049156 | 0.00049755 | 0.00050353
| 10496512 | CLC006 | CLC | 95032394 | 17425956 | 1.9544 | 143.5841 | -37.8979 | 111 | 97.6 | 5.4% | 7.3% | 116.994 | 102.8704 | 0.01 | 0.02 | -1412.36 | 131.1176 | 1.424% | 119.103 | 104.7248 | 0.01 | 0.02 | -1437.82 | 133.4812 | 1.564% | 142.4% | 0.9616% | 0.976% | 0.9904% | 1.005% | 1.019% | 1.034% | 1.048% | 1.063% | 1.077% | 1.091% | 1.106% | 1.12% | 1.135% | 1.149% | 1.164% | 1.178% | 1.193% | 1.207% | 1.221% | 1.236% | 0.00038942 | 0.00039526 | 0.00040111 | 0.00040695 | 0.0004128 | 0.00041864 | 0.00042449 | 0.00043034 | 0.00043618 | 0.00044203 | 0.00044787 | 0.00045372 | 0.00045956 | 0.00046541 | 0.00047125 | 0.0004771 | 0.00048294 | 0.00048879 | 0.00049463 | 0.00050048
| 10497201 | CLC006 | CLC | 17429010 | 17429006 | 0.51175 | 143.6557 | -37.9818 | 108 | 95.5 | 5.4% | 7.3% | 113.832 | 100.657 | 0.01 | 0.02 | -1317.5 | 127.007 | 1.443% | 115.884 | 102.4715 | 0.01 | 0.02 | -1341.25 | 129.2965 | 1.588% | 144.3% | 0.9634% | 0.9785% | 0.9935% | 1.009% | 1.024% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.129% | 1.144% | 1.159% | 1.174% | 1.189% | 1.204% | 1.219% | 1.234% | 1.249% | 0.00039017 | 0.00039627 | 0.00040237 | 0.00040846 | 0.00041456 | 0.00042066 | 0.00042675 | 0.00043285 | 0.00043895 | 0.00044504 | 0.00045114 | 0.00045724 | 0.00046333 | 0.00046943 | 0.00047553 | 0.00048163 | 0.00048772 | 0.00049382 | 0.00049992 | 0.00050601
| 10497202 | CLC006 | CLC | 17429014 | 17429010 | 1.0095 | 143.6554 | -37.9829 | 108 | 95.5 | 5.4% | 7.3% | 113.832 | 100.657 | 0.01 | 0.02 | -1317.5 | 127.007 | 1.443% | 115.884 | 102.4715 | 0.01 | 0.02 | -1341.25 | 129.2965 | 1.588% | 144.3% | 0.9634% | 0.9785% | 0.9935% | 1.009% | 1.024% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.129% | 1.144% | 1.159% | 1.174% | 1.189% | 1.204% | 1.219% | 1.234% | 1.249% | 0.00039017 | 0.00039627 | 0.00040237 | 0.00040846 | 0.00041456 | 0.00042066 | 0.00042675 | 0.00043285 | 0.00043895 | 0.00044504 | 0.00045114 | 0.00045724 | 0.00046333 | 0.00046943 | 0.00047553 | 0.00048163 | 0.00048772 | 0.00049382 | 0.00049992 | 0.00050601
| 10497203 | CLC006 | CLC | 17429018 | 17429014 | 1.3535 | 143.6552 | -37.9841 | 108 | 95.5 | 5.4% | 7.3% | 113.832 | 100.657 | 0.01 | 0.02 | -1317.5 | 127.007 | 1.443% | 115.884 | 102.4715 | 0.01 | 0.02 | -1341.25 | 129.2965 | 1.588% | 144.3% | 0.9634% | 0.9785% | 0.9935% | 1.009% | 1.024% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.129% | 1.144% | 1.159% | 1.174% | 1.189% | 1.204% | 1.219% | 1.234% | 1.249% | 0.00039017 | 0.00039627 | 0.00040237 | 0.00040846 | 0.00041456 | 0.00042066 | 0.00042675 | 0.00043285 | 0.00043895 | 0.00044504 | 0.00045114 | 0.00045724 | 0.00046333 | 0.00046943 | 0.00047553 | 0.00048163 | 0.00048772 | 0.00049382 | 0.00049992 | 0.00050601
| 10497204 | CLC006 | CLC | 17429022 | 17429018 | 1.2777 | 143.655 | -37.9853 | 108 | 95.5 | 5.4% | 7.3% | 113.832 | 100.657 | 0.01 | 0.02 | -1317.5 | 127.007 | 1.443% | 115.884 | 102.4715 | 0.01 | 0.02 | -1341.25 | 129.2965 | 1.588% | 144.3% | 0.9634% | 0.9785% | 0.9935% | 1.009% | 1.024% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.129% | 1.144% | 1.159% | 1.174% | 1.189% | 1.204% | 1.219% | 1.234% | 1.249% | 0.00039017 | 0.00039627 | 0.00040237 | 0.00040846 | 0.00041456 | 0.00042066 | 0.00042675 | 0.00043285 | 0.00043895 | 0.00044504 | 0.00045114 | 0.00045724 | 0.00046333 | 0.00046943 | 0.00047553 | 0.00048163 | 0.00048772 | 0.00049382 | 0.00049992 | 0.00050601
| 10497206 | CLC006 | CLC | 17429022 | 17429027 | 2.0436 | 143.6562 | -37.9862 | 108 | 95.5 | 5.4% | 7.3% | 113.832 | 100.657 | 0.01 | 0.02 | -1317.5 | 127.007 | 1.443% | 115.884 | 102.4715 | 0.01 | 0.02 | -1341.25 | 129.2965 | 1.588% | 144.3% | 0.9634% | 0.9785% | 0.9935% | 1.009% | 1.024% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.129% | 1.144% | 1.159% | 1.174% | 1.189% | 1.204% | 1.219% | 1.234% | 1.249% | 0.00039017 | 0.00039627 | 0.00040237 | 0.00040846 | 0.00041456 | 0.00042066 | 0.00042675 | 0.00043285 | 0.00043895 | 0.00044504 | 0.00045114 | 0.00045724 | 0.00046333 | 0.00046943 | 0.00047553 | 0.00048163 | 0.00048772 | 0.00049382 | 0.00049992 | 0.00050601
| 10500258 | CLC013 | CLC | 17443068 | 17443508 | 2.4305 | 143.7451 | -38.4323 | 126 | 110 | 5.4% | 7.3% | 132.804 | 115.94 | 0.01 | 0.02 | -1686.4 | 149.668 | 1.403% | 135.198 | 118.03 | 0.01 | 0.02 | -1716.8 | 152.366 | 1.536% | 140.3% | 0.9594% | 0.9732% | 0.9869% | 1.001% | 1.014% | 1.028% | 1.042% | 1.055% | 1.069% | 1.083% | 1.097% | 1.11% | 1.124% | 1.138% | 1.152% | 1.165% | 1.179% | 1.193% | 1.206% | 1.22% | 0.00038855 | 0.00039411 | 0.00039967 | 0.00040522 | 0.00041078 | 0.00041634 | 0.0004219 | 0.00042745 | 0.00043301 | 0.00043857 | 0.00044412 | 0.00044968 | 0.00045524 | 0.00046079 | 0.00046635 | 0.00047191 | 0.00047747 | 0.00048302 | 0.00048858 | 0.00049414
| 10500737 | CLC013 | CLC | 17445122 | 17555460 | 0.19684 | 143.7492 | -38.4804 | 145 | 127 | 5.4% | 7.3% | 152.83 | 133.858 | 0.01 | 0.02 | -1897.2 | 171.802 | 1.413% | 155.585 | 136.271 | 0.01 | 0.02 | -1931.4 | 174.899 | 1.548% | 141.3% | 0.9604% | 0.9744% | 0.9885% | 1.002% | 1.017% | 1.031% | 1.045% | 1.059% | 1.073% | 1.087% | 1.101% | 1.115% | 1.129% | 1.143% | 1.157% | 1.171% | 1.185% | 1.199% | 1.213% | 1.227% | 0.00038894 | 0.00039462 | 0.0004003 | 0.00040599 | 0.00041167 | 0.00041736 | 0.00042304 | 0.00042873 | 0.00043441 | 0.0004401 | 0.00044578 | 0.00045146 | 0.00045715 | 0.00046283 | 0.00046852 | 0.0004742 | 0.00047989 | 0.00048557 | 0.00049126 | 0.00049694
| 10500739 | CLC013 | CLC | 17445126 | 17555464 | 1.3541 | 143.7465 | -38.4801 | 145 | 127 | 5.4% | 7.3% | 152.83 | 133.858 | 0.01 | 0.02 | -1897.2 | 171.802 | 1.413% | 155.585 | 136.271 | 0.01 | 0.02 | -1931.4 | 174.899 | 1.548% | 141.3% | 0.9604% | 0.9744% | 0.9885% | 1.002% | 1.017% | 1.031% | 1.045% | 1.059% | 1.073% | 1.087% | 1.101% | 1.115% | 1.129% | 1.143% | 1.157% | 1.171% | 1.185% | 1.199% | 1.213% | 1.227% | 0.00038894 | 0.00039462 | 0.0004003 | 0.00040599 | 0.00041167 | 0.00041736 | 0.00042304 | 0.00042873 | 0.00043441 | 0.0004401 | 0.00044578 | 0.00045146 | 0.00045715 | 0.00046283 | 0.00046852 | 0.0004742 | 0.00047989 | 0.00048557 | 0.00049126 | 0.00049694
| 10500741 | CLC013 | CLC | 17456712 | 17445133 | 0.98008 | 143.7456 | -38.4823 | 145 | 127 | 5.4% | 7.3% | 152.83 | 133.858 | 0.01 | 0.02 | -1897.2 | 171.802 | 1.413% | 155.585 | 136.271 | 0.01 | 0.02 | -1931.4 | 174.899 | 1.548% | 141.3% | 0.9604% | 0.9744% | 0.9885% | 1.002% | 1.017% | 1.031% | 1.045% | 1.059% | 1.073% | 1.087% | 1.101% | 1.115% | 1.129% | 1.143% | 1.157% | 1.171% | 1.185% | 1.199% | 1.213% | 1.227% | 0.00038894 | 0.00039462 | 0.0004003 | 0.00040599 | 0.00041167 | 0.00041736 | 0.00042304 | 0.00042873 | 0.00043441 | 0.0004401 | 0.00044578 | 0.00045146 | 0.00045715 | 0.00046283 | 0.00046852 | 0.0004742 | 0.00047989 | 0.00048557 | 0.00049126 | 0.00049694
| 10502811 | CLC013 | CLC | 17555464 | 17456708 | 0.25466 | 143.7454 | -38.48 | 145 | 127 | 5.4% | 7.3% | 152.83 | 133.858 | 0.01 | 0.02 | -1897.2 | 171.802 | 1.413% | 155.585 | 136.271 | 0.01 | 0.02 | -1931.4 | 174.899 | 1.548% | 141.3% | 0.9604% | 0.9744% | 0.9885% | 1.002% | 1.017% | 1.031% | 1.045% | 1.059% | 1.073% | 1.087% | 1.101% | 1.115% | 1.129% | 1.143% | 1.157% | 1.171% | 1.185% | 1.199% | 1.213% | 1.227% | 0.00038894 | 0.00039462 | 0.0004003 | 0.00040599 | 0.00041167 | 0.00041736 | 0.00042304 | 0.00042873 | 0.00043441 | 0.0004401 | 0.00044578 | 0.00045146 | 0.00045715 | 0.00046283 | 0.00046852 | 0.0004742 | 0.00047989 | 0.00048557 | 0.00049126 | 0.00049694
| 10502812 | CLC013 | CLC | 17555464 | 17456712 | 0.18674 | 143.7459 | -38.4805 | 145 | 127 | 5.4% | 7.3% | 152.83 | 133.858 | 0.01 | 0.02 | -1897.2 | 171.802 | 1.413% | 155.585 | 136.271 | 0.01 | 0.02 | -1931.4 | 174.899 | 1.548% | 141.3% | 0.9604% | 0.9744% | 0.9885% | 1.002% | 1.017% | 1.031% | 1.045% | 1.059% | 1.073% | 1.087% | 1.101% | 1.115% | 1.129% | 1.143% | 1.157% | 1.171% | 1.185% | 1.199% | 1.213% | 1.227% | 0.00038894 | 0.00039462 | 0.0004003 | 0.00040599 | 0.00041167 | 0.00041736 | 0.00042304 | 0.00042873 | 0.00043441 | 0.0004401 | 0.00044578 | 0.00045146 | 0.00045715 | 0.00046283 | 0.00046852 | 0.0004742 | 0.00047989 | 0.00048557 | 0.00049126 | 0.00049694
| 10502855 | CLC013 | CLC | 17456864 | 17456860 | 0.21253 | 143.7184 | -38.5087 | 147 | 129 | 5.4% | 7.3% | 154.938 | 135.966 | 0.01 | 0.02 | -1897.2 | 173.91 | 1.418% | 157.731 | 138.417 | 0.01 | 0.02 | -1931.4 | 177.045 | 1.556% | 141.8% | 0.961% | 0.9752% | 0.9894% | 1.004% | 1.018% | 1.032% | 1.046% | 1.061% | 1.075% | 1.089% | 1.103% | 1.117% | 1.132% | 1.146% | 1.16% | 1.174% | 1.189% | 1.203% | 1.217% | 1.231% | 0.00038917 | 0.00039493 | 0.0004007 | 0.00040646 | 0.00041222 | 0.00041798 | 0.00042375 | 0.00042951 | 0.00043527 | 0.00044104 | 0.0004468 | 0.00045256 | 0.00045832 | 0.00046409 | 0.00046985 | 0.00047561 | 0.00048138 | 0.00048714 | 0.0004929 | 0.00049866
| 10502857 | CLC013 | CLC | 17555481 | 17456864 | 0.84808 | 143.7193 | -38.5077 | 147 | 129 | 5.4% | 7.3% | 154.938 | 135.966 | 0.01 | 0.02 | -1897.2 | 173.91 | 1.418% | 157.731 | 138.417 | 0.01 | 0.02 | -1931.4 | 177.045 | 1.556% | 141.8% | 0.961% | 0.9752% | 0.9894% | 1.004% | 1.018% | 1.032% | 1.046% | 1.061% | 1.075% | 1.089% | 1.103% | 1.117% | 1.132% | 1.146% | 1.16% | 1.174% | 1.189% | 1.203% | 1.217% | 1.231% | 0.00038917 | 0.00039493 | 0.0004007 | 0.00040646 | 0.00041222 | 0.00041798 | 0.00042375 | 0.00042951 | 0.00043527 | 0.00044104 | 0.0004468 | 0.00045256 | 0.00045832 | 0.00046409 | 0.00046985 | 0.00047561 | 0.00048138 | 0.00048714 | 0.0004929 | 0.00049866
| 10502919 | CLC013 | CLC | 17457164 | 17457145 | 1.4223 | 143.7227 | -38.5189 | 147 | 129 | 5.4% | 7.3% | 154.938 | 135.966 | 0.01 | 0.02 | -1897.2 | 173.91 | 1.418% | 157.731 | 138.417 | 0.01 | 0.02 | -1931.4 | 177.045 | 1.556% | 141.8% | 0.961% | 0.9752% | 0.9894% | 1.004% | 1.018% | 1.032% | 1.046% | 1.061% | 1.075% | 1.089% | 1.103% | 1.117% | 1.132% | 1.146% | 1.16% | 1.174% | 1.189% | 1.203% | 1.217% | 1.231% | 0.00038917 | 0.00039493 | 0.0004007 | 0.00040646 | 0.00041222 | 0.00041798 | 0.00042375 | 0.00042951 | 0.00043527 | 0.00044104 | 0.0004468 | 0.00045256 | 0.00045832 | 0.00046409 | 0.00046985 | 0.00047561 | 0.00048138 | 0.00048714 | 0.0004929 | 0.00049866
| 10502924 | CLC013 | CLC | 155049103 | 17457168 | 2.4611 | 143.7201 | -38.5112 | 147 | 129 | 5.4% | 7.3% | 154.938 | 135.966 | 0.01 | 0.02 | -1897.2 | 173.91 | 1.418% | 157.731 | 138.417 | 0.01 | 0.02 | -1931.4 | 177.045 | 1.556% | 141.8% | 0.961% | 0.9752% | 0.9894% | 1.004% | 1.018% | 1.032% | 1.046% | 1.061% | 1.075% | 1.089% | 1.103% | 1.117% | 1.132% | 1.146% | 1.16% | 1.174% | 1.189% | 1.203% | 1.217% | 1.231% | 0.00038917 | 0.00039493 | 0.0004007 | 0.00040646 | 0.00041222 | 0.00041798 | 0.00042375 | 0.00042951 | 0.00043527 | 0.00044104 | 0.0004468 | 0.00045256 | 0.00045832 | 0.00046409 | 0.00046985 | 0.00047561 | 0.00048138 | 0.00048714 | 0.0004929 | 0.00049866
| 10503126 | WIN011 | WIN | 17458163 | 17458159 | 1.1709 | 143.7983 | -38.3407 | 112 | 98.2 | 5.4% | 7.3% | 118.048 | 103.5028 | 0.01 | 0.02 | -1454.52 | 132.5932 | 1.416% | 120.176 | 105.3686 | 0.01 | 0.02 | -1480.74 | 134.9834 | 1.552% | 141.6% | 0.9607% | 0.9748% | 0.989% | 1.003% | 1.017% | 1.031% | 1.046% | 1.06% | 1.074% | 1.088% | 1.102% | 1.116% | 1.13% | 1.145% | 1.159% | 1.173% | 1.187% | 1.201% | 1.215% | 1.229% | 0.00038906 | 0.00039479 | 0.00040052 | 0.00040624 | 0.00041197 | 0.0004177 | 0.00042343 | 0.00042915 | 0.00043488 | 0.00044061 | 0.00044633 | 0.00045206 | 0.00045779 | 0.00046351 | 0.00046924 | 0.00047497 | 0.0004807 | 0.00048642 | 0.00049215 | 0.00049788
| 10503127 | WIN011 | WIN | 17458167 | 17458163 | 0.36713 | 143.7996 | -38.3411 | 112 | 98.2 | 5.4% | 7.3% | 118.048 | 103.5028 | 0.01 | 0.02 | -1454.52 | 132.5932 | 1.416% | 120.176 | 105.3686 | 0.01 | 0.02 | -1480.74 | 134.9834 | 1.552% | 141.6% | 0.9607% | 0.9748% | 0.989% | 1.003% | 1.017% | 1.031% | 1.046% | 1.06% | 1.074% | 1.088% | 1.102% | 1.116% | 1.13% | 1.145% | 1.159% | 1.173% | 1.187% | 1.201% | 1.215% | 1.229% | 0.00038906 | 0.00039479 | 0.00040052 | 0.00040624 | 0.00041197 | 0.0004177 | 0.00042343 | 0.00042915 | 0.00043488 | 0.00044061 | 0.00044633 | 0.00045206 | 0.00045779 | 0.00046351 | 0.00046924 | 0.00047497 | 0.0004807 | 0.00048642 | 0.00049215 | 0.00049788
| 10503128 | WIN011 | WIN | 17458171 | 17458167 | 2.04 | 143.8009 | -38.3414 | 114 | 100 | 5.4% | 7.3% | 120.156 | 105.4 | 0.01 | 0.02 | -1475.6 | 134.912 | 1.417% | 122.322 | 107.3 | 0.01 | 0.02 | -1502.2 | 137.344 | 1.554% | 141.7% | 0.9608% | 0.975% | 0.9892% | 1.003% | 1.018% | 1.032% | 1.046% | 1.06% | 1.074% | 1.089% | 1.103% | 1.117% | 1.131% | 1.145% | 1.159% | 1.174% | 1.188% | 1.202% | 1.216% | 1.23% | 0.00038912 | 0.00039487 | 0.00040061 | 0.00040636 | 0.0004121 | 0.00041785 | 0.0004236 | 0.00042934 | 0.00043509 | 0.00044083 | 0.00044658 | 0.00045233 | 0.00045807 | 0.00046382 | 0.00046956 | 0.00047531 | 0.00048106 | 0.0004868 | 0.00049255 | 0.0004983
| 10503129 | WIN011 | WIN | 17458175 | 17458171 | 1.6475 | 143.8022 | -38.3418 | 114 | 100 | 5.4% | 7.3% | 120.156 | 105.4 | 0.01 | 0.02 | -1475.6 | 134.912 | 1.417% | 122.322 | 107.3 | 0.01 | 0.02 | -1502.2 | 137.344 | 1.554% | 141.7% | 0.9608% | 0.975% | 0.9892% | 1.003% | 1.018% | 1.032% | 1.046% | 1.06% | 1.074% | 1.089% | 1.103% | 1.117% | 1.131% | 1.145% | 1.159% | 1.174% | 1.188% | 1.202% | 1.216% | 1.23% | 0.00038912 | 0.00039487 | 0.00040061 | 0.00040636 | 0.0004121 | 0.00041785 | 0.0004236 | 0.00042934 | 0.00043509 | 0.00044083 | 0.00044658 | 0.00045233 | 0.00045807 | 0.00046382 | 0.00046956 | 0.00047531 | 0.00048106 | 0.0004868 | 0.00049255 | 0.0004983
| 10503130 | WIN011 | WIN | 17458179 | 17458175 | 1.0817 | 143.8035 | -38.3421 | 114 | 100 | 5.4% | 7.3% | 120.156 | 105.4 | 0.01 | 0.02 | -1475.6 | 134.912 | 1.417% | 122.322 | 107.3 | 0.01 | 0.02 | -1502.2 | 137.344 | 1.554% | 141.7% | 0.9608% | 0.975% | 0.9892% | 1.003% | 1.018% | 1.032% | 1.046% | 1.06% | 1.074% | 1.089% | 1.103% | 1.117% | 1.131% | 1.145% | 1.159% | 1.174% | 1.188% | 1.202% | 1.216% | 1.23% | 0.00038912 | 0.00039487 | 0.00040061 | 0.00040636 | 0.0004121 | 0.00041785 | 0.0004236 | 0.00042934 | 0.00043509 | 0.00044083 | 0.00044658 | 0.00045233 | 0.00045807 | 0.00046382 | 0.00046956 | 0.00047531 | 0.00048106 | 0.0004868 | 0.00049255 | 0.0004983
| 10503180 | WIN011 | WIN | 102623859 | 17458369 | 0.41168 | 143.8339 | -38.3167 | 112 | 98.7 | 5.4% | 7.3% | 118.048 | 104.0298 | 0.01 | 0.02 | -1401.82 | 132.0662 | 1.431% | 120.176 | 105.9051 | 0.01 | 0.02 | -1427.09 | 134.4469 | 1.573% | 143.1% | 0.9623% | 0.977% | 0.9916% | 1.006% | 1.021% | 1.036% | 1.05% | 1.065% | 1.08% | 1.094% | 1.109% | 1.124% | 1.138% | 1.153% | 1.168% | 1.182% | 1.197% | 1.212% | 1.226% | 1.241% | 0.00038971 | 0.00039565 | 0.00040159 | 0.00040754 | 0.00041348 | 0.00041942 | 0.00042536 | 0.00043131 | 0.00043725 | 0.00044319 | 0.00044913 | 0.00045507 | 0.00046102 | 0.00046696 | 0.0004729 | 0.00047884 | 0.00048479 | 0.00049073 | 0.00049667 | 0.00050261
| 10503181 | WIN011 | WIN | 17458369 | 17458373 | 0.8551 | 143.8341 | -38.3157 | 112 | 98.7 | 5.4% | 7.3% | 118.048 | 104.0298 | 0.01 | 0.02 | -1401.82 | 132.0662 | 1.431% | 120.176 | 105.9051 | 0.01 | 0.02 | -1427.09 | 134.4469 | 1.573% | 143.1% | 0.9623% | 0.977% | 0.9916% | 1.006% | 1.021% | 1.036% | 1.05% | 1.065% | 1.08% | 1.094% | 1.109% | 1.124% | 1.138% | 1.153% | 1.168% | 1.182% | 1.197% | 1.212% | 1.226% | 1.241% | 0.00038971 | 0.00039565 | 0.00040159 | 0.00040754 | 0.00041348 | 0.00041942 | 0.00042536 | 0.00043131 | 0.00043725 | 0.00044319 | 0.00044913 | 0.00045507 | 0.00046102 | 0.00046696 | 0.0004729 | 0.00047884 | 0.00048479 | 0.00049073 | 0.00049667 | 0.00050261
| 10503182 | WIN011 | WIN | 17458373 | 17458377 | 0.55458 | 143.8342 | -38.3147 | 112 | 98.7 | 5.4% | 7.3% | 118.048 | 104.0298 | 0.01 | 0.02 | -1401.82 | 132.0662 | 1.431% | 120.176 | 105.9051 | 0.01 | 0.02 | -1427.09 | 134.4469 | 1.573% | 143.1% | 0.9623% | 0.977% | 0.9916% | 1.006% | 1.021% | 1.036% | 1.05% | 1.065% | 1.08% | 1.094% | 1.109% | 1.124% | 1.138% | 1.153% | 1.168% | 1.182% | 1.197% | 1.212% | 1.226% | 1.241% | 0.00038971 | 0.00039565 | 0.00040159 | 0.00040754 | 0.00041348 | 0.00041942 | 0.00042536 | 0.00043131 | 0.00043725 | 0.00044319 | 0.00044913 | 0.00045507 | 0.00046102 | 0.00046696 | 0.0004729 | 0.00047884 | 0.00048479 | 0.00049073 | 0.00049667 | 0.00050261
| 10503183 | WIN011 | WIN | 17458377 | 17458381 | 0.17412 | 143.8344 | -38.3136 | 112 | 98.7 | 5.4% | 7.3% | 118.048 | 104.0298 | 0.01 | 0.02 | -1401.82 | 132.0662 | 1.431% | 120.176 | 105.9051 | 0.01 | 0.02 | -1427.09 | 134.4469 | 1.573% | 143.1% | 0.9623% | 0.977% | 0.9916% | 1.006% | 1.021% | 1.036% | 1.05% | 1.065% | 1.08% | 1.094% | 1.109% | 1.124% | 1.138% | 1.153% | 1.168% | 1.182% | 1.197% | 1.212% | 1.226% | 1.241% | 0.00038971 | 0.00039565 | 0.00040159 | 0.00040754 | 0.00041348 | 0.00041942 | 0.00042536 | 0.00043131 | 0.00043725 | 0.00044319 | 0.00044913 | 0.00045507 | 0.00046102 | 0.00046696 | 0.0004729 | 0.00047884 | 0.00048479 | 0.00049073 | 0.00049667 | 0.00050261
| 10503196 | WIN011 | WIN | 17458425 | 17459341 | 0.62953 | 143.8403 | -38.3067 | 112 | 98.7 | 5.4% | 7.3% | 118.048 | 104.0298 | 0.01 | 0.02 | -1401.82 | 132.0662 | 1.431% | 120.176 | 105.9051 | 0.01 | 0.02 | -1427.09 | 134.4469 | 1.573% | 143.1% | 0.9623% | 0.977% | 0.9916% | 1.006% | 1.021% | 1.036% | 1.05% | 1.065% | 1.08% | 1.094% | 1.109% | 1.124% | 1.138% | 1.153% | 1.168% | 1.182% | 1.197% | 1.212% | 1.226% | 1.241% | 0.00038971 | 0.00039565 | 0.00040159 | 0.00040754 | 0.00041348 | 0.00041942 | 0.00042536 | 0.00043131 | 0.00043725 | 0.00044319 | 0.00044913 | 0.00045507 | 0.00046102 | 0.00046696 | 0.0004729 | 0.00047884 | 0.00048479 | 0.00049073 | 0.00049667 | 0.00050261
| 10509240 | WND014 | WND | 17487988 | 17487997 | 2.3131 | 144.3669 | -37.2563 | 133 | 119 | 6.3% | 8.8% | 141.379 | 126.497 | 0.01 | 0.02 | -1488.2 | 156.261 | 1.563% | 142.709 | 129.472 | 0.01 | 0.02 | -1323.7 | 155.946 | 1.733% | 156.3% | 0.9757% | 0.9949% | 1.014% | 1.033% | 1.052% | 1.071% | 1.091% | 1.11% | 1.129% | 1.148% | 1.167% | 1.186% | 1.206% | 1.225% | 1.244% | 1.263% | 1.282% | 1.301% | 1.32% | 1.34% | 0.00039515 | 0.0004029 | 0.00041066 | 0.00041841 | 0.00042617 | 0.00043392 | 0.00044168 | 0.00044943 | 0.00045718 | 0.00046494 | 0.00047269 | 0.00048045 | 0.0004882 | 0.00049596 | 0.00050371 | 0.00051147 | 0.00051922 | 0.00052698 | 0.00053473 | 0.00054249
| 10509296 | BAN003 | BAN | 17488388 | 17488392 | 0.66445 | 144.1738 | -37.3431 | 139 | 123 | 6.3% | 8.8% | 147.757 | 130.749 | 0.01 | 0.02 | -1700.8 | 164.765 | 1.515% | 149.147 | 133.824 | 0.01 | 0.02 | -1532.3 | 164.47 | 1.662% | 151.5% | 0.9708% | 0.9883% | 1.006% | 1.023% | 1.041% | 1.058% | 1.076% | 1.093% | 1.111% | 1.128% | 1.146% | 1.163% | 1.181% | 1.198% | 1.216% | 1.233% | 1.251% | 1.268% | 1.286% | 1.304% | 0.00039316 | 0.00040025 | 0.00040734 | 0.00041443 | 0.00042152 | 0.00042861 | 0.00043571 | 0.0004428 | 0.00044989 | 0.00045698 | 0.00046407 | 0.00047116 | 0.00047826 | 0.00048535 | 0.00049244 | 0.00049953 | 0.00050662 | 0.00051371 | 0.0005208 | 0.0005279
| 10517240 | MNA034 | MNA | 17530221 | 177651649 | 0.33676 | 145.2012 | -36.5576 | 121 | 107 | 6.3% | 8.8% | 128.623 | 113.741 | 0.01 | 0.02 | -1488.2 | 143.505 | 1.512% | 129.833 | 116.416 | 0.01 | 0.02 | -1341.7 | 143.25 | 1.658% | 151.2% | 0.9705% | 0.988% | 1.005% | 1.023% | 1.04% | 1.058% | 1.075% | 1.092% | 1.11% | 1.127% | 1.145% | 1.162% | 1.18% | 1.197% | 1.214% | 1.232% | 1.249% | 1.267% | 1.284% | 1.302% | 0.00039305 | 0.0004001 | 0.00040716 | 0.00041421 | 0.00042127 | 0.00042832 | 0.00043538 | 0.00044243 | 0.00044949 | 0.00045654 | 0.0004636 | 0.00047065 | 0.00047771 | 0.00048476 | 0.00049182 | 0.00049887 | 0.00050593 | 0.00051298 | 0.00052004 | 0.00052709
| 10517843 | SHP014 | SHP | 17538781 | 17538785 | 0.78091 | 145.0744 | -36.4275 | 111 | 98.4 | 6.3% | 8.8% | 117.993 | 104.5992 | 0.01 | 0.02 | -1339.38 | 131.3868 | 1.522% | 119.103 | 107.0592 | 0.01 | 0.02 | -1204.38 | 131.1468 | 1.673% | 152.2% | 0.9715% | 0.9893% | 1.007% | 1.025% | 1.043% | 1.06% | 1.078% | 1.096% | 1.114% | 1.131% | 1.149% | 1.167% | 1.185% | 1.202% | 1.22% | 1.238% | 1.256% | 1.273% | 1.291% | 1.309% | 0.00039346 | 0.00040065 | 0.00040784 | 0.00041503 | 0.00042222 | 0.00042941 | 0.0004366 | 0.00044379 | 0.00045098 | 0.00045818 | 0.00046537 | 0.00047256 | 0.00047975 | 0.00048694 | 0.00049413 | 0.00050132 | 0.00050851 | 0.00051571 | 0.0005229 | 0.00053009
| 10518222 | MNA034 | MNA | 17544104 | 63130713 | 0.97986 | 145.216 | -36.6702 | 127 | 111 | 6.3% | 8.8% | 135.001 | 117.993 | 0.01 | 0.02 | -1700.8 | 152.009 | 1.47% | 136.271 | 120.768 | 0.01 | 0.02 | -1550.3 | 151.774 | 1.598% | 147% | 0.9663% | 0.9823% | 0.9983% | 1.014% | 1.03% | 1.046% | 1.062% | 1.078% | 1.094% | 1.11% | 1.126% | 1.142% | 1.158% | 1.174% | 1.19% | 1.206% | 1.222% | 1.238% | 1.254% | 1.27% | 0.00039132 | 0.0003978 | 0.00040428 | 0.00041076 | 0.00041724 | 0.00042372 | 0.0004302 | 0.00043668 | 0.00044315 | 0.00044963 | 0.00045611 | 0.00046259 | 0.00046907 | 0.00047555 | 0.00048203 | 0.00048851 | 0.00049499 | 0.00050147 | 0.00050795 | 0.00051443
| 10518814 | SHTSMNA | KYM | 17551297 | 17551301 | 0.34594 | 145.3755 | -36.3478 | 113 | 99.7 | 6.3% | 8.8% | 120.119 | 105.9811 | 0.01 | 0.02 | -1413.79 | 134.2569 | 1.504% | 121.249 | 108.4736 | 0.01 | 0.02 | -1277.54 | 134.0244 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039269 | 0.00039962 | 0.00040656 | 0.00041349 | 0.00042043 | 0.00042737 | 0.0004343 | 0.00044124 | 0.00044817 | 0.00045511 | 0.00046204 | 0.00046898 | 0.00047591 | 0.00048285 | 0.00048978 | 0.00049672 | 0.00050366 | 0.00051059 | 0.00051753 | 0.00052446
| 10518815 | SHTSSHP | KYM | 17551301 | 17551305 | 0.30255 | 145.3754 | -36.3484 | 113 | 99.7 | 6.3% | 8.8% | 120.119 | 105.9811 | 0.01 | 0.02 | -1413.79 | 134.2569 | 1.504% | 121.249 | 108.4736 | 0.01 | 0.02 | -1277.54 | 134.0244 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.072% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.192% | 1.209% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039269 | 0.00039962 | 0.00040656 | 0.00041349 | 0.00042043 | 0.00042737 | 0.0004343 | 0.00044124 | 0.00044817 | 0.00045511 | 0.00046204 | 0.00046898 | 0.00047591 | 0.00048285 | 0.00048978 | 0.00049672 | 0.00050366 | 0.00051059 | 0.00051753 | 0.00052446
| 10522097 | RCT014 | RCTS | 17587246 | 17587250 | 0.59501 | 142.2836 | -34.3965 | 110 | 95.6 | 6.3% | 8.8% | 116.93 | 101.6228 | 0.01 | 0.02 | -1530.72 | 132.2372 | 1.453% | 118.03 | 104.0128 | 0.01 | 0.02 | -1401.72 | 132.0472 | 1.573% | 145.3% | 0.9645% | 0.9799% | 0.9953% | 1.011% | 1.026% | 1.041% | 1.057% | 1.072% | 1.088% | 1.103% | 1.118% | 1.134% | 1.149% | 1.165% | 1.18% | 1.195% | 1.211% | 1.226% | 1.242% | 1.257% | 0.00039059 | 0.00039682 | 0.00040306 | 0.0004093 | 0.00041553 | 0.00042177 | 0.000428 | 0.00043424 | 0.00044047 | 0.00044671 | 0.00045294 | 0.00045918 | 0.00046542 | 0.00047165 | 0.00047789 | 0.00048412 | 0.00049036 | 0.00049659 | 0.00050283 | 0.00050906
| 10522099 | RCT014 | RCTS | 17587254 | 17587258 | 0.89478 | 142.2813 | -34.3924 | 110 | 95.6 | 6.3% | 8.8% | 116.93 | 101.6228 | 0.01 | 0.02 | -1530.72 | 132.2372 | 1.453% | 118.03 | 104.0128 | 0.01 | 0.02 | -1401.72 | 132.0472 | 1.573% | 145.3% | 0.9645% | 0.9799% | 0.9953% | 1.011% | 1.026% | 1.041% | 1.057% | 1.072% | 1.088% | 1.103% | 1.118% | 1.134% | 1.149% | 1.165% | 1.18% | 1.195% | 1.211% | 1.226% | 1.242% | 1.257% | 0.00039059 | 0.00039682 | 0.00040306 | 0.0004093 | 0.00041553 | 0.00042177 | 0.000428 | 0.00043424 | 0.00044047 | 0.00044671 | 0.00045294 | 0.00045918 | 0.00046542 | 0.00047165 | 0.00047789 | 0.00048412 | 0.00049036 | 0.00049659 | 0.00050283 | 0.00050906
| 10522100 | RCT014 | RCTS | 17587258 | 17587262 | 0.65266 | 142.2803 | -34.3912 | 110 | 95.6 | 6.3% | 8.8% | 116.93 | 101.6228 | 0.01 | 0.02 | -1530.72 | 132.2372 | 1.453% | 118.03 | 104.0128 | 0.01 | 0.02 | -1401.72 | 132.0472 | 1.573% | 145.3% | 0.9645% | 0.9799% | 0.9953% | 1.011% | 1.026% | 1.041% | 1.057% | 1.072% | 1.088% | 1.103% | 1.118% | 1.134% | 1.149% | 1.165% | 1.18% | 1.195% | 1.211% | 1.226% | 1.242% | 1.257% | 0.00039059 | 0.00039682 | 0.00040306 | 0.0004093 | 0.00041553 | 0.00042177 | 0.000428 | 0.00043424 | 0.00044047 | 0.00044671 | 0.00045294 | 0.00045918 | 0.00046542 | 0.00047165 | 0.00047789 | 0.00048412 | 0.00049036 | 0.00049659 | 0.00050283 | 0.00050906
| 10522151 | STN021 | STN | 17587843 | 17587847 | 0.2179 | 145.4188 | -36.4205 | 116 | 101 | 6.3% | 8.8% | 123.308 | 107.363 | 0.01 | 0.02 | -1594.5 | 139.253 | 1.458% | 124.468 | 109.888 | 0.01 | 0.02 | -1458 | 139.048 | 1.581% | 145.8% | 0.965% | 0.9806% | 0.9962% | 1.012% | 1.027% | 1.043% | 1.059% | 1.074% | 1.09% | 1.105% | 1.121% | 1.137% | 1.152% | 1.168% | 1.183% | 1.199% | 1.214% | 1.23% | 1.246% | 1.261% | 0.00039082 | 0.00039713 | 0.00040345 | 0.00040976 | 0.00041607 | 0.00042238 | 0.0004287 | 0.00043501 | 0.00044132 | 0.00044763 | 0.00045395 | 0.00046026 | 0.00046657 | 0.00047288 | 0.0004792 | 0.00048551 | 0.00049182 | 0.00049814 | 0.00050445 | 0.00051076
| 10522627 | SHL004 | SHL | 17592562 | 17592566 | 1.124 | 143.4559 | -35.2572 | 106 | 94.1 | 6.3% | 8.8% | 112.678 | 100.0283 | 0.01 | 0.02 | -1264.97 | 125.3277 | 1.528% | 113.738 | 102.3808 | 0.01 | 0.02 | -1135.72 | 125.0952 | 1.681% | 152.8% | 0.9721% | 0.9901% | 1.008% | 1.026% | 1.044% | 1.062% | 1.08% | 1.098% | 1.116% | 1.134% | 1.152% | 1.17% | 1.188% | 1.206% | 1.224% | 1.241% | 1.259% | 1.277% | 1.295% | 1.313% | 0.0003937 | 0.00040097 | 0.00040824 | 0.00041551 | 0.00042278 | 0.00043005 | 0.00043732 | 0.00044459 | 0.00045186 | 0.00045914 | 0.00046641 | 0.00047368 | 0.00048095 | 0.00048822 | 0.00049549 | 0.00050276 | 0.00051003 | 0.00051731 | 0.00052458 | 0.00053185
| 10523686 | MNA034 | MNA | 17607074 | 17607079 | 0.52726 | 145.2945 | -36.5001 | 117 | 103 | 6.3% | 8.8% | 124.371 | 109.489 | 0.01 | 0.02 | -1488.2 | 139.253 | 1.495% | 125.541 | 112.064 | 0.01 | 0.02 | -1347.7 | 139.018 | 1.634% | 149.5% | 0.9688% | 0.9857% | 1.002% | 1.019% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.12% | 1.137% | 1.154% | 1.171% | 1.188% | 1.205% | 1.221% | 1.238% | 1.255% | 1.272% | 1.289% | 0.00039235 | 0.00039917 | 0.00040599 | 0.00041281 | 0.00041963 | 0.00042646 | 0.00043328 | 0.0004401 | 0.00044692 | 0.00045374 | 0.00046057 | 0.00046739 | 0.00047421 | 0.00048103 | 0.00048785 | 0.00049468 | 0.0005015 | 0.00050832 | 0.00051514 | 0.00052196
| 10524876 | STN011 | STN | 17628385 | 17628431 | 0.466 | 145.7813 | -36.4183 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10524879 | STN011 | STN | 17628398 | 17628403 | 0.17451 | 145.7814 | -36.4134 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10524880 | STN011 | STN | 17628398 | 17628436 | 1.0356 | 145.7807 | -36.4141 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10524881 | STN011 | STN | 195039898 | 17628398 | 0.37927 | 145.782 | -36.414 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10524882 | STN011 | STN | 17628403 | 17628407 | 0.75044 | 145.7817 | -36.4119 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10524884 | STN011 | STN | 17628407 | 17628421 | 1.5806 | 145.7827 | -36.4101 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10524886 | STN011 | STN | 17628436 | 17628440 | 0.56164 | 145.7795 | -36.4139 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10524929 | MNASTN | MNA | 17628871 | 17628875 | 0.83038 | 145.3693 | -36.3861 | 113 | 99.3 | 6.3% | 8.8% | 120.119 | 105.5559 | 0.01 | 0.02 | -1456.31 | 134.6821 | 1.489% | 121.249 | 108.0384 | 0.01 | 0.02 | -1321.06 | 134.4596 | 1.624% | 148.9% | 0.9682% | 0.9848% | 1.001% | 1.018% | 1.035% | 1.051% | 1.068% | 1.085% | 1.101% | 1.118% | 1.134% | 1.151% | 1.168% | 1.184% | 1.201% | 1.218% | 1.234% | 1.251% | 1.267% | 1.284% | 0.00039208 | 0.00039881 | 0.00040555 | 0.00041228 | 0.00041901 | 0.00042575 | 0.00043248 | 0.00043921 | 0.00044594 | 0.00045268 | 0.00045941 | 0.00046614 | 0.00047288 | 0.00047961 | 0.00048634 | 0.00049307 | 0.00049981 | 0.00050654 | 0.00051327 | 0.00052001
| 10525571 | CHA006 | CHA | 17640632 | 17640636 | 0.40308 | 144.1303 | -36.0404 | 101 | 90 | 6.3% | 8.8% | 107.363 | 95.67 | 0.01 | 0.02 | -1169.3 | 119.056 | 1.544% | 108.373 | 97.92 | 0.01 | 0.02 | -1045.3 | 118.826 | 1.705% | 154.4% | 0.9738% | 0.9923% | 1.011% | 1.029% | 1.048% | 1.066% | 1.085% | 1.103% | 1.122% | 1.14% | 1.159% | 1.177% | 1.196% | 1.214% | 1.233% | 1.251% | 1.27% | 1.288% | 1.307% | 1.325% | 0.00039437 | 0.00040186 | 0.00040936 | 0.00041685 | 0.00042435 | 0.00043184 | 0.00043934 | 0.00044683 | 0.00045433 | 0.00046182 | 0.00046932 | 0.00047681 | 0.00048431 | 0.0004918 | 0.0004993 | 0.00050679 | 0.00051429 | 0.00052178 | 0.00052928 | 0.00053677
| 10526831 | CHA005 | CHA | 17669546 | 17673670 | 0.1876 | 144.2355 | -35.9208 | 101 | 90 | 6.3% | 8.8% | 107.363 | 95.67 | 0.01 | 0.02 | -1169.3 | 119.056 | 1.544% | 108.373 | 97.92 | 0.01 | 0.02 | -1045.3 | 118.826 | 1.705% | 154.4% | 0.9738% | 0.9923% | 1.011% | 1.029% | 1.048% | 1.066% | 1.085% | 1.103% | 1.122% | 1.14% | 1.159% | 1.177% | 1.196% | 1.214% | 1.233% | 1.251% | 1.27% | 1.288% | 1.307% | 1.325% | 0.00039437 | 0.00040186 | 0.00040936 | 0.00041685 | 0.00042435 | 0.00043184 | 0.00043934 | 0.00044683 | 0.00045433 | 0.00046182 | 0.00046932 | 0.00047681 | 0.00048431 | 0.0004918 | 0.0004993 | 0.00050679 | 0.00051429 | 0.00052178 | 0.00052928 | 0.00053677
| 10526950 | NKA002 | RCTS | 132832512 | 17671414 | 0.23931 | 145.284 | -36.093 | 116 | 102 | 6.3% | 8.8% | 123.308 | 108.426 | 0.01 | 0.02 | -1488.2 | 138.19 | 1.491% | 124.468 | 110.976 | 0.01 | 0.02 | -1349.2 | 137.96 | 1.628% | 149.1% | 0.9684% | 0.9851% | 1.002% | 1.018% | 1.035% | 1.052% | 1.069% | 1.085% | 1.102% | 1.119% | 1.135% | 1.152% | 1.169% | 1.185% | 1.202% | 1.219% | 1.236% | 1.252% | 1.269% | 1.286% | 0.00039217 | 0.00039894 | 0.0004057 | 0.00041246 | 0.00041923 | 0.00042599 | 0.00043275 | 0.00043952 | 0.00044628 | 0.00045304 | 0.00045981 | 0.00046657 | 0.00047334 | 0.0004801 | 0.00048686 | 0.00049363 | 0.00050039 | 0.00050715 | 0.00051392 | 0.00052068
| 10527087 | RCT011 | RCTS | 17780253 | 17673586 | 0.24529 | 142.2254 | -34.2751 | 111 | 96.6 | 6.3% | 8.8% | 117.993 | 102.6858 | 0.01 | 0.02 | -1530.72 | 133.3002 | 1.457% | 119.103 | 105.1008 | 0.01 | 0.02 | -1400.22 | 133.1052 | 1.579% | 145.7% | 0.9649% | 0.9804% | 0.996% | 1.011% | 1.027% | 1.043% | 1.058% | 1.074% | 1.089% | 1.105% | 1.12% | 1.136% | 1.151% | 1.167% | 1.182% | 1.198% | 1.213% | 1.229% | 1.245% | 1.26% | 0.00039076 | 0.00039705 | 0.00040334 | 0.00040964 | 0.00041593 | 0.00042222 | 0.00042851 | 0.0004348 | 0.0004411 | 0.00044739 | 0.00045368 | 0.00045997 | 0.00046627 | 0.00047256 | 0.00047885 | 0.00048514 | 0.00049144 | 0.00049773 | 0.00050402 | 0.00051031
| 10527460 | SHP014 | SHP | 17681399 | 17681394 | 0.25715 | 145.1212 | -36.441 | 112 | 98.9 | 6.3% | 8.8% | 119.056 | 105.1307 | 0.01 | 0.02 | -1392.53 | 132.9813 | 1.507% | 120.176 | 107.6032 | 0.01 | 0.02 | -1257.28 | 132.7488 | 1.65% | 150.7% | 0.97% | 0.9872% | 1.004% | 1.022% | 1.039% | 1.056% | 1.073% | 1.091% | 1.108% | 1.125% | 1.142% | 1.16% | 1.177% | 1.194% | 1.211% | 1.228% | 1.246% | 1.263% | 1.28% | 1.297% | 0.00039282 | 0.0003998 | 0.00040678 | 0.00041376 | 0.00042073 | 0.00042771 | 0.00043469 | 0.00044167 | 0.00044865 | 0.00045563 | 0.00046261 | 0.00046959 | 0.00047657 | 0.00048355 | 0.00049053 | 0.0004975 | 0.00050448 | 0.00051146 | 0.00051844 | 0.00052542
| 10530492 | KYM004 | KYM | 17723454 | 17723458 | 1.2985 | 145.0284 | -36.2569 | 108 | 95.3 | 6.3% | 8.8% | 114.804 | 101.3039 | 0.01 | 0.02 | -1350.01 | 128.3041 | 1.504% | 115.884 | 103.6864 | 0.01 | 0.02 | -1219.76 | 128.0816 | 1.646% | 150.4% | 0.9697% | 0.9868% | 1.004% | 1.021% | 1.038% | 1.055% | 1.073% | 1.09% | 1.107% | 1.124% | 1.141% | 1.158% | 1.175% | 1.193% | 1.21% | 1.227% | 1.244% | 1.261% | 1.278% | 1.295% | 0.00039271 | 0.00039965 | 0.00040659 | 0.00041353 | 0.00042047 | 0.00042742 | 0.00043436 | 0.0004413 | 0.00044824 | 0.00045518 | 0.00046212 | 0.00046907 | 0.00047601 | 0.00048295 | 0.00048989 | 0.00049683 | 0.00050377 | 0.00051072 | 0.00051766 | 0.0005246
| 10532216 | SHN011 | SHN | 17747154 | 17747158 | 0.1383 | 145.4245 | -36.3 | 113 | 99.6 | 6.3% | 8.8% | 120.119 | 105.8748 | 0.01 | 0.02 | -1424.42 | 134.3632 | 1.5% | 121.249 | 108.3648 | 0.01 | 0.02 | -1288.42 | 134.1332 | 1.64% | 150% | 0.9693% | 0.9863% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039253 | 0.00039942 | 0.0004063 | 0.00041318 | 0.00042007 | 0.00042695 | 0.00043383 | 0.00044072 | 0.0004476 | 0.00045449 | 0.00046137 | 0.00046825 | 0.00047514 | 0.00048202 | 0.0004889 | 0.00049579 | 0.00050267 | 0.00050956 | 0.00051644 | 0.00052332
| 10532256 | STL007 | STL | 17748045 | 17748050 | 1.1777 | 143.124 | -37.0079 | 121 | 106 | 6.3% | 8.8% | 128.623 | 112.678 | 0.01 | 0.02 | -1594.5 | 144.568 | 1.478% | 129.833 | 115.328 | 0.01 | 0.02 | -1450.5 | 144.338 | 1.609% | 147.8% | 0.9671% | 0.9833% | 0.9996% | 1.016% | 1.032% | 1.048% | 1.065% | 1.081% | 1.097% | 1.113% | 1.13% | 1.146% | 1.162% | 1.178% | 1.195% | 1.211% | 1.227% | 1.243% | 1.26% | 1.276% | 0.00039164 | 0.00039822 | 0.00040481 | 0.00041139 | 0.00041798 | 0.00042456 | 0.00043114 | 0.00043773 | 0.00044431 | 0.0004509 | 0.00045748 | 0.00046407 | 0.00047065 | 0.00047724 | 0.00048382 | 0.00049041 | 0.00049699 | 0.00050358 | 0.00051016 | 0.00051675
| 10533376 | BSPBBD | BBD | 17776213 | 17764875 | 1.1897 | 142.9903 | -34.7156 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10534019 | BSPBBD | BBD | 17776200 | 17776196 | 0.19633 | 142.9845 | -34.7159 | 115 | 102 | 6.3% | 8.8% | 122.245 | 108.426 | 0.01 | 0.02 | -1381.9 | 136.064 | 1.524% | 123.395 | 110.976 | 0.01 | 0.02 | -1241.9 | 135.814 | 1.676% | 152.4% | 0.9718% | 0.9896% | 1.007% | 1.025% | 1.043% | 1.061% | 1.079% | 1.097% | 1.114% | 1.132% | 1.15% | 1.168% | 1.186% | 1.204% | 1.221% | 1.239% | 1.257% | 1.275% | 1.293% | 1.311% | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075
| 10534244 | RCT011 | RCTS | 95332489 | 17780233 | 1.2288 | 142.2197 | -34.2609 | 112 | 97.3 | 6.3% | 8.8% | 119.056 | 103.4299 | 0.01 | 0.02 | -1562.61 | 134.6821 | 1.452% | 120.176 | 105.8624 | 0.01 | 0.02 | -1431.36 | 134.4896 | 1.571% | 145.2% | 0.9643% | 0.9797% | 0.9951% | 1.01% | 1.026% | 1.041% | 1.056% | 1.072% | 1.087% | 1.103% | 1.118% | 1.133% | 1.149% | 1.164% | 1.179% | 1.195% | 1.21% | 1.225% | 1.241% | 1.256% | 0.00039054 | 0.00039676 | 0.00040298 | 0.0004092 | 0.00041542 | 0.00042164 | 0.00042786 | 0.00043408 | 0.0004403 | 0.00044651 | 0.00045273 | 0.00045895 | 0.00046517 | 0.00047139 | 0.00047761 | 0.00048383 | 0.00049005 | 0.00049627 | 0.00050249 | 0.00050871
| 10534245 | RCT011 | RCTS | 17780233 | 17780237 | 0.25866 | 142.2195 | -34.2598 | 112 | 97.3 | 6.3% | 8.8% | 119.056 | 103.4299 | 0.01 | 0.02 | -1562.61 | 134.6821 | 1.452% | 120.176 | 105.8624 | 0.01 | 0.02 | -1431.36 | 134.4896 | 1.571% | 145.2% | 0.9643% | 0.9797% | 0.9951% | 1.01% | 1.026% | 1.041% | 1.056% | 1.072% | 1.087% | 1.103% | 1.118% | 1.133% | 1.149% | 1.164% | 1.179% | 1.195% | 1.21% | 1.225% | 1.241% | 1.256% | 0.00039054 | 0.00039676 | 0.00040298 | 0.0004092 | 0.00041542 | 0.00042164 | 0.00042786 | 0.00043408 | 0.0004403 | 0.00044651 | 0.00045273 | 0.00045895 | 0.00046517 | 0.00047139 | 0.00047761 | 0.00048383 | 0.00049005 | 0.00049627 | 0.00050249 | 0.00050871
| 10534246 | RCT011 | RCTS | 17780237 | 17780241 | 0.49689 | 142.2193 | -34.2587 | 112 | 97.3 | 6.3% | 8.8% | 119.056 | 103.4299 | 0.01 | 0.02 | -1562.61 | 134.6821 | 1.452% | 120.176 | 105.8624 | 0.01 | 0.02 | -1431.36 | 134.4896 | 1.571% | 145.2% | 0.9643% | 0.9797% | 0.9951% | 1.01% | 1.026% | 1.041% | 1.056% | 1.072% | 1.087% | 1.103% | 1.118% | 1.133% | 1.149% | 1.164% | 1.179% | 1.195% | 1.21% | 1.225% | 1.241% | 1.256% | 0.00039054 | 0.00039676 | 0.00040298 | 0.0004092 | 0.00041542 | 0.00042164 | 0.00042786 | 0.00043408 | 0.0004403 | 0.00044651 | 0.00045273 | 0.00045895 | 0.00046517 | 0.00047139 | 0.00047761 | 0.00048383 | 0.00049005 | 0.00049627 | 0.00050249 | 0.00050871
| 10534247 | RCT011 | RCTS | 95332546 | 17780253 | 0.2916 | 142.2259 | -34.2762 | 111 | 96.6 | 6.3% | 8.8% | 117.993 | 102.6858 | 0.01 | 0.02 | -1530.72 | 133.3002 | 1.457% | 119.103 | 105.1008 | 0.01 | 0.02 | -1400.22 | 133.1052 | 1.579% | 145.7% | 0.9649% | 0.9804% | 0.996% | 1.011% | 1.027% | 1.043% | 1.058% | 1.074% | 1.089% | 1.105% | 1.12% | 1.136% | 1.151% | 1.167% | 1.182% | 1.198% | 1.213% | 1.229% | 1.245% | 1.26% | 0.00039076 | 0.00039705 | 0.00040334 | 0.00040964 | 0.00041593 | 0.00042222 | 0.00042851 | 0.0004348 | 0.0004411 | 0.00044739 | 0.00045368 | 0.00045997 | 0.00046627 | 0.00047256 | 0.00047885 | 0.00048514 | 0.00049144 | 0.00049773 | 0.00050402 | 0.00051031
| 10535259 | KYM001 | KYM | 17794851 | 140042432 | 1.5901 | 144.9601 | -36.3553 | 109 | 96.3 | 6.3% | 8.8% | 115.867 | 102.3669 | 0.01 | 0.02 | -1350.01 | 129.3671 | 1.509% | 116.957 | 104.7744 | 0.01 | 0.02 | -1218.26 | 129.1396 | 1.653% | 150.9% | 0.9702% | 0.9875% | 1.005% | 1.022% | 1.039% | 1.057% | 1.074% | 1.091% | 1.109% | 1.126% | 1.143% | 1.16% | 1.178% | 1.195% | 1.212% | 1.23% | 1.247% | 1.264% | 1.282% | 1.299% | 0.0003929 | 0.00039991 | 0.00040691 | 0.00041392 | 0.00042092 | 0.00042793 | 0.00043494 | 0.00044194 | 0.00044895 | 0.00045595 | 0.00046296 | 0.00046997 | 0.00047697 | 0.00048398 | 0.00049098 | 0.00049799 | 0.000505 | 0.000512 | 0.00051901 | 0.00052601
| 10537497 | WIN011 | WIN | 17824161 | 17824165 | 0.34236 | 143.8006 | -38.3185 | 110 | 97.3 | 5.4% | 7.3% | 115.94 | 102.5542 | 0.01 | 0.02 | -1338.58 | 129.3258 | 1.444% | 118.03 | 104.4029 | 0.01 | 0.02 | -1362.71 | 131.6571 | 1.589% | 144.4% | 0.9636% | 0.9786% | 0.9937% | 1.009% | 1.024% | 1.039% | 1.054% | 1.069% | 1.084% | 1.099% | 1.114% | 1.13% | 1.145% | 1.16% | 1.175% | 1.19% | 1.205% | 1.22% | 1.235% | 1.25% | 0.00039022 | 0.00039633 | 0.00040244 | 0.00040855 | 0.00041467 | 0.00042078 | 0.00042689 | 0.000433 | 0.00043911 | 0.00044523 | 0.00045134 | 0.00045745 | 0.00046356 | 0.00046967 | 0.00047579 | 0.0004819 | 0.00048801 | 0.00049412 | 0.00050023 | 0.00050635
| 10538355 | KYM004 | KYM | 17837804 | 17837808 | 0.27419 | 145.2053 | -36.1472 | 113 | 99.5 | 6.3% | 8.8% | 120.119 | 105.7685 | 0.01 | 0.02 | -1435.05 | 134.4695 | 1.496% | 121.249 | 108.256 | 0.01 | 0.02 | -1299.3 | 134.242 | 1.635% | 149.6% | 0.9689% | 0.9858% | 1.003% | 1.02% | 1.036% | 1.053% | 1.07% | 1.087% | 1.104% | 1.121% | 1.138% | 1.154% | 1.171% | 1.188% | 1.205% | 1.222% | 1.239% | 1.256% | 1.273% | 1.289% | 0.00039238 | 0.00039921 | 0.00040605 | 0.00041288 | 0.00041971 | 0.00042654 | 0.00043338 | 0.00044021 | 0.00044704 | 0.00045387 | 0.00046071 | 0.00046754 | 0.00047437 | 0.0004812 | 0.00048804 | 0.00049487 | 0.0005017 | 0.00050854 | 0.00051537 | 0.0005222
| 10540707 | RCT011 | RCTS | 41070665 | 95332546 | 0.76092 | 142.2265 | -34.2772 | 111 | 96.6 | 6.3% | 8.8% | 117.993 | 102.6858 | 0.01 | 0.02 | -1530.72 | 133.3002 | 1.457% | 119.103 | 105.1008 | 0.01 | 0.02 | -1400.22 | 133.1052 | 1.579% | 145.7% | 0.9649% | 0.9804% | 0.996% | 1.011% | 1.027% | 1.043% | 1.058% | 1.074% | 1.089% | 1.105% | 1.12% | 1.136% | 1.151% | 1.167% | 1.182% | 1.198% | 1.213% | 1.229% | 1.245% | 1.26% | 0.00039076 | 0.00039705 | 0.00040334 | 0.00040964 | 0.00041593 | 0.00042222 | 0.00042851 | 0.0004348 | 0.0004411 | 0.00044739 | 0.00045368 | 0.00045997 | 0.00046627 | 0.00047256 | 0.00047885 | 0.00048514 | 0.00049144 | 0.00049773 | 0.00050402 | 0.00051031
| 10541616 | SHL004 | SHL | 157074000 | 42236359 | 0.78571 | 143.447 | -35.2206 | 107 | 95.1 | 6.3% | 8.8% | 113.741 | 101.0913 | 0.01 | 0.02 | -1264.97 | 126.3907 | 1.533% | 114.811 | 103.4688 | 0.01 | 0.02 | -1134.22 | 126.1532 | 1.689% | 153.3% | 0.9726% | 0.9908% | 1.009% | 1.027% | 1.045% | 1.063% | 1.081% | 1.1% | 1.118% | 1.136% | 1.154% | 1.172% | 1.19% | 1.208% | 1.226% | 1.245% | 1.263% | 1.281% | 1.299% | 1.317% | 0.0003939 | 0.00040124 | 0.00040858 | 0.00041592 | 0.00042326 | 0.0004306 | 0.00043794 | 0.00044528 | 0.00045262 | 0.00045996 | 0.0004673 | 0.00047464 | 0.00048198 | 0.00048932 | 0.00049666 | 0.000504 | 0.00051134 | 0.00051868 | 0.00052602 | 0.00053336
| 10543005 | MRO005 | MRO | 52301478 | 52301488 | 1.1256 | 143.7192 | -36.8467 | 106 | 95.2 | 6.3% | 8.8% | 112.678 | 101.1976 | 0.01 | 0.02 | -1148.04 | 124.1584 | 1.582% | 113.738 | 103.5776 | 0.01 | 0.02 | -1016.04 | 123.8984 | 1.762% | 158.2% | 0.9776% | 0.9974% | 1.017% | 1.037% | 1.057% | 1.077% | 1.096% | 1.116% | 1.136% | 1.156% | 1.175% | 1.195% | 1.215% | 1.235% | 1.255% | 1.274% | 1.294% | 1.314% | 1.334% | 1.354% | 0.00039592 | 0.00040393 | 0.00041194 | 0.00041995 | 0.00042796 | 0.00043598 | 0.00044399 | 0.000452 | 0.00046001 | 0.00046802 | 0.00047604 | 0.00048405 | 0.00049206 | 0.00050007 | 0.00050808 | 0.00051609 | 0.00052411 | 0.00053212 | 0.00054013 | 0.00054814
| 10551476 | STN024 | STN | 122260734 | 194880973 | 0.25998 | 145.7832 | -36.4119 | 118 | 104 | 6.3% | 8.8% | 125.434 | 110.552 | 0.01 | 0.02 | -1488.2 | 140.316 | 1.5% | 126.614 | 113.152 | 0.01 | 0.02 | -1346.2 | 140.076 | 1.64% | 150% | 0.9692% | 0.9862% | 1.003% | 1.02% | 1.037% | 1.054% | 1.071% | 1.088% | 1.105% | 1.122% | 1.139% | 1.156% | 1.173% | 1.19% | 1.207% | 1.224% | 1.241% | 1.258% | 1.275% | 1.292% | 0.00039252 | 0.0003994 | 0.00040628 | 0.00041316 | 0.00042004 | 0.00042692 | 0.0004338 | 0.00044068 | 0.00044756 | 0.00045444 | 0.00046132 | 0.0004682 | 0.00047508 | 0.00048197 | 0.00048885 | 0.00049573 | 0.00050261 | 0.00050949 | 0.00051637 | 0.00052325
| 10553394 | STN012 | STN | 138130888 | 138130883 | 0.814 | 145.4074 | -36.4278 | 117 | 102 | 6.3% | 8.8% | 124.371 | 108.426 | 0.01 | 0.02 | -1594.5 | 140.316 | 1.462% | 125.541 | 110.976 | 0.01 | 0.02 | -1456.5 | 140.106 | 1.586% | 146.2% | 0.9654% | 0.9812% | 0.9969% | 1.013% | 1.028% | 1.044% | 1.06% | 1.075% | 1.091% | 1.107% | 1.123% | 1.138% | 1.154% | 1.17% | 1.186% | 1.201% | 1.217% | 1.233% | 1.248% | 1.264% | 0.00039098 | 0.00039735 | 0.00040372 | 0.00041008 | 0.00041645 | 0.00042282 | 0.00042919 | 0.00043555 | 0.00044192 | 0.00044829 | 0.00045465 | 0.00046102 | 0.00046739 | 0.00047376 | 0.00048012 | 0.00048649 | 0.00049286 | 0.00049922 | 0.00050559 | 0.00051196
| 10554676 | MRO008 | MRO | 154141526 | 154141539 | 0.16801 | 143.4793 | -37.0371 | 115 | 103 | 6.3% | 8.8% | 122.245 | 109.489 | 0.01 | 0.02 | -1275.6 | 135.001 | 1.568% | 123.395 | 112.064 | 0.01 | 0.02 | -1133.1 | 134.726 | 1.741% | 156.8% | 0.9762% | 0.9955% | 1.015% | 1.034% | 1.053% | 1.073% | 1.092% | 1.111% | 1.131% | 1.15% | 1.169% | 1.189% | 1.208% | 1.227% | 1.247% | 1.266% | 1.285% | 1.305% | 1.324% | 1.343% | 0.00039535 | 0.00040317 | 0.000411 | 0.00041882 | 0.00042664 | 0.00043446 | 0.00044229 | 0.00045011 | 0.00045793 | 0.00046576 | 0.00047358 | 0.0004814 | 0.00048922 | 0.00049705 | 0.00050487 | 0.00051269 | 0.00052052 | 0.00052834 | 0.00053616 | 0.00054398
| 10554851 | ECA010 | ECA | 154782467 | 154782487 | 0.60178 | 144.7327 | -36.1272 | 101 | 90.5 | 6.3% | 8.8% | 107.363 | 96.2015 | 0.01 | 0.02 | -1116.15 | 118.5245 | 1.57% | 108.373 | 98.464 | 0.01 | 0.02 | -990.9 | 118.282 | 1.744% | 157% | 0.9764% | 0.9958% | 1.015% | 1.035% | 1.054% | 1.073% | 1.093% | 1.112% | 1.132% | 1.151% | 1.17% | 1.19% | 1.209% | 1.228% | 1.248% | 1.267% | 1.287% | 1.306% | 1.325% | 1.345% | 0.00039544 | 0.00040329 | 0.00041114 | 0.00041899 | 0.00042685 | 0.0004347 | 0.00044255 | 0.0004504 | 0.00045825 | 0.00046611 | 0.00047396 | 0.00048181 | 0.00048966 | 0.00049751 | 0.00050537 | 0.00051322 | 0.00052107 | 0.00052892 | 0.00053677 | 0.00054463
| 10556318 | BMH003 | BMH | 161364362 | 161364370 | 0.36746 | 144.1984 | -37.7326 | 138 | 121 | 5.4% | 7.3% | 145.452 | 127.534 | 0.01 | 0.02 | -1791.8 | 163.37 | 1.416% | 148.074 | 129.833 | 0.01 | 0.02 | -1824.1 | 166.315 | 1.552% | 141.6% | 0.9607% | 0.9749% | 0.989% | 1.003% | 1.017% | 1.031% | 1.046% | 1.06% | 1.074% | 1.088% | 1.102% | 1.116% | 1.13% | 1.145% | 1.159% | 1.173% | 1.187% | 1.201% | 1.215% | 1.229% | 0.00038907 | 0.00039479 | 0.00040052 | 0.00040625 | 0.00041198 | 0.00041771 | 0.00042344 | 0.00042916 | 0.00043489 | 0.00044062 | 0.00044635 | 0.00045208 | 0.00045781 | 0.00046353 | 0.00046926 | 0.00047499 | 0.00048072 | 0.00048645 | 0.00049218 | 0.0004979
| 10571996 | FNS013 | FNS | 15541622 | 181632471 | 0.46027 | 144.4233 | -38.0257 | 108 | 95.3 | 5.4% | 7.3% | 113.832 | 100.4462 | 0.01 | 0.02 | -1338.58 | 127.2178 | 1.436% | 115.884 | 102.2569 | 0.01 | 0.02 | -1362.71 | 129.5111 | 1.579% | 143.6% | 0.9627% | 0.9775% | 0.9924% | 1.007% | 1.022% | 1.037% | 1.052% | 1.066% | 1.081% | 1.096% | 1.111% | 1.126% | 1.141% | 1.155% | 1.17% | 1.185% | 1.2% | 1.215% | 1.229% | 1.244% | 0.00038988 | 0.00039589 | 0.00040189 | 0.00040789 | 0.00041389 | 0.00041989 | 0.00042589 | 0.00043189 | 0.00043789 | 0.00044389 | 0.00044989 | 0.00045589 | 0.00046189 | 0.0004679 | 0.0004739 | 0.0004799 | 0.0004859 | 0.0004919 | 0.0004979 | 0.0005039
| 10579356 | CRO021 | CRO | 17778931 | 17286129 | 2.3426 | 144.3507 | -38.1006 | 106 | 93.7 | 5.4% | 7.3% | 111.724 | 98.7598 | 0.01 | 0.02 | -1296.42 | 124.6882 | 1.442% | 113.738 | 100.5401 | 0.01 | 0.02 | -1319.79 | 126.9359 | 1.586% | 144.2% | 0.9633% | 0.9783% | 0.9934% | 1.008% | 1.023% | 1.038% | 1.053% | 1.068% | 1.083% | 1.098% | 1.113% | 1.129% | 1.144% | 1.159% | 1.174% | 1.189% | 1.204% | 1.219% | 1.234% | 1.249% | 0.00039013 | 0.00039621 | 0.00040229 | 0.00040837 | 0.00041445 | 0.00042053 | 0.00042661 | 0.00043269 | 0.00043878 | 0.00044486 | 0.00045094 | 0.00045702 | 0.0004631 | 0.00046918 | 0.00047526 | 0.00048134 | 0.00048743 | 0.00049351 | 0.00049959 | 0.00050567
| 10579357 | CRO021 | CRO | 17286134 | 17778931 | 2.8277 | 144.3512 | -38.1009 | 106 | 93.7 | 5.4% | 7.3% | 111.724 | 98.7598 | 0.01 | 0.02 | -1296.42 | 124.6882 | 1.442% | 113.738 | 100.5401 | 0.01 | 0.02 | -1319.79 | 126.9359 | 1.586% | 144.2% | 0.9633% | 0.9783% | 0.9934% | 1.008% | 1.023% | 1.038% | 1.053% | 1.068% | 1.083% | 1.098% | 1.113% | 1.129% | 1.144% | 1.159% | 1.174% | 1.189% | 1.204% | 1.219% | 1.234% | 1.249% | 0.00039013 | 0.00039621 | 0.00040229 | 0.00040837 | 0.00041445 | 0.00042053 | 0.00042661 | 0.00043269 | 0.00043878 | 0.00044486 | 0.00045094 | 0.00045702 | 0.0004631 | 0.00046918 | 0.00047526 | 0.00048134 | 0.00048743 | 0.00049351 | 0.00049959 | 0.00050567
| 10581766 | WMN013 | WMN | 16663575 | 184520752 | 0.64948 | 142.6635 | -34.7456 | 112 | 97.8 | 6.3% | 8.8% | 119.056 | 103.9614 | 0.01 | 0.02 | -1509.46 | 134.1506 | 1.467% | 120.176 | 106.4064 | 0.01 | 0.02 | -1376.96 | 133.9456 | 1.594% | 146.7% | 0.966% | 0.9819% | 0.9978% | 1.014% | 1.03% | 1.045% | 1.061% | 1.077% | 1.093% | 1.109% | 1.125% | 1.141% | 1.157% | 1.173% | 1.189% | 1.204% | 1.22% | 1.236% | 1.252% | 1.268% | 0.0003912 | 0.00039764 | 0.00040407 | 0.00041051 | 0.00041695 | 0.00042339 | 0.00042983 | 0.00043627 | 0.0004427 | 0.00044914 | 0.00045558 | 0.00046202 | 0.00046846 | 0.0004749 | 0.00048133 | 0.00048777 | 0.00049421 | 0.00050065 | 0.00050709 | 0.00051353

## Energy at risk
Powercor
Lines flood resilience program
Weighted energy at risk (MWh)
| Span ID | Feeder | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
| 10058538 | BAS033 | 107.03 | 87.7727 | 89.9011 | 92.1309 | 94.0567 | 96.3878 | 99.6311 | 103.0772 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137
| 10060242 | HTN032 | 67.7046 | 67.4005 | 67.6032 | 67.7046 | 67.4005 | 67.1978 | 67.5019 | 67.9073 | 67.6032 | 67.6032 | 67.6032 | 67.6032 | 67.6032 | 67.6032 | 67.6032 | 67.6032 | 67.6032 | 67.6032 | 67.6032 | 67.6032
| 10069507 | WND014 | 58.7854 | 59.0895 | 60.0017 | 60.7111 | 61.3193 | 62.1301 | 63.4477 | 65.0694 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802
| 10084145 | MDA032 | 76.7251 | 77.0292 | 77.5359 | 77.6373 | 77.3332 | 77.3332 | 77.9414 | 78.7522 | 78.5495 | 78.5495 | 78.5495 | 78.5495 | 78.5495 | 78.5495 | 78.5495 | 78.5495 | 78.5495 | 78.5495 | 78.5495 | 78.5495
| 10093224 | EHK022 | 59.3935 | 59.4949 | 59.6976 | 59.9003 | 59.9003 | 60.103 | 60.7111 | 61.3193 | 61.522 | 61.522 | 61.522 | 61.522 | 61.522 | 61.522 | 61.522 | 61.522 | 61.522 | 61.522 | 61.522 | 61.522
| 10097205 | BAS022 | 132.1658 | 134.1929 | 136.7268 | 99.4284 | 100.1379 | 101.2528 | 103.3812 | 105.7124 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381
| 10137677 | BAS033 | 107.03 | 87.7727 | 89.9011 | 92.1309 | 94.0567 | 96.3878 | 99.6311 | 103.0772 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137 | 105.8137
| 10154574 | CMN005 | 103.584 | 103.9894 | 104.3948 | 105.0029 | 105.1043 | 105.5097 | 105.9151 | 106.5232 | 107.03 | 107.03 | 107.03 | 107.03 | 107.03 | 107.03 | 107.03 | 107.03 | 107.03 | 107.03 | 107.03 | 107.03
| 10156754 | STL005 | 88.8876 | 88.5835 | 88.6849 | 88.5835 | 87.9754 | 87.3673 | 87.1646 | 87.2659 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578
| 10156772 | STL005 | 88.8876 | 88.5835 | 88.6849 | 88.5835 | 87.9754 | 87.3673 | 87.1646 | 87.2659 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578
| 10156819 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10158895 | CMN002 | 36.7916 | 36.8929 | 37.0956 | 37.3997 | 37.501 | 37.7037 | 38.1092 | 38.5146 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173
| 10158902 | CMN002 | 36.7916 | 36.8929 | 37.0956 | 37.3997 | 37.501 | 37.7037 | 38.1092 | 38.5146 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173
| 10159643 | STL007 | 66.4883 | 65.1707 | 64.3599 | 63.6504 | 62.8396 | 61.7247 | 62.1301 | 61.522 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10159700 | STL007 | 66.4883 | 65.1707 | 64.3599 | 63.6504 | 62.8396 | 61.7247 | 62.1301 | 61.522 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10159749 | STL007 | 66.4883 | 65.1707 | 64.3599 | 63.6504 | 62.8396 | 61.7247 | 62.1301 | 61.522 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10159758 | STL007 | 66.4883 | 65.1707 | 64.3599 | 63.6504 | 62.8396 | 61.7247 | 62.1301 | 61.522 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10159822 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10159823 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10159824 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10159833 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10160457 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10160458 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10160460 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10162366 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10162370 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10162417 | STL007 | 66.4883 | 65.1707 | 64.3599 | 63.6504 | 62.8396 | 61.7247 | 62.1301 | 61.522 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10162477 | STL007 | 66.4883 | 65.1707 | 64.3599 | 63.6504 | 62.8396 | 61.7247 | 62.1301 | 61.522 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10165961 | HSM004 | 54.1231 | 54.2245 | 54.4272 | 54.3258 | 53.7177 | 53.4136 | 53.6164 | 53.9204 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136
| 10167756 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10167757 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10167767 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10170532 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10173413 | BATSBAS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10173503 | CHM011 | 23.6155 | 23.5142 | 23.5142 | 23.5142 | 23.3115 | 23.2101 | 23.1087 | 23.2101 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074
| 10182107 | BET005 | 120.3074 | 122.4358 | 125.1724 | 127.7062 | 129.0239 | 130.8482 | 133.8889 | 137.5376 | 139.362 | 139.362 | 139.362 | 139.362 | 139.362 | 139.362 | 139.362 | 139.362 | 139.362 | 139.362 | 139.362 | 139.362
| 10182494 | HSM004 | 54.1231 | 54.2245 | 54.4272 | 54.3258 | 53.7177 | 53.4136 | 53.6164 | 53.9204 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136
| 10183243 | NHL016 | 35.3726 | 34.9672 | 34.8658 | 34.5618 | 34.055 | 33.6496 | 33.4469 | 33.3455 | 32.8387 | 32.8387 | 32.8387 | 32.8387 | 32.8387 | 32.8387 | 32.8387 | 32.8387 | 32.8387 | 32.8387 | 32.8387 | 32.8387
| 10184457 | EHK031 | 107.7395 | 110.3747 | 113.618 | 116.2532 | 118.6857 | 121.1182 | 124.5643 | 128.8211 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355
| 10186354 | EHK024 | 94.5634 | 95.881 | 97.8068 | 99.3271 | 99.8339 | 100.746 | 102.5704 | 104.8002 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097
| 10186356 | EHK024 | 94.5634 | 95.881 | 97.8068 | 99.3271 | 99.8339 | 100.746 | 102.5704 | 104.8002 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097
| 10186359 | EHK024 | 94.5634 | 95.881 | 97.8068 | 99.3271 | 99.8339 | 100.746 | 102.5704 | 104.8002 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097
| 10186730 | BET006 | 162.9775 | 165.2073 | 167.8425 | 170.5791 | 172.0994 | 173.9237 | 177.1671 | 180.7145 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147
| 10187532 | BET006 | 162.9775 | 165.2073 | 167.8425 | 170.5791 | 172.0994 | 173.9237 | 177.1671 | 180.7145 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147
| 10187618 | BET006 | 162.9775 | 165.2073 | 167.8425 | 170.5791 | 172.0994 | 173.9237 | 177.1671 | 180.7145 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147
| 10187619 | BET006 | 162.9775 | 165.2073 | 167.8425 | 170.5791 | 172.0994 | 173.9237 | 177.1671 | 180.7145 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147
| 10190219 | NHL015 | 34.1564 | 34.055 | 34.1564 | 34.055 | 33.7509 | 33.4469 | 33.4469 | 33.4469 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10191201 | NKA006 | 86.0497 | 99.4284 | 100.746 | 101.6582 | 101.4555 | 101.6582 | 102.9758 | 104.3948 | 104.2934 | 104.2934 | 104.2934 | 104.2934 | 104.2934 | 104.2934 | 104.2934 | 104.2934 | 104.2934 | 104.2934 | 104.2934 | 104.2934
| 10191767 | BAN003 | 104.0907 | 106.4219 | 109.7666 | 112.0977 | 113.9221 | 116.2532 | 119.8006 | 122.6385 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561
| 10196439 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10196454 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10196456 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10198480 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10203381 | SHN011 | 79.563 | 80.4752 | 81.7928 | 82.8064 | 82.9077 | 83.5158 | 85.1375 | 87.0632 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673
| 10205049 | NHL015 | 34.1564 | 34.055 | 34.1564 | 34.055 | 33.7509 | 33.4469 | 33.4469 | 33.4469 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10206645 | KGT004 | 59.5962 | 60.0017 | 60.9139 | 61.4206 | 61.3193 | 61.4206 | 62.2315 | 63.4477 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10207652 | KGT004 | 59.5962 | 60.0017 | 60.9139 | 61.4206 | 61.3193 | 61.4206 | 62.2315 | 63.4477 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10207676 | HTN011 | 12.9733 | 13.176 | 13.3787 | 13.4801 | 13.4801 | 13.5815 | 13.7842 | 14.0882 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896
| 10208645 | HTN011 | 12.9733 | 13.176 | 13.3787 | 13.4801 | 13.4801 | 13.5815 | 13.7842 | 14.0882 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896
| 10208648 | HTN011 | 12.9733 | 13.176 | 13.3787 | 13.4801 | 13.4801 | 13.5815 | 13.7842 | 14.0882 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896
| 10209776 | HTN011 | 12.9733 | 13.176 | 13.3787 | 13.4801 | 13.4801 | 13.5815 | 13.7842 | 14.0882 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896
| 10209778 | HTN011 | 12.9733 | 13.176 | 13.3787 | 13.4801 | 13.4801 | 13.5815 | 13.7842 | 14.0882 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896 | 14.1896
| 10210955 | BAS011 | 217.6074 | 131.7604 | 134.9024 | 137.7403 | 139.5647 | 141.5918 | 144.9365 | 148.4839 | 150.4096 | 150.4096 | 150.4096 | 150.4096 | 150.4096 | 150.4096 | 150.4096 | 150.4096 | 150.4096 | 150.4096 | 150.4096 | 150.4096
| 10213821 | SHN021 | 71.7587 | 72.7723 | 74.0899 | 75.2048 | 75.8129 | 76.6237 | 78.1441 | 79.8671 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10214005 | EHK024 | 94.5634 | 95.881 | 97.8068 | 99.3271 | 99.8339 | 100.746 | 102.5704 | 104.8002 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097
| 10214006 | EHK024 | 94.5634 | 95.881 | 97.8068 | 99.3271 | 99.8339 | 100.746 | 102.5704 | 104.8002 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097
| 10214007 | EHK024 | 94.5634 | 95.881 | 97.8068 | 99.3271 | 99.8339 | 100.746 | 102.5704 | 104.8002 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097 | 105.5097
| 10218050 | ART023 | 55.7448 | 55.238 | 55.1367 | 54.934 | 54.5285 | 54.2245 | 54.1231 | 53.9204 | 53.6164 | 53.6164 | 53.6164 | 53.6164 | 53.6164 | 53.6164 | 53.6164 | 53.6164 | 53.6164 | 53.6164 | 53.6164 | 53.6164
| 10219401 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10224712 | KYM001 | 81.3874 | 81.8942 | 83.1104 | 84.3267 | 84.428 | 84.6307 | 85.7456 | 87.4686 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768
| 10224713 | KYM001 | 81.3874 | 81.8942 | 83.1104 | 84.3267 | 84.428 | 84.6307 | 85.7456 | 87.4686 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768
| 10224837 | ECA007 | 65.6775 | 65.2721 | 65.0694 | 64.2585 | 62.4342 | 60.7111 | 60.103 | 61.4206 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139
| 10224838 | ECA007 | 65.6775 | 65.2721 | 65.0694 | 64.2585 | 62.4342 | 60.7111 | 60.103 | 61.4206 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139
| 10224869 | ECA007 | 65.6775 | 65.2721 | 65.0694 | 64.2585 | 62.4342 | 60.7111 | 60.103 | 61.4206 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139
| 10224870 | ECA007 | 65.6775 | 65.2721 | 65.0694 | 64.2585 | 62.4342 | 60.7111 | 60.103 | 61.4206 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139
| 10225122 | ECA007 | 65.6775 | 65.2721 | 65.0694 | 64.2585 | 62.4342 | 60.7111 | 60.103 | 61.4206 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139
| 10225129 | ECA007 | 65.6775 | 65.2721 | 65.0694 | 64.2585 | 62.4342 | 60.7111 | 60.103 | 61.4206 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139
| 10225165 | ECA007 | 65.6775 | 65.2721 | 65.0694 | 64.2585 | 62.4342 | 60.7111 | 60.103 | 61.4206 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139 | 60.9139
| 10228259 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10229034 | NHL015 | 34.1564 | 34.055 | 34.1564 | 34.055 | 33.7509 | 33.4469 | 33.4469 | 33.4469 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10229043 | NHL015 | 34.1564 | 34.055 | 34.1564 | 34.055 | 33.7509 | 33.4469 | 33.4469 | 33.4469 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10229105 | NHL015 | 34.1564 | 34.055 | 34.1564 | 34.055 | 33.7509 | 33.4469 | 33.4469 | 33.4469 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10229268 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10229636 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10229638 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10229671 | KYM006 | 66.4883 | 66.387 | 66.2856 | 66.2856 | 65.9816 | 65.7789 | 65.9816 | 66.4883 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843
| 10229688 | KYM006 | 66.4883 | 66.387 | 66.2856 | 66.2856 | 65.9816 | 65.7789 | 65.9816 | 66.4883 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843
| 10229690 | KYM006 | 66.4883 | 66.387 | 66.2856 | 66.2856 | 65.9816 | 65.7789 | 65.9816 | 66.4883 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843
| 10229741 | KYM006 | 66.4883 | 66.387 | 66.2856 | 66.2856 | 65.9816 | 65.7789 | 65.9816 | 66.4883 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843
| 10229744 | KYM006 | 66.4883 | 66.387 | 66.2856 | 66.2856 | 65.9816 | 65.7789 | 65.9816 | 66.4883 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843
| 10229786 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10229796 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10229864 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10229887 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10229924 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10229929 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10229934 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10229935 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10229987 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10230057 | NHL015 | 34.1564 | 34.055 | 34.1564 | 34.055 | 33.7509 | 33.4469 | 33.4469 | 33.4469 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10230058 | NHL015 | 34.1564 | 34.055 | 34.1564 | 34.055 | 33.7509 | 33.4469 | 33.4469 | 33.4469 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10230280 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10231029 | KYM003 | 54.3258 | 54.5285 | 55.3394 | 55.9475 | 55.7448 | 55.9475 | 56.8597 | 58.1773 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732
| 10231053 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10231059 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10231086 | KYM002 | 58.8868 | 58.2786 | 58.2786 | 57.2651 | 56.657 | 56.2516 | 56.1502 | 55.7448 | 55.4407 | 55.4407 | 55.4407 | 55.4407 | 55.4407 | 55.4407 | 55.4407 | 55.4407 | 55.4407 | 55.4407 | 55.4407 | 55.4407
| 10232140 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232141 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232159 | SHP011 | 96.2865 | 95.4756 | 95.2729 | 95.3743 | 94.8675 | 94.158 | 93.9553 | 94.158 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553
| 10232252 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232276 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232278 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232347 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232355 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232383 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232388 | SHTSSHP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SHP014
| 10232390 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232400 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232401 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232488 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232489 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232490 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10232493 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10233610 | KYM006 | 66.4883 | 66.387 | 66.2856 | 66.2856 | 65.9816 | 65.7789 | 65.9816 | 66.4883 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843 | 66.1843
| 10233711 | KYM001 | 81.3874 | 81.8942 | 83.1104 | 84.3267 | 84.428 | 84.6307 | 85.7456 | 87.4686 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768
| 10233712 | KYM001 | 81.3874 | 81.8942 | 83.1104 | 84.3267 | 84.428 | 84.6307 | 85.7456 | 87.4686 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768
| 10233713 | KYM001 | 81.3874 | 81.8942 | 83.1104 | 84.3267 | 84.428 | 84.6307 | 85.7456 | 87.4686 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768
| 10233714 | KYM001 | 81.3874 | 81.8942 | 83.1104 | 84.3267 | 84.428 | 84.6307 | 85.7456 | 87.4686 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768
| 10233715 | KYM001 | 81.3874 | 81.8942 | 83.1104 | 84.3267 | 84.428 | 84.6307 | 85.7456 | 87.4686 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768
| 10233717 | KYM001 | 81.3874 | 81.8942 | 83.1104 | 84.3267 | 84.428 | 84.6307 | 85.7456 | 87.4686 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768
| 10234489 | SHP011 | 96.2865 | 95.4756 | 95.2729 | 95.3743 | 94.8675 | 94.158 | 93.9553 | 94.158 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553 | 93.9553
| 10240137 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10240291 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10240307 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10240313 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10240609 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10243207 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10243209 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10243244 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10243245 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10244130 | TNA022 | 153.5516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10244137 | TNA022 | 153.5516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10246348 | WBL006 | 46.2175 | 46.7243 | 47.4337 | 48.1432 | 48.65 | 49.1568 | 49.9676 | 50.9811 | 51.5893 | 51.5893 | 51.5893 | 51.5893 | 51.5893 | 51.5893 | 51.5893 | 51.5893 | 51.5893 | 51.5893 | 51.5893 | 51.5893
| 10251564 | SHN021 | 71.7587 | 72.7723 | 74.0899 | 75.2048 | 75.8129 | 76.6237 | 78.1441 | 79.8671 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10253006 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10253013 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10253014 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10253028 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10253030 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10253061 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10256915 | HSM004 | 54.1231 | 54.2245 | 54.4272 | 54.3258 | 53.7177 | 53.4136 | 53.6164 | 53.9204 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136
| 10261741 | KYM003 | 54.3258 | 54.5285 | 55.3394 | 55.9475 | 55.7448 | 55.9475 | 56.8597 | 58.1773 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732
| 10261832 | KYM003 | 54.3258 | 54.5285 | 55.3394 | 55.9475 | 55.7448 | 55.9475 | 56.8597 | 58.1773 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732
| 10261833 | KYM003 | 54.3258 | 54.5285 | 55.3394 | 55.9475 | 55.7448 | 55.9475 | 56.8597 | 58.1773 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732
| 10262007 | KYM003 | 54.3258 | 54.5285 | 55.3394 | 55.9475 | 55.7448 | 55.9475 | 56.8597 | 58.1773 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732
| 10262050 | KYM003 | 54.3258 | 54.5285 | 55.3394 | 55.9475 | 55.7448 | 55.9475 | 56.8597 | 58.1773 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732 | 57.8732
| 10262851 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10262865 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10262868 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10263212 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10263224 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10263226 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10263303 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10263304 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10263307 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10263308 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10263310 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10263393 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10263844 | EHK031 | 107.7395 | 110.3747 | 113.618 | 116.2532 | 118.6857 | 121.1182 | 124.5643 | 128.8211 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355
| 10263847 | EHK031 | 107.7395 | 110.3747 | 113.618 | 116.2532 | 118.6857 | 121.1182 | 124.5643 | 128.8211 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355 | 131.355
| 10264152 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10264167 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10264169 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10264170 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10264171 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10269387 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10273779 | BAN003 | 104.0907 | 106.4219 | 109.7666 | 112.0977 | 113.9221 | 116.2532 | 119.8006 | 122.6385 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561
| 10274498 | BMH003 | 77.6373 | 80.2725 | 83.0091 | 85.2389 | 87.2659 | 89.7998 | 93.5499 | 96.5905 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149
| 10274507 | BMH003 | 77.6373 | 80.2725 | 83.0091 | 85.2389 | 87.2659 | 89.7998 | 93.5499 | 96.5905 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149
| 10274517 | BMH003 | 77.6373 | 80.2725 | 83.0091 | 85.2389 | 87.2659 | 89.7998 | 93.5499 | 96.5905 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149
| 10274874 | BMH006 | 52.5015 | 52.6028 | 53.1096 | 53.8191 | 54.1231 | 54.4272 | 55.5421 | 56.5556 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651
| 10275122 | BMH006 | 52.5015 | 52.6028 | 53.1096 | 53.8191 | 54.1231 | 54.4272 | 55.5421 | 56.5556 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651
| 10275306 | BMH006 | 52.5015 | 52.6028 | 53.1096 | 53.8191 | 54.1231 | 54.4272 | 55.5421 | 56.5556 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651
| 10275360 | BMH006 | 52.5015 | 52.6028 | 53.1096 | 53.8191 | 54.1231 | 54.4272 | 55.5421 | 56.5556 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651
| 10275362 | BMH006 | 52.5015 | 52.6028 | 53.1096 | 53.8191 | 54.1231 | 54.4272 | 55.5421 | 56.5556 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651 | 57.2651
| 10278483 | SHP012 | 74.1912 | 75.0021 | 76.6237 | 77.84 | 77.84 | 78.4481 | 79.8671 | 81.7928 | 82.0969 | 82.0969 | 82.0969 | 82.0969 | 82.0969 | 82.0969 | 82.0969 | 82.0969 | 82.0969 | 82.0969 | 82.0969 | 82.0969
| 10281761 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10281764 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10281798 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10282283 | BMH003 | 77.6373 | 80.2725 | 83.0091 | 85.2389 | 87.2659 | 89.7998 | 93.5499 | 96.5905 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149
| 10282315 | BMH003 | 77.6373 | 80.2725 | 83.0091 | 85.2389 | 87.2659 | 89.7998 | 93.5499 | 96.5905 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149
| 10282316 | BMH003 | 77.6373 | 80.2725 | 83.0091 | 85.2389 | 87.2659 | 89.7998 | 93.5499 | 96.5905 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149
| 10282317 | BMH003 | 77.6373 | 80.2725 | 83.0091 | 85.2389 | 87.2659 | 89.7998 | 93.5499 | 96.5905 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149
| 10282347 | BMH003 | 77.6373 | 80.2725 | 83.0091 | 85.2389 | 87.2659 | 89.7998 | 93.5499 | 96.5905 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149
| 10282348 | BMH003 | 77.6373 | 80.2725 | 83.0091 | 85.2389 | 87.2659 | 89.7998 | 93.5499 | 96.5905 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149
| 10283440 | HSM002 | 33.1428 | 33.1428 | 33.3455 | 33.4469 | 33.3455 | 33.2442 | 33.5482 | 33.8523 | 33.6496 | 33.6496 | 33.6496 | 33.6496 | 33.6496 | 33.6496 | 33.6496 | 33.6496 | 33.6496 | 33.6496 | 33.6496 | 33.6496
| 10284224 | HSM004 | 54.1231 | 54.2245 | 54.4272 | 54.3258 | 53.7177 | 53.4136 | 53.6164 | 53.9204 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136
| 10284360 | HSM004 | 54.1231 | 54.2245 | 54.4272 | 54.3258 | 53.7177 | 53.4136 | 53.6164 | 53.9204 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136
| 10290339 | NHL015 | 34.1564 | 34.055 | 34.1564 | 34.055 | 33.7509 | 33.4469 | 33.4469 | 33.4469 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10298697 | HSM004 | 54.1231 | 54.2245 | 54.4272 | 54.3258 | 53.7177 | 53.4136 | 53.6164 | 53.9204 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136
| 10298698 | HSM004 | 54.1231 | 54.2245 | 54.4272 | 54.3258 | 53.7177 | 53.4136 | 53.6164 | 53.9204 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136 | 53.4136
| 10308414 | BBD014 | 125.071 | 124.0575 | 123.5507 | 122.8412 | 121.4223 | 120.3074 | 120.1047 | 120.206 | 118.9898 | 118.9898 | 118.9898 | 118.9898 | 118.9898 | 118.9898 | 118.9898 | 118.9898 | 118.9898 | 118.9898 | 118.9898 | 118.9898
| 10315838 | CTN003 | 21.7911 | 21.8925 | 22.0952 | 22.1966 | 22.0952 | 22.0952 | 22.2979 | 22.602 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006
| 10315839 | CTN003 | 21.7911 | 21.8925 | 22.0952 | 22.1966 | 22.0952 | 22.0952 | 22.2979 | 22.602 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006
| 10315842 | CTN003 | 21.7911 | 21.8925 | 22.0952 | 22.1966 | 22.0952 | 22.0952 | 22.2979 | 22.602 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006
| 10315843 | CTN003 | 21.7911 | 21.8925 | 22.0952 | 22.1966 | 22.0952 | 22.0952 | 22.2979 | 22.602 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006
| 10315857 | CTN003 | 21.7911 | 21.8925 | 22.0952 | 22.1966 | 22.0952 | 22.0952 | 22.2979 | 22.602 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006
| 10315858 | CTN003 | 21.7911 | 21.8925 | 22.0952 | 22.1966 | 22.0952 | 22.0952 | 22.2979 | 22.602 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006
| 10315859 | CTN003 | 21.7911 | 21.8925 | 22.0952 | 22.1966 | 22.0952 | 22.0952 | 22.2979 | 22.602 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006
| 10318791 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10320316 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10320317 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10320318 | STL006 | 33.8523 | 33.4469 | 33.5482 | 33.5482 | 33.3455 | 33.0415 | 33.2442 | 33.3455 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10320465 | STL005 | 88.8876 | 88.5835 | 88.6849 | 88.5835 | 87.9754 | 87.3673 | 87.1646 | 87.2659 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578 | 86.6578
| 10327284 | WSFWMN | 253.5273 | 255.9801 | 260.4903 | 263.7134 | 263.9465 | 264.9297 | 269.6122 | 275.7036 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164
| 10327285 | WSFWMN | 253.5273 | 255.9801 | 260.4903 | 263.7134 | 263.9465 | 264.9297 | 269.6122 | 275.7036 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164
| 10327294 | WSFWMN | 253.5273 | 255.9801 | 260.4903 | 263.7134 | 263.9465 | 264.9297 | 269.6122 | 275.7036 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164
| 10327298 | WSFWMN | 253.5273 | 255.9801 | 260.4903 | 263.7134 | 263.9465 | 264.9297 | 269.6122 | 275.7036 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164
| 10327338 | WSFWMN | 253.5273 | 255.9801 | 260.4903 | 263.7134 | 263.9465 | 264.9297 | 269.6122 | 275.7036 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164 | 275.9164
| 10328372 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10328909 | TNA022 | 153.5516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10329039 | TNA022 | 153.5516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10331635 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10331638 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10331644 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10331648 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10334019 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334157 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334179 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334194 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334197 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334198 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334199 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334201 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334243 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334245 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334849 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334851 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334853 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334854 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334855 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334857 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334858 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334859 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334929 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334930 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10334955 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10335111 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10335133 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10335134 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10335163 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10335335 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10335353 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10335473 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10335478 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10335641 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10335642 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10335643 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10335708 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10337277 | FNS013 | 115.8478 | 118.179 | 120.8142 | 123.6521 | 126.0846 | 128.6184 | 131.8618 | 135.7132 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593
| 10337280 | FNS013 | 115.8478 | 118.179 | 120.8142 | 123.6521 | 126.0846 | 128.6184 | 131.8618 | 135.7132 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593
| 10337583 | FNS022 | 62.4342 | 63.8531 | 65.5761 | 67.2992 | 68.5154 | 69.833 | 71.556 | 73.4818 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994
| 10337585 | FNS022 | 62.4342 | 63.8531 | 65.5761 | 67.2992 | 68.5154 | 69.833 | 71.556 | 73.4818 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994 | 74.7994
| 10337818 | GHP022 | 60.8125 | 61.826 | 63.245 | 64.2585 | 64.8667 | 65.5761 | 66.9951 | 68.7181 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262
| 10338170 | WBE023 | 140.9836 | 144.0243 | 147.7744 | 151.2204 | 154.4637 | 158.9233 | 163.687 | 169.0587 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089
| 10338172 | WBE023 | 140.9836 | 144.0243 | 147.7744 | 151.2204 | 154.4637 | 158.9233 | 163.687 | 169.0587 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089 | 172.8089
| 10339279 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10341919 | SHL005 | 40.339 | 40.339 | 40.339 | 40.339 | 39.9335 | 39.7308 | 39.9335 | 40.2376 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349
| 10341923 | SHL005 | 40.339 | 40.339 | 40.339 | 40.339 | 39.9335 | 39.7308 | 39.9335 | 40.2376 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349
| 10342346 | KGT004 | 59.5962 | 60.0017 | 60.9139 | 61.4206 | 61.3193 | 61.4206 | 62.2315 | 63.4477 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10342482 | KGT004 | 59.5962 | 60.0017 | 60.9139 | 61.4206 | 61.3193 | 61.4206 | 62.2315 | 63.4477 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10342495 | KGT004 | 59.5962 | 60.0017 | 60.9139 | 61.4206 | 61.3193 | 61.4206 | 62.2315 | 63.4477 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10342875 | KGT004 | 59.5962 | 60.0017 | 60.9139 | 61.4206 | 61.3193 | 61.4206 | 62.2315 | 63.4477 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10342881 | KGT004 | 59.5962 | 60.0017 | 60.9139 | 61.4206 | 61.3193 | 61.4206 | 62.2315 | 63.4477 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10343245 | KGTSGSF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10343246 | KGTSGSF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10343647 | KGT004 | 59.5962 | 60.0017 | 60.9139 | 61.4206 | 61.3193 | 61.4206 | 62.2315 | 63.4477 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10343727 | KGT004 | 59.5962 | 60.0017 | 60.9139 | 61.4206 | 61.3193 | 61.4206 | 62.2315 | 63.4477 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10352910 | SHL005 | 40.339 | 40.339 | 40.339 | 40.339 | 39.9335 | 39.7308 | 39.9335 | 40.2376 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349 | 40.0349
| 10360536 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10360621 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10360625 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10360626 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10360627 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10360628 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10363777 | OYN005 | 33.2442 | 33.3455 | 33.4469 | 33.5482 | 33.3455 | 33.1428 | 33.2442 | 33.4469 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428 | 33.1428
| 10364607 | CTN003 | 21.7911 | 21.8925 | 22.0952 | 22.1966 | 22.0952 | 22.0952 | 22.2979 | 22.602 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006 | 22.5006
| 10366996 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10366997 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10367014 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10367015 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10367016 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10367017 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10367019 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10367159 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10367160 | MBN031 | 59.2922 | 59.799 | 60.9139 | 61.7247 | 61.826 | 62.1301 | 63.245 | 64.5626 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664 | 64.664
| 10367815 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10367829 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10367836 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10367934 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10367937 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10367938 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10367939 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10367947 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10367948 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10367952 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10368011 | HTN013 | 51.792 | 51.792 | 51.792 | 51.5893 | 51.0825 | 50.5757 | 50.373 | 50.373 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635
| 10368178 | HTN013 | 51.792 | 51.792 | 51.792 | 51.5893 | 51.0825 | 50.5757 | 50.373 | 50.373 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635
| 10369081 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10369082 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10369084 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10369089 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10369091 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10369646 | HTN013 | 51.792 | 51.792 | 51.792 | 51.5893 | 51.0825 | 50.5757 | 50.373 | 50.373 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635
| 10369837 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10369838 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10369839 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10369847 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10369863 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10369865 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10370437 | HTN013 | 51.792 | 51.792 | 51.792 | 51.5893 | 51.0825 | 50.5757 | 50.373 | 50.373 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635
| 10370496 | HTN013 | 51.792 | 51.792 | 51.792 | 51.5893 | 51.0825 | 50.5757 | 50.373 | 50.373 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635
| 10370722 | HTN013 | 51.792 | 51.792 | 51.792 | 51.5893 | 51.0825 | 50.5757 | 50.373 | 50.373 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635 | 49.6635
| 10373068 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10373078 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10373097 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10373098 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10373099 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10373102 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10373201 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10373265 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10373267 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10373268 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10373284 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10373345 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10373712 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10374056 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10376361 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10376367 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10376369 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10376370 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10376373 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10376473 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10376557 | RCT014 | 100.2393 | 100.442 | 100.8474 | 100.9488 | 100.5433 | 100.442 | 101.0501 | 101.6582 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555
| 10376558 | RCT014 | 100.2393 | 100.442 | 100.8474 | 100.9488 | 100.5433 | 100.442 | 101.0501 | 101.6582 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555
| 10378233 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378430 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378796 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378807 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378828 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378830 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378852 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378869 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378872 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378875 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378881 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378887 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378888 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378889 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10378892 | RCT013 | 114.1248 | 114.3275 | 115.4424 | 115.8478 | 115.341 | 115.2397 | 116.5573 | 118.2803 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708 | 117.5708
| 10379177 | RCT014 | 100.2393 | 100.442 | 100.8474 | 100.9488 | 100.5433 | 100.442 | 101.0501 | 101.6582 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555
| 10379178 | RCT014 | 100.2393 | 100.442 | 100.8474 | 100.9488 | 100.5433 | 100.442 | 101.0501 | 101.6582 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555
| 10379182 | RCT014 | 100.2393 | 100.442 | 100.8474 | 100.9488 | 100.5433 | 100.442 | 101.0501 | 101.6582 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555
| 10382614 | SHTSNKA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10382624 | SHTSNKA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10382634 | SHTSNKA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10382635 | SHTSNKA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10382636 | SHTSNKA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10382650 | SHN011 | 79.563 | 80.4752 | 81.7928 | 82.8064 | 82.9077 | 83.5158 | 85.1375 | 87.0632 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673
| 10382652 | SHN011 | 79.563 | 80.4752 | 81.7928 | 82.8064 | 82.9077 | 83.5158 | 85.1375 | 87.0632 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673
| 10382708 | SHN011 | 79.563 | 80.4752 | 81.7928 | 82.8064 | 82.9077 | 83.5158 | 85.1375 | 87.0632 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673
| 10383250 | MBN032 | 130.7469 | 133.3821 | 136.4227 | 138.8552 | 140.2742 | 142.0985 | 145.2405 | 148.8893 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055
| 10383467 | MBN032 | 130.7469 | 133.3821 | 136.4227 | 138.8552 | 140.2742 | 142.0985 | 145.2405 | 148.8893 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055 | 150.1055
| 10383807 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10383946 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10383947 | CTN006 | 64.664 | 64.5626 | 64.7653 | 64.7653 | 64.3599 | 64.0558 | 64.1572 | 64.4612 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545 | 63.9545
| 10385402 | CTN004 | 102.8745 | 102.165 | 101.8609 | 102.9758 | 101.7596 | 100.9488 | 100.8474 | 100.6447 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366
| 10385403 | CTN004 | 102.8745 | 102.165 | 101.8609 | 102.9758 | 101.7596 | 100.9488 | 100.8474 | 100.6447 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366 | 100.0366
| 10386137 | CTN002 | 28.3792 | 28.2778 | 28.4805 | 28.5819 | 28.4805 | 28.4805 | 28.6832 | 28.9873 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859
| 10386152 | CTN002 | 28.3792 | 28.2778 | 28.4805 | 28.5819 | 28.4805 | 28.4805 | 28.6832 | 28.9873 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859 | 28.8859
| 10386978 | SHN024 | 77.6373 | 78.8535 | 80.7793 | 82.0969 | 82.6036 | 83.3131 | 85.2389 | 87.57 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727
| 10386985 | SHN024 | 77.6373 | 78.8535 | 80.7793 | 82.0969 | 82.6036 | 83.3131 | 85.2389 | 87.57 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727
| 10387051 | SHN011 | 79.563 | 80.4752 | 81.7928 | 82.8064 | 82.9077 | 83.5158 | 85.1375 | 87.0632 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673
| 10387092 | SHN021 | 71.7587 | 72.7723 | 74.0899 | 75.2048 | 75.8129 | 76.6237 | 78.1441 | 79.8671 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10387109 | SHN021 | 71.7587 | 72.7723 | 74.0899 | 75.2048 | 75.8129 | 76.6237 | 78.1441 | 79.8671 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10387129 | SHN011 | 79.563 | 80.4752 | 81.7928 | 82.8064 | 82.9077 | 83.5158 | 85.1375 | 87.0632 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673
| 10387271 | SHN011 | 79.563 | 80.4752 | 81.7928 | 82.8064 | 82.9077 | 83.5158 | 85.1375 | 87.0632 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673
| 10388106 | MNA021 | 89.3944 | 89.3944 | 89.6984 | 89.7998 | 89.4957 | 89.293 | 89.7998 | 90.4079 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039
| 10388760 | HTN034 | 33.1428 | 33.4469 | 33.7509 | 33.9536 | 33.7509 | 33.6496 | 33.9536 | 34.4604 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577 | 34.2577
| 10389372 | GHP022 | 60.8125 | 61.826 | 63.245 | 64.2585 | 64.8667 | 65.5761 | 66.9951 | 68.7181 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262
| 10389980 | GHP021 | 95.577 | 98.3135 | 101.5569 | 104.3948 | 106.5232 | 108.9557 | 112.9085 | 117.2668 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115
| 10390524 | BMH005 | 113.314 | 117.2668 | 121.9291 | 126.1859 | 129.936 | 134.497 | 139.666 | 144.7337 | 149.1933 | 149.1933 | 149.1933 | 149.1933 | 149.1933 | 149.1933 | 149.1933 | 149.1933 | 149.1933 | 149.1933 | 149.1933 | 149.1933
| 10391055 | CHM011 | 23.6155 | 23.5142 | 23.5142 | 23.5142 | 23.3115 | 23.2101 | 23.1087 | 23.2101 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074
| 10391593 | CHM011 | 23.6155 | 23.5142 | 23.5142 | 23.5142 | 23.3115 | 23.2101 | 23.1087 | 23.2101 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074 | 23.0074
| 10394458 | SHTSKYM1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10394464 | SHTSKYM1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10394473 | SHTSMNA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10395561 | RCT015 | 33.8523 | 33.9536 | 34.055 | 34.1564 | 34.2577 | 34.3591 | 34.4604 | 34.5618 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645
| 10395563 | RCT015 | 33.8523 | 33.9536 | 34.055 | 34.1564 | 34.2577 | 34.3591 | 34.4604 | 34.5618 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645
| 10395566 | RCT015 | 33.8523 | 33.9536 | 34.055 | 34.1564 | 34.2577 | 34.3591 | 34.4604 | 34.5618 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645 | 34.7645
| 10395712 | RCT011 | 39.9335 | 40.5417 | 41.2511 | 41.9606 | 42.1633 | 42.5688 | 43.3796 | 44.2918 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958
| 10395713 | RCT011 | 39.9335 | 40.5417 | 41.2511 | 41.9606 | 42.1633 | 42.5688 | 43.3796 | 44.2918 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958
| 10395714 | RCT011 | 39.9335 | 40.5417 | 41.2511 | 41.9606 | 42.1633 | 42.5688 | 43.3796 | 44.2918 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958
| 10400226 | MDA023 | 176.559 | 178.0793 | 180.6131 | 182.3361 | 183.0456 | 184.1605 | 186.593 | 189.5323 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431
| 10400310 | MDA023 | 176.559 | 178.0793 | 180.6131 | 182.3361 | 183.0456 | 184.1605 | 186.593 | 189.5323 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431
| 10400311 | MDA023 | 176.559 | 178.0793 | 180.6131 | 182.3361 | 183.0456 | 184.1605 | 186.593 | 189.5323 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431
| 10400312 | MDA023 | 176.559 | 178.0793 | 180.6131 | 182.3361 | 183.0456 | 184.1605 | 186.593 | 189.5323 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431 | 190.3431
| 10402508 | RCT011 | 39.9335 | 40.5417 | 41.2511 | 41.9606 | 42.1633 | 42.5688 | 43.3796 | 44.2918 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958
| 10402528 | RCT011 | 39.9335 | 40.5417 | 41.2511 | 41.9606 | 42.1633 | 42.5688 | 43.3796 | 44.2918 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958
| 10403961 | CLC003 | 70.9479 | 71.8601 | 73.4818 | 74.7994 | 75.1034 | 75.8129 | 77.3332 | 79.4617 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739
| 10403963 | CLC003 | 70.9479 | 71.8601 | 73.4818 | 74.7994 | 75.1034 | 75.8129 | 77.3332 | 79.4617 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739
| 10403984 | CLC003 | 70.9479 | 71.8601 | 73.4818 | 74.7994 | 75.1034 | 75.8129 | 77.3332 | 79.4617 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739
| 10404053 | CLC003 | 70.9479 | 71.8601 | 73.4818 | 74.7994 | 75.1034 | 75.8129 | 77.3332 | 79.4617 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739
| 10404054 | CLC003 | 70.9479 | 71.8601 | 73.4818 | 74.7994 | 75.1034 | 75.8129 | 77.3332 | 79.4617 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739
| 10404060 | CLC003 | 70.9479 | 71.8601 | 73.4818 | 74.7994 | 75.1034 | 75.8129 | 77.3332 | 79.4617 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739
| 10408207 | SHTSKYM1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10408211 | SHN021 | 71.7587 | 72.7723 | 74.0899 | 75.2048 | 75.8129 | 76.6237 | 78.1441 | 79.8671 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10408220 | SHN021 | 71.7587 | 72.7723 | 74.0899 | 75.2048 | 75.8129 | 76.6237 | 78.1441 | 79.8671 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10408238 | SHN021 | 71.7587 | 72.7723 | 74.0899 | 75.2048 | 75.8129 | 76.6237 | 78.1441 | 79.8671 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10408241 | SHN021 | 71.7587 | 72.7723 | 74.0899 | 75.2048 | 75.8129 | 76.6237 | 78.1441 | 79.8671 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10408242 | SHN021 | 71.7587 | 72.7723 | 74.0899 | 75.2048 | 75.8129 | 76.6237 | 78.1441 | 79.8671 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10408420 | SHN021 | 71.7587 | 72.7723 | 74.0899 | 75.2048 | 75.8129 | 76.6237 | 78.1441 | 79.8671 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10408427 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10408436 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10409274 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10411123 | KGT004 | 59.5962 | 60.0017 | 60.9139 | 61.4206 | 61.3193 | 61.4206 | 62.2315 | 63.4477 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10411149 | KGT004 | 59.5962 | 60.0017 | 60.9139 | 61.4206 | 61.3193 | 61.4206 | 62.2315 | 63.4477 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10411734 | GHP022 | 60.8125 | 61.826 | 63.245 | 64.2585 | 64.8667 | 65.5761 | 66.9951 | 68.7181 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262 | 69.3262
| 10414656 | FNS012 | 65.6775 | 66.7924 | 68.2114 | 69.4276 | 70.3398 | 71.3533 | 72.8736 | 75.1034 | 76.3197 | 76.3197 | 76.3197 | 76.3197 | 76.3197 | 76.3197 | 76.3197 | 76.3197 | 76.3197 | 76.3197 | 76.3197 | 76.3197
| 10419901 | CLC003 | 70.9479 | 71.8601 | 73.4818 | 74.7994 | 75.1034 | 75.8129 | 77.3332 | 79.4617 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739
| 10419913 | CLC003 | 70.9479 | 71.8601 | 73.4818 | 74.7994 | 75.1034 | 75.8129 | 77.3332 | 79.4617 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739
| 10423140 | NKA001 | 26.1494 | 26.4534 | 26.9602 | 27.2643 | 27.2643 | 27.467 | 27.9737 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832
| 10423219 | NKA001 | 26.1494 | 26.4534 | 26.9602 | 27.2643 | 27.2643 | 27.467 | 27.9737 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832
| 10423495 | NKA001 | 26.1494 | 26.4534 | 26.9602 | 27.2643 | 27.2643 | 27.467 | 27.9737 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832
| 10423534 | NKA001 | 26.1494 | 26.4534 | 26.9602 | 27.2643 | 27.2643 | 27.467 | 27.9737 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832 | 28.6832
| 10423865 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10423867 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10423890 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10423949 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10424032 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10424065 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10424522 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10424523 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10424698 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10424827 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10424852 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10424853 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10424854 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10424855 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10424858 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10424860 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10424875 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10424888 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10424889 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10424893 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10424936 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10424937 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10424938 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10424939 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10424955 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10424956 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10425007 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10425014 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10425042 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10425088 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10425089 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10425120 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10425132 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10425165 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10425193 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10425308 | GHP021 | 95.577 | 98.3135 | 101.5569 | 104.3948 | 106.5232 | 108.9557 | 112.9085 | 117.2668 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115
| 10425309 | GHP021 | 95.577 | 98.3135 | 101.5569 | 104.3948 | 106.5232 | 108.9557 | 112.9085 | 117.2668 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115
| 10427665 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10427689 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10427723 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10427805 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10427869 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10427995 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10428001 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10428002 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10428050 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10428821 | KGT002 | 70.5425 | 70.6439 | 70.9479 | 71.0493 | 70.6439 | 70.2384 | 70.4411 | 70.8466 | 70.4411 | 70.4411 | 70.4411 | 70.4411 | 70.4411 | 70.4411 | 70.4411 | 70.4411 | 70.4411 | 70.4411 | 70.4411 | 70.4411
| 10429014 | CME016 | 94.158 | 95.3743 | 96.8946 | 98.4149 | 99.1244 | 99.9352 | 101.7596 | 104.1921 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056
| 10431269 | NKA005 | 45.204 | 45.8121 | 46.7243 | 47.3324 | 47.4337 | 47.7378 | 48.65 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662
| 10431301 | NKA005 | 45.204 | 45.8121 | 46.7243 | 47.3324 | 47.4337 | 47.7378 | 48.65 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662
| 10431302 | NKA005 | 45.204 | 45.8121 | 46.7243 | 47.3324 | 47.4337 | 47.7378 | 48.65 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662
| 10431333 | NKA005 | 45.204 | 45.8121 | 46.7243 | 47.3324 | 47.4337 | 47.7378 | 48.65 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662
| 10431335 | NKA005 | 45.204 | 45.8121 | 46.7243 | 47.3324 | 47.4337 | 47.7378 | 48.65 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662
| 10431408 | NKA005 | 45.204 | 45.8121 | 46.7243 | 47.3324 | 47.4337 | 47.7378 | 48.65 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662
| 10434063 | CME016 | 94.158 | 95.3743 | 96.8946 | 98.4149 | 99.1244 | 99.9352 | 101.7596 | 104.1921 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056
| 10434065 | CME016 | 94.158 | 95.3743 | 96.8946 | 98.4149 | 99.1244 | 99.9352 | 101.7596 | 104.1921 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056
| 10434066 | CME016 | 94.158 | 95.3743 | 96.8946 | 98.4149 | 99.1244 | 99.9352 | 101.7596 | 104.1921 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056
| 10434067 | CME016 | 94.158 | 95.3743 | 96.8946 | 98.4149 | 99.1244 | 99.9352 | 101.7596 | 104.1921 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056
| 10434068 | CME016 | 94.158 | 95.3743 | 96.8946 | 98.4149 | 99.1244 | 99.9352 | 101.7596 | 104.1921 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056
| 10434345 | CME016 | 94.158 | 95.3743 | 96.8946 | 98.4149 | 99.1244 | 99.9352 | 101.7596 | 104.1921 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056
| 10434431 | CME016 | 94.158 | 95.3743 | 96.8946 | 98.4149 | 99.1244 | 99.9352 | 101.7596 | 104.1921 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056
| 10434583 | CME016 | 94.158 | 95.3743 | 96.8946 | 98.4149 | 99.1244 | 99.9352 | 101.7596 | 104.1921 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056
| 10438628 | GCY011 | 132.0645 | 133.6861 | 135.8146 | 137.639 | 138.2471 | 140.2742 | 142.0985 | 144.8351 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527
| 10438867 | GCY011 | 132.0645 | 133.6861 | 135.8146 | 137.639 | 138.2471 | 140.2742 | 142.0985 | 144.8351 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527
| 10439185 | GCY014 | 132.9767 | 134.1929 | 135.8146 | 138.0444 | 138.6525 | 139.9701 | 141.6931 | 143.7202 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527
| 10439186 | GCY014 | 132.9767 | 134.1929 | 135.8146 | 138.0444 | 138.6525 | 139.9701 | 141.6931 | 143.7202 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527
| 10439593 | GCY011 | 132.0645 | 133.6861 | 135.8146 | 137.639 | 138.2471 | 140.2742 | 142.0985 | 144.8351 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527
| 10441147 | GCY014 | 132.9767 | 134.1929 | 135.8146 | 138.0444 | 138.6525 | 139.9701 | 141.6931 | 143.7202 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527
| 10441152 | GCY014 | 132.9767 | 134.1929 | 135.8146 | 138.0444 | 138.6525 | 139.9701 | 141.6931 | 143.7202 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527
| 10441153 | GCY014 | 132.9767 | 134.1929 | 135.8146 | 138.0444 | 138.6525 | 139.9701 | 141.6931 | 143.7202 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527
| 10441155 | GCY014 | 132.9767 | 134.1929 | 135.8146 | 138.0444 | 138.6525 | 139.9701 | 141.6931 | 143.7202 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527
| 10441156 | GCY014 | 132.9767 | 134.1929 | 135.8146 | 138.0444 | 138.6525 | 139.9701 | 141.6931 | 143.7202 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527 | 146.1527
| 10444738 | CME016 | 94.158 | 95.3743 | 96.8946 | 98.4149 | 99.1244 | 99.9352 | 101.7596 | 104.1921 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056
| 10444739 | CME016 | 94.158 | 95.3743 | 96.8946 | 98.4149 | 99.1244 | 99.9352 | 101.7596 | 104.1921 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056
| 10444742 | CME016 | 94.158 | 95.3743 | 96.8946 | 98.4149 | 99.1244 | 99.9352 | 101.7596 | 104.1921 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056 | 105.2056
| 10444771 | CME014 | 126.7941 | 128.4157 | 130.6455 | 132.3685 | 133.1794 | 134.497 | 136.4227 | 138.4498 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728
| 10444772 | CME014 | 126.7941 | 128.4157 | 130.6455 | 132.3685 | 133.1794 | 134.497 | 136.4227 | 138.4498 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728
| 10444773 | CME014 | 126.7941 | 128.4157 | 130.6455 | 132.3685 | 133.1794 | 134.497 | 136.4227 | 138.4498 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728
| 10445669 | GHP012 | 105.7124 | 107.5368 | 109.7666 | 111.7936 | 113.0099 | 114.7329 | 116.9627 | 119.902 | 121.4223 | 121.4223 | 121.4223 | 121.4223 | 121.4223 | 121.4223 | 121.4223 | 121.4223 | 121.4223 | 121.4223 | 121.4223 | 121.4223
| 10449773 | CDN004 | 13.6828 | 13.5815 | 13.6828 | 13.8855 | 13.7842 | 13.7842 | 13.8855 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882
| 10449775 | CDN004 | 13.6828 | 13.5815 | 13.6828 | 13.8855 | 13.7842 | 13.7842 | 13.8855 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882
| 10449921 | CDN004 | 13.6828 | 13.5815 | 13.6828 | 13.8855 | 13.7842 | 13.7842 | 13.8855 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882 | 14.0882
| 10451873 | NKA002 | 60.2044 | 60.3057 | 61.0152 | 61.522 | 61.522 | 61.522 | 62.2315 | 63.245 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10451874 | NKA002 | 60.2044 | 60.3057 | 61.0152 | 61.522 | 61.522 | 61.522 | 62.2315 | 63.245 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10451880 | NKA002 | 60.2044 | 60.3057 | 61.0152 | 61.522 | 61.522 | 61.522 | 62.2315 | 63.245 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10452431 | NKA002 | 60.2044 | 60.3057 | 61.0152 | 61.522 | 61.522 | 61.522 | 62.2315 | 63.245 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10453092 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10453231 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10457145 | SHN024 | 77.6373 | 78.8535 | 80.7793 | 82.0969 | 82.6036 | 83.3131 | 85.2389 | 87.57 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727 | 87.7727
| 10457656 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10457822 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10457823 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10457824 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10457825 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10457879 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10457889 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10457891 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10458007 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10458226 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10458228 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10458278 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10458309 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10458332 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10458955 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459329 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459384 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459436 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459437 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459605 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459607 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459611 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459612 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459677 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459745 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459909 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459910 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459911 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459916 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459918 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459919 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459924 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10459926 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10460035 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10460197 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10460219 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10460333 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10460342 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10460429 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10460430 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10460433 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10461431 | CHA006 | 73.7858 | 74.7994 | 76.2183 | 77.1305 | 77.1305 | 77.4346 | 78.8535 | 80.5766 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739
| 10462669 | CME015 | 88.8876 | 88.8876 | 89.5971 | 90.3066 | 90.2052 | 90.0025 | 90.9147 | 92.0296 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435
| 10462672 | CME015 | 88.8876 | 88.8876 | 89.5971 | 90.3066 | 90.2052 | 90.0025 | 90.9147 | 92.0296 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435
| 10464607 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10464701 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10464822 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10464823 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10465191 | MNA021 | 89.3944 | 89.3944 | 89.6984 | 89.7998 | 89.4957 | 89.293 | 89.7998 | 90.4079 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039
| 10465192 | MNA021 | 89.3944 | 89.3944 | 89.6984 | 89.7998 | 89.4957 | 89.293 | 89.7998 | 90.4079 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039
| 10465193 | MNA021 | 89.3944 | 89.3944 | 89.6984 | 89.7998 | 89.4957 | 89.293 | 89.7998 | 90.4079 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039
| 10466002 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10466004 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10466061 | MNA021 | 89.3944 | 89.3944 | 89.6984 | 89.7998 | 89.4957 | 89.293 | 89.7998 | 90.4079 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039 | 90.1039
| 10466179 | STN012 | 106.7259 | 108.753 | 111.1855 | 113.4153 | 115.037 | 116.8614 | 119.8006 | 122.7399 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616
| 10466185 | STN012 | 106.7259 | 108.753 | 111.1855 | 113.4153 | 115.037 | 116.8614 | 119.8006 | 122.7399 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616
| 10466201 | STN021 | 61.826 | 62.6369 | 63.7518 | 64.5626 | 65.2721 | 66.0829 | 67.1978 | 68.5154 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235
| 10466203 | STN021 | 61.826 | 62.6369 | 63.7518 | 64.5626 | 65.2721 | 66.0829 | 67.1978 | 68.5154 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235
| 10466206 | STN021 | 61.826 | 62.6369 | 63.7518 | 64.5626 | 65.2721 | 66.0829 | 67.1978 | 68.5154 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235
| 10466208 | STN021 | 61.826 | 62.6369 | 63.7518 | 64.5626 | 65.2721 | 66.0829 | 67.1978 | 68.5154 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235
| 10466709 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10466711 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10466713 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10466718 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10466720 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10467873 | CRO021 | 58.4814 | 58.1773 | 57.9746 | 57.7719 | 57.3665 | 56.961 | 56.961 | 57.0624 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556
| 10470103 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10470105 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10470196 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10470961 | GHP011 | 114.3275 | 116.2532 | 119.1925 | 121.625 | 123.2467 | 125.5778 | 129.8347 | 133.9902 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295
| 10474297 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10475546 | NKA005 | 45.204 | 45.8121 | 46.7243 | 47.3324 | 47.4337 | 47.7378 | 48.65 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662
| 10475590 | CME015 | 88.8876 | 88.8876 | 89.5971 | 90.3066 | 90.2052 | 90.0025 | 90.9147 | 92.0296 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435 | 92.435
| 10475691 | CME014 | 126.7941 | 128.4157 | 130.6455 | 132.3685 | 133.1794 | 134.497 | 136.4227 | 138.4498 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728
| 10475743 | CME014 | 126.7941 | 128.4157 | 130.6455 | 132.3685 | 133.1794 | 134.497 | 136.4227 | 138.4498 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728
| 10475844 | CME014 | 126.7941 | 128.4157 | 130.6455 | 132.3685 | 133.1794 | 134.497 | 136.4227 | 138.4498 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728 | 140.1728
| 10478222 | STL007 | 66.4883 | 65.1707 | 64.3599 | 63.6504 | 62.8396 | 61.7247 | 62.1301 | 61.522 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10478223 | STL007 | 66.4883 | 65.1707 | 64.3599 | 63.6504 | 62.8396 | 61.7247 | 62.1301 | 61.522 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10478419 | STL007 | 66.4883 | 65.1707 | 64.3599 | 63.6504 | 62.8396 | 61.7247 | 62.1301 | 61.522 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10478541 | STL007 | 66.4883 | 65.1707 | 64.3599 | 63.6504 | 62.8396 | 61.7247 | 62.1301 | 61.522 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10478730 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10478733 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10478736 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10478833 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10478837 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10478838 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10478853 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10478856 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10478857 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10479404 | GHP011 | 114.3275 | 116.2532 | 119.1925 | 121.625 | 123.2467 | 125.5778 | 129.8347 | 133.9902 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295 | 136.9295
| 10480544 | CME021 | 72.8736 | 72.8736 | 73.2791 | 73.3804 | 73.1777 | 72.975 | 73.2791 | 73.7858 | 73.6845 | 73.6845 | 73.6845 | 73.6845 | 73.6845 | 73.6845 | 73.6845 | 73.6845 | 73.6845 | 73.6845 | 73.6845 | 73.6845
| 10480683 | NKA005 | 45.204 | 45.8121 | 46.7243 | 47.3324 | 47.4337 | 47.7378 | 48.65 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662
| 10480701 | NKA005 | 45.204 | 45.8121 | 46.7243 | 47.3324 | 47.4337 | 47.7378 | 48.65 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662 | 49.8662
| 10481505 | WND014 | 58.7854 | 59.0895 | 60.0017 | 60.7111 | 61.3193 | 62.1301 | 63.4477 | 65.0694 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802
| 10483642 | BAS022 | 132.1658 | 134.1929 | 136.7268 | 99.4284 | 100.1379 | 101.2528 | 103.3812 | 105.7124 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381 | 107.6381
| 10484201 | CMN004 | 36.9943 | 37.3997 | 38.0078 | 38.5146 | 38.7173 | 39.0214 | 39.5281 | 40.4403 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417
| 10485104 | NKA002 | 60.2044 | 60.3057 | 61.0152 | 61.522 | 61.522 | 61.522 | 62.2315 | 63.245 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10485105 | NKA002 | 60.2044 | 60.3057 | 61.0152 | 61.522 | 61.522 | 61.522 | 62.2315 | 63.245 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10485108 | NKA002 | 60.2044 | 60.3057 | 61.0152 | 61.522 | 61.522 | 61.522 | 62.2315 | 63.245 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10485125 | NKA002 | 60.2044 | 60.3057 | 61.0152 | 61.522 | 61.522 | 61.522 | 62.2315 | 63.245 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10485132 | NKA002 | 60.2044 | 60.3057 | 61.0152 | 61.522 | 61.522 | 61.522 | 62.2315 | 63.245 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10488457 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10488513 | BETSMRO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10488844 | BET006 | 162.9775 | 165.2073 | 167.8425 | 170.5791 | 172.0994 | 173.9237 | 177.1671 | 180.7145 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147 | 183.147
| 10489049 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10489273 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10489291 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10489354 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10489395 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10489507 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10489512 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10489514 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10489526 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10489528 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10489555 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10489942 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10489943 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10490021 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10490026 | MRO007 | 56.3529 | 56.8597 | 57.6705 | 58.4814 | 58.7854 | 58.9881 | 59.9003 | 60.9139 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179 | 61.2179
| 10490184 | CMN004 | 36.9943 | 37.3997 | 38.0078 | 38.5146 | 38.7173 | 39.0214 | 39.5281 | 40.4403 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417
| 10490223 | CMN004 | 36.9943 | 37.3997 | 38.0078 | 38.5146 | 38.7173 | 39.0214 | 39.5281 | 40.4403 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417 | 40.5417
| 10491306 | CMN002 | 36.7916 | 36.8929 | 37.0956 | 37.3997 | 37.501 | 37.7037 | 38.1092 | 38.5146 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173
| 10494246 | CMN002 | 36.7916 | 36.8929 | 37.0956 | 37.3997 | 37.501 | 37.7037 | 38.1092 | 38.5146 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173 | 38.7173
| 10495435 | BAN003 | 104.0907 | 106.4219 | 109.7666 | 112.0977 | 113.9221 | 116.2532 | 119.8006 | 122.6385 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561
| 10496492 | GHP021 | 95.577 | 98.3135 | 101.5569 | 104.3948 | 106.5232 | 108.9557 | 112.9085 | 117.2668 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115
| 10496504 | GHP021 | 95.577 | 98.3135 | 101.5569 | 104.3948 | 106.5232 | 108.9557 | 112.9085 | 117.2668 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115 | 120.6115
| 10496512 | CLC006 | 124.4629 | 124.4629 | 124.6656 | 124.8683 | 124.6656 | 124.3616 | 124.767 | 125.1724 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751
| 10497201 | CLC006 | 124.4629 | 124.4629 | 124.6656 | 124.8683 | 124.6656 | 124.3616 | 124.767 | 125.1724 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751
| 10497202 | CLC006 | 124.4629 | 124.4629 | 124.6656 | 124.8683 | 124.6656 | 124.3616 | 124.767 | 125.1724 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751
| 10497203 | CLC006 | 124.4629 | 124.4629 | 124.6656 | 124.8683 | 124.6656 | 124.3616 | 124.767 | 125.1724 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751
| 10497204 | CLC006 | 124.4629 | 124.4629 | 124.6656 | 124.8683 | 124.6656 | 124.3616 | 124.767 | 125.1724 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751
| 10497206 | CLC006 | 124.4629 | 124.4629 | 124.6656 | 124.8683 | 124.6656 | 124.3616 | 124.767 | 125.1724 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751 | 125.3751
| 10500258 | CLC013 | 68.6168 | 69.3262 | 70.8466 | 72.1642 | 72.8736 | 73.5831 | 74.394 | 76.0156 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265
| 10500737 | CLC013 | 68.6168 | 69.3262 | 70.8466 | 72.1642 | 72.8736 | 73.5831 | 74.394 | 76.0156 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265
| 10500739 | CLC013 | 68.6168 | 69.3262 | 70.8466 | 72.1642 | 72.8736 | 73.5831 | 74.394 | 76.0156 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265
| 10500741 | CLC013 | 68.6168 | 69.3262 | 70.8466 | 72.1642 | 72.8736 | 73.5831 | 74.394 | 76.0156 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265
| 10502811 | CLC013 | 68.6168 | 69.3262 | 70.8466 | 72.1642 | 72.8736 | 73.5831 | 74.394 | 76.0156 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265
| 10502812 | CLC013 | 68.6168 | 69.3262 | 70.8466 | 72.1642 | 72.8736 | 73.5831 | 74.394 | 76.0156 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265
| 10502855 | CLC013 | 68.6168 | 69.3262 | 70.8466 | 72.1642 | 72.8736 | 73.5831 | 74.394 | 76.0156 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265
| 10502857 | CLC013 | 68.6168 | 69.3262 | 70.8466 | 72.1642 | 72.8736 | 73.5831 | 74.394 | 76.0156 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265
| 10502919 | CLC013 | 68.6168 | 69.3262 | 70.8466 | 72.1642 | 72.8736 | 73.5831 | 74.394 | 76.0156 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265
| 10502924 | CLC013 | 68.6168 | 69.3262 | 70.8466 | 72.1642 | 72.8736 | 73.5831 | 74.394 | 76.0156 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265 | 76.8265
| 10503126 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10503127 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10503128 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10503129 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10503130 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10503180 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10503181 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10503182 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10503183 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10503196 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10509240 | WND014 | 58.7854 | 59.0895 | 60.0017 | 60.7111 | 61.3193 | 62.1301 | 63.4477 | 65.0694 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802 | 65.8802
| 10509296 | BAN003 | 104.0907 | 106.4219 | 109.7666 | 112.0977 | 113.9221 | 116.2532 | 119.8006 | 122.6385 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561 | 123.9561
| 10517240 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10517843 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10518222 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10518814 | SHTSMNA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10518815 | SHTSSHP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10522097 | RCT014 | 100.2393 | 100.442 | 100.8474 | 100.9488 | 100.5433 | 100.442 | 101.0501 | 101.6582 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555
| 10522099 | RCT014 | 100.2393 | 100.442 | 100.8474 | 100.9488 | 100.5433 | 100.442 | 101.0501 | 101.6582 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555
| 10522100 | RCT014 | 100.2393 | 100.442 | 100.8474 | 100.9488 | 100.5433 | 100.442 | 101.0501 | 101.6582 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555 | 101.4555
| 10522151 | STN021 | 61.826 | 62.6369 | 63.7518 | 64.5626 | 65.2721 | 66.0829 | 67.1978 | 68.5154 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235 | 69.1235
| 10522627 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10523686 | MNA034 | 66.7924 | 67.4005 | 68.2114 | 68.7181 | 68.7181 | 68.9208 | 69.833 | 70.8466 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439 | 70.6439
| 10524876 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10524879 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10524880 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10524881 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10524882 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10524884 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10524886 | STN011 | 73.8872 | 74.1912 | 74.9007 | 75.3061 | 75.4075 | 75.6102 | 76.421 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359 | 77.5359
| 10524929 | MNASTN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10525571 | CHA006 | 73.7858 | 74.7994 | 76.2183 | 77.1305 | 77.1305 | 77.4346 | 78.8535 | 80.5766 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739 | 80.3739
| 10526831 | CHA005 | 53.6164 | 53.7177 | 54.4272 | 54.8326 | 54.5285 | 54.4272 | 55.3394 | 56.5556 | 56.2516 | 56.2516 | 56.2516 | 56.2516 | 56.2516 | 56.2516 | 56.2516 | 56.2516 | 56.2516 | 56.2516 | 56.2516 | 56.2516
| 10526950 | NKA002 | 60.2044 | 60.3057 | 61.0152 | 61.522 | 61.522 | 61.522 | 62.2315 | 63.245 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436 | 63.1436
| 10527087 | RCT011 | 39.9335 | 40.5417 | 41.2511 | 41.9606 | 42.1633 | 42.5688 | 43.3796 | 44.2918 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958
| 10527460 | SHP014 | 56.4543 | 56.7583 | 57.3665 | 57.6705 | 57.4678 | 57.5692 | 58.0759 | 58.6841 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827 | 58.5827
| 10530492 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10532216 | SHN011 | 79.563 | 80.4752 | 81.7928 | 82.8064 | 82.9077 | 83.5158 | 85.1375 | 87.0632 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673 | 87.3673
| 10532256 | STL007 | 66.4883 | 65.1707 | 64.3599 | 63.6504 | 62.8396 | 61.7247 | 62.1301 | 61.522 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10533376 | BSPBBD | 342.0399 | 342.2325 | 344.7562 | 345.8711 | 343.9555 | 342.8811 | 345.6988 | 350.0063 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367
| 10534019 | BSPBBD | 342.0399 | 342.2325 | 344.7562 | 345.8711 | 343.9555 | 342.8811 | 345.6988 | 350.0063 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367 | 348.5367
| 10534244 | RCT011 | 39.9335 | 40.5417 | 41.2511 | 41.9606 | 42.1633 | 42.5688 | 43.3796 | 44.2918 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958
| 10534245 | RCT011 | 39.9335 | 40.5417 | 41.2511 | 41.9606 | 42.1633 | 42.5688 | 43.3796 | 44.2918 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958
| 10534246 | RCT011 | 39.9335 | 40.5417 | 41.2511 | 41.9606 | 42.1633 | 42.5688 | 43.3796 | 44.2918 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958
| 10534247 | RCT011 | 39.9335 | 40.5417 | 41.2511 | 41.9606 | 42.1633 | 42.5688 | 43.3796 | 44.2918 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958
| 10535259 | KYM001 | 81.3874 | 81.8942 | 83.1104 | 84.3267 | 84.428 | 84.6307 | 85.7456 | 87.4686 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768 | 88.0768
| 10537497 | WIN011 | 44.8999 | 45.0012 | 45.6094 | 46.0148 | 46.2175 | 46.3189 | 46.8256 | 47.5351 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378 | 47.7378
| 10538355 | KYM004 | 54.8326 | 55.3394 | 56.3529 | 57.0624 | 56.8597 | 57.0624 | 58.1773 | 59.3935 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922 | 59.2922
| 10540707 | RCT011 | 39.9335 | 40.5417 | 41.2511 | 41.9606 | 42.1633 | 42.5688 | 43.3796 | 44.2918 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958 | 44.5958
| 10541616 | SHL004 | 80.8806 | 80.7793 | 80.982 | 81.1847 | 80.5766 | 80.1711 | 80.5766 | 81.1847 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793 | 80.7793
| 10543005 | MRO005 | 59.9003 | 60.2044 | 60.6098 | 60.9139 | 60.9139 | 61.0152 | 61.3193 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233 | 61.6233
| 10551476 | STN024 | 122.1318 | 123.348 | 125.9832 | 127.8076 | 128.213 | 129.0239 | 131.9631 | 135.5105 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119 | 135.6119
| 10553394 | STN012 | 106.7259 | 108.753 | 111.1855 | 113.4153 | 115.037 | 116.8614 | 119.8006 | 122.7399 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616 | 124.3616
| 10554676 | MRO008 | 65.8802 | 66.0829 | 66.4883 | 66.7924 | 66.7924 | 66.8937 | 67.4005 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073 | 67.9073
| 10554851 | ECA010 | 81.3874 | 81.7928 | 82.9077 | 83.5158 | 83.8199 | 84.3267 | 85.5429 | 87.1646 | 87.4686 | 87.4686 | 87.4686 | 87.4686 | 87.4686 | 87.4686 | 87.4686 | 87.4686 | 87.4686 | 87.4686 | 87.4686 | 87.4686
| 10556318 | BMH003 | 77.6373 | 80.2725 | 83.0091 | 85.2389 | 87.2659 | 89.7998 | 93.5499 | 96.5905 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149 | 98.4149
| 10571996 | FNS013 | 115.8478 | 118.179 | 120.8142 | 123.6521 | 126.0846 | 128.6184 | 131.8618 | 135.7132 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593 | 139.1593
| 10579356 | CRO021 | 58.4814 | 58.1773 | 57.9746 | 57.7719 | 57.3665 | 56.961 | 56.961 | 57.0624 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556
| 10579357 | CRO021 | 58.4814 | 58.1773 | 57.9746 | 57.7719 | 57.3665 | 56.961 | 56.961 | 57.0624 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556 | 56.5556
| 10581766 | WMN013 | 71.9615 | 72.1642 | 72.8736 | 73.2791 | 73.0764 | 72.975 | 73.7858 | 75.0021 | 74.698 | 74.698 | 74.698 | 74.698 | 74.698 | 74.698 | 74.698 | 74.698 | 74.698 | 74.698 | 74.698 | 74.698

## Calcs
Powercor
Lines flood resilience program
| Total where option 2 is preferred option |  |  |  | 483 | 507 | 328 | [102 empty] | 73057964.1442 | 18629179.5849 | -10798229.3593 | 62259734.7849 | 100
| Feeders | ZSS | Identified | Spans part | Spans | No. unique | No. unique | VCR | Incremental | [100 empty] | Option 2 | Option 2 | Option 2 | Option 2 | Option 2
|  |  | spans | pf SubT | for | wood poles | concrete poles |  | VNR | Probability of flood | [19 empty] | Value of energy at risk ($ 2023) | [19 empty] | Value of incremental network resilience ($ 2023) | [19 empty] | Safety risk ($ 2023) | [19 empty] | Total risk ($ 2023) | [19 empty] | Total benefits | Total capex | Annualised capex | NPV ($2023) | preferred
|  |  |  | loop | remediation |  |  | ($ 2023) | ($ 2023) | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | PV ($ 2023) | ($ 2023) | PV ($ 2023)
| ART023 | ART | 1 | FALSE | 1 | 1 | 1 | 43695.1925 | 10892.5056 | 0.0097197 | 0.0098987 | 0.010078 | 0.010257 | 0.010436 | 0.010615 | 0.010794 | 0.010973 | 0.011152 | 0.011331 | 0.01151 | 0.011689 | 0.011868 | 0.012047 | 0.012226 | 0.012405 | 0.012584 | 0.012763 | 0.012942 | 0.013121 | 23675.0603 | 23891.849 | 24279.2346 | 24619.6112 | 24864.3843 | 25149.825 | 25526.1129 | 25852.221 | 26125.7713 | 26545.1048 | 26964.4383 | 27383.7718 | 27803.1053 | 28222.4388 | 28641.7722 | 29061.1057 | 29480.4392 | 29899.7727 | 30319.1062 | 30738.4397 | 5901.8101 | 5955.852 | 6052.421 | 6137.2713 | 6198.2893 | 6269.4451 | 6363.2476 | 6444.5411 | 6512.7327 | 6617.2658 | 6721.7989 | 6826.3319 | 6930.865 | 7035.398 | 7139.9311 | 7244.4642 | 7348.9972 | 7453.5303 | 7558.0634 | 7662.5964 | 0.00039363 | 0.00040088 | 0.00040813 | 0.00041537 | 0.00042262 | 0.00042987 | 0.00043712 | 0.00044437 | 0.00045162 | 0.00045887 | 0.00046611 | 0.00047336 | 0.00048061 | 0.00048786 | 0.00049511 | 0.00050236 | 0.00050961 | 0.00051686 | 0.0005241 | 0.00053135 | 29576.8708 | 29847.7014 | 30331.656 | 30756.8829 | 31062.6741 | 31419.2705 | 31889.3609 | 32296.7626 | 32638.5045 | 33162.3711 | 33686.2376 | 34210.1042 | 34733.9707 | 35257.8373 | 35781.7038 | 36305.5704 | 36829.4369 | 37353.3035 | 37877.1701 | 38401.0366 | 479164.8858 | 46500.5006 | -26953.5794 | 452211.3064 | TRUE
| BAN003 | BAN | 4 | FALSE | 4 | 8 | 0 | 44753.327 | 10611.3343 | 0.0096632 | 0.0098234 | 0.0099835 | 0.010144 | 0.010304 | 0.010464 | 0.010624 | 0.010784 | 0.010944 | 0.011105 | 0.011265 | 0.011425 | 0.011585 | 0.011745 | 0.011905 | 0.012066 | 0.012226 | 0.012386 | 0.012546 | 0.012706 | 45015.1504 | 46786.0653 | 49043.2437 | 50888.2577 | 52533.0014 | 54441.2177 | 56961.137 | 59189.4901 | 60713.8742 | 61602.3381 | 62490.8021 | 63379.266 | 64267.73 | 65156.1939 | 66044.6579 | 66933.1218 | 67821.5858 | 68710.0497 | 69598.5137 | 70486.9776 | 10673.4145 | 11093.3111 | 11628.5043 | 12065.9703 | 12455.9508 | 12908.4026 | 13505.8935 | 14034.252 | 14395.6944 | 14606.3555 | 14817.0167 | 15027.6778 | 15238.339 | 15449.0002 | 15659.6613 | 15870.3225 | 16080.9837 | 16291.6448 | 16502.306 | 16712.9672 | 0.0015654 | 0.0015913 | 0.0016172 | 0.0016432 | 0.0016691 | 0.0016951 | 0.001721 | 0.001747 | 0.0017729 | 0.0017989 | 0.0018248 | 0.0018507 | 0.0018767 | 0.0019026 | 0.0019286 | 0.0019545 | 0.0019805 | 0.0020064 | 0.0020324 | 0.0020583 | 55688.5665 | 57879.378 | 60671.7496 | 62954.2297 | 64988.9539 | 67349.622 | 70467.0322 | 73223.7438 | 75109.5703 | 76208.6954 | 77307.8206 | 78406.9457 | 79506.0709 | 80605.196 | 81704.3211 | 82803.4463 | 83902.5714 | 85001.6966 | 86100.8217 | 87199.9468 | 1048046.9047 | 150928.0615 | -87484.0364 | 960562.8684 | TRUE
| BAS011 | BAS | 1 | FALSE | 1 | 0 | 2 | 37239.5893 | 9753.9335 | 0.0096325 | 0.0097825 | 0.0099324 | 0.010082 | 0.010232 | 0.010382 | 0.010532 | 0.010682 | 0.010832 | 0.010982 | 0.011132 | 0.011282 | 0.011432 | 0.011582 | 0.011732 | 0.011882 | 0.012031 | 0.012181 | 0.012331 | 0.012481 | 78058.2905 | 47999.6586 | 49897.4814 | 51716.2264 | 53180.4566 | 54743.4322 | 56845.824 | 59066.2019 | 60672.0468 | 61511.8455 | 62351.6441 | 63191.4427 | 64031.2414 | 64871.04 | 65710.8386 | 66550.6373 | 67390.4359 | 68230.2345 | 69070.0332 | 69909.8318 | 20445.3214 | 12572.2513 | 13069.3363 | 13545.7088 | 13929.2255 | 14338.6059 | 14889.2723 | 15470.8421 | 15891.451 | 16111.4142 | 16331.3775 | 16551.3407 | 16771.3039 | 16991.2671 | 17211.2303 | 17431.1936 | 17651.1568 | 17871.12 | 18091.0832 | 18311.0464 | 0.0003901 | 0.00039617 | 0.00040224 | 0.00040831 | 0.00041439 | 0.00042046 | 0.00042653 | 0.0004326 | 0.00043867 | 0.00044474 | 0.00045082 | 0.00045689 | 0.00046296 | 0.00046903 | 0.0004751 | 0.00048118 | 0.00048725 | 0.00049332 | 0.00049939 | 0.00050546 | 98503.6124 | 60571.9103 | 62966.8181 | 65261.9355 | 67109.6825 | 69082.0385 | 71735.0968 | 74537.0444 | 76563.4983 | 77623.2601 | 78683.022 | 79742.7839 | 80802.5457 | 81862.3076 | 82922.0695 | 83981.8313 | 85041.5932 | 86101.355 | 87161.1169 | 88220.8788 | 1111478.233 | 55268.9859 | -32036.1497 | 1079442.0833 | TRUE
| BAS022 | BAS | 2 | FALSE | 2 | 3 | 1 | 37239.5893 | 9753.9335 | 0.0096345 | 0.0097851 | 0.0099357 | 0.010086 | 0.010237 | 0.010388 | 0.010538 | 0.010689 | 0.010839 | 0.01099 | 0.011141 | 0.011291 | 0.011442 | 0.011592 | 0.011743 | 0.011893 | 0.012044 | 0.012195 | 0.012345 | 0.012496 | 47419.2432 | 48899.1133 | 50589.2264 | 37346.3703 | 38174.4519 | 39167.3175 | 40570.4375 | 42078.1177 | 43448.2978 | 44051.9543 | 44655.6107 | 45259.2672 | 45862.9236 | 46466.5801 | 47070.2365 | 47673.893 | 48277.5494 | 48881.2059 | 49484.8624 | 50088.5188 | 12420.2268 | 12807.8399 | 13250.5207 | 9781.902 | 9998.7962 | 10258.8513 | 10626.3618 | 11021.2591 | 11380.1418 | 11538.2538 | 11696.3658 | 11854.4777 | 12012.5897 | 12170.7017 | 12328.8136 | 12486.9256 | 12645.0376 | 12803.1495 | 12961.2615 | 13119.3735 | 0.00078036 | 0.00079255 | 0.00080475 | 0.00081695 | 0.00082915 | 0.00084135 | 0.00085354 | 0.00086574 | 0.00087794 | 0.00089014 | 0.00090233 | 0.00091453 | 0.00092673 | 0.00093893 | 0.00095113 | 0.00096332 | 0.00097552 | 0.00098772 | 0.00099992 | 0.0010121 | 59839.4707 | 61706.954 | 63839.7479 | 47128.2731 | 48173.249 | 49426.1696 | 51196.8001 | 53099.3776 | 54828.4405 | 55590.209 | 56351.9774 | 57113.7458 | 57875.5143 | 58637.2827 | 59399.0511 | 60160.8196 | 60922.588 | 61684.3564 | 62446.1249 | 63207.8933 | 820206.7431 | 84232.516 | -48824.5885 | 771382.1546 | TRUE
| BAS033 | BAS | 2 | FALSE | 2 | 2 | 2 | 37239.5893 | 9753.9335 | 0.0096308 | 0.0097801 | 0.0099295 | 0.010079 | 0.010228 | 0.010378 | 0.010527 | 0.010676 | 0.010826 | 0.010975 | 0.011124 | 0.011274 | 0.011423 | 0.011572 | 0.011722 | 0.011871 | 0.01202 | 0.01217 | 0.012319 | 0.012469 | 38385.9774 | 31967.5885 | 33242.8011 | 34579.7314 | 35825.6495 | 37249.6647 | 39057.2047 | 40981.4155 | 42657.9383 | 43246.4589 | 43834.9796 | 44423.5002 | 45012.0209 | 45600.5415 | 46189.0622 | 46777.5828 | 47366.1035 | 47954.6241 | 48543.1448 | 49131.6654 | 10054.1998 | 8373.0712 | 8707.0797 | 9057.2535 | 9383.589 | 9756.5725 | 10230.0102 | 10734.0067 | 11173.1279 | 11327.2754 | 11481.4229 | 11635.5705 | 11789.718 | 11943.8656 | 12098.0131 | 12252.1607 | 12406.3082 | 12560.4558 | 12714.6033 | 12868.7508 | 0.00078005 | 0.00079215 | 0.00080425 | 0.00081635 | 0.00082844 | 0.00084054 | 0.00085264 | 0.00086473 | 0.00087683 | 0.00088893 | 0.00090102 | 0.00091312 | 0.00092522 | 0.00093732 | 0.00094941 | 0.00096151 | 0.00097361 | 0.0009857 | 0.0009978 | 0.0010099 | 48440.1779 | 40340.6605 | 41949.8816 | 43636.9857 | 45209.2394 | 47006.238 | 49287.2157 | 51715.423 | 53831.067 | 54573.7352 | 55316.4034 | 56059.0716 | 56801.7398 | 57544.408 | 58287.0762 | 59029.7444 | 59772.4127 | 60515.0809 | 61257.7491 | 62000.4173 | 750218.9345 | 93001.0013 | -53907.1588 | 696311.7757 | TRUE
| BATSBAS1 | BAS | 1 | TRUE | 0 | 0 | 0 | 37239.5893 | 9753.9335 | 0.0096271 | 0.0097752 | 0.0099233 | 0.010071 | 0.010219 | 0.010368 | 0.010516 | 0.010664 | 0.010812 | 0.01096 | 0.011108 | 0.011256 | 0.011404 | 0.011552 | 0.011701 | 0.011849 | 0.011997 | 0.012145 | 0.012293 | 0.012441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00038988 | 0.00039587 | 0.00040187 | 0.00040787 | 0.00041387 | 0.00041987 | 0.00042586 | 0.00043186 | 0.00043786 | 0.00044386 | 0.00044986 | 0.00045585 | 0.00046185 | 0.00046785 | 0.00047385 | 0.00047985 | 0.00048585 | 0.00049184 | 0.00049784 | 0.00050384 | 0.00038988 | 0.00039587 | 0.00040187 | 0.00040787 | 0.00041387 | 0.00041987 | 0.00042586 | 0.00043186 | 0.00043786 | 0.00044386 | 0.00044986 | 0.00045585 | 0.00046185 | 0.00046785 | 0.00047385 | 0.00047985 | 0.00048585 | 0.00049184 | 0.00049784 | 0.00050384 | 0.0063627 | 0 | 0 | 0.0063627 | TRUE
| BBD014 | BBD | 1 | FALSE | 1 | 0 | 2 | 52622.2251 | 10836.9058 | 0.0097225 | 0.0099024 | 0.010082 | 0.010262 | 0.010442 | 0.010622 | 0.010802 | 0.010982 | 0.011162 | 0.011342 | 0.011522 | 0.011701 | 0.011881 | 0.012061 | 0.012241 | 0.012421 | 0.012601 | 0.012781 | 0.012961 | 0.013141 | 63988.563 | 64644.4988 | 65550.1122 | 66336.6636 | 66719.9321 | 67246.2903 | 68270.0451 | 69465.676 | 69889.3238 | 71015.8283 | 72142.3328 | 73268.8374 | 74395.3419 | 75521.8464 | 76648.3509 | 77774.8554 | 78901.36 | 80027.8645 | 81154.369 | 82280.8735 | 13177.6645 | 13312.7465 | 13499.2465 | 13661.2272 | 13740.1567 | 13848.5537 | 14059.3836 | 14305.6092 | 14392.8543 | 14624.8441 | 14856.834 | 15088.8239 | 15320.8137 | 15552.8036 | 15784.7935 | 16016.7834 | 16248.7732 | 16480.7631 | 16712.753 | 16944.7429 | 0.00039374 | 0.00040103 | 0.00040831 | 0.0004156 | 0.00042288 | 0.00043017 | 0.00043746 | 0.00044474 | 0.00045203 | 0.00045931 | 0.0004666 | 0.00047389 | 0.00048117 | 0.00048846 | 0.00049574 | 0.00050303 | 0.00051031 | 0.0005176 | 0.00052489 | 0.00053217 | 77166.2279 | 77957.2457 | 79049.3591 | 79997.8912 | 80460.0892 | 81094.8444 | 82329.4291 | 83771.2857 | 84282.1785 | 85640.6729 | 86999.1673 | 88357.6617 | 89716.1561 | 91074.6505 | 92433.1449 | 93791.6393 | 95150.1337 | 96508.6281 | 97867.1225 | 99225.6169 | 1240801.3067 | 55268.9859 | -32036.1497 | 1208765.157 | TRUE
| BET005 | BETS | 1 | FALSE | 1 | 2 | 0 | 39529.3474 | 10836.9965 | 0.009782 | 0.0099818 | 0.010182 | 0.010381 | 0.010581 | 0.010781 | 0.010981 | 0.01118 | 0.01138 | 0.01158 | 0.01178 | 0.011979 | 0.012179 | 0.012379 | 0.012579 | 0.012779 | 0.012978 | 0.013178 | 0.013378 | 0.013578 | 46520.1493 | 48309.995 | 50378.2079 | 52406.4551 | 53966.0066 | 55762.333 | 58115.3939 | 60785.2391 | 62692.0143 | 63792.5003 | 64892.9864 | 65993.4725 | 67093.9585 | 68194.4446 | 69294.9306 | 70395.4167 | 71495.9028 | 72596.3888 | 73696.8749 | 74797.361 | 12753.5294 | 13244.2167 | 13811.2187 | 14367.264 | 14794.816 | 15287.2801 | 15932.3733 | 16664.3131 | 17187.0568 | 17488.7557 | 17790.4547 | 18092.1537 | 18393.8527 | 18695.5516 | 18997.2506 | 19298.9496 | 19600.6486 | 19902.3475 | 20204.0465 | 20505.7455 | 0.00039615 | 0.00040424 | 0.00041233 | 0.00042042 | 0.00042851 | 0.0004366 | 0.00044469 | 0.00045278 | 0.00046087 | 0.00046896 | 0.00047705 | 0.00048514 | 0.00049323 | 0.00050132 | 0.00050941 | 0.0005175 | 0.00052559 | 0.00053368 | 0.00054177 | 0.00054986 | 59273.6791 | 61554.2121 | 64189.427 | 66773.7195 | 68760.8231 | 71049.6135 | 74047.7677 | 77449.5526 | 79879.0715 | 81281.2565 | 82683.4416 | 84085.6266 | 85487.8117 | 86889.9967 | 88292.1818 | 89694.3668 | 91096.5519 | 92498.7369 | 93900.922 | 95303.107 | 1121223.2693 | 37732.0154 | -21871.0091 | 1099352.2602 | TRUE
| BET006 | BETS | 5 | FALSE | 5 | 6 | 3 | 39529.3474 | 10836.9965 | 0.0098166 | 0.010028 | 0.010239 | 0.01045 | 0.010662 | 0.010873 | 0.011084 | 0.011296 | 0.011507 | 0.011718 | 0.01193 | 0.012141 | 0.012352 | 0.012563 | 0.012775 | 0.012986 | 0.013197 | 0.013409 | 0.01362 | 0.013831 | 63242.4919 | 65487.6015 | 67934.0506 | 70466.389 | 72531.8477 | 74753.3901 | 77627.1355 | 80690.826 | 83306.6499 | 84836.3382 | 86366.0265 | 87895.7148 | 89425.4031 | 90955.0914 | 92484.7797 | 94014.468 | 95544.1563 | 97073.8446 | 98603.5329 | 100133.2212 | 17337.9706 | 17953.4688 | 18624.1644 | 19318.4067 | 19884.6535 | 20493.6908 | 21281.53 | 22121.4428 | 22838.5726 | 23257.9377 | 23677.3027 | 24096.6678 | 24516.0328 | 24935.3979 | 25354.7629 | 25774.128 | 26193.493 | 26612.858 | 27032.2231 | 27451.5881 | 0.0019878 | 0.0020305 | 0.0020733 | 0.0021161 | 0.0021589 | 0.0022017 | 0.0022445 | 0.0022873 | 0.00233 | 0.0023728 | 0.0024156 | 0.0024584 | 0.0025012 | 0.002544 | 0.0025867 | 0.0026295 | 0.0026723 | 0.0027151 | 0.0027579 | 0.0028007 | 80580.4645 | 83441.0724 | 86558.2171 | 89784.7978 | 92416.5033 | 95247.0832 | 98908.6678 | 102812.2711 | 106145.2249 | 108094.2783 | 110043.3317 | 111992.385 | 113941.4384 | 115890.4918 | 117839.5452 | 119788.5986 | 121737.652 | 123686.7053 | 125635.7587 | 127584.8121 | 1500525.8079 | 196099.525 | -113667.2519 | 1386858.556 | TRUE
| BETSMRO | BETS | 1 | TRUE | 0 | 0 | 0 | 39529.3474 | 10836.9965 | 0.0097306 | 0.0099132 | 0.010096 | 0.010278 | 0.010461 | 0.010644 | 0.010826 | 0.011009 | 0.011191 | 0.011374 | 0.011557 | 0.011739 | 0.011922 | 0.012105 | 0.012287 | 0.01247 | 0.012652 | 0.012835 | 0.013018 | 0.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00039407 | 0.00040146 | 0.00040886 | 0.00041625 | 0.00042365 | 0.00043105 | 0.00043844 | 0.00044584 | 0.00045323 | 0.00046063 | 0.00046802 | 0.00047542 | 0.00048281 | 0.00049021 | 0.00049761 | 0.000505 | 0.0005124 | 0.00051979 | 0.00052719 | 0.00053458 | 0.00039407 | 0.00040146 | 0.00040886 | 0.00041625 | 0.00042365 | 0.00043105 | 0.00043844 | 0.00044584 | 0.00045323 | 0.00046063 | 0.00046802 | 0.00047542 | 0.00048281 | 0.00049021 | 0.00049761 | 0.000505 | 0.0005124 | 0.00051979 | 0.00052719 | 0.00053458 | 0.0065923 | 0 | 0 | 0.0065923 | TRUE
| BMH003 | BMH | 10 | FALSE | 10 | 15 | 0 | 38093.4326 | 10804.6535 | 0.0096222 | 0.0097686 | 0.0099151 | 0.010062 | 0.010208 | 0.010355 | 0.010501 | 0.010648 | 0.010794 | 0.01094 | 0.011087 | 0.011233 | 0.01138 | 0.011526 | 0.011673 | 0.011819 | 0.011966 | 0.012112 | 0.012259 | 0.012405 | 28457.2751 | 29871.0914 | 31352.597 | 32670.4061 | 33934.2734 | 35420.653 | 37421.8336 | 39177.0992 | 40466.1997 | 41015.334 | 41564.4682 | 42113.6025 | 42662.7368 | 43211.8711 | 43761.0053 | 44310.1396 | 44859.2739 | 45408.4082 | 45957.5424 | 46506.6767 | 8071.4962 | 8472.5048 | 8892.7126 | 9266.4901 | 9624.9679 | 10046.5581 | 10614.1641 | 11112.0199 | 11477.6547 | 11633.4087 | 11789.1628 | 11944.9168 | 12100.6708 | 12256.4249 | 12412.1789 | 12567.9329 | 12723.6869 | 12879.441 | 13035.195 | 13190.949 | 0.0038968 | 0.0039561 | 0.0040154 | 0.0040747 | 0.0041341 | 0.0041934 | 0.0042527 | 0.004312 | 0.0043713 | 0.0044307 | 0.00449 | 0.0045493 | 0.0046086 | 0.0046679 | 0.0047273 | 0.0047866 | 0.0048459 | 0.0049052 | 0.0049645 | 0.0050239 | 36528.7752 | 38343.6002 | 40245.3136 | 41936.9003 | 43559.2455 | 45467.2152 | 48036.002 | 50289.1235 | 51943.8588 | 52648.7471 | 53353.6355 | 54058.5239 | 54763.4122 | 55468.3006 | 56173.189 | 56878.0773 | 57582.9657 | 58287.854 | 58992.7424 | 59697.6308 | 713227.7398 | 282990.1152 | -164032.5682 | 549195.1716 | TRUE
| BMH005 | BBD | 1 | FALSE | 1 | 2 | 0 | 52622.2251 | 10836.9058 | 0.0096205 | 0.0097665 | 0.0099124 | 0.010058 | 0.010204 | 0.01035 | 0.010496 | 0.010642 | 0.010788 | 0.010934 | 0.01108 | 0.011226 | 0.011372 | 0.011518 | 0.011664 | 0.011809 | 0.011955 | 0.012101 | 0.012247 | 0.012393 | 57365.5994 | 60267.239 | 63599.6603 | 66789.1034 | 69771.8042 | 73253.7207 | 77141.5706 | 81052.0499 | 84695.1363 | 85840.8205 | 86986.5048 | 88132.189 | 89277.8733 | 90423.5576 | 91569.2418 | 92714.9261 | 93860.6103 | 95006.2946 | 96151.9789 | 97297.6631 | 11813.7459 | 12411.3032 | 13097.5747 | 13754.4017 | 14368.6525 | 15085.7108 | 15886.3661 | 16691.6816 | 17441.9308 | 17677.8706 | 17913.8103 | 18149.75 | 18385.6897 | 18621.6294 | 18857.5691 | 19093.5088 | 19329.4485 | 19565.3882 | 19801.3279 | 20037.2676 | 0.00038961 | 0.00039552 | 0.00040143 | 0.00040734 | 0.00041325 | 0.00041916 | 0.00042507 | 0.00043098 | 0.00043689 | 0.0004428 | 0.00044871 | 0.00045462 | 0.00046053 | 0.00046644 | 0.00047235 | 0.00047826 | 0.00048417 | 0.00049008 | 0.00049599 | 0.0005019 | 69179.3457 | 72678.5426 | 76697.2354 | 80543.5054 | 84140.4572 | 88339.4318 | 93027.9371 | 97743.732 | 102137.0676 | 103518.6915 | 104900.3155 | 106281.9395 | 107663.5634 | 109045.1874 | 110426.8114 | 111808.4354 | 113190.0593 | 114571.6833 | 115953.3073 | 117334.9312 | 1388940.4307 | 37732.0154 | -21871.0091 | 1367069.4216 | TRUE
| BMH006 | BMH | 5 | FALSE | 5 | 8 | 1 | 38093.4326 | 10804.6535 | 0.0096121 | 0.0097553 | 0.0098984 | 0.010042 | 0.010185 | 0.010328 | 0.010471 | 0.010614 | 0.010757 | 0.0109 | 0.011043 | 0.011187 | 0.01133 | 0.011473 | 0.011616 | 0.011759 | 0.011902 | 0.012045 | 0.012188 | 0.012332 | 19223.877 | 19547.7962 | 20025.6884 | 20586.646 | 20998.0513 | 21412.7724 | 22154.2286 | 22866.8623 | 23465.9503 | 23778.178 | 24090.4057 | 24402.6335 | 24714.8612 | 25027.0889 | 25339.3167 | 25651.5444 | 25963.7721 | 26275.9998 | 26588.2276 | 26900.4553 | 5452.5758 | 5544.4508 | 5679.9981 | 5839.1056 | 5955.7948 | 6073.4245 | 6283.7279 | 6485.8561 | 6655.7788 | 6744.3377 | 6832.8966 | 6921.4555 | 7010.0144 | 7098.5733 | 7187.1322 | 7275.6911 | 7364.25 | 7452.8089 | 7541.3678 | 7629.9267 | 0.0019464 | 0.0019753 | 0.0020043 | 0.0020333 | 0.0020623 | 0.0020913 | 0.0021202 | 0.0021492 | 0.0021782 | 0.0022072 | 0.0022362 | 0.0022652 | 0.0022941 | 0.0023231 | 0.0023521 | 0.0023811 | 0.0024101 | 0.0024391 | 0.002468 | 0.002497 | 24676.4548 | 25092.249 | 25705.6885 | 26425.7536 | 26953.8482 | 27486.199 | 28437.9586 | 29352.7205 | 30121.7313 | 30522.5179 | 30923.3046 | 31324.0912 | 31724.8779 | 32125.6646 | 32526.4512 | 32927.2379 | 33328.0245 | 33728.8112 | 34129.5979 | 34530.3845 | 426470.3362 | 178562.5544 | -103502.1112 | 322968.225 | TRUE
| BSPBBD | BBD | 2 | FALSE | 2 | 4 | 0 | 52622.2251 | 10836.9058 | 0.0097177 | 0.009896 | 0.010074 | 0.010253 | 0.010431 | 0.010609 | 0.010788 | 0.010966 | 0.011144 | 0.011322 | 0.011501 | 0.011679 | 0.011857 | 0.012036 | 0.012214 | 0.012392 | 0.012571 | 0.012749 | 0.012927 | 0.013106 | 174907.1923 | 178216.8171 | 182765.8678 | 186602.1991 | 188796.0268 | 191423.5535 | 196240.2617 | 201969.5893 | 204391.8448 | 207662.1468 | 210932.4489 | 214202.7509 | 217473.0529 | 220743.3549 | 224013.6569 | 227283.9589 | 230554.261 | 233824.563 | 237094.865 | 240365.167 | 36020.0041 | 36701.5809 | 37638.4025 | 38428.4481 | 38880.2402 | 39421.3473 | 40413.2897 | 41593.1748 | 42092.0088 | 42765.4877 | 43438.9665 | 44112.4453 | 44785.9242 | 45459.403 | 46132.8818 | 46806.3607 | 47479.8395 | 48153.3183 | 48826.7972 | 49500.276 | 0.00078709 | 0.00080153 | 0.00081597 | 0.00083042 | 0.00084486 | 0.0008593 | 0.00087374 | 0.00088818 | 0.00090263 | 0.00091707 | 0.00093151 | 0.00094595 | 0.0009604 | 0.00097484 | 0.00098928 | 0.0010037 | 0.0010182 | 0.0010326 | 0.001047 | 0.0010615 | 210927.1972 | 214918.3989 | 220404.2711 | 225030.6481 | 227676.2678 | 230844.9017 | 236653.5523 | 243562.765 | 246483.8545 | 250427.6354 | 254371.4163 | 258315.1971 | 262258.978 | 266202.7589 | 270146.5397 | 274090.3206 | 278034.1015 | 281977.8823 | 285921.6632 | 289865.4441 | 3566759.1277 | 75464.0307 | -43742.0182 | 3523017.1096 | TRUE
| CDN004 | CDN | 3 | FALSE | 3 | 6 | 0 | 45429.2584 | 10860.1496 | 0.0095977 | 0.009736 | 0.0098743 | 0.010013 | 0.010151 | 0.010289 | 0.010428 | 0.010566 | 0.010704 | 0.010842 | 0.010981 | 0.011119 | 0.011257 | 0.011396 | 0.011534 | 0.011672 | 0.011811 | 0.011949 | 0.012087 | 0.012226 | 5965.9115 | 6007.0568 | 6137.8597 | 6316.0387 | 6356.5472 | 6443.1582 | 6577.7821 | 6762.3296 | 6850.8511 | 6939.3726 | 7027.8941 | 7116.4155 | 7204.937 | 7293.4585 | 7381.98 | 7470.5015 | 7559.0229 | 7647.5444 | 7736.0659 | 7824.5874 | 1426.1886 | 1436.0247 | 1467.2939 | 1509.8887 | 1519.5725 | 1540.2774 | 1572.4601 | 1616.5774 | 1637.739 | 1658.9006 | 1680.0622 | 1701.2238 | 1722.3855 | 1743.5471 | 1764.7087 | 1785.8703 | 1807.0319 | 1828.1935 | 1849.3552 | 1870.5168 | 0.0011661 | 0.0011829 | 0.0011997 | 0.0012165 | 0.0012333 | 0.0012501 | 0.0012669 | 0.0012837 | 0.0013005 | 0.0013173 | 0.0013341 | 0.0013509 | 0.0013677 | 0.0013845 | 0.0014013 | 0.0014181 | 0.0014349 | 0.0014517 | 0.0014685 | 0.0014853 | 7392.1013 | 7443.0827 | 7605.1548 | 7825.9287 | 7876.121 | 7983.4368 | 8150.2435 | 8378.9083 | 8488.5914 | 8598.2745 | 8707.9576 | 8817.6407 | 8927.3238 | 9037.0069 | 9146.6901 | 9256.3732 | 9366.0563 | 9475.7394 | 9585.4225 | 9695.1056 | 122138.5843 | 113196.0461 | -65613.0273 | 56525.557 | TRUE
| CHA005 | CHA | 1 | FALSE | 1 | 2 | 0 | 48008.7507 | 11465.9097 | 0.009738 | 0.009923 | 0.010108 | 0.010293 | 0.010478 | 0.010663 | 0.010848 | 0.011033 | 0.011219 | 0.011404 | 0.011589 | 0.011774 | 0.011959 | 0.012144 | 0.012329 | 0.012514 | 0.012699 | 0.012884 | 0.013069 | 0.013254 | 25066.0291 | 25590.7028 | 26412.2869 | 27096.2223 | 27430.4603 | 27863.068 | 28821.7454 | 29957.6955 | 30296.4362 | 30796.2397 | 31296.0432 | 31795.8468 | 32295.6503 | 32795.4538 | 33295.2574 | 33795.0609 | 34294.8644 | 34794.668 | 35294.4715 | 35794.2751 | 5986.5092 | 6111.8168 | 6308.0354 | 6471.3794 | 6551.2053 | 6654.5248 | 6883.4853 | 7154.7838 | 7235.6851 | 7355.053 | 7474.4208 | 7593.7887 | 7713.1566 | 7832.5244 | 7951.8923 | 8071.2602 | 8190.628 | 8309.9959 | 8429.3638 | 8548.7316 | 0.00039437 | 0.00040186 | 0.00040936 | 0.00041685 | 0.00042435 | 0.00043184 | 0.00043934 | 0.00044683 | 0.00045433 | 0.00046182 | 0.00046932 | 0.00047681 | 0.00048431 | 0.0004918 | 0.0004993 | 0.00050679 | 0.00051429 | 0.00052178 | 0.00052928 | 0.00053677 | 31052.5387 | 31702.52 | 32720.3227 | 33567.6021 | 33981.666 | 34517.5932 | 35705.2311 | 37112.4797 | 37532.1217 | 38151.2931 | 38770.4645 | 39389.6359 | 40008.8074 | 40627.9788 | 41247.1502 | 41866.3216 | 42485.493 | 43104.6644 | 43723.8358 | 44343.0072 | 539054.1441 | 37732.0154 | -21871.0091 | 517183.135 | TRUE
| CHA006 | CHA | 2 | FALSE | 2 | 3 | 1 | 48008.7507 | 11465.9097 | 0.0097357 | 0.00992 | 0.010104 | 0.010289 | 0.010473 | 0.010657 | 0.010842 | 0.011026 | 0.01121 | 0.011395 | 0.011579 | 0.011763 | 0.011948 | 0.012132 | 0.012316 | 0.012501 | 0.012685 | 0.012869 | 0.013053 | 0.013238 | 34487.407 | 35623.0361 | 36973.2693 | 38098.2979 | 38780.8273 | 39618.9284 | 41042.7061 | 42652.5496 | 43256.4773 | 43967.707 | 44678.9367 | 45390.1664 | 46101.3961 | 46812.6258 | 47523.8554 | 48235.0851 | 48946.3148 | 49657.5445 | 50368.7742 | 51080.0039 | 8236.6129 | 8507.8347 | 8830.3103 | 9099.0004 | 9262.0087 | 9462.172 | 9802.2122 | 10186.6905 | 10330.9263 | 10500.7889 | 10670.6516 | 10840.5143 | 11010.377 | 11180.2397 | 11350.1024 | 11519.9651 | 11689.8278 | 11859.6905 | 12029.5531 | 12199.4158 | 0.00078855 | 0.00080348 | 0.00081841 | 0.00083334 | 0.00084827 | 0.0008632 | 0.00087813 | 0.00089306 | 0.00090798 | 0.00092291 | 0.00093784 | 0.00095277 | 0.0009677 | 0.00098263 | 0.00099756 | 0.0010125 | 0.0010274 | 0.0010423 | 0.0010573 | 0.0010722 | 42724.0207 | 44130.8716 | 45803.5804 | 47197.2992 | 48042.8368 | 49081.1012 | 50844.9192 | 52839.241 | 53587.4045 | 54468.4969 | 55349.5892 | 56230.6816 | 57111.774 | 57992.8664 | 58873.9588 | 59755.0512 | 60636.1436 | 61517.236 | 62398.3284 | 63279.4208 | 764592.9783 | 84232.516 | -48824.5885 | 715768.3898 | TRUE
| CHM011 | CHM | 3 | FALSE | 3 | 4 | 2 | 43924.3002 | 11308.0279 | 0.0095823 | 0.0097155 | 0.0098487 | 0.0099819 | 0.010115 | 0.010248 | 0.010381 | 0.010515 | 0.010648 | 0.010781 | 0.010914 | 0.011047 | 0.011181 | 0.011314 | 0.011447 | 0.01158 | 0.011713 | 0.011847 | 0.01198 | 0.012113 | 9939.6854 | 10034.5918 | 10172.1577 | 10309.7237 | 10357.2268 | 10447.9825 | 10537.5522 | 10719.5567 | 10760.5372 | 10895.1384 | 11029.7396 | 11164.3408 | 11298.9419 | 11433.5431 | 11568.1443 | 11702.7454 | 11837.3466 | 11971.9478 | 12106.549 | 12241.1501 | 2558.9079 | 2583.341 | 2618.7564 | 2654.1719 | 2666.4013 | 2689.7657 | 2712.8249 | 2759.6808 | 2770.2309 | 2804.8831 | 2839.5354 | 2874.1876 | 2908.8398 | 2943.492 | 2978.1442 | 3012.7964 | 3047.4486 | 3082.1008 | 3116.753 | 3151.4052 | 0.0011642 | 0.0011804 | 0.0011966 | 0.0012127 | 0.0012289 | 0.0012451 | 0.0012613 | 0.0012775 | 0.0012936 | 0.0013098 | 0.001326 | 0.0013422 | 0.0013584 | 0.0013746 | 0.0013907 | 0.0014069 | 0.0014231 | 0.0014393 | 0.0014555 | 0.0014716 | 12498.5945 | 12617.9339 | 12790.9154 | 12963.8968 | 13023.6293 | 13137.7495 | 13250.3784 | 13479.2387 | 13530.7695 | 13700.0229 | 13869.2763 | 14038.5297 | 14207.783 | 14377.0364 | 14546.2898 | 14715.5432 | 14884.7966 | 15054.05 | 15223.3034 | 15392.5568 | 197987.7922 | 130733.0166 | -75778.1679 | 122209.6243 | TRUE
| CLC003 | CLC | 8 | FALSE | 8 | 12 | 2 | 44906.1835 | 10807.394 | 0.0095863 | 0.0097209 | 0.0098554 | 0.0099899 | 0.010124 | 0.010259 | 0.010394 | 0.010528 | 0.010663 | 0.010797 | 0.010932 | 0.011066 | 0.011201 | 0.011335 | 0.01147 | 0.011604 | 0.011739 | 0.011873 | 0.012008 | 0.012142 | 30542.0689 | 31368.8865 | 32520.719 | 33555.7402 | 34145.8737 | 34926.4536 | 36094.0495 | 37567.5214 | 38484.3499 | 38969.9185 | 39455.4871 | 39941.0557 | 40426.6243 | 40912.193 | 41397.7616 | 41883.3302 | 42368.8988 | 42854.4675 | 43340.0361 | 43825.6047 | 7350.4392 | 7549.4261 | 7826.6331 | 8075.7276 | 8217.7527 | 8405.6118 | 8686.6125 | 9041.2271 | 9261.8766 | 9378.7365 | 9495.5964 | 9612.4563 | 9729.3162 | 9846.176 | 9963.0359 | 10079.8958 | 10196.7557 | 10313.6156 | 10430.4755 | 10547.3354 | 0.0031058 | 0.0031494 | 0.003193 | 0.0032366 | 0.0032802 | 0.0033237 | 0.0033673 | 0.0034109 | 0.0034545 | 0.0034981 | 0.0035417 | 0.0035853 | 0.0036289 | 0.0036724 | 0.003716 | 0.0037596 | 0.0038032 | 0.0038468 | 0.0038904 | 0.003934 | 37892.5112 | 38918.3157 | 40347.3553 | 41631.471 | 42363.6297 | 43332.0687 | 44780.6653 | 46608.752 | 47746.2299 | 48348.6585 | 48951.087 | 49553.5156 | 50155.9441 | 50758.3727 | 51360.8012 | 51963.2298 | 52565.6583 | 53168.0869 | 53770.5155 | 54372.944 | 671466.2009 | 281661.0781 | -163262.2043 | 508203.9966 | TRUE
| CLC006 | CLC | 6 | FALSE | 6 | 3 | 5 | 44906.1835 | 10807.394 | 0.0096313 | 0.0097808 | 0.0099303 | 0.01008 | 0.010229 | 0.010379 | 0.010528 | 0.010678 | 0.010827 | 0.010977 | 0.011126 | 0.011276 | 0.011425 | 0.011575 | 0.011724 | 0.011874 | 0.012023 | 0.012173 | 0.012323 | 0.012472 | 53830.6876 | 54666.339 | 55592.3845 | 56521.152 | 57266.4092 | 57961.7059 | 58988.353 | 60020.4441 | 60959.419 | 61801.1949 | 62642.9707 | 63484.7466 | 64326.5225 | 65168.2983 | 66010.0742 | 66851.85 | 67693.6259 | 68535.4017 | 69377.1776 | 70218.9534 | 12955.2192 | 13156.3321 | 13379.1998 | 13602.7226 | 13782.0807 | 13949.4151 | 14196.4942 | 14444.8834 | 14670.8628 | 14873.4497 | 15076.0366 | 15278.6235 | 15481.2103 | 15683.7972 | 15886.3841 | 16088.971 | 16291.5578 | 16494.1447 | 16696.7316 | 16899.3184 | 0.0023403 | 0.0023766 | 0.0024129 | 0.0024493 | 0.0024856 | 0.0025219 | 0.0025583 | 0.0025946 | 0.0026309 | 0.0026672 | 0.0027036 | 0.0027399 | 0.0027762 | 0.0028126 | 0.0028489 | 0.0028852 | 0.0029216 | 0.0029579 | 0.0029942 | 0.0030305 | 66785.9091 | 67822.6735 | 68971.5867 | 70123.877 | 71048.4924 | 71911.1235 | 73184.8497 | 74465.3301 | 75630.2845 | 76674.6473 | 77719.01 | 78763.3728 | 79807.7356 | 80852.0983 | 81896.4611 | 82940.8239 | 83985.1866 | 85029.5494 | 86073.9122 | 87118.2749 | 1096274.5453 | 194770.4878 | -112896.8879 | 983377.6574 | TRUE
| CLC013 | CLC | 10 | FALSE | 10 | 14 | 2 | 44906.1835 | 10807.394 | 0.0096052 | 0.009746 | 0.0098869 | 0.010028 | 0.010169 | 0.010309 | 0.01045 | 0.010591 | 0.010732 | 0.010873 | 0.011013 | 0.011154 | 0.011295 | 0.011436 | 0.011577 | 0.011718 | 0.011858 | 0.011999 | 0.01214 | 0.012281 | 29596.6971 | 30341.1298 | 31454.5305 | 32495.8792 | 33276.2053 | 34065.5046 | 34911.3404 | 36153.0641 | 37024.538 | 37510.3792 | 37996.2204 | 38482.0616 | 38967.9027 | 39453.7439 | 39939.5851 | 40425.4263 | 40911.2675 | 41397.1087 | 41882.9498 | 42368.791 | 7122.9203 | 7302.08 | 7570.0377 | 7820.655 | 8008.453 | 8198.4106 | 8401.9745 | 8700.8153 | 8910.5495 | 9027.4749 | 9144.4004 | 9261.3259 | 9378.2514 | 9495.1769 | 9612.1024 | 9729.0278 | 9845.9533 | 9962.8788 | 10079.8043 | 10196.7298 | 0.0038899 | 0.0039469 | 0.004004 | 0.004061 | 0.004118 | 0.0041751 | 0.0042321 | 0.0042891 | 0.0043462 | 0.0044032 | 0.0044602 | 0.0045172 | 0.0045743 | 0.0046313 | 0.0046883 | 0.0047454 | 0.0048024 | 0.0048594 | 0.0049165 | 0.0049735 | 36719.6213 | 37643.2138 | 39024.5723 | 40316.5383 | 41284.6624 | 42263.9194 | 43313.3192 | 44853.8837 | 45935.0918 | 46537.8585 | 47140.6253 | 47743.392 | 48346.1587 | 48948.9254 | 49551.6922 | 50154.4589 | 50757.2256 | 51359.9923 | 51962.759 | 52565.5258 | 648876.761 | 319393.0935 | -185133.2134 | 463743.5476 | TRUE
| CME014 | CME | 6 | FALSE | 6 | 4 | 5 | 46875.2879 | 11543.2868 | 0.0096986 | 0.0098705 | 0.010042 | 0.010214 | 0.010386 | 0.010558 | 0.01073 | 0.010902 | 0.011074 | 0.011246 | 0.011418 | 0.01159 | 0.011762 | 0.011934 | 0.012106 | 0.012278 | 0.01245 | 0.012622 | 0.012793 | 0.012965 | 57643.4422 | 59415.6829 | 61500.334 | 63378.2853 | 64839.9018 | 66565.4001 | 68618.0126 | 70753.4629 | 72763.7498 | 73893.503 | 75023.2563 | 76153.0095 | 77282.7627 | 78412.516 | 79542.2692 | 80672.0225 | 81801.7757 | 82931.529 | 84061.2822 | 85191.0355 | 14195.0016 | 14631.4252 | 15144.7815 | 15607.2369 | 15967.1677 | 16392.0808 | 16897.5474 | 17423.4133 | 17918.4571 | 18196.6648 | 18474.8725 | 18753.0801 | 19031.2878 | 19309.4955 | 19587.7032 | 19865.9109 | 20144.1186 | 20422.3263 | 20700.534 | 20978.7417 | 0.0023566 | 0.0023984 | 0.0024402 | 0.002482 | 0.0025237 | 0.0025655 | 0.0026073 | 0.0026491 | 0.0026909 | 0.0027326 | 0.0027744 | 0.0028162 | 0.002858 | 0.0028998 | 0.0029415 | 0.0029833 | 0.0030251 | 0.0030669 | 0.0031087 | 0.0031504 | 71838.4461 | 74047.1105 | 76645.1179 | 78985.5247 | 80807.072 | 82957.4834 | 85515.5627 | 88176.8789 | 90682.2095 | 92090.1705 | 93498.1315 | 94906.0925 | 96314.0534 | 97722.0144 | 99129.9754 | 100537.9364 | 101945.8974 | 103353.8583 | 104761.8193 | 106169.7803 | 1286198.808 | 213636.4955 | -123832.3925 | 1162366.4155 | TRUE
| CME015 | CME | 3 | FALSE | 3 | 0 | 5 | 46875.2879 | 11543.2868 | 0.0097146 | 0.0098918 | 0.010069 | 0.010246 | 0.010424 | 0.010601 | 0.010778 | 0.010955 | 0.011133 | 0.01131 | 0.011487 | 0.011665 | 0.011842 | 0.012019 | 0.012196 | 0.012374 | 0.012551 | 0.012728 | 0.012905 | 0.013083 | 40476.991 | 41215.6267 | 42289.1311 | 43374.4268 | 44075.3308 | 44724.1854 | 45932.9514 | 47260.9766 | 48237.2885 | 49005.4022 | 49773.516 | 50541.6298 | 51309.7435 | 52077.8573 | 52845.971 | 53614.0848 | 54382.1986 | 55150.3123 | 55918.4261 | 56686.5399 | 9967.6725 | 10149.5654 | 10413.9215 | 10681.1813 | 10853.7826 | 11013.5665 | 11311.2315 | 11638.2647 | 11878.6866 | 12067.8387 | 12256.9908 | 12446.1428 | 12635.2949 | 12824.447 | 13013.599 | 13202.7511 | 13391.9032 | 13581.0552 | 13770.2073 | 13959.3594 | 0.0011803 | 0.0012018 | 0.0012233 | 0.0012449 | 0.0012664 | 0.0012879 | 0.0013095 | 0.001331 | 0.0013526 | 0.0013741 | 0.0013956 | 0.0014172 | 0.0014387 | 0.0014602 | 0.0014818 | 0.0015033 | 0.0015249 | 0.0015464 | 0.0015679 | 0.0015895 | 50444.6647 | 51365.1933 | 52703.0539 | 54055.6093 | 54929.1147 | 55737.7532 | 57244.1842 | 58899.2426 | 60115.9765 | 61073.2423 | 62030.5082 | 62987.774 | 63945.0399 | 64902.3057 | 65859.5716 | 66816.8374 | 67774.1033 | 68731.3691 | 69688.635 | 70645.9008 | 864306.4828 | 138172.4648 | -80090.3743 | 784216.1085 | TRUE
| CME016 | CME | 12 | FALSE | 12 | 11 | 7 | 46875.2879 | 11543.2868 | 0.0097042 | 0.009878 | 0.010052 | 0.010226 | 0.0104 | 0.010573 | 0.010747 | 0.010921 | 0.011095 | 0.011269 | 0.011442 | 0.011616 | 0.01179 | 0.011964 | 0.012138 | 0.012312 | 0.012485 | 0.012659 | 0.012833 | 0.013007 | 42831.3233 | 44161.6983 | 45655.1629 | 47173.4028 | 48321.1529 | 49530.6987 | 51264.0562 | 53338.458 | 54714.5392 | 55571.7638 | 56428.9884 | 57286.213 | 58143.4376 | 59000.6623 | 59857.8869 | 60715.1115 | 61572.3361 | 62429.5607 | 63286.7853 | 64144.0099 | 10547.4392 | 10875.0511 | 11242.8246 | 11616.6992 | 11899.3387 | 12197.1957 | 12624.0442 | 13134.8765 | 13473.7438 | 13684.8399 | 13895.936 | 14107.032 | 14318.1281 | 14529.2242 | 14740.3203 | 14951.4164 | 15162.5124 | 15373.6085 | 15584.7046 | 15795.8007 | 0.004716 | 0.0048005 | 0.004885 | 0.0049694 | 0.0050539 | 0.0051384 | 0.0052228 | 0.0053073 | 0.0053918 | 0.0054763 | 0.0055607 | 0.0056452 | 0.0057297 | 0.0058142 | 0.0058986 | 0.0059831 | 0.0060676 | 0.0061521 | 0.0062365 | 0.006321 | 53378.7673 | 55036.7542 | 56897.9924 | 58790.1069 | 60220.4966 | 61727.8996 | 63888.1056 | 66473.3398 | 68188.2884 | 69256.6092 | 70324.9299 | 71393.2507 | 72461.5715 | 73529.8923 | 74598.213 | 75666.5338 | 76734.8546 | 77803.1754 | 78871.4961 | 79939.8169 | 963865.6271 | 400967.5352 | -232417.074 | 731448.553 | TRUE
| CME021 | CME | 1 | FALSE | 1 | 2 | 0 | 46875.2879 | 11543.2868 | 0.0097177 | 0.009896 | 0.010074 | 0.010253 | 0.010431 | 0.010609 | 0.010788 | 0.010966 | 0.011144 | 0.011322 | 0.011501 | 0.011679 | 0.011857 | 0.012036 | 0.012214 | 0.012392 | 0.012571 | 0.012749 | 0.012927 | 0.013106 | 33195.264 | 33804.3584 | 34604.9045 | 35266.0975 | 35780.3131 | 36291.1402 | 37054.8362 | 37927.8123 | 38491.5851 | 39107.4566 | 39723.3281 | 40339.1996 | 40955.0711 | 41570.9426 | 42186.814 | 42802.6855 | 43418.557 | 44034.4285 | 44650.3 | 45266.1715 | 8174.5088 | 8324.5015 | 8521.6402 | 8684.4625 | 8811.0908 | 8936.8846 | 9124.9488 | 9339.9238 | 9478.7558 | 9630.4174 | 9782.079 | 9933.7406 | 10085.4022 | 10237.0638 | 10388.7254 | 10540.387 | 10692.0486 | 10843.7102 | 10995.3718 | 11147.0334 | 0.00039354 | 0.00040077 | 0.00040799 | 0.00041521 | 0.00042243 | 0.00042965 | 0.00043687 | 0.00044409 | 0.00045131 | 0.00045853 | 0.00046576 | 0.00047298 | 0.0004802 | 0.00048742 | 0.00049464 | 0.00050186 | 0.00050908 | 0.0005163 | 0.00052352 | 0.00053075 | 41369.7732 | 42128.8603 | 43126.5451 | 43950.5604 | 44591.4043 | 45228.0252 | 46179.7854 | 47267.7365 | 47970.3414 | 48737.8745 | 49505.4076 | 50272.9407 | 51040.4738 | 51808.0069 | 52575.5399 | 53343.073 | 54110.6061 | 54878.1392 | 55645.6723 | 56413.2054 | 695593.4619 | 37732.0154 | -21871.0091 | 673722.4528 | TRUE
| CMN002 | CMN | 4 | FALSE | 4 | 5 | 3 | 38419.8192 | 9746.8225 | 0.0097362 | 0.0099207 | 0.010105 | 0.01029 | 0.010474 | 0.010659 | 0.010843 | 0.011028 | 0.011212 | 0.011397 | 0.011581 | 0.011766 | 0.01195 | 0.012134 | 0.012319 | 0.012503 | 0.012688 | 0.012872 | 0.013057 | 0.013241 | 13762.3445 | 14061.7475 | 14401.9367 | 14785.0674 | 15090.9358 | 15439.7456 | 15875.8751 | 16317.7516 | 16678.0555 | 16952.4765 | 17226.8975 | 17501.3185 | 17775.7395 | 18050.1605 | 18324.5815 | 18599.0024 | 18873.4234 | 19147.8444 | 19422.2654 | 19696.6864 | 3491.4045 | 3567.3608 | 3653.6643 | 3750.8617 | 3828.4582 | 3916.9487 | 4027.5915 | 4139.6923 | 4231.0987 | 4300.7173 | 4370.3358 | 4439.9544 | 4509.573 | 4579.1915 | 4648.8101 | 4718.4287 | 4788.0472 | 4857.6658 | 4927.2844 | 4996.9029 | 0.0015772 | 0.0016071 | 0.001637 | 0.0016668 | 0.0016967 | 0.0017266 | 0.0017565 | 0.0017864 | 0.0018163 | 0.0018461 | 0.001876 | 0.0019059 | 0.0019358 | 0.0019657 | 0.0019956 | 0.0020255 | 0.0020553 | 0.0020852 | 0.0021151 | 0.002145 | 17253.7506 | 17629.1099 | 18055.6027 | 18535.9308 | 18919.3957 | 19356.6961 | 19903.4684 | 20457.4457 | 20909.156 | 21253.1956 | 21597.2352 | 21941.2748 | 22285.3144 | 22629.354 | 22973.3935 | 23317.4331 | 23661.4727 | 24005.5123 | 24349.5519 | 24693.5915 | 299829.0426 | 177233.5173 | -102731.7473 | 197097.2953 | TRUE
| CMN004 | CMN | 3 | FALSE | 3 | 3 | 3 | 38419.8192 | 9746.8225 | 0.0097544 | 0.009945 | 0.010136 | 0.010326 | 0.010517 | 0.010707 | 0.010898 | 0.011088 | 0.011279 | 0.01147 | 0.01166 | 0.011851 | 0.012041 | 0.012232 | 0.012422 | 0.012613 | 0.012803 | 0.012994 | 0.013185 | 0.013375 | 13864.0981 | 14289.8529 | 14800.48 | 15279.8019 | 15643.6881 | 16052.2366 | 16550.1099 | 17228.1167 | 17568.1182 | 17864.9414 | 18161.7647 | 18458.5879 | 18755.4112 | 19052.2344 | 19349.0577 | 19645.8809 | 19942.7042 | 20239.5274 | 20536.3507 | 20833.1739 | 3517.2186 | 3625.2295 | 3754.7718 | 3876.3721 | 3968.6874 | 4072.3331 | 4198.6399 | 4370.6451 | 4456.901 | 4532.2028 | 4607.5047 | 4682.8065 | 4758.1084 | 4833.4103 | 4908.7121 | 4984.014 | 5059.3158 | 5134.6177 | 5209.9195 | 5285.2214 | 0.0011851 | 0.0012083 | 0.0012314 | 0.0012546 | 0.0012777 | 0.0013009 | 0.001324 | 0.0013472 | 0.0013703 | 0.0013935 | 0.0014166 | 0.0014398 | 0.0014629 | 0.0014861 | 0.0015092 | 0.0015324 | 0.0015555 | 0.0015787 | 0.0016018 | 0.001625 | 17381.318 | 17915.0836 | 18555.253 | 19156.1753 | 19612.3767 | 20124.571 | 20748.7511 | 21598.7632 | 22025.0206 | 22397.1457 | 22769.2708 | 23141.3959 | 23513.521 | 23885.6462 | 24257.7713 | 24629.8964 | 25002.0215 | 25374.1467 | 25746.2718 | 26118.3969 | 313419.4724 | 139501.5019 | -80860.7382 | 232558.7342 | TRUE
| CMN005 | CMN | 1 | FALSE | 1 | 1 | 1 | 38419.8192 | 9746.8225 | 0.0097456 | 0.0099332 | 0.010121 | 0.010308 | 0.010496 | 0.010684 | 0.010871 | 0.011059 | 0.011246 | 0.011434 | 0.011622 | 0.011809 | 0.011997 | 0.012185 | 0.012372 | 0.01256 | 0.012747 | 0.012935 | 0.013123 | 0.01331 | 38784.2148 | 39685.5644 | 40592.7585 | 41586.0791 | 42383.8085 | 43307.8054 | 44237.6468 | 45259.4591 | 46246.2443 | 47017.7134 | 47789.1824 | 48560.6514 | 49332.1205 | 50103.5895 | 50875.0585 | 51646.5276 | 52417.9966 | 53189.4657 | 53960.9347 | 54732.4037 | 9839.267 | 10067.9327 | 10298.0811 | 10550.0791 | 10752.4572 | 10986.8683 | 11222.7622 | 11481.9883 | 11732.3284 | 11928.0444 | 12123.7603 | 12319.4763 | 12515.1923 | 12710.9082 | 12906.6242 | 13102.3401 | 13298.0561 | 13493.7721 | 13689.488 | 13885.204 | 0.00039468 | 0.00040227 | 0.00040987 | 0.00041747 | 0.00042507 | 0.00043266 | 0.00044026 | 0.00044786 | 0.00045546 | 0.00046306 | 0.00047065 | 0.00047825 | 0.00048585 | 0.00049345 | 0.00050104 | 0.00050864 | 0.00051624 | 0.00052384 | 0.00053144 | 0.00053903 | 48623.4822 | 49753.4975 | 50890.84 | 52136.1586 | 53136.2661 | 54294.6742 | 55460.4094 | 56741.4479 | 57978.5732 | 58945.7582 | 59912.9432 | 60880.1282 | 61847.3132 | 62814.4982 | 63781.6832 | 64748.8682 | 65716.0532 | 66683.2382 | 67650.4232 | 68617.6082 | 836217.3381 | 46500.5006 | -26953.5794 | 809263.7587 | TRUE
| CRO021 | CRO | 3 | FALSE | 3 | 2 | 2 | 53295.2727 | 11724.3791 | 0.0096332 | 0.0097834 | 0.0099336 | 0.010084 | 0.010234 | 0.010384 | 0.010534 | 0.010684 | 0.010835 | 0.010985 | 0.011135 | 0.011285 | 0.011435 | 0.011585 | 0.011736 | 0.011886 | 0.012036 | 0.012186 | 0.012336 | 0.012486 | 30024.6395 | 30334.1231 | 30692.3979 | 31047.4281 | 31288.6532 | 31523.3893 | 31979.2465 | 32492.8175 | 32656.8617 | 33109.4744 | 33562.0871 | 34014.6998 | 34467.3125 | 34919.9253 | 35372.538 | 35825.1507 | 36277.7634 | 36730.3761 | 37182.9889 | 37635.6016 | 6605.0934 | 6673.1764 | 6751.993 | 6830.0958 | 6883.1627 | 6934.802 | 7035.0856 | 7148.0657 | 7184.1536 | 7283.7235 | 7383.2933 | 7482.8632 | 7582.4331 | 7682.0029 | 7781.5728 | 7881.1426 | 7980.7125 | 8080.2824 | 8179.8522 | 8279.4221 | 0.0011704 | 0.0011886 | 0.0012069 | 0.0012251 | 0.0012434 | 0.0012616 | 0.0012798 | 0.0012981 | 0.0013163 | 0.0013346 | 0.0013528 | 0.0013711 | 0.0013893 | 0.0014075 | 0.0014258 | 0.001444 | 0.0014623 | 0.0014805 | 0.0014988 | 0.001517 | 36629.7341 | 37007.3007 | 37444.3921 | 37877.5251 | 38171.8171 | 38458.1925 | 39014.3334 | 39640.8844 | 39841.0166 | 40393.1992 | 40945.3818 | 41497.5644 | 42049.747 | 42601.9296 | 43154.1122 | 43706.2948 | 44258.4774 | 44810.66 | 45362.8426 | 45915.0252 | 583871.3859 | 93001.0013 | -53907.1588 | 529964.2271 | TRUE
| CTN002 | CTN | 2 | FALSE | 2 | 4 | 0 | 42808.6941 | 11497.5591 | 0.0097498 | 0.0099388 | 0.010128 | 0.010317 | 0.010506 | 0.010695 | 0.010884 | 0.011073 | 0.011262 | 0.011451 | 0.01164 | 0.011829 | 0.012018 | 0.012207 | 0.012396 | 0.012585 | 0.012774 | 0.012963 | 0.013152 | 0.013341 | 11844.8126 | 12031.3346 | 12348.0459 | 12623.2745 | 12808.9763 | 13039.4415 | 13364.3544 | 13740.592 | 13926.2938 | 14160.0396 | 14393.7855 | 14627.5313 | 14861.2771 | 15095.023 | 15328.7688 | 15562.5146 | 15796.2604 | 16030.0063 | 16263.7521 | 16497.4979 | 3181.2798 | 3231.3758 | 3316.4382 | 3390.3591 | 3440.2349 | 3502.1332 | 3589.3983 | 3690.4482 | 3740.324 | 3803.1034 | 3865.8829 | 3928.6624 | 3991.4418 | 4054.2213 | 4117.0007 | 4179.7802 | 4242.5596 | 4305.3391 | 4368.1185 | 4430.898 | 0.00078969 | 0.00080501 | 0.00082032 | 0.00083563 | 0.00085094 | 0.00086625 | 0.00088156 | 0.00089687 | 0.00091218 | 0.00092749 | 0.0009428 | 0.00095811 | 0.00097342 | 0.00098873 | 0.001004 | 0.0010194 | 0.0010347 | 0.00105 | 0.0010653 | 0.0010806 | 15026.0932 | 15262.7113 | 15664.4849 | 16013.6344 | 16249.212 | 16541.5755 | 16953.7536 | 17431.0411 | 17666.6187 | 17963.144 | 18259.6693 | 18556.1946 | 18852.7199 | 19149.2452 | 19445.7705 | 19742.2958 | 20038.8211 | 20335.3464 | 20631.8717 | 20928.397 | 255633.8192 | 75464.0307 | -43742.0182 | 211891.8011 | TRUE
| CTN003 | CTN | 8 | FALSE | 8 | 6 | 4 | 42808.6941 | 11497.5591 | 0.0097489 | 0.0099376 | 0.010126 | 0.010315 | 0.010504 | 0.010693 | 0.010881 | 0.01107 | 0.011259 | 0.011447 | 0.011636 | 0.011825 | 0.012014 | 0.012202 | 0.012391 | 0.01258 | 0.012769 | 0.012957 | 0.013146 | 0.013335 | 9094.2838 | 9313.4561 | 9578.2029 | 9801.4695 | 9935.225 | 10113.7361 | 10386.6715 | 10710.9133 | 10844.6688 | 11026.4553 | 11208.2418 | 11390.0283 | 11571.8148 | 11753.6013 | 11935.3878 | 12117.1743 | 12298.9608 | 12480.7473 | 12662.5338 | 12844.3203 | 2442.5427 | 2501.408 | 2572.5137 | 2632.4787 | 2668.4027 | 2716.3472 | 2789.6522 | 2876.7371 | 2912.6611 | 2961.4854 | 3010.3096 | 3059.1338 | 3107.958 | 3156.7822 | 3205.6065 | 3254.4307 | 3303.2549 | 3352.0791 | 3400.9033 | 3449.7276 | 0.0031585 | 0.0032196 | 0.0032808 | 0.0033419 | 0.0034031 | 0.0034642 | 0.0035254 | 0.0035865 | 0.0036476 | 0.0037088 | 0.0037699 | 0.0038311 | 0.0038922 | 0.0039534 | 0.0040145 | 0.0040757 | 0.0041368 | 0.0041979 | 0.0042591 | 0.0043202 | 11536.8297 | 11814.8674 | 12150.7199 | 12433.9516 | 12603.6312 | 12830.0868 | 13176.3272 | 13587.6539 | 13757.3336 | 13987.9444 | 14218.5551 | 14449.1659 | 14679.7767 | 14910.3875 | 15140.9983 | 15371.6091 | 15602.2199 | 15832.8307 | 16063.4414 | 16294.0522 | 198656.3024 | 223734.0179 | -129685.3267 | 68970.9757 | TRUE
| CTN004 | CTN | 2 | FALSE | 2 | 2 | 1 | 42808.6941 | 11497.5591 | 0.0097932 | 0.0099967 | 0.0102 | 0.010404 | 0.010607 | 0.010811 | 0.011014 | 0.011218 | 0.011421 | 0.011625 | 0.011828 | 0.012032 | 0.012235 | 0.012439 | 0.012642 | 0.012846 | 0.013049 | 0.013253 | 0.013456 | 0.01366 | 43128.6951 | 43721.288 | 44478.5484 | 45862.4743 | 46207.2918 | 46718.5428 | 47550.1903 | 48331.3997 | 48910.8569 | 49782.3468 | 50653.8366 | 51525.3265 | 52396.8164 | 53268.3062 | 54139.7961 | 55011.286 | 55882.7758 | 56754.2657 | 57625.7555 | 58497.2454 | 11583.5049 | 11742.6635 | 11946.0485 | 12317.7433 | 12410.3544 | 12547.6662 | 12771.0301 | 12980.8473 | 13136.478 | 13370.5427 | 13604.6075 | 13838.6722 | 14072.7369 | 14306.8017 | 14540.8664 | 14774.9312 | 15008.9959 | 15243.0607 | 15477.1254 | 15711.1902 | 0.00079321 | 0.00080969 | 0.00082618 | 0.00084266 | 0.00085914 | 0.00087563 | 0.00089211 | 0.00090859 | 0.00092508 | 0.00094156 | 0.00095804 | 0.00097452 | 0.00099101 | 0.0010075 | 0.001024 | 0.0010405 | 0.0010569 | 0.0010734 | 0.0010899 | 0.0011064 | 54712.2008 | 55463.9524 | 56424.5978 | 58180.2185 | 58617.6471 | 59266.2099 | 60321.2213 | 61312.2479 | 62047.3358 | 63152.8904 | 64258.445 | 65363.9997 | 66469.5543 | 67575.1089 | 68680.6636 | 69786.2182 | 70891.7728 | 71997.3274 | 73102.8821 | 74208.4367 | 909925.4128 | 65366.5083 | -37889.084 | 872036.3288 | TRUE
| CTN006 | CTN | 16 | FALSE | 16 | 19 | 9 | 42808.6941 | 11497.5591 | 0.0097721 | 0.0099686 | 0.010165 | 0.010361 | 0.010558 | 0.010754 | 0.010951 | 0.011147 | 0.011344 | 0.01154 | 0.011737 | 0.011933 | 0.01213 | 0.012326 | 0.012522 | 0.012719 | 0.012915 | 0.013112 | 0.013308 | 0.013505 | 27050.9286 | 27551.4983 | 28182.6762 | 28727.3501 | 29088.7877 | 29490.0676 | 30076.2888 | 30760.9472 | 31056.9708 | 31594.8257 | 32132.6806 | 32670.5355 | 33208.3904 | 33746.2453 | 34284.1002 | 34821.9551 | 35359.81 | 35897.6649 | 36435.5198 | 36973.3747 | 7265.3384 | 7399.7814 | 7569.3032 | 7715.5917 | 7812.6666 | 7920.4424 | 8077.8896 | 8261.7752 | 8341.2812 | 8485.7383 | 8630.1954 | 8774.6524 | 8919.1095 | 9063.5666 | 9208.0236 | 9352.4807 | 9496.9378 | 9641.3948 | 9785.8519 | 9930.309 | 0.006332 | 0.0064593 | 0.0065866 | 0.0067139 | 0.0068412 | 0.0069685 | 0.0070958 | 0.0072231 | 0.0073504 | 0.0074777 | 0.007605 | 0.0077322 | 0.0078595 | 0.0079868 | 0.0081141 | 0.0082414 | 0.0083687 | 0.008496 | 0.0086233 | 0.0087506 | 34316.2734 | 34951.2861 | 35751.9859 | 36442.9486 | 36901.4611 | 37410.5169 | 38154.1855 | 39022.7297 | 39398.2594 | 40080.5715 | 40762.8835 | 41445.1956 | 42127.5077 | 42809.8198 | 43492.1319 | 44174.444 | 44856.7561 | 45539.0682 | 46221.3803 | 46903.6924 | 575340.0593 | 607164.5826 | -351937.2601 | 223402.7991 | TRUE
| ECA007 | ECA | 7 | FALSE | 7 | 5 | 8 | 47522.4048 | 11920.0275 | 0.0097678 | 0.0099628 | 0.010158 | 0.010353 | 0.010548 | 0.010743 | 0.010938 | 0.011133 | 0.011328 | 0.011523 | 0.011718 | 0.011913 | 0.012108 | 0.012303 | 0.012498 | 0.012693 | 0.012888 | 0.013083 | 0.013278 | 0.013473 | 30486.6768 | 30903.3815 | 31410.4239 | 31614.5181 | 31295.5394 | 30994.4905 | 31241.0191 | 32495.0998 | 32791.4936 | 33355.9988 | 33920.5041 | 34485.0093 | 35049.5145 | 35614.0198 | 36178.525 | 36743.0302 | 37307.5355 | 37872.0407 | 38436.5459 | 39001.0512 | 7646.9621 | 7751.484 | 7878.6652 | 7929.8581 | 7849.8488 | 7774.3368 | 7836.1735 | 8150.7341 | 8225.0784 | 8366.6731 | 8508.2677 | 8649.8624 | 8791.457 | 8933.0516 | 9074.6463 | 9216.2409 | 9357.8356 | 9499.4302 | 9641.0249 | 9782.6195 | 0.002769 | 0.0028243 | 0.0028796 | 0.0029349 | 0.0029901 | 0.0030454 | 0.0031007 | 0.003156 | 0.0032113 | 0.0032666 | 0.0033218 | 0.0033771 | 0.0034324 | 0.0034877 | 0.003543 | 0.0035982 | 0.0036535 | 0.0037088 | 0.0037641 | 0.0038194 | 38133.6416 | 38654.8683 | 39289.092 | 39544.3791 | 39145.3912 | 38768.8303 | 39077.1957 | 40645.837 | 41016.5753 | 41722.6752 | 42428.7751 | 43134.875 | 43840.975 | 44547.0749 | 45253.1748 | 45959.2748 | 46665.3747 | 47371.4746 | 48077.5746 | 48783.6745 | 606629.3323 | 315405.9821 | -182822.1216 | 423807.2107 | TRUE
| ECA010 | ECA | 1 | FALSE | 1 | 0 | 2 | 47522.4048 | 11920.0275 | 0.0097644 | 0.0099583 | 0.010152 | 0.010346 | 0.01054 | 0.010734 | 0.010928 | 0.011122 | 0.011315 | 0.011509 | 0.011703 | 0.011897 | 0.012091 | 0.012285 | 0.012479 | 0.012673 | 0.012867 | 0.01306 | 0.013254 | 0.013448 | 37765.9969 | 38707.7567 | 39999.2797 | 41062.1842 | 41983.9952 | 43014.8105 | 44423.4051 | 46068.6856 | 47035.3225 | 47841.2548 | 48647.187 | 49453.1192 | 50259.0515 | 51064.9837 | 51870.916 | 52676.8482 | 53482.7804 | 54288.7127 | 55094.6449 | 55900.5771 | 9472.8313 | 9709.0526 | 10033.0048 | 10299.6127 | 10530.8303 | 10789.3893 | 11142.7066 | 11555.3917 | 11797.8529 | 12000.0045 | 12202.1562 | 12404.3079 | 12606.4596 | 12808.6113 | 13010.763 | 13212.9147 | 13415.0664 | 13617.2181 | 13819.3698 | 14021.5215 | 0.00039544 | 0.00040329 | 0.00041114 | 0.00041899 | 0.00042685 | 0.0004347 | 0.00044255 | 0.0004504 | 0.00045825 | 0.00046611 | 0.00047396 | 0.00048181 | 0.00048966 | 0.00049751 | 0.00050537 | 0.00051322 | 0.00052107 | 0.00052892 | 0.00053677 | 0.00054463 | 47238.8285 | 48416.8097 | 50032.2849 | 51361.7973 | 52514.8259 | 53804.2002 | 55566.1121 | 57624.0777 | 58833.1758 | 59841.2598 | 60849.3437 | 61857.4277 | 62865.5116 | 63873.5955 | 64881.6795 | 65889.7634 | 66897.8473 | 67905.9313 | 68914.0152 | 69922.0991 | 839875.5346 | 55268.9859 | -32036.1497 | 807839.3849 | TRUE
| EHK022 | EHK | 1 | FALSE | 1 | 2 | 0 | 45714.8889 | 11125.7391 | 0.0098149 | 0.010026 | 0.010236 | 0.010447 | 0.010658 | 0.010869 | 0.011079 | 0.01129 | 0.011501 | 0.011711 | 0.011922 | 0.012133 | 0.012344 | 0.012554 | 0.012765 | 0.012976 | 0.013187 | 0.013397 | 0.013608 | 0.013819 | 26649.1636 | 27267.7766 | 27935.7716 | 28607.6721 | 29184.7142 | 29862.473 | 30749.476 | 31648.1957 | 32345.4821 | 32938.1464 | 33530.8107 | 34123.475 | 34716.1393 | 35308.8036 | 35901.4679 | 36494.1322 | 37086.7965 | 37679.4608 | 38272.125 | 38864.7893 | 6485.6691 | 6636.2224 | 6798.7939 | 6962.3159 | 7102.752 | 7267.6997 | 7483.5717 | 7702.2952 | 7871.9954 | 8016.2335 | 8160.4716 | 8304.7097 | 8448.9478 | 8593.1859 | 8737.424 | 8881.662 | 9025.9001 | 9170.1382 | 9314.3763 | 9458.6144 | 0.00039748 | 0.00040602 | 0.00041455 | 0.00042309 | 0.00043162 | 0.00044015 | 0.00044869 | 0.00045722 | 0.00046576 | 0.00047429 | 0.00048282 | 0.00049136 | 0.00049989 | 0.00050843 | 0.00051696 | 0.00052549 | 0.00053403 | 0.00054256 | 0.0005511 | 0.00055963 | 33134.8331 | 33903.9994 | 34734.5659 | 35569.9883 | 36287.4666 | 37130.1731 | 38233.0482 | 39350.4913 | 40217.478 | 40954.3804 | 41691.2828 | 42428.1852 | 43165.0876 | 43901.9899 | 44638.8923 | 45375.7947 | 46112.6971 | 46849.5995 | 47586.5019 | 48323.4043 | 579226.0391 | 37732.0154 | -21871.0091 | 557355.03 | TRUE
| EHK024 | EHK | 6 | FALSE | 6 | 5 | 4 | 45714.8889 | 11125.7391 | 0.0097859 | 0.0099869 | 0.010188 | 0.010389 | 0.01059 | 0.010791 | 0.010992 | 0.011193 | 0.011394 | 0.011595 | 0.011796 | 0.011997 | 0.012199 | 0.0124 | 0.012601 | 0.012802 | 0.013003 | 0.013204 | 0.013405 | 0.013606 | 42303.9822 | 43774.6726 | 45552.8132 | 47173.8065 | 48332.0654 | 49699.6383 | 51542.3599 | 53626.0681 | 54958.8503 | 55928.5933 | 56898.3363 | 57868.0793 | 58837.8223 | 59807.5653 | 60777.3083 | 61747.0513 | 62716.7944 | 63686.5374 | 64656.2804 | 65626.0234 | 10295.6188 | 10653.5441 | 11086.2944 | 11480.7993 | 11762.6875 | 12095.5169 | 12543.9843 | 13051.1013 | 13375.4636 | 13611.4722 | 13847.4808 | 14083.4894 | 14319.498 | 14555.5066 | 14791.5153 | 15027.5239 | 15263.5325 | 15499.5411 | 15735.5497 | 15971.5583 | 0.0023778 | 0.0024267 | 0.0024756 | 0.0025244 | 0.0025733 | 0.0026221 | 0.002671 | 0.0027198 | 0.0027687 | 0.0028175 | 0.0028664 | 0.0029152 | 0.0029641 | 0.0030129 | 0.0030618 | 0.0031106 | 0.0031595 | 0.0032083 | 0.0032572 | 0.0033061 | 52599.6034 | 54428.2191 | 56639.11 | 58654.6083 | 60094.7554 | 61795.1579 | 64086.3469 | 66677.1721 | 68334.3166 | 69540.0683 | 70745.82 | 71951.5716 | 73157.3233 | 74363.075 | 75568.8267 | 76774.5783 | 77980.33 | 79186.0817 | 80391.8334 | 81597.585 | 968742.0375 | 204868.0102 | -118749.8222 | 849992.2154 | TRUE
| EHK031 | EHK | 3 | FALSE | 3 | 4 | 2 | 45714.8889 | 11125.7391 | 0.0098134 | 0.010024 | 0.010234 | 0.010444 | 0.010654 | 0.010864 | 0.011075 | 0.011285 | 0.011495 | 0.011705 | 0.011916 | 0.012126 | 0.012336 | 0.012546 | 0.012756 | 0.012967 | 0.013177 | 0.013387 | 0.013597 | 0.013807 | 48333.8054 | 50576.6927 | 53154.7316 | 55504.759 | 57806.704 | 60155.4011 | 63063.9826 | 66457.0942 | 69026.5807 | 70288.8859 | 71551.1911 | 72813.4963 | 74075.8015 | 75338.1067 | 76600.4119 | 77862.7171 | 79125.0223 | 80387.3275 | 81649.6327 | 82911.9379 | 11763.1109 | 12308.9677 | 12936.391 | 13508.3226 | 14068.5524 | 14640.1602 | 15348.0285 | 16173.818 | 16799.1599 | 17106.3701 | 17413.5802 | 17720.7904 | 18028.0006 | 18335.2107 | 18642.4209 | 18949.631 | 19256.8412 | 19564.0514 | 19871.2615 | 20178.4717 | 0.0011923 | 0.0012178 | 0.0012433 | 0.0012689 | 0.0012944 | 0.00132 | 0.0013455 | 0.001371 | 0.0013966 | 0.0014221 | 0.0014477 | 0.0014732 | 0.0014987 | 0.0015243 | 0.0015498 | 0.0015754 | 0.0016009 | 0.0016264 | 0.001652 | 0.0016775 | 60096.9175 | 62885.6616 | 66091.1238 | 69013.0829 | 71875.2577 | 74795.5626 | 78412.0125 | 82630.9136 | 85825.742 | 87395.2574 | 88964.7728 | 90534.2882 | 92103.8036 | 93673.319 | 95242.8343 | 96812.3497 | 98381.8651 | 99951.3805 | 101520.8959 | 103090.4113 | 1191044.7079 | 130733.0166 | -75778.1679 | 1115266.54 | TRUE
| FNS012 | FNS | 1 | FALSE | 1 | 2 | 0 | 47157.5465 | 11382.8682 | 0.0096163 | 0.0097609 | 0.0099054 | 0.01005 | 0.010194 | 0.010339 | 0.010483 | 0.010628 | 0.010773 | 0.010917 | 0.011062 | 0.011206 | 0.011351 | 0.011495 | 0.01164 | 0.011784 | 0.011929 | 0.012073 | 0.012218 | 0.012362 | 29783.5803 | 30744.3988 | 31862.4465 | 32903.7671 | 33815.4902 | 34789.0639 | 36026.9888 | 37641.2227 | 38770.9648 | 39291.1325 | 39811.3001 | 40331.4678 | 40851.6355 | 41371.8032 | 41891.9708 | 42412.1385 | 42932.3062 | 43452.4738 | 43972.6415 | 44492.8092 | 7189.1477 | 7421.0697 | 7690.9436 | 7942.2971 | 8162.3684 | 8397.3692 | 8696.179 | 9085.822 | 9358.5187 | 9484.0766 | 9609.6344 | 9735.1923 | 9860.7501 | 9986.308 | 10111.8658 | 10237.4236 | 10362.9815 | 10488.5393 | 10614.0972 | 10739.655 | 0.00038944 | 0.00039529 | 0.00040115 | 0.000407 | 0.00041285 | 0.00041871 | 0.00042456 | 0.00043041 | 0.00043627 | 0.00044212 | 0.00044797 | 0.00045383 | 0.00045968 | 0.00046553 | 0.00047138 | 0.00047724 | 0.00048309 | 0.00048894 | 0.0004948 | 0.00050065 | 36972.7284 | 38165.4689 | 39553.3905 | 40846.0646 | 41977.859 | 43186.4335 | 44723.1682 | 46727.0451 | 48129.4839 | 48775.2095 | 49420.935 | 50066.6605 | 50712.386 | 51358.1116 | 52003.8371 | 52649.5626 | 53295.2881 | 53941.0137 | 54586.7392 | 55232.4647 | 672523.712 | 37732.0154 | -21871.0091 | 650652.703 | TRUE
| FNS013 | FNS | 3 | FALSE | 3 | 5 | 0 | 47157.5465 | 11382.8682 | 0.0096165 | 0.0097611 | 0.0099057 | 0.01005 | 0.010195 | 0.010339 | 0.010484 | 0.010629 | 0.010773 | 0.010918 | 0.011062 | 0.011207 | 0.011352 | 0.011496 | 0.011641 | 0.011785 | 0.01193 | 0.012075 | 0.012219 | 0.012364 | 52535.9919 | 54398.9744 | 56435.7841 | 58604.6043 | 60617.2157 | 62712.4189 | 65192.9465 | 68022.5106 | 70698.6303 | 71647.5167 | 72596.4031 | 73545.2896 | 74494.176 | 75443.0624 | 76391.9488 | 77340.8353 | 78289.7217 | 79238.6081 | 80187.4945 | 81136.381 | 12681.115 | 13130.8009 | 13622.4452 | 14145.954 | 14631.7573 | 15137.4966 | 15736.2452 | 16419.2442 | 17065.2048 | 17294.2466 | 17523.2884 | 17752.3302 | 17981.372 | 18210.4138 | 18439.4556 | 18668.4974 | 18897.5392 | 19126.581 | 19355.6228 | 19584.6645 | 0.0011683 | 0.0011859 | 0.0012035 | 0.001221 | 0.0012386 | 0.0012562 | 0.0012738 | 0.0012913 | 0.0013089 | 0.0013265 | 0.001344 | 0.0013616 | 0.0013792 | 0.0013967 | 0.0014143 | 0.0014319 | 0.0014494 | 0.001467 | 0.0014846 | 0.0015021 | 65217.1081 | 67529.7765 | 70058.2304 | 72750.5596 | 75248.9743 | 77849.9167 | 80929.193 | 84441.756 | 87763.8364 | 88941.7646 | 90119.6929 | 91297.6211 | 92475.5493 | 93653.4776 | 94831.4058 | 96009.3341 | 97187.2623 | 98365.1905 | 99543.1188 | 100721.047 | 1215856.535 | 94330.0384 | -54677.5227 | 1161179.0123 | TRUE
| FNS022 | FNS | 2 | FALSE | 2 | 3 | 0 | 47157.5465 | 11382.8682 | 0.0096203 | 0.0097661 | 0.009912 | 0.010058 | 0.010204 | 0.01035 | 0.010495 | 0.010641 | 0.010787 | 0.010933 | 0.011079 | 0.011225 | 0.01137 | 0.011516 | 0.011662 | 0.011808 | 0.011954 | 0.0121 | 0.012246 | 0.012391 | 28324.4518 | 29407.3663 | 30651.9262 | 31920.1876 | 32968.3023 | 34082.6144 | 35415.7067 | 36874.2227 | 38049.8801 | 38564.3445 | 39078.8089 | 39593.2734 | 40107.7378 | 40622.2022 | 41136.6667 | 41651.1311 | 42165.5955 | 42680.0599 | 43194.5244 | 43708.9888 | 6836.9439 | 7098.3374 | 7398.7487 | 7704.8811 | 7957.8746 | 8226.8467 | 8548.628 | 8900.6839 | 9184.4636 | 9308.6448 | 9432.826 | 9557.0072 | 9681.1884 | 9805.3696 | 9929.5508 | 10053.732 | 10177.9132 | 10302.0944 | 10426.2756 | 10550.4568 | 0.0007792 | 0.00079102 | 0.00080283 | 0.00081464 | 0.00082646 | 0.00083827 | 0.00085008 | 0.0008619 | 0.00087371 | 0.00088552 | 0.00089734 | 0.00090915 | 0.00092096 | 0.00093277 | 0.00094459 | 0.0009564 | 0.00096821 | 0.00098003 | 0.00099184 | 0.0010037 | 35161.3965 | 36505.7045 | 38050.6757 | 39625.0696 | 40926.1777 | 42309.4619 | 43964.3356 | 45774.9075 | 47234.3446 | 47872.9902 | 48511.6358 | 49150.2815 | 49788.9271 | 50427.5728 | 51066.2184 | 51704.864 | 52343.5097 | 52982.1553 | 53620.801 | 54259.4466 | 656784.5724 | 56598.023 | -32806.5136 | 623978.0588 | TRUE
| GCY011 | GCY | 3 | FALSE | 3 | 4 | 1 | 45326.5658 | 10725.2654 | 0.0096247 | 0.0097721 | 0.0099194 | 0.010067 | 0.010214 | 0.010361 | 0.010509 | 0.010656 | 0.010803 | 0.010951 | 0.011098 | 0.011245 | 0.011393 | 0.01154 | 0.011687 | 0.011835 | 0.011982 | 0.012129 | 0.012277 | 0.012424 | 57614.0119 | 59214.2655 | 61064.0298 | 62803.4816 | 64004.2136 | 65879.4791 | 67685.264 | 69956.0068 | 71568.4612 | 72544.5069 | 73520.5525 | 74496.5982 | 75472.6438 | 76448.6895 | 77424.7351 | 78400.7808 | 79376.8264 | 80352.8721 | 81328.9177 | 82304.9634 | 13632.7462 | 14011.4015 | 14449.0965 | 14860.6892 | 15144.8089 | 15588.538 | 16015.8266 | 16553.1344 | 16934.6767 | 17165.6306 | 17396.5846 | 17627.5385 | 17858.4924 | 18089.4464 | 18320.4003 | 18551.3542 | 18782.3082 | 19013.2621 | 19244.216 | 19475.17 | 0.0011693 | 0.0011872 | 0.0012051 | 0.001223 | 0.0012409 | 0.0012588 | 0.0012767 | 0.0012946 | 0.0013125 | 0.0013305 | 0.0013484 | 0.0013663 | 0.0013842 | 0.0014021 | 0.00142 | 0.0014379 | 0.0014558 | 0.0014737 | 0.0014916 | 0.0015095 | 71246.7592 | 73225.6682 | 75513.1276 | 77664.1719 | 79149.0237 | 81468.0184 | 83701.0918 | 86509.1426 | 88503.1393 | 89710.1388 | 90917.1384 | 92124.138 | 93331.1376 | 94538.1372 | 95745.1368 | 96952.1364 | 98159.136 | 99366.1356 | 100573.1352 | 101780.1348 | 1253327.6516 | 103098.5237 | -59760.093 | 1193567.5586 | TRUE
| GCY014 | GCY | 7 | FALSE | 7 | 10 | 1 | 45326.5658 | 10725.2654 | 0.0096137 | 0.0097573 | 0.009901 | 0.010045 | 0.010188 | 0.010332 | 0.010476 | 0.010619 | 0.010763 | 0.010907 | 0.01105 | 0.011194 | 0.011338 | 0.011481 | 0.011625 | 0.011768 | 0.011912 | 0.012056 | 0.012199 | 0.012343 | 57945.3493 | 59349.1057 | 60950.6431 | 62850.1717 | 64029.8508 | 65549.707 | 67279.2231 | 69177.5333 | 71300.0222 | 72251.6643 | 73203.3064 | 74154.9485 | 75106.5906 | 76058.2327 | 77009.8748 | 77961.517 | 78913.1591 | 79864.8012 | 80816.4433 | 81768.0854 | 13711.1479 | 14043.3076 | 14422.2667 | 14871.7371 | 15150.8752 | 15510.5067 | 15919.7484 | 16368.9304 | 16871.1581 | 17096.3376 | 17321.5172 | 17546.6967 | 17771.8762 | 17997.0557 | 18222.2352 | 18447.4147 | 18672.5942 | 18897.7738 | 19122.9533 | 19348.1328 | 0.0027253 | 0.0027661 | 0.0028068 | 0.0028475 | 0.0028882 | 0.002929 | 0.0029697 | 0.0030104 | 0.0030511 | 0.0030919 | 0.0031326 | 0.0031733 | 0.003214 | 0.0032547 | 0.0032955 | 0.0033362 | 0.0033769 | 0.0034176 | 0.0034584 | 0.0034991 | 71656.4999 | 73392.4161 | 75372.9126 | 77721.9116 | 79180.7289 | 81060.2166 | 83198.9745 | 85546.4667 | 88171.1834 | 89348.0051 | 90524.8267 | 91701.6484 | 92878.47 | 94055.2917 | 95232.1134 | 96408.935 | 97585.7567 | 98762.5783 | 99939.4 | 101116.2216 | 1248730.3304 | 216294.5698 | -125373.1203 | 1123357.2101 | TRUE
| GHP011 | GHP | 2 | FALSE | 2 | 3 | 1 | 38273.3274 | 10683.9189 | 0.0096151 | 0.0097592 | 0.0099034 | 0.010047 | 0.010192 | 0.010336 | 0.01048 | 0.010624 | 0.010768 | 0.010912 | 0.011056 | 0.0112 | 0.011345 | 0.011489 | 0.011633 | 0.011777 | 0.011921 | 0.012065 | 0.012209 | 0.012354 | 42072.7957 | 43422.7421 | 45178.1015 | 46771.0086 | 48074.4726 | 49676.4855 | 52076.6253 | 54482.5164 | 56432.9973 | 57188.3246 | 57943.6519 | 58698.9793 | 59454.3066 | 60209.634 | 60964.9613 | 61720.2886 | 62475.616 | 63230.9433 | 63986.2707 | 64741.598 | 11744.5326 | 12121.3673 | 12611.3721 | 13056.0288 | 13419.8881 | 13867.0866 | 14537.0806 | 15208.68 | 15753.1527 | 15964.0007 | 16174.8487 | 16385.6968 | 16596.5448 | 16807.3929 | 17018.2409 | 17229.0889 | 17439.937 | 17650.785 | 17861.6331 | 18072.4811 | 0.00077878 | 0.00079046 | 0.00080213 | 0.0008138 | 0.00082548 | 0.00083715 | 0.00084883 | 0.0008605 | 0.00087217 | 0.00088385 | 0.00089552 | 0.00090719 | 0.00091887 | 0.00093054 | 0.00094221 | 0.00095389 | 0.00096556 | 0.00097724 | 0.00098891 | 0.0010006 | 53817.329 | 55544.1102 | 57789.4744 | 59827.0383 | 61494.3615 | 63543.5729 | 66613.7068 | 69691.1973 | 72186.1508 | 73152.3262 | 74118.5016 | 75084.677 | 76050.8524 | 77017.0278 | 77983.2031 | 78949.3785 | 79915.5539 | 80881.7293 | 81847.9047 | 82814.0801 | 999739.8309 | 84232.516 | -48824.5885 | 950915.2424 | TRUE
| GHP012 | GHP | 1 | FALSE | 1 | 1 | 1 | 38273.3274 | 10683.9189 | 0.0096144 | 0.0097583 | 0.0099022 | 0.010046 | 0.01019 | 0.010334 | 0.010478 | 0.010622 | 0.010765 | 0.010909 | 0.011053 | 0.011197 | 0.011341 | 0.011485 | 0.011629 | 0.011773 | 0.011917 | 0.01206 | 0.012204 | 0.012348 | 38899.4868 | 40163.0091 | 41600.2731 | 42984.1554 | 44074.1367 | 45377.9462 | 46903.9563 | 48742.9448 | 50029.6525 | 50698.3176 | 51366.9828 | 52035.648 | 52704.3132 | 53372.9784 | 54041.6436 | 54710.3088 | 55378.974 | 56047.6392 | 56716.3044 | 57384.9696 | 10858.71 | 11211.4196 | 11612.6289 | 11998.9367 | 12303.2027 | 12667.1584 | 13093.1409 | 13606.4907 | 13965.6724 | 14152.3289 | 14338.9854 | 14525.6419 | 14712.2983 | 14898.9548 | 15085.6113 | 15272.2678 | 15458.9243 | 15645.5808 | 15832.2373 | 16018.8937 | 0.00038936 | 0.00039519 | 0.00040102 | 0.00040684 | 0.00041267 | 0.0004185 | 0.00042432 | 0.00043015 | 0.00043598 | 0.00044181 | 0.00044763 | 0.00045346 | 0.00045929 | 0.00046511 | 0.00047094 | 0.00047677 | 0.0004826 | 0.00048842 | 0.00049425 | 0.00050008 | 49758.1972 | 51374.4291 | 53212.9024 | 54983.0925 | 56377.3398 | 58045.105 | 59997.0976 | 62349.436 | 63995.3253 | 64850.647 | 65705.9687 | 66561.2903 | 67416.612 | 68271.9337 | 69127.2554 | 69982.5771 | 70837.8988 | 71693.2204 | 72548.5421 | 73403.8638 | 898035.0259 | 46500.5006 | -26953.5794 | 871081.4465 | TRUE
| GHP021 | GHP | 5 | FALSE | 5 | 8 | 1 | 38273.3274 | 10683.9189 | 0.0096214 | 0.0097676 | 0.0099138 | 0.01006 | 0.010206 | 0.010352 | 0.010499 | 0.010645 | 0.010791 | 0.010937 | 0.011083 | 0.01123 | 0.011376 | 0.011522 | 0.011668 | 0.011814 | 0.011961 | 0.012107 | 0.012253 | 0.012399 | 35195.3827 | 36753.2386 | 38534.0063 | 40194.975 | 41610.5645 | 43170.4503 | 45368.4452 | 47775.8497 | 49813.4294 | 50488.3443 | 51163.2593 | 51838.1743 | 52513.0892 | 53188.0042 | 53862.9191 | 54537.8341 | 55212.7491 | 55887.664 | 56562.579 | 57237.4939 | 9824.7172 | 10259.5894 | 10756.6869 | 11220.3428 | 11615.5017 | 12050.9405 | 12664.5062 | 13336.5281 | 13905.3142 | 14093.7153 | 14282.1164 | 14470.5175 | 14658.9186 | 14847.3197 | 15035.7208 | 15224.1218 | 15412.5229 | 15600.924 | 15789.3251 | 15977.7262 | 0.0019482 | 0.0019778 | 0.0020074 | 0.002037 | 0.0020666 | 0.0020962 | 0.0021259 | 0.0021555 | 0.0021851 | 0.0022147 | 0.0022443 | 0.0022739 | 0.0023035 | 0.0023331 | 0.0023627 | 0.0023923 | 0.0024219 | 0.0024515 | 0.0024811 | 0.0025107 | 45020.1018 | 47012.8299 | 49290.6952 | 51415.3198 | 53226.0683 | 55221.3929 | 58032.9535 | 61112.38 | 63718.7457 | 64582.0618 | 65445.3779 | 66308.694 | 67172.0101 | 68035.3262 | 68898.6423 | 69761.9583 | 70625.2744 | 71488.5905 | 72351.9066 | 73215.2227 | 873149.868 | 178562.5544 | -103502.1112 | 769647.7568 | TRUE
| GHP022 | GHP | 3 | FALSE | 3 | 5 | 1 | 38273.3274 | 10683.9189 | 0.0096124 | 0.0097556 | 0.0098988 | 0.010042 | 0.010185 | 0.010328 | 0.010472 | 0.010615 | 0.010758 | 0.010901 | 0.011045 | 0.011188 | 0.011331 | 0.011474 | 0.011617 | 0.011761 | 0.011904 | 0.012047 | 0.01219 | 0.012333 | 22372.794 | 23084.5644 | 23961.0425 | 24697.2575 | 25286.5429 | 25922.5607 | 26850.7056 | 27917.937 | 28545.0002 | 28925.0021 | 29305.004 | 29685.0059 | 30065.0078 | 30445.0097 | 30825.0116 | 31205.0135 | 31585.0154 | 31965.0173 | 32345.0192 | 32725.0211 | 6245.3184 | 6444.0077 | 6688.6747 | 6894.1876 | 7058.6853 | 7236.2284 | 7495.3181 | 7793.2335 | 7968.2769 | 8074.3536 | 8180.4303 | 8286.5071 | 8392.5838 | 8498.6605 | 8604.7372 | 8710.814 | 8816.8907 | 8922.9674 | 9029.0442 | 9135.1209 | 0.0011678 | 0.0011852 | 0.0012026 | 0.00122 | 0.0012374 | 0.0012548 | 0.0012722 | 0.0012896 | 0.001307 | 0.0013244 | 0.0013418 | 0.0013592 | 0.0013766 | 0.001394 | 0.0014114 | 0.0014288 | 0.0014462 | 0.0014636 | 0.001481 | 0.0014984 | 28618.1136 | 29528.5733 | 30649.7184 | 31591.4463 | 32345.2294 | 33158.7903 | 34346.025 | 35711.1717 | 36513.2784 | 36999.3571 | 37485.4357 | 37971.5143 | 38457.593 | 38943.6716 | 39429.7503 | 39915.8289 | 40401.9075 | 40887.9862 | 41374.0648 | 41860.1435 | 513583.5955 | 121964.5314 | -70695.5976 | 442887.9979 | TRUE
| HSM002 | HSM | 1 | FALSE | 1 | 2 | 0 | 41631.5752 | 11021.0193 | 0.0095742 | 0.0097047 | 0.0098352 | 0.0099657 | 0.010096 | 0.010227 | 0.010357 | 0.010488 | 0.010618 | 0.010749 | 0.010879 | 0.01101 | 0.01114 | 0.011271 | 0.011401 | 0.011532 | 0.011662 | 0.011792 | 0.011923 | 0.012053 | 13210.3578 | 13390.4021 | 13653.446 | 13876.6419 | 14015.737 | 14153.7309 | 14465.4324 | 14780.4375 | 14874.7291 | 15057.5264 | 15240.3236 | 15423.1209 | 15605.9182 | 15788.7154 | 15971.5127 | 16154.3099 | 16337.1072 | 16519.9045 | 16702.7017 | 16885.499 | 3497.1439 | 3544.8065 | 3614.4415 | 3673.5276 | 3710.3498 | 3746.8806 | 3829.3965 | 3912.787 | 3937.7486 | 3986.14 | 4034.5315 | 4082.9229 | 4131.3144 | 4179.7058 | 4228.0973 | 4276.4887 | 4324.8802 | 4373.2716 | 4421.6631 | 4470.0545 | 0.00038773 | 0.00039302 | 0.0003983 | 0.00040359 | 0.00040887 | 0.00041416 | 0.00041944 | 0.00042473 | 0.00043001 | 0.00043529 | 0.00044058 | 0.00044586 | 0.00045115 | 0.00045643 | 0.00046172 | 0.000467 | 0.00047229 | 0.00047757 | 0.00048286 | 0.00048814 | 16707.502 | 16935.209 | 17267.8879 | 17550.1699 | 17726.0872 | 17900.6119 | 18294.8293 | 18693.2249 | 18812.4781 | 19043.6669 | 19274.8556 | 19506.0443 | 19737.233 | 19968.4217 | 20199.6104 | 20430.7991 | 20661.9878 | 20893.1766 | 21124.3653 | 21355.554 | 272217.0518 | 37732.0154 | -21871.0091 | 250346.0428 | TRUE
| HSM004 | HSM | 7 | FALSE | 7 | 7 | 6 | 41631.5752 | 11021.0193 | 0.0095931 | 0.0097299 | 0.0098667 | 0.010004 | 0.01014 | 0.010277 | 0.010414 | 0.010551 | 0.010687 | 0.010824 | 0.010961 | 0.011098 | 0.011235 | 0.011371 | 0.011508 | 0.011645 | 0.011782 | 0.011919 | 0.012055 | 0.012192 | 21615.5231 | 21964.8112 | 22356.8867 | 22624.6405 | 22677.3032 | 22853.1329 | 23245.2084 | 23684.1117 | 23765.7086 | 24069.9004 | 24374.0923 | 24678.2842 | 24982.4761 | 25286.6679 | 25590.8598 | 25895.0517 | 26199.2436 | 26503.4354 | 26807.6273 | 27111.8192 | 5722.2216 | 5814.6877 | 5918.4808 | 5989.3626 | 6003.3039 | 6049.8508 | 6153.6439 | 6269.8337 | 6291.4346 | 6371.9625 | 6452.4905 | 6533.0184 | 6613.5463 | 6694.0742 | 6774.6022 | 6855.1301 | 6935.658 | 7016.186 | 7096.7139 | 7177.2418 | 0.0027195 | 0.0027583 | 0.0027971 | 0.0028358 | 0.0028746 | 0.0029134 | 0.0029522 | 0.002991 | 0.0030297 | 0.0030685 | 0.0031073 | 0.0031461 | 0.0031849 | 0.0032236 | 0.0032624 | 0.0033012 | 0.00334 | 0.0033788 | 0.0034175 | 0.0034563 | 27337.7474 | 27779.5017 | 28275.3703 | 28614.006 | 28680.6099 | 28902.9867 | 29398.8553 | 29953.9484 | 30057.1462 | 30441.866 | 30826.5859 | 31211.3057 | 31596.0256 | 31980.7454 | 32365.4652 | 32750.1851 | 33134.9049 | 33519.6248 | 33904.3446 | 34289.0645 | 438727.9337 | 297869.0115 | -172656.981 | 266070.9527 | TRUE
| HTN011 | HTN | 5 | FALSE | 5 | 7 | 1 | 38280.733 | 9773.4555 | 0.0095227 | 0.009636 | 0.0097493 | 0.0098626 | 0.0099759 | 0.010089 | 0.010202 | 0.010316 | 0.010429 | 0.010542 | 0.010656 | 0.010769 | 0.010882 | 0.010996 | 0.011109 | 0.011222 | 0.011336 | 0.011449 | 0.011562 | 0.011675 | 4729.2227 | 4860.2668 | 4993.0693 | 5089.3644 | 5147.8332 | 5245.4471 | 5383.525 | 5563.3857 | 5664.9562 | 5726.5023 | 5788.0484 | 5849.5945 | 5911.1406 | 5972.6867 | 6034.2328 | 6095.7789 | 6157.325 | 6218.8711 | 6280.4172 | 6341.9633 | 1207.418 | 1240.8749 | 1274.7807 | 1299.3658 | 1314.2935 | 1339.2153 | 1374.468 | 1420.3882 | 1446.3202 | 1462.0335 | 1477.7469 | 1493.4602 | 1509.1735 | 1524.8869 | 1540.6002 | 1556.3135 | 1572.0269 | 1587.7402 | 1603.4536 | 1619.1669 | 0.0019282 | 0.0019512 | 0.0019741 | 0.0019971 | 0.00202 | 0.002043 | 0.0020659 | 0.0020888 | 0.0021118 | 0.0021347 | 0.0021577 | 0.0021806 | 0.0022036 | 0.0022265 | 0.0022494 | 0.0022724 | 0.0022953 | 0.0023183 | 0.0023412 | 0.0023642 | 5936.6427 | 6101.1436 | 6267.852 | 6388.7322 | 6462.1287 | 6584.6644 | 6757.995 | 6983.776 | 7111.2784 | 7188.5379 | 7265.7974 | 7343.0568 | 7420.3163 | 7497.5758 | 7574.8352 | 7652.0947 | 7729.3541 | 7806.6136 | 7883.8731 | 7961.1325 | 100857.1398 | 159696.5467 | -92566.6067 | 8290.5331 | TRUE
| HTN013 | HTN | 6 | FALSE | 6 | 12 | 0 | 38280.733 | 9773.4555 | 0.0095343 | 0.0096514 | 0.0097686 | 0.0098858 | 0.010003 | 0.01012 | 0.010237 | 0.010354 | 0.010472 | 0.010589 | 0.010706 | 0.010823 | 0.01094 | 0.011058 | 0.011175 | 0.011292 | 0.011409 | 0.011526 | 0.011643 | 0.011761 | 18902.9549 | 19135.2685 | 19367.5821 | 19523.1838 | 19560.5353 | 19593.3405 | 19740.7589 | 19966.7078 | 19908.253 | 20131.0195 | 20353.786 | 20576.5525 | 20799.319 | 21022.0855 | 21244.8519 | 21467.6184 | 21690.3849 | 21913.1514 | 22135.9179 | 22358.6844 | 4826.1142 | 4885.4262 | 4944.7382 | 4984.4649 | 4994.0011 | 5002.3766 | 5040.014 | 5097.701 | 5082.7769 | 5139.6514 | 5196.5259 | 5253.4005 | 5310.275 | 5367.1495 | 5424.024 | 5480.8985 | 5537.7731 | 5594.6476 | 5651.5221 | 5708.3966 | 0.0023167 | 0.0023452 | 0.0023736 | 0.0024021 | 0.0024306 | 0.0024591 | 0.0024875 | 0.002516 | 0.0025445 | 0.002573 | 0.0026014 | 0.0026299 | 0.0026584 | 0.0026868 | 0.0027153 | 0.0027438 | 0.0027723 | 0.0028007 | 0.0028292 | 0.0028577 | 23729.0714 | 24020.697 | 24312.3227 | 24507.6511 | 24554.5388 | 24595.7195 | 24780.7754 | 25064.4113 | 24991.0325 | 25270.6735 | 25550.3145 | 25829.9556 | 26109.5966 | 26389.2376 | 26668.8787 | 26948.5197 | 27228.1608 | 27507.8018 | 27787.4428 | 28067.0839 | 367948.189 | 226392.0922 | -131226.0546 | 236722.1344 | TRUE
| HTN032 | KGTS | 1 | FALSE | 1 | 1 | 1 | 43210.6088 | 11999.4652 | 0.0095375 | 0.0096557 | 0.0097739 | 0.0098922 | 0.01001 | 0.010129 | 0.010247 | 0.010365 | 0.010483 | 0.010602 | 0.01072 | 0.010838 | 0.010956 | 0.011075 | 0.011193 | 0.011311 | 0.011429 | 0.011547 | 0.011666 | 0.011784 | 27902.348 | 28121.3964 | 28551.3662 | 28940.0837 | 29154.4717 | 29410.1118 | 29888.0655 | 30414.521 | 30623.7307 | 30969.1248 | 31314.5189 | 31659.913 | 32005.307 | 32350.7011 | 32696.0952 | 33041.4893 | 33386.8834 | 33732.2775 | 34077.6716 | 34423.0657 | 7748.404 | 7809.2331 | 7928.6345 | 8036.5803 | 8096.1153 | 8167.1058 | 8299.8322 | 8446.0274 | 8504.1244 | 8600.0393 | 8695.9543 | 8791.8693 | 8887.7843 | 8983.6992 | 9079.6142 | 9175.5292 | 9271.4441 | 9367.3591 | 9463.2741 | 9559.1891 | 0.00038625 | 0.00039104 | 0.00039582 | 0.00040061 | 0.0004054 | 0.00041019 | 0.00041498 | 0.00041977 | 0.00042455 | 0.00042934 | 0.00043413 | 0.00043892 | 0.00044371 | 0.0004485 | 0.00045328 | 0.00045807 | 0.00046286 | 0.00046765 | 0.00047244 | 0.00047723 | 35650.7523 | 35930.63 | 36480.0011 | 36976.6644 | 37250.5874 | 37577.2181 | 38187.8982 | 38860.5489 | 39127.8555 | 39569.1645 | 40010.4736 | 40451.7827 | 40893.0917 | 41334.4008 | 41775.7099 | 42217.0189 | 42658.328 | 43099.6371 | 43540.9461 | 43982.2552 | 567882.4816 | 46500.5006 | -26953.5794 | 540928.9021 | TRUE
| HTN034 | KGTS | 24 | FALSE | 24 | 28 | 11 | 43210.6088 | 11999.4652 | 0.0095305 | 0.0096464 | 0.0097624 | 0.0098783 | 0.0099942 | 0.01011 | 0.010226 | 0.010342 | 0.010458 | 0.010574 | 0.01069 | 0.010806 | 0.010922 | 0.011038 | 0.011153 | 0.011269 | 0.011385 | 0.011501 | 0.011617 | 0.011733 | 13648.851 | 13941.6131 | 14237.4214 | 14493.0132 | 14575.5541 | 14700.3423 | 15003.2585 | 15399.808 | 15480.8258 | 15652.4307 | 15824.0356 | 15995.6404 | 16167.2453 | 16338.8502 | 16510.4551 | 16682.06 | 16853.6649 | 17025.2698 | 17196.8747 | 17368.4795 | 3790.2478 | 3871.547 | 3953.6921 | 4024.6692 | 4047.5906 | 4082.2439 | 4166.3629 | 4276.4836 | 4298.982 | 4346.6362 | 4394.2904 | 4441.9446 | 4489.5988 | 4537.253 | 4584.9072 | 4632.5614 | 4680.2156 | 4727.8698 | 4775.524 | 4823.1782 | 0.0092632 | 0.0093759 | 0.0094885 | 0.0096012 | 0.0097139 | 0.0098266 | 0.0099392 | 0.010052 | 0.010165 | 0.010277 | 0.01039 | 0.010503 | 0.010615 | 0.010728 | 0.010841 | 0.010953 | 0.011066 | 0.011179 | 0.011291 | 0.011404 | 17439.1081 | 17813.1694 | 18191.123 | 18517.692 | 18623.1544 | 18782.5961 | 19169.6313 | 19676.3017 | 19779.818 | 19999.0772 | 20218.3364 | 20437.5956 | 20656.8548 | 20876.114 | 21095.3732 | 21314.6324 | 21533.8916 | 21753.1507 | 21972.4099 | 22191.6691 | 285200.7816 | 832227.6376 | -482392.9508 | -197192.1692 | FALSE
| KGT002 | KGTS | 1 | FALSE | 1 | 2 | 0 | 43210.6088 | 11999.4652 | 0.009697 | 0.0098684 | 0.01004 | 0.010211 | 0.010383 | 0.010554 | 0.010725 | 0.010897 | 0.011068 | 0.01124 | 0.011411 | 0.011582 | 0.011754 | 0.011925 | 0.012097 | 0.012268 | 0.01244 | 0.012611 | 0.012782 | 0.012954 | 29558.1399 | 30123.8479 | 30778.9973 | 31349.2095 | 31693.5661 | 32031.9171 | 32646.0993 | 33358.7314 | 33689.5753 | 34211.3133 | 34733.0514 | 35254.7894 | 35776.5274 | 36298.2654 | 36820.0034 | 37341.7414 | 37863.4794 | 38385.2174 | 38906.9554 | 39428.6934 | 8208.2128 | 8365.3083 | 8547.2415 | 8705.5878 | 8801.2147 | 8895.1738 | 9065.7305 | 9263.6264 | 9355.5009 | 9500.386 | 9645.2712 | 9790.1564 | 9935.0416 | 10079.9268 | 10224.812 | 10369.6971 | 10514.5823 | 10659.4675 | 10804.3527 | 10949.2379 | 0.00039271 | 0.00039965 | 0.00040659 | 0.00041353 | 0.00042047 | 0.00042742 | 0.00043436 | 0.0004413 | 0.00044824 | 0.00045518 | 0.00046212 | 0.00046907 | 0.00047601 | 0.00048295 | 0.00048989 | 0.00049683 | 0.00050377 | 0.00051072 | 0.00051766 | 0.0005246 | 37766.3531 | 38489.1566 | 39326.2392 | 40054.7977 | 40494.7812 | 40927.0914 | 41711.8303 | 42622.3582 | 43045.0766 | 43711.6998 | 44378.323 | 45044.9462 | 45711.5694 | 46378.1926 | 47044.8158 | 47711.439 | 48378.0622 | 49044.6854 | 49711.3086 | 50377.9318 | 626817.1767 | 37732.0154 | -21871.0091 | 604946.1676 | TRUE
| KGT004 | KGTS | 11 | FALSE | 11 | 10 | 12 | 43210.6088 | 11999.4652 | 0.009704 | 0.0098778 | 0.010052 | 0.010225 | 0.010399 | 0.010573 | 0.010747 | 0.01092 | 0.011094 | 0.011268 | 0.011442 | 0.011615 | 0.011789 | 0.011963 | 0.012137 | 0.01231 | 0.012484 | 0.012658 | 0.012832 | 0.013005 | 24989.6608 | 25610.1582 | 26456.8504 | 27138.1107 | 27553.7208 | 28060.4176 | 28898.0934 | 29939.25 | 30269.8612 | 30743.9513 | 31218.0414 | 31692.1315 | 32166.2216 | 32640.3117 | 33114.4017 | 33588.4918 | 34062.5819 | 34536.672 | 35010.7621 | 35484.8521 | 6939.5589 | 7111.8693 | 7346.9934 | 7536.1774 | 7651.5912 | 7792.2995 | 8024.9197 | 8314.046 | 8405.8558 | 8537.5093 | 8669.1628 | 8800.8163 | 8932.4698 | 9064.1233 | 9195.7768 | 9327.4302 | 9459.0837 | 9590.7372 | 9722.3907 | 9854.0442 | 0.0043229 | 0.0044003 | 0.0044777 | 0.0045551 | 0.0046325 | 0.0047099 | 0.0047873 | 0.0048647 | 0.0049421 | 0.0050196 | 0.005097 | 0.0051744 | 0.0052518 | 0.0053292 | 0.0054066 | 0.005484 | 0.0055614 | 0.0056388 | 0.0057162 | 0.0057936 | 31929.224 | 32722.0319 | 33803.8482 | 34674.2927 | 35205.3166 | 35852.7218 | 36923.0179 | 38253.3009 | 38675.722 | 39281.4656 | 39887.2093 | 40492.9529 | 41098.6966 | 41704.4402 | 42310.1839 | 42915.9275 | 43521.6712 | 44127.4148 | 44733.1585 | 45338.9021 | 554895.2505 | 520273.9923 | -301571.9438 | 253323.3067 | TRUE
| KGTSGSF | KGTS | 2 | TRUE | 0 | 0 | 0 | 43210.6088 | 11999.4652 | 0.0096746 | 0.0098386 | 0.010003 | 0.010166 | 0.01033 | 0.010494 | 0.010658 | 0.010822 | 0.010986 | 0.01115 | 0.011314 | 0.011478 | 0.011642 | 0.011806 | 0.01197 | 0.012134 | 0.012298 | 0.012462 | 0.012626 | 0.01279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007836 | 0.00079688 | 0.00081016 | 0.00082344 | 0.00083672 | 0.00085 | 0.00086328 | 0.00087656 | 0.00088984 | 0.00090312 | 0.0009164 | 0.00092968 | 0.00094296 | 0.00095624 | 0.00096952 | 0.0009828 | 0.00099608 | 0.0010094 | 0.0010226 | 0.0010359 | 0.0007836 | 0.00079688 | 0.00081016 | 0.00082344 | 0.00083672 | 0.00085 | 0.00086328 | 0.00087656 | 0.00088984 | 0.00090312 | 0.0009164 | 0.00092968 | 0.00094296 | 0.00095624 | 0.00096952 | 0.0009828 | 0.00099608 | 0.0010094 | 0.0010226 | 0.0010359 | 0.012936 | 0 | 0 | 0.012936 | TRUE
| KYM001 | KYM | 9 | FALSE | 9 | 7 | 6 | 47800.3495 | 11425.2342 | 0.0097222 | 0.009902 | 0.010082 | 0.010262 | 0.010441 | 0.010621 | 0.010801 | 0.010981 | 0.011161 | 0.011341 | 0.01152 | 0.0117 | 0.01188 | 0.01206 | 0.01224 | 0.012419 | 0.012599 | 0.012779 | 0.012959 | 0.013139 | 37822.6636 | 38762.0752 | 40052.1067 | 41363.0462 | 42138.4437 | 42967.0411 | 44270.0815 | 45911.4867 | 46987.7302 | 47744.7745 | 48501.8189 | 49258.8632 | 50015.9075 | 50772.9518 | 51529.9961 | 52287.0404 | 53044.0848 | 53801.1291 | 54558.1734 | 55315.2177 | 9040.3688 | 9264.9069 | 9573.2501 | 9886.5907 | 10071.9261 | 10269.9774 | 10581.4299 | 10973.7584 | 11231.002 | 11411.9507 | 11592.8993 | 11773.848 | 11954.7966 | 12135.7453 | 12316.6939 | 12497.6426 | 12678.5912 | 12859.5399 | 13040.4885 | 13221.4372 | 0.0035436 | 0.0036091 | 0.0036746 | 0.0037402 | 0.0038057 | 0.0038713 | 0.0039368 | 0.0040023 | 0.0040679 | 0.0041334 | 0.0041989 | 0.0042645 | 0.00433 | 0.0043956 | 0.0044611 | 0.0045266 | 0.0045922 | 0.0046577 | 0.0047233 | 0.0047888 | 46863.036 | 48026.9857 | 49625.3605 | 51249.6407 | 52210.3737 | 53237.0224 | 54851.5153 | 56885.2491 | 58218.7363 | 59156.7294 | 60094.7224 | 61032.7154 | 61970.7085 | 62908.7015 | 63846.6945 | 64784.6876 | 65722.6806 | 66660.6736 | 67598.6667 | 68536.6597 | 829539.2895 | 297869.0115 | -172656.981 | 656882.3085 | TRUE
| KYM002 | KYM | 1 | FALSE | 1 | 2 | 0 | 47800.3495 | 11425.2342 | 0.009718 | 0.0098965 | 0.010075 | 0.010253 | 0.010432 | 0.01061 | 0.010789 | 0.010967 | 0.011146 | 0.011324 | 0.011502 | 0.011681 | 0.011859 | 0.012038 | 0.012216 | 0.012395 | 0.012573 | 0.012751 | 0.01293 | 0.013108 | 27354.4214 | 27569.0046 | 28066.0775 | 28066.4 | 28251.591 | 28529.2163 | 28956.7313 | 29223.1184 | 29536.5872 | 30009.4548 | 30482.3225 | 30955.1901 | 31428.0577 | 31900.9253 | 32373.7929 | 32846.6605 | 33319.5282 | 33792.3958 | 34265.2634 | 34738.131 | 6538.2508 | 6589.5404 | 6708.3507 | 6708.4278 | 6752.6921 | 6819.0501 | 6921.2347 | 6984.9065 | 7059.8318 | 7172.8566 | 7285.8813 | 7398.9061 | 7511.9308 | 7624.9556 | 7737.9804 | 7851.0051 | 7964.0299 | 8077.0547 | 8190.0794 | 8303.1042 | 0.00039356 | 0.00040079 | 0.00040801 | 0.00041524 | 0.00042247 | 0.00042969 | 0.00043692 | 0.00044414 | 0.00045137 | 0.0004586 | 0.00046582 | 0.00047305 | 0.00048028 | 0.0004875 | 0.00049473 | 0.00050195 | 0.00050918 | 0.00051641 | 0.00052363 | 0.00053086 | 33892.6726 | 34158.5454 | 34774.4286 | 34774.8282 | 35004.2836 | 35348.2669 | 35877.9664 | 36208.0254 | 36596.4195 | 37182.3119 | 37768.2042 | 38354.0966 | 38939.989 | 39525.8814 | 40111.7738 | 40697.6662 | 41283.5586 | 41869.451 | 42455.3433 | 43041.2357 | 539885.5782 | 37732.0154 | -21871.0091 | 518014.5691 | TRUE
| KYM003 | KYM | 6 | FALSE | 6 | 6 | 6 | 47800.3495 | 11425.2342 | 0.0096964 | 0.0098676 | 0.010039 | 0.01021 | 0.010381 | 0.010552 | 0.010724 | 0.010895 | 0.011066 | 0.011237 | 0.011408 | 0.01158 | 0.011751 | 0.011922 | 0.012093 | 0.012264 | 0.012436 | 0.012607 | 0.012778 | 0.012949 | 25179.4571 | 25719.6638 | 26555.0016 | 27304.6809 | 27661.958 | 28220.413 | 29145.8597 | 30297.3684 | 30612.6457 | 31086.2717 | 31559.8976 | 32033.5236 | 32507.1495 | 32980.7755 | 33454.4014 | 33928.0274 | 34401.6533 | 34875.2793 | 35348.9053 | 35822.5312 | 6018.391 | 6147.5112 | 6347.1735 | 6526.3618 | 6611.7581 | 6745.24 | 6966.4401 | 7241.6736 | 7317.0312 | 7430.2372 | 7543.4432 | 7656.6492 | 7769.8553 | 7883.0613 | 7996.2673 | 8109.4733 | 8222.6794 | 8335.8854 | 8449.0914 | 8562.2974 | 0.0023561 | 0.0023977 | 0.0024393 | 0.0024809 | 0.0025225 | 0.0025641 | 0.0026057 | 0.0026473 | 0.0026889 | 0.0027305 | 0.0027721 | 0.0028137 | 0.0028553 | 0.0028969 | 0.0029385 | 0.0029801 | 0.0030217 | 0.0030633 | 0.0031049 | 0.0031465 | 31197.8505 | 31867.1774 | 32902.1776 | 33831.0452 | 34273.7187 | 34965.6556 | 36112.3025 | 37539.0446 | 37929.6796 | 38516.5116 | 39103.3436 | 39690.1756 | 40277.0076 | 40863.8397 | 41450.6717 | 42037.5037 | 42624.3357 | 43211.1677 | 43797.9998 | 44384.8318 | 542768.6934 | 279003.0038 | -161721.4764 | 381047.217 | TRUE
| KYM004 | KYM | 22 | FALSE | 22 | 11 | 28 | 47800.3495 | 11425.2342 | 0.0097024 | 0.0098757 | 0.010049 | 0.010222 | 0.010395 | 0.010569 | 0.010742 | 0.010915 | 0.011088 | 0.011262 | 0.011435 | 0.011608 | 0.011781 | 0.011954 | 0.012128 | 0.012301 | 0.012474 | 0.012647 | 0.012821 | 0.012994 | 25430.2437 | 26123.5131 | 27068.5978 | 27881.8965 | 28253.6774 | 28826.9105 | 29871.875 | 30988.1843 | 31426.2743 | 31917.2451 | 32408.216 | 32899.1868 | 33390.1577 | 33881.1285 | 34372.0994 | 34863.0702 | 35354.0411 | 35845.0119 | 36335.9828 | 36826.9536 | 6078.334 | 6244.0392 | 6469.9332 | 6664.3278 | 6753.1908 | 6890.2049 | 7139.9722 | 7406.7924 | 7511.5046 | 7628.8564 | 7746.2082 | 7863.56 | 7980.9118 | 8098.2636 | 8215.6154 | 8332.9672 | 8450.319 | 8567.6708 | 8685.0226 | 8802.3743 | 0.0086444 | 0.0087988 | 0.0089531 | 0.0091074 | 0.0092618 | 0.0094161 | 0.0095705 | 0.0097248 | 0.0098792 | 0.010033 | 0.010188 | 0.010342 | 0.010497 | 0.010651 | 0.010805 | 0.01096 | 0.011114 | 0.011268 | 0.011423 | 0.011577 | 31508.5863 | 32367.5611 | 33538.54 | 34546.2334 | 35006.8775 | 35717.1249 | 37011.8568 | 38394.9864 | 38937.7887 | 39546.1115 | 40154.4343 | 40762.7571 | 41371.0799 | 41979.4027 | 42587.7255 | 43196.0483 | 43804.3711 | 44412.6939 | 45021.0167 | 45629.3395 | 555741.0295 | 981291.8873 | -568796.6461 | -13055.6166 | FALSE
| KYM006 | KYM | 6 | FALSE | 6 | 5 | 6 | 47800.3495 | 11425.2342 | 0.0097044 | 0.0098783 | 0.010052 | 0.010226 | 0.0104 | 0.010574 | 0.010748 | 0.010922 | 0.011096 | 0.01127 | 0.011443 | 0.011617 | 0.011791 | 0.011965 | 0.012139 | 0.012313 | 0.012487 | 0.012661 | 0.012835 | 0.013009 | 30842.3337 | 31347.1678 | 31850.3167 | 32401.324 | 32801.1738 | 33247.1968 | 33898.1331 | 34711.1797 | 35102.6043 | 35652.7691 | 36202.9338 | 36753.0985 | 37303.2633 | 37853.428 | 38403.5927 | 38953.7574 | 39503.9222 | 40054.0869 | 40604.2516 | 41154.4164 | 7371.9312 | 7492.5965 | 7612.8592 | 7744.5608 | 7840.1329 | 7946.7413 | 8102.328 | 8296.6623 | 8390.2206 | 8521.7209 | 8653.2212 | 8784.7215 | 8916.2218 | 9047.7221 | 9179.2225 | 9310.7228 | 9442.2231 | 9573.7234 | 9705.2237 | 9836.724 | 0.0023581 | 0.0024003 | 0.0024426 | 0.0024848 | 0.0025271 | 0.0025693 | 0.0026116 | 0.0026539 | 0.0026961 | 0.0027384 | 0.0027806 | 0.0028229 | 0.0028651 | 0.0029074 | 0.0029496 | 0.0029919 | 0.0030342 | 0.0030764 | 0.0031187 | 0.0031609 | 38214.2673 | 38839.7667 | 39463.1783 | 40145.8873 | 40641.3092 | 41193.9406 | 42000.4638 | 43007.8447 | 43492.8276 | 44174.4927 | 44856.1578 | 45537.8229 | 46219.4879 | 46901.153 | 47582.8181 | 48264.4832 | 48946.1483 | 49627.8134 | 50309.4785 | 50991.1435 | 632586.3659 | 260136.9962 | -150785.9719 | 481800.394 | TRUE
| MBN031 | MBN | 14 | FALSE | 14 | 9 | 12 | 42126.3122 | 11964.0504 | 0.0096396 | 0.0097918 | 0.0099441 | 0.010096 | 0.010249 | 0.010401 | 0.010553 | 0.010706 | 0.010858 | 0.01101 | 0.011162 | 0.011315 | 0.011467 | 0.011619 | 0.011771 | 0.011924 | 0.012076 | 0.012228 | 0.012381 | 0.012533 | 24077.3447 | 24666.7389 | 25517.384 | 26253.0079 | 26692.7247 | 27222.5594 | 28116.7664 | 29116.6956 | 29577.2181 | 29992.0315 | 30406.8449 | 30821.6582 | 31236.4716 | 31651.285 | 32066.0984 | 32480.9118 | 32895.7252 | 33310.5386 | 33725.3519 | 34140.1653 | 6838.0675 | 7005.4579 | 7247.0447 | 7455.965 | 7580.8464 | 7731.3217 | 7985.2803 | 8269.2644 | 8400.0547 | 8517.8635 | 8635.6722 | 8753.481 | 8871.2897 | 8989.0985 | 9106.9072 | 9224.716 | 9342.5247 | 9460.3335 | 9578.1422 | 9695.951 | 0.0054654 | 0.0055517 | 0.005638 | 0.0057244 | 0.0058107 | 0.005897 | 0.0059834 | 0.0060697 | 0.0061561 | 0.0062424 | 0.0063287 | 0.0064151 | 0.0065014 | 0.0065877 | 0.0066741 | 0.0067604 | 0.0068467 | 0.0069331 | 0.0070194 | 0.0071058 | 30915.4177 | 31672.2023 | 32764.4344 | 33708.9786 | 34273.577 | 34953.8869 | 36102.0527 | 37385.966 | 37977.2789 | 38509.9012 | 39042.5234 | 39575.1456 | 40107.7678 | 40640.3901 | 41173.0123 | 41705.6345 | 42238.2567 | 42770.879 | 43303.5012 | 43836.1234 | 540229.8331 | 501407.9846 | -290636.4392 | 249593.3938 | TRUE
| MBN032 | MBN | 2 | FALSE | 2 | 0 | 4 | 42126.3122 | 11964.0504 | 0.0096451 | 0.0097992 | 0.0099533 | 0.010107 | 0.010262 | 0.010416 | 0.01057 | 0.010724 | 0.010878 | 0.011032 | 0.011186 | 0.01134 | 0.011494 | 0.011649 | 0.011803 | 0.011957 | 0.012111 | 0.012265 | 0.012419 | 0.012573 | 53123.9671 | 55060.6321 | 57201.5035 | 59122.9235 | 60637.7938 | 62348.9744 | 64670.5267 | 67261.8134 | 68785.7853 | 69760.3073 | 70734.8294 | 71709.3515 | 72683.8735 | 73658.3956 | 74632.9177 | 75607.4397 | 76581.9618 | 77556.4839 | 78531.0059 | 79505.528 | 15087.4307 | 15637.4518 | 16245.4683 | 16791.1597 | 17221.3892 | 17707.3717 | 18366.7024 | 19102.6387 | 19535.4532 | 19812.2216 | 20088.9899 | 20365.7583 | 20642.5267 | 20919.2951 | 21196.0634 | 21472.8318 | 21749.6002 | 22026.3686 | 22303.137 | 22579.9053 | 0.00078121 | 0.00079369 | 0.00080618 | 0.00081866 | 0.00083114 | 0.00084362 | 0.00085611 | 0.00086859 | 0.00088107 | 0.00089355 | 0.00090604 | 0.00091852 | 0.000931 | 0.00094348 | 0.00095597 | 0.00096845 | 0.00098093 | 0.00099341 | 0.0010059 | 0.0010184 | 68211.3986 | 70698.0847 | 73446.9726 | 75914.0839 | 77859.1839 | 80056.347 | 83037.2299 | 86364.453 | 88321.2393 | 89572.5298 | 90823.8202 | 92075.1107 | 93326.4012 | 94577.6916 | 95828.9821 | 97080.2725 | 98331.563 | 99582.8535 | 100834.1439 | 102085.4344 | 1241905.8134 | 110537.9718 | -64072.2994 | 1177833.5139 | TRUE
| MDA023 | MDA | 4 | FALSE | 4 | 2 | 4 | 44598.6589 | 11923.6919 | 0.0096451 | 0.0097992 | 0.0099533 | 0.010107 | 0.010262 | 0.010416 | 0.01057 | 0.010724 | 0.010878 | 0.011032 | 0.011186 | 0.01134 | 0.011495 | 0.011649 | 0.011803 | 0.011957 | 0.012111 | 0.012265 | 0.012419 | 0.012573 | 75948.3045 | 77826.3125 | 80175.137 | 82193.288 | 83771.2756 | 85547.343 | 87959.8549 | 90648.1814 | 92344.31 | 93652.639 | 94960.9679 | 96269.2969 | 97577.6258 | 98885.9548 | 100194.2837 | 101502.6126 | 102810.9416 | 104119.2705 | 105427.5995 | 106735.9284 | 20305.1887 | 20807.2843 | 21435.2551 | 21974.8187 | 22396.7022 | 22871.5434 | 23516.5414 | 24235.28 | 24688.7491 | 25038.5379 | 25388.3267 | 25738.1155 | 26087.9043 | 26437.6931 | 26787.4819 | 27137.2707 | 27487.0595 | 27836.8483 | 28186.6371 | 28536.4259 | 0.0015624 | 0.0015874 | 0.0016124 | 0.0016373 | 0.0016623 | 0.0016873 | 0.0017122 | 0.0017372 | 0.0017622 | 0.0017871 | 0.0018121 | 0.0018371 | 0.001862 | 0.001887 | 0.0019119 | 0.0019369 | 0.0019619 | 0.0019868 | 0.0020118 | 0.0020368 | 96253.4947 | 98633.5984 | 101610.3938 | 104168.1083 | 106167.9794 | 108418.8881 | 111476.3981 | 114883.4631 | 117033.0609 | 118691.1787 | 120349.2965 | 122007.4142 | 123665.532 | 125323.6498 | 126981.7675 | 128639.8853 | 130298.0031 | 131956.1209 | 133614.2386 | 135272.3564 | 1669207.0265 | 148269.9872 | -85943.3085 | 1583263.7179 | TRUE
| MDA032 | MDA | 1 | FALSE | 1 | 1 | 1 | 44598.6589 | 11923.6919 | 0.0096531 | 0.0098098 | 0.0099666 | 0.010123 | 0.01028 | 0.010437 | 0.010594 | 0.01075 | 0.010907 | 0.011064 | 0.011221 | 0.011378 | 0.011534 | 0.011691 | 0.011848 | 0.012005 | 0.012161 | 0.012318 | 0.012475 | 0.012632 | 33031.1796 | 33700.66 | 34464.4956 | 35052.3766 | 35455.7992 | 35996.5026 | 36824.5235 | 37758.238 | 38210.2555 | 38759.4628 | 39308.6701 | 39857.8773 | 40407.0846 | 40956.2919 | 41505.4992 | 42054.7064 | 42603.9137 | 43153.121 | 43702.3283 | 44251.5355 | 8831.0639 | 9010.0531 | 9214.2687 | 9371.4419 | 9479.2991 | 9623.859 | 9845.2349 | 10094.8685 | 10215.7178 | 10362.5513 | 10509.3849 | 10656.2184 | 10803.0519 | 10949.8854 | 11096.719 | 11243.5525 | 11390.386 | 11537.2196 | 11684.0531 | 11830.8866 | 0.00039093 | 0.00039728 | 0.00040363 | 0.00040998 | 0.00041632 | 0.00042267 | 0.00042902 | 0.00043537 | 0.00044172 | 0.00044807 | 0.00045442 | 0.00046077 | 0.00046712 | 0.00047347 | 0.00047981 | 0.00048616 | 0.00049251 | 0.00049886 | 0.00050521 | 0.00051156 | 41862.2439 | 42710.7135 | 43678.7647 | 44423.8189 | 44935.0986 | 45620.3621 | 46669.7588 | 47853.107 | 48425.9738 | 49122.0146 | 49818.0554 | 50514.0962 | 51210.137 | 51906.1778 | 52602.2186 | 53298.2594 | 53994.3002 | 54690.341 | 55386.3818 | 56082.4227 | 699703.7944 | 46500.5006 | -26953.5794 | 672750.215 | TRUE
| MNA021 | MNA | 5 | FALSE | 5 | 5 | 3 | 48575.8986 | 11806.2544 | 0.0096776 | 0.0098425 | 0.010007 | 0.010172 | 0.010337 | 0.010502 | 0.010667 | 0.010832 | 0.010997 | 0.011162 | 0.011327 | 0.011492 | 0.011657 | 0.011822 | 0.011987 | 0.012152 | 0.012317 | 0.012482 | 0.012647 | 0.012812 | 42024.0728 | 42740.3551 | 43604.4492 | 44373.2505 | 44940.0969 | 45553.7776 | 46531.8428 | 47571.3603 | 48133.3341 | 48855.3012 | 49577.2683 | 50299.2354 | 51021.2025 | 51743.1696 | 52465.1367 | 53187.1038 | 53909.0709 | 54631.0381 | 55353.0052 | 56074.9723 | 10213.8491 | 10387.9398 | 10597.9557 | 10784.811 | 10922.5817 | 11071.7353 | 11309.4517 | 11562.1039 | 11698.6902 | 11874.1626 | 12049.6349 | 12225.1073 | 12400.5796 | 12576.052 | 12751.5244 | 12926.9967 | 13102.4691 | 13277.9414 | 13453.4138 | 13628.8861 | 0.0019596 | 0.001993 | 0.0020264 | 0.0020598 | 0.0020932 | 0.0021266 | 0.00216 | 0.0021934 | 0.0022268 | 0.0022602 | 0.0022936 | 0.002327 | 0.0023604 | 0.0023938 | 0.0024272 | 0.0024606 | 0.002494 | 0.0025274 | 0.0025608 | 0.0025942 | 52237.9238 | 53128.2969 | 54202.4069 | 55158.0636 | 55862.6807 | 56625.5149 | 57841.2966 | 59133.4664 | 59832.0265 | 60729.466 | 61626.9055 | 62524.345 | 63421.7845 | 64319.224 | 65216.6635 | 66114.103 | 67011.5425 | 67908.982 | 68806.4215 | 69703.861 | 867895.709 | 177233.5173 | -102731.7473 | 765163.9617 | TRUE
| MNA034 | MNA | 40 | FALSE | 40 | 37 | 28 | 48575.8986 | 11806.2544 | 0.0096801 | 0.0098459 | 0.010012 | 0.010178 | 0.010343 | 0.010509 | 0.010675 | 0.010841 | 0.011007 | 0.011172 | 0.011338 | 0.011504 | 0.01167 | 0.011836 | 0.012001 | 0.012167 | 0.012333 | 0.012499 | 0.012665 | 0.01283 | 31407.2 | 32235.9862 | 33173.1508 | 33973.0528 | 34526.4975 | 35183.4229 | 36211.5098 | 37307.6628 | 37769.8712 | 38338.8254 | 38907.7797 | 39476.7339 | 40045.6881 | 40614.6424 | 41183.5966 | 41752.5508 | 42321.5051 | 42890.4593 | 43459.4136 | 44028.3678 | 7633.4439 | 7834.8783 | 8062.6539 | 8257.0682 | 8391.5816 | 8551.2457 | 8801.1197 | 9067.537 | 9179.8757 | 9318.1586 | 9456.4416 | 9594.7245 | 9733.0075 | 9871.2904 | 10009.5734 | 10147.8563 | 10286.1393 | 10424.4222 | 10562.7052 | 10700.9881 | 0.015681 | 0.01595 | 0.016218 | 0.016487 | 0.016755 | 0.017024 | 0.017292 | 0.017561 | 0.01783 | 0.018098 | 0.018367 | 0.018635 | 0.018904 | 0.019173 | 0.019441 | 0.01971 | 0.019978 | 0.020247 | 0.020515 | 0.020784 | 39040.6595 | 40070.8805 | 41235.8209 | 42230.1375 | 42918.0959 | 43734.6856 | 45012.6468 | 46375.2174 | 46949.7647 | 47657.0022 | 48364.2396 | 49071.4771 | 49778.7145 | 50485.952 | 51193.1894 | 51900.4269 | 52607.6643 | 53314.9018 | 54022.1392 | 54729.3767 | 673886.1462 | 1471808.0871 | -853119.7643 | -179233.6181 | FALSE
| MNASTN | MNA | 1 | TRUE | 0 | 0 | 0 | 48575.8986 | 11806.2544 | 0.0096815 | 0.0098478 | 0.010014 | 0.01018 | 0.010347 | 0.010513 | 0.010679 | 0.010845 | 0.011012 | 0.011178 | 0.011344 | 0.01151 | 0.011677 | 0.011843 | 0.012009 | 0.012175 | 0.012342 | 0.012508 | 0.012674 | 0.01284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00039208 | 0.00039881 | 0.00040555 | 0.00041228 | 0.00041901 | 0.00042575 | 0.00043248 | 0.00043921 | 0.00044594 | 0.00045268 | 0.00045941 | 0.00046614 | 0.00047288 | 0.00047961 | 0.00048634 | 0.00049307 | 0.00049981 | 0.00050654 | 0.00051327 | 0.00052001 | 0.00039208 | 0.00039881 | 0.00040555 | 0.00041228 | 0.00041901 | 0.00042575 | 0.00043248 | 0.00043921 | 0.00044594 | 0.00045268 | 0.00045941 | 0.00046614 | 0.00047288 | 0.00047961 | 0.00048634 | 0.00049307 | 0.00049981 | 0.00050654 | 0.00051327 | 0.00052001 | 0.0064834 | 0 | 0 | 0.0064834 | TRUE
| MRO005 | MRO | 54 | FALSE | 54 | 58 | 31 | 40985.6902 | 10762.4764 | 0.0097494 | 0.0099383 | 0.010127 | 0.010316 | 0.010505 | 0.010694 | 0.010883 | 0.011072 | 0.011261 | 0.01145 | 0.011638 | 0.011827 | 0.012016 | 0.012205 | 0.012394 | 0.012583 | 0.012772 | 0.012961 | 0.01315 | 0.013339 | 23935.4204 | 24523.0379 | 25157.433 | 25755.2517 | 26226.8626 | 26742.8969 | 27350.9169 | 27963.6451 | 28440.749 | 28917.8529 | 29394.9567 | 29872.0606 | 30349.1644 | 30826.2683 | 31303.3722 | 31780.476 | 32257.5799 | 32734.6838 | 33211.7876 | 33688.8915 | 6285.2277 | 6439.5308 | 6606.1173 | 6763.0992 | 6886.94 | 7022.446 | 7182.1066 | 7343.0036 | 7468.2868 | 7593.57 | 7718.8532 | 7844.1364 | 7969.4197 | 8094.7029 | 8219.9861 | 8345.2693 | 8470.5525 | 8595.8357 | 8721.1189 | 8846.4022 | 0.021321 | 0.021734 | 0.022147 | 0.02256 | 0.022973 | 0.023386 | 0.0238 | 0.024213 | 0.024626 | 0.025039 | 0.025452 | 0.025865 | 0.026278 | 0.026691 | 0.027104 | 0.027518 | 0.027931 | 0.028344 | 0.028757 | 0.02917 | 30220.6695 | 30962.5905 | 31763.5724 | 32518.3735 | 33113.8256 | 33765.3663 | 34533.0473 | 35306.6729 | 35909.0604 | 36511.4479 | 37113.8354 | 37716.2229 | 38318.6104 | 38920.9979 | 39523.3854 | 40125.7728 | 40728.1603 | 41330.5478 | 41932.9353 | 42535.3228 | 519271.9017 | 1950897.7272 | -1130819.5844 | -611547.6827 | FALSE
| MRO007 | MRO | 24 | FALSE | 24 | 21 | 23 | 40985.6902 | 10762.4764 | 0.0097535 | 0.0099438 | 0.010134 | 0.010324 | 0.010515 | 0.010705 | 0.010895 | 0.011085 | 0.011276 | 0.011466 | 0.011656 | 0.011846 | 0.012037 | 0.012227 | 0.012417 | 0.012607 | 0.012798 | 0.012988 | 0.013178 | 0.013368 | 22527.3154 | 23173.2798 | 23953.44 | 24746.2456 | 25333.3061 | 25880.6402 | 26747.9472 | 27675.5294 | 28291.0422 | 28768.4075 | 29245.7728 | 29723.1381 | 30200.5034 | 30677.8688 | 31155.2341 | 31632.5994 | 32109.9647 | 32587.3301 | 33064.6954 | 33542.0607 | 5915.4719 | 6085.0964 | 6289.9595 | 6498.1432 | 6652.3 | 6796.0251 | 7023.7721 | 7267.347 | 7428.9751 | 7554.327 | 7679.6789 | 7805.0307 | 7930.3826 | 8055.7345 | 8181.0863 | 8306.4382 | 8431.7901 | 8557.142 | 8682.4938 | 8807.8457 | 0.0094799 | 0.0096648 | 0.0098498 | 0.010035 | 0.01022 | 0.010405 | 0.010589 | 0.010774 | 0.010959 | 0.011144 | 0.011329 | 0.011514 | 0.011699 | 0.011884 | 0.012069 | 0.012254 | 0.012439 | 0.012624 | 0.012808 | 0.012993 | 28442.7968 | 29258.3859 | 30243.4094 | 31244.3989 | 31985.6164 | 32676.6757 | 33771.7299 | 34942.8872 | 35720.0282 | 36322.7456 | 36925.463 | 37528.1804 | 38130.8977 | 38733.6151 | 39336.3325 | 39939.0499 | 40541.7673 | 41144.4846 | 41747.202 | 42349.9194 | 509225.533 | 1031779.4994 | -598061.3173 | -88835.7842 | FALSE
| MRO008 | MRO | 22 | FALSE | 22 | 18 | 18 | 40985.6902 | 10762.4764 | 0.0097316 | 0.0099145 | 0.010097 | 0.01028 | 0.010463 | 0.010646 | 0.010829 | 0.011012 | 0.011195 | 0.011378 | 0.011561 | 0.011744 | 0.011927 | 0.01211 | 0.012293 | 0.012476 | 0.012659 | 0.012842 | 0.013025 | 0.013208 | 26276.7155 | 26853.0829 | 27516.3818 | 28143.0548 | 28643.8908 | 29188.9525 | 29915.4768 | 30649.6012 | 31158.7971 | 31667.993 | 32177.1889 | 32686.3848 | 33195.5807 | 33704.7766 | 34213.9725 | 34723.1684 | 35232.3643 | 35741.5602 | 36250.7561 | 36759.9521 | 6900.0309 | 7051.3799 | 7225.5562 | 7390.115 | 7521.63 | 7664.7583 | 7855.5372 | 8048.3117 | 8182.022 | 8315.7323 | 8449.4426 | 8583.1529 | 8716.8632 | 8850.5734 | 8984.2837 | 9117.994 | 9251.7043 | 9385.4146 | 9519.1249 | 9652.8352 | 0.0086704 | 0.0088334 | 0.0089964 | 0.0091594 | 0.0093224 | 0.0094854 | 0.0096484 | 0.0098114 | 0.0099744 | 0.010137 | 0.0103 | 0.010463 | 0.010626 | 0.010789 | 0.010952 | 0.011115 | 0.011278 | 0.011441 | 0.011604 | 0.011767 | 33176.7551 | 33904.4716 | 34741.947 | 35533.179 | 36165.5302 | 36853.7203 | 37771.0237 | 38697.9226 | 39340.829 | 39983.7354 | 40626.6417 | 41269.5481 | 41912.4545 | 42555.3608 | 43198.2672 | 43841.1736 | 44484.08 | 45126.9863 | 45769.8927 | 46412.7991 | 567917.3453 | 837009.0115 | -485164.4293 | 82752.916 | TRUE
| NHL015 | NHL | 8 | FALSE | 8 | 9 | 5 | 44485.8086 | 11603.2642 | 0.0095668 | 0.0096948 | 0.0098228 | 0.0099508 | 0.010079 | 0.010207 | 0.010335 | 0.010463 | 0.010591 | 0.010719 | 0.010847 | 0.010975 | 0.011103 | 0.011231 | 0.011359 | 0.011487 | 0.011615 | 0.011743 | 0.011871 | 0.011999 | 14536.4453 | 14687.2416 | 14925.4619 | 15075.1038 | 15132.7042 | 15186.8416 | 15377.3097 | 15567.7777 | 15614.989 | 15803.7255 | 15992.4621 | 16181.1986 | 16369.9351 | 16558.6717 | 16747.4082 | 16936.1447 | 17124.8813 | 17313.6178 | 17502.3543 | 17691.0908 | 3791.5511 | 3830.8834 | 3893.0185 | 3932.0497 | 3947.0737 | 3961.1944 | 4010.8743 | 4060.5542 | 4072.8684 | 4122.0966 | 4171.3249 | 4220.5532 | 4269.7815 | 4319.0098 | 4368.238 | 4417.4663 | 4466.6946 | 4515.9229 | 4565.1512 | 4614.3794 | 0.0030995 | 0.0031409 | 0.0031824 | 0.0032239 | 0.0032654 | 0.0033068 | 0.0033483 | 0.0033898 | 0.0034313 | 0.0034727 | 0.0035142 | 0.0035557 | 0.0035972 | 0.0036386 | 0.0036801 | 0.0037216 | 0.003763 | 0.0038045 | 0.003846 | 0.0038875 | 18327.9995 | 18518.1281 | 18818.4836 | 19007.1567 | 19079.7812 | 19148.0393 | 19388.1873 | 19628.3353 | 19687.8608 | 19925.8257 | 20163.7905 | 20401.7554 | 20639.7202 | 20877.6851 | 21115.6499 | 21353.6148 | 21591.5796 | 21829.5445 | 22067.5093 | 22305.4742 | 288609.3763 | 307966.5339 | -178509.9152 | 110099.4611 | TRUE
| NHL016 | NHL | 1 | FALSE | 1 | 1 | 1 | 44485.8086 | 11603.2642 | 0.009538 | 0.0096564 | 0.0097748 | 0.0098933 | 0.010012 | 0.01013 | 0.010249 | 0.010367 | 0.010485 | 0.010604 | 0.010722 | 0.010841 | 0.010959 | 0.011077 | 0.011196 | 0.011314 | 0.011433 | 0.011551 | 0.01167 | 0.011788 | 15008.788 | 15020.9743 | 15161.1081 | 15210.9603 | 15167.3271 | 15164.0293 | 15248.8776 | 15378.3328 | 15317.6137 | 15490.608 | 15663.6022 | 15836.5964 | 16009.5907 | 16182.5849 | 16355.5791 | 16528.5733 | 16701.5676 | 16874.5618 | 17047.556 | 17220.5503 | 3914.7525 | 3917.9311 | 3954.4823 | 3967.4853 | 3956.1044 | 3955.2442 | 3977.3753 | 4011.1412 | 3995.3038 | 4040.426 | 4085.5482 | 4130.6704 | 4175.7926 | 4220.9148 | 4266.037 | 4311.1592 | 4356.2814 | 4401.4036 | 4446.5258 | 4491.648 | 0.00038627 | 0.00039106 | 0.00039586 | 0.00040066 | 0.00040545 | 0.00041025 | 0.00041504 | 0.00041984 | 0.00042463 | 0.00042943 | 0.00043423 | 0.00043902 | 0.00044382 | 0.00044861 | 0.00045341 | 0.00045821 | 0.000463 | 0.0004678 | 0.00047259 | 0.00047739 | 18923.5409 | 18938.9058 | 19115.5908 | 19178.4459 | 19123.4319 | 19119.274 | 19226.2533 | 19389.4743 | 19312.9179 | 19531.0344 | 19749.1508 | 19967.2672 | 20185.3837 | 20403.5001 | 20621.6166 | 20839.733 | 21057.8494 | 21275.9659 | 21494.0823 | 21712.1988 | 286164.7435 | 46500.5006 | -26953.5794 | 259211.1641 | TRUE
| NKA001 | NKA | 4 | FALSE | 4 | 2 | 6 | 52400.9885 | 12452.6513 | 0.009688 | 0.0098565 | 0.010025 | 0.010193 | 0.010362 | 0.01053 | 0.010699 | 0.010867 | 0.011035 | 0.011204 | 0.011372 | 0.011541 | 0.011709 | 0.011878 | 0.012046 | 0.012215 | 0.012383 | 0.012551 | 0.01272 | 0.012888 | 13275.057 | 13662.8965 | 14162.5889 | 14562.952 | 14803.5868 | 15156.0745 | 15682.6034 | 16333.5091 | 16586.6676 | 16839.8261 | 17092.9845 | 17346.143 | 17599.3015 | 17852.46 | 18105.6184 | 18358.7769 | 18611.9354 | 18865.0939 | 19118.2524 | 19371.4108 | 3154.7049 | 3246.8717 | 3365.6193 | 3460.7623 | 3517.9471 | 3601.7128 | 3726.8379 | 3881.5202 | 3941.6811 | 4001.8421 | 4062.0031 | 4122.164 | 4182.325 | 4242.486 | 4302.6469 | 4362.8079 | 4422.9689 | 4483.1299 | 4543.2908 | 4603.4518 | 0.0015694 | 0.0015967 | 0.0016239 | 0.0016512 | 0.0016785 | 0.0017058 | 0.0017331 | 0.0017604 | 0.0017877 | 0.0018149 | 0.0018422 | 0.0018695 | 0.0018968 | 0.0019241 | 0.0019514 | 0.0019786 | 0.0020059 | 0.0020332 | 0.0020605 | 0.0020878 | 16429.7635 | 16909.7698 | 17528.2098 | 18023.716 | 18321.5355 | 18757.789 | 19409.4431 | 20215.031 | 20528.3505 | 20841.67 | 21154.9895 | 21468.3089 | 21781.6284 | 22094.9479 | 22408.2673 | 22721.5868 | 23034.9063 | 23348.2258 | 23661.5452 | 23974.8647 | 291797.1307 | 203538.9731 | -117979.4583 | 173817.6724 | TRUE
| NKA002 | RCTS | 10 | FALSE | 10 | 11 | 7 | 53595.3633 | 11939.647 | 0.0097128 | 0.0098895 | 0.010066 | 0.010243 | 0.01042 | 0.010596 | 0.010773 | 0.01095 | 0.011126 | 0.011303 | 0.01148 | 0.011656 | 0.011833 | 0.01201 | 0.012186 | 0.012363 | 0.01254 | 0.012716 | 0.012893 | 0.01307 | 31339.9985 | 31963.8155 | 32917.6348 | 33773.6103 | 34356.1836 | 34938.7568 | 35930.9664 | 37115.0504 | 37653.5005 | 38251.4299 | 38849.3592 | 39447.2886 | 40045.2179 | 40643.1473 | 41241.0766 | 41839.006 | 42436.9353 | 43034.8647 | 43632.794 | 44230.7234 | 6981.733 | 7120.7032 | 7333.1892 | 7523.8782 | 7653.6603 | 7783.4424 | 8004.4808 | 8268.2638 | 8388.2164 | 8521.4194 | 8654.6225 | 8787.8255 | 8921.0285 | 9054.2316 | 9187.4346 | 9320.6377 | 9453.8407 | 9587.0438 | 9720.2468 | 9853.4498 | 0.0039335 | 0.004005 | 0.0040766 | 0.0041481 | 0.0042197 | 0.0042912 | 0.0043628 | 0.0044343 | 0.0045059 | 0.0045774 | 0.004649 | 0.0047206 | 0.0047921 | 0.0048637 | 0.0049352 | 0.0050068 | 0.0050783 | 0.0051499 | 0.0052214 | 0.005293 | 38321.7354 | 39084.5227 | 40250.8281 | 41297.4927 | 42009.8481 | 42722.2035 | 43935.4516 | 45383.3186 | 46041.7214 | 46772.8539 | 47503.9863 | 48235.1188 | 48966.2513 | 49697.3837 | 50428.5162 | 51159.6487 | 51890.7811 | 52621.9136 | 53353.0461 | 54084.1785 | 661397.4556 | 400967.5352 | -232417.074 | 428980.3815 | TRUE
| NKA005 | RCTS | 9 | FALSE | 9 | 9 | 7 | 53595.3633 | 11939.647 | 0.0097109 | 0.009887 | 0.010063 | 0.010239 | 0.010415 | 0.010591 | 0.010767 | 0.010943 | 0.011119 | 0.011295 | 0.011471 | 0.011648 | 0.011824 | 0.012 | 0.012176 | 0.012352 | 0.012528 | 0.012704 | 0.01288 | 0.013056 | 23526.8259 | 24275.6027 | 25199.8462 | 25974.4446 | 26477.6386 | 27097.8102 | 28074.6532 | 29247.0462 | 29717.5729 | 30188.0996 | 30658.6262 | 31129.1529 | 31599.6796 | 32070.2063 | 32540.733 | 33011.2596 | 33481.7863 | 33952.313 | 34422.8397 | 34893.3663 | 5241.1623 | 5407.9702 | 5613.8675 | 5786.4278 | 5898.5263 | 6036.6843 | 6254.2994 | 6515.4779 | 6620.299 | 6725.1201 | 6829.9411 | 6934.7622 | 7039.5832 | 7144.4043 | 7249.2253 | 7354.0464 | 7458.8674 | 7563.6885 | 7668.5095 | 7773.3306 | 0.0035394 | 0.0036036 | 0.0036678 | 0.0037319 | 0.0037961 | 0.0038603 | 0.0039245 | 0.0039886 | 0.0040528 | 0.004117 | 0.0041811 | 0.0042453 | 0.0043095 | 0.0043736 | 0.0044378 | 0.004502 | 0.0045661 | 0.0046303 | 0.0046945 | 0.0047587 | 28767.9917 | 29683.5765 | 30813.7173 | 31760.8762 | 32376.1686 | 33134.4984 | 34328.9565 | 35762.5282 | 36337.876 | 36913.2237 | 37488.5715 | 38063.9193 | 38639.2671 | 39214.6149 | 39789.9627 | 40365.3105 | 40940.6583 | 41516.0061 | 42091.3539 | 42666.7017 | 516294.8379 | 363235.5198 | -210546.0649 | 305748.7729 | TRUE
| NKA006 | RCTS | 1 | FALSE | 1 | 0 | 2 | 53595.3633 | 11939.647 | 0.009727 | 0.0099084 | 0.01009 | 0.010271 | 0.010453 | 0.010634 | 0.010815 | 0.010997 | 0.011178 | 0.01136 | 0.011541 | 0.011722 | 0.011904 | 0.012085 | 0.012267 | 0.012448 | 0.01263 | 0.012811 | 0.012992 | 0.013174 | 44859.4312 | 52800.7519 | 54479.9762 | 55961.6447 | 56836.4743 | 57938.4227 | 59690.569 | 61528.0725 | 62482.3468 | 63496.3571 | 64510.3673 | 65524.3776 | 66538.3879 | 67552.3981 | 68566.4084 | 69580.4187 | 70594.4289 | 71608.4392 | 72622.4495 | 73636.4597 | 9993.5095 | 11762.6283 | 12136.7156 | 12466.7927 | 12661.6819 | 12907.1672 | 13297.4996 | 13706.8474 | 13919.4348 | 14145.3298 | 14371.2248 | 14597.1198 | 14823.0148 | 15048.9098 | 15274.8048 | 15500.6998 | 15726.5948 | 15952.4898 | 16178.3848 | 16404.2798 | 0.00039392 | 0.00040127 | 0.00040861 | 0.00041596 | 0.00042331 | 0.00043065 | 0.000438 | 0.00044535 | 0.0004527 | 0.00046004 | 0.00046739 | 0.00047474 | 0.00048208 | 0.00048943 | 0.00049678 | 0.00050412 | 0.00051147 | 0.00051882 | 0.00052616 | 0.00053351 | 54852.9411 | 64563.3807 | 66616.6922 | 68428.4378 | 69498.1566 | 70845.5903 | 72988.069 | 75234.9204 | 76401.782 | 77641.6873 | 78881.5926 | 80121.4979 | 81361.4031 | 82601.3084 | 83841.2137 | 85081.119 | 86321.0242 | 87560.9295 | 88800.8348 | 90040.74 | 1089205.5095 | 55268.9859 | -32036.1497 | 1057169.3598 | TRUE
| OYN005 | RCTS | 1 | FALSE | 1 | 2 | 0 | 53595.3633 | 11939.647 | 0.0096701 | 0.0098326 | 0.009995 | 0.010157 | 0.01032 | 0.010482 | 0.010645 | 0.010807 | 0.01097 | 0.011132 | 0.011295 | 0.011457 | 0.01162 | 0.011782 | 0.011944 | 0.012107 | 0.012269 | 0.012432 | 0.012594 | 0.012757 | 17229.5437 | 17572.4078 | 17917.0368 | 18263.4307 | 18443.4126 | 18619.8646 | 18966.2586 | 19373.1239 | 19485.5746 | 19774.1446 | 20062.7146 | 20351.2846 | 20639.8546 | 20928.4246 | 21216.9946 | 21505.5646 | 21794.1346 | 22082.7046 | 22371.2746 | 22659.8446 | 3838.2923 | 3914.6735 | 3991.4478 | 4068.6153 | 4108.7106 | 4148.0195 | 4225.187 | 4315.826 | 4340.8771 | 4405.1629 | 4469.4488 | 4533.7346 | 4598.0205 | 4662.3063 | 4726.5922 | 4790.8781 | 4855.1639 | 4919.4498 | 4983.7356 | 5048.0215 | 0.00039162 | 0.0003982 | 0.00040478 | 0.00041136 | 0.00041794 | 0.00042451 | 0.00043109 | 0.00043767 | 0.00044425 | 0.00045083 | 0.00045741 | 0.00046399 | 0.00047057 | 0.00047715 | 0.00048373 | 0.00049031 | 0.00049688 | 0.00050346 | 0.00051004 | 0.00051662 | 21067.8364 | 21487.0816 | 21908.485 | 22332.0465 | 22552.1236 | 22767.8845 | 23191.446 | 23688.9504 | 23826.4521 | 24179.308 | 24532.1639 | 24885.0197 | 25237.8756 | 25590.7314 | 25943.5873 | 26296.4432 | 26649.299 | 27002.1549 | 27355.0108 | 27707.8666 | 347318.4911 | 37732.0154 | -21871.0091 | 325447.482 | TRUE
| RCT011 | RCTS | 11 | FALSE | 11 | 3 | 12 | 53595.3633 | 11939.647 | 0.0096454 | 0.0097996 | 0.0099539 | 0.010108 | 0.010262 | 0.010417 | 0.010571 | 0.010725 | 0.010879 | 0.011033 | 0.011188 | 0.011342 | 0.011496 | 0.01165 | 0.011805 | 0.011959 | 0.012113 | 0.012267 | 0.012422 | 0.012576 | 20643.6366 | 21293.1202 | 22006.7277 | 22732.0643 | 23190.399 | 23765.2528 | 24576.4957 | 25459.4027 | 26002.806 | 26371.4308 | 26740.0557 | 27108.6805 | 27477.3053 | 27845.9302 | 28214.555 | 28583.1798 | 28951.8046 | 29320.4295 | 29689.0543 | 30057.6791 | 4598.863 | 4743.551 | 4902.5241 | 5064.1101 | 5166.2152 | 5294.2776 | 5475.0013 | 5671.6899 | 5792.746 | 5874.8659 | 5956.9859 | 6039.1059 | 6121.2259 | 6203.3459 | 6285.4659 | 6367.5859 | 6449.7058 | 6531.8258 | 6613.9458 | 6696.0658 | 0.0042968 | 0.0043655 | 0.0044342 | 0.0045029 | 0.0045716 | 0.0046403 | 0.004709 | 0.0047777 | 0.0048465 | 0.0049152 | 0.0049839 | 0.0050526 | 0.0051213 | 0.00519 | 0.0052587 | 0.0053274 | 0.0053961 | 0.0054648 | 0.0055335 | 0.0056022 | 25242.5039 | 26036.6755 | 26909.2563 | 27796.1789 | 28356.6188 | 29059.535 | 30051.5017 | 31131.0973 | 31795.5568 | 32246.3017 | 32697.0466 | 33147.7915 | 33598.5363 | 34049.2812 | 34500.0261 | 34950.771 | 35401.5159 | 35852.2608 | 36303.0056 | 36753.7505 | 449806.1897 | 388211.9385 | -225023.412 | 224782.7777 | TRUE
| RCT013 | RCTS | 15 | FALSE | 15 | 24 | 4 | 53595.3633 | 11939.647 | 0.0096603 | 0.0098195 | 0.0099787 | 0.010138 | 0.010297 | 0.010456 | 0.010616 | 0.010775 | 0.010934 | 0.011093 | 0.011252 | 0.011412 | 0.011571 | 0.01173 | 0.011889 | 0.012048 | 0.012207 | 0.012367 | 0.012526 | 0.012685 | 59087.9808 | 60168.4041 | 61740.1366 | 62945.4019 | 63654.1693 | 64581.4886 | 66314.3838 | 68303.8811 | 68897.3191 | 69900.4634 | 70903.6077 | 71906.752 | 72909.8962 | 73913.0405 | 74916.1848 | 75919.3291 | 76922.4734 | 77925.6176 | 78928.7619 | 79931.9062 | 13163.2587 | 13403.9488 | 13754.0898 | 14022.5914 | 14180.4862 | 14387.0687 | 14773.1125 | 15216.3206 | 15348.5231 | 15571.9974 | 15795.4717 | 16018.9461 | 16242.4204 | 16465.8948 | 16689.3691 | 16912.8435 | 17136.3178 | 17359.7921 | 17583.2665 | 17806.7408 | 0.0058683 | 0.0059651 | 0.0060618 | 0.0061585 | 0.0062552 | 0.0063519 | 0.0064486 | 0.0065453 | 0.006642 | 0.0067387 | 0.0068354 | 0.0069321 | 0.0070288 | 0.0071255 | 0.0072223 | 0.007319 | 0.0074157 | 0.0075124 | 0.0076091 | 0.0077058 | 72251.2453 | 73572.3589 | 75494.2324 | 76967.9994 | 77834.6618 | 78968.5636 | 81087.5027 | 83520.2082 | 84245.8488 | 85472.4675 | 86699.0863 | 87925.705 | 89152.3237 | 90378.9424 | 91605.5611 | 92832.1798 | 94058.7986 | 95285.4173 | 96512.036 | 97738.6547 | 1215377.9575 | 563322.1562 | -326524.4086 | 888853.549 | TRUE
| RCT014 | RCTS | 8 | FALSE | 8 | 9 | 3 | 53595.3633 | 11939.647 | 0.0096463 | 0.0098008 | 0.0099553 | 0.01011 | 0.010264 | 0.010419 | 0.010573 | 0.010728 | 0.010882 | 0.011037 | 0.011191 | 0.011346 | 0.0115 | 0.011655 | 0.01181 | 0.011964 | 0.012119 | 0.012273 | 0.012428 | 0.012582 | 51823.3077 | 52759.8993 | 53808.0051 | 54698.0724 | 55311.033 | 56087.0681 | 57263.4749 | 58449.954 | 59173.5894 | 60013.775 | 60853.9607 | 61694.1463 | 62534.3319 | 63374.5176 | 64214.7032 | 65054.8889 | 65895.0745 | 66735.2602 | 67575.4458 | 68415.6315 | 11544.8793 | 11753.5274 | 11987.018 | 12185.3018 | 12321.8534 | 12494.7337 | 12756.8065 | 13021.123 | 13182.3301 | 13369.5015 | 13556.6729 | 13743.8443 | 13931.0157 | 14118.1871 | 14305.3586 | 14492.53 | 14679.7014 | 14866.8728 | 15054.0442 | 15241.2156 | 0.0031252 | 0.0031753 | 0.0032254 | 0.0032754 | 0.0033255 | 0.0033755 | 0.0034256 | 0.0034757 | 0.0035257 | 0.0035758 | 0.0036258 | 0.0036759 | 0.003726 | 0.003776 | 0.0038261 | 0.0038761 | 0.0039262 | 0.0039763 | 0.0040263 | 0.0040764 | 63368.1902 | 64513.43 | 65795.0264 | 66883.3775 | 67632.8897 | 68581.8052 | 70020.2848 | 71471.0804 | 72355.9229 | 73383.2801 | 74410.6372 | 75437.9943 | 76465.3514 | 77492.7085 | 78520.0656 | 79547.4227 | 80574.7798 | 81602.137 | 82629.4941 | 83656.8512 | 1048367.6921 | 252697.548 | -146473.7655 | 901893.9266 | TRUE
| RCT015 | RCTS | 3 | FALSE | 3 | 3 | 3 | 53595.3633 | 11939.647 | 0.0096456 | 0.0097998 | 0.0099541 | 0.010108 | 0.010263 | 0.010417 | 0.010571 | 0.010725 | 0.01088 | 0.011034 | 0.011188 | 0.011343 | 0.011497 | 0.011651 | 0.011805 | 0.01196 | 0.012114 | 0.012268 | 0.012423 | 0.012577 | 17500.1904 | 17833.3289 | 18168.1435 | 18504.6342 | 18842.8009 | 19182.6437 | 19524.1626 | 19867.3576 | 20271.3287 | 20558.7758 | 20846.2228 | 21133.6699 | 21421.1169 | 21708.5639 | 21996.011 | 22283.458 | 22570.9051 | 22858.3521 | 23145.7991 | 23433.2462 | 3898.5853 | 3972.7999 | 4047.3878 | 4122.3491 | 4197.6839 | 4273.392 | 4349.4735 | 4425.9283 | 4515.9225 | 4579.9582 | 4643.9939 | 4708.0296 | 4772.0653 | 4836.101 | 4900.1367 | 4964.1724 | 5028.2081 | 5092.2438 | 5156.2795 | 5220.3152 | 0.0011719 | 0.0011906 | 0.0012094 | 0.0012281 | 0.0012468 | 0.0012656 | 0.0012843 | 0.0013031 | 0.0013218 | 0.0013406 | 0.0013593 | 0.0013781 | 0.0013968 | 0.0014155 | 0.0014343 | 0.001453 | 0.0014718 | 0.0014905 | 0.0015093 | 0.001528 | 21398.7769 | 21806.13 | 22215.5325 | 22626.9845 | 23040.486 | 23456.037 | 23873.6374 | 24293.2872 | 24787.2526 | 25138.7354 | 25490.2181 | 25841.7009 | 26193.1836 | 26544.6664 | 26896.1491 | 27247.6319 | 27599.1146 | 27950.5974 | 28302.0801 | 28653.5629 | 357611.1834 | 139501.5019 | -80860.7382 | 276750.4452 | TRUE
| SHL004 | SHL | 38 | FALSE | 38 | 30 | 31 | 44855.7307 | 11725.215 | 0.00973 | 0.0099124 | 0.010095 | 0.010277 | 0.01046 | 0.010642 | 0.010825 | 0.011007 | 0.011189 | 0.011372 | 0.011554 | 0.011737 | 0.011919 | 0.012102 | 0.012284 | 0.012466 | 0.012649 | 0.012831 | 0.013014 | 0.013196 | 35300.0873 | 35916.8526 | 36669.6425 | 37425.7498 | 37804.7493 | 38270.5616 | 39123.4339 | 40083.0235 | 40543.8596 | 41204.8606 | 41865.8616 | 42526.8626 | 43187.8636 | 43848.8646 | 44509.8656 | 45170.8666 | 45831.8676 | 46492.8686 | 47153.8696 | 47814.8706 | 9227.3854 | 9388.6069 | 9585.3849 | 9783.0301 | 9882.1 | 10003.8625 | 10226.802 | 10477.6371 | 10598.099 | 10770.8835 | 10943.6681 | 11116.4527 | 11289.2373 | 11462.0219 | 11634.8065 | 11807.591 | 11980.3756 | 12153.1602 | 12325.9448 | 12498.7294 | 0.014974 | 0.015254 | 0.015535 | 0.015816 | 0.016097 | 0.016377 | 0.016658 | 0.016939 | 0.01722 | 0.0175 | 0.017781 | 0.018062 | 0.018343 | 0.018623 | 0.018904 | 0.019185 | 0.019466 | 0.019746 | 0.020027 | 0.020308 | 44527.4877 | 45305.4747 | 46255.0429 | 47208.7957 | 47686.8654 | 48274.4405 | 49350.2525 | 50560.6776 | 51141.9758 | 51975.7616 | 52809.5475 | 53643.3334 | 54477.1192 | 55310.9051 | 56144.691 | 56978.4768 | 57812.2627 | 58646.0485 | 59479.8344 | 60313.6203 | 743922.4687 | 1422649.5122 | -824625.4571 | -80702.9884 | FALSE
| SHL005 | SHL | 3 | FALSE | 3 | 1 | 4 | 44855.7307 | 11725.215 | 0.0097111 | 0.0098872 | 0.010063 | 0.010239 | 0.010416 | 0.010592 | 0.010768 | 0.010944 | 0.01112 | 0.011296 | 0.011472 | 0.011648 | 0.011825 | 0.012001 | 0.012177 | 0.012353 | 0.012529 | 0.012705 | 0.012881 | 0.013057 | 17571.5751 | 17890.25 | 18208.9249 | 18527.5998 | 18656.8649 | 18876.0307 | 19287.8091 | 19752.5448 | 19969.3085 | 20285.5813 | 20601.8541 | 20918.1269 | 21234.3997 | 21550.6725 | 21866.9453 | 22183.2181 | 22499.4909 | 22815.7638 | 23132.0366 | 23448.3094 | 4593.1812 | 4676.4823 | 4759.7833 | 4843.0844 | 4876.8741 | 4934.1637 | 5041.8019 | 5163.2831 | 5219.9448 | 5302.618 | 5385.2912 | 5467.9644 | 5550.6375 | 5633.3107 | 5715.9839 | 5798.6571 | 5881.3303 | 5964.0035 | 6046.6767 | 6129.3499 | 0.0011798 | 0.0012012 | 0.0012226 | 0.001244 | 0.0012654 | 0.0012868 | 0.0013082 | 0.0013296 | 0.001351 | 0.0013724 | 0.0013938 | 0.0014152 | 0.0014366 | 0.001458 | 0.0014794 | 0.0015008 | 0.0015222 | 0.0015436 | 0.001565 | 0.0015864 | 22164.7575 | 22566.7335 | 22968.7095 | 23370.6855 | 23533.7402 | 23810.1957 | 24329.6123 | 24915.8292 | 25189.2546 | 25588.2007 | 25987.1467 | 26386.0927 | 26785.0387 | 27183.9847 | 27582.9308 | 27981.8768 | 28380.8228 | 28779.7688 | 29178.7148 | 29577.6609 | 366803.4176 | 129403.9795 | -75007.804 | 291795.6136 | TRUE
| SHN011 | SHN | 8 | FALSE | 8 | 6 | 9 | 47127.1698 | 12114.7415 | 0.0096884 | 0.009857 | 0.010026 | 0.010194 | 0.010363 | 0.010531 | 0.0107 | 0.010868 | 0.011037 | 0.011206 | 0.011374 | 0.011543 | 0.011711 | 0.01188 | 0.012048 | 0.012217 | 0.012385 | 0.012554 | 0.012723 | 0.012891 | 36327.5467 | 37383.3345 | 38645.1649 | 39781.8515 | 40489.1615 | 41449.5964 | 42930.7737 | 44593.4557 | 45443.2396 | 46137.2839 | 46831.3281 | 47525.3724 | 48219.4166 | 48913.4609 | 49607.5051 | 50301.5494 | 50995.5936 | 51689.6379 | 52383.6821 | 53077.7264 | 9338.5374 | 9609.9434 | 9934.3157 | 10226.5179 | 10408.3425 | 10655.2366 | 11035.9953 | 11463.4125 | 11681.8621 | 11860.2765 | 12038.691 | 12217.1054 | 12395.5198 | 12573.9342 | 12752.3486 | 12930.7631 | 13109.1775 | 13287.5919 | 13466.0063 | 13644.4207 | 0.0031389 | 0.0031935 | 0.0032481 | 0.0033027 | 0.0033573 | 0.003412 | 0.0034666 | 0.0035212 | 0.0035758 | 0.0036304 | 0.003685 | 0.0037396 | 0.0037942 | 0.0038488 | 0.0039035 | 0.0039581 | 0.0040127 | 0.0040673 | 0.0041219 | 0.0041765 | 45666.0872 | 46993.2811 | 48579.4838 | 50008.3728 | 50897.5074 | 52104.8364 | 53966.7725 | 56056.8718 | 57125.1053 | 57997.5641 | 58870.0228 | 59742.4815 | 60614.9402 | 61487.399 | 62359.8577 | 63232.3164 | 64104.7751 | 64977.2339 | 65849.6926 | 66722.1513 | 811256.0999 | 361906.4827 | -209775.701 | 601480.3989 | TRUE
| SHN021 | SHN | 10 | FALSE | 10 | 7 | 10 | 47127.1698 | 12114.7415 | 0.0096948 | 0.0098655 | 0.010036 | 0.010207 | 0.010378 | 0.010548 | 0.010719 | 0.01089 | 0.01106 | 0.011231 | 0.011402 | 0.011573 | 0.011743 | 0.011914 | 0.012085 | 0.012255 | 0.012426 | 0.012597 | 0.012768 | 0.012938 | 32785.9008 | 33834.4135 | 35043.0491 | 36175.3766 | 37077.7959 | 38090.7689 | 39475.1877 | 40988.0983 | 42106.0856 | 42755.9348 | 43405.784 | 44055.6331 | 44705.4823 | 45355.3314 | 46005.1806 | 46655.0298 | 47304.8789 | 47954.7281 | 48604.5772 | 49254.4264 | 8428.1045 | 8697.6403 | 9008.3381 | 9299.4198 | 9531.4001 | 9791.7999 | 10147.6854 | 10536.6016 | 10823.9969 | 10991.0504 | 11158.1038 | 11325.1572 | 11492.2106 | 11659.264 | 11826.3174 | 11993.3708 | 12160.4243 | 12327.4777 | 12494.5311 | 12661.5845 | 0.0039262 | 0.0039953 | 0.0040645 | 0.0041336 | 0.0042027 | 0.0042719 | 0.004341 | 0.0044101 | 0.0044793 | 0.0045484 | 0.0046175 | 0.0046867 | 0.0047558 | 0.0048249 | 0.004894 | 0.0049632 | 0.0050323 | 0.0051014 | 0.0051706 | 0.0052397 | 41214.0093 | 42532.0579 | 44051.3913 | 45474.8005 | 46609.2003 | 47882.5731 | 49622.8775 | 51524.7043 | 52930.087 | 53746.9897 | 54563.8923 | 55380.795 | 56197.6976 | 57014.6003 | 57831.5029 | 58648.4056 | 59465.3082 | 60282.2109 | 61099.1135 | 61916.0161 | 746895.4833 | 408406.9834 | -236729.2804 | 510166.2029 | TRUE
| SHN024 | SHN | 3 | FALSE | 3 | 2 | 4 | 47127.1698 | 12114.7415 | 0.0096659 | 0.009827 | 0.0099881 | 0.010149 | 0.01031 | 0.010471 | 0.010632 | 0.010793 | 0.010954 | 0.011116 | 0.011277 | 0.011438 | 0.011599 | 0.01176 | 0.011921 | 0.012082 | 0.012243 | 0.012404 | 0.012565 | 0.012726 | 35365.966 | 36518.5449 | 38023.5463 | 39266.9163 | 40136.313 | 41113.4358 | 42710.7574 | 44543.5338 | 45312.8882 | 45979.1327 | 46645.3771 | 47311.6215 | 47977.8659 | 48644.1104 | 49310.3548 | 49976.5992 | 50642.8437 | 51309.0881 | 51975.3325 | 52641.5769 | 9091.3487 | 9387.6363 | 9774.5193 | 10094.1462 | 10317.6375 | 10568.8215 | 10979.4368 | 11450.5793 | 11648.3534 | 11819.6214 | 11990.8895 | 12162.1575 | 12333.4256 | 12504.6937 | 12675.9617 | 12847.2298 | 13018.4978 | 13189.7659 | 13361.034 | 13532.302 | 0.0011744 | 0.0011939 | 0.0012135 | 0.0012331 | 0.0012526 | 0.0012722 | 0.0012918 | 0.0013113 | 0.0013309 | 0.0013505 | 0.00137 | 0.0013896 | 0.0014092 | 0.0014287 | 0.0014483 | 0.0014679 | 0.0014874 | 0.001507 | 0.0015266 | 0.0015462 | 44457.3159 | 45906.1824 | 47798.0668 | 49361.0637 | 50453.9518 | 51682.2585 | 53690.1955 | 55994.1144 | 56961.2429 | 57798.7554 | 58636.2679 | 59473.7804 | 60311.293 | 61148.8055 | 61986.318 | 62823.8305 | 63661.343 | 64498.8555 | 65336.368 | 66173.8805 | 804193.6421 | 148269.9872 | -85943.3085 | 718250.3336 | TRUE
| SHP011 | SHP | 2 | FALSE | 2 | 0 | 4 | 50191.6347 | 11451.8596 | 0.009711 | 0.0098871 | 0.010063 | 0.010239 | 0.010415 | 0.010592 | 0.010768 | 0.010944 | 0.01112 | 0.011296 | 0.011472 | 0.011648 | 0.011824 | 0.012 | 0.012176 | 0.012352 | 0.012529 | 0.012705 | 0.012881 | 0.013057 | 46931.1987 | 47379.8559 | 48121.3374 | 49015.5019 | 49593.5506 | 50054.8803 | 50777.5495 | 51719.3235 | 52438.4094 | 53268.8394 | 54099.2693 | 54929.6993 | 55760.1293 | 56590.5593 | 57420.9892 | 58251.4192 | 59081.8492 | 59912.2791 | 60742.7091 | 61573.1391 | 10707.9496 | 10810.3165 | 10979.4949 | 11183.5099 | 11315.3991 | 11420.6573 | 11585.5435 | 11800.4212 | 11964.4898 | 12153.963 | 12343.4361 | 12532.9093 | 12722.3824 | 12911.8556 | 13101.3287 | 13290.8019 | 13480.275 | 13669.7482 | 13859.2214 | 14048.6945 | 0.00078655 | 0.00080082 | 0.00081508 | 0.00082934 | 0.0008436 | 0.00085787 | 0.00087213 | 0.00088639 | 0.00090066 | 0.00091492 | 0.00092918 | 0.00094345 | 0.00095771 | 0.00097197 | 0.00098624 | 0.0010005 | 0.0010148 | 0.001029 | 0.0010433 | 0.0010576 | 57639.1491 | 58190.1732 | 59100.8332 | 60199.0126 | 60908.9505 | 61475.5384 | 62363.0938 | 63519.7456 | 64402.9001 | 65422.8032 | 66442.7064 | 67462.6095 | 68482.5127 | 69502.4158 | 70522.3189 | 71542.2221 | 72562.1252 | 73582.0284 | 74601.9315 | 75621.8346 | 941096.9039 | 110537.9718 | -64072.2994 | 877024.6044 | TRUE
| SHP012 | SHP | 1 | FALSE | 1 | 1 | 1 | 50191.6347 | 11451.8596 | 0.0097397 | 0.0099253 | 0.010111 | 0.010297 | 0.010482 | 0.010668 | 0.010854 | 0.011039 | 0.011225 | 0.011411 | 0.011596 | 0.011782 | 0.011968 | 0.012153 | 0.012339 | 0.012524 | 0.01271 | 0.012896 | 0.013081 | 0.013267 | 36268.4753 | 37363.7355 | 38885.5945 | 40228.1539 | 40953.4816 | 42004.4249 | 43508.4113 | 45319.6327 | 46253.1013 | 47018.0953 | 47783.0894 | 48548.0834 | 49313.0775 | 50078.0715 | 50843.0655 | 51608.0596 | 52373.0536 | 53138.0477 | 53903.0417 | 54668.0358 | 8275.1137 | 8525.0113 | 8872.2428 | 9178.5648 | 9344.0575 | 9583.8436 | 9926.9972 | 10340.2504 | 10553.2331 | 10727.7762 | 10902.3193 | 11076.8625 | 11251.4056 | 11425.9487 | 11600.4918 | 11775.0349 | 11949.578 | 12124.1212 | 12298.6643 | 12473.2074 | 0.00039444 | 0.00040196 | 0.00040947 | 0.00041699 | 0.00042451 | 0.00043203 | 0.00043955 | 0.00044707 | 0.00045459 | 0.0004621 | 0.00046962 | 0.00047714 | 0.00048466 | 0.00049218 | 0.0004997 | 0.00050722 | 0.00051473 | 0.00052225 | 0.00052977 | 0.00053729 | 44543.5894 | 45888.7472 | 47757.8377 | 49406.719 | 50297.5395 | 51588.269 | 53435.409 | 55659.8836 | 56806.3348 | 57745.872 | 58685.4092 | 59624.9463 | 60564.4835 | 61504.0207 | 62443.5579 | 63383.095 | 64322.6322 | 65262.1694 | 66201.7065 | 67141.2437 | 806313.1581 | 46500.5006 | -26953.5794 | 779359.5787 | TRUE
| SHP014 | SHP | 21 | FALSE | 21 | 16 | 22 | 50191.6347 | 11451.8596 | 0.009704 | 0.0098778 | 0.010052 | 0.010225 | 0.010399 | 0.010573 | 0.010747 | 0.01092 | 0.011094 | 0.011268 | 0.011442 | 0.011615 | 0.011789 | 0.011963 | 0.012137 | 0.01231 | 0.012484 | 0.012658 | 0.012832 | 0.013006 | 27496.6726 | 28139.7861 | 28941.604 | 29597.9768 | 29995.1459 | 30550.1355 | 31325.5707 | 32165.3988 | 32620.7731 | 33131.7008 | 33642.6285 | 34153.5562 | 34664.4839 | 35175.4116 | 35686.3393 | 36197.267 | 36708.1947 | 37219.1224 | 37730.0501 | 38240.9778 | 6273.7154 | 6420.45 | 6603.3949 | 6753.1547 | 6843.7739 | 6970.4018 | 7147.3272 | 7338.9447 | 7442.8441 | 7559.4188 | 7675.9934 | 7792.5681 | 7909.1427 | 8025.7174 | 8142.292 | 8258.8667 | 8375.4413 | 8492.016 | 8608.5906 | 8725.1653 | 0.0082528 | 0.0084006 | 0.0085484 | 0.0086962 | 0.008844 | 0.0089917 | 0.0091395 | 0.0092873 | 0.0094351 | 0.0095829 | 0.0097306 | 0.0098784 | 0.010026 | 0.010174 | 0.010322 | 0.01047 | 0.010617 | 0.010765 | 0.010913 | 0.011061 | 33770.3963 | 34560.2444 | 35545.0074 | 36351.1402 | 36838.9286 | 37520.5463 | 38472.907 | 39504.3527 | 40063.6267 | 40691.1292 | 41318.6317 | 41946.1342 | 42573.6367 | 43201.1392 | 43828.6417 | 44456.1442 | 45083.6467 | 45711.1492 | 46338.6517 | 46966.1542 | 577709.426 | 909814.968 | -527365.7197 | 50343.7063 | TRUE
| SHTSKYM1 | KYM | 3 | TRUE | 0 | 0 | 0 | 47800.3495 | 11425.2342 | 0.0096965 | 0.0098678 | 0.010039 | 0.01021 | 0.010382 | 0.010553 | 0.010724 | 0.010895 | 0.011067 | 0.011238 | 0.011409 | 0.01158 | 0.011752 | 0.011923 | 0.012094 | 0.012265 | 0.012437 | 0.012608 | 0.012779 | 0.01295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011781 | 0.0011989 | 0.0012197 | 0.0012405 | 0.0012613 | 0.0012821 | 0.0013029 | 0.0013237 | 0.0013445 | 0.0013653 | 0.0013861 | 0.0014069 | 0.0014277 | 0.0014485 | 0.0014694 | 0.0014902 | 0.001511 | 0.0015318 | 0.0015526 | 0.0015734 | 0.0011781 | 0.0011989 | 0.0012197 | 0.0012405 | 0.0012613 | 0.0012821 | 0.0013029 | 0.0013237 | 0.0013445 | 0.0013653 | 0.0013861 | 0.0014069 | 0.0014277 | 0.0014485 | 0.0014694 | 0.0014902 | 0.001511 | 0.0015318 | 0.0015526 | 0.0015734 | 0.01955 | 0 | 0 | 0.01955 | TRUE
| SHTSMNA | KYM | 2 | TRUE | 0 | 0 | 0 | 47800.3495 | 11425.2342 | 0.0096965 | 0.0098678 | 0.010039 | 0.01021 | 0.010382 | 0.010553 | 0.010724 | 0.010895 | 0.011067 | 0.011238 | 0.011409 | 0.01158 | 0.011752 | 0.011923 | 0.012094 | 0.012265 | 0.012437 | 0.012608 | 0.012779 | 0.01295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00078538 | 0.00079925 | 0.00081312 | 0.00082699 | 0.00084086 | 0.00085473 | 0.0008686 | 0.00088247 | 0.00089634 | 0.00091021 | 0.00092409 | 0.00093796 | 0.00095183 | 0.0009657 | 0.00097957 | 0.00099344 | 0.0010073 | 0.0010212 | 0.0010351 | 0.0010489 | 0.00078538 | 0.00079925 | 0.00081312 | 0.00082699 | 0.00084086 | 0.00085473 | 0.0008686 | 0.00088247 | 0.00089634 | 0.00091021 | 0.00092409 | 0.00093796 | 0.00095183 | 0.0009657 | 0.00097957 | 0.00099344 | 0.0010073 | 0.0010212 | 0.0010351 | 0.0010489 | 0.013033 | 0 | 0 | 0.013033 | TRUE
| SHTSNKA | KYM | 5 | TRUE | 0 | 0 | 0 | 47800.3495 | 11425.2342 | 0.0096927 | 0.0098626 | 0.010033 | 0.010203 | 0.010373 | 0.010543 | 0.010713 | 0.010883 | 0.011052 | 0.011222 | 0.011392 | 0.011562 | 0.011732 | 0.011902 | 0.012072 | 0.012242 | 0.012412 | 0.012582 | 0.012752 | 0.012922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019627 | 0.0019971 | 0.0020315 | 0.0020659 | 0.0021003 | 0.0021348 | 0.0021692 | 0.0022036 | 0.002238 | 0.0022724 | 0.0023068 | 0.0023413 | 0.0023757 | 0.0024101 | 0.0024445 | 0.0024789 | 0.0025134 | 0.0025478 | 0.0025822 | 0.0026166 | 0.0019627 | 0.0019971 | 0.0020315 | 0.0020659 | 0.0021003 | 0.0021348 | 0.0021692 | 0.0022036 | 0.002238 | 0.0022724 | 0.0023068 | 0.0023413 | 0.0023757 | 0.0024101 | 0.0024445 | 0.0024789 | 0.0025134 | 0.0025478 | 0.0025822 | 0.0026166 | 0.032541 | 0 | 0 | 0.032541 | TRUE
| SHTSSHP | KYM | 2 | TRUE | 0 | 0 | 0 | 47800.3495 | 11425.2342 | 0.0096942 | 0.0098647 | 0.010035 | 0.010206 | 0.010376 | 0.010547 | 0.010717 | 0.010888 | 0.011058 | 0.011229 | 0.011399 | 0.01157 | 0.01174 | 0.011911 | 0.012081 | 0.012252 | 0.012422 | 0.012593 | 0.012763 | 0.012934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00078519 | 0.000799 | 0.00081281 | 0.00082662 | 0.00084043 | 0.00085424 | 0.00086805 | 0.00088186 | 0.00089567 | 0.00090948 | 0.00092329 | 0.0009371 | 0.00095091 | 0.00096472 | 0.00097853 | 0.00099233 | 0.0010061 | 0.00102 | 0.0010338 | 0.0010476 | 0.00078519 | 0.000799 | 0.00081281 | 0.00082662 | 0.00084043 | 0.00085424 | 0.00086805 | 0.00088186 | 0.00089567 | 0.00090948 | 0.00092329 | 0.0009371 | 0.00095091 | 0.00096472 | 0.00097853 | 0.00099233 | 0.0010061 | 0.00102 | 0.0010338 | 0.0010476 | 0.013023 | 0 | 0 | 0.013023 | TRUE
| STL005 | STL | 3 | FALSE | 3 | 6 | 0 | 47316.7282 | 10850.5896 | 0.0096793 | 0.0098448 | 0.01001 | 0.010176 | 0.010341 | 0.010507 | 0.010672 | 0.010838 | 0.011003 | 0.011169 | 0.011334 | 0.0115 | 0.011665 | 0.011831 | 0.011996 | 0.012162 | 0.012327 | 0.012493 | 0.012658 | 0.012824 | 40709.7103 | 41264.1742 | 42005.9027 | 42651.6177 | 43047.7742 | 43434.4059 | 44016.2395 | 44750.8244 | 45117.6129 | 45796.2537 | 46474.8946 | 47153.5354 | 47832.1763 | 48510.8171 | 49189.458 | 49868.0988 | 50546.7397 | 51225.3805 | 51904.0214 | 52582.6622 | 9335.4798 | 9462.6285 | 9632.7204 | 9780.7946 | 9871.6405 | 9960.3023 | 10093.7273 | 10262.1811 | 10346.2923 | 10501.9171 | 10657.5418 | 10813.1666 | 10968.7913 | 11124.416 | 11280.0408 | 11435.6655 | 11591.2902 | 11746.915 | 11902.5397 | 12058.1645 | 0.001176 | 0.0011961 | 0.0012162 | 0.0012363 | 0.0012564 | 0.0012765 | 0.0012966 | 0.0013167 | 0.0013368 | 0.0013569 | 0.0013771 | 0.0013972 | 0.0014173 | 0.0014374 | 0.0014575 | 0.0014776 | 0.0014977 | 0.0015178 | 0.0015379 | 0.001558 | 50045.1912 | 50726.8039 | 51638.6243 | 52432.4135 | 52919.416 | 53394.7094 | 54109.9682 | 55013.0068 | 55463.9065 | 56298.1722 | 57132.4378 | 57966.7034 | 58800.969 | 59635.2346 | 60469.5002 | 61303.7658 | 62138.0314 | 62972.297 | 63806.5626 | 64640.8283 | 812316.0132 | 113196.0461 | -65613.0273 | 746702.9859 | TRUE
| STL006 | STL | 20 | FALSE | 20 | 20 | 8 | 47316.7282 | 10850.5896 | 0.0096921 | 0.0098619 | 0.010032 | 0.010202 | 0.010371 | 0.010541 | 0.010711 | 0.010881 | 0.011051 | 0.01122 | 0.01139 | 0.01156 | 0.01173 | 0.0119 | 0.012069 | 0.012239 | 0.012409 | 0.012579 | 0.012749 | 0.012918 | 15524.6746 | 15607.4777 | 15924.3147 | 16193.8564 | 16363.9213 | 16480.1762 | 16848.3803 | 17167.6603 | 17329.582 | 17595.8663 | 17862.1507 | 18128.435 | 18394.7194 | 18661.0037 | 18927.2881 | 19193.5724 | 19459.8568 | 19726.1411 | 19992.4255 | 20258.7099 | 3560.0913 | 3579.0796 | 3651.7361 | 3713.5469 | 3752.5459 | 3779.2053 | 3863.6412 | 3936.8579 | 3973.9895 | 4035.0534 | 4096.1173 | 4157.1811 | 4218.245 | 4279.3089 | 4340.3727 | 4401.4366 | 4462.5004 | 4523.5643 | 4584.6282 | 4645.692 | 0.0078502 | 0.0079878 | 0.0081253 | 0.0082628 | 0.0084004 | 0.0085379 | 0.0086754 | 0.008813 | 0.0089505 | 0.009088 | 0.0092255 | 0.0093631 | 0.0095006 | 0.0096381 | 0.0097757 | 0.0099132 | 0.010051 | 0.010188 | 0.010326 | 0.010463 | 19084.7738 | 19186.5652 | 19576.0589 | 19907.4115 | 20116.4756 | 20259.3901 | 20712.0302 | 21104.5271 | 21303.5805 | 21630.9288 | 21958.2772 | 22285.6255 | 22612.9739 | 22940.3222 | 23267.6706 | 23595.0189 | 23922.3673 | 24249.7156 | 24577.064 | 24904.4123 | 310948.2274 | 598396.0973 | -346854.6898 | -35906.4624 | FALSE
| STL007 | STL | 11 | FALSE | 11 | 15 | 6 | 47316.7282 | 10850.5896 | 0.0096944 | 0.0098649 | 0.010035 | 0.010206 | 0.010377 | 0.010547 | 0.010718 | 0.010888 | 0.011059 | 0.011229 | 0.0114 | 0.01157 | 0.011741 | 0.011911 | 0.012082 | 0.012253 | 0.012423 | 0.012594 | 0.012764 | 0.012935 | 30498.5741 | 30420.0791 | 30560.9566 | 30737.6934 | 30853.2166 | 30803.9104 | 31507.5959 | 31695.6556 | 32245.1441 | 32742.4157 | 33239.6873 | 33736.959 | 34234.2306 | 34731.5022 | 35228.7738 | 35726.0454 | 36223.3171 | 36720.5887 | 37217.8603 | 37715.1319 | 6993.8799 | 6975.8795 | 7008.1853 | 7048.7143 | 7075.2059 | 7063.899 | 7225.267 | 7268.3925 | 7394.4002 | 7508.4337 | 7622.4672 | 7736.5006 | 7850.5341 | 7964.5675 | 8078.601 | 8192.6345 | 8306.6679 | 8420.7014 | 8534.7349 | 8648.7683 | 0.0043186 | 0.0043946 | 0.0044706 | 0.0045465 | 0.0046225 | 0.0046985 | 0.0047745 | 0.0048504 | 0.0049264 | 0.0050024 | 0.0050783 | 0.0051543 | 0.0052303 | 0.0053063 | 0.0053822 | 0.0054582 | 0.0055342 | 0.0056102 | 0.0056861 | 0.0057621 | 37492.4583 | 37395.963 | 37569.1464 | 37786.4122 | 37928.4271 | 37867.8141 | 38732.8677 | 38964.0529 | 39639.5493 | 40250.8544 | 40862.1596 | 41473.4647 | 42084.7699 | 42696.075 | 43307.3802 | 43918.6854 | 44529.9905 | 45141.2957 | 45752.6008 | 46363.906 | 584420.2719 | 448797.073 | -260141.0174 | 324279.2545 | TRUE
| STN011 | STN | 19 | FALSE | 19 | 23 | 8 | 50364.8111 | 12003.9056 | 0.0096757 | 0.0098401 | 0.010004 | 0.010169 | 0.010333 | 0.010497 | 0.010662 | 0.010826 | 0.01099 | 0.011155 | 0.011319 | 0.011483 | 0.011648 | 0.011812 | 0.011976 | 0.012141 | 0.012305 | 0.012469 | 0.012634 | 0.012798 | 36006.4607 | 36768.6896 | 37740.2291 | 38567.7882 | 39243.817 | 39975.1095 | 41036.3064 | 42276.7163 | 42918.4533 | 43560.1902 | 44201.9272 | 44843.6642 | 45485.4012 | 46127.1381 | 46768.8751 | 47410.6121 | 48052.349 | 48694.086 | 49335.823 | 49977.56 | 8581.7488 | 8763.4178 | 8994.9736 | 9192.2133 | 9353.3375 | 9527.6331 | 9780.5579 | 10076.1961 | 10229.1471 | 10382.0981 | 10535.0492 | 10688.0002 | 10840.9513 | 10993.9023 | 11146.8533 | 11299.8044 | 11452.7554 | 11605.7064 | 11758.6575 | 11911.6085 | 0.0074451 | 0.0075715 | 0.007698 | 0.0078244 | 0.0079509 | 0.0080773 | 0.0082038 | 0.0083302 | 0.0084567 | 0.0085831 | 0.0087096 | 0.008836 | 0.0089625 | 0.0090889 | 0.0092154 | 0.0093418 | 0.0094683 | 0.0095947 | 0.0097212 | 0.0098476 | 44588.2169 | 45532.1149 | 46735.2104 | 47760.0093 | 48597.1624 | 49502.7507 | 50816.8725 | 52352.9207 | 53147.6088 | 53942.297 | 54736.9851 | 55531.6732 | 56326.3614 | 57121.0495 | 57915.7376 | 58710.4258 | 59505.1139 | 60299.802 | 61094.4902 | 61889.1783 | 762967.8987 | 654994.1203 | -379661.2035 | 383306.6953 | TRUE
| STN012 | STN | 3 | FALSE | 3 | 0 | 5 | 50364.8111 | 12003.9056 | 0.0096544 | 0.0098116 | 0.0099688 | 0.010126 | 0.010283 | 0.010441 | 0.010598 | 0.010755 | 0.010912 | 0.011069 | 0.011227 | 0.011384 | 0.011541 | 0.011698 | 0.011855 | 0.012013 | 0.01217 | 0.012327 | 0.012484 | 0.012642 | 51894.632 | 53741.435 | 55823.8916 | 57841.4905 | 59579.4448 | 61449.672 | 63943.8699 | 66484.6163 | 68347.7704 | 69332.515 | 70317.2597 | 71302.0043 | 72286.7489 | 73271.4936 | 74256.2382 | 75240.9828 | 76225.7275 | 77210.4721 | 78195.2167 | 79179.9614 | 12368.5218 | 12808.6872 | 13305.0181 | 13785.8909 | 14200.1135 | 14645.8618 | 15240.3268 | 15845.8861 | 16289.9486 | 16524.6518 | 16759.355 | 16994.0582 | 17228.7614 | 17463.4645 | 17698.1677 | 17932.8709 | 18167.5741 | 18402.2773 | 18636.9805 | 18871.6837 | 0.0011729 | 0.0011921 | 0.0012112 | 0.0012303 | 0.0012494 | 0.0012685 | 0.0012876 | 0.0013067 | 0.0013258 | 0.0013449 | 0.001364 | 0.0013831 | 0.0014022 | 0.0014213 | 0.0014404 | 0.0014595 | 0.0014786 | 0.0014977 | 0.0015168 | 0.0015359 | 64263.155 | 66550.1234 | 69128.9109 | 71627.3827 | 73779.5595 | 76095.5351 | 79184.1979 | 82330.5037 | 84637.7203 | 85857.1682 | 87076.616 | 88296.0639 | 89515.5117 | 90734.9595 | 91954.4074 | 93173.8552 | 94393.3031 | 95612.7509 | 96832.1987 | 98051.6466 | 1184642.1723 | 138172.4648 | -80090.3743 | 1104551.7979 | TRUE
| STN021 | STN | 5 | FALSE | 5 | 3 | 6 | 50364.8111 | 12003.9056 | 0.0096738 | 0.0098375 | 0.010001 | 0.010165 | 0.010329 | 0.010492 | 0.010656 | 0.01082 | 0.010983 | 0.011147 | 0.011311 | 0.011474 | 0.011638 | 0.011802 | 0.011965 | 0.012129 | 0.012293 | 0.012457 | 0.01262 | 0.012784 | 30122.8507 | 31034.2969 | 32112.2712 | 33052.963 | 33954.3001 | 34920.895 | 36064.0451 | 37336.0397 | 38237.2947 | 38807.1647 | 39377.0347 | 39946.9047 | 40516.7747 | 41086.6447 | 41656.5147 | 42226.3847 | 42796.2547 | 43366.1247 | 43935.9947 | 44505.8647 | 7179.4542 | 7396.6875 | 7653.611 | 7877.8147 | 8092.6386 | 8323.016 | 8595.4734 | 8898.6395 | 9113.4438 | 9249.2661 | 9385.0885 | 9520.9108 | 9656.7331 | 9792.5554 | 9928.3778 | 10064.2001 | 10200.0224 | 10335.8447 | 10471.6671 | 10607.4894 | 0.0019588 | 0.001992 | 0.0020251 | 0.0020583 | 0.0020914 | 0.0021246 | 0.0021577 | 0.0021909 | 0.002224 | 0.0022572 | 0.0022903 | 0.0023234 | 0.0023566 | 0.0023897 | 0.0024229 | 0.002456 | 0.0024892 | 0.0025223 | 0.0025555 | 0.0025886 | 37302.3069 | 38430.9864 | 39765.8843 | 40930.7797 | 42046.9408 | 43243.9131 | 44659.5206 | 46234.6814 | 47350.7407 | 48056.4331 | 48762.1255 | 49467.8178 | 50173.5102 | 50879.2025 | 51584.8949 | 52290.5872 | 52996.2796 | 53701.972 | 54407.6643 | 55113.3567 | 669510.7932 | 222404.9808 | -128914.9628 | 540595.8304 | TRUE
| STN024 | STN | 21 | FALSE | 21 | 12 | 25 | 50364.8111 | 12003.9056 | 0.0096768 | 0.0098415 | 0.010006 | 0.010171 | 0.010336 | 0.0105 | 0.010665 | 0.01083 | 0.010994 | 0.011159 | 0.011324 | 0.011488 | 0.011653 | 0.011818 | 0.011982 | 0.012147 | 0.012312 | 0.012476 | 0.012641 | 0.012806 | 59523.3903 | 61139.2625 | 63490.4082 | 65469.9169 | 66741.0539 | 68233.318 | 70882.2958 | 73911.7237 | 75091.836 | 76216.6665 | 77341.497 | 78466.3275 | 79591.1581 | 80715.9886 | 81840.8191 | 82965.6496 | 84090.4801 | 85215.3106 | 86340.1412 | 87464.9717 | 14186.7535 | 14571.8791 | 15132.2491 | 15604.0435 | 15907.0052 | 16262.6701 | 16894.0252 | 17616.0564 | 17897.3234 | 18165.4145 | 18433.5057 | 18701.5968 | 18969.6879 | 19237.7791 | 19505.8702 | 19773.9613 | 20042.0525 | 20310.1436 | 20578.2347 | 20846.3259 | 0.0082297 | 0.0083698 | 0.0085098 | 0.0086499 | 0.0087899 | 0.00893 | 0.0090701 | 0.0092101 | 0.0093502 | 0.0094902 | 0.0096303 | 0.0097704 | 0.0099104 | 0.01005 | 0.010191 | 0.010331 | 0.010471 | 0.010611 | 0.010751 | 0.010891 | 73710.152 | 75711.1499 | 78622.6658 | 81073.969 | 82648.0679 | 84495.9971 | 87776.3301 | 91527.7894 | 92989.1687 | 94382.0905 | 95775.0123 | 97167.9341 | 98560.8559 | 99953.7777 | 101346.6995 | 102739.6213 | 104132.5431 | 105525.4649 | 106918.3866 | 108311.3084 | 1317183.5384 | 917254.4161 | -531677.9261 | 785505.6123 | TRUE
| TNA022 | TNA | 4 | FALSE | 4 | 6 | 2 | 49768.8721 | 11659.7375 | 0.0095937 | 0.0097307 | 0.0098676 | 0.010005 | 0.010142 | 0.010279 | 0.010416 | 0.010553 | 0.01069 | 0.010827 | 0.010964 | 0.0111 | 0.011237 | 0.011374 | 0.011511 | 0.011648 | 0.011785 | 0.011922 | 0.012059 | 0.012196 | 73315.7744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17176.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015541 | 0.0015763 | 0.0015985 | 0.0016207 | 0.0016429 | 0.001665 | 0.0016872 | 0.0017094 | 0.0017316 | 0.0017538 | 0.001776 | 0.0017982 | 0.0018204 | 0.0018426 | 0.0018648 | 0.0018869 | 0.0019091 | 0.0019313 | 0.0019535 | 0.0019757 | 90492.0279 | 0.0015763 | 0.0015985 | 0.0016207 | 0.0016429 | 0.001665 | 0.0016872 | 0.0017094 | 0.0017316 | 0.0017538 | 0.001776 | 0.0017982 | 0.0018204 | 0.0018426 | 0.0018648 | 0.0018869 | 0.0019091 | 0.0019313 | 0.0019535 | 0.0019757 | 88948.8344 | 168465.032 | -97649.177 | -8700.3426 | FALSE
| WBE023 | WBE | 2 | FALSE | 2 | 4 | 0 | 39317.7095 | 10727.8793 | 0.009594 | 0.009731 | 0.0098681 | 0.010005 | 0.010142 | 0.010279 | 0.010416 | 0.010553 | 0.010691 | 0.010828 | 0.010965 | 0.011102 | 0.011239 | 0.011376 | 0.011513 | 0.01165 | 0.011787 | 0.011924 | 0.012061 | 0.012198 | 53180.7747 | 55103.9405 | 57335.1523 | 59487.1734 | 61595.5047 | 64230.3541 | 67037.8009 | 70148.9284 | 72636.3259 | 73567.662 | 74498.9982 | 75430.3343 | 76361.6704 | 77293.0066 | 78224.3427 | 79155.6788 | 80087.015 | 81018.3511 | 81949.6872 | 82881.0234 | 14510.4315 | 15035.1694 | 15643.9579 | 16231.1392 | 16806.3996 | 17525.3211 | 18291.336 | 19140.2105 | 19818.8995 | 20073.0156 | 20327.1317 | 20581.2477 | 20835.3638 | 21089.4799 | 21343.5959 | 21597.712 | 21851.8281 | 22105.9441 | 22360.0602 | 22614.1763 | 0.00077707 | 0.00078817 | 0.00079927 | 0.00081038 | 0.00082148 | 0.00083258 | 0.00084368 | 0.00085479 | 0.00086589 | 0.00087699 | 0.00088809 | 0.0008992 | 0.0009103 | 0.0009214 | 0.0009325 | 0.00094361 | 0.00095471 | 0.00096581 | 0.00097691 | 0.00098801 | 67691.2069 | 70139.1106 | 72979.111 | 75718.3134 | 78401.9052 | 81755.6761 | 85329.1378 | 89289.1397 | 92455.2263 | 93640.6785 | 94826.1307 | 96011.5829 | 97197.0351 | 98382.4874 | 99567.9396 | 100753.3918 | 101938.844 | 103124.2962 | 104309.7484 | 105495.2006 | 1274585.1635 | 75464.0307 | -43742.0182 | 1230843.1453 | TRUE
| WBL006 | WBL | 1 | FALSE | 1 | 1 | 1 | 45090.5514 | 10938.1181 | 0.0095341 | 0.0096513 | 0.0097684 | 0.0098855 | 0.010003 | 0.01012 | 0.010237 | 0.010354 | 0.010471 | 0.010588 | 0.010705 | 0.010823 | 0.01094 | 0.011057 | 0.011174 | 0.011291 | 0.011408 | 0.011525 | 0.011643 | 0.01176 | 19868.8684 | 20333.5045 | 20892.7791 | 21459.5479 | 21942.3845 | 22430.574 | 23064.4684 | 23801.566 | 24357.9517 | 24630.4221 | 24902.8925 | 25175.3629 | 25447.8333 | 25720.3037 | 25992.774 | 26265.2444 | 26537.7148 | 26810.1852 | 27082.6556 | 27355.126 | 4819.8131 | 4932.5251 | 5068.1945 | 5205.682 | 5322.809 | 5441.2346 | 5595.0054 | 5773.8114 | 5908.7801 | 5974.8763 | 6040.9725 | 6107.0687 | 6173.1648 | 6239.261 | 6305.3572 | 6371.4534 | 6437.5496 | 6503.6457 | 6569.7419 | 6635.8381 | 0.00038611 | 0.00039086 | 0.0003956 | 0.00040034 | 0.00040509 | 0.00040983 | 0.00041457 | 0.00041932 | 0.00042406 | 0.0004288 | 0.00043355 | 0.00043829 | 0.00044304 | 0.00044778 | 0.00045252 | 0.00045727 | 0.00046201 | 0.00046675 | 0.0004715 | 0.00047624 | 24688.6819 | 25266.03 | 25960.974 | 26665.2303 | 27265.1939 | 27871.809 | 28659.4742 | 29575.3779 | 30266.7323 | 30605.2988 | 30943.8654 | 31282.432 | 31620.9985 | 31959.5651 | 32298.1317 | 32636.6983 | 32975.2648 | 33313.8314 | 33652.398 | 33990.9645 | 426746.5036 | 46500.5006 | -26953.5794 | 399792.9242 | TRUE
| WIN011 | WIN | 14 | FALSE | 14 | 18 | 3 | 36385.0727 | 10747.6467 | 0.0096167 | 0.0097614 | 0.0099061 | 0.010051 | 0.010195 | 0.01034 | 0.010485 | 0.010629 | 0.010774 | 0.010919 | 0.011063 | 0.011208 | 0.011353 | 0.011497 | 0.011642 | 0.011787 | 0.011931 | 0.012076 | 0.012221 | 0.012365 | 15710.7236 | 15983.0601 | 16439.1205 | 16827.4531 | 17144.857 | 17426.2629 | 17863.3973 | 18384.2643 | 18713.9385 | 18965.215 | 19216.4916 | 19467.7681 | 19719.0446 | 19970.3211 | 20221.5976 | 20472.8741 | 20724.1506 | 20975.4271 | 21226.7036 | 21477.9801 | 4640.7302 | 4721.1747 | 4855.8886 | 4970.5966 | 5064.3533 | 5147.4768 | 5276.6002 | 5430.4571 | 5527.8383 | 5602.0619 | 5676.2855 | 5750.5091 | 5824.7327 | 5898.9563 | 5973.1799 | 6047.4035 | 6121.6271 | 6195.8507 | 6270.0743 | 6344.2979 | 0.0054524 | 0.0055344 | 0.0056164 | 0.0056985 | 0.0057805 | 0.0058625 | 0.0059445 | 0.0060266 | 0.0061086 | 0.0061906 | 0.0062726 | 0.0063546 | 0.0064367 | 0.0065187 | 0.0066007 | 0.0066827 | 0.0067647 | 0.0068468 | 0.0069288 | 0.0070108 | 20351.4593 | 20704.2403 | 21295.0147 | 21798.0555 | 22209.2161 | 22573.7455 | 23140.0034 | 23814.7275 | 24241.783 | 24567.2831 | 24892.7833 | 25218.2835 | 25543.7837 | 25869.2839 | 26194.7841 | 26520.2843 | 26845.7845 | 27171.2847 | 27496.7849 | 27822.285 | 346497.1473 | 422491.6171 | -244893.3064 | 101603.8409 | TRUE
| WMN013 | WMN | 1 | FALSE | 1 | 1 | 1 | 61329.3035 | 12664.203 | 0.0096597 | 0.0098187 | 0.0099776 | 0.010137 | 0.010296 | 0.010455 | 0.010614 | 0.010773 | 0.010932 | 0.011091 | 0.011249 | 0.011408 | 0.011567 | 0.011726 | 0.011885 | 0.012044 | 0.012203 | 0.012362 | 0.012521 | 0.01268 | 42631.5093 | 43455.2128 | 44592.9734 | 45555.5419 | 46142.0326 | 46789.5559 | 48028.8662 | 49551.8358 | 50079.2703 | 50807.5907 | 51535.9111 | 52264.2314 | 52992.5518 | 53720.8721 | 54449.1925 | 55177.5128 | 55905.8332 | 56634.1535 | 57362.4739 | 58090.7942 | 8803.1994 | 8973.2902 | 9208.2322 | 9406.998 | 9528.1054 | 9661.8158 | 9917.7274 | 10232.2132 | 10341.1259 | 10491.5205 | 10641.9151 | 10792.3097 | 10942.7043 | 11093.099 | 11243.4936 | 11393.8882 | 11544.2828 | 11694.6774 | 11845.072 | 11995.4666 | 0.0003912 | 0.00039764 | 0.00040407 | 0.00041051 | 0.00041695 | 0.00042339 | 0.00042983 | 0.00043627 | 0.0004427 | 0.00044914 | 0.00045558 | 0.00046202 | 0.00046846 | 0.0004749 | 0.00048133 | 0.00048777 | 0.00049421 | 0.00050065 | 0.00050709 | 0.00051353 | 51434.7091 | 52428.5034 | 53801.206 | 54962.5403 | 55670.1384 | 56451.3722 | 57946.594 | 59784.0495 | 60420.3967 | 61299.1117 | 62177.8266 | 63056.5416 | 63935.2566 | 64813.9715 | 65692.6865 | 66571.4015 | 67450.1165 | 68328.8314 | 69207.5464 | 70086.2614 | 869858.8092 | 46500.5006 | -26953.5794 | 842905.2297 | TRUE
| WND014 | WND | 3 | FALSE | 3 | 5 | 1 | 34098.9574 | 9467.2647 | 0.0097441 | 0.0099313 | 0.010118 | 0.010306 | 0.010493 | 0.01068 | 0.010867 | 0.011054 | 0.011241 | 0.011428 | 0.011616 | 0.011803 | 0.01199 | 0.012177 | 0.012364 | 0.012551 | 0.012738 | 0.012925 | 0.013113 | 0.0133 | 19532.3446 | 20010.4318 | 20702.2194 | 21334.415 | 21939.4018 | 22625.9701 | 23510.6713 | 24526.7994 | 25252.8197 | 25673.2101 | 26093.6005 | 26513.9908 | 26934.3812 | 27354.7716 | 27775.162 | 28195.5524 | 28615.9428 | 29036.3332 | 29456.7236 | 29877.1139 | 5422.9774 | 5555.714 | 5747.7825 | 5923.3058 | 6091.2749 | 6281.8943 | 6527.5235 | 6809.6422 | 7011.2152 | 7127.9327 | 7244.6503 | 7361.3678 | 7478.0854 | 7594.803 | 7711.5205 | 7828.2381 | 7944.9556 | 8061.6732 | 8178.3907 | 8295.1083 | 0.0011839 | 0.0012066 | 0.0012293 | 0.0012521 | 0.0012748 | 0.0012975 | 0.0013203 | 0.001343 | 0.0013657 | 0.0013885 | 0.0014112 | 0.0014339 | 0.0014567 | 0.0014794 | 0.0015022 | 0.0015249 | 0.0015476 | 0.0015704 | 0.0015931 | 0.0016158 | 24955.3232 | 25566.147 | 26450.0031 | 27257.7221 | 28030.678 | 28907.8657 | 30038.1962 | 31336.443 | 32264.0362 | 32801.1442 | 33338.2521 | 33875.3601 | 34412.4681 | 34949.5761 | 35486.684 | 36023.792 | 36560.9 | 37098.0079 | 37635.1159 | 38172.2239 | 454701.755 | 121964.5314 | -70695.5976 | 384006.1574 | TRUE
| WSFWMN | WMN | 5 | FALSE | 5 | 6 | 2 | 61329.3035 | 12664.203 | 0.0096621 | 0.0098219 | 0.0099817 | 0.010141 | 0.010301 | 0.010461 | 0.010621 | 0.010781 | 0.01094 | 0.0111 | 0.01126 | 0.01142 | 0.01158 | 0.011739 | 0.011899 | 0.012059 | 0.012219 | 0.012379 | 0.012538 | 0.012698 | 150232.7905 | 154194.8012 | 159464.4194 | 164021.8389 | 166753.4705 | 169970.8618 | 175617.2168 | 182286.8195 | 185131.4903 | 187835.4353 | 190539.3803 | 193243.3253 | 195947.2704 | 198651.2154 | 201355.1604 | 204059.1054 | 206763.0504 | 209466.9954 | 212170.9404 | 214874.8854 | 31022.341 | 31840.4769 | 32928.6274 | 33869.7124 | 34433.7811 | 35098.1567 | 36264.1016 | 37641.3421 | 38228.7528 | 38787.1043 | 39345.4558 | 39903.8073 | 40462.1588 | 41020.5103 | 41578.8618 | 42137.2133 | 42695.5648 | 43253.9163 | 43812.2678 | 44370.6193 | 0.0019565 | 0.0019888 | 0.0020212 | 0.0020535 | 0.0020859 | 0.0021183 | 0.0021506 | 0.002183 | 0.0022153 | 0.0022477 | 0.00228 | 0.0023124 | 0.0023447 | 0.0023771 | 0.0024095 | 0.0024418 | 0.0024742 | 0.0025065 | 0.0025389 | 0.0025712 | 181255.1334 | 186035.2801 | 192393.0488 | 197891.5534 | 201187.2537 | 205069.0206 | 211881.3205 | 219928.1638 | 223360.2454 | 226622.5419 | 229884.8384 | 233147.135 | 236409.4315 | 239671.7281 | 242934.0246 | 246196.3212 | 249458.6177 | 252720.9142 | 255983.2108 | 259245.5073 | 3179769.8864 | 168465.032 | -97649.177 | 3082120.7094 | TRUE

## Sensitivities
Powercor
Lines flood resilience program
| Total |  | 73057964.1442 | -10798229.3593 | 62259734.7849 |  |  | 61179911.849 | 63339557.7209 | 69565531.1994 | 54953938.3705 | 53874115.4346
|  |  | Option 2 | Option 2 | Option 2 | Option 2 | Capex sensitivity | 10% | -10% | 0% | 0% | 10% | Preferred
|  |  | Total benefits | Annualised capex |  | preferred | Benefits sensitivity | 0% | 0% | 10% | -10% | -10% | option
| Feeders | ZSS | PV ($2023) | PV ($2023) | NPV ($2023) |  |  | Sensitivity 1 | Sensitivity 2 | Sensitivity 3 | Sensitivity 4 | Sensitivity 5 | unchanged
| ART023 | ART | 479164.8858 | -26953.5794 | 452211.3064 | TRUE |  | 449515.9484 | 454906.6643 | 500127.7949 | 404294.8178 | 401599.4598 | TRUE
| BAN003 | BAN | 1048046.9047 | -87484.0364 | 960562.8684 | TRUE |  | 951814.4647 | 969311.272 | 1065367.5588 | 855758.1779 | 847009.7742 | TRUE
| BAS011 | BAS | 1111478.233 | -32036.1497 | 1079442.0833 | TRUE |  | 1076238.4683 | 1082645.6983 | 1190589.9066 | 968294.26 | 965090.645 | TRUE
| BAS022 | BAS | 820206.7431 | -48824.5885 | 771382.1546 | TRUE |  | 766499.6957 | 776264.6134 | 853402.8289 | 689361.4803 | 684479.0214 | TRUE
| BAS033 | BAS | 750218.9345 | -53907.1588 | 696311.7757 | TRUE |  | 690921.0599 | 701702.4916 | 771333.6692 | 621289.8823 | 615899.1664 | TRUE
| BATSBAS1 | BAS | 0.0063627 | 0 | 0.0063627 | TRUE |  | 0.0063627 | 0.0063627 | 0.006999 | 0.0057264 | 0.0057264 | TRUE
| BBD014 | BBD | 1240801.3067 | -32036.1497 | 1208765.157 | TRUE |  | 1205561.5421 | 1211968.772 | 1332845.2877 | 1084685.0264 | 1081481.4114 | TRUE
| BET005 | BETS | 1121223.2693 | -21871.0091 | 1099352.2602 | TRUE |  | 1097165.1593 | 1101539.3611 | 1211474.5872 | 987229.9333 | 985042.8324 | TRUE
| BET006 | BETS | 1500525.8079 | -113667.2519 | 1386858.556 | TRUE |  | 1375491.8309 | 1398225.2812 | 1536911.1368 | 1236805.9752 | 1225439.2501 | TRUE
| BETSMRO | BETS | 0.0065923 | 0 | 0.0065923 | TRUE |  | 0.0065923 | 0.0065923 | 0.0072515 | 0.0059331 | 0.0059331 | TRUE
| BMH003 | BMH | 713227.7398 | -164032.5682 | 549195.1716 | TRUE |  | 532791.9148 | 565598.4284 | 620517.9456 | 477872.3976 | 461469.1408 | TRUE
| BMH005 | BBD | 1388940.4307 | -21871.0091 | 1367069.4216 | TRUE |  | 1364882.3207 | 1369256.5225 | 1505963.4647 | 1228175.3786 | 1225988.2777 | TRUE
| BMH006 | BMH | 426470.3362 | -103502.1112 | 322968.225 | TRUE |  | 312618.0139 | 333318.4361 | 365615.2586 | 280321.1914 | 269970.9803 | TRUE
| BSPBBD | BBD | 3566759.1277 | -43742.0182 | 3523017.1096 | TRUE |  | 3518642.9077 | 3527391.3114 | 3879693.0223 | 3166341.1968 | 3161966.995 | TRUE
| CDN004 | CDN | 122138.5843 | -65613.0273 | 56525.557 | TRUE |  | 49964.2543 | 63086.8597 | 68739.4154 | 44311.6986 | 37750.3958 | TRUE
| CHA005 | CHA | 539054.1441 | -21871.0091 | 517183.135 | TRUE |  | 514996.0341 | 519370.2359 | 571088.5494 | 463277.7206 | 461090.6197 | TRUE
| CHA006 | CHA | 764592.9783 | -48824.5885 | 715768.3898 | TRUE |  | 710885.9309 | 720650.8486 | 792227.6876 | 639309.0919 | 634426.6331 | TRUE
| CHM011 | CHM | 197987.7922 | -75778.1679 | 122209.6243 | TRUE |  | 114631.8075 | 129787.4411 | 142008.4036 | 102410.8451 | 94833.0283 | TRUE
| CLC003 | CLC | 671466.2009 | -163262.2043 | 508203.9966 | TRUE |  | 491877.7762 | 524530.2171 | 575350.6167 | 441057.3765 | 424731.1561 | TRUE
| CLC006 | CLC | 1096274.5453 | -112896.8879 | 983377.6574 | TRUE |  | 972087.9686 | 994667.3462 | 1093005.1119 | 873750.2028 | 862460.514 | TRUE
| CLC013 | CLC | 648876.761 | -185133.2134 | 463743.5476 | TRUE |  | 445230.2263 | 482256.8689 | 528631.2237 | 398855.8715 | 380342.5502 | TRUE
| CME014 | CME | 1286198.808 | -123832.3925 | 1162366.4155 | TRUE |  | 1149983.1763 | 1174749.6548 | 1290986.2963 | 1033746.5347 | 1021363.2955 | TRUE
| CME015 | CME | 864306.4828 | -80090.3743 | 784216.1085 | TRUE |  | 776207.0711 | 792225.1459 | 870646.7568 | 697785.4602 | 689776.4228 | TRUE
| CME016 | CME | 963865.6271 | -232417.074 | 731448.553 | TRUE |  | 708206.8456 | 754690.2604 | 827835.1158 | 635061.9903 | 611820.2829 | TRUE
| CME021 | CME | 695593.4619 | -21871.0091 | 673722.4528 | TRUE |  | 671535.3519 | 675909.5537 | 743281.799 | 604163.1066 | 601976.0057 | TRUE
| CMN002 | CMN | 299829.0426 | -102731.7473 | 197097.2953 | TRUE |  | 186824.1206 | 207370.47 | 227080.1996 | 167114.391 | 156841.2163 | TRUE
| CMN004 | CMN | 313419.4724 | -80860.7382 | 232558.7342 | TRUE |  | 224472.6603 | 240644.808 | 263900.6814 | 201216.7869 | 193130.7131 | TRUE
| CMN005 | CMN | 836217.3381 | -26953.5794 | 809263.7587 | TRUE |  | 806568.4007 | 811959.1166 | 892885.4925 | 725642.0249 | 722946.6669 | TRUE
| CRO021 | CRO | 583871.3859 | -53907.1588 | 529964.2271 | TRUE |  | 524573.5112 | 535354.943 | 588351.3657 | 471577.0885 | 466186.3726 | TRUE
| CTN002 | CTN | 255633.8192 | -43742.0182 | 211891.8011 | TRUE |  | 207517.5992 | 216266.0029 | 237455.183 | 186328.4191 | 181954.2173 | TRUE
| CTN003 | CTN | 198656.3024 | -129685.3267 | 68970.9757 | TRUE |  | 56002.443 | 81939.5083 | 88836.6059 | 49105.3454 | 36136.8127 | TRUE
| CTN004 | CTN | 909925.4128 | -37889.084 | 872036.3288 | TRUE |  | 868247.4204 | 875825.2372 | 963028.8701 | 781043.7875 | 777254.8791 | TRUE
| CTN006 | CTN | 575340.0593 | -351937.2601 | 223402.7991 | TRUE |  | 188209.0731 | 258596.5252 | 280936.8051 | 165868.7932 | 130675.0672 | TRUE
| ECA007 | ECA | 606629.3323 | -182822.1216 | 423807.2107 | TRUE |  | 405524.9986 | 442089.4229 | 484470.144 | 363144.2775 | 344862.0653 | TRUE
| ECA010 | ECA | 839875.5346 | -32036.1497 | 807839.3849 | TRUE |  | 804635.7699 | 811042.9998 | 891826.9383 | 723851.8314 | 720648.2164 | TRUE
| EHK022 | EHK | 579226.0391 | -21871.0091 | 557355.03 | TRUE |  | 555167.9291 | 559542.131 | 615277.634 | 499432.4261 | 497245.3252 | TRUE
| EHK024 | EHK | 968742.0375 | -118749.8222 | 849992.2154 | TRUE |  | 838117.2332 | 861867.1976 | 946866.4191 | 753118.0116 | 741243.0294 | TRUE
| EHK031 | EHK | 1191044.7079 | -75778.1679 | 1115266.54 | TRUE |  | 1107688.7232 | 1122844.3568 | 1234371.0108 | 996162.0692 | 988584.2524 | TRUE
| FNS012 | FNS | 672523.712 | -21871.0091 | 650652.703 | TRUE |  | 648465.602 | 652839.8039 | 717905.0742 | 583400.3317 | 581213.2308 | TRUE
| FNS013 | FNS | 1215856.535 | -54677.5227 | 1161179.0123 | TRUE |  | 1155711.26 | 1166646.7645 | 1282764.6658 | 1039593.3588 | 1034125.6065 | TRUE
| FNS022 | FNS | 656784.5724 | -32806.5136 | 623978.0588 | TRUE |  | 620697.4074 | 627258.7101 | 689656.516 | 558299.6015 | 555018.9501 | TRUE
| GCY011 | GCY | 1253327.6516 | -59760.093 | 1193567.5586 | TRUE |  | 1187591.5493 | 1199543.5679 | 1318900.3237 | 1068234.7934 | 1062258.7841 | TRUE
| GCY014 | GCY | 1248730.3304 | -125373.1203 | 1123357.2101 | TRUE |  | 1110819.8981 | 1135894.5221 | 1248230.2432 | 998484.1771 | 985946.865 | TRUE
| GHP011 | GHP | 999739.8309 | -48824.5885 | 950915.2424 | TRUE |  | 946032.7835 | 955797.7012 | 1050889.2254 | 850941.2593 | 846058.8004 | TRUE
| GHP012 | GHP | 898035.0259 | -26953.5794 | 871081.4465 | TRUE |  | 868386.0885 | 873776.8044 | 960884.9491 | 781277.9439 | 778582.5859 | TRUE
| GHP021 | GHP | 873149.868 | -103502.1112 | 769647.7568 | TRUE |  | 759297.5457 | 779997.9679 | 856962.7436 | 682332.77 | 671982.5589 | TRUE
| GHP022 | GHP | 513583.5955 | -70695.5976 | 442887.9979 | TRUE |  | 435818.4381 | 449957.5576 | 494246.3574 | 391529.6383 | 384460.0786 | TRUE
| HSM002 | HSM | 272217.0518 | -21871.0091 | 250346.0428 | TRUE |  | 248158.9418 | 252533.1437 | 277567.7479 | 223124.3376 | 220937.2367 | TRUE
| HSM004 | HSM | 438727.9337 | -172656.981 | 266070.9527 | TRUE |  | 248805.2546 | 283336.6508 | 309943.7461 | 222198.1593 | 204932.4612 | TRUE
| HTN011 | HTN | 100857.1398 | -92566.6067 | 8290.5331 | TRUE |  | -966.1276 | 17547.1938 | 18376.2471 | -1795.1809 | -11051.8415 | FALSE
| HTN013 | HTN | 367948.189 | -131226.0546 | 236722.1344 | TRUE |  | 223599.529 | 249844.7399 | 273516.9533 | 199927.3155 | 186804.7101 | TRUE
| HTN032 | KGTS | 567882.4816 | -26953.5794 | 540928.9021 | TRUE |  | 538233.5442 | 543624.2601 | 597717.1503 | 484140.654 | 481445.2961 | TRUE
| HTN034 | KGTS | 285200.7816 | -482392.9508 | -197192.1692 | FALSE |  | -245431.4642 | -148952.8741 | -168672.091 | -225712.2473 | -273951.5424 | TRUE
| KGT002 | KGTS | 626817.1767 | -21871.0091 | 604946.1676 | TRUE |  | 602759.0667 | 607133.2686 | 667627.8853 | 542264.45 | 540077.3491 | TRUE
| KGT004 | KGTS | 554895.2505 | -301571.9438 | 253323.3067 | TRUE |  | 223166.1124 | 283480.5011 | 308812.8318 | 197833.7817 | 167676.5873 | TRUE
| KGTSGSF | KGTS | 0.012936 | 0 | 0.012936 | TRUE |  | 0.012936 | 0.012936 | 0.01423 | 0.011643 | 0.011643 | TRUE
| KYM001 | KYM | 829539.2895 | -172656.981 | 656882.3085 | TRUE |  | 639616.6104 | 674148.0066 | 739836.2375 | 573928.3796 | 556662.6815 | TRUE
| KYM002 | KYM | 539885.5782 | -21871.0091 | 518014.5691 | TRUE |  | 515827.4682 | 520201.67 | 572003.1269 | 464026.0113 | 461838.9104 | TRUE
| KYM003 | KYM | 542768.6934 | -161721.4764 | 381047.217 | TRUE |  | 364875.0693 | 397219.3646 | 435324.0863 | 326770.3476 | 310598.2 | TRUE
| KYM004 | KYM | 555741.0295 | -568796.6461 | -13055.6166 | FALSE |  | -69935.2812 | 43824.048 | 42518.4863 | -68629.7196 | -125509.3842 | TRUE
| KYM006 | KYM | 632586.3659 | -150785.9719 | 481800.394 | TRUE |  | 466721.7968 | 496878.9912 | 545059.0306 | 418541.7574 | 403463.1602 | TRUE
| MBN031 | MBN | 540229.8331 | -290636.4392 | 249593.3938 | TRUE |  | 220529.7499 | 278657.0377 | 303616.3771 | 195570.4105 | 166506.7666 | TRUE
| MBN032 | MBN | 1241905.8134 | -64072.2994 | 1177833.5139 | TRUE |  | 1171426.284 | 1184240.7439 | 1302024.0952 | 1053642.9326 | 1047235.7026 | TRUE
| MDA023 | MDA | 1669207.0265 | -85943.3085 | 1583263.7179 | TRUE |  | 1574669.3871 | 1591858.0488 | 1750184.4206 | 1416343.0153 | 1407748.6844 | TRUE
| MDA032 | MDA | 699703.7944 | -26953.5794 | 672750.215 | TRUE |  | 670054.8571 | 675445.573 | 742720.5945 | 602779.8356 | 600084.4776 | TRUE
| MNA021 | MNA | 867895.709 | -102731.7473 | 765163.9617 | TRUE |  | 754890.787 | 775437.1364 | 851953.5326 | 678374.3908 | 668101.2161 | TRUE
| MNA034 | MNA | 673886.1462 | -853119.7643 | -179233.6181 | FALSE |  | -264545.5945 | -93921.6417 | -111845.0035 | -246622.2327 | -331934.2091 | TRUE
| MNASTN | MNA | 0.0064834 | 0 | 0.0064834 | TRUE |  | 0.0064834 | 0.0064834 | 0.0071318 | 0.0058351 | 0.0058351 | TRUE
| MRO005 | MRO | 519271.9017 | -1130819.5844 | -611547.6827 | FALSE |  | -724629.6411 | -498465.7243 | -559620.4925 | -663474.8729 | -776556.8313 | TRUE
| MRO007 | MRO | 509225.533 | -598061.3173 | -88835.7842 | FALSE |  | -148641.916 | -29029.6525 | -37913.2309 | -139758.3376 | -199564.4693 | TRUE
| MRO008 | MRO | 567917.3453 | -485164.4293 | 82752.916 | TRUE |  | 34236.473 | 131269.3589 | 139544.6505 | 25961.1814 | -22555.2615 | FALSE
| NHL015 | NHL | 288609.3763 | -178509.9152 | 110099.4611 | TRUE |  | 92248.4696 | 127950.4526 | 138960.3987 | 81238.5235 | 63387.532 | TRUE
| NHL016 | NHL | 286164.7435 | -26953.5794 | 259211.1641 | TRUE |  | 256515.8061 | 261906.522 | 287827.6384 | 230594.6897 | 227899.3318 | TRUE
| NKA001 | NKA | 291797.1307 | -117979.4583 | 173817.6724 | TRUE |  | 162019.7266 | 185615.6183 | 202997.3855 | 144637.9594 | 132840.0135 | TRUE
| NKA002 | RCTS | 661397.4556 | -232417.074 | 428980.3815 | TRUE |  | 405738.6741 | 452222.0889 | 495120.1271 | 362840.636 | 339598.9286 | TRUE
| NKA005 | RCTS | 516294.8379 | -210546.0649 | 305748.7729 | TRUE |  | 284694.1664 | 326803.3794 | 357378.2567 | 254119.2891 | 233064.6826 | TRUE
| NKA006 | RCTS | 1089205.5095 | -32036.1497 | 1057169.3598 | TRUE |  | 1053965.7448 | 1060372.9748 | 1166089.9108 | 948248.8089 | 945045.1939 | TRUE
| OYN005 | RCTS | 347318.4911 | -21871.0091 | 325447.482 | TRUE |  | 323260.3811 | 327634.5829 | 360179.3311 | 290715.6329 | 288528.532 | TRUE
| RCT011 | RCTS | 449806.1897 | -225023.412 | 224782.7777 | TRUE |  | 202280.4365 | 247285.1189 | 269763.3967 | 179802.1588 | 157299.8176 | TRUE
| RCT013 | RCTS | 1215377.9575 | -326524.4086 | 888853.549 | TRUE |  | 856201.1081 | 921505.9898 | 1010391.3447 | 767315.7532 | 734663.3123 | TRUE
| RCT014 | RCTS | 1048367.6921 | -146473.7655 | 901893.9266 | TRUE |  | 887246.55 | 916541.3031 | 1006730.6958 | 797057.1574 | 782409.7808 | TRUE
| RCT015 | RCTS | 357611.1834 | -80860.7382 | 276750.4452 | TRUE |  | 268664.3713 | 284836.519 | 312511.5635 | 240989.3268 | 232903.253 | TRUE
| SHL004 | SHL | 743922.4687 | -824625.4571 | -80702.9884 | FALSE |  | -163165.5341 | 1759.5573 | -6310.7415 | -155095.2353 | -237557.781 | TRUE
| SHL005 | SHL | 366803.4176 | -75007.804 | 291795.6136 | TRUE |  | 284294.8332 | 299296.394 | 328475.9553 | 255115.2718 | 247614.4914 | TRUE
| SHN011 | SHN | 811256.0999 | -209775.701 | 601480.3989 | TRUE |  | 580502.8288 | 622457.969 | 682606.0089 | 520354.7889 | 499377.2188 | TRUE
| SHN021 | SHN | 746895.4833 | -236729.2804 | 510166.2029 | TRUE |  | 486493.2748 | 533839.1309 | 584855.7512 | 435476.6545 | 411803.7265 | TRUE
| SHN024 | SHN | 804193.6421 | -85943.3085 | 718250.3336 | TRUE |  | 709656.0027 | 726844.6644 | 798669.6978 | 637830.9694 | 629236.6385 | TRUE
| SHP011 | SHP | 941096.9039 | -64072.2994 | 877024.6044 | TRUE |  | 870617.3745 | 883431.8344 | 971134.2948 | 782914.914 | 776507.6841 | TRUE
| SHP012 | SHP | 806313.1581 | -26953.5794 | 779359.5787 | TRUE |  | 776664.2208 | 782054.9366 | 859990.8945 | 698728.2629 | 696032.9049 | TRUE
| SHP014 | SHP | 577709.426 | -527365.7197 | 50343.7063 | TRUE |  | -2392.8656 | 103080.2783 | 108114.6489 | -7427.2363 | -60163.8082 | FALSE
| SHTSKYM1 | KYM | 0.01955 | 0 | 0.01955 | TRUE |  | 0.01955 | 0.01955 | 0.021505 | 0.017595 | 0.017595 | TRUE
| SHTSMNA | KYM | 0.013033 | 0 | 0.013033 | TRUE |  | 0.013033 | 0.013033 | 0.014337 | 0.01173 | 0.01173 | TRUE
| SHTSNKA | KYM | 0.032541 | 0 | 0.032541 | TRUE |  | 0.032541 | 0.032541 | 0.035795 | 0.029287 | 0.029287 | TRUE
| SHTSSHP | KYM | 0.013023 | 0 | 0.013023 | TRUE |  | 0.013023 | 0.013023 | 0.014326 | 0.011721 | 0.011721 | TRUE
| STL005 | STL | 812316.0132 | -65613.0273 | 746702.9859 | TRUE |  | 740141.6832 | 753264.2886 | 827934.5872 | 665471.3846 | 658910.0819 | TRUE
| STL006 | STL | 310948.2274 | -346854.6898 | -35906.4624 | FALSE |  | -70591.9314 | -1220.9934 | -4811.6397 | -67001.2851 | -101686.7541 | TRUE
| STL007 | STL | 584420.2719 | -260141.0174 | 324279.2545 | TRUE |  | 298265.1528 | 350293.3562 | 382721.2817 | 265837.2273 | 239823.1256 | TRUE
| STN011 | STN | 762967.8987 | -379661.2035 | 383306.6953 | TRUE |  | 345340.5749 | 421272.8156 | 459603.4851 | 307009.9054 | 269043.7851 | TRUE
| STN012 | STN | 1184642.1723 | -80090.3743 | 1104551.7979 | TRUE |  | 1096542.7605 | 1112560.8354 | 1223016.0152 | 986087.5807 | 978078.5433 | TRUE
| STN021 | STN | 669510.7932 | -128914.9628 | 540595.8304 | TRUE |  | 527704.3341 | 553487.3266 | 607546.9097 | 473644.751 | 460753.2548 | TRUE
| STN024 | STN | 1317183.5384 | -531677.9261 | 785505.6123 | TRUE |  | 732337.8197 | 838673.4049 | 917223.9661 | 653787.2585 | 600619.4659 | TRUE
| TNA022 | TNA | 88948.8344 | -97649.177 | -8700.3426 | FALSE |  | -18465.2603 | 1064.5751 | 194.5408 | -17595.2261 | -27360.1438 | TRUE
| WBE023 | WBE | 1274585.1635 | -43742.0182 | 1230843.1453 | TRUE |  | 1226468.9435 | 1235217.3472 | 1358301.6617 | 1103384.629 | 1099010.4272 | TRUE
| WBL006 | WBL | 426746.5036 | -26953.5794 | 399792.9242 | TRUE |  | 397097.5663 | 402488.2821 | 442467.5746 | 357118.2738 | 354422.9159 | TRUE
| WIN011 | WIN | 346497.1473 | -244893.3064 | 101603.8409 | TRUE |  | 77114.5102 | 126093.1715 | 136253.5556 | 66954.1261 | 42464.7955 | TRUE
| WMN013 | WMN | 869858.8092 | -26953.5794 | 842905.2297 | TRUE |  | 840209.8718 | 845600.5877 | 929891.1107 | 755919.3488 | 753223.9909 | TRUE
| WND014 | WND | 454701.755 | -70695.5976 | 384006.1574 | TRUE |  | 376936.5977 | 391075.7172 | 429476.3329 | 338535.9819 | 331466.4222 | TRUE
| WSFWMN | WMN | 3179769.8864 | -97649.177 | 3082120.7094 | TRUE |  | 3072355.7917 | 3091885.6271 | 3400097.698 | 2764143.7207 | 2754378.803 | TRUE

## Workings_risks
Powercor
Lines flood resilience program
WORKINGS - RISKS
Spans for remediation
This methodology sets out to determine the HV and Subtransmission spans to remediate for clearance breaches under existing 1-in-100 year flood zones
Analysis of identified spans with clearance breaches (i.e. distance of conductor sag to water is less than 4.4m) and minimum required lifting height
Likelihood of 1-in-100 year flood
| At risk feeders in 1-in-100 year flood zone | 363
| Feeders that had previously flooded | 10 | based on historical flood data
| Historical annual likelihood of 1-in-100 year flood | 33.33% | based on historical flood data
| Annual likelihood of 1-in-100 yr flood impacting at risk feeder | 0.9183%
Likelihood a person coming into contact with live span under flooded conditions
| Historical annual average of contact with HV lines | 43 | across entire HV network
| Total number of HV and ST spans | 388672
| Annual likelihood of contact under flooded conditions | 0.01106%
| Probability of consequence of death due to contact with conductor for the public | 2.176e-05 | based on Ofgem DNO Common Netwoork Asset Indicies Methodology
| Disproportionate factor - single fatality or serious injury | 3 | Powercor value framework

## Misc_calcs
Powercor
Lines flood resilience program
ESCALATION & OTHER
| Year end |  |  |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
|  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
DISCOUNT FACTOR |  |  |  | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
| Discount factor |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129
0

## Data
Powercor
Lines flood resilience program
DATA
No change to existing practices
Not applicable (compliance)
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
DROPDOWN LISTS
| Business |  |  | Type |  | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Subtransmission | Capex first year
| CitiPower | CP |  | - Select - |  | FALSE | June | 6 | CY | Not used |  | 2023 | BATS | 2026-27
| Powercor | PA |  | Capex |  | TRUE | December | 12 | FY |  |  | 2022 | BATSBAS1 | 2025-26
| United Energy | UE |  | Opex | [7 empty] | 2021 | BETSMRO | 2024-25
[12 empty] | 2020 | KGTSGSF
KGTSHL
MNASTN
SHTS
SHTSKYM1
SHTSMNA
SHTSNKA
SHTSSHP

## VCR_data
Powercor
Lines flood resilience program
|  | VCR | Value of network reliability
Zone Sub Station | ZSS | Weighted ave | Weighted ave | `
Hoppers Crossing Pump | HCP | 52200 | 10649.2292
Werribee | WBE | 39317.7095 | 10727.8793
Laverton | LV | 39298.3448 | 10827.1949
Toyota | TYA | 52200 | 10649.2292
Altona Chemical | AC | 55160.9365 | 11253.2846
Compol | CPL | 52200 | 10649.2292
Laverton North | LVN | 54508.9897 | 11317.9252
Ballarat North | BAN | 44753.327 | 10611.3343
Challicum Hills Wind Farm | CHW | 52200 | 10649.2292
Ballarat South | BAS | 37239.5893 | 9753.9335
Ballarat Gold Fields | BGF | 52200 | 10649.2292
Bungal Dam | BGL | 52200 | 10649.2292
Bendigo | BETS | 39529.3474 | 10836.9965
Bendigo | BGO | 42734.8155 | 10810.6924
Eaglehawk | EHK | 45714.8889 | 11125.7391
Castlemaine | CMN | 38419.8192 | 9746.8225
Maryborough | MRO | 40985.6902 | 10762.4764
Charlton | CTN | 42808.6941 | 11497.5591
Brooklyn | BLTS | 51573.35 | 11164.202
Altona | AL | 44780.7607 | 10889.8827
Bacchus Marsh | BMH | 38093.4326 | 10804.6535
Blue Circle Geelong | BCG | 52200 | 10649.2292
Waurn Ponds | WPD | 40240.0236 | 10709.8847
Corio | CRO | 53295.2727 | 11724.3791
Ford Norlane | FDN | 52200 | 10649.2292
Ford North Shore | FNS | 47157.5465 | 11382.8682
Shell Refining Corio | SRC | 52200 | 10649.2292
Geelong B | GB | 52231.1123 | 10888.58
Geelong City | GCY | 45326.5658 | 10725.2654
Geelong | GL | 37042.7803 | 10614.5948
Geelong East | GLE | 43192.2035 | 10984.5034
Drysdale | DDL | 36243.9558 | 10819.1703
Winchelsea | WIN | 36385.0727 | 10747.6467
Torquay | TQY | 36500.4227 | 10752.0314
Charam | CHM | 43924.3002 | 11308.0279
Horsham | HSM | 41631.5752 | 11021.0193
Nhill | NHL | 44485.8086 | 11603.2642
Stawell | STL | 47316.7282 | 10850.5896
Ararat | ART | 43695.1925 | 10892.5056
Heywood | HYTS | 67045.2152 | 13927.2621
Kerang | KGTS | 43210.6088 | 11999.4652
Cohuna | CHA | 48008.7507 | 11465.9097
Swan Hill | SHL | 44855.7307 | 11725.215
Woodend | WND | 34098.9574 | 9467.2647
Gisborne | GSB | 30762.9223 | 9076.1772
St Albans | SA | 35433.1387 | 10550.928
Sunshine East | SSE | 45569.8274 | 11085.074
Red Cliffs | RCTS | 53595.3633 | 11939.647
Merbein | MBN | 42126.3122 | 11964.0504
Dareton | DTN | 74790 | 15257.7749
Buronga | BNG | 52200 | 10649.2292
Mildura | MDA | 44598.6589 | 11923.6919
Kyabram | KYM | 47800.3495 | 11425.2342
Stanhope | SHP | 50191.6347 | 11451.8596
Echuca | ECA | 47522.4048 | 11920.0275
Mooroopna | MNA | 48575.8986 | 11806.2544
Shepparton | STN | 50364.8111 | 12003.9056
Numurkah | NKA | 52400.9885 | 12452.6513
Cobram East | CME | 46875.2879 | 11543.2868
Shepparton North | SHN | 47127.1698 | 12114.7415
Camperdown | CDN | 45429.2584 | 10860.1496
Cobden | COB | 52118.0985 | 10674.7661
Colac | CLC | 44906.1835 | 10807.394
Hamilton | HTN | 38280.733 | 9773.4555
Oakland's Hill Wind Farm | OWF | 52200 | 10649.2292
Koroit | KRT | 47052.9427 | 10746.9273
Terang | TRG | 45911.034 | 10967.1275
Warrnambool | WBL | 45090.5514 | 10938.1181
Portland | PLD | 42177.4532 | 10825.3545
Codrington Wind Farm | CWF | 52200 | 10649.2292
Yambuk Wind Farm | YWF | 52200 | 10649.2292
Wemen | WMN | 61329.3035 | 12664.203
Robinvale | RVL | 49456.6662 | 11978.2737
Boundary Bend | BBD | 52622.2251 | 10836.9058
Ouyen | OYN | 42821.2873 | 12027.3951
Melton | MLN | 37902.176 | 10765.6536
Sunshine | SU | 47673.7846 | 10966.4757
Truganina | TNA | 49768.8721 | 11659.7375
Gheringhap | GHP | 38273.3274 | 10683.9189