{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Contents","Cover","1. F-Factor summary","2. Individual fire start info","3. Systems and Audit"],"not_rendered":{"charts":0,"images":3,"macros":1,"external_links":0,"defined_names":7,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Contents","index":0,"n_rows":22,"n_cols":15,"rows_kept":22,"cut":false,"hidden":false,"merged":[[8,2,9,3],[2,1,2,10],[4,1,4,10]]}
[" "]
[]
[null,"Electricity Distribution Network Service Provider\nF-factor Reporting Template"]
[]
[null,"Table of contents"]
[]
[]
[null,null,"Cover sheet",null,null,"2. Fire start report"]
[]
[]
[]
[null,null,"1. F-factor summary",null,null,"3. Systems and Audit"]
[]
[]
[]
[]
[]
[]
[null,null,{"$f":"\"NOTE: This spreadsheet includes IRU targets up to and including FY\"&yearMax","v":"NOTE: This spreadsheet includes IRU targets up to and including FY2024/25"}]
[]
[null,null,{"$f":"\"NOTE: This spreadsheet was last updated on \"&TEXT(revisionDate,\"DD MMMM YYY\")","v":"NOTE: This spreadsheet was last updated on 08 August 2024"},null,null,null,null,null,null,null,null,null,null,null,"2024-08-08"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,true]

{"sheet":"Cover","index":1,"n_rows":49,"n_cols":6,"rows_kept":49,"cut":false,"hidden":false,"merged":[[10,1,11,8],[13,1,13,8],[48,2,48,6],[42,2,42,3],[42,4,42,7],[46,2,46,6],[47,2,47,6],[38,2,38,3],[38,4,38,7],[41,2,41,3],[41,4,41,7],[37,2,37,3],[37,4,37,7],[32,3,32,8],[30,3,30,8],[15,1,15,8],[26,3,26,8],[28,3,28,8],[26,1,26,2],[31,3,31,5],[14,1,14,8],[16,1,16,8],[17,1,17,8],[21,1,21,8],[19,1,19,8]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Distribution Network Service Provider"]
[null,"Fire start report"]
[]
[null,"This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.  "]
[]
[]
[null,"Colour coding of input sheets:"]
[null,"Dark blue = AER headings"]
[null,"Grey = AER instructions"]
[null,"Yellow = Input cells"]
[null,"Light orange = Automatically-generated cells"]
[]
[null,"Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so."]
[null,"The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings."]
[null,"All dollar amounts are to be unrounded, and in nominal terms."]
[]
[]
[]
[]
[null,"DNSP:",null,"Powercor"]
[]
[null,"DNSP - trading name:",null,"Powercor Australia Ltd"]
[]
[null,"DNSP - Australian business number: ",null,"ACN 064 651 109"]
[]
[null,"Reporting year:",null,"2023/24"]
[]
[]
[]
[]
[null,"Business address","Address",null,"40 Market Street"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode"]
[]
[null,"Postal address","Address",null,"Locked Bag 14090"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode"]
[]
[]
[null,"Contact name/s"]
[null,"Contact phone/s"]
[null,"Contact email address/s"]

{"sheet":"1. F-Factor summary","index":2,"n_rows":21,"n_cols":15,"rows_kept":21,"cut":false,"hidden":false,"merged":[[5,1,5,2],[3,6,3,8],[4,6,4,8],[5,6,5,8],[11,2,11,3],[12,2,12,3],[13,2,13,3],[6,2,6,3],[7,2,7,3],[8,2,8,3],[9,2,9,3],[10,2,10,3]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"},"IRU target:",{"$f":"IF(SUM(K2:O2)=0,\"\",SUM(K2:O2))","v":185.5},null,null,null,null,null,null,"AusNet Services","CitiPower","Jemena","Powercor","United Energy"]
[null,"F-factor data reporting","IRU amount:",{"$f":"IF(SUM('2. Individual fire start info'!S38:S1315)=0,\"\",SUM('2. Individual fire start info'!S38:S1315))","v":186.10119999999986},null,null,null,null,null,"current",{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>K1),\"\",LOOKUP($B3,$J3:$J101,K3:K101))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>L1),\"\",LOOKUP($B3,$J3:$J101,L3:L101))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>M1),\"\",LOOKUP($B3,$J3:$J101,M3:M101))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>N1),\"\",LOOKUP($B3,$J3:$J101,N3:N101))","v":185.5},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>O1),\"\",LOOKUP($B3,$J3:$J101,O3:O101))","v":""}]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2023/24"},"Revenue adjustment:",{"$f":"IF(OR(D1=\"\",D2=\"\"),\"\",15000*(D1-D2))","v":-9017.9999999979536},null,null,null,null,null,"2016/17",247.7,3.4,9.6999999999999993,468,22.3]
[null,null,null,null,null,null,null,null,null,"2017/18",247.7,3.4,9.6999999999999993,468,22.3]
[null,"Table 2: Summary of total fire starts by F factor Order definition",null,null,null,null,null,null,null,"2018/19",247.7,3.4,9.6999999999999993,468,22.3]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\"",null,null,null,null,null,null,null,"2019/20",221.1,3.4,9.6999999999999993,412.8,22.3]
[null,"Kind of Fire Start by definition of fire start under clause 5 of F-factor Order","Total fires by cause",null,null,null,null,null,null,"2020/21",177.5,1.3,4.2,277.60000000000002,18.7]
[null,"Started in or originated from a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1315,'1. F-Factor summary'!$B8)","v":165},null,null,null,null,null,null,"2021/22",164.3,1.9,3.7,235.2,19]
[null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1315,'1. F-Factor summary'!$B9)","v":16},null,null,null,null,null,null,"2022/23",149.69999999999999,1.5,2.7,188,13.9]
[null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1315,'1. F-Factor summary'!$B10)","v":33},null,null,null,null,null,null,"2023/24",131.69999999999999,1.7,2.7,185.5,14.2]
[null,"Started by lightning striking a distribution system or a part of a distribution system ",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1315,'1. F-Factor summary'!$B11)","v":16},null,null,null,null,null,null,"2024/25",127,1.7,2.2999999999999998,147.9,11.7]
[null,"Started by any other thing forming part of or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1315,'1. F-Factor summary'!$B12)","v":14}]
[null,"Otherwise started by a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1315,'1. F-Factor summary'!$B13)","v":0}]
[null,"Total",{"$f":"SUM(C8:C13)","v":244}]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,45496]

{"sheet":"2. Individual fire start info","index":3,"n_rows":337,"n_cols":25,"rows_kept":337,"cut":false,"hidden":false,"merged":[[25,1,25,18],[27,1,27,20],[26,1,26,21],[35,19,35,21],[33,1,33,4],[35,2,35,10],[28,1,28,18],[29,1,29,18],[35,11,35,13],[35,14,35,17],[13,1,13,11],[22,1,22,21],[24,1,24,21],[14,1,14,20],[15,1,15,18],[16,1,16,18],[18,1,18,18],[21,1,21,18],[19,1,19,18],[23,1,23,18],[20,1,20,18],[17,1,17,18],[3,22,3,24],[4,22,4,24],[5,22,5,24],[7,1,7,21],[11,1,11,2],[9,1,9,21]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2023/24"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"\"Enter into this worksheet fire start data, from any IT system, which have been recorded by \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\". Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.\"","v":"Enter into this worksheet fire start data, from any IT system, which have been recorded by Powercor. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council."}]
[]
[null,"\"Fire\" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.  "]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 3 - Individual Fire Starts"]
[null,"   (1) Date - dd/mm/yyyy"]
[null,"   (2) Time - if known, the 24-hour time of the fire start hh:mm"]
[null,"   (3) Latitude and longitude of the fire start as decimal coordinates"]
[null,"   (4) Address of the property on which the incident occurred or closest to the incident"]
[null,"   (5) Asset number for the asset nearest the fire start"]
[null,{"$f":"\"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the \"&B1&\" network\"","v":"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the Powercor network"}]
[null,"   (7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)"]
[null,"   (8) Network categorisation - CBD, Urban, Rural Long or Rural Short"]
[null,"   (9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories"]
[null,"   (10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer"]
[null,"   (11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council [Note: This is interpreted as the initiating event rather than the cause. For instance, a fuse failure resulting from a lightning strike would be attributed to \"lightning\" even if the fuse should have protected against such strikes.]"]
[null,"   (12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council"]
[null,"   (13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website) [Note: The fire danger rating applies from the time it was issued; ratings do no apply retrospectively. The rating from the previous day carries into the current day until the rating is changed. If no fire danger rating is issued for the day, a rating of \"No forecast\" applies for the whole day.]"]
[null,{"$f":"\"   (14) \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\"'s record number for the incident\"","v":"   (14) Powercor's record number for the incident"}]
[null,"   (15) ESV's OSIRIS reference number for the incident"]
[null,"   (16) Free text description of the fault containing relevant comments from field reports "]
[]
[]
[]
[null,"Table 2: Individual Fire Starts"]
[]
[null,"Number","Fire starts",null,null,null,null,null,null,null,null,"Fire Type",null,null,"Risk Factors",null,null,null,"IRU \namount","Additional information"]
[null,null,"Date 1","Time 2","Latitude 3","Longitude 3","Address of incident 4","ID of \nnearest \nasset 5","ID of nearest \npolyphase \nline 6","Voltage of line in which \nfire start \noccurred 7","Network categorisation 8","Type of primary asset \ninvolved in fire start 9","Phase(s) of \nline or \ntransformer 10","Kind of fire start as per Clause 5\nof F-factor Order-In-Council 11","Location \narea 12","Location\nmultiplier","Fire \ndanger \nrating 13","Danger multiplier","Product of multipliers","DNSP record number 14","OSIRIS \n(ESV) reference \nnumber 15","Fault \ndescription 16"]
[{"$f":"COUNTA(C38:O38,Q38,T38:V38)","v":17},1,"2023-07-02","11:21",-36.778213000000001,144.23465899999999,"16 Akins Rise, Golden Square VIC 3555, Australia","60247949","BET001","Low voltage AC (<1kV)","Rural Long"," - services pit","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",{"$f":"IF(O38=\"\",\"\",IF(O38=\"LBRA only\",0.2,IF(O38=\"HBRA only\",1,IF(O38=\"within electric line construction area\",19.8,IF(O38=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"No rating",{"$f":"IF(Q38=\"\",\"\",IF(Q38=\"No rating\",0.05,IF(Q38=\"Moderate\",0.334,IF(Q38=\"High\",0.678,IF(Q38=\"Extreme\",2.272,4.754)))))","v":0.05},{"$f":"IF(OR(P38=\"\",R38=\"\"),\"\",IF(AND(O38=\"within electric line construction area\",Q38=\"No forecast\"),1,P38*R38))","v":1.0000000000000002E-2},"INC-0021175","20230704PWA_01","Bendigo fault crew were called out to an all supply failure at # 15 Akins Rise, upon inspection of the LV service pit on the boundary of #15 & #16 crew found that an illegal connection from pit to #16 had caused a fault at a IPC connected by unknown party resulting in a fire which caused damage to wiring and outage to both properties.\nIllegal wiring was run into LV pit, further illegal wiring was found at the back of the meter board at #16 Akins Rise, matter was reported to police.\nNo reported 3rd party damage or injuries.",null,null,"Overhead conductors"]
[17,2,"2023-07-03","15:00",-38.315359000000001,142.26153500000001,"341 Badhams Rd, Toolong VIC 3285, Australia","30326905","KRT013","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",{"$f":"IF(Q39=\"\",\"\",IF(Q39=\"No rating\",0.05,IF(Q39=\"Moderate\",0.334,IF(Q39=\"High\",0.678,IF(Q39=\"Extreme\",2.272,4.754)))))","v":0.05},0.22999999999999998,"INC-0021177","20230704PWA_02","Fire comms reported a pole fire at the incident location. On arrival the crew found that an overheated connection caused a 480V FOLCB to catch fire.\nThere was no ground fire and no other reported damage or injuries.",null,null," - overhead conductor (bare; aluminium core steel reinforced)"]
[17,3,"2023-07-03","18:05",-34.170062000000001,142.145566,"2 ETHERINGTON DRIVE, MILDURA VIC 3500","34005004","MBN023","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0021191","20230705PWA_01","Customer REC called in urgent isolation request at the incident location. \nUpon arrival Mildura fault crew found that a LV service fuse had overheated, melted and burnt the chipboard meter panel it was mounted on. \nMinor damage resulted in the meter panel which didn't need replacing.\nNo 3rd party damage or injuries.",null,null," - overhead conductor (bare; all aluminium conductor)"]
[17,4,"2023-07-05","22:25",-37.321573999999998,144.134716,"7 Western Ave, Hepburn VIC 3461, Australia","30007819","BAN008","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0021213","20230706PWA_01","A report was received from the CFA relating to a fuse box fire on a pole at the above address. \nA crew attended and determined that the incoming active conductor to an LV fuse box on Westav Pole 5 had overheated and caught fire.\nWhen the crew arrived the fire had been extinguished. \nThere was no ground fire or third party damage. ",null,null," - overhead conductor (bare; copper)"]
[17,5,"2023-07-06","09:19",-38.466087999999999,144.10215299999999,"16 Inlet Cres, Aireys Inlet VIC 3231, Australia","30070126","TQY021","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0021214","20230706PWA_02","While running through a park reserve customer witnessed overhead line on fire. \nWhen crews arrived on site they noted that a pole-to-pole overhead service caught fire due to contact and rubbing against tree branches.\nNo ground fire occurred. ",null,null," - overhead conductor (bare; steel)"]
[17,6,"2023-07-14","09:38",-37.902374999999999,144.67225199999999,"36 Anton Cl, Werribee VIC 3030, Australia","30115932","WBE022","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0021335","20230717PWA_01","Report of fire at incident location\nOn arrival crew found FOLCB on customers fascia burnt\nThere was no injuries.",null,null," - overhead conductor (ABC)"]
[17,7,"2023-07-15","20:00",-38.302799999999998,142.37349900000001,"Anne St/High St, Koroit VIC 3282, Australia","31028806","KRT013","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0021336","20230717PWA_02","A nearby customer reported a pole fire and an orange glow coming from the pole at the incident location.\nOn arrival the crew found that a low voltage UG fuse box had overheated and failed on the pole at the incident location.\n Debris had fallen to the ground, however there was no ground fire due to the wet conditions.\nThere were no reported injuries or third party damage.",null,null," - overhead conductor (covered uninsulated)"]
[17,8,"2023-07-17","18:52",-36.762822,144.22886600000001,"6 Wicks Rd, Maiden Gully VIC 3551, Australia","31003170","BET006","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0021387","20230719PWA_01","Vicfire reported fire at incident location.\nUpon arrival crew found that the 100a folcb had melted and transformer lv leads were damaged and required replacing. \nFire brigade were onsite. \nCharred debris fell to ground, no grassfire.",null,null," - overhead conductor (insulated)"]
[17,9,"2023-08-03","21:11",-38.126385999999997,144.323669,"26-28 Glenfine Ave, Hamlyn Heights VIC 3215, Australia","30300576","GL013","22kV AC","Urban"," - fuse (Fault Tamer)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0021615","20230807PWA_01","A crew was dispatched to investigate a pole fire, on arrival the crew found a HV fuse had broken in half and was dangling by the lead against the pole. \nThe crew believed the fuse broke by a possum climbing on the fuse between the crossarm and fuse unit.\nA vehicle below the pole was damaged by fallen fuse debris & molten from the burning fuse unit. \nThere was no ground fire or reported injuries.",null,null,"Service lines"]
[{"$f":"COUNTA(C47:O47,Q47,T47:V47)","v":17},10,"2023-08-17","12:58",-37.049135999999997,143.73960700000001,"35 NOLAN STREET, MARYBOROUGH VIC 3465","33013531","MRO006","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O47=\"\",\"\",IF(O47=\"LBRA only\",0.2,IF(O47=\"HBRA only\",1,IF(O47=\"within electric line construction area\",19.8,IF(O47=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"No rating",{"$f":"IF(Q47=\"\",\"\",IF(Q47=\"No rating\",0.05,IF(Q47=\"Moderate\",0.334,IF(Q47=\"High\",0.678,IF(Q47=\"Extreme\",2.272,4.754)))))","v":0.05},{"$f":"IF(OR(P47=\"\",R47=\"\"),\"\",IF(AND(O47=\"within electric line construction area\",Q47=\"No forecast\"),1,P47*R47))","v":1.0000000000000002E-2},"INC-0021775","20230817PWA_02","Crew found fire on 3 phase FOLCB fIre services had already left the scene as fire extinguished itself on cross arm.\nThere was no ground fire or injuries",null,null," - overhead service conductor (residential)"]
[{"$f":"COUNTA(C48:O48,Q48,T48:V48)","v":17},11,"2023-08-18","13:27",-36.141796999999997,145.61256700000001,"108 Centre Rd, Invergordon VIC 3636, Australia","32182228","NKA001","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O48=\"\",\"\",IF(O48=\"LBRA only\",0.2,IF(O48=\"HBRA only\",1,IF(O48=\"within electric line construction area\",19.8,IF(O48=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"No rating",{"$f":"IF(Q48=\"\",\"\",IF(Q48=\"No rating\",0.05,IF(Q48=\"Moderate\",0.334,IF(Q48=\"High\",0.678,IF(Q48=\"Extreme\",2.272,4.754)))))","v":0.05},{"$f":"IF(OR(P48=\"\",R48=\"\"),\"\",IF(AND(O48=\"within electric line construction area\",Q48=\"No forecast\"),1,P48*R48))","v":1.0000000000000002E-2},"INC-0021795","20230821PWA_01","HV lead and an LA tail had made contact resulting in both of them being destroyed.",null,null," - overhead service conductor (commercial / industrial)"]
[17,12,"2023-08-24","19:14",-34.340518000000003,142.17292599999999,"360 Wilga Rd, Red Cliffs VIC 3496, Australia","31035887","RCT022","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","single phase","Started in or originated from a distribution system","HBRA only",1,"No rating",0.05,0.05,"INC-0022624","20231020PWA_02","Fire reported in meter board.\nboard, meters and fuses replaced\nno ground fire\nFound during outage data review",null,null," - overhead service conductor (subdivision / construction)"]
[17,13,"2023-09-04","07:19",-37.849106880000001,144.86834450000001,"87 Maddox road Williamstown North","33074942","BLT017","22kV AC","Urban"," - connector / termination","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0021959","20230905PWA_01","Ground fire found at base of pole, \nCrew found bridging connector had ruptured consistent with high fault current flow from bird-initiated fault downstream ",null,null," - overhead service conductor (other)"]
[17,14,"2023-09-08","08:00",-38.346226999999999,142.321775,"85 Survey Ln, Killarney VIC 3283, Australia","32198187","KRT022","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0022041","20230911PWA_01","Customer reported Pole to pole power line near road has snapped, power line is lying on the side road/nature strip and partially on road, crossarm and pole is on fire.\nCrew found pole 14 had burnt and/or broken at LV crossarm position",null,null," - underground service cable (residential)"]
[17,15,"2023-09-08","07:13",-38.338199000000003,142.33918199999999,"999 Princes Hwy, Tower Hill VIC 3283, Australia","31030123","KRT022","22kV AC","Rural Short"," - guy wire","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0022043","20230911PWA_02","a crew reported the guy wire red hot and now smoking on the ground -  later reported pole on fire.  \nStay apparently failed  and top section contacted HV fuse\nPole burnt at stay bolt position, isolated and extinguished by crew , \nsevere storm in progress",null,null," - underground service cable (commercial / industrial)"]
[17,16,"2023-09-08","18:16",-38.274976000000002,141.96518900000001,"54 Fergusons Rd, Codrington VIC 3285, Australia","31028725","KRT013","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0022047","20230911PWA_05","Fire at top crossarm of pole.",null,null," - underground service cable (subdivision / construction)"]
[17,17,"2023-09-08","17:52",-38.427852000000001,142.97336999999999,"Paddock opposite 355 Merretts Rd, Glenfyne.","30597314","TRG013","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0022048","20230911PWA_06","A customer and the emergency services reported a pole on fire and wires down at the incident location. On arrival the crew found that a SWER tee-off pole had burnt off near the top of the pole.",null,null," - underground service cable (other)"]
[17,18,"2023-09-13","08:21",-35.906720999999997,145.639037,"14 Schubert St, Cobram VIC 3644, Australia","31037763","CME015","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0022076","20230913PWA_02","Customer advised of LV supply box on fire. Upon arrival the crew found that FOLCB was burnt.\nThere was no reportable ground fire.",null,null,"Underground cables"]
[17,19,"2023-09-13","13:49",-36.033253999999999,145.99529000000001,"103 Benalla-Yarrawonga Rd, Yarrawonga VIC 3730, Australia","33082072","CME014","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0022088","20230913PWA_04","Emergency services reported of pole fire.\n\nUpon arrival the crew found that FOLCB was burnt.\nThere was no reportable ground fire.",null,null," - underground cable"]
[17,20,"2023-09-13","04:00",-38.237102,142.893102,"235 Terang-Framlingham Rd, Terang VIC 3264, Australia","33036073","TRG022","Low voltage AC (<1kV)","Rural Long"," - connection box","two phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0022093","20230914PWA_01","Crews were dispatched to a fault at the incident location.\nOn arrival the crew found that the 2 phase FOLCB had overheated and had been completely destroyed by fire, there was no ground fire as there is gravel around the base of the pole. \nThere were no reported injuries or third party damage.",null,null," - underground communications cable"]
[17,21,"2023-09-14","19:31",-37.313197000000002,144.587974,"35 Robertson Dr, Newham VIC 3442, Australia","33030594","WND013","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0022135","20230915PWA_02","Report received of sparks coming from transformer pole opposite house.\nOn arrival crew found a FOLCB on pole had caught fire and was totally destroyed.\nFire brigade onsite.\nMolten material at base of pole but no ground fire",null,null,"Poles"]
[17,22,"2023-09-17","08:00",-37.762748000000002,144.809889,"17 Gray Ct, St Albans VIC 3021, Australia","33075672","SU012","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0022166","20230918PWA_02","emergency services report fuse box at POA has caught fire and melted\n\nAttending Powercor fault crew found that there had been a fire at the 1-phase POA attached to the customer’s fascia.  The FOLCB and overhead service at the POA has been consumed by fire, and there is minor customer damage caused by the fire",null,null," - pole (concrete)"]
[17,23,"2023-09-24","17:00",-37.976812000000002,144.08067800000001,"418 Tall Tree Rd, Lethbridge VIC 3332, Australia","30251536","GHP011","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0022281","20230925PWA_01","Vic fire reported ground fire \nCrew found 1 Ha fire ignited near base of pole and suspected issue with FSD box",null,null," - pole (steel)"]
[17,24,"2023-09-25","15:28",-36.376595999999999,145.23079100000001,"880 Merrigum-Ardmona Rd, Tatura VIC 3616, Australia","32187595","MNA014","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0022290","20230926PWA_03","crew attended a reported fault.  \nUpon arrival crew made area safe and noted that the FOLCB on the pole at the dairy had caught fire and melted",null,null," - pole (wood)"]
[17,25,"2023-09-29","16:44",-36.298797,144.78092699999999,"510 Graham Rd, Nanneella VIC 3561, Australia","30152685","KYM001","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0022323","20231002PWA_01","Fire comms reported fire around pole at above address.  Crew arrived to find arcing at base of boric acid fuse and Ground fire at base of pole ",null,null,"Crossarms"]
[17,26,"2023-10-02","23:55",-38.482905000000002,143.60503800000001,"130 McDonalds Rd, Kawarren VIC 3249, Australia","30054861","CLC003","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within electric line construction area",19.8,"Moderate",0.33400000000000002,6.6132000000000009,"INC-0022372","20231004PWA_01","Upon arrival crew confirmed pole fire was out and that the LV Fuse was the cause of the fire and outage. FOLCB (fuse box) was brunt and melted, parts of it fell to the ground of the pole. Fire did not spread around the base of pole due to gravel. \n",null,null," - crossarm (wood)"]
[17,27,"2023-10-03","19:00",-37.904885999999998,144.24051600000001,"245-265 Durdidwarrah Rd, Anakie VIC 3213, Australia","32071133","GHP022","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0022378","20231004PWA_02","On arrival crew discovered the LV service out, burn marks on the pole from the FOLCB and small burn marks on the ground with melted components. \nThere was no reported injuries.",null,null," - crossarm (steel)"]
[17,28,"2023-10-03","18:16",-36.779530999999999,144.314831,"5 Chelsea Blvd, Strathdale VIC 3550, Australia","35097603","BGO013","Low voltage AC (<1kV)","Rural Short"," - pole (steel)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0022382","20231004PWA_03","Reports from vic fire of light column sparking and smoking.  On arrival, crew found failed circuit board behind public lighting column access panel.  \n No ground fires or injuries. ",null,null," - crossarm (other)"]
[17,29,"2023-10-03","09:52",-37.149717000000003,143.10933499999999,"44 C241, Crowlands VIC 3377, Australia","32089103","ART023","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0022390","20231005PWA_01","The crew reported that HV crossarm snapped, split bolt on the ends of the blue phase which burnt through the wood. This dropped insulator into the LV conductor, causing possible HVI. Crew also reported approximately 270 customers out. Broken pieces of wooden cross arm on the ground. No ground fire.",null,null,"Overhead assets"]
[17,30,"2023-10-04","04:15",-38.296987000000001,144.091129,"20 Karamarra Rd, Gherang VIC 3240, Australia","32067612","WIN022","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within electric line construction area",19.8,"Moderate",0.33400000000000002,6.6132000000000009,"INC-0022407","20231005PWA_05","On arrival crew confirmed cause of fire to be LV FOLCB, with burns on the pole around it and at the base of pole, with melted components on the ground.\nWet weather seems to have eliminated the fire around the base of pole. ",null,null," - capacity balancing units"]
[17,31,"2023-10-04","07:22",-37.820661999999999,144.785854,"183 State Route 40, Laverton North VIC 3026, Australia","84740325","LVN023","22kV AC","Urban"," - switch (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0022414","20231006PWA_02","customer reported large bang and sparking on corner of Fitzgerald/William Angliss Drive\ncrew found connection to 22kV switchgear damaged by overheating. ",null,null," - connector / termination"]
[17,32,"2023-10-05","21:14",-38.352612999999998,141.60762299999999,"4 Glenelg St, Portland VIC 3305, Australia","33056452","PLD004","Low voltage AC (<1kV)","Rural Short"," - lamps (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0022463","20231010PWA_01","Crew restoring supply after replacing faulty FSD identified watchman lighting had caught fire. \nThe ignition was believed to have occurred at the external PE control",null,null," - dropper / bridge"]
[17,33,"2023-10-10","09:12",-37.488289999999999,144.59099699999999,"42B Aitken St, Gisborne VIC 3437, Australia","30031820","GSB011","Low voltage AC (<1kV)","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0022498","20231012PWA_04","LV Bridge from ABC to Isolator was sparking arcing until parted sent molten plastic to ground.\nCrews found no presence of fire only some charred insulation at base of pole ",null,null," - guy wire"]
[17,34,"2023-10-17","21:46",-37.731814,144.57639699999999,"2 Waterway Blvd, Weir Views VIC 3338, Australia","30104930","MLN032","Low voltage AC (<1kV)","Rural Short"," - lamps (major road)","single phase","Started in or originated from a distribution system","HBRA only",1,"No rating",0.05,0.05,"INC-0022582","20231018PWA_01","Small grass fire extinguished by CFA.",null,null," - insulator tie wires / connections"]
[17,35,"2023-10-17","07:52",-38.751213999999997,143.665977,"17 Murray St, Apollo Bay VIC 3233, Australia","30280603","CLC013","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0026285","20240701PWA_08","Cust reported smoke and flame coming from outside property. Flame was orange was constant but has now stopped. Pole was also making a buzzing noise\nCrew found deteriorated HV insulated leads",null,null," - insulators"]
[17,36,"2023-10-19","15:13",-37.680968,144.67308,"1498 Melton Hwy, Plumpton VIC 3335, Australia","33075166","MLN021","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0022616","20231020PWA_01","Crew Replaced faulty transformer.\nOn energisation sparks from emanated from faultily isolator igniting grass stubble at base of pole.\nFire self extinquished.\nThere was no reported injuries.",null,null," - tower"]
[17,37,"2023-10-24","20:28",-38.162018000000003,144.42884000000001,"72 Point Henry Rd, Moolap VIC 3224, Australia","32076475","GLE031","22kV AC","Rural Short"," - pole (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0022691","20231026PWA_01","Car hit pole and snapped it. It broke the guy which made contact with the LV and fence causing a ground fire.\nthere was a ground fire and fatality(non electrical)",null,null," - traction lines"]
[17,38,"2023-10-30","13:17",-35.659218000000003,144.11435599999999,"2146 Kerang-Koondrook Rd, Koondrook VIC 3580, Australia","33017321","KGT003","22kV AC","Rural Long"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0022738","20231031PWA_02","Bird induced flashover between HV conductor and metal crossarm.\nMolten particles fell to ground and started a grass fire.\nThere were no reported injuries",null,null,"Underground assets"]
[17,39,"2023-11-02","04:09",-36.038471000000001,145.280664,"682 Centre Rd, Waaia VIC 3637, Australia","33081659","NKA006","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0022811","20231103PWA_02","Report received of grass fire and conductor on ground.\nOn arrival crew found centre phase conductor had failed striking the ground and causing a grass fire.\nThere was no reported injuries.\n",null,null," - LV pillar"]
[17,40,"2023-11-04","19:19",-38.135370999999999,144.31800100000001,"8 Ingrid Ct, Herne Hill VIC 3218, Australia","30546526","GL014","22kV AC","Urban"," - fuse (powder filled)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0022846","20231108PWA_01","Pole fire start no ground fire, tracking.",null,null," - services pit"]
[17,41,"2023-11-04","19:08",-37.342275000000001,144.14765,"6 Daly St, Daylesford VIC 3460, Australia","30148312","BAN008","Low voltage AC (<1kV)","Rural Long"," - overhead conductor (ABC)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0022847","20231108PWA_02","The fire brigade extinguished a small fire at the base of the pole LIS: 945221. ",null,null,"Transformers"]
[17,42,"2023-11-07","21:39",-37.787539000000002,144.803282,"212 Glengala Rd, Sunshine West VIC 3020, Australia","32164858","SU035","22kV AC","Urban"," - switch (any other type)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026334","20240703PWA_02","Cust adv pole opposite this address had flames up the top of it for about 5 mins, no longer on fire. Strong electrical burning smell. Unsure if cause of outage\nAttending crew found damaged gas switch and hv isolators damaged by lightning.",null,null," - transformer (pole mounted)"]
[17,43,"2023-11-08","21:00",-37.830748999999997,144.84322800000001,"Unit 7/414 Blackshaws Rd, Altona North VIC 3025, Australia","30114530","BLTS-TYA","66kV AC","Urban"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0022881","20231109PWA_01","66 KV Pole fire potentially due to lightning, fire brigade on site.\nInsulators detached, 66 KV hanging low.\nNo ground fire or injuries reported.",null,null," - transformer (kiosk mounted)"]
[17,44,"2023-11-10","13:40",-36.307032,144.76263499999999,"564 Christie Rd, Nanneella VIC 3561, Australia","32182720","KYM001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0022925","20231113PWA_02","CFA requested attendance to fire and wire down at intersection of Christie Road and Bennett Road, Fairy Dell (Rochester)\nCrew found termination crossarm at LIS 22954 Wiloglen P4 broken at disk insulator causing wire to fall to ground causing fire to paddock (180m x116m) roughly 40 Large round Hay bales and 100m of fencing.",null,null," - transformer (ground outdoor mounted)"]
[17,45,"2023-11-12","16:42",-35.253174999999999,141.59531999999999,"617 Boinka South Rd, Boinka VIC 3490, Australia","32141529","OYN001","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0022939","20231113PWA_05","Header/Tractor hit SWER pole knocking it over, starting 10m x 10m grass fire, protection operated",null,null," - transformer (indoor chamber mounted)"]
[17,46,"2023-11-14","07:44",-36.482273999999997,142.61461199999999,"Knapdale, 5846 Stawell-Warracknabeal Rd, Minyip VIC 3392, Australia","30084530","STL006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0022968","20231114PWA_01","T-off crossarm fire. Resulted in fallen 22kV conductor on the ground. \nNo ground fire. \nProtection operated.",null,null," - transformer (any other type)"]
[17,47,"2023-11-14","07:52",-36.253366,142.38505599999999,"9 C234, Warracknabeal VIC 3393, Australia","32115450","HSM005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0022972","20231114PWA_02","HV crossarm fire due to dust on insulator. No ground fire.  No photos provided by crew.",null,null," - measurement transformer (current transformer)"]
[17,48,"2023-11-14","08:53",-36.51258,142.33619999999999,"2695 Henty Hwy, Jung VIC 3401, Australia","32094206","HSM005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0022973","20231114PWA_03","Wood crossarm fire has resulted in 22kV conductor and attached insulator falling off the crossarm and hanging approx. 3 feet of a metal fence. (Protection did not operate). There was no shocks. Pole top fire only - no ground fire. ",null,null," - measurement transformer (voltage transformer)"]
[17,49,"2023-11-16","23:40",-36.759450000000001,144.22529900000001,"12 Lupson Ct, Maiden Gully VIC 3551, Australia","33012057","BET006","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0023016","20231120PWA_01","Fire comms reported fire associated with Powercor assets at the incident location.\nBendigo fault crew found that large tree had leaned onto 22kV conductors of the BET006 feeder in proximity to LIS 429058.\nTree base is located 10M from line.\nContact with HV resulted in several branches burning, several recloses on feeder CB before controlled interruption to trim offending branches.\nNo ground fire as a result on the incident.",null,null," - measurement transformer (capacitive voltage transformer)"]
[17,50,"2023-11-19","07:04",-37.532850000000003,144.055048,"250 Ormond Rd, Springbank VIC 3352, Australia","33003778","BAN003","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0023025","20231120PWA_03","Emergency services reported that a pole fire caused a grass fire. \nAttending crew reported that the FOLCB had failed, causing the grass to catch fire.  \nBurn area <1m2.  Fire was extinguished prior to the crew's attendance.",null,null,"Fuses and switchgear"]
[17,51,"2023-11-22","20:43",-36.411973000000003,145.090136,"375 Brewer Rd, Cooma VIC 3616, Australia","30247157","SHP014","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0023104","20231124PWA_02","Part supply notifications from customers resulted in Shepparton fault crew undertaking a line patrol, discovering a large tree have come down over 22kV conductors at the incident location. Crew found large tree which failed at the root plate coming down over 22kV conductors between P8 Cornish and P9 Cornish, tree base was 15.0M from line.\nGround fire resulted from downed conductors, 6M x 8M in size, which largely self extinguished however crew called CFA to come and douse to ensure any embers would not reignite the crop the fire occurred in.",null,null," - fuse (boric acid)"]
[17,52,"2023-11-23","07:14",-37.655349000000001,144.45062100000001,"20 Lerderderg Park Rd, Merrimu VIC 3340, Australia","33075941","MLN022","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0023090","20231123PWA_02","CFA reported truck pulled wires down, has started a grass fire at cnr gisborne rd & albert st - \nattending crew found an overhead service and HV conductors had been brought down and a small ground fire ensued.",null,null," - fuse (EDO fuse)"]
[17,53,"2023-11-24","14:25",-38.383114999999997,142.482136,"169 Koroit St, Warrnambool VIC 3280, Australia","34034281","WBL008","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0023119","20231127PWA_02","Fire Coms advised 3 phase power box on side of building on fire. Crew found an open point facade mounted FSD had caught fire and CFA had extinguished.\nLocal media in attendance",null,null," - fuse (Fault Tamer)"]
[17,54,"2023-11-24","17:57",-35.944904000000001,144.37342899999999,"104 Gunbower Island Rd, Gunbower VIC 3566, Australia","32034925","CHA005","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0023123","20231127PWA_03","Report of tree fire due to contact with HV. \nCrew arrived to find tree branches had made contact with HV bare conductor.\n\n",null,null," - fuse (powder filled)"]
[17,55,"2023-11-28","18:05",-38.230015000000002,142.80091899999999,"260 Dairy Ln, Terang VIC 3264, Australia","30555030","TRG022","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0026342","20240703PWA_05","customer advised Smaller box below the TF was on fire, but now out. ",null,null," - fuse (any other type)"]
[17,56,"2023-11-29","15:16",-36.240293999999999,142.397524,"Ross St, Warracknabeal VIC 3393, Australia","33050983","HSM003","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0023191","20231130PWA_03","Fire services advised of a fire at the location.\n\nUpon arrival the crew found that blue phase of LV isolator was burnt and a ground fire near the base of the pole of approximately 64m2 (8 x 8).",null,null," - circuit breaker"]
[17,57,"2023-11-29","20:59",-37.655810000000002,144.60165799999999,"Cnr Gisborne Melton Rd and Nuspan Ct, Kurunjang","30105497","MLN012","Low voltage AC (<1kV)","Rural Short"," - luminaires (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0023204","20231201PWA_01","Report received of street light on fire with fire brigade on scene to address matters. Upon arrival the fault crew found that the light head cover of the 150W HPS luminaire attached to the outreach bracket at substation pole \"GISB MLTN-NUSPAN\" on LIS-933488 had melted as a result of the incident.",null,null," - switch (disconnector/isolator)"]
[17,58,"2023-12-02","10:31",-37.820563,144.786473,"183 State Route 40, Laverton North VIC 3026, Australia","30241121","LVN034","Low voltage AC (<1kV)","Urban"," - lamps (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0023253","20231204PWA_02"," Vic Roads reported a pole fire at Corner of Gilbertson Rd and Fitzgerald Rd, LAVERTON.\n A Powercor employee was on site, he advised that the pole was a VicRoads pole and the public lighting cable was damaged.\n\n On arrival, the Faults crew found that the wiring inside the public lighting Pole 998858 (JUP) had caught fire and the P/L cable, fuses, traffic lights panel and the wiring had melted.\nThe crew advised that the cables sparking and fire was most likely caused by the raining water entering inside the pole.\nThe fire was contained inside the pole and extinguished by itself. ",null,null," - switch (earth)"]
[17,59,"2023-12-02","04:04",-38.328232999999997,142.36601999999999,"Tower Hill Park Boundary, Entrance Rd, Tower Hill VIC 3283, Australia","30135013","KRT022","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0023254","20231204PWA_03"," Crew   patrolling line  to investigate an outage found crossarm had burnt and conductor fallen to ground.",null,null," - switch (FuseSaver)"]
[17,60,"2023-12-04","19:02",-37.773009000000002,144.80949200000001,"4C Carrington Dr, Albion VIC 3020, Australia","30116083","SU022","22kV AC","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0023266","20231205PWA_01"," Vic Fire reported overhead lines burnt on a pole outside 11 Carrington Drive, Sunshine and advised that there is a Transformer nearby.\n\nOn arrival the Powercor crew found that IPC’s on pole LIS-26132 had overheated and the sparking resulted in a ground fire inside customer’s property at 13 Carrington Drive.  \nThe fire brigade was on site and extinguished the fire before the crew arrived.",null,null," - switch (any other type)"]
[17,61,"2023-12-07","06:47",-36.427377999999997,145.32097899999999,"275 Pyke Rd, Mooroopna VIC 3629, Australia","33091691","MNA021","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0023337","20231208PWA_03","A fruit bat has caused a flashover between EDO fuse flex and bracket. \nThis has caused burning particles to fall to the ground and start a very small grass fire",null,null,"SCADA, network control and protection systems"]
[17,62,"2023-12-07","14:10",-38.164760000000001,144.579386,"20 Hutchinson Ct, Drysdale VIC 3222, Australia","30067546","DDL021","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0023340","20231208PWA_04","Junction Box failure started pole fire which then resulted in a grass fire below the pole.",null,null," - audio frequency load controller (AFLC)"]
[17,63,"2023-12-08","14:13",-35.990475000000004,144.31870499999999,"912 Gunbower-Pyramid Rd, Gunbower VIC 3566","32038643","CHA005","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0023348","20231208PWA_06","Initial description is Broken wires causing pole fire and grass fire.",null,null," - arc suppresion coil"]
[17,64,"2023-12-11","14:10",-35.975926000000001,142.41009099999999,"3155 Henty Hwy, Beulah VIC 3395, Australia","30143277","HSM003","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Extreme",2.2719999999999998,2.2719999999999998,"INC-0023360","20231212PWA_01","Fire comms reported pole fire / started grass fire - on Henty highway.\nAttending crew found pole had broken mid section with the top section falling to ground. a small ground fire  occurred.\n",null,null," - automatic circuit recloser (ACR)"]
[17,65,"2023-12-12","19:24",-37.253152,144.42446000000001,"163 Harts Ln, Kyneton VIC 3444, Australia","33030133","WND014","22kV AC","Rural Short"," - surge diverter","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0023388","20231213PWA_01","Firecomms reported ground fire due to Powercor asset at the incident location. Upon arrival fault crew found that a porcelain Surge diverter had failed, resulting in the live end making contact with transformer tank and the resultant arc dropped molten material to the ground.",null,null," - communications linear assets"]
[17,66,"2023-12-12","20:58",-38.378987000000002,142.47778299999999,"67 Henna St, Warrnambool VIC 3280, Australia","30137324","WBL010","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026440","20240709PWA_01","Powercor was advised of a Power box on pole on fire outside 67 HENNA STREET,WARRNAMBOOL, VIC,3280",null,null," - communications network assets"]
[17,67,"2023-12-13","10:01",-36.025495999999997,145.24537699999999,"222 Evans Rd, Nathalia VIC 3638, Australia","30600638","NKA006","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45439999999999997,"INC-0023420","20231214PWA_03","Firecomms reported a pole fire \nAttending crew found a HV fuse had malfunctioned and a ground fire developed",null,null," - communications site infrastructure"]
[17,68,"2023-12-18","18:50",-37.685211000000002,144.085205,"49 Magnus Ln, Bungal VIC 3334, Australia","33004267","BAN003","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0023472","20231219PWA_01","Single phase fuse box burnt, fell to the ground and started small grass fire.",null,null," - field devices"]
[17,69,"2023-12-23","10:12",-35.720353000000003,143.91974200000001,"27 Ninth Street, Kerang 3579","32036926","KGT002","22kV AC","Rural Short"," - pole (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0023570","20231228PWA_01","Car hit power pole taking down pole with HV, and LV.  Pole, crossarms as well as crossarms on adjacent poles damaged.  HV and LV conductors came down together.  Feeder tripped.\nIncident cause a small grass fire 100-150msq.  \nDriver taken to hospital by ambulance",null,null," - local network wiring assets"]
[17,70,"2023-12-24","14:10",-34.761341999999999,142.97152299999999,"1633 MURRAY VALLEY HIGHWAY Lake Powell","30245132","BBD013","22kV AC","Rural Short"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0023575","20231228PWA_05","Bat has landed on HV line and caused a fault on BA fuse unit over night. Customer noticed outage in the morning. Approx. 150msq grassfire started as a result of the fault",null,null," - master station assets"]
[17,71,"2023-12-24","12:15",-38.102829,143.638001,"45 Reddies Rd, Cressy VIC 3322, Australia","30052740","CLC006","22kV AC","Rural Long"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0023579","20231228PWA_08","Emergency services were requested to attend to a pole hit by lightning, six (6) poles North of the intersection of Reddies Rd and Barpinba Rd, Cressy. This event started a grassfire at the base of pole 148, \nOn arrival crew noted the fire was extinguished, assumed to be by emergency service, whom were not at the scene.  Burn marks on the side of the pole top to bottom and around the base of the pole. Fire effected area is grass in the road reserve, approx.10m radius around pole \n\nunknown  if  network involved or  pole in vicinity of strike TBC ",null,null," - neutral earthing resistor"]
[17,72,"2023-12-25","05:36",-36.426454,144.99374800000001,"347 Morrissey Rd, Stanhope VIC 3623, Australia","30145083","SHP012","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026443","20240709PWA_03","Customers advised transformer on pole at rd side was on fire, cfa attended and put fire out, fuses are down on pole also, supply is off. \nCrew found transformer damaged by lightning",null,null," - oil-filled circuit recloser (OCR)"]
[17,73,"2023-12-25","07:26",-36.291255,144.56285,"84 Vise Rd, Bamawm VIC 3561, Australia","31025704","SHP012","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026444","20240709PWA_04","customers reported outage \nattending crew found LV box and leads burnt after lightning struck",null,null," - rapid earth fault current limiter (REFCL)"]
[17,74,"2023-12-26","14:36",-37.667206,144.58384799999999,"2 Thrice Ln, Kurunjang VIC 3337, Australia","30119541","MLN032","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0023572","20231228PWA_03","Lighting Struck an 22kV OH Line.\n\nOn arrival to site the PCA Faults Crew advised that a Lightning Strike has resulted in HV OH Conductor falling to the ground below.\nTwo pole type substations were ignited and a further two were destroyed.",null,null," - surge diverter"]
[{"$f":"COUNTA(C112:O112,Q112,T112:V112)","v":17},75,"2023-12-26","16:47",-35.242522000000001,143.485071,"1344 Murray Valley Hwy, Beverford VIC 3590, Australia","32160709","SHL004","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O112=\"\",\"\",IF(O112=\"LBRA only\",0.2,IF(O112=\"HBRA only\",1,IF(O112=\"within electric line construction area\",19.8,IF(O112=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Moderate",{"$f":"IF(Q112=\"\",\"\",IF(Q112=\"No rating\",0.05,IF(Q112=\"Moderate\",0.334,IF(Q112=\"High\",0.678,IF(Q112=\"Extreme\",2.272,4.754)))))","v":0.33400000000000002},{"$f":"IF(OR(P112=\"\",R112=\"\"),\"\",IF(AND(O112=\"within electric line construction area\",Q112=\"No forecast\"),1,P112*R112))","v":6.6800000000000012E-2},"INC-0023577","20231228PWA_07","Customer reported burnt out switchboard. \n Upon arrival crew found meter panel burnt and had self-extinguished.\n",null,null," - voltage regulator"]
[17,76,"2023-12-27","00:49",-36.269376000000001,145.02959000000001,"899 Matheson Rd, Kyvalley VIC 3621, Australia","30146221","KYM004","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0023576","20231228PWA_06","Emergency services requested Powercor attendance at a grass fire near pole\nUpon arrival crew found EDO fuse above origin of fire had operated.  ",null,null,"Public lighting"]
[17,77,"2023-12-27","14:04",-38.726010000000002,143.70782199999999,"1 Motts Ln, Skenes Creek VIC 3233, Australia","30562684","CLC013","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0023580","20231228PWA_09","Call reporting burning of a pole top asset at the address.\n On arrival, Crew confirmed burnt HV dropper lead to Transformer on Pole 594E",null,null," - brackets (major road)"]
[17,78,"2024-01-01","06:55",-34.754866,143.03224,"548 Paul Ln, Boundary Bend VIC 3599, Australia","30225997","BBD014","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0023601","20240102PWA_01","Reports of no supply and fuse down at above address.  \nOn arrival, crew found ground fire and evidence of flashover.  \nCrew reported there had been a bat stuck behind the HV fuse mount.",null,null," - brackets (minor road)"]
[17,79,"2024-01-02","19:31",-36.304533999999997,145.01381000000001,"1367 Peppertree Ln, Kyabram VIC 3620, Australia","30250390","KYM006","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026475","20240709PWA_09","Report of crossarm fire\ncrew fouind burnt out junction box\nno ground fire\nfound during Outage data review\nno photos found",null,null," - lamps (major road)"]
[17,80,"2024-01-03","13:34",-35.474502999999999,143.46161499999999,"Lake Boga-Ultima Rd, Goschen VIC 3585, Australia","32156307","SHL001","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0026477","20240709PWA_10","TX LEAKING OIL needs replacing, possibly blown caused a fire.\nFound during OMS data review",null,null," - lamps (minor road)"]
[17,81,"2024-01-04","10:57",-35.692151000000003,142.61685800000001,"1761 Hopetoun-Sea Lake Rd, Woomelang VIC 3485, Australia","31022184","OYN005","12.7kV AC (SWER)","Rural Long"," - fuse (boric acid)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0023629","20240104PWA_01","Fire brigade report states pole has caused grass fire\nAttending crew found boric acid fuse had malfunctioned and a ground fire occurred.",null,null," - luminaires (major road)"]
[17,82,"2024-01-05","02:37",-34.136645000000001,142.03056599999999,"554 Wentworth Rd, Merbein VIC 3505, Australia","33064909","MBN013","22kV AC","Rural Short"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0023637","20240105PWA_01","crew attending fault identified a small grassfire at base of pole. Fire had self extinguished",null,null," - luminaires (minor road)"]
[17,83,"2024-01-06","13:20",-38.207360999999999,144.45144500000001,"361 Melaluka Rd, Leopold VIC 3224, Australia","30595774","GLE024","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0023648","20240108PWA_01","Customer advised pole LIS 135406 is currently on fire and fire brigade on site.\nOn arrival crew found an LV fuse box had caught fire and melted. \nCFA had extinguished. No ground fire.",null,null," - poles / columns (major road)"]
[17,84,"2024-01-06","07:36",-35.235970000000002,143.456312,"244 School Rd, Beverford VIC 3590, Australia","33070419","SHL004","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026478","20240709PWA_11","Report of supply interruption\ncrew found EDO fuse barrel burnt and on ground\nno ground fire\nFound during Outage data review",null,null," - poles / columns (minor road)"]
[17,85,"2024-01-07","10:02",-36.218124000000003,143.89745099999999,"Ellerslie Rd, Fernihurst VIC 3518, Australia","30300397","CTN002","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0026599","20240716PWA_04","Nephew on site something on pole has caught on fire (sounds like a box of some sort)\nFire is out\nno ground fire\nFound during Outage data review\nno photos located",null,null,"Other "]
[17,86,"2024-01-07","01:01",-36.707462,141.188109,"Bulls and Blacks Rd, Minimay VIC 3413, Australia","30620522","HSM004","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0026602","20240716PWA_05","Pole hit by lightening and burnt off, wet around pole   Pole 1 - holding the\nline side conductor up by tie  Pole 2 - conductor on pole.\nno ground fire\nFound during Outage data review",null,null," - connection box"]
[17,87,"2024-01-12","08:09",-38.459674,144.09307100000001,"Koninderie, 60 Bimbadeen Dr, Fairhaven VIC 3231, Australia","32070192","TQY021","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0026606","20240716PWA_06","FOLCB on pole end burnt and melted.\nNo ground fire\nFound during Outage data review",null,null," - earth / earthing"]
[17,88,"2024-01-13","10:29",-36.024782999999999,145.31345899999999,"1124 Tyacks Rd, Waaia VIC 3637, Australia","30126451","NKA006","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","single phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0023749","20240115PWA_01","Customer reports of all supply fail resulted fault crew being dispatched to the incident location. Upon arrival crew found that a LV XLPE service cable had been brought down by an unknown 3rd party and a ground fire of approx 10M x 100M in size.\nOne customer also had POA damage and was left off supply pending REC repair."]
[17,89,"2024-01-14","14:57",-38.001111999999999,141.81916000000001,"48 Camerons Ln, Breakaway Creek VIC 3303, Australia","30092785","HTN011","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0026609","20240716PWA_07","Box on pole approx. 2 metres off the ground appears burnt, and blackening on pole goes down to ground level.\nno ground fire\nFound during Outage data review"]
[17,90,"2024-01-15","13:11",-37.771327999999997,144.787791,"760 Ballarat Rd, Deer Park VIC 3023, Australia","30341178","SU021","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0023788","20240117PWA_01","Reporting pole to pole cable has come down and is on the ground. Also advised on top of the pole end there is a FIRE on the wire.\nCrew found IPC connection on LV had failed causing conductor to fall with supply end remaining aloft",null,null,"Extra low voltage AC (<50V)"]
[17,91,"2024-01-17","16:21",-38.160744000000001,144.56775300000001,"18 Barringup Ave, Clifton Springs VIC 3222, Australia","30269501","DDL022","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026610","20240716PWA_08","Replaced burnt out 400amp fsd\nno ground fire\nno photos\nfound during Outage data review",null,null,"Low voltage AC (<1kV)"]
[17,92,"2024-01-20","15:44",-37.052419,143.81170399999999,"Carisbrook Leisure Centre, 15 Landrigan Rd, Carisbrook VIC 3464, Australia","32029203","MRO007","Low voltage AC (<1kV)","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0023867","20240123PWA_01","Emerg services advise truck has brought down wires at intersection of Landrigan Road and Marion Lane, Carisbrook, across from Primary School. May have potentially created small grass fire. Truck has left scene and also reports of damage at Victoria Street.",null,null,"2.2kV AC"]
[17,93,"2024-01-20","21:39",-34.343764,142.32109800000001,"449 Johns Way, Red Cliffs VIC 3496, Australia","31021134","RCT014","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0023880","20240123PWA_02","Firecom reports customer call stating Grass fire at 449 Johns Way Red cliffs.\nCrew found Pelican has hit line, conductor on ground",null,null,"6.6kV AC"]
[17,94,"2024-01-20","03:02",-35.255228000000002,143.435732,"28 Pompy Ln, Woorinen North VIC 3589, Australia","32159601","SHL002","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0026624","20240717PWA_03","candleing hv EDO fuse due to water ingress\nno ground fire\nno photos taken\nfound during outage data review",null,null,"11kV AC"]
[17,95,"2024-01-21","02:29",-37.864820000000002,144.76988299999999,"83 Railway Ave, Laverton VIC 3028, Australia","33072703","LVN022","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026634","20240717PWA_07","FSD burn out - Outage data review\nno ground fire\n",null,null,"12.7kV AC (SWER)"]
[17,96,"2024-01-24","03:39",-37.586601000000002,143.82569599999999,"16 Macquarie Cl, Delacombe VIC 3356, Australia","30002708","BAS022","22kV AC","Rural Long"," - insulators","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0023909","20240125PWA_01","Crew advised pole struck by lightning , Fire started at base of pole.",null,null,"22kV AC"]
[17,97,"2024-01-24","14:14",-38.531827,142.79589799999999,"Four Winds, 2594 Great Ocean Rd, Nirranda South VIC 3268, Australia","30137236","WBL012","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0023913","20240125PWA_02","Lightning strike hit line and line parted falling to ground causing small ground fire",null,null,"33kV AC"]
[17,98,"2024-01-24","05:00",-37.993659000000001,143.18748400000001,"52 McLeod Rd, Derrinallum VIC 3325, Australia","30050040","CDN006","22kV AC","Rural Long"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0023926","20240129PWA_02","An outage was reported so a crew was dispatched to patrol the area to find the cause, this was after a thunderstorm event on the morning of 24th January. The crew reached pole  GEELENGA 19 and found that it had (most likely) been struck by lightning, causing a 5m x 5m ground fire at the base of the pole.",null,null,"66kV AC"]
[17,99,"2024-01-24","17:05",-38.090760000000003,142.33681899999999,"141 Minjah-Hawkesdale Rd, Hawkesdale VIC 3287, Australia","32197639","KRT013","22kV AC","Rural Long"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0026636","20240717PWA_08","Transformer has exploded. Parts of transformer on ground with burnt grass around.\nLightning in area\nOutage data review\nno photos provided",null,null,"132kV AC"]
[17,100,"2024-01-25","10:30",-38.179400000000001,144.38968499999999,"230 Wilsons Rd, Whittington VIC 3219, Australia","30297658","GLE013","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026651","20240718PWA_01","3 phase n/screen service insulation failed. Due to junction box fusing arrangement Powercor is required to replace box. \nLiaising with REC to replace box on Powercor s behalf. REC will make contact when repairs are complete 20m of 35mm 3 phase XLPE service cable required\nNo ground fire\nOutage data review\nno photos",null,null,"220kV AC"]
[{"$f":"COUNTA(C138:O138,Q138,T138:V138)","v":17},101,"2024-01-27","22:15",-38.281286000000001,141.65265299999999,"120 Uniting Church Camp Rd, Allestree VIC 3305, Australia","32133068","PLD001","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","single phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O138=\"\",\"\",IF(O138=\"LBRA only\",0.2,IF(O138=\"HBRA only\",1,IF(O138=\"within electric line construction area\",19.8,IF(O138=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"Moderate",{"$f":"IF(Q138=\"\",\"\",IF(Q138=\"No rating\",0.05,IF(Q138=\"Moderate\",0.334,IF(Q138=\"High\",0.678,IF(Q138=\"Extreme\",2.272,4.754)))))","v":0.33400000000000002},{"$f":"IF(OR(P138=\"\",R138=\"\"),\"\",IF(AND(O138=\"within electric line construction area\",Q138=\"No forecast\"),1,P138*R138))","v":0.33400000000000002},"INC-0023923","20240129PWA_01","Customer reported switchboard on fire and power flickering. On arrival crew found the service fuse and some wiring insulation had melted due to overheating. There was also evidence the fuse had been smoking which was also witnessed by the CFA. ",null,null,"330kV AC"]
[{"$f":"COUNTA(C139:O139,Q139,T139:V139)","v":17},102,"2024-01-28","12:07",-36.254658999999997,144.931839,"2121 Finlay Rd, Tongala VIC 3621, Australia","33091576","KYM006","22kV AC","Rural Short"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",{"$f":"IF(O139=\"\",\"\",IF(O139=\"LBRA only\",0.2,IF(O139=\"HBRA only\",1,IF(O139=\"within electric line construction area\",19.8,IF(O139=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Moderate",{"$f":"IF(Q139=\"\",\"\",IF(Q139=\"No rating\",0.05,IF(Q139=\"Moderate\",0.334,IF(Q139=\"High\",0.678,IF(Q139=\"Extreme\",2.272,4.754)))))","v":0.33400000000000002},{"$f":"IF(OR(P139=\"\",R139=\"\"),\"\",IF(AND(O139=\"within electric line construction area\",Q139=\"No forecast\"),1,P139*R139))","v":6.6800000000000012E-2},"INC-0023928","20240129PWA_03","CFA reported ground fire in vicinity of Powercor asset at the incident location. Upon arrival Shepparton fault crew found that 2 crows have caused a flashover on P122 KYM ECA 2, on KYM6 subsidiary circuit.\nGround fire of approximately 75M x 55M resulted due to ignited bird remnants falling to ground, some minor damage to adjoining properties boundary fence.",null,null,"500kV AC"]
[17,103,"2024-02-06","05:00",-37.572102999999998,142.63399999999999,"Maroona-Glenthompson Rd, Stavely (near corner of Stavely Rd)","30552698","ART033","22kV AC","Rural Long"," - switch (any other type)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024073","20240206PWA_02","fire communications reported a grass fire. \nCrew in attendance reported that a NGK Gas Switch flashed over between the red and blue phases.  Two sheds broken on each insulator.  \nFlashover potentially caused by bird (non-found) or moisture as it was damp. ",null,null,"Extra low voltage DC (<120V ripple free)"]
[17,104,"2024-02-07","15:09",-36.721499999999999,144.246746,"22 Crowther St, Eaglehawk VIC 3556, Australia","30024927","BET006","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024109","20240208PWA_01","Fire service reported that a sparking wire caused grass fire outside property.\n\nUpon arrival the crew found that a service wire insulation was impacted by a tree resulting in approximately 5m2 ground fire. ",null,null,"Low voltage DC (<1.5kV)"]
[17,105,"2024-02-09","18:42",-35.728853999999998,143.10669100000001,"40 Railway St, Culgoa VIC 3530, Australia","33016140 & 32026313","CTN003","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.67800000000000005,3.1187999999999998,"INC-0024149","20240212PWA_02","Firecom reported grassfire possibly started by PCA assets.\nUpon arrival crew found that a tipper truck had made contact with the HV O/H.\nConductors initiated approx 0.2 HA grass fire.\nThere were no reported injuries.",null,null,"600V DC"]
[17,106,"2024-02-10","07:45",-37.384901999999997,143.980345,"T Mays Rd, Newlyn VIC 3364, Australia","33001193","BAN009","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024152","20240212PWA_03","Vic fire reported a fire near the corner of T may rd and G May rd Newlyn, the fault crew on arrival found an EDO tube had candled and fallen to the ground starting a small fire along the roadside.\nThe fire was extinguished, and the fire truck had left the scene.",null,null,"1500V DC"]
[17,107,"2024-02-10","03:02",-37.786487000000001,144.66185899999999,"738 Troups Rd S, Mount Cottrell VIC 3024, Australia","32177875","TNA022","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0024154","20240212PWA_04","Report of crossarm failure.\nOn arrival crew found tracking had resulted in crossarm being burnt through at strap bolt.\nHV fell into LV below.\nThere was no ground fire or reported injuries.",null,null,"Earthing cable"]
[17,108,"2024-02-11","16:07",-37.870573,144.80556000000001,"32 Kookaburra St, Altona VIC 3018, Australia","32167630","AL006","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024160","20240212PWA_05","Following supply issues a crew found a burnt off copper to aluminium T clamp.\nThere was hot molten material dropped to ground scorching a small patch of grass.\nThere was no reported injuries."]
[17,109,"2024-02-11","18:48",-37.866334000000002,144.78784200000001,"2A Valente St, Altona Meadows VIC 3028, Australia","33075201","LVN022","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024176","20240213PWA_02","Customer reported Tx out front of their property exploded, seen flames and now just smoke and fire brigade onsite. Upon arrival, crew found IPC connector overheated resulted in small grass fire at the base of pole."]
[17,110,"2024-02-13","17:22",-35.306094999999999,143.55122800000001,"92 Murraydale Rd, Swan Hill VIC 3585, Australia","30276240","SHL004","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45439999999999997,"INC-0024226","20240215PWA_01","Powercor received a report from CFA that vegetation had caught fire outside of 92 Murraydale Road, Swan Hill. CFA extinguished fire. No reports of grassfire.\nAttending crews found  a branch had snapped and this branch had evidence of severe scorching.  One conductor had parted  and fallen to ground. No evidence was found of grass/ground fire.\n\n",null,null,"single wire earth return (SWER)"]
[17,111,"2024-02-13","15:47",-36.335321,144.23233200000001,"Bendigo-Pyramid Rd, Dingee VIC 3571, Australia","32041033","EHK024","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Extreme",2.2719999999999998,10.451199999999998,"INC-0024233","20240215PWA_04","HV wire down reported on LIS-350311.\n2 bays of conductor, road side and centre have been brought down by a tree falling onto them.\nThere was a ground fire, 24m x 130m.\n ",null,null,"single phase"]
[17,112,"2024-02-13","14:56",-36.012825999999997,143.46742900000001,"50 Boyds Rd, Jeruk VIC 3527","32022324","CTN001","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Extreme",2.2719999999999998,10.451199999999998,"INC-0024260","20240216PWA_04"," Branch from Big red gum tree has fallen on conductor in between Tunstall p2 lis 601905 and p3 lis 601906. BA fuse is open and sitting at base of pole at sw 27098 jeruk east p8\n Swer conductor down\nCrew identified small ground fire beneath fallen conductor. \n",null,null,"two phase"]
[17,113,"2024-02-14","11:37",-37.077092,144.727293,"1615 Dairy Flat Rd, Tooborac VIC 3522, Australia","30148829","BGO023","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024237","20240215PWA_05","Pole struck by lightning\nresulted in pole being damaged and grass fire\nno reported injuries",null,null,"three phase"]
[17,114,"2024-02-14","11:05",-38.108423999999999,144.03726900000001,"Liston Lodge, 209 McCallum Rd, Inverleigh VIC 3321, Australia","33038748","WIN023","22kV AC","Rural Short"," - connector / termination","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024238","20240215PWA_06","Report of pole sparking and grass fire.\nOn arrival crew found HV connection on transformer bushing had overheated dropping molten material to ground.\nThere was a ground fire and no injuries"]
[17,115,"2024-02-14","20:34",-36.720443000000003,144.68812800000001,"44 Cornella-Toolleen Rd, Toolleen VIC 3551, Australia","30336794","SHP021","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024239","20240215PWA_07","Boric acid fuse has candled and started a grass fire\nno reported injuries"]
[17,116,"2024-02-16","14:58",-37.04354,144.232722,"14 A Vanstan Rd, Castlemaine VIC 3450, Australia","33026672","CMN003","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024278","20240409PWA_01","Powercor received a report of low wires.\nattending crew found 3 spans of line had been brought to ground when a private person felled a tree into the line \na ground fire of 100 by 50 M ensued.",null,null,"Negligible: no ground fire"]
[17,117,"2024-02-17","13:53",-38.227083,142.57599999999999,"420 Cooramook School Rd, Grassmere VIC 3281, Australia","33102147","KRT012","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.67800000000000005,3.1187999999999998,"INC-0024280","20240219PWA_01","VIC fire reported pole fire. \nOn arrival crew found a grass fire had started at the base of a substation pole. The substation had a recently melted HV bushing cover on one phase. ",null,null,"Localised: less than 10 sq.m"]
[17,118,"2024-02-18","12:33",-37.432225000000003,143.28663,"588 Old Shirley Rd, Beaufort VIC 3373, Australia","32000519","BAS011","12.7kV AC (SWER)","Rural Long"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024284","20240219PWA_02","Vic Fire reported a pole and grass fire at the incident address. \nFire originated near SWER inter pole 9 and subsequent grass fire of approximately 4.5 hectares in private property. Around one third of the wooden pole top was burnt.\nA fallen SWER high voltage conductor located between poles 9 and 10 landed across the Ararat to Ballarat railway line. ",null,null,"Small: 10 - 1000 aq.m"]
[17,119,"2024-02-22","11:42",-37.659193999999999,143.69277399999999,"210 Vermont Rd, Smythesdale VIC 3351, Australia","33002655","BAS033","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Extreme",2.2719999999999998,10.451199999999998,"INC-0024351","20240223PWA_01","Vic Fire reported a fire start. \n\nUpon arrival the crew found that a large gum tree had fallen on a line which resulted in fire start. Tree appeared to be from within the private property.",null,null,"Medium: 1000 sq.m - 10 ha"]
[17,120,"2024-02-22","14:39",-37.851436999999997,144.77766500000001,"18 Hillman St, Laverton VIC 3028, Australia","30274126","LV006","Low voltage AC (<1kV)","Urban"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45439999999999997,"INC-0024352","20240223PWA_02","Customer (Western Autistic School) reported a fire start from pole substation which was put out by fire extinguisher.\n\nUpon arrival the crew found that one phase of FSD was burnt & melted which started a small ground fire.",null,null,"Large: more than 10 ha"]
[17,121,"2024-02-22","11:11",-37.718888999999997,144.44944000000001,"5 Smiths Rd, Parwan VIC 3340, Australia","30299075","BMH006","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","HBRA only",1,"Extreme",2.2719999999999998,2.2719999999999998,"INC-0024386","20240409PWA_02","Vic fire reported of bushfire. The ACR was also operated.\n\nUpon arrival the crew found large fire more than 5 - 10 hectares.\n\nCause of the fire has not been determined at the time of the report. Investigators are reported to have been attending in due course."]
[17,122,"2024-02-25","16:43",-36.475977999999998,145.22278700000001,"1345 Murchison-Tatura Rd, Tatura VIC 3616, Australia","33094296","MNA021","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024364","20240226PWA_01","pelican hit the conductor causing fire to start at base of the pole.\n Grassfire burnt 10m wide x 30m long either side of pole mainly in road reserve and a small area in private property"]
[17,123,"2024-02-25","23:39",-37.811982,144.77152799999999,"380 Boundary Rd, Derrimut VIC 3026, Australia","30227918","TNA014","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0026659","20240718PWA_03","Connection at pole caused ground fire\nLimited information found\nFound during outage data review\nsmall grass fire\n",null,null,"Started in or originated from a distribution system"]
[17,124,"2024-02-26","00:20",-38.154882000000001,144.57775000000001,"48A Dundundra Dr, Clifton Springs VIC 3222, Australia","32071386","DDL022","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024370","20240226PWA_02","crew attending fault identified a Crossarm fire ",null,null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system"]
[17,125,"2024-02-27","00:59",-37.811982,144.77152799999999,"380 Boundary Rd, Derrimut VIC 3026, Australia","30227918","TNA014","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024387","20240227PWA_02","Fire start by attempted copper theft.",null,null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system"]
[17,126,"2024-02-27","17:24",-36.629165999999998,142.632519,"5 Stewart St, Rupanyup VIC 3388, Australia","32096325","STL006","22kV AC","Rural Long"," - pole (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024416","20240229PWA_02","Powercor was advised of a leaning pole.\n\nCrew attending site has advised, a vehicle has collided with LIS-70466, which in turn has snapped LIS-70464 at the base. it appears  the associated clashing of LV mains at 2x separate locations creating 2x small fires, 2m and 1m square. ",null,null,"Started by lightning striking a distribution system or a part of a distribution system "]
[17,127,"2024-02-29","05:39",-34.784371,142.50804400000001,"Hattah-Robinvale Rd, Hattah VIC 3501, Australia","32140315","WETSBPA","66kV AC","Rural Long"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0024428","20240229PWA_03","Upon arrival crew advised that 66kV pole WETS-BPA P13 LIS-6591. SAP ID: 32140315 had had a pole top fire, lightning suspected.",null,null,"Started by any other thing forming part of or coming into contact with a distribution system"]
[17,128,"2024-03-01","13:35",-36.318012000000003,145.04951,"37 Fischer St, Kyabram VIC 3620, Australia","33090501","KYM005","22kV AC","Urban"," - dropper / bridge","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024493","20240304PWA_01","Customer advised of bright flash from pole. After the flash the neighbours front yard caught on fire.\n\nUpon arrival the crew found that fire of approximately 7 x 2 = 14m2 was started in nature strip with bird on scene.",null,null,"Otherwise started by a distribution system"]
[17,129,"2024-03-02","13:29",-37.821176000000001,144.82103499999999,"21 Little Boundary Rd, Laverton North VIC 3026, Australia","32178781","BLT016","22kV AC","Urban"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024497","20240304PWA_03","fire comms - Powerlines down causing a grassfire at cnr of 818 Little Boundary Rd and Westside Dve.\n\nAttending Powercor fault crew confirmed that a council tree on the south side of Little Boundary Rd has had one of its limbs fall and contact the HV bare overhead span between LIS-17716 and LIS-17715.\n\nThe contact resulted in the tripping of BLT016 CB, resulting in the customers supplied from this feeder being off supply for a short time.  The contact also resulted in a grass fire at either pole (approx. 20m² per fire)"]
[17,130,"2024-03-05","07:59",-36.397241000000001,145.29541499999999,"60 Ardmona Rd, Ardmona VIC 3629, Australia","30131133","MNA014","22kV AC","Rural Long"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024550","20240306PWA_02","Customer reported a fire caused by a bat. Upon inspection, crew said that the bat was still attached to the insulator, causing an arc and the dry grass below caught fire. The fire was extinguished last night. "]
[17,131,"2024-03-05","16:33",-35.535746000000003,142.86926700000001,"Daniels Rd, Sea Lake VIC 3533, Australia","30100581","CTN003","22kV AC","Rural Long"," - pole (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024557","20240306PWA_08","CFA reported wires down and fire at the incident location, Upon arrival Swan Hill fault crew found that a tractor scarifying paddock has clipped pole Collier 3, causing it to break at ground level, resulting in the 3 phase 22kV conductors clashing and making contact with ground, igniting the stubble, approximately 400m x 400m of stubble burnt, CFA in attendance.\nNo reported injuries or 3rd party damage.\nHV fuses at Sea Lake P729 operated.",null,null,1]
[17,132,"2024-03-06","09:53",-38.383270000000003,142.508352,"22 McGregors Rd, Warrnambool VIC 3280, Australia","30136785","WBL003","22kV AC","Urban"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024554","20240306PWA_05","HV 22kV bare conductor has failed and fell to the ground. Protection has operated. \n",null,null,2]
[17,133,"2024-03-06","11:07",-38.299975000000003,141.57743600000001,"187 Crowes Rd, Bolwarra VIC 3305, Australia","31019501","PLD003","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0024555","20240306PWA_06","Pole top fire  on PLD003.\nDual circuit 22kV/66kV wooden pole.\n Fire started at 22kV crossarm and spread to ground and resulted in burnt grass area of 2000m2",null,null,5]
[17,134,"2024-03-06","12:42",-38.069183000000002,144.36277899999999,"18 Kalver St, Corio VIC 3214, Australia","31011885","FNS011","Low voltage AC (<1kV)","Rural Short"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024556","20240306PWA_07","Deteriorated neutral screen service failed at customers attachment (at the roller) causing small ground fire.",null,null,10]
[17,135,"2024-03-06","17:29",-35.951565000000002,145.682401,"Murray Valley Hwy, Cobram VIC 3644, Australia","30143478","CME021","22kV AC","Rural Short"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024559","20240307PWA_01","CFA reported fire in vicinity of Powercor electricity assets, Upon arrival Cobram fault crew found that a bird had flashed over on Switch pole Wyatt P1, causing a ground fire of approximately 50M x 10M in size, CFA & police in attendance, CFA extinguished fire.\nCME21 feeder auto reclosed for the incident. No injuries or 3rd party damage.",null,null,15]
[17,136,"2024-03-06","09:43",-37.743156999999997,144.73486299999999,"7 Toolondo Cl, Caroline Springs VIC 3023",30225346,"TNA021","Low voltage AC (<1kV)","Urban"," - underground cable","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024560","20240307PWA_02","One bay of 4c cables supplying lighting poles has been dug up by excavation machinery during road works. Cable was hit between poles LIS 934718 and LIS 983169. Sparks and smoke coming from the pit have been noted by the crews (please refer to photos) - fire as per photo evidence. No shock resulted from incident.  ",null,null,20]
[17,137,"2024-03-07","03:01",-37.332087000000001,144.77102199999999,"133 Sheehans Rd, Romsey VIC 3434, Australia","32048408","GSB012","12.7kV AC (SWER)","Rural Short"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024585","20240308PWA_01","All supply fail resulted in Kyneton fault crew patrolling affected line, finding a pole fire had commenced on P10 Tickawarra, a SWER t/off structure, causing pole to burn off and fall to ground.\nNo ground fire resulted due to damp conditions, Tickawarra P9A ACR tripped to lockout for the incident.",null,null,25]
[17,138,"2024-03-07","09:08",-37.280389999999997,144.74918099999999,"Warrawee Stud, 2026 Lancefield-Kilmore Rd, Lancefield VIC 3435, Australia","31006268","WND013","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024588","20240308PWA_02","Crossarm fire, no ground fire",null,null,30]
[17,139,"2024-03-07","10:32",-37.666894999999997,144.40616399999999,"152 Mortons Rd Pentland Hills Vic ","30102956","BMH003","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0024596","20240308PWA_04","Crossarm caught fire dropping hot fragments to ground igniting grass ,  small grass fire started.",null,null,50]
[17,140,"2024-03-07","04:40",-37.671852000000001,144.60193200000001,"27 Cameron Ct, Kurunjang VIC 3337, Australia","30103522","MLN012","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024597","20240308PWA_05","Attending Powercor fault crew confirmed that the HV crossarm on HV/LV pole LIS-110926 caught fire and left burn marks on the pole.\n\nThis resulted in the crossarm breaking and the blue HV phase making contact with the LV bare overhead line beneath.\n\nUpon inspection by the LEI, the contact did not result in a confirmed HVI.\nThere was no reported injury, shocks, ground fire or any third party damage as a result of this incident.\n",null,null,100]
[17,141,"2024-03-08","22:56",-38.285361999999999,142.02999600000001,"155 Henshaws Rd, Yambuk VIC 3285, Australia","30227220","KRTPLD2","66kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024608","20240312PWA_01","A customer reported \"all the poles in the street are sparking and heard a loud bang from pole across the road. Sparks started a grass fire and she had to put it out.\" \nOn arrival the crew found that the insulators on P161 KRT-PLD No2 YWF 66kV Line (LISW-985007) had flashed over due to a large build-up of salt due to a long dry spell, combined with a very thick fog. A small grass fire of less than 0.5m2 occurred on the ground below the pole, which the customer had extinguished. There was no other damage or injuries reported. No photos were available of the pole due to the fog and darkness."]
[17,142,"2024-03-08","23:40",-38.472330999999997,144.04275699999999,"745 Great Ocean Rd, Eastern View VIC 3231, Australia","32083486","TQY021","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0026791","20240725PWA_04","Service wire was smoking and previously on fire. Still supply at premise as per emergency services.\nFound during Outage data review\nno ground fire\nno photos"]
[17,143,"2024-03-09","10:40",-38.131698999999998,143.229737,"Camperdown-Lismore Rd, Kariah VIC 3260, Australia","30042332","CDN004","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Extreme",2.2719999999999998,10.451199999999998,"INC-0024612","20240312PWA_03","Fire crews reported: Pole/Crossarm fire on Camperdown-Lismore Rd, near Milangil Rd - approx. 20m of grass burnt.\nOn arrival the fault crew found that a grey fog type insulator had burnt through the crossarm, allowing the 22kV HV conductor to rest on the top of the HV crossarm. A ground fire occurred around the base of the pole approx. 40m x 10m = 400m2 in size, which was extinguished by fire crews. There were no reported injuries, most of the area burnt was road reserve, with only superficial third-party damage to fences and pasture."]
[17,144,"2024-03-09","19:00",-37.686157999999999,144.53547,"790 High St, Melton West VIC 3337, Australia","33074803","MLN022","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","HBRA only",1,"Extreme",2.2719999999999998,2.2719999999999998,"INC-0024613","20240312PWA_04","Overhead conductor parted at  insulator and fell to ground resulting in ground fire "]
[17,145,"2024-03-09","07:10",-34.293118999999997,142.162789,"37 Boobook Ave, Red Cliffs VIC 3496, Australia","30097086","RCT023","Low voltage AC (<1kV)","Rural Long"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024619","20240312PWA_06","At BOOBOOK BLK 369 4 substation an IPC on LV leads has failed then caught fire, it has subsequently dropped burning material to the ground this has started a small grass fire. \nCFA were on site and contained fire.\nNo other asset or property damage reported.\nNo injuries reported."]
[17,146,"2024-03-09","04:00",-38.298563000000001,142.02721,"5 Henshaws Rd, Yambuk VIC 3285, Australia","30227207","KRTPLD2","66kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Extreme",2.2719999999999998,10.451199999999998,"INC-0024626","20240312PWA_07","Vic Emergency reported a grassfire at the incident location. On arrival the crew found that a flashover had occurred involving all three phases and all of the insulators on P174 KRT-PLD No2 YWF 66kV Line (LIS-984992), apparently due to a large salt build up and heavy fog/dew. This flashover resulted in debris falling to the ground and causing a grassfire of approx. 25m x 4m = 100m2. There was damage caused to an adjacent fence by the fire, however no injuries were reported."]
[17,147,"2024-03-09","03:30",-38.266055999999999,142.86919,"Princes Hwy, Terang VIC 3264, Australia","30134373","TRGWBL1","66kV AC","Rural Long"," - connector / termination","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Extreme",2.2719999999999998,10.451199999999998,"INC-0024631","20240312PWA_08","Vic Emergency reported a grassfire at the incident location that may have been started by Powercor assets. On arrival the crew found that an Ampac connection on the centre phase 66kV bridge had failed on P1250 TRG-WBL No1 66kV Line (LIS-408477), causing debris to fall to the ground and starting a small grassfire of approx. 12m x 3m = 36m2 in size. There were no injuries or other damage reported."]
[17,148,"2024-03-09","21:48",-35.354322000000003,143.54365200000001,"70A Yana St, Swan Hill VIC 3585, Australia","32157423","SHL007","22kV AC","Urban"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024635","20240312PWA_09","Yana P18A HV CHP 'B' phase failed below insulating sheds.  This failure has caused a short circuit load on upstream steel conductor which has then caused a steel HV splice to fail.  The conductor has then fallen onto LV and ground.  A small ground fire also started but was quickly extinguished.  "]
[17,149,"2024-03-10","12:57",-37.868994999999998,144.80768699999999,"1 Robin St, Altona VIC 3018, Australia","32167311","AL007","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024609","20240312PWA_02","crew attending fault identified that a lead had failed at a LV Isolator resulting in a small fire around the base of the pole and nature strip"]
[17,150,"2024-03-10","21:00",-37.791356,144.80019799999999,"22 Ralph St, Sunshine West VIC 3020, Australia","32163781","SU035","Low voltage AC (<1kV)","Urban"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024694","20240314PWA_05","LV Fused Isolator burnt out and caused small fire at base of pole."]
[17,151,"2024-03-11","13:00",-37.975512000000002,144.49108899999999,"114 Minns Rd, Little River VIC 3211, Australia","30059670","FNS022","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0024661","20240313PWA_02","Fuse box fire on a pole caused a small grassfire"]
[17,152,"2024-03-11","16:45",-38.052582999999998,141.712478,"130 Milltown Mission Rd, Milltown VIC 3304, Australia","32129379","HYT011","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Extreme",2.2719999999999998,2.2719999999999998,"INC-0024662","20240313PWA_03","Tree on powerlines and grass had caught fire "]
[17,153,"2024-03-11","20:07",-36.752048000000002,142.17633499999999,"339 Golf Course Rd, Haven VIC 3401, Australia","30138325","HSM004","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0024668","20240313PWA_07","Ms Kerryn Prouse reported pole fire at the pole in her front yard Crew reported that it seems that there was a broken HV SWER that has melted away, causing a pole fire below "]
[17,154,"2024-03-12","11:09",-36.056953,142.05624700000001,"170 Ellam-Willenabrina Rd, Jeparit VIC 3423, Australia","32103878","NHL015","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0024665","20240313PWA_04"," SWER line had been brought down by a truck , started grass fire."]
[17,155,"2024-03-12","14:02",-38.294119000000002,144.39249100000001,"33 Horwood Dr, Breamlea VIC 3227, Australia","32070503","WPD022","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024667","20240313PWA_06","Fire coms reporting tree branch has brought down wires and started a pole fire.\ncrew found pole top fire on pole 25, no involvement from branch. "]
[17,156,"2024-03-12","16:36",-35.810357000000003,144.21538799999999,"28 Sampson St, Cohuna VIC 3568, Australia","32038185","CHA003","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024670","20240313PWA_08","Candling fuse caught fire no ground fire"]
[17,157,"2024-03-12","15:44",-36.364395999999999,145.45565500000001,"365A New Dookie Rd, Lemnos VIC 3631, Australia","30270908","SHN014","22kV AC","Urban"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024674","20240314PWA_01","Customer reported \"pole top exploded' and set ground on fire.  Upon arrival crew found a bat that had been on the insulator for a while has somehow shorted, caught fire then dropped to the ground and ignited the grass underneath.  Fire contained to approx. 3m X 2m.\nNo media\nNo injuries reported. "]
[17,158,"2024-03-13","17:00",-38.374001999999997,142.491805,"96 Jamieson St, Warrnambool VIC 3280, Australia","32198218","WBL008","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024680","20240314PWA_02","A Powercor crew working at the WBL ZSS called to report that they could see a conductor sparking across Jamieson St. On arrival the fault crew found a sparking 4 core service cable between LIS-12583 & LIS-13077. Whilst they were preparing to isolate the supply to the service cable, it dropped some sparks into the roadside grassed area, starting a small grassfire approx. 1m2 in size. The fault crew extinguished the fire, and the CFA were not required."]
[17,159,"2024-03-13","08:31",-35.955219999999997,145.556881,"Churchill Rd, Yarroweyah VIC 3644, Australia","33083064","NKA005","22kV AC","Rural Short"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024683","20240314PWA_03","arroweyah Fire Brigade called to advise grass fire underneath pole on CRN of Chruchill Road and Kokoda Road, also customer on corner reports intermittent supply at time of fire. \n\nUpon arrival the crew found a burnt bird on ground which appeared to be caused from flashover by bridging the insulator."]
[17,160,"2024-03-13","19:00",-37.789586,144.84538499999999,"43 Duke St, Sunshine VIC 3020, Australia","32167518","SSE034","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024695","20240314PWA_06","Pole fire tracking across brown insulators caused crossarm to burn."]
[17,161,"2024-03-13","13:00",-37.896932,144.66155900000001,"20 Scotsburn Grv, Werribee VIC 3030, Australia","32166268","WBE024","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026785","20240725PWA_02","Customer reports fire this morning at top of power pole. Fire and arching has now stopped, \nReplaced damaged neutral screen service\nno ground fire\nFound during Outage  data review\nno photos of incident provided"]
[17,162,"2024-03-13","14:40",-38.206173,142.20532700000001,"Tarrone North Rd, Tarrone VIC 3283, Australia","30622128","KRTPLD2","66kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0026793","20240725PWA_05","KRT-PLD No.2 66kV Line has Tripped to Lock Out. \nWires down at LIS 6481 Possible pole fire cause crew had to walk in and to dark for photos ATL aware\nNo ground fire\nFound during Outage data review"]
[17,163,"2024-03-14","14:43",-37.056739,143.86312599999999,"3414 Pyrenees Hwy, Carisbrook VIC 3464, Australia","30023519","MRO007","22kV AC","Rural Long"," - automatic circuit recloser (ACR)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.67800000000000005,3.1187999999999998,"INC-0024699","20240314PWA_07","Crew investigating outage found bird/s had caused flashover on Automatic circuit recloser structure.\nFire brigade had extinguished small fire. 10 X 5 m"]
[17,164,"2024-03-14","16:50",-38.180396999999999,144.375586,"42 Fellmongers Rd, Breakwater VIC 3219, Australia","32068323","GLE012","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024702","20240315PWA_01","The fire authority reported a pole fire. On arrival the crew confirmed a pole had caught fire, the HV intermediate crossarm was severely burnt. The fire had spread to the below ground causing a small grass fire.\nThe pole required replacement."]
[17,165,"2024-03-14","20:11",-38.160493000000002,144.345989,"2 Bloomsbury St, Newtown VIC 3220, Australia","30058211","GL022","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026784","20240725PWA_01","hv int x arm , burnt due to tracking, arm broke in half and dropped one phase into lv. No hv injection\nNo Ground fire\nOutage data review"]
[{"$f":"COUNTA(C203:O203,Q203,T203:V203)","v":17},166,"2024-03-14","11:20",-36.079554000000002,141.66044299999999,"Warraquil East Rd, Netherby VIC 3418, Australia","32105641","NHL016","12.7kV AC (SWER)","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O203=\"\",\"\",IF(O203=\"LBRA only\",0.2,IF(O203=\"HBRA only\",1,IF(O203=\"within electric line construction area\",19.8,IF(O203=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"High",{"$f":"IF(Q203=\"\",\"\",IF(Q203=\"No rating\",0.05,IF(Q203=\"Moderate\",0.334,IF(Q203=\"High\",0.678,IF(Q203=\"Extreme\",2.272,4.754)))))","v":0.67800000000000005},{"$f":"IF(OR(P203=\"\",R203=\"\"),\"\",IF(AND(O203=\"within electric line construction area\",Q203=\"No forecast\"),1,P203*R203))","v":0.67800000000000005},"INC-0026797","20240725PWA_06","Netherby north pole13 pole fire\nP bracket installed\nno ground fire\nno photos\nFound during Outage data review"]
[17,167,"2024-03-15","19:52",-35.348256999999997,143.56239400000001,"4 Gray St, Swan Hill VIC 3585, Australia","32155667","SHL007","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024732","20240318PWA_06","CFA reported, pole fire started a grass fire. intersection Gray St and Campbell St.\ncrew found Lv isolator had ruptured and  dropped  partially burnt material to the ground below "]
[17,168,"2024-03-16","20:40",-38.691907999999998,143.15570199999999,"Old Ocean Road, Princetown VIC 3269, Australia","30566740","COB011","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0024718","20240318PWA_01","The fire authority reported a grass fire had occurred due to a pole fire. On arrival the crew confirmed that there was no pole fire, however a grass fire had occurred due to a swan flying into the HV conductor.\n\nThe swan had fallen to the ground, starting the grass fire which totalled approximately 30m x 30m. \n"]
[17,169,"2024-03-16","22:18",-35.983209000000002,145.69560799999999,"Chapel Rd, Cobram East VIC 3644, Australia","33085672","NKACME","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026800","20240725PWA_07","Vicfire reported pole fire. intersection of chapel rd and healy rd. Crew found bird had flashed over Small grass fire Found during Outage data review"]
[17,170,"2024-03-19","07:09",-37.067677000000003,142.769418,"11A Ararat Rd, Stawell VIC 3380, Australia","30078114","ARTSTL","66kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024755","20240319PWA_02","Pole top fire on 66kV wood pole. Fire attributed to leakage current between steel crossarms supporting 66kV ARTSTL circuits. No ground fire. "]
[17,171,"2024-03-19","16:53",-36.900142000000002,141.22676799999999,"1386 Patyah road Patyah Vic 3318","32122568","CHM011","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0024767","20240320PWA_01","Fire and fallen pole reported, person reported receiving electric shock from fire suppression equipment. \nAttending crew found pole was burnt near ground level and lying on ground with conductor attached.\na ground fire ensued"]
[17,172,"2024-03-19","11:43",-36.731219000000003,144.26355000000001,"48 Sandhurst Rd, California Gully VIC 3556, Australia","33019314","EHK023","22kV AC","Rural Short"," - surge diverter","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024781","20240320PWA_04","Surge arrestor has ruptured during REFCL testing. \nBits of surge arrestor fell to the ground and started a very small ground fire (approx. 0.1m2)."]
[17,173,"2024-03-19","14:15",-36.333913000000003,144.641222,"Odonnell Rd, Rochester VIC 3561 (Near intersection of Odonnell Rd and Lowe Rd)","32183808","SHP012","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024784","20240320PWA_05","Crossarm broke due to tracking. \nThis caused the conductor to fall down and start grass fire.\n"]
[17,174,"2024-03-19","21:23",-38.367576,142.493627,"84 Mortlake Rd, Warrnambool VIC 3280, Australia","31029522","WBL005","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024790","20240320PWA_07","The fire brigade reported a pole fire, they were enroute to the incident. The crew arrived and confirmed a fire had occurred causing significant damage to pole 20"]
[17,175,"2024-03-19","23:20",-36.901983999999999,142.05870300000001,"1303 Lower Norton-Nurrabiel Rd, Nurrabiel VIC 3401","32103486","HOTSCHM","66kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0024798","20240321PWA_01","HOTS-CHM/IKA P214 (LIS 9059)\nBottom X arm burnt off at the strap bolt, 66kv conductor came down and started a small fire approx. 1m2 that put itself out."]
[17,176,"2024-03-19","23:20",-36.903016000000001,142.05516600000001,"1303 Lower Norton-Nurrabiel Rd, Nurrabiel VIC 3401","32103504","HOTSCHM","66kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,"INC-0024799","20240321PWA_02","HOTS-CHM/IKA P 216 (LIS 9061) \nFound the X arm on fire while doing a line patrol, extinguished a small fire approx 4m2 at the base of the pole and called the fire brigade to put the arm out that was still attached to the pole."]
[17,177,"2024-03-21","21:08",-37.36,144.58220600000001,"Mount Macedon Rd, Mount Macedon VIC 3441, Australia","33028413","WND012","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024812","20240322PWA_01","Reports of ground fire and tree on conductor in Mt Macedon.  \nOn arrival, crew found large Tree had fallen from opposite side of road at pole 46 and ground fire At pole 32 some 2km Away.\n\n"]
[17,178,"2024-03-22","21:38",-36.199173000000002,145.37424300000001,"Boundary Rd, Tallygaroopna VIC 3635, Australia","33083631","SHN011","22kV AC","Rural Long"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0024839","20240325PWA_01","Reports from CFA of flying fox on fire at pole 46 \nOn arrival, crew found no asset damage.  Fire at base of pole with fire around channel on side of the road. "]
[17,179,"2024-03-22","15:35",-37.911112000000003,142.97384400000001,"1052 DARLINGTON - NERRIN ROAD DUNDONNELL VIC 3271","30046461","CDN006","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024841","20240325PWA_03","Powercor was advised that a Grassfire potentially started from fuse blown\nAttending crew  found 2 Hv fuses had operated and fire at base of  fuse pole. \nNo cause for fuse operation found"]
[17,180,"2024-03-22","20:22",-38.178173999999999,144.41977399999999,"350 BELLARINE HIGHWAY,MOOLAP,VIC,3224","33041572","GLE024","22kV AC","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0024845","20240325PWA_04","emergency services report ground fire at base of pole.\nAttending crew found HV isolator on ACR pole had malfunctioned and fallen debris had caused ground fire of 15 by 3 Meters. "]
[17,181,"2024-03-23","22:24",-38.157221,144.33229399999999,"4A Vista Rd, Newtown VIC 3220, Australia","30279169","GL021","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024840","20240325PWA_02","Per firecom wire down and small grass fire \nAttending crew found customers tree had rubbed through service at #5 \nFallen service ignited small ground fire of 6 by 2 metres in leaf litter in customer's front yard. "]
[17,182,"2024-03-23","09:30",-37.411906999999999,143.894374,"29 King St, Creswick VIC 3363, Australia","32014461","BAN009","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024862","20240325PWA_06","Report of HV intermediate cross arm burnt out with the 2x HV conductors resting on the LV cross arm."]
[17,183,"2024-03-23","11:40",-37.860174000000001,144.68964600000001,"32A Elder Rd, Hoppers Crossing VIC 3029, Australia","70429794","LV009","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024864","20240325PWA_08","Crew investigating fault found that there was tracking from polluted insulators which lead to the strap bolt heating up and the X arm snapping resulted in HVI"]
[17,184,"2024-03-23","13:00",-37.614463000000001,144.441812,"246 Camerons Rd, Coimadai VIC 3340, Australia","70258869","MLN022","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0024865","20240325PWA_09","Crew found that there was tracking from polluted insulators which lead to the strap bolt heating up and the X arm snapping resulted in cross arm fire "]
[17,185,"2024-03-24","20:27",-35.911217999999998,144.13215,"132 Ladson Rd, Mincha West VIC 3568, Australia","33020830","CHA006","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0026823","20240726PWA_06","Replaced burnt out FSD,\nno ground fire\nfound during outage data review"]
[17,186,"2024-03-24","22:52",-36.380248000000002,145.33171300000001,"Excelsior Ave, Ardmona VIC 3629, Australia","33094028","MNA021","22kV AC","Rural Short"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024863","20240325PWA_07","CFA reported pole fire at the above address.  \nOn arrival, crew found what looked to be a deceased fruit bat that was hanging from the insulator on pole 32   Ground fire underneath the pole with superficial damage to a fence."]
[17,187,"2024-03-25","00:14",-37.751953999999998,144.84266400000001,"70 Penna Ave, Sunshine North VIC 3020, Australia","30103335","SSE032","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024867","20240325PWA_10","MFB reported sparking wires near the incident location. \nOn arrival the crew found that a bird had flown into the HV conductor causing a ground fire"]
[17,188,"2024-03-26","10:27",-37.831929000000002,144.54254499999999,"Ballan Rd Service Rd, Wyndham Vale VIC 3024 (Near intersection of Ripley Road and Ballan Road)","30117574","TNA022","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0024885","20240327PWA_02","Customer advised that horizontal crossarm has snapped on the intersection of ripleys rd and ballan rd. wire was hanging low.\n\nUpon arrival the crew found that crossarm was burnt with insulator dislodged.\n\nThere was no reportable ground fire or electric shock."]
[17,189,"2024-03-26","16:39",-37.911082999999998,144.655843,"13 Pagnoccolo St, Werribee VIC 3030, Australia","75253849","WBE024","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024902","20240327PWA_04","The customer reported that service line has come off house and down on the front yard. Has made burn marks on gutter, boat & patch of grass where wire has landed. \nOn inspection crew found deteriorated service wire with a neutral screen cable.\nThere was no reported injuries "]
[17,190,"2024-03-27","10:05",-36.002741999999998,145.40424200000001,"858 Shinnicks Rd, Katunga VIC 3640, Australia","30125807","NKA006","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024907","20240327PWA_05","Excavator has come into contact with OH lines and started a grass fire. \nConductors and crossarm damaged\nthere were no reported injuries"]
[17,191,"2024-03-27","16:18",-34.292245999999999,142.24043399999999,"718 Woomera Ave, Red Cliffs VIC 3496, Australia","33104850","RCT022","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024909","20240328PWA_01","Reports from CFA of fire at Red Cliffs Terminal Station.  SP Ausnet operator called to attend.  Operator found fire at base of Powercor pole 924334 inside yard with a deceased Goanna at the base of the pole.  Operator advised that there was damage to Powercor conduit around earth cable at base of pole only.    Size of fire approx. 40mx20m"]
[17,192,"2024-03-27","23:35",-38.156830999999997,144.56071600000001,"2 Bungalalli Ave, Clifton Springs VIC 3222, Australia","30059203","DDL022","22kV AC","Urban"," - fuse (powder filled)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024918","20240328PWA_03","Reports of pole cnr Berrigan St sending off amber sparks from insulators falling to ground level\nCrew found PF fuse unit candled at substation pole\nSmall burn on ground from fallen porcelain. "]
[17,193,"2024-03-30","16:26",-35.735481,143.872759,"72 Wandella Road Kerang 3579, Kerang-Quambatook Road (corner McKenzie Road/Lake Wandella)","33019851","KGTSGSF","66kV AC","Rural Long"," - pole (concrete)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0024922","20240402PWA_01","Crew requested to patrol KGTS-GSF 66kV line near SW 31357 after successful reclose and VicEmergency incident. \nCrew found a grass fire 40x15m had occurred at P58, LIS 711236\nNo cause could be located\nNo asset damage"]
[17,194,"2024-03-30","21:17",-38.549056,143.982327,"79 Charles St, Lorne VIC 3232, Australia","33045242","CLC014","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0024925","20240402PWA_02","Fire Comms reported a fire at the incident location. On arrival the crew found that an LV FOLCB had overheated and caught fire dropping debris to the ground, resulting in a ground fire of approx. 5m x 3.5m = 17.5m2. There were no reported injuries or third party damage."]
[17,195,"2024-03-30","01:38",-36.409944000000003,145.48006899999999,"95 Beckham Rd, Shepparton East VIC 3631, Australia","33094012","STN011","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024933","20240402PWA_03","Customer reported, can see small wire detached from pole top to fuse box on pole out front, photo requested, cannot reach by hand, bat hit line last night caused small fire at base of pole, believes effecting 1 phase to pump site across road.\nCrew found, Bat has hit the insulator breaking the wrap on to the pole, wire low but still I the air, 10 square meter grass fire "]
[17,196,"2024-03-30","23:44",-36.673409999999997,144.325298,"10 Ligar St, Huntly VIC 3551, Australia","32036074","EHK033","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024937","20240402PWA_04","Customer reported sparking service and burnt grass.\nCrew found LV service wire had failed, made safe and replaced. \nThere was no reported injuries"]
[17,197,"2024-03-31","07:55",-37.657328,144.60915199999999,"49A Croxton Dr, Kurunjang VIC 3337, Australia","30104871","MLN012","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024938","20240402PWA_05","Report from emergency services requesting attendance to a pole fire at Croxton Drive.\n Upon arrival the fault crew found a FOLCB had caught fire and burnt out "]
[17,198,"2024-04-01","21:47",-38.334130999999999,144.20783900000001,"120 Portreath Rd, Bellbrae VIC 3228, Australia","32079181","TQY021","22kV AC","Rural Short"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.67800000000000005,3.1187999999999998,"INC-0024955","20240402PWA_08","A customer reported flickering/dim lights at the incident location. On arrival the crew found that a HV fuse unit had been struck by lightning and the bottom section of the HV fuse unit had fallen down, alive via back feed through the transformer. The HV lead contacted the pole, resulting in a pole fire in the area of the substation earth cable. There was only superficial damage done to the pole. There was no reported ground fire, HVI or third-party damage."]
[17,199,"2024-04-01","18:38",-36.069442000000002,145.46117899999999,"136 Naring Rd, Numurkah VIC 3636, Australia","32184097","NKA001","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0024968","20240403PWA_01","Emerg services reported attendance to grass fire that has burnt the base of pole at intersection of Naring and Kinnairds Roads, Numurkah. Fire crew enroute."]
[17,200,"2024-04-01","18:41",-38.175533000000001,144.336929,"2 Oxford St, Belmont VIC 3216, Australia","32071733","GCY011","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0026535","20240712PWA_01","customer advised   adv flames/sparks on power line going over roadway to house across the road. Flames are 5m along the line."]
[{"$f":"COUNTA(C238:O238,Q238,T238:V238)","v":17},201,"2024-04-01","23:20",-38.095125000000003,144.380629,"83 The Esplanade, North Shore VIC 3214","30621063","CRO023","22kV AC","Rural Short"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",{"$f":"IF(O238=\"\",\"\",IF(O238=\"LBRA only\",0.2,IF(O238=\"HBRA only\",1,IF(O238=\"within electric line construction area\",19.8,IF(O238=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"High",{"$f":"IF(Q238=\"\",\"\",IF(Q238=\"No rating\",0.05,IF(Q238=\"Moderate\",0.334,IF(Q238=\"High\",0.678,IF(Q238=\"Extreme\",2.272,4.754)))))","v":0.67800000000000005},{"$f":"IF(OR(P238=\"\",R238=\"\"),\"\",IF(AND(O238=\"within electric line construction area\",Q238=\"No forecast\"),1,P238*R238))","v":0.13560000000000003},"INC-0026536","20240712PWA_02","fault cases indicate pole fire in area during storm conditions\npole and switch replaced due to burning"]
[{"$f":"COUNTA(C239:O239,Q239,T239:V239)","v":17},202,"2024-04-02","01:48",-37.275928,142.95309,"105 Grano St, Ararat VIC 3377, Australia","33049414","ART023","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O239=\"\",\"\",IF(O239=\"LBRA only\",0.2,IF(O239=\"HBRA only\",1,IF(O239=\"within electric line construction area\",19.8,IF(O239=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"Moderate",{"$f":"IF(Q239=\"\",\"\",IF(Q239=\"No rating\",0.05,IF(Q239=\"Moderate\",0.334,IF(Q239=\"High\",0.678,IF(Q239=\"Extreme\",2.272,4.754)))))","v":0.33400000000000002},{"$f":"IF(OR(P239=\"\",R239=\"\"),\"\",IF(AND(O239=\"within electric line construction area\",Q239=\"No forecast\"),1,P239*R239))","v":1.5364},"INC-0024949","20240402PWA_07","House fire resulted in an overhead service line coming to ground which started a grass fire of 0.3 square metres in the road reserve.\nThe house was completely destroyed which caused a wire down. "]
[17,203,"2024-04-04","12:02",-37.462870000000002,144.60113000000001,"7 A Galilee Ct, New Gisborne VIC 3438, Australia","34014519","GSB013","Low voltage AC (<1kV)","Rural Short"," - LV pillar","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0025021","20240404PWA_03","A LV pillar has caught fire due to vehicle impact.  Small ground fire resulted from the pillar fire approx. 1m2. The fire was put out by nearby tradesmen."]
[17,204,"2024-04-06","00:11",-37.7986,144.62725399999999,"1627 Boundary Rd, Mount Cottrell VIC 3024, Australia","33108886","TNA022","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0025045","20240408PWA_01","Customer reported that the fuse box on pole outside her property caught fire. \nOn arrival, the Faults crew found that the 100A single phase fuse box on pole 962313 had caught fire.\nSmall grass fire, no injuries"]
[17,205,"2024-04-08","14:44",-37.720678999999997,144.43940799999999,"402 Cummings Rd, Parwan VIC 3340, Australia","33077287","BMH006","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0025066","20240409PWA_03","fire agency reported HV powerline down. started grass fire at multiple locations on smiths road Parwan. requesting urgent attendance\n\nCrew found steel conductor had parted at several locations and was on the ground "]
[17,206,"2024-04-09","16:50",-37.913640999999998,144.09010000000001,"290 Medina Rd, Lethbridge VIC 3332, Australia","33045348","GHP011","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0025082","20240410PWA_02","Pole box caught fire and dropped to the ground causing a ground fire approximately 1 metre square."]
[17,207,"2024-04-12","12:28",-38.261712000000003,144.40523999999999,"48 Breamlea Rd, Connewarre VIC 3227, Australia","30589943","WPD022","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0025136","20240412PWA_03","Pole mounted FOLCB has failed and started a large grass fire.\nFire is 100m2 x 180m2 in size. \nCFA has attended site to extinguish fire. "]
[17,208,"2024-04-19","02:21",-37.582245999999998,143.86999,"3 Elsworth St E, Golden Point VIC 3350, Australia","30014627","BAS032","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0025249","20240422PWA_05","Powercor was advised of a pole top fire \nCrew found top of pole had burnt off allowing HV to fall into circuit below "]
[17,209,"2024-04-21","11:42",-36.361604999999997,145.44677799999999,"285 New Dookie Rd, Grahamvale VIC 3631, Australia","33092861","SHN014","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0025247","20240422PWA_03","Report of Bat, damage to HV insulators at SHAHOLLI P3 S/S (LIS 29972)\nCrew found Bird/Bat had caused HV fault, conductor on ground, small grass fire less than 100m2."]
[17,210,"2024-04-22","13:00",-38.033141999999998,144.38633200000001,"86-90 Canterbury Rd W, Lara VIC 3212, Australia","33044549","FNS021","22kV AC","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0025264","20240423PWA_03","HV droppers have burnt out, dropping burning material to the ground below, causing grass fire on nature strip. Pole mounted substation: CANTERBURY RD WEST P5. Size of grass fire was approx. 3m2. "]
[17,211,"2024-05-01","14:55",-38.327914,144.31638100000001,"19 BAINES CRESCENT, TORQUAY VIC 3228","30070330","TQY032","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0025393","20240502PWA_01","fire brigade recieved report of pole box on fire\nCrew found fused mains box on pole supplying  19 Baines Cres  had burnt"]
[17,212,"2024-05-02","18:32",-38.011209999999998,143.95417499999999,"Cressy-Shelford Rd, Shelford VIC 3329 (Near intersection of Cressy-Shelford Rd and Rokewood-Shelford Rd","32071209","GHP021","12.7kV AC (SWER)","Rural Long"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Moderate",0.33400000000000002,1.5364,"INC-0025423","20240506PWA_01","A customer reported a pole top had been on fire, causing an insulator to fall to ground.\nA crew was dispatched to investigate, on arrival the crew found a SWER pole had in fact been on fire, causing the top section of the pole to break away from the pole. \nThe p bracket of the insulator had burnt out.\n There was no evidence of ground fire start. "]
[17,213,"2024-05-04","19:06",-37.726025999999997,144.65361899999999,"18 Old Leakes Rd, Rockbank VIC 3335","30565255","MLN032","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"No rating",0.05,0.05,"INC-0026637","20240717PWA_09","Fire brigade reported fire on pole \nCrew found Fuse mains box up pole end burnt out - supplying rockbank general store"]
[17,214,"2024-05-10","19:00",-38.383420999999998,142.23789400000001,"6 Bank St, Port Fairy VIC 3284, Australia","33100291","KRT022","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0025533","20240513PWA_01","A customer called to report the pole opposite their property was on fire, and they had contacted the CFA. On arrival the crew found that one of the phases of an isolator style Krone box had overheated and failed. There were no injuries, third party damage or ground fires reported."]
[17,215,"2024-05-12","10:06",-37.471411000000003,143.644946,"2132 Western Hwy Burrumbeet VIC 3352","30303398","BAN-BGR","66kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0025534","20240513PWA_02","A report of wires arcing and sparking outside the above address, on arrival the crew found a 66/22kV pole had burnt through at the 22kV position on the pole.\nA couple of small spot burns on the ground, no injuries"]
[17,216,"2024-05-16","08:20",-37.486117,144.141966,"1219 SPARGO CREEK ROAD, SPARGO CREEK VIC 3461","32012259","BAN003","12.7kV AC (SWER)","Rural Long"," - insulator tie wires / connections","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0025605","20240516PWA_02","T/C crew Reports Broken Tie and SWER line burning on pole at RICHARD P7 \nCrew advised tie had fractured and conductor had fallen midway down pole.\nThe insulator was undamaged\npole burnt but serviceable\nThere were no injuries or ground fire."]
[17,217,"2024-05-17","17:50",-37.240755,144.43354500000001,"29 BURTON AVENUE, KYNETON VIC 3444","30038447","WND014","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0025648","20240520PWA_03","Emergency services reported pole top fire.  Upon arrival crew found an FOLCB had caught fire. FOLCB burnt, minor charring on pole.\nNo ground fire reported\nNo injuries or other damage\nESV did not require any preservation"]
[17,218,"2024-05-20","08:00",-36.710551000000002,142.18806599999999,"7 Burgess St, Horsham VIC 3400, Australia","30586864","HSM010","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0025652","20240520PWA_04","As per fire comms - fire in pole box\nAttending crew burnt box on pole. \n "]
[17,219,"2024-05-22","22:17",-34.260199999999998,141.85192000000001,"2893 STURT HIGHWAY,MERRINEE,VIC,3496","32146425","RCT023","12.7kV AC (SWER)","Rural Long"," - fuse (EDO fuse)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"No rating",0.05,0.05,"INC-0026467","20240709PWA_08","customer reports transformer out the front is glowing and can smell electrical burning smell,\nCrew found EDO fuse malfunction"]
[17,220,"2024-05-25","17:43",-35.991329999999998,144.41278600000001,"83 Phyland Rd, Patho VIC 3564, Australia",705008,"CHA005","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0026324","20240703PWA_01","Cust reporting fire at the base of Pole NO. 705008 where wires were burning, halfway up pole between  ground at trans also wires on fire\nNo Detail to indicate if  Krone box or underground customers mains"]
[17,221,"2024-05-27","06:59",-35.349359999999997,143.54877099999999,"30 WILKINS GROVE, SWAN HILL VIC 3585","33067456","SHL007","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0025738","20240527PWA_05","Emerg services report service line on fire to No.30\nAttending crew found customers connection box had ignited and damaged  service tails."]
[17,222,"2024-05-27","16:00",-37.195768999999999,144.39682199999999,"34 DAVY STREET, MALMSBURY VIC 3446","33031370","CMN001","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0025778","20240528PWA_04","Upon arrival crew made area safe and noted that the FOLCB on MALMSBURY TOWN 1E (LIS-908105) had melted completely.\nNo grassfire, no third-party authorities in attendance. \nRequested ESV call back "]
[17,223,"2024-06-01","07:30",-37.626337999999997,143.83586,"4 Magpie Rd, Magpie VIC 3352, Australia","51003660","BAS022","22kV AC","Rural Long"," - switch (disconnector/isolator)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0025892","20240604PWA_01","A passerby reported a pole on fire. Upon arrival, a fault crew found that there had been a flashover on the ACR located at MAGPIE P93  No groundfire."]
[17,224,"2024-06-01","23:39",-36.378531000000002,141.23736099999999,"18 Commercial St E, Kaniva VIC 3419","32122731","NHL031","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0026660","20240718PWA_04","Box on pole sparking on Madden St and Commercial Street intersection\nKRONE box melted \nno ground fire\nFound during Outage data review"]
[17,225,"2024-06-03","03:49",-36.847518999999998,144.610658,"160 MURPHYS LANE, KNOWSLEY VIC 3523","30553792","BGO023","22kV AC","Rural Long"," - voltage regulator","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0025870","20240603PWA_02","Report of ACR operation at above address.  On arrival crew found regulator on fire.  CFA attended to extinguish.  No ground fire.  Minor oil spill/splash into bunded area.  Crew advised lid of failed regulator slightly lifted.  Unknown cause at this point in time. \n\n*note address is incorrect as coordinates not accepoed correct coordinates  are:\n\n-36.847520, 144.610658"]
[17,226,"2024-06-05","21:40",-38.180101999999998,144.32943599999999,"40 PAVO STREET, BELMONT VIC 3216","32079532","GLE012","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0025935","20240606PWA_03","Emergency Services reported a tree on fire and contacting powerlines. On arrival the crew found a tree on the nature strip had been almost completely burnt, with burnt debris strewn across the nature strip. The services to both 40 & 42 Pavo Street and the overhead internet cable had been damaged by the fire. The service to 40 Pavo St was a black XLPE service and the service to 42 Pavo St was a grey twisted service. Both services were badly damaged in the fire, so it couldn't be determined if one of the services may have started the fire. There were no reported injuries, and no reported third-party damage."]
[17,227,"2024-06-06","07:35",-37.804478000000003,144.81309899999999,"98 N View Dr, Sunshine West VIC 3020, Australia","30333154","SSE014","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0025946","20240606PWA_04","Report was received of pole mounted transformer fire. Upon arrival crew identified that a connection between a FSD and LV lead has caught fire.  There was no ground fire. ESV was contacted: not required to preserve the site "]
[17,228,"2024-06-08","11:30",-37.718860999999997,144.68853200000001,"45 Vere Ct, Deanside VIC 3336, Australia","30105746","MLN021","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No rating",0.05,0.05,"INC-0025957","20240611PWA_03","Fire Comms reported - Pole fire at LIS-775423 outside 111 Vere Crt, Deanside .\nOn arrival to site the PCA Field Crew have advised that the Tx LV Fuse Box on Pole 2 had caught fire and melted, causing melted debris to also fall to the ground below and around the pole. scorch marks present around the base of pole.\nThere was no reported ground fire, third party damage, injury or shocks as a result of this incident. \n"]
[17,229,"2024-06-11","05:19",-37.731360000000002,144.432525,"Groundsmans House, 404 Aerodrome Rd, Parwan VIC 3340, Australia","30117793","BMH006","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No rating",0.05,0.05,"INC-0025969","20240611PWA_07","Customer reported the transformer blew up and the pole is on fire. Customer called CFA.\nOn arrival to site the PCA Field Crew have advised that the Tx LV Fuse Box on Pole 10 had caught fire and melted, causing melted debris to also fall to the ground below and around the pole - Scorch marks present around the base of pole.\n\nThere was no reported ground fire, third party damage, injury or shocks as a result of this incident. "]
[17,230,"2024-06-11","23:15",-38.183911999999999,144.350021,"35 BAILEY STREET, BELMONT VIC 3216","32075439","GLE012","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0025995","20240613PWA_05","On arrival crew confirmed melting and burning at the overhead point of attachment (POA) box at the residential address. \nCFA had put the fire out. "]
[17,231,"2024-06-14","02:37",-37.801136,144.81086400000001,"46 Cawood Dr, Sunshine West VIC 3020, Australia","30624826","SSE033","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0026663","20240718PWA_05","Report of pole fire\nno ground fire\nfound during Outage data review\nno photos of initial incident"]
[17,232,"2024-06-16","17:57",-36.239916000000001,144.94797,"566 Henderson Rd, Tongala VIC 3621, Australia","30124705","KYM004","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0026030","20240617PWA_01","Fire comms reported wire down, arcing and fire start at the incident location. \nUpon arrival Shepparton fault crew found that a 3/2.75 Steel conductor failed "]
[17,233,"2024-06-16","21:23",-38.217495999999997,144.571575,"541A Swan Bay Rd, Mannerim VIC 3222, Australia","30068402","DDL024","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"No rating",0.05,0.05,"INC-0026664","20240718PWA_06","Replaced burnt out edo tube\nno ground fire\nfound during Outage data review"]
[17,234,"2024-06-26","13:30",-38.016010999999999,144.20385899999999,"Greenbanks, 870 Steiglitz Rd, Sutherlands Creek VIC 3331, Australia","33045503","GHP011","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No rating",0.05,0.22999999999999998,"INC-0026209","20240627PWA_02","customer reported box at pole top has burnt out. side melted. part has fallen to the ground, grass around base of pole blackened\nCrew found FSD had malfunctioned and heated material fell to ground causing a small grass fire"]
[17,235,"2024-06-27","17:24",-36.327312999999997,141.65223,"36 Davis Avenue Nhill 3418",35413487,"NHL016","Low voltage AC (<1kV)","Rural Long"," - lamps (minor road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0026236","20240628PWA_01","Report received regarding street light sparking and caught on fire. \nUpon arrival, the fault crew found that a LED  street light had been on fire.\n\nOsiris notification draft  generated but unable to process due to addressing issue , 23/07 processed once Osiris working correctly again"]
[17,236,"2023-08-11","12:15:00",-38.161453999999999,144.36523099999999,"136 Verner St, Geelong VIC 3220, Australia",30059155,"GLE032","22kV AC","Urban"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0021706","20230811PWA_02","Work crew in process of installing one of the leads of the PDGU to the HV conductor using a operating stick when this has come out of end of stick & contacted LV conductors below. Resource partner has what looks to be minor flash burns to face and is currently being taken to local medical clinic for assessment. There was HVI damage and evidence of fire."]
[17,237,"2023-10-13","13:36:00",-38.252687999999999,144.53804299999999,"7 Smithton Grove, Ocean Grove VIC 3226, Australia",30296424,"DDL011","Low voltage AC (<1kV)","Rural Short"," - fuse (powder filled)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0026284","20240701PWA_07","REC has reported fuse on meter panel with Powercor tag on it has caught fire and melted. Fuse is still smoking Crew confirmed and replaced case found during data reviews, limited information & no Images - Deemed fire"]
[17,238,"2023-11-24","18:03:00",-37.477113000000003,144.58905899999999,"25 Cherry Ln, Gisborne VIC 3437, Australia",32044161,"GSB011","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026335","20240703PWA_03","CUST called and adv last week the transformer on LIS 910976 was sparking and there was a small fire, he adv no one called us, as they didn't loose supply.... He has now noticed that his service line is black and smoking today in the rain Crew found damaged service"]
[17,239,"2024-01-07","13:02:00",-37.634262,144.27112,"478 INGLISTON ROAD, BALLAN VIC 3342",32167579,"BMH003","12.7kV AC (SWER)","Rural Long"," - fuse (EDO fuse)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0026597","20240716PWA_03","Reports lights flickering then power went off on a SWER line, possible fuse blown at transformer on pole. EDO fuse tube link burnt and melted. no ground fire Found during Outage data review"]
[17,240,"2024-04-05","03:34:00",-37.971220000000002,144.516761,"155 Old Melbourne Rd, Little River VIC 3211, Australia",30259354,"FNS022","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,"INC-0026618","20240717PWA_01","crew investigating meter alarm found EDO fuse had malfunctioned"]
[17,241,"2024-04-15","20:46:00",-37.672887000000003,144.56626399999999,"46 Rathdowne Cct, Melton West VIC 3337, Australia",30546055,"MLN023","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0026621","20240717PWA_02","crew investigating outage found fuse holder in pillar burnt"]
[17,242,"2024-04-17","02:01:00",-37.496226,144.57648399999999,"25 Daly Street, Gisborne",32048981,"GSB011","Low voltage AC (<1kV)","Rural Short"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,"INC-0025197","20240418PWA_01","In order to meet timely fire reporting requirements to the AER, Powercor is required to submit a final list of fires related to the Powercor distribution network for the year ending 30 June 2024. At the time of preparing this report, Powercor does not know whether the fire at the Gisborne golf club related to the Powercor network, and is unaware of the status or findings of any investigation of this incident by ESV or other relevant authorities. As it is not presently clear whether this incident related to the Powercor network, but Powercor must nevertheless decide whether the incident should be included in its fire reporting, Powercor has chosen to adopt a conservative approach by the inclusion of this uncertain case (noting that this approach is more favourable to customers and less favourable to Powercor than the alternative approach of excluding this incident). "]
[17,243,"2024-03-10","20:25:00",-36.411973000000003,145.090136,"4405 Midland Hwy, Girgarre East VIC 3616 (375 Brewer Rd, Cooma VIC 3616, Australia)",30247157,"SHP014","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,"INC-0024642","20240312PWA_11","Emergency services reported wire down. Upon arrival crew found someone had been trimming trees and a branch had fallen onto the HV line bringing the conductor to the ground and starting a small grass fire. 4 CFA trucks on site. No media, no police, no injuries reported"]
[17,244,"2024-06-16","22:25:00",-38.090322,144.347285,"547 Thompson Rd, Norlane VIC 3214",32084786,"GTSGLE1","66kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"No rating",0.05,1.0000000000000002E-2,"INC-0026666","20240718PWA_07","Party Balloons wrapped around HV conductors, on fire. No ground fire found during outage data review."]
[0,245,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,246,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,247,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,248,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,249,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,250,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,251,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,252,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,253,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,254,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,255,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,256,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,257,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,258,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,259,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,260,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,261,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,262,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,263,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,264,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,265,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C303:O303,Q303,T303:V303)","v":0},266,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(O303=\"\",\"\",IF(O303=\"LBRA only\",0.2,IF(O303=\"HBRA only\",1,IF(O303=\"within electric line construction area\",19.8,IF(O303=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":""},null,{"$f":"IF(Q303=\"\",\"\",IF(Q303=\"No rating\",0.05,IF(Q303=\"Moderate\",0.334,IF(Q303=\"High\",0.678,IF(Q303=\"Extreme\",2.272,4.754)))))","v":""},{"$f":"IF(OR(P303=\"\",R303=\"\"),\"\",IF(AND(O303=\"within electric line construction area\",Q303=\"No forecast\"),1,P303*R303))","v":""}]
[0,267,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,268,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,269,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,270,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,271,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,272,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,273,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,274,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,275,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,276,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,277,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,278,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,279,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,280,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,281,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,282,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,283,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,284,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,285,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,286,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,287,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,288,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,289,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,290,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,291,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,292,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,293,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,294,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,295,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,296,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,297,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,298,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,299,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,300,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]

{"sheet":"3. Systems and Audit","index":4,"n_rows":29,"n_cols":5,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,1,29,4],[3,5,3,6],[4,5,4,6],[5,5,5,6],[6,1,6,4],[9,1,9,4],[14,1,14,4],[10,1,10,4],[13,1,13,4],[12,1,12,4],[11,1,11,4]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2023/24"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 4 - Information or reporting systems"]
[null,"   (1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system"]
[null,"   (2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No"]
[null,"   (3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with"]
[null,"   (4) Whether the data entered into or removed from the IT system has been audited - Yes or No"]
[]
[]
[null,"Table 4: Information or reporting systems"]
[]
[null,"Information or reporting systems","Name","System Audited","Relevant Standards"]
[null,"System 1","Network Incidents Database","Yes","None applicable"]
[null,"System 2","Outage Management System (OMS)","Yes","None applicable"]
[null,"System 3 ","Smallworld GIS (Graphical Information System)","Yes","None applicable"]
[null,"System 4"]
[null,"System 5"]
[null,"System 6"]
[null,"System 7"]
[null,"System 8"]
[]
[null,"The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data."]