{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Contents","Cover","1. F-Factor summary","2. Individual fire start info","3. Systems and Audit"],"not_rendered":{"charts":0,"images":3,"macros":1,"external_links":0,"defined_names":7,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Contents","index":0,"n_rows":22,"n_cols":15,"rows_kept":22,"cut":false,"hidden":false,"merged":[[8,2,9,3],[2,1,2,10],[4,1,4,10]]}
[" "]
[]
[null,"Electricity Distribution Network Service Provider\nF-factor Reporting Template"]
[]
[null,"Table of contents"]
[]
[]
[null,null,"Cover sheet",null,null,"2. Fire start report"]
[]
[]
[]
[null,null,"1. F-factor summary",null,null,"3. Systems and Audit"]
[]
[]
[]
[]
[]
[]
[null,null,{"$f":"\"NOTE: This spreadsheet includes IRU targets up to and including FY\"&yearMax","v":"NOTE: This spreadsheet includes IRU targets up to and including FY2024/25"}]
[]
[null,null,{"$f":"\"NOTE: This spreadsheet was last updated on \"&TEXT(revisionDate,\"DD MMMM YYY\")","v":"NOTE: This spreadsheet was last updated on 23 July 2024"},null,null,null,null,null,null,null,null,null,null,null,"2024-07-23"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,true]

{"sheet":"Cover","index":1,"n_rows":49,"n_cols":7,"rows_kept":49,"cut":false,"hidden":false,"merged":[[10,1,11,8],[13,1,13,8],[42,2,42,3],[42,4,42,7],[38,2,38,3],[38,4,38,7],[41,2,41,3],[41,4,41,7],[37,2,37,3],[37,4,37,7],[32,3,32,8],[30,3,30,8],[15,1,15,8],[26,3,26,8],[28,3,28,8],[26,1,26,2],[31,3,31,5],[14,1,14,8],[16,1,16,8],[17,1,17,8],[21,1,21,8],[19,1,19,8]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Distribution Network Service Provider"]
[null,"Fire start report"]
[]
[null,"This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.  "]
[]
[]
[null,"Colour coding of input sheets:"]
[null,"Dark blue = AER headings"]
[null,"Grey = AER instructions"]
[null,"Yellow = Input cells"]
[null,"Light orange = Automatically-generated cells"]
[]
[null,"Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so."]
[null,"The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings."]
[null,"All dollar amounts are to be unrounded, and in nominal terms."]
[]
[]
[]
[]
[null,"DNSP:",null,"United Energy"]
[]
[null,"DNSP - trading name:",null,"United Energy Pty Ltd\t\t\t\t"]
[]
[null,"DNSP - Australian business number: ",null,"70 064 651 029"]
[]
[null,"Reporting year:",null,"2023/24"]
[]
[]
[]
[]
[null,"Business address","Address",null,"635 Waverley Rd"]
[null,null,"Suburb",null,"Glen Waverley"]
[null,null,null,"State","Victoria","Postcode",3150]
[]
[null,"Postal address","Address",null,"40 Market St"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode",3000]
[]
[]
[null,"Contact name/s"]
[null,"Contact phone/s"]
[null,"Contact email address/s"]

{"sheet":"1. F-Factor summary","index":2,"n_rows":21,"n_cols":15,"rows_kept":21,"cut":false,"hidden":false,"merged":[[5,1,5,2],[3,6,3,8],[4,6,4,8],[5,6,5,8],[11,2,11,3],[12,2,12,3],[13,2,13,3],[6,2,6,3],[7,2,7,3],[8,2,8,3],[9,2,9,3],[10,2,10,3]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"United Energy"},"IRU target:",{"$f":"IF(SUM(K2:O2)=0,\"\",SUM(K2:O2))","v":14.2},null,null,null,null,null,null,"AusNet Services","CitiPower","Jemena","Powercor","United Energy"]
[null,"F-factor data reporting","IRU amount:",{"$f":"IF(SUM('2. Individual fire start info'!S38:S1915)=0,\"\",SUM('2. Individual fire start info'!S38:S1915))","v":24.454400000000021},null,null,null,null,null,"current",{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>K1),\"\",LOOKUP($B3,$J3:$J101,K3:K101))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>L1),\"\",LOOKUP($B3,$J3:$J101,L3:L101))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>M1),\"\",LOOKUP($B3,$J3:$J101,M3:M101))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>N1),\"\",LOOKUP($B3,$J3:$J101,N3:N101))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>O1),\"\",LOOKUP($B3,$J3:$J101,O3:O101))","v":14.2}]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2023/24"},"Revenue adjustment:",{"$f":"IF(OR(D1=\"\",D2=\"\"),\"\",15000*(D1-D2))","v":-153816.00000000032},null,null,null,null,null,"2016/17",247.7,3.4,9.6999999999999993,468,22.3]
[null,null,null,null,null,null,null,null,null,"2017/18",247.7,3.4,9.6999999999999993,468,22.3]
[null,"Table 2: Summary of total fire starts by F factor Order definition",null,null,null,null,null,null,null,"2018/19",247.7,3.4,9.6999999999999993,468,22.3]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\"",null,null,null,null,null,null,null,"2019/20",221.1,3.4,9.6999999999999993,412.8,22.3]
[null,"Kind of Fire Start by definition of fire start under clause 5 of F-factor Order","Total fires by cause",null,null,null,null,null,null,"2020/21",177.5,1.3,4.2,277.60000000000002,18.7]
[null,"Started in or originated from a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1915,'1. F-Factor summary'!$B8)","v":77},null,null,null,null,null,null,"2021/22",164.3,1.9,3.7,235.2,19]
[null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1915,'1. F-Factor summary'!$B9)","v":21},null,null,null,null,null,null,"2022/23",149.69999999999999,1.5,2.7,188,13.9]
[null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1915,'1. F-Factor summary'!$B10)","v":8},null,null,null,null,null,null,"2023/24",131.69999999999999,1.7,2.7,185.5,14.2]
[null,"Started by lightning striking a distribution system or a part of a distribution system ",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1915,'1. F-Factor summary'!$B11)","v":2},null,null,null,null,null,null,"2024/25",127,1.7,2.2999999999999998,147.9,11.7]
[null,"Started by any other thing forming part of or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1915,'1. F-Factor summary'!$B12)","v":2}]
[null,"Otherwise started by a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1915,'1. F-Factor summary'!$B13)","v":0}]
[null,"Total",{"$f":"SUM(C8:C13)","v":110}]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,45496]

{"sheet":"2. Individual fire start info","index":3,"n_rows":237,"n_cols":25,"rows_kept":237,"cut":false,"hidden":false,"merged":[[25,1,25,18],[27,1,27,20],[26,1,26,21],[35,19,35,21],[33,1,33,4],[35,2,35,10],[28,1,28,18],[29,1,29,18],[35,11,35,13],[35,14,35,17],[13,1,13,11],[22,1,22,21],[24,1,24,21],[14,1,14,20],[15,1,15,18],[16,1,16,18],[18,1,18,18],[21,1,21,18],[19,1,19,18],[23,1,23,18],[20,1,20,18],[17,1,17,18],[3,22,3,24],[4,22,4,24],[5,22,5,24],[7,1,7,21],[11,1,11,2],[9,1,9,21]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"United Energy"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2023/24"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"\"Enter into this worksheet fire start data, from any IT system, which have been recorded by \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\". Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.\"","v":"Enter into this worksheet fire start data, from any IT system, which have been recorded by United Energy. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council."}]
[]
[null,"\"Fire\" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.  "]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"United Energy must provide:"}]
[]
[null,"Table 3 - Individual Fire Starts"]
[null,"   (1) Date - dd/mm/yyyy"]
[null,"   (2) Time - if known, the 24-hour time of the fire start hh:mm"]
[null,"   (3) Latitude and longitude of the fire start as decimal coordinates"]
[null,"   (4) Address of the property on which the incident occurred or closest to the incident"]
[null,"   (5) Asset number for the asset nearest the fire start"]
[null,{"$f":"\"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the \"&B1&\" network\"","v":"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the United Energy network"}]
[null,"   (7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)"]
[null,"   (8) Network categorisation - CBD, Urban, Rural Long or Rural Short"]
[null,"   (9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories"]
[null,"   (10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer"]
[null,"   (11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council [Note: This is interpreted as the initiating event rather than the cause. For instance, a fuse failure resulting from a lightning strike would be attributed to \"lightning\" even if the fuse should have protected against such strikes.]"]
[null,"   (12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council"]
[null,"   (13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website) [Note: The fire danger rating applies from the time it was issued; ratings do no apply retrospectively. The rating from the previous day carries into the current day until the rating is changed. If no fire danger rating is issued for the day, a rating of \"No forecast\" applies for the whole day.]"]
[null,{"$f":"\"   (14) \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\"'s record number for the incident\"","v":"   (14) United Energy's record number for the incident"}]
[null,"   (15) ESV's OSIRIS reference number for the incident"]
[null,"   (16) Free text description of the fault containing relevant comments from field reports "]
[]
[]
[]
[null,"Table 2: Individual Fire Starts"]
[]
[null,"Number","Fire starts",null,null,null,null,null,null,null,null,"Fire Type",null,null,"Risk Factors",null,null,null,"IRU \namount","Additional information"]
[null,null,"Date 1","Time 2","Latitude 3","Longitude 3","Address of incident 4","ID of \nnearest \nasset 5","ID of nearest \npolyphase \nline 6","Voltage of line in which \nfire start \noccurred 7","Network categorisation 8","Type of primary asset \ninvolved in fire start 9","Phase(s) of \nline or \ntransformer 10","Kind of fire start as per Clause 5\nof F-factor Order-In-Council 11","Location \narea 12","Location\nmultiplier","Fire \ndanger \nrating 13","Danger multiplier","Product of multipliers","DNSP record number 14","OSIRIS \n(ESV) reference \nnumber 15","Fault \ndescription 16"]
[{"$f":"COUNTA(C38:O38,Q38,T38:V38)","v":17},1,"2023-07-02","09:42:00",-38.362163000000002,145.12721199999999,"133 Stumpy Gully Rd, Balnarring VIC 3926, Australia",1105891,"MTN32","Low voltage AC (<1kV)","Rural"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"No Rating",0.05,0.05,1720710,"20230803UTD_01","UE fault crew attended a premise for an all-supply failure. On arrival they discovered a 3 phase Fused Mains Box feeding an underground service line burnt out on the pole. FMB replaced, u/g re-terminated within new box ",null,null,"Overhead conductors"]
[17,2,"2023-07-02","17:13:00",-38.104238000000002,145.13914199999999,"1 Inverness St, Seaford VIC 3198, Australia",8830557,"CRM24","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1720913,"20230703UTD_04","Crew attended reports of a pole fire from fire authority.  On arrival the discovered a 3 phase Fused Mains Box was severely fire damaged.  Crew replaced box and supply was restored",null,null," - overhead conductor (bare; aluminium core steel reinforced)"]
[17,3,"2023-07-15","05:26:00",-38.140737999999999,145.170356,"1 Manorwoods Dr, Frankston VIC 3199, Australia",3306483,"LWN35","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1724620,"20230717UTD_02","Crew attended reports of smoke from a pole. On arrival a possum shorted across phases on a cable head pole causing a flashover leading to a ground fire. Repairs made, supply restored. ",null,null," - overhead conductor (bare; all aluminium conductor)"]
[17,4,"2023-07-16","18:31:00",-38.231476000000001,145.178483,"27 Park Ln, Somerville VIC 3912, Australia",1111914,"HGS22","Low voltage AC (<1kV)","Rural"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1724802,"20230718UTD_02","IPC ABC connector and lead from substation burnt out. Crew made safe and performed repairs.",null,null," - overhead conductor (bare; copper)"]
[17,5,"2023-07-19","19:19:00",-38.061356000000004,145.126779,"62 Bondi Rd, Bonbeach VIC 3196, Australia",3306958,"CRM15","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1725722,"20230721UTD_01","Crew were called to a report of a pole fire. On arrival the discovered a 3 phase Fused Mains Box was severly fire damaged. Crew replaced box and supply was restored",null,null," - overhead conductor (bare; steel)"]
[17,6,"2023-07-29","12:07:00",-38.357968999999997,145.15886900000001,"19 Wellington Rd, Bittern VIC 3918, Australia",1107246,"HGS23","22kV AC","Rural"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","HBRA only",1,"No Rating",0.05,0.05,1727837,"20230803UTD_02","Crew were called to an all-supply failure and discovered a candled 6 Amp Boric Acid fuse. Replaced BA fuse on blue phase.",null,null," - overhead conductor (ABC)"]
[17,7,"2023-08-04","12:47:00",-37.935054999999998,145.05002300000001,"486 State Route 14, Moorabbin VIC 3189, Australia",1816978,"MR 15","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1729428,"20230808UTD_01","Crew attended a FRV reported pole fire.  On arrival the crew could find no evidence of fire damage up the pole but noticed the pole had a scorch mark at the base.  Although not conclusive, the likelihood of insulator leakage into the pole was the deemed the most likely scenario. Crew has organised insulator cleaning.",null,null," - overhead conductor (covered uninsulated)"]
[17,8,"2023-09-05","06:00:00",-37.893298000000001,145.09599600000001,"5 Park Rd, Oakleigh VIC 3166, Australia",2329427,"OAK35","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1737260,"20230906UTD_01","FRV advised of a fire on a pole, on attendance the crew discovered a small control box for a watchman light had caught fire resulting in molten metal singeing grass underneath. Crew cut away all leads made safe and referred for replacement",null,null," - overhead conductor (insulated)"]
[17,9,"2023-09-08","14:19:00",-38.352882000000001,145.025272,"31 Bowrings Rd, Red Hill VIC 3937, Australia",1308150,"DMA23","22kV AC","Rural"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"No Rating",0.05,0.05,1738541,"20230911UTD_02","CFA reported a fire start from tree branch contact to HV overhead conductors. On arrival crew discovered burnt branches and broken conductor.  Crew arrived made safe cut tree away clear and made repairs to conductor.",null,null,"Service lines"]
[17,10,"2023-09-11","18:42:00",-37.780627000000003,145.163535,"267 Blackburn Rd Service Rd, Doncaster East VIC 3109, Australia",7070613,"DC10","Low voltage AC (<1kV)","Urban","Public lighting","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1739329,"20230912UTD_01","Street light head on fire. Isolate for Fire services to spray fire to extinguish.",null,null," - overhead service conductor (residential)"]
[17,11,"2023-09-23","02:24:00",-38.167262999999998,145.206851,"350 North Rd, Langwarrin VIC 3910, Australia",3302140,"FSH21","22kV AC","Rural"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","HBRA only",1,"No Rating",0.05,0.05,1742536,"20231002UTD_01","After replacing a transformer fuse the crew noticed the red phase BA fuse at a nearby Switch pole was candling. The crew replaced 15e BA fuse red phase.",null,null," - overhead service conductor (commercial / industrial)"]
[17,12,"2023-10-03","09:23:00",-38.016339000000002,145.22332399999999,"25 Capital Dr, Dandenong South VIC 3175, Australia",635252,"DVY22","22kV AC","Urban"," - transformer (pole mounted)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1744565,"20231003UTD_02","Crew attended reports of a transformer on fire.  On attendance they discovered a small branch from council tree had bridged between the white phase bushing and transformer.  Crew isolated supply and removed branch.",null,null," - overhead service conductor (subdivision / construction)"]
[17,13,"2023-10-03","11:42:00",-38.471437999999999,144.94338200000001,"535 Meakins Rd, Flinders VIC 3929, Australia",9821901,"RBD21","22kV AC","Rural"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1744669,"20231004UTD_01","During a lightning storm a crew was investigating an outage discovered a 3/12 steel conductor had failed at the wrap on which showed signs of rust. The conductor left scorch marks in the grass underneath. Crew made safe and repaired section of damaged conductor.",null,null," - overhead service conductor (other)"]
[17,14,"2023-10-03","14:21:00",-37.982557999999997,145.22697299999999,"4 Bess Ct, Dandenong VIC 3175, Australia",625984,"DN 11","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1744740,"20231006UTD_01","Crew were called and discovered a centre phase insulator had become detached from \"P\" Bracket and was resting on HV steel crossarm.  This resulted in a small fire start at the LV kingbolt.  Centre phase \"P\" Bracket replaced along with LV crossarm",null,null," - underground service cable (residential)"]
[17,15,"2023-10-03","18:08:00",-38.201521999999997,145.126349,"162A Moorooduc Hwy, Mount Eliza VIC 3930, Australia",3314709,"FSH12","Low voltage AC (<1kV)","Rural"," - connection box","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1744793,"20231004UTD_02","Crew responded from a report of sparking/Arcing coming from a pole.  On arrival the crew discovered a pole mounted 3 phase FMB had a bird next inside which had ignited burning out the FMB. Crew Isolated and replaced the FMB.",null,null," - underground service cable (commercial / industrial)"]
[17,16,"2023-10-09","14:45:00",-37.982112999999998,145.130763,"119-121 Centre Dandenong Rd, Dingley Village VIC 3172, Australia",611818,"SS 23","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1746209,"20231012UTD_02","Crew attended a report of a crossarm hanging down from a transformer sparking. On arrival the crew discovered a HV dressing down crossarm had burnt through on the road side dropper. Crew isolated transformer replaced HV fuse units, 15e ba fuses, 22kv lightning arrestors, hvabc dropper leads.",null,null," - underground service cable (subdivision / construction)"]
[17,17,"2023-10-10","08:15:00",-37.894241000000001,145.13794300000001,"55 Ricketts Rd, Mount Waverley VIC 3149, Australia",600877,"NO 04","22kV AC","Urban"," - dropper / bridge","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1746519,"20231012UTD_03","Customer rang though that a piece of cardboard has blown onto transformer has caught fire.  On arrival the crew discovered that the cardboard had landed between HV the bushings on a ground type transformer and had ignited. Crew replaced red and white phase hv droppers/hv bushing covers and red and white phase 63a powder filled fuses ",null,null," - underground service cable (other)"]
[17,18,"2023-10-18","12:21:00",-38.213405999999999,145.055575,"8 Tallis Dr, Mornington VIC 3931, Australia",1100893,"MTN35","22kV AC","Rural"," - overhead conductor (ABC)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1748518,"20231018UTD_01","Crew attended a report of cable sparking and small flame present. On arrival they found a HV Cable failed and caught fire and dropped to the ground (there was no evidence of any ground fire) Crew isolated cable and arranged repairs.",null,null,"Underground cables"]
[17,19,"2023-10-18","22:49:00",-37.937423000000003,145.00258700000001,"8/440 Hampton St, Hampton VIC 3188, Australia",1818347,"SR 23","Low voltage AC (<1kV)","Urban"," - lamps (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1748636,"20231019UTD_04","Customer reported fire on street light pole. On arrival fire was extinguished but 150W sodium head was burnt out. Crew arranged for head to be replaced",null,null," - underground cable"]
[17,20,"2023-10-22","12:45:00",-38.136297999999996,145.13520800000001,"23 Fairway St, Frankston VIC 3199, Australia",3307929,"FTN11","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1749368,"20231023UTD_03","Fire HV Crossarm and Hvi. Crew made site safe and prepared for repairs with other crews.",null,null," - underground communications cable"]
[17,21,"2023-10-23","21:49:00",-38.121102,145.12519,"259-262 Nepean Hwy, Seaford VIC 3198, Australia",3317739,"FTN21","22kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1749791,"20231024UTD_01","FRV advised fire on a pole top. On arrival the crew discovered the HV leads looked to have discharged creating a small fire as witnessed by the FRV crew.  Crew isolated and repair leads and HV covers to transformer.",null,null,"Poles"]
[17,22,"2023-10-25","10:49:00",-37.920521999999998,145.18875499999999,"16 Rata St, Wheelers Hill VIC 3150, Australia",9957896,"MGE12","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1750266,"20231025UTD_02","Crew attended a report of a fault and on arrival discovered a burnt-out pillar which showed clear signs a fire was present at some point.  Although the fire was contained inside the pillar there was scorch marks on the ground within these confines. Crew made safe and arranged U/G crew to repair.",null,null," - pole (concrete)"]
[17,23,"2023-10-27","18:07:00",-37.834052,145.17309800000001,"335 Springvale Rd, Forest Hill VIC 3131, Australia",7048120,"NW 14","22kV AC","Urban"," - surge diverter","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1750975,"20231030UTD_06","Crew were called to an outage and on arrival discovered a surge diverter failed and the resulting flashover ignited a small grass fire underneath.   Crew cut surge diverter lead away from line and restored supply.",null,null," - pole (steel)"]
[17,24,"2023-11-02","17:39:00",-38.284692999999997,145.17986500000001,"20 Graydens Rd, Tyabb VIC 3913, Australia",1105759,"HGS22","22kV AC","Rural"," - pole (wood)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1752385,"20231103UTD_01","Crew were called to a car into a pole.  On arrival the crash has caused the HV conductors to fail onto the steel crossarm igniting a pole fire.  Crew made safe and arranged repairs.",null,null," - pole (wood)"]
[17,25,"2023-11-08","08:05:00",-38.291414000000003,144.988474,"1 Stanley Cres, Mount Martha VIC 3934, Australia",1314143,"DMA14","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1753214,"20231108UTD_01","Crew were called to a reported pole on fire. On arrival, the crew discovered a LV Krone box had overheated and caught fire causing the LV ABC conductor to fail resulting in a small ground fire. Crew made safe prepared all isolations and prepared for repairs.",null,null,"Crossarms"]
[17,26,"2023-11-17","00:43:00",-38.171014999999997,145.24007599999999,"640 North Rd, Cranbourne South VIC 3977, Australia",3300970,"LWN21","22kV AC","Rural"," - fuse (boric acid)","single phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1755899,"20231117UTD_01","Crew were called to a report of a fire start on pole. On arrival they discovered a B/A HV Fuses candled and had dropped debris onto grass causing a small grassfire. Crew replaced x2 B/A fuse units and x2 65amp B/A fuses.",null,null," - crossarm (wood)"]
[17,27,"2023-11-21","15:35:00",-37.849316999999999,145.12814,"24 Andrews St, Burwood VIC 3125, Australia",7026468,"EB 14","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1756811,"20231122UTD_02","Small fire start at base of pole from balloon contact to HV Conductors. Crew made safe noticed small fire at base of pole.",null,null," - crossarm (steel)"]
[17,28,"2023-12-03","13:38:00",-38.370109999999997,144.90892199999999,"181 Jetty Rd, Rosebud VIC 3939, Australia",1311693,"RBD12","22kV AC","Rural"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1759739,"20231205UTD_04","A tree fault caused feeder to trip instead of ACR due to LLW mode being enabled at time of fault. Several Km's upstream of this fault a set of Mid Span Isolators failed due to the fault current. This caused molten metal to fall to the ground and ignite a small grass fire. Crew made safe and removed the Mid Span Isolators.",null,null," - crossarm (other)"]
[17,29,"2023-12-08","12:35:00",-37.933500000000002,145.05638500000001,"21 E Boundary Rd, Bentleigh East VIC 3165, Australia",1802116,"MR 15","11kV AC","Urban"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1761106,"20231214UTD_04","FRV reported that a tree has fallen onto the powerlines and was on fire. On arrival the crew observed that there was no active fire, but a large branch was resting on the HV.  Crew removed branch and repaired 2 broken strands of conductor and restored supply.",null,null,"Overhead assets"]
[17,30,"2023-12-08","15:09:00",-37.794063999999999,145.14225999999999,"77 Wetherby Rd, Doncaster VIC 3108, Australia",7061505,"DC 03","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1761198,"20231214UTD_03","Crew were called to reports of a branch was on fire. On arrival private tree was clear of lines when crew arrived and was not on fire. Crew inspected lines for damage but all was ok.",null,null," - capacity balancing units"]
[17,31,"2023-12-08","16:04:00",-37.918911000000001,145.04173800000001,"520 Centre Rd, Bentleigh VIC 3204, Australia",2321229,"BT 13","Low voltage AC (<1kV)","Urban"," - pole (wood)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1761243,"20231211UTD_03","Crew were called by FRV to a report of a pole fire. On arrival they discovered the red phase LV conductor was in contact with a streetlight stay wire which had caused a pole fire.  The crew disconnected stay wire and arranged pole replacement.",null,null," - connector / termination"]
[17,32,"2023-12-09","21:23:00",-38.365288,144.91836799999999,"127 Austin Ave, McCrae VIC 3938, Australia",1316648,"RBD24","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1761534,"20231214UTD_02","RB7683 - W & B ref to tbl#1761536 - pole number 1316648 cause is possum Found what we think is reminisce of a possum on white and blue 22kv phases, conductor not damaged, removed what was left from the line with operating stick, all ok on completion. no signs of fire.",null,null," - dropper / bridge"]
[17,33,"2023-12-13","00:15:00",-37.972589999999997,145.07069000000001,"33 Elliott St, Cheltenham VIC 3192, Australia",1813116,"M  31","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"High",0.67800000000000005,0.1356,1762422,"20231213UTD_01","Crew were called to a lightning strike on overhead conductors which has caused fire at meter board and damaged meter and switchboard wiring.",null,null," - guy wire"]
[17,34,"2023-12-13","14:09:00",-37.928511,145.025295,"38 Studley Rd, Brighton East VIC 3187, Australia",1806710,"MR 31","11kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1762676,"20231219UTD_02","Crew were called by FRV in relation to a gum tree branch failure from council park which brought down HV conductors.  Although no mention of fire in early report subsequent photos of the branch indicate flames were likely present at some point. Conductor repaired supply restored. ",null,null," - insulator tie wires / connections"]
[17,35,"2023-12-13","21:15:00",-38.227663999999997,145.031678,"34 Nunns Rd, Mornington VIC 3931, Australia",1100134,"MTN34","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1762774,"20231214UTD_01","Crew were called to reports of a pole on fire. On arrival they discovered a 3 phase fused mains box caught fire.  Crew replaced box and restored supply",null,null," - insulators"]
[17,36,"2023-12-18","00:32:00",-38.359516999999997,144.75462099999999,"64 Hughes Rd, Sorrento VIC 3943, Australia",1306319,"STO13","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1763720,"20231218UTD_02","Crew were called to reports of a loud bang and loss of supply.  On arrival they discovered a LV 3 phase krone box had caught fire.  Crew isolated and replaced krone box and damage droppers.",null,null," - tower"]
[17,37,"2023-12-22","17:36:00",-38.353451999999997,145.19780900000001,"120 Disney St, Crib Point VIC 3919, Australia",1110732,"HGS31","22kV AC","Rural"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1765079,"20231224UTD_01","Crew were called to reports of a tree on conductor.  On arrival the crew discovered a cypress branch had failed and landed across 2 phases. Although branch was on the ground when crew arrived damage is consistent with flame being present at some point. Crew did some emergency clearing and referred to Veg crew to complete clean up.",null,null," - traction lines"]
[17,38,"2023-12-25","00:15:00",-38.320847000000001,144.72067899999999,"3684 Point Nepean Rd, Portsea VIC 3944, Australia",1302761,"STO22","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1765324,"20231225UTD_01","Crew were investigation an outage and they discovered a HV intermediate crossarm had caught fire.  Crossarm replaced, supply restored",null,null,"Underground assets"]
[{"$f":"COUNTA(C76:O76,Q76,T76:V76)","v":17},39,"2023-12-26","22:20:00",-37.935113999999999,144.99795700000001,"91 Orlando St, Hampton VIC 3188, Australia",1809963,"MR 13","11kV AC","Urban"," - surge diverter","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1765694,"20240820UTD_01","Crew were called to reports of a deceased possum was on fire on pole.  On arrival the crew discovered a possum flashed over at the surge diverters.  Crew organised replacement of all surge diverters.",null,null," - LV pillar"]
[17,40,"2023-12-31","21:38:00",-38.328752000000001,144.70465100000001,"7 Bass Rd, Portsea VIC 3944, Australia",1318262,"STO13","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1766279,"20240102UTD_01","Crew were called to reports of a pole fire.  On arrival they discovered a LV 3 phase krone box had caught fire.  Crew isolated and replaced krone box and retored supply.",null,null," - services pit"]
[17,41,"2024-01-01","14:32:00",-37.775773999999998,145.18282600000001,"444 Serpells Terrace, Donvale VIC 3111, Australia",7070503,"NW 13","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1766309,"20240102UTD_02","Crew were called to a meter board fire.  On arrival the discovered a meter board fuse looks to have overheated causing the meter panel to catch fire.  Customer advised to lodge a claim for damage/REC costs with UE",null,null,"Transformers"]
[17,42,"2024-01-06","14:57:00",-38.372402000000001,144.78912800000001,"70 Murray St, Rye VIC 3941, Australia",1303185,"STO14","22kV AC","Rural"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1767059,"20240109UTD_05","Customer called to report a pole mounted transformer was sparking and some flame was witnessed.  On arrival the crew discovered broken HV bushing on transformer.  Crew isolated transformer and arranged replacement.",null,null," - transformer (pole mounted)"]
[17,43,"2024-01-06","18:02:00",-38.366809000000003,144.920084,"4 Wilgah Rd, Rosebud VIC 3939, Australia",1310780,"RBD24","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1767089,"20240109UTD_03","Crew were called to reports of material falling from pole into grass.  On arrival the crew observed white phase LV isolator ampact connection lug was arcing and has scorched the LV crossarm indicating the possibility of a flame at some point. There was no evidence of a ground fire. Crew made safe replaced white phase isolator",null,null," - transformer (kiosk mounted)"]
[17,44,"2024-01-07","21:13:00",-38.110813,145.133554,"53A Seaford Grove, Seaford VIC 3198, Australia",3305389,"FTN12","Low voltage AC (<1kV)","Urban"," - lamps (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1767187,"20240109UTD_06","Customer reported that a street light was on fire. On arrival there was no visible flame however the crew replaced a 250W HP Sodium head. Crew made safe and replaced streetlight .",null,null," - transformer (ground outdoor mounted)"]
[17,45,"2024-01-09","15:38:00",-37.907193999999997,144.987843,"284 State Route 33, Brighton VIC 3186, Australia",1805652,"NB 33","11kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1767623,"20240111UTD_01","Top of pole fire at crossarm brace straps burnt through crossarm dropped into LV No HVI.  Crew made safe prepared for repairs.",null,null," - transformer (indoor chamber mounted)"]
[17,46,"2024-01-09","15:51:00",-38.159249000000003,145.16198,"21 Kilburn Cres, Frankston VIC 3199, Australia",3315069,"FSH34","22kV AC","Urban"," - underground cable","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1767629,"20240125UTD_02","Customer reported flames emanating from base of a pole. On arrival crew discovered a HV U/G cable had faulted and caused a flashover and likely flames at the base of pole where grass was blackened. Section of cable was isolated and repairs initiated.",null,null," - transformer (any other type)"]
[17,47,"2024-01-11","17:29:00",-37.939554000000001,145.13964999999999,"A229/59 Autumn Terrace, Clayton South VIC 3169, Australia",637944,"SS 22","Low voltage AC (<1kV)","Urban"," - underground cable","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1768204,"20240112UTD_01","Fire services reported a fire at base of a pole. On arrival the crew discovered an LV Underground cable faulted and caught fire and started a small grass fire at base of pole.  Crew made safe and arranged replacement of cable.",null,null," - measurement transformer (current transformer)"]
[17,48,"2024-01-12","07:31:00",-37.852048000000003,145.035776,"1269 Malvern Rd, Malvern VIC 3144, Australia",2312846,"K  24","Low voltage AC (<1kV)","Urban"," - underground cable","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1768281,"20240118UTD_03","Customer reported a pole on fire. On arrival the crew discovered an LV Underground cable faulted and caught fire and burnt the of pole.  Although burnt debris on ground no vegetation underneath saw no ground fire. Crew made safe and arranged replacement of cable.",null,null," - measurement transformer (voltage transformer)"]
[17,49,"2024-01-12","21:30:00",-38.372115000000001,144.76711399999999,"81 Dana Ave, Blairgowrie VIC 3942, Australia",1304618,"STO21","Low voltage AC (<1kV)","Rural"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1768541,"20240115UTD_01","Fire services reported a pole on fire. On arrival the crew discovered an LV 3 phase krone box faulted and caught fire. Crew made safe and arranged replacement of Krone box.",null,null," - measurement transformer (capacitive voltage transformer)"]
[17,50,"2024-01-14","21:51:00",-37.932181,145.00465399999999,"6A Hamel St, Hampton VIC 3188, Australia",1809416,"MR 12","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1768833,"20240130UTD_04","Emergency services reported a tree has fallen onto the wires and is on fire and FRV are on the way.  Although no fire was witnessed by the crew witness reports are consistent with a likely fire event.  Branch was removed from conductor.",null,null,"Fuses and switchgear"]
[17,51,"2024-01-18","18:16:00",-38.426183999999999,144.85915499999999,"725 Truemans Rd, Fingal VIC 3939, Australia",1306118,"STO21","22kV AC","Rural"," - dropper / bridge","two phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1770173,"20240119UTD_03","Fire services reported a pole on fire. On arrival the crew discovered two live line clamps burnt off Ampact bail connectors on pole causing small grass fire.  Crew made safe and arranged replacement connections.",null,null," - fuse (boric acid)"]
[17,52,"2024-01-21","12:03:00",-38.373367000000002,144.92339100000001,"76 Elizabeth Dr, Rosebud VIC 3939, Australia",1311231,"RBD24","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1770743,"20240122UTD_01","Crew were called to reports of a pole on fire. On arrival they discovered a single-phase fused mains box caught fire.  Although debris on the ground crew reported grass too green/wet to catch alight. Crew replaced box and restored supply",null,null," - fuse (EDO fuse)"]
[17,53,"2024-01-21","23:19:00",-37.886240000000001,145.03738000000001,"67 Neerim Rd, Caulfield VIC 3162, Australia",2334358,"CFD24","11kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1770808,"20240122UTD_02","FRV reported that a tree has fallen onto the powerlines and possibly caught fire. On arrival the crew observed that there was a large branch was resting on the HV and showed signs fire had been present at some point.  Crew made safe and cut large tree branch clear of conductors.",null,null," - fuse (Fault Tamer)"]
[17,54,"2024-01-23","08:28:00",-38.193317999999998,145.21667099999999,"1795 Dandenong-Hastings Rd, Langwarrin South VIC 3911, Australia",3301031,"HGS33","22kV AC","Rural"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1771207,"20240124UTD_01","Crew were called to patrol a feeder that had successfully reclosed. During the patrol they discovered a 65amp B/A fuse had candled. Crew made safe and replaced fuse.",null,null," - fuse (powder filled)"]
[17,55,"2024-01-24","14:41:00",-37.925144000000003,145.143136,"State Route 49, Clayton South VIC 3169, Australia",8806193,"SVW41","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1771744,"20240130UTD_02","Customer reported Palm frond briefly caught fire when contacting HV in the wind.  Although no fire was witnessed by the crew when the frond was removed the crew identified charring on the end of the frond consistent with a likely fire event. Frond was removed from conductor.",null,null," - fuse (any other type)"]
[17,56,"2024-02-02","01:27:00",-38.371561,145.04369800000001,"207 Red Hill Rd, Red Hill South VIC 3937, Australia",1308542,"DMA15","22kV AC","Rural"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1773673,"20240202UTD_01","UE Analytics monitoring of the network requested a crew to investigate a set of HV Fuses due to sustained low volts. During the investigation they discovered a 65amp B/A fuse had candled.  Crew made safe and replaced fuse.",null,null," - circuit breaker"]
[17,57,"2024-02-02","14:30:00",-37.875127999999997,145.126711,"63 A Wadham Parade, Mount Waverley VIC 3149, Australia",8802712,"BW 33","11kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1773899,"20240205UTD_01","UE recieved a call from FRV to advise report of pole/wires on fire. On arrival the crew confirmed a fire start on both the branch and crossarm caused by a branch from a council tree. Crew isolated supply removed branch and replaced damaged crossarms.",null,null," - switch (disconnector/isolator)"]
[17,58,"2024-02-04","16:26:00",-37.801245999999999,145.12347,"65 Woodhouse Grove, Box Hill North VIC 3129, Australia",7031305,"DC 05","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1774202,"20240205UTD_02","A customer UE called about a loud bang and a small grass fire underneath a pole.  On arrival crew found a council managed tree in a park had grown through the LV and had clashed the LV conductors igniting a small grass fire at the base of pole. Crew cut tree away from LV, fitted spreader and restored supply.",null,null," - switch (earth)"]
[17,59,"2024-02-12","06:44:00",-37.975960000000001,145.01774900000001,"583/589 Balcombe Rd, Black Rock VIC 3193, Australia",1811668,"BR 04","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1776205,"20240212UTD_01","Crew were called to reports of a pole fire.  On arrival they discovered a LV 3 phase krone box had caught fire.  Debris from box scorched a small amount of grass underneath.  Crew isolated and replaced krone box and retored supply.",null,null," - switch (FuseSaver)"]
[17,60,"2024-02-12","18:42:00",-37.948739000000003,145.205769,"97 Rawdon Hill Dr, Dandenong North VIC 3175, Australia",8812331,"LD 06","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1776445,"20240213UTD_01","Crew were called to reports of a LV Pillar on fire. On arrival the crew discovered a burnt-out pillar which had also singed grass nearby. Crew made safe and organised repairs.",null,null," - switch (any other type)"]
[17,61,"2024-02-13","15:14:00",-38.090660999999997,145.17738600000001,"2 Stephanie Ct, Carrum Downs VIC 3201, Australia",9871936,"CRM14","Low voltage AC (<1kV)","Rural"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45440000000000003,1779825,"20240822UTD_04","Subsequent to a major storm event on the 13 February a customer reported that meter box and associated wiring has likely caught fire as a result of an HV injection.  Crew isolated supply while REC affected repairs",null,null,"SCADA, network control and protection systems"]
[17,62,"2024-02-13","15:33:00",-37.918906,145.146727,"25 Garden Rd, Clayton VIC 3168, Australia",622914,"SV 23","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45440000000000003,1776445,"20240215UTD_08","Crew were called to a major tree trunk failure in which a large Eucalypt broke off at the trunk and crashed through the HV conductors igniting the tree in the process. Crew isolated line before repairing conductors..",null,null," - audio frequency load controller (AFLC)"]
[17,63,"2024-02-13","15:39:00",-38.169176999999998,145.22417799999999,"500 North Rd, Pearcedale VIC 3912, Australia",3300979,"LWN21","22kV AC","Rural"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Extreme",2.2719999999999998,2.2719999999999998,1777723,"20240215UTD_01","During major storm event a crew attended a report of wires down. On arrival crew discovered a fallen tree branch had brought down HV conductors.  One of the conductors made contact with the pole causing a small fire on the pole.  There was no ground fire or fire damage evident on the broken branch.",null,null," - arc suppresion coil"]
[17,64,"2024-02-13","18:13:00",-37.989970999999997,145.040719,"66 Tramway Parade, Beaumaris VIC 3193, Australia",1810767,"BR 09","11kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45440000000000003,1777563,"20240215UTD_02","During major storm event customer reports indicate a tree branch on fire. On arrival the crew removed a branch which had broke and fallen on the HV conductors. Branch cleared. Supply restored",null,null," - automatic circuit recloser (ACR)"]
[17,65,"2024-02-13","20:09:00",-37.919536000000001,145.18009599999999,"79 Chancellor Dr, Wheelers Hill VIC 3150, Australia",614566,"MGE23","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45440000000000003,1777868,"20240215UTD_03","During major storm event customer reports indicate a road reserve tree branch on fire. On arrival the crew removed a branch which had broke and fallen on the HV conductors. Branch cleared. Supply restored.",null,null," - communications linear assets"]
[17,66,"2024-02-13","21:24:00",-37.89105,145.188411,"73 Madigan Dr, Glen Waverley VIC 3150, Australia",612985,"MGE23","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45440000000000003,1778000,"20240215UTD_04","During major storm event customer reports indicate a tree branch on fire. On arrival the crew removed a branch which had broke and fallen on the HV conductors. Branch cleared. Supply restored",null,null," - communications network assets"]
[17,67,"2024-02-13","23:12:00",-37.936205000000001,145.17130700000001,"8 Smith Rd, Springvale VIC 3171, Australia",622328,"SVW53","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45440000000000003,1778143,"20240215UTD_05","During major storm event FRV reports indicate a road reserve tree branch on fire. On arrival the crew noticed the branch which had broken and fallen on the HV conductors had cleared itself.  Supply restored",null,null," - communications site infrastructure"]
[17,68,"2024-02-21","06:35:00",-38.235053999999998,145.06177600000001,"24 Latham St, Mornington VIC 3931, Australia",9867969,"MTN21","22kV AC","Urban"," - surge diverter","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1782060,"20240223UTD_02","FRV reported to UE there was a fire on pole.  Although there was no fire when the crew arrived on site there was a blown PF fuse and a damaged LA that needed replacement on a Cable Head pole. Made safe and organised LA replacement.",null,null," - field devices"]
[17,69,"2024-02-21","19:21:00",-38.299984000000002,145.17576,"14 Hilltop Rise, Hastings VIC 3915, Australia",1109843,"HGS23","22kV AC","Rural"," - fuse (powder filled)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1782470,"20240223UTD_03","Customer reported explosion on pole and started a small fire which they extinguished underneath. On arrival the crew discovered a candled HV 5-amp PF Fuse. Replaced PF Fuse and restored supply.",null,null," - local network wiring assets"]
[17,70,"2024-02-22","10:36:00",-37.884791,145.12038000000001,"4 Leonie Ave, Mount Waverley VIC 3149, Australia",2324419,"OAK33","11kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45440000000000003,1782712,"20240223UTD_04","Customer reported tree branch on HV.  On arrival the crew discovered a tree branch across the HV which was severely charred indicating fire at some point.  Crew removed branch and restored supply.",null,null," - master station assets"]
[17,71,"2024-02-22","12:18:00",-38.196759,145.13208599999999,"104 Moorooduc Hwy, Frankston South VIC 3199, Australia",3314720,"FSH12","22kV AC","Rural"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Extreme",2.2719999999999998,2.2719999999999998,1782810,"20240223UTD_05","Crew were called to reports of a large tree that had brought down HV conductor and ignited a ground fire.  On arrival the crew were met by CFA crew extinguishing a ground fire and major damage to conductors. Crew made safe and arrange vegetation crews to clear tree.",null,null," - neutral earthing resistor"]
[17,72,"2024-02-22","12:27:00",-38.222810000000003,145.10164800000001,"590 C784, Mornington VIC 3931, Australia",1104287,"FSH-MTN 66kV","66kV AC","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","HBRA only",1,"Extreme",2.2719999999999998,2.2719999999999998,1782821,"20240223UTD_06","Secondary fault to tree fault further upstream causing 66kV Ampac connector failure causing grass fire. Isolated line and affected repairs.",null,null," - oil-filled circuit recloser (OCR)"]
[17,73,"2024-02-22","15:40:00",-37.952005999999997,145.02112199999999,"283 State Route 19, Highett VIC 3190, Australia",1824961,"SR 25","11kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45440000000000003,1782905,"20240223UTD_07","FRV advised of a tree branch on fire. On arrival a large eucalypt branch was across HV conductors. Removed tree made repairs restored supply.",null,null," - rapid earth fault current limiter (REFCL)"]
[17,74,"2024-02-25","22:49:00",-38.053930000000001,145.118135,"2 Sherwood Ave, Chelsea VIC 3196, Australia",3302871,"CRM13","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1783697,"20240226UTD_04","Customer and FRV reported a small fire on a pole.  On arrival the crew discovered a burnt-out isolator had dropped debris causing scorch marks on the ground underneath. Replaced LV Isolator and restored supply.",null,null," - surge diverter"]
[17,75,"2024-02-26","08:40:00",-37.948,145.06392299999999,"39 Keys Rd, Moorabbin VIC 3189, Australia",1816802,"HT 07","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1783797,"20240226UTD_05","Crew were called to a pole fire; on arrival they discovered that a 22kV strain crossarm was severely damaged via leakage from the glass insulator discs. Made safe and organised replacement HV Strain Arm",null,null," - voltage regulator"]
[17,76,"2024-03-04","08:17:00",-38.238636999999997,145.226867,"48 Bungower Rd, Somerville VIC 3912, Australia",9816818,"HGS33","22kV AC","Rural"," - fuse (boric acid)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1785616,"20240305UTD_02","Crew were called to reports of sparking pole. On arrival they discovered 2 X BA fuses had burn marks on the barrel which they believe was caused by a lightning strike.  Crew replaced fuses and restored supply.",null,null,"Public lighting"]
[17,77,"2024-03-07","16:05:00",-38.059801,145.11784800000001,"4 Shenfield Ave, Bonbeach VIC 3196, Australia",3302970,"CRM23","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1786825,"20240312UTD_12","Crew were called to reports of a pole on fire. On arrival they discovered there was no visible fire present however a 3 phase fused mains box had damage consistent with a likely fire.  Crew replaced box and restored supply.",null,null," - brackets (major road)"]
[17,78,"2024-03-09","11:42:00",-37.90016,145.08980600000001,"36 Portman St, Oakleigh VIC 3166, Australia",2325487,"OAK22","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45440000000000003,1787295,"20240312UTD_14","Crew were called to reports of a pole fire.  On arrival they discovered a LV 3 phase krone box had caught fire. Crew isolated and replaced krone box and restored supply.",null,null," - brackets (minor road)"]
[17,79,"2024-03-09","15:01:00",-38.371977999999999,144.77387400000001,"12 Hilltop Ave, Blairgowrie VIC 3942, Australia",1304663,"STO21","Low voltage AC (<1kV)","Rural"," - switch (disconnector/isolator)","single phase","Started in or originated from a distribution system","HBRA only",1,"Extreme",2.2719999999999998,2.2719999999999998,1787324,"20240312UTD_03","Crew were called to reports of a pole fire. On arrival the crew discovered that the contacts on the red phase LV isolator had overheated dropping molten metal to the ground igniting a small grass fire. Crew replaced isolator.",null,null," - lamps (major road)"]
[17,80,"2024-03-09","17:15:00",-38.331203000000002,144.711231,"338 Hotham Rd, Portsea VIC 3944, Australia",1307142,"STO13","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45440000000000003,1787339,"20240313UTD_02","Crew were called to reports of a pole fire.  On arrival they discovered a LV 3 phase krone box had caught fire.  Debris from box scorched a small amount of grass underneath.  Crew isolated and replaced krone box and restored supply.",null,null," - lamps (minor road)"]
[17,81,"2024-03-10","17:35:00",-38.197395,145.08616599999999,"46 A Kolora Cres, Mount Eliza VIC 3930, Australia",3312892,"MTN22","Low voltage AC (<1kV)","Rural"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1787579,"20240313UTD_03","Crew were called to reports of a pole fire.  On arrival they discovered an IPC connecter on a bare/ABC interface connection showing severe melting and charring consistent with the likely fire event as described. Crew isolated and replaced interface connection and restored supply.",null,null," - luminaires (major road)"]
[17,82,"2024-03-10","18:13:00",-38.310507000000001,145.002501,"93A Rymer Ave, Safety Beach VIC 3936, Australia",1303024,"DMA12","Low voltage AC (<1kV)","Urban"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1787609,"20240312UTD_09","Crew were called to reports of a pole fire.  On arrival they discovered the IPC connections had overloaded and caught fire damaging the LV leads to a LV Krone Box. Replaced LV leads and connections.",null,null," - luminaires (minor road)"]
[17,83,"2024-03-10","18:31:00",-37.905920999999999,145.12055100000001,"57 Patrick St, Oakleigh East VIC 3166, Australia",2325875,"CDA23","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1787625,"20240312UTD_11","Crew were called to reports of a pole fire.  On arrival they discovered a LV 3 phase krone box had caught fire.  Debris from box scorched a small amount of grass underneath.  Crew isolated and replaced krone box and restored supply.",null,null," - poles / columns (major road)"]
[17,84,"2024-03-10","18:36:00",-38.399507,144.81327899999999,"328 Dundas St, Rye VIC 3941, Australia",1305324,"STO14","Low voltage AC (<1kV)","Rural"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,1787629,"20240312UTD_05","Crew were called to reports of a pole on fire. On arrival they discovered a single-phase fused mains box caught fire and molten plastic ignited a small ground fire. Crew replaced box and restored supply.",null,null," - poles / columns (minor road)"]
[17,85,"2024-03-10","20:13:00",-38.207140000000003,145.22462899999999,"23 Middle Rd, Pearcedale VIC 3912, Australia",3302146,"HGS33","Low voltage AC (<1kV)","Rural"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,1787680,"20240312UTD_07","Crew were called to reports of a pole on fire. On arrival they discovered a 3 phase fused mains box caught fire and molten plastic ignited a small ground fire.  Crew replaced box and restored supply.",null,null,"Other "]
[17,86,"2024-03-10","21:03:00",-38.320210000000003,144.715754,"3732 Point Nepean Rd, Portsea VIC 3944, Australia",1307170,"STO22","Low voltage AC (<1kV)","Urban"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1787691,"20240312UTD_06","Fire services reported a pole on fire. On arrival the crew discovered fire damage to an Ampact connector on pole.   Crew made safe and arranged replacement connections.",null,null," - connection box"]
[17,87,"2024-03-13","14:57:00",-37.904792999999998,145.002815,"14 Warleigh Grove, Brighton VIC 3186, Australia",2307865,"NB 23","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1788486,"20240314UTD_01","Crew were called to reports from FRV of a box arcing and sparking on customer POA. On arrival they discovered the service cable leads from UE (SEC) owned porcelain fuse box to customer mains box burnt outburnt out. Supply Isolated and customer to engage REC to fit FMB.",null,null," - earth / earthing"]
[17,88,"2024-03-17","11:59:00",-37.815075,145.15138099999999,"21 Athol Ct, Blackburn VIC 3130, Australia",7038675,"NW 31","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1789368,"20240318UTD_01","Crew were called to reports a wire down igniting a small grass fire. On arrival they discovered the neutral screen service cable had blown out at the wrap on, dropped to the ground a had ignited a small grass fire. Crew replaced service and restored supply."]
[17,89,"2024-03-20","00:37:00",-38.391765999999997,144.79952900000001,"61 Heyfield Rd, Rye VIC 3941, Australia",1305571,"STO21","22kV AC","Rural"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,0.67800000000000005,1790023,"20240320UTD_01","Fire services reported a pole on fire. On arrival the crew discovered a HV intermediate crossarm on fire. Construction crew arranged to replace crossarm."]
[17,90,"2024-03-20","03:14:00",-38.023040999999999,145.20730499999999,"42 Elliott Rd, Dandenong South VIC 3175, Australia",635730,"DSH14","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1790037,"20240320UTD_02","Fire services reported a pole on fire. On arrival the crew discovered a HV dressing down crossarm on fire. Construction crew arranged to replace crossarm.",null,null,"Extra low voltage AC (<50V)"]
[17,91,"2024-03-20","14:49:00",-37.786212999999996,145.171661,"72-74 Woodhouse Rd, Donvale VIC 3111, Australia",7070700,"DC 10","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.1356,1790287,"20240321UTD_02","Customer reports indicate a tree branch has fallen on lines and is on fire. On arrival the crew removed a branch which had broke and fallen on the HV conductors. Branch cleared. Supply restored",null,null,"Low voltage AC (<1kV)"]
[17,92,"2024-03-28","12:54:00",-37.985618000000002,145.033064,"59 Reserve Rd, Beaumaris VIC 3193, Australia",1811769,"BR 09","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1792371,"20240402UTD_02","Crew were called by FRV reports of a pole fire.  On arrival they discovered a LV 3 phase krone box had caught fire.  Debris from box scorched a small amount of grass underneath.  Crew isolated and replaced krone box and restored supply.",null,null,"2.2kV AC"]
[17,93,"2024-04-02","13:46:00",-37.943908,145.072791,"110 Cochranes Rd, Moorabbin VIC 3189, Australia",1815332,"HT 03","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1792903,"20240404UTD_02","Crew were called by FRV reports of a pole fire.  On arrival they discovered a HV centre phase isolator had leaked current into the crossarm causing the isolator to fall against the pole thus burning the pole also.  Crew isolated line and replaced isolators to a gas switch.",null,null,"6.6kV AC"]
[17,94,"2024-04-12","06:25:00",-38.372075000000002,144.86101600000001,"77 Truemans Rd, Capel Sound VIC 3940, Australia",8828045,"RBD14","Low voltage AC (<1kV)","Urban"," - underground service cable (residential)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1795264,"20240412UTD_03","Crew responded to reports of smoke coming from pole out front of property. On arrival the crew discovered that an underground XLPE cable pole to pit has failed just above ground level.  Cable isolated and underground crew to complete repairs. ",null,null,"11kV AC"]
[17,95,"2024-04-19","07:34:00",-37.903306999999998,145.04407499999999,"303 Grange Rd, Ormond VIC 3204, Australia",2327378,"BT 09","11kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1796798,"20240419UTD_02","Customer witnessed flames from a metal box on the pole. On arrival connections to the top of a vacuum switch have overheated charring the connection and melted the cover. Supply Isolated, Connection repaired.",null,null,"12.7kV AC (SWER)"]
[17,96,"2024-04-27","12:30:00",-38.112793000000003,145.19494,"46A McCormicks Rd, Skye VIC 3977, Australia",3310938,"FTN25","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1798356,"20240429UTD_02","Crew were called by emergency services to reports of a pole on fire. On arrival they discovered a 3 phase fused mains box caught fire.  Crew replaced box and other damaged assets and restored supply.",null,null,"22kV AC"]
[17,97,"2024-04-27","17:16:00",-37.807144000000001,145.12939399999999,"20 Wimmera St, Box Hill North VIC 3129, Australia",7037053,"DC 06","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6799999999999998E-2,1798378,"20240429UTD_03","Crew responded to a report of a power line on fire. On arrival they discovered a single-phase copper neutral screen service which had blown out near the causing a flashover that blackened the facia board. Service replaced and supply restored.",null,null,"33kV AC"]
[17,98,"2024-05-07","08:07:00",-38.284413999999998,145.00859299999999,"15 Scenic View Dr, Mount Martha VIC 3934, Australia",1103270,"DMA14","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1800731,"20240509UTD_02","Crew were called by emergency services to reports of a pole on fire. On arrival they discovered a single-phase fused mains box caught fire.   Crew replaced box and restored supply.",null,null,"66kV AC"]
[17,99,"2024-05-09","11:26:00",-37.946969000000003,145.14920499999999,"4 Osborne Ave, Springvale VIC 3171, Australia",611854,"SS 22","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1801527,"20240510UTD_03","Crew were called by emergency services to reports of a pole on fire. On arrival they discovered a fused mains box caught fire and debris had dropped to the ground scorching the grass underneath.   Crew replaced box and restored supply.",null,null,"132kV AC"]
[17,100,"2024-05-10","02:01:00",-38.419286,144.83294100000001,"Miami Dr/Bass Meadows Bvd, St Andrews Beach VIC 3941, Australia",1305808,"STO14","Low voltage AC (<1kV)","Rural"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"No Rating",0.05,0.05,1801694,"20240510UTD_04","Crew were called by emergency services to reports of a pole on fire. On arrival they discovered a krone box caught fire. Debris has fallen onto grass underneath singeing some blades of grass.  Crew replaced box and restored supply.",null,null,"220kV AC"]
[17,101,"2024-05-24","16:13:00",-38.472839999999998,145.00971699999999,"28 King St, Flinders VIC 3929, Australia",1312956,"RBD21","Low voltage AC (<1kV)","Rural"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1805833,"20240527UTD_06","Crew were called to reports of a pole on fire. On arrival they discovered a fused mains box caught fire and debris had dropped to the ground scorching the grass underneath.   Crew replaced box and restored supply.",null,null,"330kV AC"]
[17,102,"2024-05-24","18:19:00",-37.937567000000001,145.03792100000001,"958 Nepean Hwy Service Rd, Moorabbin VIC 3189, Australia",1817099,"MR 23","Low voltage AC (<1kV)","Urban"," - lamps (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1805852,"20240527UTD_07","FRV reported fire on street light pole. On arrival fire was extinguished but 250W sodium head was burnt out. Crew arranged for head to be replaced",null,null,"500kV AC"]
[{"$f":"COUNTA(C140:O140,Q140,T140:V140)","v":17},103,"2024-05-27","06:11:00",-37.988795000000003,145.100797,"34 De Havilland Rd, Mordialloc VIC 3195, Australia",1806827,"MC 32","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1806071,"20240527UTD_08","Crew responded to customer reports of sparking and a fire coming from pole top.  On arrival crew discovered that a possum on a concrete pole steel crossarm.  ",null,null,"Extra low voltage DC (<120V ripple free)"]
[17,104,"2024-06-02","11:26:00",-38.021084000000002,145.098375,"75 Station St, Aspendale VIC 3195, Australia",3303394,"MC 21","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1807807,"20240603UTD_05","Crew were called by emergency services to reports of a pole on fire. On arrival they discovered a 3 phase FOLCB caught fire. Crew replaced box and restored supply.",null,null,"Low voltage DC (<1.5kV)"]
[17,105,"2024-06-03","20:43:00",-38.002654999999997,145.26848000000001,"11 Edinborough St, Hallam VIC 3803, Australia",616535,"DN 21","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1808107,"20240604UTD_01","Crew were called by emergency services to reports of a house fire. On arrival they discovered a customer's 1 phase FMB caught fire at POA. This fire spread to the service line which failed and fell to the ground likely on fire causing scorch marks on the adjacent pavement. ",null,null,"600V DC"]
[17,106,"2024-06-12","07:16:00",-37.924377,145.056129,"4 Moray St, Bentleigh East VIC 3165, Australia",1802475,"MR 22","11kV AC","Urban"," - fuse (powder filled)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1810102,"20240621UTD_03","Crew were called by emergency services to reports of a pole on fire. On arrival they discovered a possum hanging over white phase fuse unit that may have caught fire at time of fault but showed little evidence of such.  Crew removed possum.",null,null,"1500V DC"]
[17,107,"2024-06-17","18:04:00",-38.235402999999998,145.028885,"1C Coral Rd, Mornington VIC 3931, Australia",1102075,"MTN31","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1811770,"20240619UTD_02","Crew were called by emergency services to reports of a pole on fire. On arrival they discovered a krone box caught fire. Debris has fallen onto grass underneath singeing some blades of grass.  Crew replaced box and restored supply.",null,null,"Earthing cable"]
[17,108,"2024-06-21","12:37:00",-38.042873,145.10952399999999,"5 Lilliput Ln, Edithvale VIC 3196, Australia",3302837,"CRM23","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1813010,"20240624UTD_07","Crew were called by customer to reports of a pole on fire, customer advised FRV as well. On arrival they discovered a krone box caught fire. Crew replaced box and restored supply."]
[17,109,"2024-06-22","08:44:00",-38.200949999999999,145.126633,"156 Moorooduc Hwy Service Rd, Mount Eliza VIC 3930, Australia",3317488,"FSH12","Low voltage AC (<1kV)","Rural"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"No Rating",0.05,0.05,1813113,"20240624UTD_08","Crew were called by emergency services to reports of a pole on fire. On arrival they discovered a 3 phase FOLCB caught fire. Crew replaced box and restored supply."]
[17,110,"2024-06-29","14:10:00",-37.868025000000003,145.060315,"2 Moira St, Malvern East VIC 3145, Australia",2317287,"EM 06","11kV AC","Urban"," - surge diverter","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No Rating",0.05,0.01,1814651,"20240701UTD_01","Customer reported loud bang and fire on top of pole.  On arrival crew discovered the blue phase surge arrestor had faulted. Debris fell on to the green grass below can singed it slightly.  Surge arrester cut clear, and a replacement arranged",null,null,"single wire earth return (SWER)"]
[0,111,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(O148=\"\",\"\",IF(O148=\"LBRA only\",0.2,IF(O148=\"HBRA only\",1,IF(O148=\"within electric line construction area\",19.8,IF(O148=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":""},null,{"$f":"IF(Q148=\"\",\"\",IF(Q148=\"No rating\",0.05,IF(Q148=\"Moderate\",0.334,IF(Q148=\"High\",0.678,IF(Q148=\"Extreme\",2.272,4.754)))))","v":""},{"$f":"IF(OR(P148=\"\",R148=\"\"),\"\",IF(AND(O148=\"within electric line construction area\",Q148=\"No forecast\"),1,P148*R148))","v":""},null,null,null,null,null,"single phase"]
[0,112,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"two phase"]
[0,113,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"three phase"]
[0,114,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,115,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,116,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Negligible: no ground fire"]
[0,117,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Localised: less than 10 sq.m"]
[0,118,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Small: 10 - 1000 aq.m"]
[0,119,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Medium: 1000 sq.m - 10 ha"]
[0,120,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Large: more than 10 ha"]
[0,121,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,122,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,123,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Started in or originated from a distribution system"]
[0,124,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system"]
[0,125,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system"]
[0,126,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Started by lightning striking a distribution system or a part of a distribution system "]
[0,127,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Started by any other thing forming part of or coming into contact with a distribution system"]
[0,128,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Otherwise started by a distribution system"]
[0,129,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,130,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,{"$f":"IF(Q167=\"\",\"\",IF(Q167=\"No rating\",0.05,IF(Q167=\"Moderate\",0.334,IF(Q167=\"High\",0.678,IF(Q167=\"Extreme\",2.272,4.754)))))","v":""},""]
[0,131,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,1]
[0,132,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,2]
[0,133,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,5]
[0,134,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",{"$f":"IF(OR(P171=\"\",R171=\"\"),\"\",IF(AND(O171=\"within electric line construction area\",Q171=\"No forecast\"),1,P171*R171))","v":""},null,null,null,null,null,10]
[0,135,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,15]
[0,136,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,20]
[0,137,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,25]
[0,138,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,30]
[0,139,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,50]
[0,140,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,100]
[0,141,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,142,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,143,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,144,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,145,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,146,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,147,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,148,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,149,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,150,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,151,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,152,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,153,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,154,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",{"$f":"IF(OR(P191=\"\",R191=\"\"),\"\",IF(AND(O191=\"within electric line construction area\",Q191=\"No forecast\"),1,P191*R191))","v":""}]
[0,155,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,156,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,157,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,158,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,159,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,160,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C198:O198,Q198,T198:V198)","v":0},161,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C199:O199,Q199,T199:V199)","v":0},162,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,163,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,164,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,165,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,166,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,167,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(O204=\"\",\"\",IF(O204=\"LBRA only\",0.2,IF(O204=\"HBRA only\",1,IF(O204=\"within electric line construction area\",19.8,IF(O204=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":""},null,"",""]
[0,168,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,169,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,170,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C208:O208,Q208,T208:V208)","v":0},171,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C209:O209,Q209,T209:V209)","v":0},172,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,173,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,174,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,175,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,176,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,177,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,178,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,179,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,180,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,181,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,182,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,183,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C221:O221,Q221,T221:V221)","v":0},184,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C222:O222,Q222,T222:V222)","v":0},185,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,186,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,187,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,188,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,189,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,190,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,191,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,192,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,193,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,194,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,{"$f":"IF(Q231=\"\",\"\",IF(Q231=\"No rating\",0.05,IF(Q231=\"Moderate\",0.334,IF(Q231=\"High\",0.678,IF(Q231=\"Extreme\",2.272,4.754)))))","v":""},""]
[0,195,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,196,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C234:O234,Q234,T234:V234)","v":0},197,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(O234=\"\",\"\",IF(O234=\"LBRA only\",0.2,IF(O234=\"HBRA only\",1,IF(O234=\"within electric line construction area\",19.8,IF(O234=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":""},null,"",{"$f":"IF(OR(P234=\"\",R234=\"\"),\"\",IF(AND(O234=\"within electric line construction area\",Q234=\"No forecast\"),1,P234*R234))","v":""}]
[{"$f":"COUNTA(C235:O235,Q235,T235:V235)","v":0},198,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(O235=\"\",\"\",IF(O235=\"LBRA only\",0.2,IF(O235=\"HBRA only\",1,IF(O235=\"within electric line construction area\",19.8,IF(O235=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":""},null,"",{"$f":"IF(OR(P235=\"\",R235=\"\"),\"\",IF(AND(O235=\"within electric line construction area\",Q235=\"No forecast\"),1,P235*R235))","v":""}]
[0,199,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,200,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]

{"sheet":"3. Systems and Audit","index":4,"n_rows":29,"n_cols":5,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,1,29,4],[3,5,3,6],[4,5,4,6],[5,5,5,6],[6,1,6,4],[9,1,9,4],[14,1,14,4],[10,1,10,4],[13,1,13,4],[12,1,12,4],[11,1,11,4]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"United Energy"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2023/24"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"United Energy must provide:"}]
[]
[null,"Table 4 - Information or reporting systems"]
[null,"   (1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system"]
[null,"   (2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No"]
[null,"   (3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with"]
[null,"   (4) Whether the data entered into or removed from the IT system has been audited - Yes or No"]
[]
[]
[null,"Table 4: Information or reporting systems"]
[]
[null,"Information or reporting systems","Name","System Audited","Relevant Standards"]
[null,"System 1","Geographical Information System (GIS)","Yes","N/A"]
[null,"System 2","Distribution Management System (DMS)","Yes","N/A"]
[null,"System 3 "]
[null,"System 4"]
[null,"System 5"]
[null,"System 6"]
[null,"System 7"]
[null,"System 8"]
[]
[null,"The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data."]