{"text_format":"1","workbook":"xlsx","n_sheets":13,"sheets":["Dashboard","KTS","SMTS H","SMTS GIS","ROTS GIL","DDTS","NPSD","WOTS Spare","BATS","TTS","MWTS","AEMO Data 2024","2024 Lookup"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":37,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Dashboard","index":0,"n_rows":16,"n_cols":19,"rows_kept":16,"cut":false,"hidden":false,"merged":[[1,5,1,18],[0,5,0,18],[0,0,1,3],[6,14,7,14],[6,15,7,15],[6,16,7,16],[6,17,7,17],[6,18,7,18],[6,9,7,9],[6,10,7,10],[6,11,7,11],[6,12,7,12],[6,13,7,13]]}
["Select the station along with the respective voltage from the dropdowns in the table below. \n22kV and 66kV at the same station would require two separate rows for each voltage.\nAdd project name in cell directly above the table.",null,null,null,null,"This table gives the summated result for the stations and the respective voltages. \n"]
[null,null,null,null,null,"Coincident demand forecasts are calculated for the time when the entire region expereiences its peak demand\nNon-coincident forecasts are individual, independent calculations of maximum demand for each connection point"]
[]
[null,"Project Name","BATS"]
[null,"Coincedence","Coincident"]
[]
[null,"Station ID","Voltage",null,null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033]
[null,null,null,null,null,{"$f":"IF(C4=\"\",\"Insert Project Name in C4\", C4)","v":"BATS"}]
[null,null,null,null,null,"Summer POE10 MW",{"$f":"$C$5","v":"Coincident"},"summer","poe10",{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H9,AEMO_DATA_2024[Type],I9,AEMO_DATA_2024[seasonYr],J$7,AEMO_DATA_2024[coincidence],G9))","v":636.86383000000001},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H9,AEMO_DATA_2024[Type],I9,AEMO_DATA_2024[seasonYr],K$7,AEMO_DATA_2024[coincidence],G9))","v":645.97244999999998},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H9,AEMO_DATA_2024[Type],I9,AEMO_DATA_2024[seasonYr],L$7,AEMO_DATA_2024[coincidence],G9))","v":713.02949000000001},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H9,AEMO_DATA_2024[Type],I9,AEMO_DATA_2024[seasonYr],M$7,AEMO_DATA_2024[coincidence],G9))","v":731.41715999999997},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H9,AEMO_DATA_2024[Type],I9,AEMO_DATA_2024[seasonYr],N$7,AEMO_DATA_2024[coincidence],G9))","v":747.55160999999998},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H9,AEMO_DATA_2024[Type],I9,AEMO_DATA_2024[seasonYr],O$7,AEMO_DATA_2024[coincidence],G9))","v":770.08933000000002},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H9,AEMO_DATA_2024[Type],I9,AEMO_DATA_2024[seasonYr],P$7,AEMO_DATA_2024[coincidence],G9))","v":792.14915999999994},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H9,AEMO_DATA_2024[Type],I9,AEMO_DATA_2024[seasonYr],Q$7,AEMO_DATA_2024[coincidence],G9))","v":813.92243999999994},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H9,AEMO_DATA_2024[Type],I9,AEMO_DATA_2024[seasonYr],R$7,AEMO_DATA_2024[coincidence],G9))","v":838.42187000000001},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H9,AEMO_DATA_2024[Type],I9,AEMO_DATA_2024[seasonYr],S$7,AEMO_DATA_2024[coincidence],G9))","v":860.91971000000001}]
[null,null,null,null,null,"Summer POE10 MVAR",{"$f":"$C$5","v":"Coincident"},"summer","poe10",{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H10,AEMO_DATA_2024[Type],I10,AEMO_DATA_2024[seasonYr],J$7,AEMO_DATA_2024[coincidence],G10))","v":124.68867934438981},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H10,AEMO_DATA_2024[Type],I10,AEMO_DATA_2024[seasonYr],K$7,AEMO_DATA_2024[coincidence],G10))","v":127.16919323631339},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H10,AEMO_DATA_2024[Type],I10,AEMO_DATA_2024[seasonYr],L$7,AEMO_DATA_2024[coincidence],G10))","v":140.61520728666281},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H10,AEMO_DATA_2024[Type],I10,AEMO_DATA_2024[seasonYr],M$7,AEMO_DATA_2024[coincidence],G10))","v":144.91679176429659},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H10,AEMO_DATA_2024[Type],I10,AEMO_DATA_2024[seasonYr],N$7,AEMO_DATA_2024[coincidence],G10))","v":148.83091579278729},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H10,AEMO_DATA_2024[Type],I10,AEMO_DATA_2024[seasonYr],O$7,AEMO_DATA_2024[coincidence],G10))","v":153.97744870592868},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H10,AEMO_DATA_2024[Type],I10,AEMO_DATA_2024[seasonYr],P$7,AEMO_DATA_2024[coincidence],G10))","v":158.9816369634633},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H10,AEMO_DATA_2024[Type],I10,AEMO_DATA_2024[seasonYr],Q$7,AEMO_DATA_2024[coincidence],G10))","v":163.79600142363373},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H10,AEMO_DATA_2024[Type],I10,AEMO_DATA_2024[seasonYr],R$7,AEMO_DATA_2024[coincidence],G10))","v":169.1353395671442},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H10,AEMO_DATA_2024[Type],I10,AEMO_DATA_2024[seasonYr],S$7,AEMO_DATA_2024[coincidence],G10))","v":174.08031013514261}]
[null,null,null,null,null,"Summer POE50 MW","Coincident","summer","poe50",{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H11,AEMO_DATA_2024[Type],I11,AEMO_DATA_2024[seasonYr],J$7,AEMO_DATA_2024[coincidence],G11))","v":587.95285000000001},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H11,AEMO_DATA_2024[Type],I11,AEMO_DATA_2024[seasonYr],K$7,AEMO_DATA_2024[coincidence],G11))","v":596.79514000000006},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H11,AEMO_DATA_2024[Type],I11,AEMO_DATA_2024[seasonYr],L$7,AEMO_DATA_2024[coincidence],G11))","v":663.78698999999995},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H11,AEMO_DATA_2024[Type],I11,AEMO_DATA_2024[seasonYr],M$7,AEMO_DATA_2024[coincidence],G11))","v":681.44223},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H11,AEMO_DATA_2024[Type],I11,AEMO_DATA_2024[seasonYr],N$7,AEMO_DATA_2024[coincidence],G11))","v":698.45718999999997},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H11,AEMO_DATA_2024[Type],I11,AEMO_DATA_2024[seasonYr],O$7,AEMO_DATA_2024[coincidence],G11))","v":718.68997000000002},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H11,AEMO_DATA_2024[Type],I11,AEMO_DATA_2024[seasonYr],P$7,AEMO_DATA_2024[coincidence],G11))","v":740.94893999999999},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H11,AEMO_DATA_2024[Type],I11,AEMO_DATA_2024[seasonYr],Q$7,AEMO_DATA_2024[coincidence],G11))","v":762.54332000000011},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H11,AEMO_DATA_2024[Type],I11,AEMO_DATA_2024[seasonYr],R$7,AEMO_DATA_2024[coincidence],G11))","v":785.04325000000006},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H11,AEMO_DATA_2024[Type],I11,AEMO_DATA_2024[seasonYr],S$7,AEMO_DATA_2024[coincidence],G11))","v":806.76105000000007}]
[null,null,null,null,null,"Summer POE50 MVAr","Coincident","summer","poe50",{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H12,AEMO_DATA_2024[Type],I12,AEMO_DATA_2024[seasonYr],J$7,AEMO_DATA_2024[coincidence],G12))","v":115.4747245666656},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H12,AEMO_DATA_2024[Type],I12,AEMO_DATA_2024[seasonYr],K$7,AEMO_DATA_2024[coincidence],G12))","v":117.90506664489931},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H12,AEMO_DATA_2024[Type],I12,AEMO_DATA_2024[seasonYr],L$7,AEMO_DATA_2024[coincidence],G12))","v":131.3388000639475},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H12,AEMO_DATA_2024[Type],I12,AEMO_DATA_2024[seasonYr],M$7,AEMO_DATA_2024[coincidence],G12))","v":135.502407815336},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H12,AEMO_DATA_2024[Type],I12,AEMO_DATA_2024[seasonYr],N$7,AEMO_DATA_2024[coincidence],G12))","v":139.5824041964423},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H12,AEMO_DATA_2024[Type],I12,AEMO_DATA_2024[seasonYr],O$7,AEMO_DATA_2024[coincidence],G12))","v":144.29472759414631},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H12,AEMO_DATA_2024[Type],I12,AEMO_DATA_2024[seasonYr],P$7,AEMO_DATA_2024[coincidence],G12))","v":149.33643026980212},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H12,AEMO_DATA_2024[Type],I12,AEMO_DATA_2024[seasonYr],Q$7,AEMO_DATA_2024[coincidence],G12))","v":154.1170931662389},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H12,AEMO_DATA_2024[Type],I12,AEMO_DATA_2024[seasonYr],R$7,AEMO_DATA_2024[coincidence],G12))","v":159.0797612332542},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H12,AEMO_DATA_2024[Type],I12,AEMO_DATA_2024[seasonYr],S$7,AEMO_DATA_2024[coincidence],G12))","v":163.87778620161799}]
[null,"KTS","66 kV",null,null,"Winter POE10 MW","Coincident","winter","poe10",{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H13,AEMO_DATA_2024[Type],I13,AEMO_DATA_2024[seasonYr],J$7,AEMO_DATA_2024[coincidence],G13))","v":499.54375000000005},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H13,AEMO_DATA_2024[Type],I13,AEMO_DATA_2024[seasonYr],K$7,AEMO_DATA_2024[coincidence],G13))","v":506.40479999999997},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H13,AEMO_DATA_2024[Type],I13,AEMO_DATA_2024[seasonYr],L$7,AEMO_DATA_2024[coincidence],G13))","v":579.75321999999994},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H13,AEMO_DATA_2024[Type],I13,AEMO_DATA_2024[seasonYr],M$7,AEMO_DATA_2024[coincidence],G13))","v":601.38263000000006},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H13,AEMO_DATA_2024[Type],I13,AEMO_DATA_2024[seasonYr],N$7,AEMO_DATA_2024[coincidence],G13))","v":626.94750999999997},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H13,AEMO_DATA_2024[Type],I13,AEMO_DATA_2024[seasonYr],O$7,AEMO_DATA_2024[coincidence],G13))","v":654.21603000000005},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H13,AEMO_DATA_2024[Type],I13,AEMO_DATA_2024[seasonYr],P$7,AEMO_DATA_2024[coincidence],G13))","v":680.04282999999987},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H13,AEMO_DATA_2024[Type],I13,AEMO_DATA_2024[seasonYr],Q$7,AEMO_DATA_2024[coincidence],G13))","v":705.73351000000002},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H13,AEMO_DATA_2024[Type],I13,AEMO_DATA_2024[seasonYr],R$7,AEMO_DATA_2024[coincidence],G13))","v":733.79969000000006},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H13,AEMO_DATA_2024[Type],I13,AEMO_DATA_2024[seasonYr],S$7,AEMO_DATA_2024[coincidence],G13))","v":0}]
[null,null,null,null,null,"Winter POE10 MVAr","Coincident","winter","poe10",{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H14,AEMO_DATA_2024[Type],I14,AEMO_DATA_2024[seasonYr],J$7,AEMO_DATA_2024[coincidence],G14))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H14,AEMO_DATA_2024[Type],I14,AEMO_DATA_2024[seasonYr],K$7,AEMO_DATA_2024[coincidence],G14))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H14,AEMO_DATA_2024[Type],I14,AEMO_DATA_2024[seasonYr],L$7,AEMO_DATA_2024[coincidence],G14))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H14,AEMO_DATA_2024[Type],I14,AEMO_DATA_2024[seasonYr],M$7,AEMO_DATA_2024[coincidence],G14))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H14,AEMO_DATA_2024[Type],I14,AEMO_DATA_2024[seasonYr],N$7,AEMO_DATA_2024[coincidence],G14))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H14,AEMO_DATA_2024[Type],I14,AEMO_DATA_2024[seasonYr],O$7,AEMO_DATA_2024[coincidence],G14))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H14,AEMO_DATA_2024[Type],I14,AEMO_DATA_2024[seasonYr],P$7,AEMO_DATA_2024[coincidence],G14))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H14,AEMO_DATA_2024[Type],I14,AEMO_DATA_2024[seasonYr],Q$7,AEMO_DATA_2024[coincidence],G14))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H14,AEMO_DATA_2024[Type],I14,AEMO_DATA_2024[seasonYr],R$7,AEMO_DATA_2024[coincidence],G14))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H14,AEMO_DATA_2024[Type],I14,AEMO_DATA_2024[seasonYr],S$7,AEMO_DATA_2024[coincidence],G14))","v":0}]
[null,null,null,null,null,"Winter POE50 MW","Coincident","winter","poe50",{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H15,AEMO_DATA_2024[Type],I15,AEMO_DATA_2024[seasonYr],J$7,AEMO_DATA_2024[coincidence],G15))","v":488.31734},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H15,AEMO_DATA_2024[Type],I15,AEMO_DATA_2024[seasonYr],K$7,AEMO_DATA_2024[coincidence],G15))","v":495.0095},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H15,AEMO_DATA_2024[Type],I15,AEMO_DATA_2024[seasonYr],L$7,AEMO_DATA_2024[coincidence],G15))","v":568.00838999999996},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H15,AEMO_DATA_2024[Type],I15,AEMO_DATA_2024[seasonYr],M$7,AEMO_DATA_2024[coincidence],G15))","v":589.54743999999994},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H15,AEMO_DATA_2024[Type],I15,AEMO_DATA_2024[seasonYr],N$7,AEMO_DATA_2024[coincidence],G15))","v":614.99458000000004},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H15,AEMO_DATA_2024[Type],I15,AEMO_DATA_2024[seasonYr],O$7,AEMO_DATA_2024[coincidence],G15))","v":642.20348999999999},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H15,AEMO_DATA_2024[Type],I15,AEMO_DATA_2024[seasonYr],P$7,AEMO_DATA_2024[coincidence],G15))","v":667.73009999999999},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H15,AEMO_DATA_2024[Type],I15,AEMO_DATA_2024[seasonYr],Q$7,AEMO_DATA_2024[coincidence],G15))","v":693.03171999999995},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H15,AEMO_DATA_2024[Type],I15,AEMO_DATA_2024[seasonYr],R$7,AEMO_DATA_2024[coincidence],G15))","v":720.37750999999992},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MW],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H15,AEMO_DATA_2024[Type],I15,AEMO_DATA_2024[seasonYr],S$7,AEMO_DATA_2024[coincidence],G15))","v":0}]
[null,null,null,null,null,"Winter POE50 MVAr","Coincident","winter","poe50",{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H16,AEMO_DATA_2024[Type],I16,AEMO_DATA_2024[seasonYr],J$7,AEMO_DATA_2024[coincidence],G16))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H16,AEMO_DATA_2024[Type],I16,AEMO_DATA_2024[seasonYr],K$7,AEMO_DATA_2024[coincidence],G16))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H16,AEMO_DATA_2024[Type],I16,AEMO_DATA_2024[seasonYr],L$7,AEMO_DATA_2024[coincidence],G16))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H16,AEMO_DATA_2024[Type],I16,AEMO_DATA_2024[seasonYr],M$7,AEMO_DATA_2024[coincidence],G16))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H16,AEMO_DATA_2024[Type],I16,AEMO_DATA_2024[seasonYr],N$7,AEMO_DATA_2024[coincidence],G16))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H16,AEMO_DATA_2024[Type],I16,AEMO_DATA_2024[seasonYr],O$7,AEMO_DATA_2024[coincidence],G16))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H16,AEMO_DATA_2024[Type],I16,AEMO_DATA_2024[seasonYr],P$7,AEMO_DATA_2024[coincidence],G16))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H16,AEMO_DATA_2024[Type],I16,AEMO_DATA_2024[seasonYr],Q$7,AEMO_DATA_2024[coincidence],G16))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H16,AEMO_DATA_2024[Type],I16,AEMO_DATA_2024[seasonYr],R$7,AEMO_DATA_2024[coincidence],G16))","v":0},{"$f":"SUM(SUMIFS(AEMO_DATA_2024[MVAr],AEMO_DATA_2024[Station], Dashboard!$B$8:$B$33,AEMO_DATA_2024[Voltage],Dashboard!$C$8:$C$33,AEMO_DATA_2024[season],H16,AEMO_DATA_2024[Type],I16,AEMO_DATA_2024[seasonYr],S$7,AEMO_DATA_2024[coincidence],G16))","v":0}]

{"sheet":"KTS","index":1,"n_rows":22,"n_cols":30,"rows_kept":22,"cut":false,"hidden":false,"merged":[[1,11,2,11],[1,12,2,12],[1,13,2,13],[1,14,2,14],[1,5,2,5],[1,6,2,6],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,10,2,10],[1,20,2,20],[1,21,2,21],[1,22,2,22],[1,23,2,23],[1,24,2,24],[1,25,2,25],[1,26,2,26],[1,27,2,27],[1,28,2,28],[1,29,2,29]]}
[]
[null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033,null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033]
[null,"KTS Subsystem",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"KTS 66kV"]
[null,"Summer POE10 MW","Coincident","summer","poe10",2537.07692,2581.1561899999997,2672.9775800000007,2741.02747,2799.9148300000002,2881.0088599999999,2952.6400599999997,3028.9225299999994,3116.1040199999998,3195.3565000000003,null,"Summer POE10 MW","Coincident","summer","poe10",344.17587000000003,350.59548999999998,413.33529000000004,422.97477000000003,431.29455999999999,443.12866000000002,454.70341999999999,466.37993,479.51319000000001,491.49452000000002]
[null,"Summer POE10 MVAR","Coincident","summer","poe10",548.31422783225617,559.88179178219741,580.98923723528048,598.2084227260907,613.73639105967857,633.89586685870165,652.10346290310258,670.66666988364602,691.17845428768635,710.09584099186884,null,"Summer POE10 MVAR","Coincident","summer","poe10",67.642355524118003,69.341110071096793,81.71602617533101,84.112129390726494,86.277092234653907,89.1450772012779,91.927563221566402,94.601333229606212,97.560179661480504,100.29515387887761]
[null,"Summer POE50 MW","Coincident","summer","poe50",2355.8721400000004,2398.9347200000002,2485.1860799999995,2550.2934700000001,2611.9136600000002,2684.3958099999995,2756.0076300000005,2831.1004699999999,2910.7104499999996,2986.68867,null,"Summer POE50 MW","Coincident","summer","poe50",314.83569,321.15262999999999,384.66932000000003,393.88189,402.70501000000002,413.19739000000004,424.87215000000003,436.44076000000001,448.42245000000003,459.95029]
[null,"Summer POE50 MVAr","Coincident","summer","poe50",511.35686569297053,522.70516655644383,542.63547668366687,559.27654753788806,575.39516138952092,593.80528181973864,612.04259834492939,630.38215120388509,649.3554466030854,667.62116112544311,null,"Summer POE50 MVAr","Coincident","summer","poe50",62.115189810196803,63.794601279678901,76.315869579826298,78.631550578489296,80.891331801812697,83.506560691900006,86.307884925566597,88.961328501371298,91.703239719447396,94.352784522996103]
[null,"Winter POE10 MW","Coincident","winter","poe10",2050.1572000000001,2098.3143399999999,2214.1829699999998,2294.0697500000001,2387.3946599999999,2486.1295099999998,2571.9513999999999,2664.0349900000001,2764.3012699999995,0,null,"Winter POE10 MW","Coincident","winter","poe10",262.49952999999999,265.88682,332.29566999999997,344.21328,358.34854999999999,373.42304000000001,387.64721999999995,401.75536999999997,417.17448000000002,0]
[null,"Winter POE10 MVAr","Coincident","winter","poe10",0,0,0,0,0,0,0,0,0,0,null,"Winter POE10 MVAr","Coincident","winter","poe10",0,0,0,0,0,0,0,0,0,0]
[null,"Winter POE50 MW","Coincident","winter","poe50",2001.6741900000002,2048.9577200000003,2164.1995000000002,2243.53766,2336.1967400000003,2434.4726799999994,2519.0101399999999,2609.4732300000001,2706.9187699999998,0,null,"Winter POE50 MW","Coincident","winter","poe50",256.56383,259.86671000000001,325.95648,337.84247999999997,351.93209000000002,366.99423000000002,381.06707999999998,394.97323,410.00352999999996,0]
[null,"Winter POE50 MVAr","Coincident","winter","poe50",0,0,0,0,0,0,0,0,0,0,null,"Winter POE50 MVAr","Coincident","winter","poe50",0,0,0,0,0,0,0,0,0,0]
[]
[null,"Stations",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Stations","CP_ID","CP_NAME","Voltages"]
[null,"ATS_West","66 kV",null,null,null,null,null,null,null,null,null,null,null,null,null,"KTS","KTSEJ","Keilor East (Jemena) 66 kV","66 kV"]
[null,"BLTS","66 kV",null,null,null,null,null,null,null,null,null,null,null,null,null,"KTS","KTSEP","Keilor East (Powercor) 66 kV","66 kV"]
[null,"BLTS","22 kV"]
[null,"DPTS","66 kV"]
[null,"FBTS","66 kV"]
[null,"KTS","66 kV"]
[null,"TTS","66 kV"]
[null,"WMTS","66 kV"]
[null,"WMTS","22 kV"]

{"sheet":"SMTS H","index":2,"n_rows":37,"n_cols":15,"rows_kept":37,"cut":false,"hidden":false,"merged":[[1,11,2,11],[1,12,2,12],[1,13,2,13],[1,14,2,14],[1,5,2,5],[1,6,2,6],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,10,2,10]]}
[]
[null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033]
[null,"SMTS H"]
[null,"Summer POE10 MW","Coincident","summer","poe10",7247.518039999999,7311.9634999999998,7447.3548200000005,7626.5521300000009,7777.6093900000005,8004.5669300000009,8208.9797899999994,8413.7430399999976,8649.7447100000027,8861.3377799999998]
[null,"Summer POE10 MVAR","Coincident","summer","poe10",1233.4784398232264,1253.6906872861957,1286.9707806044146,1326.0401482297032,1361.1474165515726,1408.2147142425035,1451.2257375173613,1493.5140738573114,1540.0783216188102,1582.9854047124745]
[null,"Summer POE50 MW","Coincident","summer","poe50",6667.4005600000019,6727.3462099999997,6842.3089499999996,7011.115389999999,7168.6308199999994,7368.9235700000008,7571.9787499999993,7771.8280499999992,7984.31682,8185.0027600000012]
[null,"Summer POE50 MVAr","Coincident","summer","poe50",1143.4530351323153,1162.9888486475518,1193.0173817218658,1230.5231648377148,1266.8221303258354,1309.6490142600796,1352.5786335592475,1394.1887997035205,1437.0204920449403,1478.2632493796245]
[null,"Winter POE10 MW","Coincident","winter","poe10",5530.8787199999997,5623.0818499999996,5833.8405700000003,6048.9849000000004,6310.892240000001,6581.1999099999994,6828.8894700000001,7081.2296399999996,7356.3360599999996,0]
[null,"Winter POE10 MVAr","Coincident","winter","poe10",0,0,0,0,0,0,0,0,0,0]
[null,"Winter POE50 MW","Coincident","winter","poe50",5397.13436,5487.2262799999999,5696.8649900000009,5910.4825899999996,6170.4753199999996,6439.4767899999997,6683.5447699999995,6931.3916899999995,7198.6571199999998,0]
[null,"Winter POE50 MVAr","Coincident","winter","poe50",0,0,0,0,0,0,0,0,0,0]
[]
[null,"Stations","Voltages"]
[null,"ATS_West","66 kV"]
[null,"BLTS","22 kV"]
[null,"BTS","66 kV"]
[null,"BTS","22 kV"]
[null,"CBTS","66 kV"]
[null,"DPTS","66 kV"]
[null,"ERTS","66 kV"]
[null,"FBTS","66 kV"]
[null,"GTS","66 kV"]
[null,"HTS","66 kV"]
[null,"KTS","66 kV"]
[null,"MTS","66 kV"]
[null,"MTS","22 kV"]
[null,"RTS","66 kV"]
[null,"RTS","22 kV"]
[null,"RWTS","66 kV"]
[null,"RWTS","22 kV"]
[null,"SMTS","66 kV"]
[null,"SVTS","66 kV"]
[null,"TSTS","66 kV"]
[null,"TTS","66 kV"]
[null,"WMTS","66 kV"]
[null,"WMTS","22 kV"]
[null,"ATS_BLTS","66 kV"]

{"sheet":"SMTS GIS","index":3,"n_rows":37,"n_cols":15,"rows_kept":37,"cut":false,"hidden":false,"merged":[[1,11,2,11],[1,12,2,12],[1,13,2,13],[1,14,2,14],[1,5,2,5],[1,6,2,6],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,10,2,10]]}
[]
[null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033]
[null,"SMTS GIS"]
[null,"Summer POE10 MW","Coincident","summer","poe10",7247.518039999999,7311.9634999999998,7447.3548200000005,7626.5521300000009,7777.6093900000005,8004.5669300000009,8208.9797899999994,8413.7430399999976,8649.7447100000027,8861.3377799999998]
[null,"Summer POE10 MVAR","Coincident","summer","poe10",1233.4784398232264,1253.6906872861957,1286.9707806044146,1326.0401482297032,1361.1474165515726,1408.2147142425035,1451.2257375173613,1493.5140738573114,1540.0783216188102,1582.9854047124745]
[null,"Summer POE50 MW","Coincident","summer","poe50",6667.4005600000019,6727.3462099999997,6842.3089499999996,7011.115389999999,7168.6308199999994,7368.9235700000008,7571.9787499999993,7771.8280499999992,7984.31682,8185.0027600000012]
[null,"Summer POE50 MVAr","Coincident","summer","poe50",1143.4530351323153,1162.9888486475518,1193.0173817218658,1230.5231648377148,1266.8221303258354,1309.6490142600796,1352.5786335592475,1394.1887997035205,1437.0204920449403,1478.2632493796245]
[null,"Winter POE10 MW","Coincident","winter","poe10",5530.8787199999997,5623.0818499999996,5833.8405700000003,6048.9849000000004,6310.892240000001,6581.1999099999994,6828.8894700000001,7081.2296399999996,7356.3360599999996,0]
[null,"Winter POE10 MVAr","Coincident","winter","poe10",0,0,0,0,0,0,0,0,0,0]
[null,"Winter POE50 MW","Coincident","winter","poe50",5397.13436,5487.2262799999999,5696.8649900000009,5910.4825899999996,6170.4753199999996,6439.4767899999997,6683.5447699999995,6931.3916899999995,7198.6571199999998,0]
[null,"Winter POE50 MVAr","Coincident","winter","poe50",0,0,0,0,0,0,0,0,0,0]
[]
[null,"Stations","Voltages"]
[null,"ATS_West","66 kV"]
[null,"BLTS","22 kV"]
[null,"BTS","66 kV"]
[null,"BTS","22 kV"]
[null,"CBTS","66 kV"]
[null,"DPTS","66 kV"]
[null,"ERTS","66 kV"]
[null,"FBTS","66 kV"]
[null,"GTS","66 kV"]
[null,"HTS","66 kV"]
[null,"KTS","66 kV"]
[null,"MTS","66 kV"]
[null,"MTS","22 kV"]
[null,"RTS","66 kV"]
[null,"RTS","22 kV"]
[null,"RWTS","66 kV"]
[null,"RWTS","22 kV"]
[null,"SMTS","66 kV"]
[null,"SVTS","66 kV"]
[null,"TSTS","66 kV"]
[null,"TTS","66 kV"]
[null,"WMTS","66 kV"]
[null,"WMTS","22 kV"]
[null,"ATS_BLTS","66 kV"]

{"sheet":"ROTS GIL","index":4,"n_rows":29,"n_cols":15,"rows_kept":29,"cut":false,"hidden":false,"merged":[[1,11,2,11],[1,12,2,12],[1,13,2,13],[1,14,2,14],[1,5,2,5],[1,6,2,6],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,10,2,10]]}
[]
[null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033]
[null,"ROTS GIL"]
[null,"Summer POE10 MW","Coincident","summer","poe10",5002.848750000001,5039.1698500000011,5080.4147800000019,5190.5011500000001,5279.6990799999994,5423.0926500000005,5544.3945799999992,5668.3458799999999,5813.9462699999995,5941.6304800000007]
[null,"Summer POE10 MVAR","Coincident","summer","poe10",747.41298780933903,759.43967863027922,771.77505688035615,794.06089939399976,813.84407547927526,841.03138742736337,864.69161506400087,888.33423281268517,914.34888996502025,938.17453175020148]
[null,"Summer POE50 MW","Coincident","summer","poe50",4611.8049699999992,4645.5357199999999,4671.860169999999,4775.2358000000004,4869.1009299999996,4994.7692800000004,5115.2741999999998,5236.08367,5366.0590899999997,5486.5377800000006]
[null,"Summer POE50 MVAr","Coincident","summer","poe50",694.33516481601828,706.05023328675884,716.28989146047684,737.70194331111213,758.23343234155243,782.97401077559425,806.60390595683123,829.88127065564493,853.74519455460222,876.6218614994134]
[null,"Winter POE10 MW","Coincident","winter","poe10",3701.5175700000004,3764.1857199999999,3860.1639700000001,3997.1240000000003,4167.0419400000001,4339.1542199999994,4493.1791299999995,4652.2045100000005,4825.798490000001,0]
[null,"Winter POE10 MVAr","Coincident","winter","poe10",0,0,0,0,0,0,0,0,0,0]
[null,"Winter POE50 MW","Coincident","winter","poe50",3612.4805099999999,3673.8188299999997,3769.3632400000001,3905.4080199999994,4074.1441500000005,4245.4886100000003,4397.2290200000007,4553.3952799999997,4721.9396099999994,0]
[null,"Winter POE50 MVAr","Coincident","winter","poe50",0,0,0,0,0,0,0,0,0,0]
[]
[null,"Stations","Voltages"]
[null,"ERTS","66 kV"]
[null,"CBTS","66 kV"]
[null,"TBTS","66 kV"]
[null,"TTS","66 kV"]
[null,"SMTS","66 kV"]
[null,"BTS","66 kV"]
[null,"BTS","22 kV"]
[null,"RTS","66 kV"]
[null,"RTS","22 kV"]
[null,"RWTS","66 kV"]
[null,"RWTS","22 kV"]
[null,"TSTS","66 kV"]
[null,"SVTS","66 kV"]
[null,"HTS","66 kV"]
[null,"MTS","66 kV"]
[null,"MTS","22 kV"]

{"sheet":"DDTS","index":5,"n_rows":19,"n_cols":15,"rows_kept":19,"cut":false,"hidden":false,"merged":[[1,11,2,11],[1,12,2,12],[1,13,2,13],[1,14,2,14],[1,5,2,5],[1,6,2,6],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,10,2,10]]}
[]
[null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033]
[null,"DDTS"]
[null,"Summer POE10 MW","Coincident","summer","poe10",1144.5328699999998,1167.43253,1178.17785,1204.61934,1227.31711,1259.60859,1283.4969299999998,1313.03658,1346.9612199999999,1376.80618]
[null,"Summer POE10 MVAR","Coincident","summer","poe10",155.92759190261717,160.71634865332163,163.01792859899501,167.57540041543038,171.576583095704,176.93291379640368,180.77237380212767,185.55035384674983,190.89153198412913,195.75202581447067]
[null,"Summer POE50 MW","Coincident","summer","poe50",1041.44182,1064.21983,1071.5365899999999,1096.26323,1119.9664600000001,1147.92913,1171.29882,1199.9929499999998,1230.1552099999999,1258.2063499999999]
[null,"Summer POE50 MVAr","Coincident","summer","poe50",143.76581478379501,148.5787696505237,150.43920408129085,154.80271154425756,158.96584662457914,163.78040099952139,167.57500524661089,172.27160399574564,177.14493526172961,181.79538676885852]
[null,"Winter POE10 MW","Coincident","winter","poe10",876.25147000000004,904.26423999999997,926.44116000000008,958.43748000000005,996.2503099999999,1036.32637,1066.59512,1103.24882,1143.2825,0]
[null,"Winter POE10 MVAr","Coincident","winter","poe10",0,0,0,0,0,0,0,0,0,0]
[null,"Winter POE50 MW","Coincident","winter","poe50",853.88577999999995,881.53283999999996,903.62071000000003,935.40242999999998,972.94164999999998,1012.8356800000001,1042.5829699999999,1078.5636400000001,1117.4035600000002,0]
[null,"Winter POE50 MVAr","Coincident","winter","poe50",0,0,0,0,0,0,0,0,0,0]
[]
[null,"Stations","Voltages"]
[null,"BETS","66 kV"]
[null,"BETS","22 kV"]
[null,"GNTS","66 kV"]
[null,"MBTS","66 kV"]
[null,"SHTS","66 kV"]
[null,"TTS","66 kV"]

{"sheet":"NPSD","index":6,"n_rows":21,"n_cols":15,"rows_kept":21,"cut":false,"hidden":false,"merged":[[1,11,2,11],[1,12,2,12],[1,13,2,13],[1,14,2,14],[1,5,2,5],[1,6,2,6],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,10,2,10]]}
[]
[null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033]
[null,"NPSD"]
[null,"Summer POE10 MW","Coincident","summer","poe10",2034.8433299999999,2059.0954000000002,2147.6027600000002,2207.1878100000004,2259.4121399999999,2330.7297600000002,2399.8385400000002,2467.2979099999998,2543.9467300000001,2614.4706999999999]
[null,"Summer POE10 MVAR","Coincident","summer","poe10",454.67333434965587,462.35388883235902,482.55639156519146,498.07166917013956,512.13369610461359,530.35704118240551,548.00478411267738,564.94313100056002,583.63587118801604,600.94569985430417]
[null,"Summer POE50 MW","Coincident","summer","poe50",1884.62158,1907.4449100000002,1991.4362700000001,2048.2931200000003,2102.65175,2166.4454500000002,2235.5472399999999,2301.8439000000003,2371.8494799999999,2439.44362]
[null,"Summer POE50 MVAr","Coincident","summer","poe50",422.68642036741295,430.06089833631626,449.24101106990327,464.18368715425049,478.7212296816358,495.33678043684796,512.99770568002896,529.69694256804542,546.97090254785257,563.66317317879077]
[null,"Winter POE10 MW","Coincident","winter","poe10",1667.83951,1694.08104,1802.4440100000002,1871.83869,1953.0193000000002,2039.0982800000002,2120.4517299999998,2201.2561599999999,2289.3057200000003,0]
[null,"Winter POE10 MVAr","Coincident","winter","poe10",0,0,0,0,0,0,0,0,0,0]
[null,"Winter POE50 MW","Coincident","winter","poe50",1627.31196,1652.85716,1760.5911099999998,1829.4557299999997,1909.9984399999998,1995.6167700000001,2075.7823799999996,2155.1283100000001,2240.6721699999998,0]
[null,"Winter POE50 MVAr","Coincident","winter","poe50",0,0,0,0,0,0,0,0,0,0]
[]
[null,"Stations","Voltages"]
[null,"ATS_BLTS","66 kV"]
[null,"ATS_West","66 kV"]
[null,"DPTS","66 kV"]
[null,"BLTS","22 kV"]
[null,"FBTS","66 kV"]
[null,"WMTS","22 kV"]
[null,"WMTS","66 kV"]
[null,"KTS","66 kV"]

{"sheet":"WOTS Spare","index":7,"n_rows":15,"n_cols":15,"rows_kept":15,"cut":false,"hidden":false,"merged":[[1,11,2,11],[1,12,2,12],[1,13,2,13],[1,14,2,14],[1,5,2,5],[1,6,2,6],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,10,2,10]]}
[]
[null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033]
[null,"WOTS Spare"]
[null,"Summer POE10 MW","Non-coincident","summer","poe10",101.76121000000001,101.66652999999999,101.3554,101.42287,102.05107000000001,103.04545999999999,104.01903,105.06796,106.19219,107.81797]
[null,"Summer POE10 MVAR","Non-coincident","summer","poe10",19.267384444971832,19.39492931664439,19.548918473963738,19.727889196591441,19.93397806918157,20.165634015953692,20.42199211447965,20.686851241320397,20.948187514680001,21.336850298134898]
[null,"Summer POE50 MW","Non-coincident","summer","poe50",88.445239999999998,88.235780000000005,87.793270000000007,87.729790000000008,88.183660000000003,89.849609999999998,91.812080000000009,94.179200000000009,96.878649999999993,99.435570000000013]
[null,"Summer POE50 MVAr","Non-coincident","summer","poe50",16.81505920817985,16.91922588810349,17.043603825505798,17.190347914786159,17.362748355786401,17.68628682594823,18.079169047413991,18.575938504811937,19.123262741643039,19.649492845770482]
[null,"Winter POE10 MW","Non-coincident","winter","poe10",76.993579999999994,77.23218,77.346810000000005,77.616640000000004,78.481480000000005,81.298959999999994,84.298720000000003,87.251940000000005,90.472149999999999,0]
[null,"Winter POE10 MVAr","Non-coincident","winter","poe10",0,0,0,0,0,0,0,0,0,0]
[null,"Winter POE50 MW","Non-coincident","winter","poe50",73.962230000000005,74.182649999999995,74.574240000000003,75.158680000000004,76.650930000000002,79.866050000000001,82.832319999999996,85.74127,88.876850000000005,0]
[null,"Winter POE50 MVAr","Non-coincident","winter","poe50",0,0,0,0,0,0,0,0,0,0]
[]
[null,"Stations","Voltages"]
[null,"WOTS","22 kV"]
[null,"WOTS","66 kV"]

{"sheet":"BATS","index":8,"n_rows":14,"n_cols":15,"rows_kept":14,"cut":false,"hidden":false,"merged":[[1,11,2,11],[1,12,2,12],[1,13,2,13],[1,14,2,14],[1,5,2,5],[1,6,2,6],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,10,2,10]]}
[]
[null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033]
[null,"BATS"]
[null,"Summer POE10 MW","Non-coincident","summer","poe10",204.13481999999999,204.22716,204.73308999999998,205.56367,206.48961,207.87221,209.70670000000001,211.50975,216.06447,221.44865999999999]
[null,"Summer POE10 MVAR","Non-coincident","summer","poe10",34.101357836355675,34.308401956824589,34.566042707721408,34.876118049465873,35.24422117289167,35.667903590975328,36.136203262969794,36.620967954481948,37.565478872957442,38.6292389368597]
[null,"Summer POE50 MW","Non-coincident","summer","poe50",184.14953000000003,184.13718,184.53867,185.26576,186.08825999999999,187.3674,191.44892000000002,196.71188000000001,202.06441000000001,207.26047]
[null,"Summer POE50 MVAr","Non-coincident","summer","poe50",30.895802678807399,31.086054970414011,31.326943991380645,31.620419979137608,31.971931768362161,32.379019644330135,33.207733331115875,34.247452809131111,35.319929044109017,36.353513859526551]
[null,"Winter POE10 MW","Non-coincident","winter","poe10",187.19266000000002,188.25427999999999,189.69128000000001,191.37119999999999,198.88543000000001,207.14148,214.88325,222.52631,230.85772,0]
[null,"Winter POE10 MVAr","Non-coincident","winter","poe10",0,0,0,0,0,0,0,0,0,0]
[null,"Winter POE50 MW","Non-coincident","winter","poe50",182.88155,183.92054999999999,185.33500999999998,186.99252999999999,193.60202000000001,201.79363000000001,209.40101000000001,216.88445999999999,224.94969999999998,0]
[null,"Winter POE50 MVAr","Non-coincident","winter","poe50",0,0,0,0,0,0,0,0,0,0]
[]
[null,"Stations","Voltages"]
[null,"BATS","66 kV"]

{"sheet":"TTS","index":9,"n_rows":14,"n_cols":30,"rows_kept":14,"cut":false,"hidden":false,"merged":[[1,11,2,11],[1,12,2,12],[1,13,2,13],[1,14,2,14],[1,5,2,5],[1,6,2,6],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,10,2,10],[1,20,2,20],[1,21,2,21],[1,22,2,22],[1,23,2,23],[1,24,2,24],[1,25,2,25],[1,26,2,26],[1,27,2,27],[1,28,2,28],[1,29,2,29]]}
[]
[null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033,null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033]
[null,"TTS (B12 and B34)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"TTS B34"]
[null,"Summer POE10 MW","Non-coincident","summer","poe10",515.56634999999994,534.47342000000003,535.30456000000004,539.96445999999992,550.47974999999997,565.56349999999998,573.46021999999994,587.68588999999997,604.17941999999994,618.57569000000001,null,"Summer POE10 MW",{"$f":"$C$5","v":"Non-coincident"},"summer","poe10",282.23057999999997,282.95818000000003,283.97304000000003,287.01810999999998,293.21821999999997,301.70051999999998,309.86304999999999,317.76983000000001,326.79694000000001,334.85464999999999]
[null,"Summer POE10 MVAR","Non-coincident","summer","poe10",97.271546369341308,101.26502710799079,102.04929412060829,103.5346619527305,106.15932735020769,109.6163934576379,111.7039854098106,114.8497736811904,118.3316500407312,121.5238886179268,null,"Summer POE10 MVAR",{"$f":"$C$5","v":"Non-coincident"},"summer","poe10",52.823873835373099,53.1965322733138,53.624869281464399,54.415092200583103,55.786394845405198,57.5953327785504,59.324278836679703,60.967698672768798,62.792341561966403,64.462355812301496]
[null,"Summer POE50 MW","Non-coincident","summer","poe50",460.97390999999999,482.13869,485.99964,498.01657999999998,509.03832,522.26107000000002,529.88452000000007,543.80083999999999,558.69160999999997,572.35009000000002,null,"Summer POE50 MW","Non-coincident","summer","poe50",251.08020999999999,253.01062999999999,255.58716999999999,262.38515999999998,268.80862000000002,276.24171000000001,284.32713000000001,292.01805000000002,300.12437,307.73808000000002]
[null,"Summer POE50 MVAr","Non-coincident","summer","poe50",87.375179095488605,91.777931289267087,93.111433920039801,95.930465715311897,98.6469389749372,101.76664812421259,103.80470244287929,106.8944125976524,110.0857450355102,113.14423907205179,null,"Summer POE50 MVAr","Non-coincident","summer","poe50",47.1770204938408,47.767722830979501,48.479156891473501,49.949698819403402,51.361489737521502,52.980229769503097,54.695197539054597,56.299486868433704,57.9572114806301,59.546738632942301]
[null,"Winter POE10 MW","Non-coincident","winter","poe10",418.03089,437.71451000000002,440.10874000000001,444.20474000000002,455.43207000000001,473.67869999999999,484.20867999999996,501.58398999999997,520.51916000000006,0,null,"Winter POE10 MW","Non-coincident","winter","poe10",223.87905000000001,224.74867,226.27814000000001,228.05288999999999,233.42953,242.96234999999999,251.83376000000001,260.57657999999998,270.12009,0]
[null,"Winter POE10 MVAr","Non-coincident","winter","poe10",0,0,0,0,0,0,0,0,0,0,null,"Winter POE10 MVAr","Non-coincident","winter","poe10",0,0,0,0,0,0,0,0,0,0]
[null,"Winter POE50 MW","Non-coincident","winter","poe50",404.16084999999998,423.85302000000001,426.16279999999995,431.08411000000001,446.22152,465.11345,475.46345000000002,492.57351,511.00989000000004,0,null,"Winter POE50 MW","Non-coincident","winter","poe50",216.88541000000001,217.80115000000001,219.28428,221.01509999999999,229.41433000000001,238.9443,247.72183000000001,256.33803,265.63470000000001,0]
[null,"Winter POE50 MVAr","Non-coincident","winter","poe50",0,0,0,0,0,0,0,0,0,0,null,"Winter POE50 MVAr","Non-coincident","winter","poe50",0,0,0,0,0,0,0,0,0,0]
[]
[null,"Stations","Voltages",null,null,null,null,null,null,null,null,null,null,null,null,null,"Stations","Voltages"]
[null,"TTS","66 kV",null,null,null,null,null,null,null,null,null,null,null,null,null,"TTS B34","66 kV"]

{"sheet":"MWTS","index":10,"n_rows":14,"n_cols":15,"rows_kept":14,"cut":false,"hidden":false,"merged":[[1,11,2,11],[1,12,2,12],[1,13,2,13],[1,14,2,14],[1,5,2,5],[1,6,2,6],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,10,2,10]]}
[]
[null,"2024 AEMO Forecast",null,null,null,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033]
[null,"MWTS"]
[null,"Summer POE10 MW","Non-coincident","summer","poe10",462.43038999999999,459.71391,458.40800000000002,457.82954999999998,458.09525000000002,458.16158000000001,458.78768000000002,460.69889000000001,463.18639000000002,464.68193000000002]
[null,"Summer POE10 MVAR","Non-coincident","summer","poe10",26.638002833136099,26.759209623549999,26.920536955114699,27.126712967477399,27.3758756940796,27.6656158111197,27.9893570778152,28.327342337775299,28.666142398832999,29.001845331759501]
[null,"Summer POE50 MW","Non-coincident","summer","poe50",381.76326999999998,378.73169000000001,377.11009000000001,376.20265999999998,376.13878,375.87531999999999,376.17192,377.75447000000003,380.48484000000002,388.13959999999997]
[null,"Summer POE50 MVAr","Non-coincident","summer","poe50",22.345887860972699,22.4503288931976,22.5948590740079,22.783530804780501,23.0151573251499,23.287350062332301,23.593559379414,23.9140573842602,24.265780008603599,24.929201104504799]
[null,"Winter POE10 MW","Non-coincident","winter","poe10",360.63749000000001,362.11916000000002,364.51504,367.51438000000002,371.31148999999999,380.27584000000002,394.54498999999998,408.62993,423.98126000000002,0]
[null,"Winter POE10 MVAr","Non-coincident","winter","poe10",0,0,0,0,0,0,0,0,0,0]
[null,"Winter POE50 MW","Non-coincident","winter","poe50",353.97892000000002,355.43374,357.80214999999998,360.77339000000001,364.54239000000001,372.16800000000001,386.24775,400.09554000000003,415.01841999999999,0]
[null,"Winter POE50 MVAr","Non-coincident","winter","poe50",0,0,0,0,0,0,0,0,0,0]
[]
[null,"Stations","Voltages"]
[null,"MWTS","66 kV"]

{"sheet":"AEMO Data 2024","index":11,"n_rows":5625,"n_cols":15,"rows_kept":5625,"cut":false,"hidden":false,"merged":[]}
["Region","CP_ID","Station","Voltage","CP_NAME","NSP","min_max","season","coincidence","seasonYr","Type","MW","L_L","pf","MVAr"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",145.30519000000001,"Lag",0.96791797061852103,37.720460445885401]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",125.86857000000001,"Lag",0.96768809176683102,32.797544765301303]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",145.83711,"Lag",0.96759238819659499,38.059816243856801]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",126.94694,"Lag",0.96732122342362303,33.275305660128801]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",146.3432,"Lag",0.96719034366823897,38.440110548653898]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",128.17768000000001,"Lag",0.96687341698310603,33.839139636326301]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",149.29173,"Lag",0.966833288070163,39.438386634306802]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",131.50765000000001,"Lag",0.96648091914387602,34.9340270133047]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",152.43360999999999,"Lag",0.96647541740203302,40.4963492548261]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",134.60452000000001,"Lag",0.96608100765647298,35.980589481185199]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",156.83536000000001,"Lag",0.96617163278248497,41.864020465335898]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",138.28527,"Lag",0.96572962613201996,37.165645493903298]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",161.01611,"Lag",0.96588594689676499,43.170721062981599]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",142.24287000000001,"Lag",0.96541157059754301,38.415826561192297]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",165.09873999999999,"Lag",0.96566462163271605,44.416370534812501]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",146.04611,"Lag",0.96516538561858001,39.590712010677798]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",169.48428000000001,"Lag",0.965441694908585,45.751956590373801]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",149.78900999999999,"Lag",0.96490760617107396,40.763529923785804]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",173.45529999999999,"Lag",0.96522862732983306,46.975870773547697]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",153.37738999999999,"Lag",0.96466743320152004,41.890528879105297]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",121.38103,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",118.25532,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",122.48891,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",119.33645,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",124.39455,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",120.59689,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",129.08976999999999,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",125.22537,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",134.52785,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",130.58545000000001,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",140.22756000000001,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",136.21893,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",145.57932,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",141.45822999999999,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",150.79765,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",146.54879,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",156.40566999999999,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",151.95738,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",160.59339,"Lag",0.96681659580179802,42.435172292245802]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",153.37542999999999,"Lag",0.96669333733931195,40.607004202020903]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",162.02825000000001,"Lag",0.96651229503905201,43.020394016574002]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",154.73160999999999,"Lag",0.96637390699796999,41.172297821269602]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",164.20538999999999,"Lag",0.966280425233631,43.757046386737102]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",156.83034000000001,"Lag",0.96613108121539204,41.889090472072297]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",166.83445,"Lag",0.96608902265062002,44.5902933139106]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",159.38623000000001,"Lag",0.96593129057758398,42.703804869395]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",169.84326999999999,"Lag",0.96587955510858003,45.541902060256803]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",162.32221000000001,"Lag",0.96571302005988602,43.636964668435901]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",173.31062,"Lag",0.96569590213649303,46.603223221571199]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",165.71672000000001,"Lag",0.96552238617962205,44.679836882445002]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",177.34594999999999,"Lag",0.96555156878285597,47.793930422021198]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",169.67918,"Lag",0.96537363867922998,45.852087537176402]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",181.62404000000001,"Lag",0.96542926300661203,49.0383559032378]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",173.88439,"Lag",0.96524826818966702,47.078053939870102]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",185.79141999999999,"Lag",0.96531602061452904,50.250084575568799]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",177.97843,"Lag",0.96513228627754,48.271207024675398]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",189.93501000000001,"Lag",0.96521169382572902,51.452177687712798]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",182.05233000000001,"Lag",0.96502571366754697,49.455649022902399]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",159.32687000000001,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",151.11369999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",160.70622,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",152.40262999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",162.96986999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",154.57918000000001,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",165.50432000000001,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",157.02992,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",168.43485000000001,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",159.87674999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",171.90550999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",163.26369,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",175.93601000000001,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",167.21046000000001,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",179.93040999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",171.12084999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",183.88997000000001,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",174.99611999999999,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",258.77974,"Lag",0.96800647743152901,67.080501437074602]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",226.63580999999999,"Lag",0.967710895778368,59.0325502007898]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",260.81508000000002,"Lag",0.96776223767415803,67.878585227538906]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",229.60518999999999,"Lag",0.96744468033228104,60.064491779419399]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",263.42770999999999,"Lag",0.96756938217726296,68.773634860989802]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",233.50202999999999,"Lag",0.96724440293326996,61.281072086224498]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",269.77825999999999,"Lag",0.96743801719818001,70.581315795485395]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",241.46778,"Lag",0.96712478903648103,63.493154437623502]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",277.55874,"Lag",0.96730223108193303,72.775855635797299]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",249.25832,"Lag",0.96698289333784404,65.690213023758901]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",287.90899000000002,"Lag",0.96720676455105603,75.605438899193601]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",258.41012000000001,"Lag",0.96687434233987302,68.219737546387506]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",298.12966,"Lag",0.967131532996657,78.383755202945594]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",268.35804000000002,"Lag",0.96679979525622906,70.929764792152596]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",308.00934999999998,"Lag",0.96706564745468904,81.066595743120004]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",277.84422000000001,"Lag",0.96673355489552004,73.514081309564702]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",319.02893999999998,"Lag",0.96701946296212604,84.028779577097396]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",287.77469000000002,"Lag",0.96668201804300502,76.2035796116093]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",329.25510000000003,"Lag",0.96697215696437999,86.787614992854998]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",297.39064000000002,"Lag",0.96663396424672499,78.809635316737399]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",168.37506999999999,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",165.31870000000001,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",170.44290000000001,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",167.35296,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",172.91164000000001,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",169.78935000000001,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",180.21518,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",176.19373999999999,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",188.90683000000001,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",184.81824,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",198.23864,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",194.10024000000001,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",207.21673000000001,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",202.95751999999999,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",216.21462,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",211.80767,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",225.99623,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",221.33788999999999,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",1.243E-2,"Lag",0.98737960137193603,1.9937189106750798E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",1.222E-2,"Lag",0.98737960137193603,1.9600358075985099E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",1.251E-2,"Lag",0.98737960137193603,2.0065505689899599E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",1.23E-2,"Lag",0.98737960137193603,1.97286746591339E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",1.268E-2,"Lag",0.98737960137193603,2.03381784290909E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",1.2460000000000001E-2,"Lag",0.98737960137193603,1.9985307825431601E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",1.337E-2,"Lag",0.98737960137193603,2.1444908958749599E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",1.315E-2,"Lag",0.98737960137193603,2.10920383550903E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",1.375E-2,"Lag",0.98737960137193603,2.2054412728706599E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",1.357E-2,"Lag",0.98737960137193603,2.1765700416621699E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",1.426E-2,"Lag",0.98737960137193603,2.2872430946280502E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",1.4069999999999999E-2,"Lag",0.98737960137193603,2.2567679061302002E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",1.495E-2,"Lag",0.98737960137193603,2.3979161475939201E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",1.478E-2,"Lag",0.98737960137193603,2.37064887367479E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",1.546E-2,"Lag",0.98737960137193603,2.4797179693513E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",1.5310000000000001E-2,"Lag",0.98737960137193603,2.4556586100109002E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",1.6029999999999999E-2,"Lag",0.98737960137193603,2.57114353484485E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",1.5869999999999999E-2,"Lag",0.98737960137193603,2.5454802182150798E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",1.6729999999999998E-2,"Lag",0.98737960137193603,2.6834205451000798E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",1.6590000000000001E-2,"Lag",0.98737960137193603,2.66096514304904E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",1.231E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",1.146E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",1.2330000000000001E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",1.1469999999999999E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",1.282E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",1.188E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",1.3480000000000001E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",1.2500000000000001E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",1.401E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",1.3010000000000001E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",1.4710000000000001E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",1.3679999999999999E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",1.5389999999999999E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",1.4330000000000001E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",1.5939999999999999E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",1.485E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",1.668E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",1.555E-2,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",204.12239,"Lag",0.98633197814927298,34.099364117444999]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",184.13731000000001,"Lag",0.98621591858066204,30.8938426429998]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",204.21465000000001,"Lag",0.98618118039578395,34.306395406255596]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",184.12487999999999,"Lag",0.98604733794793198,31.084082102948098]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",204.72040999999999,"Lag",0.98604498502049098,34.564008889878501]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",184.52620999999999,"Lag",0.985895111955711,31.324945460598101]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",205.55029999999999,"Lag",0.98591093293438203,34.87397355857]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",185.25261,"Lag",0.98574541365915502,31.618310775302099]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",206.47586000000001,"Lag",0.98574431313919797,35.2420157316188]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",186.07469,"Lag",0.98555935120079097,31.969755198320499]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",207.85794999999999,"Lag",0.98559632289842303,35.6656163478807]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",187.35333,"Lag",0.98539446577940704,32.376762876424003]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",209.69175000000001,"Lag",0.985475805813947,36.1338053468222]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",191.43414000000001,"Lag",0.98528770756736594,33.205362682242203]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",211.49429000000001,"Lag",0.98533977243636806,36.618488236512597]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",196.69657000000001,"Lag",0.985180541446394,34.244997150521101]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",216.04844,"Lag",0.98522001662928904,37.562907729422598]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",202.04854,"Lag",0.985064481228345,35.3173835638908]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",221.43192999999999,"Lag",0.98512401798169502,38.626555516314603]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",207.24387999999999,"Lag",0.98496327081466795,36.3508528943835]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",187.18035,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",182.87009,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",188.24195,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",183.90907999999999,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",189.67846,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",185.32312999999999,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",191.35772,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",186.98003,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",198.87142,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",193.58901,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",207.12676999999999,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",201.77995000000001,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",214.86786000000001,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",209.38668000000001,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",222.51036999999999,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",216.86960999999999,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",230.84103999999999,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",224.93414999999999,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",84.545689999999993,"Lag",0.99902021320544299,3.7453428656238001]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",73.686480000000003,"Lag",0.99900715647872795,3.2859941731594802]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",84.535730000000001,"Lag",0.99900829060222496,3.76765152031092]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",73.617670000000004,"Lag",0.99899328543490096,3.3058134505759198]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",84.641739999999999,"Lag",0.99899663426326601,3.7945145489365002]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",73.66489,"Lag",0.99897971431526,3.33018963995353]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",84.859470000000002,"Lag",0.99898510920296602,3.8260948928016201]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",73.824640000000002,"Lag",0.99896629740575005,3.3593174078772101]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",85.174689999999998,"Lag",0.99897307035622895,3.8630523867131901]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",74.08202,"Lag",0.99895228984475104,3.3938282479003101]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",85.657529999999994,"Lag",0.99896232975224297,3.9052462390990601]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",74.50694,"Lag",0.99893982437993301,3.4335720623674502]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",86.254720000000006,"Lag",0.99895229303972299,3.95147511103491]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",75.046300000000002,"Lag",0.99892820735602095,3.4773547034186101]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",86.859210000000004,"Lag",0.99894179152645501,3.9990918941424201]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",76.45438,"Lag",0.99891829893675999,3.55896364762968]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",87.509349999999998,"Lag",0.99893220198795396,4.0472686289182596]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",78.481989999999996,"Lag",0.99891115805474595,3.6654078846832099]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",89.077160000000006,"Lag",0.99892520108379201,4.1332842583134699]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",80.434460000000001,"Lag",0.998904725023253,3.7676947776457799]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",58.913150000000002,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",57.44744,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",59.235410000000002,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",57.761699999999998,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",59.682749999999999,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",58.20111,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",61.546300000000002,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",59.757469999999998,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",64.070899999999995,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",62.251170000000002,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",66.762230000000002,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",64.917259999999999,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",69.283379999999994,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",67.391109999999998,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",71.775710000000004,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",69.828180000000003,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",74.496719999999996,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",72.459280000000007,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",188.64419000000001,"Lag",0.99662869997202697,15.529497438256399]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",160.66412,"Lag",0.99656464385046195,13.3518362191327]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",188.14304999999999,"Lag",0.99658337364834604,15.5925451734914]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",160.06486000000001,"Lag",0.99651037048376601,13.407247371656601]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",188.03310999999999,"Lag",0.99654447315743899,15.6723554902352]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",159.85705999999999,"Lag",0.99646376002327197,13.4794413412324]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",187.52360999999999,"Lag",0.99648268928957895,15.7697329204449]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",159.25139999999999,"Lag",0.99638953098910299,13.5693347335955]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",187.33023,"Lag",0.99642323683082601,15.8867631175338]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",158.96248,"Lag",0.99631802203027797,13.678929146825499]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",187.86849000000001,"Lag",0.99638261103047399,16.023127899830602]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",159.40484000000001,"Lag",0.99626936915879705,13.807830126819001]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",188.55633,"Lag",0.996341160049105,16.174174766829498]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",159.99710999999999,"Lag",0.99621979197987898,13.9514388750887]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",189.11661000000001,"Lag",0.99629254491046204,16.330250084987]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",160.46189000000001,"Lag",0.99616148482664701,14.100081522547899]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",189.489,"Lag",0.99623541100430801,16.4887104291643]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",160.74131,"Lag",0.99609273236998797,14.2513061034286]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",190.13586000000001,"Lag",0.99619014792013605,16.6447318149201]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",161.29990000000001,"Lag",0.99603842689918898,14.4004575222468]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",132.94242,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",130.02618000000001,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",133.32830999999999,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",130.49717000000001,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",134.06527,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",131.22432000000001,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",134.97422,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",132.12359000000001,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",136.12620000000001,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",133.26589999999999,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",137.49629999999999,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",134.62631999999999,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",138.93216000000001,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",136.05251999999999,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",142.18695,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",138.82034999999999,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",147.21588,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",143.69203999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",3.7,"Lag",0.97052675246241005,0.91875428241650603]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",3.8250000000000002,"Lag",0.97052675246241005,0.949793278444091]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",3.7,"Lag",0.97052675246241005,0.91875428241650603]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",3.8250000000000002,"Lag",0.97052675246241005,0.949793278444091]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",3.7,"Lag",0.97052675246241005,0.91875428241650603]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",3.8250000000000002,"Lag",0.97052675246241005,0.949793278444091]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",3.7,"Lag",0.97052675246241005,0.91875428241650603]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",3.8250000000000002,"Lag",0.97052675246241005,0.949793278444091]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",3.7,"Lag",0.97052675246241005,0.91875428241650603]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",3.8250000000000002,"Lag",0.97052675246241005,0.949793278444091]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",3.7,"Lag",0.97052675246241005,0.91875428241650603]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",3.8250000000000002,"Lag",0.97052675246241005,0.949793278444091]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",3.7,"Lag",0.97052675246241005,0.91875428241650603]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",3.8250000000000002,"Lag",0.97052675246241005,0.949793278444091]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",3.7,"Lag",0.97052675246241005,0.91875428241650603]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",3.8250000000000002,"Lag",0.97052675246241005,0.949793278444091]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",3.7,"Lag",0.97052675246241005,0.91875428241650603]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",3.8250000000000002,"Lag",0.97052675246241005,0.949793278444091]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",3.7,"Lag",0.97052675246241005,0.91875428241650603]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",3.8250000000000002,"Lag",0.97052675246241005,0.949793278444091]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",2.5651299999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",2.62771,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",60.131590000000003,"Lag",0.96732201195338896,15.7614800823987]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",56.565950000000001,"Lag",0.96711528757211096,14.8760889960323]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",59.772820000000003,"Lag",0.96670471631970201,15.822344919700001]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",56.190739999999998,"Lag",0.96645436705823096,14.9328715845761]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",59.357010000000002,"Lag",0.96596237021365505,15.895678238597201]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",55.75844,"Lag",0.96565825373959802,15.0021102391173]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",59.02693,"Lag",0.96526187582100198,15.977853648803]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",55.412370000000003,"Lag",0.96490578956494699,15.080315140951299]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",58.712589999999999,"Lag",0.96452218130197898,16.070372468170401]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",55.180430000000001,"Lag",0.96412191610622699,15.1932948665001]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",58.47466,"Lag",0.96381851582721401,16.172095755938699]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",56.454030000000003,"Lag",0.96356774409587198,15.670349143592899]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",59.49342,"Lag",0.96326855965857705,16.585569361064199]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",57.794870000000003,"Lag",0.96304516059048995,16.163799067443001]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",60.687269999999998,"Lag",0.96283906427090105,17.0227439272231]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",59.019480000000001,"Lag",0.96261104324471503,16.608611709744299]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",62.008540000000004,"Lag",0.96235017444391102,17.514111686879701]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",60.236159999999998,"Lag",0.96752644622639505,15.736916194041401]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",63.173630000000003,"Lag",0.96744835990809797,16.525178084512898]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",61.383679999999998,"Lag",0.96735664044619896,16.080712076996299]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",57.648890000000002,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",56.754910000000002,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",57.677669999999999,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",56.7789,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",57.754080000000002,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",56.850580000000001,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",57.857550000000003,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",56.949390000000001,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",57.989820000000002,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",57.076970000000003,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",58.164969999999997,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",57.247439999999997,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",59.545259999999999,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",58.600250000000003,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",61.23847,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",60.26596,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",63.086019999999998,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",62.058120000000002,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",139.93586999999999,"Lag",0.96825249658537604,36.127309654300397]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",125.53238,"Lag",0.96812088952286302,32.4791873585445]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",140.60695000000001,"Lag",0.96800317664287605,36.449899454767397]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",126.0855,"Lag",0.96784181454907403,32.771900198218802]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",141.29490000000001,"Lag",0.967696456463218,36.812174314457103]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",126.65566,"Lag",0.96749825218804297,33.104341154790703]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",142.06318999999999,"Lag",0.96739342598026301,37.194320026094701]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",127.31310000000001,"Lag",0.96715868720320897,33.458410729569501]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",142.94381999999999,"Lag",0.96708100436933397,37.612910575816102]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",128.08319,"Lag",0.966808538325033,33.849003659368698]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",143.98928000000001,"Lag",0.96678584252811794,38.066244693133697]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",129.01812000000001,"Lag",0.96647786927315604,34.274342689568599]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",145.17894000000001,"Lag",0.96650293097387496,38.552375991262799]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",130.09733,"Lag",0.96616116958681797,34.732499163015198]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",146.53495000000001,"Lag",0.96627161247744897,39.053642266040498]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",131.34347,"Lag",0.96590272934857602,35.205937515766102]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",147.74575999999999,"Lag",0.96602443480705502,39.527988571290699]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",132.45638,"Lag",0.96562645526270796,35.655487665865301]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",148.94071,"Lag",0.96578823538966996,39.993334213108803]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",133.55896999999999,"Lag",0.96536262584041099,36.097440326174301]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",121.98214,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",119.37478,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",122.83383000000001,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",120.20417,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",123.78913,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",121.13787000000001,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",124.80825,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",122.13611,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",125.94116,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",123.24814000000001,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",127.21536999999999,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",124.50147,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",128.59879000000001,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",125.86400999999999,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",130.01275000000001,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",127.25834,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",131.36545000000001,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",128.59268,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",121.99511,"Lag",0.96938964212269096,30.898975231988899]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",122.20269,"Lag",0.96938964212269096,30.951551185882899]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",122.86566000000001,"Lag",0.96938964212269096,31.119468519697001]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",123.4006,"Lag",0.96938964212269096,31.2549583586799]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",123.80958,"Lag",0.96938964212269096,31.358544993344001]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",124.81765,"Lag",0.96938964212269096,31.613869407266101]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",125.44025999999999,"Lag",0.96938964212269096,31.771564342490901]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",128.25169,"Lag",0.96938964212269096,32.4836445720711]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",128.16825,"Lag",0.96938964212269096,32.4625108520937]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",131.42472000000001,"Lag",0.96938964212269096,33.287311009032102]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",131.86625000000001,"Lag",0.96938964212269096,33.3991419220431]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",135.05277000000001,"Lag",0.96938964212269096,34.206225112150001]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",135.28554,"Lag",0.96938964212269096,34.265181200346902]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",138.83341999999999,"Lag",0.96938964212269096,35.163789810528598]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",138.43682999999999,"Lag",0.96938964212269096,35.063341320525602]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",142.23867000000001,"Lag",0.96938964212269096,36.026273031443999]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",142.01942,"Lag",0.96938964212269096,35.970741294806302]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",145.77520999999999,"Lag",0.96938964212269096,36.922009441427498]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",145.22971999999999,"Lag",0.96938964212269096,36.783847493794497]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",149.1275,"Lag",0.96938964212269096,37.771078930199998]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",124.23878000000001,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",121.15555999999999,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",125.41806,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",122.31506,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",127.56639,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",124.40279,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",132.09684999999999,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",128.89571000000001,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",137.27446,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",134.02786,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",142.60993999999999,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",139.33055999999999,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",147.49901,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",144.13697999999999,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",152.29189,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",148.82881,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",157.52715000000001,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",153.8905,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",60.864100000000001,"Lag",0.96047228187381195,17.640366078048501]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",55.517560000000003,"Lag",0.96022313391117697,16.144561083095098]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",60.821759999999998,"Lag",0.95991650782567195,17.7593507173723]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",55.755870000000002,"Lag",0.95962935408021299,16.342063356596]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",60.794820000000001,"Lag",0.959253849138335,17.906952233723899]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",56.0854,"Lag",0.95893074349196605,16.589394718146899]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",61.517919999999997,"Lag",0.95860647785306796,18.272630310403901]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",57.350200000000001,"Lag",0.958277788504593,17.106624558353499]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",62.62003,"Lag",0.95797186778757903,18.751403724160301]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",58.524749999999997,"Lag",0.95760876806625095,17.605664558319798]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",64.132140000000007,"Lag",0.95727237474189697,19.374041116976599]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",59.838000000000001,"Lag",0.95684697006783603,18.1726667587881]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",65.630899999999997,"Lag",0.95667483199380199,19.974387377376701]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",61.347360000000002,"Lag",0.95621664334488099,18.775978588125501]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",67.2179,"Lag",0.95629035918440997,20.554193417227101]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",62.917070000000002,"Lag",0.95581380777441005,19.350947393360201]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",69.109120000000004,"Lag",0.95603874585552895,21.1974506494727]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",64.643180000000001,"Lag",0.95553852848812004,19.948011692846102]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",70.750420000000005,"Lag",0.95569818407275198,21.790637796282802]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",66.216800000000006,"Lag",0.95517749411304298,20.522263961761599]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",57.755400000000002,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",56.700009999999999,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",58.097230000000003,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",57.035690000000002,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",58.586449999999999,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",57.467730000000003,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",60.66977,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",59.301990000000004,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",63.118450000000003,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",61.734070000000003,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",65.713650000000001,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",64.318399999999997,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",68.135149999999996,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",66.705659999999995,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",70.534570000000002,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",69.062160000000006,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",73.164069999999995,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",71.615260000000006,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",54.959739999999996,"Lag",0.96011204771452396,16.0060463439095]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",48.263379999999998,"Lag",0.95970130016782795,14.1326013241386]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",54.900910000000003,"Lag",0.95958314743226703,16.101265968332498]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",48.441560000000003,"Lag",0.95911529971905696,14.2941293913777]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",54.869120000000002,"Lag",0.95899142430110296,16.2168642654308]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",48.712449999999997,"Lag",0.95847006715470195,14.494408670171101]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",55.157470000000004,"Lag",0.958417432141067,16.423205182036099]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",49.806060000000002,"Lag",0.95790977664244303,14.9260377039954]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",56.084429999999998,"Lag",0.95779961347044196,16.8310025808677]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",50.759149999999998,"Lag",0.95723568387499602,15.341145510028401]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",57.429009999999998,"Lag",0.95718264416521903,17.3684920580992]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",51.883659999999999,"Lag",0.95653827181909601,15.8170658593304]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",58.774169999999998,"Lag",0.95669206282894204,17.883780244456801]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",53.19558,"Lag",0.95600511294352097,16.323054469133499]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",60.148789999999998,"Lag",0.95636553077884101,18.375655072075901]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",54.515180000000001,"Lag",0.955652608811705,16.799536315343499]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",61.797260000000001,"Lag",0.95616252965833803,18.926168812830799]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",55.974939999999997,"Lag",0.95542233780818397,17.297254535893298]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",63.218310000000002,"Lag",0.95586928664343096,19.430535138901899]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",57.296660000000003,"Lag",0.95510136434877602,17.773831242855898]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",39.30489,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",38.319740000000003,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",39.525970000000001,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",38.535490000000003,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",39.96499,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",38.833649999999999,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",41.398319999999998,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",40.188049999999997,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",43.095559999999999,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",41.864370000000001,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",44.904719999999998,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",43.656399999999998,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",46.609589999999997,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",45.329340000000002,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",48.303629999999998,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",46.985860000000002,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",50.160319999999999,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",48.781410000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",221.89696000000001,"Lag",0.93493624904521699,84.211660868262499]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",211.13202999999999,"Lag",0.93475316586845303,80.250857867364303]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",222.77825000000001,"Lag",0.93397840217308103,85.232412215590003]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",211.89272,"Lag",0.93374362309262904,81.227236158674899]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",223.85825,"Lag",0.93432367177843401,85.397421516158502]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",212.45756,"Lag",0.93249335531355304,82.292206946992906]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",224.46473,"Lag",0.93337012357727001,86.314989173114895]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",212.62213,"Lag",0.93308079088870799,81.957672811704697]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",225.25485,"Lag",0.93244128051344799,87.286386789099296]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",213.3168,"Lag",0.93209701528748201,82.893950956737001]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",226.03369000000001,"Lag",0.931425687542763,88.317078933477404]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",214.00019,"Lag",0.93102068564501395,83.889523630163097]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",227.00223,"Lag",0.93042693875428395,89.411851613300101]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",214.87325999999999,"Lag",0.92996179153091696,84.949169480318005]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",228.22254000000001,"Lag",0.92953104397120201,90.535611612063093]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",215.99907999999999,"Lag",0.92901181903528096,86.038163226485196]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",229.39615000000001,"Lag",0.92879177955064296,91.532537312632002]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",217.09574000000001,"Lag",0.92822808157428305,87.006776268177703]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",230.48935,"Lag",0.92804224338326902,92.508193050487705]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",218.29178999999999,"Lag",0.92744236923176404,88.020274201815695]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",204.72987000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",200.30372,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",206.87824000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",202.39855,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",208.94709,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",204.42076,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",210.88412,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",206.31808000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",213.06665000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",208.46091000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",215.34056000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",210.69512,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",218.00788,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",213.32272,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",220.46086,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",215.74005,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",222.79518999999999,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",218.04279,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",349.61284999999998,"Lag",0.99035127458436301,48.9212968503223]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",305.02645999999999,"Lag",0.99017257060605202,43.081613215787399]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",350.33496000000002,"Lag",0.99019888067290796,49.413671521685401]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",305.32452000000001,"Lag",0.98999453801213699,43.518448117161803]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",352.03841,"Lag",0.99007762509229902,49.964739733612099]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",306.60649999999998,"Lag",0.98985281771931599,44.0143144735123]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",354.00152000000003,"Lag",0.98996329535370797,50.536381130137201]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",308.19394999999997,"Lag",0.98971933536550305,44.536753959899599]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",356.22406000000001,"Lag",0.98983461240519999,51.183628993865803]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",310.04336000000001,"Lag",0.98956919474896299,45.135131279173798]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",359.23590000000002,"Lag",0.98972113461247502,51.908153774870598]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",314.94484,"Lag",0.98945311263721303,46.107150862587197]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",362.5788,"Lag",0.98960484043623098,52.6913821657147]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",324.86416000000003,"Lag",0.98936896085625903,47.751723090593899]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",369.89316000000002,"Lag",0.98951774815678595,53.982614679924303]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",334.15219000000002,"Lag",0.98929022958843105,49.301456201038697]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",380.83803,"Lag",0.98947672634313899,55.690304188976498]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",343.86842999999999,"Lag",0.98924314691417703,50.848226413778796]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",390.71131000000003,"Lag",0.98942952921145499,57.264115968853602]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",353.08253000000002,"Lag",0.98919242099773397,52.335702371037897]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",246.65665000000001,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",241.00405000000001,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",248.85481999999999,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",243.14777000000001,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",254.19900000000001,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",247.14228,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",263.93713000000002,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",256.76560000000001,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",275.48,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",268.17270000000002,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",287.9128,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",280.49342999999999,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",299.56211000000002,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",291.93329999999997,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",310.93561,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",303.06639999999999,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",323.17971,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",314.92520999999999,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",198.61023,"Lag",0.99049656894365201,27.5784319643864]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",175.82332,"Lag",0.99035824343619805,24.5939260331231]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",197.60232999999999,"Lag",0.99032525480947597,27.688281487550899]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",174.73965999999999,"Lag",0.99016173206992997,24.693852922224799]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",196.57381000000001,"Lag",0.99012505847351695,27.831912713385901]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",173.63504,"Lag",0.98993151783495004,24.827516982640201]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",195.69309000000001,"Lag",0.98990786079465798,28.01488330794]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",173.75140999999999,"Lag",0.98969314326167301,25.1410810196139]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",195.11311000000001,"Lag",0.98969190030819698,28.233755953239001]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",176.42721,"Lag",0.98948695294674804,25.786378077915199]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",197.52422999999999,"Lag",0.98951597929323598,28.829374281528501]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",179.95829000000001,"Lag",0.98930824909335502,26.528682695077599]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",201.38543000000001,"Lag",0.98935491728926095,29.621468560456201]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",183.75443999999999,"Lag",0.98913360570338305,27.312257077677501]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",204.9161,"Lag",0.98919647740467798,30.367920485739599]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",187.12385,"Lag",0.98896036645999497,28.0375880424413]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",209.43638999999999,"Lag",0.98908607375714996,31.198617670374801]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",191.03546,"Lag",0.98883494451779497,28.788563620669901]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",213.48134999999999,"Lag",0.98898064389144302,31.9569656774229]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",194.78415000000001,"Lag",0.98871899409651898,29.5081077893627]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",142.51747,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",139.41202999999999,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",142.95097999999999,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",139.83505,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",144.86711,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",141.00971999999999,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",149.69691,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",145.79846000000001,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",155.44906,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",151.49889999999999,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",161.58185,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",157.59393,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",167.27502000000001,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",163.19423,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",172.89887999999999,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",168.70518000000001,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",179.08107000000001,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",174.69195999999999,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",272.21841000000001,"Lag",0.98604015702298597,45.968165284588899]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",240.94058000000001,"Lag",0.98596418881436498,40.799352934921401]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",274.84474,"Lag",0.98596261325866397,46.543136797075398]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",244.55766,"Lag",0.98588031518076202,41.538050666120398]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",277.95398,"Lag",0.98589769024834695,47.180724766533899]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",249.03067999999999,"Lag",0.98581278080023804,42.401009861978899]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",286.26742999999999,"Lag",0.98585221497429598,48.671845236996397]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",258.30605000000003,"Lag",0.98576802581857204,44.051092254524598]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",295.46480000000003,"Lag",0.98580456859312804,50.321951278357297]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",267.48142999999999,"Lag",0.98571807703706305,45.697564342264997]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",307.43738000000002,"Lag",0.98577160932762198,52.423124680914498]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",278.15037000000001,"Lag",0.98568098311917396,47.583304943648997]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",319.26231999999999,"Lag",0.98574645654194704,54.488613968990499]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",289.65717999999998,"Lag",0.98565583709940296,49.596221713976803]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",330.64213999999998,"Lag",0.98571958554989902,56.485136550596401]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",300.57736999999997,"Lag",0.98562813060617405,51.516788219976497]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",343.50258000000002,"Lag",0.98570298796893696,58.716980801339098]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",312.21546999999998,"Lag",0.98560964377901505,53.546634886887702]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",355.53836000000001,"Lag",0.98568918413417095,60.804301766722503]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",323.54284999999999,"Lag",0.98559565932105697,55.5168893336377]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",204.79837000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",199.77250000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",207.25744,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",202.17057,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",212.97805,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",206.72748000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",222.31028000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",215.91928999999999,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",233.17400000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",226.62307000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",244.7885,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",238.09708000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",255.83974000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",248.92544000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",266.97422,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",259.80248999999998,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",279.16636,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",271.60203999999999,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",109.12783,"Lag",0.989968824199701,15.574462176395899]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",98.212999999999994,"Lag",0.98985490960997202,14.097305181444099]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",109.42874999999999,"Lag",0.98982841519126097,15.728005333066401]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",98.433310000000006,"Lag",0.98969732837320701,14.239938995013301]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",110.12976,"Lag",0.98966682264794203,15.955954980235701]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",98.792339999999996,"Lag",0.98951238871699099,14.421606826603799]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",112.38294999999999,"Lag",0.98952742990102105,16.3935947121306]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",100.84417999999999,"Lag",0.98935635253532805,14.8319968843459]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",114.30971,"Lag",0.98939392999895803,16.782301542840099]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",102.82687,"Lag",0.98921090458497196,15.2282729938008]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",117.2638,"Lag",0.98929071552352199,17.3009274830737]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",105.34007,"Lag",0.98909252464730102,15.6872311474078]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",120.07071999999999,"Lag",0.98919159142147695,17.798191816563801]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",108.08264,"Lag",0.98898544068168803,16.1757866826275]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",122.69167,"Lag",0.98909407678773698,18.269907838322599]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",110.5883,"Lag",0.98887901336925199,16.631899948324399]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",125.62597,"Lag",0.988996937955819,18.791364612671]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",113.13028,"Lag",0.98876811697922096,17.1002621502187]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",128.36868999999999,"Lag",0.98891922215286698,19.270455807231599]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",115.67334,"Lag",0.98868247806034804,17.552332386540701]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",83.221209999999999,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",81.316890000000001,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",83.566879999999998,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",81.654880000000006,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",84.09263,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",82.172960000000003,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",85.822879999999998,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",83.498729999999995,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",89.237129999999993,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",86.879040000000003,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",92.875600000000006,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",90.491600000000005,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",96.276939999999996,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",93.835729999999998,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",99.635120000000001,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",97.125429999999994,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",103.3056,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",100.67981,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",137.30043000000001,"Lag",0.98960451018075102,19.953362311679602]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",119.03934,"Lag",0.98938757278048794,17.482000244753799]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",136.71996999999999,"Lag",0.98940187257464196,20.064810205942099]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",118.80809000000001,"Lag",0.98915572384723505,17.640708425636198]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",136.39487,"Lag",0.98920926234752804,20.201130090630699]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",119.2255,"Lag",0.98894402878117305,17.877515797562001]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",136.38686000000001,"Lag",0.98901977304881805,20.379464358665398]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",121.65553,"Lag",0.98877183834154503,18.385801868782998]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",138.50658999999999,"Lag",0.98884914435666904,20.8590926580294]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",123.80653,"Lag",0.98858373137079203,18.869662089233501]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",141.68823,"Lag",0.98869492346898702,21.487817494906299]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",126.40797999999999,"Lag",0.98840400857278798,19.419866993422399]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",144.71429000000001,"Lag",0.98855314641416003,22.086304767226501]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",129.30833999999999,"Lag",0.98824760709221604,20.001342673783299]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",147.69969,"Lag",0.98843882627985102,22.656189486068101]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",132.11405999999999,"Lag",0.98812120041269302,20.546910424898201]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",151.15731,"Lag",0.98834020181719695,23.287000736214601]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",135.05534,"Lag",0.98800595625777299,21.107842873196699]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",154.11371,"Lag",0.98822305214112904,23.863559490116]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",137.71886000000001,"Lag",0.98787357244546803,21.644764753167799]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",91.53837,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",90.007599999999996,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",91.929329999999993,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",90.468580000000003,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",93.533590000000004,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",91.593170000000001,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",96.822280000000006,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",94.869950000000003,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",100.70283000000001,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",98.734129999999993,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",104.81178,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",102.8361,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",108.66694,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",106.64601,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",112.47734,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",110.39716,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",116.64979,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",114.45771000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",62.699399999999997,"Lag",0.98962984278820298,9.1005871939513803]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",52.662379999999999,"Lag",0.98936518985686694,7.7422284928565803]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",62.868580000000001,"Lag",0.98946966747524701,9.1964638829407992]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",52.74136,"Lag",0.989169822611216,7.8258979774328603]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",63.191220000000001,"Lag",0.98933435855340801,9.3038142213956903]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",52.974299999999999,"Lag",0.98900481654513905,7.9211087789048404]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",63.562579999999997,"Lag",0.98920230415322796,9.4171918774626704]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",53.26484,"Lag",0.98884404876020005,8.0235486715497597]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",64.000299999999996,"Lag",0.98905541554708398,9.5473856237717492]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",53.622239999999998,"Lag",0.98866550002952103,8.14287232186701]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",64.620440000000002,"Lag",0.98893204438478299,9.6949849246167492]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",54.162089999999999,"Lag",0.98851668605298104,8.2796055867659906]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",65.287599999999998,"Lag",0.98879852107124599,9.8549851266678097]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",54.748959999999997,"Lag",0.9883558944359,8.4287397528710297]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",65.984380000000002,"Lag",0.98867460483494096,10.016045931892601]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",55.366109999999999,"Lag",0.98820706183556095,8.5790238431577404]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",66.717269999999999,"Lag",0.98858276108580401,10.1689851661686]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",56.892949999999999,"Lag",0.98814442063528996,8.8394121898927605]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",67.416830000000004,"Lag",0.98848956419264999,10.3181961761245]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",58.510770000000001,"Lag",0.98808767288343302,9.1128957888111408]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",39.618490000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",38.159030000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",40.0505,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",38.577759999999998,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",40.568429999999999,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",39.08314,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",41.143859999999997,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",39.646740000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",41.833390000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",40.324460000000002,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",42.633650000000003,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",41.112900000000003,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",43.45505,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",41.92248,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",45.086860000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",43.376860000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",47.017829999999996,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",45.234180000000002,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",207.05090999999999,"Lag",0.98987339306730904,29.692187315575101]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",195.41154,"Lag",0.98980642605592595,28.116974800828501]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",207.29070999999999,"Lag",0.98973486391777299,29.932357984933599]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",195.56219999999999,"Lag",0.98965863506919105,28.345081720725901]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",207.68236999999999,"Lag",0.98959412806410696,30.1970143353639]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",195.86515,"Lag",0.98950839216362096,28.597732515685198]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",208.14603,"Lag",0.98945783623286898,30.465133704883499]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",196.24672000000001,"Lag",0.98936281395622405,28.85474224651]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",208.69549000000001,"Lag",0.98931843852105505,30.7500967649245]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",196.71455,"Lag",0.98921383949598896,29.1286579218919]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",209.41969,"Lag",0.989185606468025,31.051205305533099]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",197.35704000000001,"Lag",0.98907183719464098,29.418708251052699]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",210.21544,"Lag",0.98904614505263699,31.372850409933399]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",198.07111,"Lag",0.98892270143655303,29.7292992040509]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",211.21718000000001,"Lag",0.98892147245973505,31.704234543820501]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",198.99155999999999,"Lag",0.98878938992093601,30.049681967131601]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",212.17501999999999,"Lag",0.98978849925951995,30.5562527216325]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",199.83190999999999,"Lag",0.98866555599999395,30.345648412244898]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",213.43593000000001,"Lag",0.98972610854778198,30.833060823695899]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",200.55055999999999,"Lag",0.98853462259524905,30.6332270753309]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",202.0839,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",198.71163999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",203.28434999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",199.88330999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",204.52898999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",201.10038,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",205.83043000000001,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",202.37545,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",207.19613000000001,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",203.71478999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",208.68671000000001,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",205.17899,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",210.22314,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",206.68904000000001,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",211.79818,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",208.23905999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",213.28583,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",209.70303999999999,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",269.88722999999999,"Lag",0.95976621870588497,78.961326422868495]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",250.20266000000001,"Lag",0.959563691439136,73.397887237521104]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",269.72964000000002,"Lag",0.95907824380024298,79.630172412062194]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",249.88930999999999,"Lag",0.95881751447100805,74.02271086364]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",269.23093999999998,"Lag",0.95822881100699397,80.357400564366003]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",249.23586,"Lag",0.957894545139233,74.706202108613198]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",268.45801,"Lag",0.95731058130619995,81.061287946034895]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",248.32782,"Lag",0.95689485024246201,75.371903425342296]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",267.56439,"Lag",0.95629420502157403,81.813201022816003]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",247.30010999999999,"Lag",0.95578598585362895,76.085918719222306]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",266.94954000000001,"Lag",0.95530054853032598,82.6127363981618]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",246.55110999999999,"Lag",0.95469985031526705,76.847539353899904]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",265.92363999999998,"Lag",0.954108126219396,83.464451299193797]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",245.39116999999999,"Lag",0.95339346159446003,77.661370603503201]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",265.15096,"Lag",0.95295060361745498,84.342306172319198]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",244.48325,"Lag",0.95212257049273197,78.501002669860299]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",265.74671000000001,"Lag",0.95216551841957597,85.287287285764904]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",249.80946,"Lag",0.95419029389362897,78.331431759429407]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",266.58667000000003,"Lag",0.95148089982841899,86.213817657419099]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",255.55464000000001,"Lag",0.95382148247666798,80.478357564284806]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",242.95344,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",238.99834999999999,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",244.47970000000001,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",240.49131,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",246.01430999999999,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",241.99494000000001,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",247.53635,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",243.48831999999999,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",249.17770999999999,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",245.10101,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",251.01074,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",246.90538000000001,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",257.36189000000002,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",251.92626000000001,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",266.02334000000002,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",260.41753999999997,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",275.59321999999997,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",269.68846000000002,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",20.923580000000001,"Lag",0.96180164790609501,5.9552546686997996]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",19.511130000000001,"Lag",0.96176516269234502,5.5560547025667297]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",21.136849999999999,"Lag",0.96169239073261303,6.0250695411885697]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",19.707989999999999,"Lag",0.96164787802282603,5.6212316257870398]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",21.332249999999998,"Lag",0.96152370137787901,6.0949492548742699]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",19.8872,"Lag",0.96146673442397901,5.6865355686831904]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",21.474060000000001,"Lag",0.961363534530841,6.1489967068235796]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",20.01681,"Lag",0.96129468326913603,5.7371349413469899]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",21.61788,"Lag",0.96121079395093001,6.2031466034901896]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",20.14864,"Lag",0.96113056326354096,5.7878961109125102]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",21.764469999999999,"Lag",0.96105697356932496,6.2583365874665597]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",20.283249999999999,"Lag",0.96096524305613595,5.8397001940822904]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",21.916129999999999,"Lag",0.960910512314882,6.3145121021853701]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",20.422940000000001,"Lag",0.96080780464254301,5.8924926342889998]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",22.045380000000002,"Lag",0.96069383625182703,6.3704161870679403]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",20.540320000000001,"Lag",0.96057475836620299,5.9450419076044296]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",22.15212,"Lag",0.96051189796369396,6.41697604037945]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",20.637409999999999,"Lag",0.96037901206675103,5.98887438672699]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",22.26887,"Lag",0.96039192412889696,6.4611973388514699]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",20.745100000000001,"Lag",0.96024994275256004,6.03053506238534]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",15.12758,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",14.9055,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",15.319900000000001,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",15.09502,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",15.4908,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",15.26351,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",15.63838,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",15.409050000000001,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",15.789429999999999,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",15.558059999999999,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",16.32038,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",16.028479999999998,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",16.883600000000001,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",16.584219999999998,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",17.417249999999999,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",17.108470000000001,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",17.982379999999999,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",17.656410000000001,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",117.20149000000001,"Lag",0.99252116172162996,14.4149088360174]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",102.59014999999999,"Lag",0.99241444646446697,12.7085519063021]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",116.42832,"Lag",0.99238315169723601,14.452844560153601]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",101.78722999999999,"Lag",0.99225433141949204,12.743013334538]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",116.17547999999999,"Lag",0.99229202234575498,14.508472709522]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",101.50485,"Lag",0.99214851744271704,12.795191712447799]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",115.44229,"Lag",0.99211638032990002,14.582181468191999]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",100.74347,"Lag",0.99194391625196698,12.865608356784101]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",115.55612000000001,"Lag",0.99203072793111102,14.676590274490501]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",100.82933,"Lag",0.99184450739649499,12.956750741021001]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",114.68745,"Lag",0.99178626649398505,14.790725503438001]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",99.932739999999995,"Lag",0.99155846636935996,13.0676253870599]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",114.06309,"Lag",0.99155266544034704,14.9205589023214]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",100.69653,"Lag",0.99131362623042096,13.3595711843943]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",114.79422,"Lag",0.99150877145045102,15.0556613638326]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",103.26961,"Lag",0.99130256397834904,13.709782194929099]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",117.21411000000001,"Lag",0.99148238088674301,15.397217171664799]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",105.86682999999999,"Lag",0.99128121634774802,14.0720471419879]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",119.85612,"Lag",0.99146287834642799,15.7625181267339]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",108.36136,"Lag",0.99126149122438501,14.420124932036201]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",103.26652,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",96.627700000000004,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",103.42214,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",96.946619999999996,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",103.64156,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",97.484110000000001,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",103.90752000000001,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",98.187950000000001,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",104.2914,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",99.10615,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",104.66164000000001,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",100.93671999999999,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",106.4238,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",104.38171,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",109.84175,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",107.74585,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",113.58284999999999,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",111.38231,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",232.3295,"Lag",0.99317315830715902,27.287378508782002]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",200.29938999999999,"Lag",0.99309487543646502,23.661301568154499]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",232.78631999999999,"Lag",0.993098107113774,27.492469160443399]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",200.52938,"Lag",0.99300676528474696,23.84071316244]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",233.95572000000001,"Lag",0.99302403286962604,27.7800094479236]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",201.47239999999999,"Lag",0.99291995203077998,24.1026253363165]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",235.86456999999999,"Lag",0.99295428689653198,28.147809295633799]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",203.16238999999999,"Lag",0.99283853892338703,24.445648397458498]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",238.45932999999999,"Lag",0.99288118718753404,28.606289398703399]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",206.16435999999999,"Lag",0.99275642345562398,24.950228085918098]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",241.71809999999999,"Lag",0.99280592471458096,29.151761599474]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",213.75665000000001,"Lag",0.99269133995964098,25.986291075910099]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",248.42419000000001,"Lag",0.99275559950296099,30.0662858449457]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",222.47053,"Lag",0.99264718490569903,27.1281139794451]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",257.18376000000001,"Lag",0.99271713759917102,31.209865875866701]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",230.99507,"Lag",0.99260712272813101,28.245086644254801]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",266.93184000000002,"Lag",0.99268553783778102,32.463793604006902]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",239.93907999999999,"Lag",0.99257256259985505,29.407986908372798]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",276.08087999999998,"Lag",0.99265346766522899,33.650827892210998]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",248.68648999999999,"Lag",0.99253905717705004,30.5495533139608]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",184.11929000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",181.18290999999999,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",185.43601000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",182.47504000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",187.64508000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",184.65996000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",190.38933,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",187.38051999999999,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",193.92856,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",190.89606000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",203.84954999999999,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",200.04463999999999,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",213.71641,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",209.80698000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",223.67497,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",219.63336000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",234.50518,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",230.22557,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",316.07996000000003,"Lag",0.99301777472499697,37.548488021277699]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",266.44270999999998,"Lag",0.99289621746776502,31.929135242871201]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",316.42707999999999,"Lag",0.99291844156193398,37.859009837799498]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",266.44305000000003,"Lag",0.992776328709711,32.200398656550398]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",317.48696999999999,"Lag",0.99281958696722905,38.252891998671203]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",267.15685999999999,"Lag",0.99265703691319795,32.5551016604472]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",319.25747999999999,"Lag",0.99272494090076802,38.721670878307997]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",272.45576,"Lag",0.99255938195112903,33.423323864398]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",321.59179,"Lag",0.99262408801413704,39.277215712686498]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",279.78268000000003,"Lag",0.99246393805366095,34.544074000742199]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",331.55227000000002,"Lag",0.99254590554373601,40.710179498694202]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",288.61428000000001,"Lag",0.99237387254461096,35.849239108046199]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",342.13076000000001,"Lag",0.99248582185068401,42.179961039117302]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",298.72320000000002,"Lag",0.99230832119560097,37.265861388354097]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",352.45866999999998,"Lag",0.99243076890125603,43.613955894063302]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",308.47573999999997,"Lag",0.99224805647070802,38.634719536328703]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",364.03786000000002,"Lag",0.99238529796034103,45.1834462316775]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",318.69078999999999,"Lag",0.99219587896150496,40.049777791199901]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",374.73079000000001,"Lag",0.99233861935481504,46.654612009927199]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",328.57873999999998,"Lag",0.99214446037378201,41.429813085799601]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",218.11991,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",213.54625999999999,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",219.92868000000001,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",215.32363000000001,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",222.61926,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",217.98338000000001,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",231.79656,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",225.99981,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",242.95068000000001,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",237.05893,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",255.13305,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",249.16839999999999,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",267.06007,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",260.93387999999999,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",279.04777999999999,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",272.72732000000002,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",292.07096000000001,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",285.42216999999999,"Lag","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",80.812330000000003,"Lag",0.99921283785163595,3.20834631390326]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",92.932460000000006,"Lag",0.99922003832136097,3.6725966130235399]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",80.937899999999999,"Lag",0.99920686462113395,3.2255148934313098]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",93.079369999999997,"Lag",0.99921487050364,3.6905826013898801]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",81.233490000000003,"Lag",0.999200521525755,3.2502294844708399]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",93.619590000000002,"Lag",0.99920951003367697,3.7246675168957202]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",82.958590000000001,"Lag",0.99919720328091499,3.3261418331775401]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",95.509169999999997,"Lag",0.999206583623655,3.8068801189164798]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",84.122910000000005,"Lag",0.99918474611782704,3.3989235366789101]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",96.625990000000002,"Lag",0.99919566276958105,3.8778423791273702]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",85.744470000000007,"Lag",0.99917583302046997,3.48335150080272]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",98.625600000000006,"Lag",0.99918807043992797,3.9767511966399098]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",87.657820000000001,"Lag",0.99917089570442097,3.5717449017229899]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",100.59529999999999,"Lag",0.999183613896511,4.0673030318637302]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",89.365359999999995,"Lag",0.999166325173095,3.6513564255241402]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",102.39270999999999,"Lag",0.99917951985467102,4.1503569423704603]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",90.835350000000005,"Lag",0.99915650621566299,3.7332383100824802]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",104.19011999999999,"Lag",0.99917112861142399,4.2447803452902297]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",92.234179999999995,"Lag",0.99914765926653304,3.8105816707505098]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",105.75578,"Lag",0.99916344558778503,4.3285139738351104]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",82.677139999999994,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",86.281649999999999,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",83.170990000000003,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",86.797669999999997,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",84.791200000000003,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",88.440119999999993,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",87.275199999999998,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",90.971509999999995,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",90.221950000000007,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",93.976690000000005,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",93.315309999999997,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",97.119860000000003,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",96.113259999999997,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",99.994619999999998,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",98.772180000000006,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",102.73909,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",101.64794000000001,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",105.75057,"Lead","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",407.07925999999998,"Lag",0.99537157887309702,39.302670915525297]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",351.18106999999998,"Lag",0.99529936479516701,34.171156496409502]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",405.43290000000002,"Lag",0.99529104720389705,39.485185780023599]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",351.28874000000002,"Lag",0.99520797473547096,34.514693215757902]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",403.89260999999999,"Lag",0.99519842561930205,39.722914346824197]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",351.96221000000003,"Lag",0.99510430637148495,34.955647349620001]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",407.2867,"Lag",0.99511335677562596,40.412598578147502]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",358.63177000000002,"Lag",0.99501440628237003,35.946023276584597]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",413.32472000000001,"Lag",0.99503240609542998,41.352538551005303]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",364.69896,"Lag",0.99492344193851801,36.888641087054097]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",422.7987,"Lag",0.99496360088296398,42.594547396536001]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",372.37441000000001,"Lag",0.99484273113420996,37.965542929509901]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",431.50087000000002,"Lag",0.99489361689406597,43.774540785780303]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",380.62182000000001,"Lag",0.99476400866451198,39.103788857928699]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",439.64335,"Lag",0.99482667026684801,44.8942532070336]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",388.14843999999999,"Lag",0.99468820561667104,40.1669646637718]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",449.76515999999998,"Lag",0.99478167334412004,46.128714349742097]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",396.68790000000001,"Lag",0.99463531733231603,41.256164361680597]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",458.97654999999997,"Lag",0.99474039585131602,47.260734118290898]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",405.01002999999997,"Lag",0.99458850568897295,42.306549098534397]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",256.56383,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",248.38072,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",256.51150999999999,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",248.91763,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",257.79019,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",252.01575,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",266.42378000000002,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",260.61187999999999,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",276.73576000000003,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",270.87205999999998,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",287.74639999999999,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",281.85633000000001,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",298.05959999999999,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",292.04009000000002,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",308.24315000000001,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",302.05741,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",319.40631999999999,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",312.91030000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",1.60327,"Lag",0.97431113208340403,0.37058623302481197]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",1.5655699999999999,"Lag",0.97427891593636895,0.362107962356226]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",1.5966800000000001,"Lag",0.97417085986209295,0.37010938153004802]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",1.55904,"Lag",0.97413509005517995,0.36164460413043098]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",1.5928100000000001,"Lag",0.97403320615224698,0.37023425880335198]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",1.55518,"Lag",0.97399393635103504,0.36177173028189602]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",1.58744,"Lag",0.97390030982060805,0.36996709457724403]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",1.54986,"Lag",0.97385764088837201,0.36151581044659598]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",1.5796399999999999,"Lag",0.97360857963889402,0.37028457800410303]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",1.5420700000000001,"Lag",0.97355836628003201,0.361835542751616]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",1.5712299999999999,"Lag",0.97334749071679305,0.370205344823405]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",1.5337099999999999,"Lag",0.97329044601999704,0.361767553961725]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",1.57019,"Lag",0.973242684605374,0.37071706554683698]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",1.53268,"Lag",0.97318294895637902,0.362281523563319]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",1.5653999999999999,"Lag",0.97307448420158404,0.37079425847736702]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",1.5279400000000001,"Lag",0.97301034516927698,0.36236996088465501]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",1.56426,"Lag",0.974546706309245,0.35984210764867802]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",1.5266599999999999,"Lag",0.97288428903859403,0.362946357181399]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",1.56084,"Lag",0.97444559150185595,0.35979596861554902]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",1.5212600000000001,"Lag",0.97441435959312095,0.35089490885261398]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",1.81643,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",1.7603800000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",1.8146599999999999,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",1.7586599999999999,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",1.8134300000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",1.7574700000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",1.8124100000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",1.7564900000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",1.8109900000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",1.75512,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",1.81091,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",1.75509,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",1.81098,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",1.7552000000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",1.8110299999999999,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",1.7553000000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",1.8111699999999999,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",1.75549,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",15.940160000000001,"Lag",0.92937641505944601,6.3311760703474897]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",14.59422,"Lag",0.929077504221411,5.8102629516644004]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",15.88688,"Lag",0.92904089753728303,6.3267191629367199]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",14.542289999999999,"Lag",0.92870966113910203,5.8063285286958903]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",15.81812,"Lag",0.92846039677055403,6.3280530010259897]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",14.474909999999999,"Lag",0.92807304323810302,5.8081964619928099]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",15.77632,"Lag",0.927944674809138,6.33671168692916]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",14.43446,"Lag",0.92750762874870696,5.8173776323382498]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",15.786619999999999,"Lag",0.92769134622094096,6.3533025406850303]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",14.44609,"Lag",0.92723102012652303,5.8344832300261196]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",15.79105,"Lag",0.92723909055170195,6.3772895183138401]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",14.465960000000001,"Lag",0.92674222363213798,5.8644458815723999]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",15.82394,"Lag",0.92692641743772397,6.4059291812181902]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",14.81631,"Lag",0.92653580130929203,6.0159506637667102]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",15.88974,"Lag",0.92637080169102104,6.4599166180029197]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",15.09198,"Lag",0.92603706313921297,6.1511631449204502]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",16.217099999999999,"Lag",0.92600267150524695,6.6114606598149503]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",15.39059,"Lag",0.92564325262397096,6.2915802032397901]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",16.53415,"Lag",0.92587575207695405,6.7471978522411797]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",15.70316,"Lag",0.92551465921339304,6.42558352136873]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",12.87251,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",12.53899,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",12.873340000000001,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",12.54017,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",12.898199999999999,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",12.56536,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",12.94078,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",12.608280000000001,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",13.00578,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",12.6736,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",13.09182,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",12.759980000000001,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",13.19209,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",12.860609999999999,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",13.28947,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",12.95834,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",13.392200000000001,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",13.06141,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",61.911299999999997,"Lag",0.999952156649766,0.60563546242312905]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",58,"Lag",0.999952156649766,0.56737391753268795]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",61.895609999999998,"Lag",0.999952156649766,0.60548197799612802]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",57.985799999999998,"Lag",0.999952156649766,0.56723500874598098]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",61.920679999999997,"Lag",0.999952156649766,0.60572722048082706]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",58.012390000000003,"Lag",0.999952156649766,0.56749512034024296]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",62.000689999999999,"Lag",0.999952156649766,0.60650990301775398]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",58.093699999999998,"Lag",0.999952156649766,0.56829051987877099]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",62.139119999999998,"Lag",0.999952156649766,0.60786406804196202]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",58.233409999999999,"Lag",0.999952156649766,0.5696572062584]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",62.33305,"Lag",0.999952156649766,0.60976115121139496]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",59.238999999999997,"Lag",0.999952156649766,0.57949419828825699]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",62.5623,"Lag",0.999952156649766,0.612003745531987]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",60.743729999999999,"Lag",0.999952156649766,0.59421393199392802]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",63.393630000000002,"Lag",0.999952156649766,0.62013607240892599]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",62.078209999999999,"Lag",0.999952156649766,0.60726822760546295]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",64.858530000000002,"Lag",0.999952156649766,0.63446617675019601]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",63.464100000000002,"Lag",0.999952156649766,0.62082543171872795]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",66.160169999999994,"Lag",0.999952156649766,0.64719922133670005]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",64.776759999999996,"Lag",0.999952156649766,0.63366627734956404]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",54.42821,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",52.991430000000001,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",54.443109999999997,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",53.006889999999999,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",54.52243,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",53.08672,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",54.648789999999998,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",53.213540000000002,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",54.832769999999996,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",53.39799,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",55.073270000000001,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",53.638950000000001,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",55.355829999999997,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",53.921999999999997,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",55.6342,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",54.200789999999998,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",55.929540000000003,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",54.496490000000001,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",271.20182,"Lag",0.98140546984937305,53.042429619857899]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",247.49704,"Lag",0.98127776741778305,48.576872582646601]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",275.93196,"Lag",0.98118498277356503,54.295762569289501]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",253.56488999999999,"Lag",0.98104718858435003,50.082206196258397]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",335.29180000000002,"Lag",0.98121991858357005,65.913087411624105]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",316.35045000000002,"Lag",0.98112861291355202,62.344875481929698]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",342.55662000000001,"Lag",0.981006370009194,67.734114893984795]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",323.37427000000002,"Lag",0.98090271443166699,64.120502870049094]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",348.48383999999999,"Lag",0.98078847237216205,69.3118180727203]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",329.79160999999999,"Lag",0.98067650697091102,65.790535900193404]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",356.84703000000002,"Lag",0.98056526769837005,71.398558090754506]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",337.15233000000001,"Lag",0.980436150261074,67.688428480576107]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",364.72622000000001,"Lag",0.98036261587194395,73.365928989632195]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",345.18265000000002,"Lag",0.98022534887641399,69.684269571332095]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",372.63904000000002,"Lag",0.98022527289113304,75.227218751760304]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",353.06146000000001,"Lag",0.98008276194322297,71.539152457090296]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",381.65253000000001,"Lag",0.98010253530508795,77.292854122147702]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",361.21141,"Lag",0.97994970294620698,73.442112319672404]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",389.69290000000001,"Lag",0.97997976099591499,79.171776709175205]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",368.93691999999999,"Lag",0.979820460405462,75.261720908057498]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",195.40821,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",192.03881999999999,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",196.62678,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",193.23607999999999,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",257.56741,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",254.15601000000001,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",265.03874000000002,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",260.37070999999997,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",275.12765999999999,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",270.43628000000001,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",285.70487000000003,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",281.01575000000003,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",295.47746999999998,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",290.68315999999999,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",305.05955,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",300.12157999999999,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",315.53203000000002,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",310.31009999999998,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",89.32723,"Lag",0.97974037523385604,18.259659722792499]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",72.041139999999999,"Lag",0.97899480250423498,15.0032692038605]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",89.091880000000003,"Lag",0.97926912936309995,18.428808441834502]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",71.713220000000007,"Lag",0.97839146447287295,15.154979388778401]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",89.390500000000003,"Lag",0.97883812875862897,18.687992756816399]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",71.918760000000006,"Lag",0.97784288140514897,15.396629094748]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",90.081559999999996,"Lag",0.97840043670926502,19.0326317808106]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",72.508349999999993,"Lag",0.97728962629736105,15.722152983627399]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",91.088470000000001,"Lag",0.97795041318045905,19.451562841743701]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",73.413420000000002,"Lag",0.97672550939028502,16.121899208056199]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",92.543229999999994,"Lag",0.97756633531864701,19.939490570494801]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",76.045060000000007,"Lag",0.97636989177827804,16.831530102411602]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",94.480900000000005,"Lag",0.97725172155205897,20.5041998597017]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",79.689499999999995,"Lag",0.97616374305949205,17.717764366092101]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",96.73742,"Lag",0.97702278734732395,21.103005730168299]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",83.379300000000001,"Lag",0.97604346246502904,18.5865745812645]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",98.825000000000003,"Lag",0.97674514184078398,21.6929068177738]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",87.211039999999997,"Lag",0.97589039014484702,19.5050442513256]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",101.80162,"Lag",0.97654755096510004,22.444453114719501]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",91.013369999999995,"Lag",0.97576075943433005,20.412139559955701]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",72.599450000000004,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",70.945639999999997,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",73.592100000000002,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",71.915270000000007,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",75.879710000000003,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",74.194680000000005,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",79.174539999999993,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",77.471770000000006,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",83.220889999999997,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",81.495810000000006,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",87.718170000000001,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",85.978480000000005,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",92.169749999999993,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",90.383920000000003,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",96.695819999999998,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",94.851650000000006,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",101.64245,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",99.693430000000006,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",156.76868999999999,"Lag",0.98164919685075802,30.453971694573799]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",142.04754,"Lag",0.98153709111168497,27.6807700458623]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",157.74643,"Lag",0.98150656634374001,30.766129571176599]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",142.88036,"Lag",0.981378706802703,27.965627583637499]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",158.91829000000001,"Lag",0.98137864885630999,31.104742643965501]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",143.90732,"Lag",0.98123665148204597,28.276944085241499]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",160.28917999999999,"Lag",0.98126364097144003,31.4725719309202]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",145.13308000000001,"Lag",0.98110901097972703,28.617433473120599]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",161.77520999999999,"Lag",0.98114066327666505,31.8714307703742]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",146.47402,"Lag",0.98097260409209497,28.988959948784299]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",163.44513000000001,"Lag",0.98102635724322296,32.300689699910798]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",151.04936000000001,"Lag",0.98088460261803301,29.965548097451101]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",166.34523999999999,"Lag",0.98093429441478897,32.955805898027599]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",156.09641999999999,"Lag",0.98081460135833398,31.025111317689301]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",171.05894000000001,"Lag",0.98085457841483903,33.962520745577699]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",160.74194,"Lag",0.98073221663694798,32.018982271358198]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",176.43561,"Lag",0.98080244399002203,35.0790850374377]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",165.67060000000001,"Lag",0.98067501157163095,33.0511494834629]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",181.37524999999999,"Lag",0.98075513025398897,36.106909565970803]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",170.41821999999999,"Lag",0.98062584595678404,34.0428008746674]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",121.13039999999999,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",118.99151999999999,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",122.33569,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",120.17554,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",123.70627,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",121.52482999999999,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",128.32812000000001,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",125.51069,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",133.89521999999999,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",131.03469000000001,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",139.74109000000001,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",136.84971999999999,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",145.21889999999999,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",142.24638999999999,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",150.64471,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",147.57227,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",156.55659,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",153.31254999999999,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",159.25003000000001,"Lag",0.981589781246749,30.9874504772325]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",143.53662,"Lag",0.98146464727886096,28.027324772455401]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",159.52726000000001,"Lag",0.98142156666594604,31.186906314268501]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",143.72971000000001,"Lag",0.98127681911766895,28.210930136755]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",160.18677,"Lag",0.98126522314537301,31.4510976926924]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",144.30461,"Lag",0.98110241985396196,28.459182502839699]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",161.23393999999999,"Lag",0.98110432750838505,31.796266271464301]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",145.32876999999999,"Lag",0.98092409098463795,28.800016408713301]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",162.60343,"Lag",0.98093674944033904,32.2123552416544]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",149.43592000000001,"Lag",0.98077626389142503,29.7318316112706]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",165.63994,"Lag",0.98080334943047798,32.931880809744598]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",154.44322,"Lag",0.98066121537668305,30.822618804795201]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",171.10050000000001,"Lag",0.98071473775653395,34.098267843869301]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",159.98036999999999,"Lag",0.98057199934509798,32.003434026546202]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",176.48356999999999,"Lag",0.98064960940734403,35.232147448449801]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",165.36062000000001,"Lag",0.98050687709378503,33.136782393509399]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",182.47307000000001,"Lag",0.98057916595864203,36.496074868226003]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",170.9502,"Lag",0.98043113124686698,34.3253720303439]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",188.04993999999999,"Lag",0.98051217212949804,37.678246690294202]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",176.39254,"Lag",0.98036236129524801,35.482200803954498]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",121.73044,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",119.73730999999999,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",122.53363,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",120.52959,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",123.94891,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",121.76864999999999,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",128.84123,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",126.19427,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",134.70374000000001,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",132.02780000000001,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",141.05189999999999,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",138.35954000000001,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",147.17671000000001,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",144.41663,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",153.33342999999999,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",150.48622,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",160.06862000000001,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",157.06143,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",26.925450000000001,"Lag",0.98271480931916499,5.0722737240160596]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",26.5,"Lag",0.98271480931916499,4.9921265451989001]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",26.925450000000001,"Lag",0.98271480931916499,5.0722737240160596]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",26.5,"Lag",0.98271480931916499,4.9921265451989001]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",26.925450000000001,"Lag",0.98271480931916499,5.0722737240160596]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",26.5,"Lag",0.98271480931916499,4.9921265451989001]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",26.925450000000001,"Lag",0.98271480931916499,5.0722737240160596]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",26.5,"Lag",0.98271480931916499,4.9921265451989001]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",26.925450000000001,"Lag",0.98271480931916499,5.0722737240160596]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",26.5,"Lag",0.98271480931916499,4.9921265451989001]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",26.925450000000001,"Lag",0.98271480931916499,5.0722737240160596]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",26.5,"Lag",0.98271480931916499,4.9921265451989001]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",26.925450000000001,"Lag",0.98271480931916499,5.0722737240160596]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",26.5,"Lag",0.98271480931916499,4.9921265451989001]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",26.925450000000001,"Lag",0.98271480931916499,5.0722737240160596]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",26.5,"Lag",0.98271480931916499,4.9921265451989001]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",26.925450000000001,"Lag",0.98271480931916499,5.0722737240160596]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",26.5,"Lag",0.98271480931916499,4.9921265451989001]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",26.925450000000001,"Lag",0.98271480931916499,5.0722737240160596]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",26.5,"Lag",0.98271480931916499,4.9921265451989001]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",30.204409999999999,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",29.350370000000002,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",30.204409999999999,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",29.350370000000002,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",30.204409999999999,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",29.350370000000002,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",30.204409999999999,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",29.350370000000002,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",30.204409999999999,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",29.350370000000002,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",30.204409999999999,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",29.350370000000002,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",30.204409999999999,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",29.350370000000002,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",30.204409999999999,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",29.350370000000002,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",30.204409999999999,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",29.350370000000002,"Lag","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",31.177309999999999,"Lead",0.95865351158833301,-9.2549717362819894]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",23.925609999999999,"Lead",0.95635430638404895,-7.3103581855014799]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",30.272320000000001,"Lead",0.95610120912011598,-9.2782010305660698]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",23.010899999999999,"Lead",0.95281408186940497,-7.3309809676968598]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",29.482780000000002,"Lead",0.95352598298926905,-9.3164531047947694]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",22.211760000000002,"Lead",0.94915989406494705,-7.3666587089984699]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",29.45147,"Lead",0.95293089467832504,-9.3703751550222307]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",22.170750000000002,"Lead",0.94832686735512695,-7.4179796103308204]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",29.360150000000001,"Lead",0.95199750764651803,-9.4404779372972492]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",22.06983,"Lead",0.94701094294839505,-7.4855080596787298]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",29.427129999999998,"Lead",0.95139302129776304,-9.5259793062017]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",22.127230000000001,"Lead",0.94618233601953305,-7.5684404588496799]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",29.253209999999999,"Lead",0.94990970202791503,-9.6244354280325393]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",21.943709999999999,"Lead",0.94407247240405701,-7.6643222477534101]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",29.175830000000001,"Lead",0.94865230244328003,-9.7284537690537594]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",21.856639999999999,"Lead",0.942289617287277,-7.7657421214763298]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",29.315860000000001,"Lead",0.94807429085563699,-9.8345443865491902]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",22.010429999999999,"Lead",0.96587498151741102,-5.9023098634121496]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",29.389679999999998,"Lead",0.94728402711285298,-9.9403209446349106]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",22.364989999999999,"Lead",0.96587498151741102,-5.9973885595199201]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",44.7744,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",43.27863,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",44.885150000000003,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",43.3874,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",45.075589999999998,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",43.575850000000003,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",45.326599999999999,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",43.824890000000003,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",45.652929999999998,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",44.149239999999999,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",46.05301,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",44.547359999999998,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",46.500889999999998,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",44.993250000000003,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",46.94361,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",45.434019999999997,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",47.404040000000002,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",45.892560000000003,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",45.544750000000001,"Lead",0.950945081673505,-14.816536205896]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",40.815559999999998,"Lead",0.95039953944401401,-13.357469454512399]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",45.313679999999998,"Lead",0.95001760125248103,-14.8910559320665]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",40.564920000000001,"Lead",0.94935298597167095,-13.425951373717099]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",45.10951,"Lead",0.94901599949833404,-14.983705631639999]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",40.384590000000003,"Lead",0.94822850325088603,-13.525956276053201]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",44.871079999999999,"Lead",0.947823079659735,-15.0922231431767]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",41.03,"Lead",0.94707510986192101,-13.9071592913534]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",45.027439999999999,"Lead",0.946679178096964,-15.3239258037321]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",41.601010000000002,"Lead",0.94592091493957298,-14.266791265059901]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",45.99738,"Lead",0.94588157389717697,-15.780730802311099]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",42.417909999999999,"Lead",0.94503250079157297,-14.6763798110049]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",46.88823,"Lead",0.94509465865603903,-16.2131051225691]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",43.303260000000002,"Lead",0.94419157691725797,-15.107057251431]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",47.776899999999998,"Lead",0.944466780043692,-16.622945154828201]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",44.165289999999999,"Lead",0.943519294600212,-15.5086782148311]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",48.807400000000001,"Lead",0.94389641923561096,-17.076276754624701]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",45.061540000000001,"Lead",0.94288181230100598,-15.920590520547]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",49.65437,"Lead",0.94320985823583403,-17.488214592137101]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",45.843609999999998,"Lead",0.94213321904681802,-16.312505176041999]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",36.816670000000002,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",36.100499999999997,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",36.974409999999999,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",36.255200000000002,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",37.337980000000002,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",36.467919999999999,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",38.595669999999998,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",37.68009,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",40.073430000000002,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",39.147109999999998,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",41.628680000000003,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",40.695279999999997,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",43.072290000000002,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",42.117190000000001,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",44.49409,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",43.511980000000001,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",46.053609999999999,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",45.023420000000002,"Lead","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",219.97658000000001,"Lag",0.95390647810978202,69.205797931031995]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",197.11190999999999,"Lag",0.95355242076944902,62.267634859106899]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",219.56842,"Lag",0.95333960224890202,69.532098758445699]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",197.70514,"Lag",0.95293744788862,62.897802180924202]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",219.04352,"Lag",0.95261178901812504,69.945143949253605]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",198.44265999999999,"Lag",0.95215598776126997,63.693922037811198]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",222.57548,"Lag",0.95190262276744497,71.643132479768497]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",202.38005999999999,"Lag",0.95139075719338895,65.514939190033004]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",226.18809999999999,"Lag",0.95124512352956003,73.340227809192399]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",206.15412000000001,"Lag",0.950679735628852,67.261022632835804]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",231.87151,"Lag",0.95073604818650903,75.605137473010004]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",211.02461,"Lag",0.95010836290297496,69.279256026038993]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",237.25360000000001,"Lag",0.95025359900446704,77.767773459314299]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",216.3398,"Lag",0.94959016344427505,71.421591561494395]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",242.54513,"Lag",0.94988195325750802,79.822284056611295]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",221.46532999999999,"Lag",0.94919129948787295,73.425730337551897]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",248.47761,"Lag",0.94951505673902603,82.097444424489595]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",226.68637000000001,"Lag",0.94878008183708495,75.485008003607206]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",253.82678000000001,"Lag",0.94916492303911504,84.178618982316294]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",231.69397000000001,"Lag",0.94839898828963298,77.462534953116105]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",139.39886999999999,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",137.00318999999999,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",139.99798999999999,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",137.59245999999999,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",140.92758000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",138.51211000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",145.80685,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",142.68154000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",151.69156000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",148.53618,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",157.98946000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",154.81798000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",163.93116000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",160.68672000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",169.81807000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",166.4802,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",176.25570999999999,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",172.74494000000001,"Lag","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",462.43038999999999,"Lag",0.99834498701839902,26.638002833136099]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",381.76326999999998,"Lag",0.99829131215890698,22.345887860972699]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",459.71391,"Lag",0.99831018416633299,26.759209623549999]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",378.73169000000001,"Lag",0.99824769606598396,22.4503288931976]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",458.40800000000002,"Lag",0.99828006710625905,26.920536955114699]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",377.11009000000001,"Lag",0.99820986581687898,22.5948590740079]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",457.82954999999998,"Lag",0.99824928660695,27.126712967477399]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",376.20265999999998,"Lag",0.99817116012676699,22.783530804780501]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",458.09525000000002,"Lag",0.99821912627914799,27.3758756940796]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",376.13878,"Lag",0.99813325809164899,23.0151573251499]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",458.16158000000001,"Lag",0.99818185849545404,27.6656158111197]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",375.87531999999999,"Lag",0.99808629731315401,23.287350062332301]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",458.78768000000002,"Lag",0.99814423865269897,27.9893570778152]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",376.17192,"Lag",0.99803887550610304,23.593559379414]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",460.69889000000001,"Lag",0.99811497117262105,28.327342337775299]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",377.75447000000003,"Lag",0.99800218928477802,23.9140573842602]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",463.18639000000002,"Lag",0.99809035990092698,28.666142398832999]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",380.48484000000002,"Lag",0.99797249731886495,24.265780008603599]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",464.68193000000002,"Lag",0.99805802702318802,29.001845331759501]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",388.13959999999997,"Lag",0.99794377941951595,24.929201104504799]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",360.63749000000001,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",353.97892000000002,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",362.11916000000002,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",355.43374,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",364.51504,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",357.80214999999998,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",367.51438000000002,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",360.77339000000001,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",371.31148999999999,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",364.54239000000001,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",380.27584000000002,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",372.16800000000001,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",394.54498999999998,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",386.24775,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",408.62993,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",400.09554000000003,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",423.98126000000002,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",415.01841999999999,"Lead","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",0.52603999999999995,"Lag",0.91195318247211699,0.23666916803867299]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",0.47276000000000001,"Lag",0.91195318247211699,0.212698113987459]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",0.52603999999999995,"Lag",0.91195318247211699,0.23666916803867299]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",0.47543000000000002,"Lag",0.91195318247211699,0.213899366133044]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",0.52607999999999999,"Lag",0.91195318247211699,0.236687164325498]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",0.47876000000000002,"Lag",0.91195318247211699,0.21539755701124499]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",0.53737999999999997,"Lag",0.91195318247211699,0.241771115353627]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",0.48954999999999999,"Lag",0.91195318247211699,0.22025205538235201]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",0.54615999999999998,"Lag",0.91195318247211699,0.245721300311767]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",0.49901000000000001,"Lag",0.91195318247211699,0.22450817721652]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",0.55871000000000004,"Lag",0.91195318247211699,0.25136763530318401]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",0.50987000000000005,"Lag",0.91195318247211699,0.229394169089572]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",0.56976000000000004,"Lag",0.91195318247211699,0.25633910953865602]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",0.52100000000000002,"Lag",0.91195318247211699,0.23440163589869301]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",0.57952999999999999,"Lag",0.91195318247211699,0.26073470259571901]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",0.53058000000000005,"Lag",0.91195318247211699,0.23871174659333699]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",0.59087000000000001,"Lag",0.91195318247211699,0.26583664991067402]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",0.54042999999999997,"Lag",0.91195318247211699,0.24314333222405199]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",0.60065000000000002,"Lag",0.91195318247211699,0.27023674203944398]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",0.54959000000000002,"Lag",0.91195318247211699,0.24726448190702999]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",0.56379999999999997,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",0.54654000000000003,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",0.56379999999999997,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",0.54654000000000003,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",0.56381000000000003,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",0.54654999999999998,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",0.56381999999999999,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",0.54656000000000005,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",0.56384000000000001,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",0.54657999999999995,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",0.56386000000000003,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",0.54659999999999997,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",0.56388000000000005,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",0.54662999999999995,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",0.56391000000000002,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",0.54664999999999997,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",0.56393000000000004,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",0.54666999999999999,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",43.67868,"Lag",0.931806010171778,17.013701327240199]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",40.329590000000003,"Lag",0.931295882292553,15.774366059474]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",43.562440000000002,"Lag",0.93117645868281196,17.055313094841399]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",40.206049999999998,"Lag",0.93060929651963697,15.8132764522377]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",43.509120000000003,"Lag",0.93066824262439296,17.1043011968606]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",40.145420000000001,"Lag",0.93005483629741403,15.859559478905799]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",43.452240000000003,"Lag",0.930084279367977,17.161902157059199]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",40.08099,"Lag",0.92941745999495196,15.9143665514299]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",43.4358,"Lag",0.92955343148649805,17.227878195229898]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",40.056870000000004,"Lag",0.92883804208448795,15.977500595251]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",43.446809999999999,"Lag",0.92905175419830299,17.300583771234098]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",40.060319999999997,"Lag",0.92829055196150001,16.047408583067298]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",43.424720000000001,"Lag",0.92840579379575106,17.379502395757001]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",40.030659999999997,"Lag",0.92758501489524803,16.123525918888699]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",43.400120000000001,"Lag",0.92772608183463501,17.461623721052302]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",39.998379999999997,"Lag",0.92684213493477097,16.202805249834402]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",43.43477,"Lag",0.92721445967186,17.5446580585647]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",40.665489999999998,"Lag",0.92647033514987798,16.5198822626561]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",43.496540000000003,"Lag",0.92680049235316997,17.625478256486101]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",41.409129999999998,"Lag",0.92622795373732303,16.853029372972099]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",23.054120000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",22.4421,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",23.119620000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",22.506260000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",23.21069,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",22.595980000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",23.320879999999999,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",22.70477,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",23.453859999999999,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",22.836359999999999,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",23.608409999999999,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",22.989519999999999,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",23.778320000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",23.15804,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",23.945170000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",23.32349,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",24.116820000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",23.493739999999999,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",148.35230999999999,"Lag",0.98959990976914403,21.5643362944286]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",139.76879,"Lag",0.98957660398070602,20.339755980052001]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",148.41817,"Lag",0.98956199044955995,21.613825933722101]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",139.81732,"Lag",0.989536267974507,20.386773209792299]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",148.61482000000001,"Lag",0.98952944664557196,21.676711625234802]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",139.99655999999999,"Lag",0.98950165958844705,20.447175078435901]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",148.91290000000001,"Lag",0.98949519104555905,21.756255960681099]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",140.27654999999999,"Lag",0.98946524461560703,20.524138577828101]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",149.32758000000001,"Lag",0.98946151044211195,21.852346457965599]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",140.67310000000001,"Lag",0.98942946357669004,20.617642532400499]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",149.86117999999999,"Lag",0.98942986274530598,21.963864895567401]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",141.18857,"Lag",0.98939587210503399,20.726574427290402]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",150.48761999999999,"Lag",0.98940042757855995,22.086858902963598]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",141.79683,"Lag",0.98936465886758396,20.846974758652099]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",151.09960000000001,"Lag",0.98936706067348701,22.212119266776298]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",144.54275999999999,"Lag",0.98933903666660905,21.2766781903278]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",151.74123,"Lag",0.98933564997151902,22.339897162607201]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",147.86416,"Lag",0.98931860830264196,21.7867693549642]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",154.54238000000001,"Lag",0.98931777470011795,22.771662189572801]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",151.02868000000001,"Lag",0.98930222611478402,22.270375089336]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",97.90719,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",92.037120000000002,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",98.042950000000005,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",92.313779999999994,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",98.273619999999994,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",92.732579999999999,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",98.549379999999999,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",93.252880000000005,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",98.90813,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",93.898840000000007,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",99.327349999999996,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",94.664659999999998,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",99.792230000000004,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",96.471869999999996,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",102.69131,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",99.514129999999994,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",106.10771,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",102.80077,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",65.753309999999999,"Lag",0.99416735920522803,7.1329887166818899]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",63,"Lag",0.99416022561934703,6.8385216268868199]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",65.781480000000002,"Lag",0.99412402969392599,7.1627360650391596]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",63.012740000000001,"Lag",0.994114923104506,6.8666187334639996]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",65.826070000000001,"Lag",0.99407824885957696,7.1957079817722702]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",63.041960000000003,"Lag",0.99406703399808305,6.8979468254297798]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",65.857569999999996,"Lag",0.99402553087313295,7.2314132552666104]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",63.058149999999998,"Lag",0.99401186070688496,6.9320146911695302]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",65.884240000000005,"Lag",0.99396754424103295,7.2696826414342297]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",63.069569999999999,"Lag",0.993951140314424,6.9686530865953298]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",65.978650000000002,"Lag",0.99391782955114605,7.3103112057506001]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",63.148739999999997,"Lag",0.99389905613262597,7.0076517296720002]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",66.098330000000004,"Lag",0.99386828857982101,7.3536124840629]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",63.253120000000003,"Lag",0.99384713399475499,7.0493166697318497]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",66.280010000000004,"Lag",0.99382777902074304,7.3983689933409096]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",63.419530000000002,"Lag",0.99380466545239898,7.0924400492637796]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",66.495570000000001,"Lag",0.99379177364789295,7.4442506418740804]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",63.619160000000001,"Lag",0.99376690544500002,7.1366179809105699]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",66.67295,"Lag",0.99375031314384599,7.4892254719196396]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",63.781419999999997,"Lag",0.99372341061678704,7.1799757237419399]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",59.867049999999999,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",59.150419999999997,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",60.024149999999999,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",59.303319999999999,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",60.208190000000002,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",59.48319,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",60.390389999999996,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",59.661230000000003,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",60.601399999999998,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",59.868099999999998,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",60.849730000000001,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",60.112259999999999,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",61.1173,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",60.375680000000003,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",61.422930000000001,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",60.677059999999997,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",61.725050000000003,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",60.97484,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",454.15559000000002,"Lag",0.98776276848629696,71.709364853198096]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",409.23381999999998,"Lag",0.98788110766993498,64.297413703091195]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",451.17415999999997,"Lag",0.98744647251256801,72.170757726815097]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",407.02224000000001,"Lag",0.987600710769035,64.699319561486504]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",448.39298000000002,"Lag",0.98709889670432605,72.731292523959596]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",404.98714000000001,"Lag",0.98729357404309204,65.183494837671802]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",445.15640999999999,"Lag",0.98668865688538698,73.368280514490607]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",402.60975999999999,"Lag",0.986932488619501,65.733211680830806]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",442.13193999999999,"Lag",0.98625121107227698,74.082162336457799]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",400.43892,"Lag",0.98654909337544905,66.350318144737301]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",440.48162000000002,"Lag",0.98586253159663895,74.863796030040504]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",399.41568000000001,"Lag",0.98620969071389497,67.027866491300998]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",439.91762,"Lag",0.986159039619667,73.963000381765994]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",403.92923000000002,"Lag",0.98590328749096001,68.550233057120295]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",440.52546999999998,"Lag",0.98589826771397904,74.774522945836907]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",413.06234999999998,"Lag",0.98568842786228705,70.643983108716597]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",448.32934999999998,"Lag",0.985713091615673,76.607982613061395]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",422.99034999999998,"Lag",0.98551174096634098,72.796917121129198]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",457.67664000000002,"Lag",0.98551094839025999,78.768652462680905]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",431.93547999999998,"Lag",0.98529716115469301,74.897100838768907]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",331.64078999999998,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",317.25319000000002,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",333.01152999999999,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",318.54471999999998,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",335.14330000000001,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",320.59809999999999,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",337.49103000000002,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",324.82963000000001,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",345.77497,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",338.11711000000003,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",359.88882999999998,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",352.17180999999999,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",373.12182999999999,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",365.21767999999997,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",386.25549999999998,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",378.11574000000002,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",400.67689999999999,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",392.11700000000002,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",77.876919999999998,"Lag",0.98835841842327499,11.9880247341732]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",69.853309999999993,"Lag",0.988298042473998,10.7812484923436]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",77.934129999999996,"Lag",0.98824643911703103,12.055417928267399]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",70.26585,"Lag",0.98817653942838601,10.902084438766099]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",78.030810000000002,"Lag",0.98810711578041599,12.142988217729499]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",70.815160000000006,"Lag",0.98802721713962904,11.057731707336]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",79.072370000000006,"Lag",0.98795313585619804,12.3859262355582]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",72.528090000000006,"Lag",0.98786798609732795,11.401645889943101]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",80.725520000000003,"Lag",0.98782721557124797,12.7120076539801]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",74.25976,"Lag",0.98773362201302795,11.739536963932499]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",83.145820000000001,"Lag",0.98773137378696096,13.1455386340524]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",76.414079999999998,"Lag",0.98762783364356099,12.1330637133902]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",85.482810000000001,"Lag",0.987637688819616,13.5674922632474]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",78.754059999999996,"Lag",0.98752886463211298,12.5554670480124]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",87.757549999999995,"Lag",0.98755753666992696,13.974462803160201]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",80.992990000000006,"Lag",0.98744410612687294,12.957051651019]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",90.464780000000005,"Lag",0.98749333610391998,14.443383334528299]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",83.460830000000001,"Lag",0.98737366880392796,13.3899671716088]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",93.036050000000003,"Lag",0.98744795138409902,14.8813468276058]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",85.928070000000005,"Lag",0.98732602208320897,13.8122842246876]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",61.006909999999998,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",60.005589999999998,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",61.317790000000002,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",60.311680000000003,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",61.794130000000003,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",60.783140000000003,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",62.379510000000003,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",61.363549999999996,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",64.670320000000004,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",63.376249999999999,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",67.473330000000004,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",66.17295,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",70.142840000000007,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",68.811629999999994,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",72.851020000000005,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",71.479050000000001,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",75.860309999999998,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",74.412310000000005,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",200.33449999999999,"Lag",0.98743605833008397,32.059467335242097]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",180.20854,"Lag",0.98727776809663204,29.023310730964202]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",199.40968000000001,"Lag",0.98722866336771198,32.178854336285603]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",179.22309000000001,"Lag",0.98704418918827297,29.133551227944402]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",198.69076999999999,"Lag",0.98701144163541099,32.339713247092902]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",178.44345000000001,"Lag",0.98679920131467502,29.2852485489156]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",198.21215000000001,"Lag",0.98678480394826296,32.5476801451873]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",179.52656999999999,"Lag",0.98656473574844505,29.728815995513798]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",197.77697000000001,"Lag",0.98652498821900703,32.800406184601599]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",182.47790000000001,"Lag",0.98632420515346897,30.492423240194999]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",201.13754,"Lag",0.98634630761480502,33.582749641366298]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",186.50588999999999,"Lag",0.98614315795847196,31.375452161942601]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",205.4393,"Lag",0.98618013168205998,34.5134637491566]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",190.84479999999999,"Lag",0.98596816860496805,32.311770634337101]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",209.51702,"Lag",0.98602976775347395,35.393537539319297]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",194.85778999999999,"Lag",0.98580878462019905,33.182079403750699]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",214.43906999999999,"Lag",0.98591572384911197,36.375736490346199]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",199.25310999999999,"Lag",0.98568221578066495,34.084817063580999]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",218.63511,"Lag",0.98577855440205697,37.271581388667698]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",203.22824,"Lag",0.98553473414727399,34.947335981156598]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",128.01786999999999,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",126.51576,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",128.43485000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",126.92815,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",130.75914,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",128.58667,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",135.24537000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",133.07632000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",140.61681999999999,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",138.44702000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",146.36832999999999,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",144.21108000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",151.76697999999999,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",149.56657000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",157.12287000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",154.85918000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",162.99950000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",160.60048,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",117.05677,"Lag",0.98780207391309804,18.452540662604999]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",107.4106,"Lag",0.98770939705419403,16.9973413701744]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",116.71044000000001,"Lag",0.98761840992100003,18.538527929599301]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",107.02479,"Lag",0.98750761236111495,17.0773727740577]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",116.47598000000001,"Lag",0.98742207715241004,18.650181310433702]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",106.7509,"Lag",0.98729167935756201,17.1830778346675]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",116.21751999999999,"Lag",0.98718827988376101,18.7842925241067]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",106.85095,"Lag",0.98704104138271398,17.371273052492299]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",116.08111,"Lag",0.98694782736916398,18.9409602831436]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",108.73367,"Lag",0.98681701333134397,17.8325421763534]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",117.5206,"Lag",0.98676886655070495,19.309488035288599]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",111.23390000000001,"Lag",0.98664860690576806,18.361090755153199]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",120.16637,"Lag",0.98661840409041601,19.858430100456001]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",113.95392,"Lag",0.98649353475095203,18.9212340066425]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",122.78498999999999,"Lag",0.98650123558851899,20.381637556636999]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",116.58461,"Lag",0.98637265807656804,19.446262315603398]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",125.7443,"Lag",0.98639233251355096,20.9586342650957]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",119.2825,"Lag",0.98625492810269699,19.9838217967452]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",128.31286,"Lag",0.98626714984383701,21.486950720905298]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",121.76715,"Lag",0.98612344292131804,20.499479780578099]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",84.376379999999997,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",82.823700000000002,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",84.668660000000003,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",83.109449999999995,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",85.126620000000003,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",83.560900000000004,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",85.693730000000002,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",84.121539999999996,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",88.954560000000001,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",86.989189999999994,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",92.466160000000002,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",90.488079999999997,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",95.742230000000006,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",93.718599999999995,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",98.974959999999996,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",96.893950000000004,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",102.5184,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",100.3335,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",60.114840000000001,"Lag",0.99837061807707905,3.43589092966086]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",54.733199999999997,"Lag",0.998350923466236,3.1471967909864]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",59.843449999999997,"Lag",0.99834158861245303,3.45078942643375]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",54.747839999999997,"Lag",0.99832005504335397,3.1774391577478198]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",59.595489999999998,"Lag",0.99830941945392004,3.46974475060015]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",54.857529999999997,"Lag",0.99828644188243898,3.2155803543800299]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",59.889310000000002,"Lag",0.99827363049162599,3.5236605746087899]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",55.778739999999999,"Lag",0.99825116309865902,3.3031520557165801]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",60.616129999999998,"Lag",0.99823859718297003,3.6025238331632798]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",56.573770000000003,"Lag",0.99821406563367499,3.38567438979433]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",61.914499999999997,"Lag",0.99821240414208701,3.70701977636155]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",57.683390000000003,"Lag",0.99818509203310601,3.48004497739936]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",63.124940000000002,"Lag",0.99818743493286299,3.8058686387255198]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",58.904910000000001,"Lag",0.99815876958177296,3.5794882182532599]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",64.318870000000004,"Lag",0.99816718978866403,3.8995076365236101]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",60.079219999999999,"Lag",0.99813735655842495,3.6720747155123301]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",65.700289999999995,"Lag",0.99814817329243499,4.0039282563632304]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",61.295549999999999,"Lag",0.99811625451045805,3.7676392031406198]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",66.875349999999997,"Lag",0.998126928102407,4.0989163547943903]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",62.399470000000001,"Lag",0.99809334651283599,3.8588110483431599]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",42.441319999999997,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",41.910679999999999,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",42.605519999999999,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",42.072989999999997,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",42.849919999999997,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",42.315440000000002,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",43.525080000000003,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",42.793140000000001,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",45.205730000000003,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",44.472320000000003,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",46.980319999999999,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",46.24971,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",48.630589999999998,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",47.885019999999997,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",50.263109999999998,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",49.496119999999998,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",52.056600000000003,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",51.24503,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",37.306109999999997,"Lag",0.99836170424384696,2.1380864198391598]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",32.714280000000002,"Lag",0.99833221404780204,1.89176106050826]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",37.14987,"Lag",0.99833103323594496,2.1490191595334802]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",32.538159999999998,"Lag",0.99829657088591495,1.90162735215387]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",37.04139,"Lag",0.998299484568831,2.1629526158949801]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",32.428849999999997,"Lag",0.99826002119382595,1.9155162837729001]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",36.865479999999998,"Lag",0.99825625349248903,2.1799429054839901]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",32.958889999999997,"Lag",0.99821778056282395,1.9703767443873299]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",37.024259999999998,"Lag",0.99821597731580602,2.21453867839565]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",33.459820000000001,"Lag",0.99817666757014101,2.02332690361012]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",37.926079999999999,"Lag",0.99819243315344897,2.2834395663302902]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",34.219059999999999,"Lag",0.99814960722269896,2.0845791918071002]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",38.775010000000002,"Lag",0.99816901214518305,2.3496689445652099]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",35.047080000000001,"Lag",0.99812417033819201,2.1496868683972301]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",39.62659,"Lag",0.99815127534260994,2.4129072845752702]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",35.862870000000001,"Lag",0.99810493727026295,2.2110052800540001]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",40.529789999999998,"Lag",0.99812933852566299,2.4825438691850601]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",36.638570000000001,"Lag",0.99807980185024403,2.2738022204882302]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",41.340049999999998,"Lag",0.998108265801947,2.5464368535636601]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",37.382280000000002,"Lag",0.99805634534061605,2.3341251788285202]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",27.335380000000001,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",26.58578,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",27.4559,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",26.70299,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",27.999379999999999,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",27.097899999999999,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",28.981310000000001,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",28.066230000000001,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",30.151499999999999,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",29.220050000000001,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",31.40278,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",30.457619999999999,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",32.580179999999999,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",31.611249999999998,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",33.748330000000003,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",32.751939999999998,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",35.027929999999998,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",33.987560000000002,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",204.74596,"Lag",0.98758016731824305,32.5734066549226]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",183.77619999999999,"Lag",0.98743579966422401,29.409956299554601]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",204.01584,"Lag",0.98738979417660999,32.709798520903398]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",184.00054,"Lag",0.98723029762061099,29.690335832832702]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",203.47246999999999,"Lag",0.98718439318165796,32.892436699397997]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",184.65758,"Lag",0.98701275473705097,30.054065136885601]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",205.82884999999999,"Lag",0.986996233078271,33.521532316322599]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",188.43686,"Lag",0.98682220714858804,30.897816215324902]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",208.94943000000001,"Lag",0.98679287428491003,34.300119946113]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",191.74614,"Lag",0.986604060094044,31.704870698434501]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",213.81862000000001,"Lag",0.98661751150253496,35.336397511611501]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",195.9025,"Lag",0.98640764143075899,32.633612349510599]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",218.57076000000001,"Lag",0.98646667689160294,36.3289219548655]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",200.63676000000001,"Lag",0.98624687733164096,33.623439456583597]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",223.14775,"Lag",0.98633403030748101,37.274760617063997]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",205.09690000000001,"Lag",0.98610484437888002,34.551650393237203]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",228.49135000000001,"Lag",0.98622026413193897,38.329220974811498]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",209.82121000000001,"Lag",0.98597742076725703,35.512686068462102]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",233.12734,"Lag",0.98608991224639797,39.295342647104299]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",214.16928999999999,"Lag",0.98583561288820698,36.435374292216899]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",158.46858,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",152.92228,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",158.47253000000001,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",152.90819999999999,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",158.92096000000001,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",153.33807999999999,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",159.60621,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",154.00424000000001,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",160.50237999999999,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",154.88131999999999,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",161.85576,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",157.25807,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",165.71702999999999,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",163.05485999999999,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",171.52723,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",168.78874999999999,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",177.90563,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",175.01147,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",8.4450099999999999,"Lag",0.98796980366047404,1.3218973943279899]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",7.3227000000000002,"Lag",0.98783823737491805,1.1525882573453501]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",8.4074399999999994,"Lag",0.98778198934194394,1.3264390499327301]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",7.2814899999999998,"Lag",0.98761895957407797,1.15658079081929]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",8.3873800000000003,"Lag",0.98764578123472602,1.33076768405781]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",7.2582000000000004,"Lag",0.98745951116449004,1.16042215448215]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",8.3667099999999994,"Lag",0.98749319723856099,1.3358158106486799]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",7.2338699999999996,"Lag",0.98728046190929197,1.16491814178766]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",8.33521,"Lag",0.98730299820137202,1.34106159239833]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",7.1986800000000004,"Lag",0.98705660363356396,1.1696072585201001]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",8.2909100000000002,"Lag",0.98706842428096497,1.3464402200147101]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",7.1506699999999999,"Lag",0.98677947971207103,1.1744262039647]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",8.2565500000000007,"Lag",0.98685767200423702,1.3519593174515601]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",7.1304999999999996,"Lag",0.98653559012376002,1.1820859725652999]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",8.2333800000000004,"Lag",0.98668583157654899,1.3571282431190701]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",7.2584999999999997,"Lag",0.98638709020418602,1.2100600610110701]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",8.2185799999999993,"Lag",0.98651906880534002,1.3633194096092001]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",7.3969699999999996,"Lag",0.98625204949054601,1.23937319150876]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",8.1851299999999991,"Lag",0.98630325863354595,1.3688205562142]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",7.5136099999999999,"Lag",0.98606749277628902,1.2675165745455199]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",8.5770700000000009,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",8.0054499999999997,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",8.6604100000000006,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",8.0145400000000002,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",8.8464299999999998,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",8.1848899999999993,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",9.1171600000000002,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",8.4402200000000001,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",9.4260699999999993,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",8.7313200000000002,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",9.7394099999999995,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",9.0275700000000008,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",10.015790000000001,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",9.2855600000000003,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",10.28375,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",9.53444,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",10.57987,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",9.8054799999999993,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",328.73559,"Lag",0.98989370682955502,47.094376011711503]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",285.89116999999999,"Lag",0.99182230013044703,36.788133358520099]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",326.28802999999999,"Lag",0.98968358759907304,47.234696566763098]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",285.97777000000002,"Lag",0.99178740959123501,36.878670638599203]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",323.79662000000002,"Lag",0.98944623196806503,47.418737536160101]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",286.22994999999997,"Lag",0.99174891121434505,36.998683126355601]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",322.28314,"Lag",0.98924883211373704,47.643583328506999]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",286.91059999999999,"Lag",0.99171767585631698,37.1576757186074]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",323.29052000000001,"Lag",0.991760782910593,41.758760589149503]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",288.04939000000002,"Lag",0.99169497609351398,37.3568891884672]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",324.85816999999997,"Lag",0.99174317365233899,42.006627710255003]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",293.07778000000002,"Lag",0.99168288315533804,38.037027704706702]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",326.66915999999998,"Lag",0.99172755524074896,42.281234517620199]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",301.25630000000001,"Lag",0.99167930728049503,39.106984950607398]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",333.03811000000002,"Lag",0.99169703778250795,43.186010580746597]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",308.12392999999997,"Lag",0.99164823511639799,40.0740497436948]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",341.03426999999999,"Lag",0.99167271502293997,44.288437556013101]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",315.29467,"Lag",0.99162137944264594,41.073375805581101]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",347.81614999999999,"Lag",0.99163321583073005,45.277521074877903]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",321.73667999999998,"Lag",0.99157891333484305,42.020007109294198]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",229.31666000000001,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",219.96958000000001,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",229.7482,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",220.38105999999999,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",230.29293999999999,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",220.90530999999999,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",230.98785000000001,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",221.57930999999999,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",231.81628000000001,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",222.38685000000001,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",232.80544,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",223.35511,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",234.72274999999999,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",227.85300000000001,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",242.42193,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",235.37298000000001,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",250.85865999999999,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",243.51342,"Lag","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",292.76558999999997,"Lag",0.99621941140609904,25.5298861573539]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",264.94488000000001,"Lag",0.99619342794781396,23.183563806735599]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",294.24400000000003,"Lag",0.99617717539397899,25.802557708458099]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",266.14427000000001,"Lag",0.99614641876328502,23.4327035765779]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",296.40156999999999,"Lag",0.99614233059306101,26.110630548653301]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",268.02141999999998,"Lag",0.99610763359232801,23.717126563352402]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",299.57369999999997,"Lag",0.99611540683899802,26.4825389680379]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",270.88618000000002,"Lag",0.99607771724083805,24.063112240258199]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",303.06387000000001,"Lag",0.99608428133376004,26.898821684211299]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",277.84282000000002,"Lag",0.99604901706473603,24.771747525390001]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",307.76587999999998,"Lag",0.99606005825795196,27.401014826130801]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",287.89202,"Lag",0.99603149293190596,25.724908000997299]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",318.31321000000003,"Lag",0.99604012665292196,28.412085247218101]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",298.47284000000002,"Lag",0.99601122289510102,26.738802876799198]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",328.31135999999998,"Lag",0.99601802491457503,29.3866588213534]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",308.33551999999997,"Lag",0.99598834003066705,27.701951282819198]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",339.93718000000001,"Lag",0.99601051136174201,30.456133949098401]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",319.11829,"Lag",0.99598009880758098,28.700325886613101]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",350.67804000000001,"Lag",0.99600217538227698,31.4514489315311]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",329.50796000000003,"Lag",0.99597165728716197,29.666022467994502]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",208.52690000000001,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",202.49399,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",210.53549000000001,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",204.44085999999999,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",215.68988999999999,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",208.41385,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",224.59960000000001,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",217.15948,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",235.08423999999999,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",227.45590000000001,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",246.37139999999999,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",238.57365999999999,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",257.02692999999999,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",248.98129,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",267.63837000000001,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",259.31509,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",279.19893000000002,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",270.46429999999998,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",89.397980000000004,"Lag",0.99611530355442901,7.9029539198340197]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",79.164249999999996,"Lag",0.99631487284996201,6.8151159305084601]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",90.025210000000001,"Lag",0.996086340051617,7.9881895930654698]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",79.789950000000005,"Lag",0.99630286929877698,6.88022164824761]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",91.009810000000002,"Lag",0.99607151762205304,8.0909243296448192]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",80.583299999999994,"Lag",0.99629650362384603,6.9546443743419797]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",92.064369999999997,"Lag",0.996060068621899,8.1966650420268206]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",82.815690000000004,"Lag",0.996294421988137,7.1493276797111402]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",93.214089999999999,"Lag",0.99604476564031696,8.3152240593350495]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",85.396119999999996,"Lag",0.99629132164926304,7.3751920773897899]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",94.811700000000002,"Lag",0.99603096705878902,8.4725683622750001]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",88.399940000000001,"Lag",0.99628887262162102,7.6371498838232297]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",98.011300000000006,"Lag",0.99602702204541205,8.7628689041511691]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",91.632900000000006,"Lag",0.99628779419438995,7.91761208531869]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",101.07111,"Lag",0.99602354653051495,9.0404117770939703]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",94.677199999999999,"Lag",0.99628676825487805,8.1817938834467796]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",104.4464,"Lag",0.99602269937797105,9.3433192077491096]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",97.815529999999995,"Lag",0.99628639200465696,8.4534320527830502]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",107.55361000000001,"Lag",0.99601955562002797,9.62510115434333]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",100.83704,"Lag",0.99628535253963302,8.7157839279253704]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",87.36103,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",81.269580000000005,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",88.040490000000005,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",81.894300000000001,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",89.024609999999996,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",82.828460000000007,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",90.022679999999994,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",83.781329999999997,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",91.1113,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",84.824849999999998,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",92.354889999999997,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",88.525769999999994,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",95.150689999999997,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",91.970290000000006,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",98.621960000000001,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",95.344269999999995,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",102.38306,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",98.959559999999996,"Lead","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",234.62694999999999,"Lag",0.99609415510813804,20.798188554693901]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",205.44014999999999,"Lag",0.99602848905795005,18.364318336173]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",233.47031999999999,"Lag",0.996011186746944,20.9156227455838]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",205.29214999999999,"Lag",0.99593555277444001,18.5658615941243]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",232.73060000000001,"Lag",0.99593084606961502,21.0595511192648]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",205.83273,"Lag",0.995847500310717,18.8165534376195]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",233.97143,"Lag",0.99585756027440697,21.362814793931001]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",209.91499999999999,"Lag",0.99577536084124496,19.3567631356152]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",237.29839999999999,"Lag",0.99578032117752002,21.868920042957299]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",213.3082,"Lag",0.99569011589920797,19.8683912656895]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",242.49319,"Lag",0.99571158510448499,22.530108004950002]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",217.52609000000001,"Lag",0.99561078112726398,20.448116106803099]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",247.53353999999999,"Lag",0.99565186036998998,23.1590465052202]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",222.37155000000001,"Lag",0.99554495969326795,21.060802843711599]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",252.50137000000001,"Lag",0.99560269640836296,23.7578940357043]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",227.04836,"Lag",0.99549061761070101,21.635382386235602]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",258.33040999999997,"Lag",0.995562095699977,24.4190503014607]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",232.01609999999999,"Lag",0.99544351469324999,22.224715347648502]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",263.22559999999999,"Lag",0.99551239017558202,25.0216655051073]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",236.42784,"Lag",0.99538751664493896,22.7870159379376]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",186.56725,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",181.09649999999999,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",186.99180999999999,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",181.49456000000001,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",188.00003000000001,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",182.47613999999999,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",189.19905,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",183.64841999999999,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",191.50904,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",188.42639,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",199.15231,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",196.07929999999999,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",206.27202,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",203.13319999999999,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",213.28547,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",210.05360999999999,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",220.96356,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",217.54061999999999,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",34.959690000000002,"Lag",0.99628434542127797,3.02212994375612]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",30.745239999999999,"Lag",0.99624844155978198,2.6706894178181901]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",34.877609999999997,"Lag",0.99623930809024397,3.0333548839562701]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",30.82349,"Lag",0.996198686666246,2.6952841831494001]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",34.824469999999998,"Lag",0.99619019133886699,3.0485603391190099]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",30.97214,"Lag",0.99614537597410202,2.7273167886470699]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",34.926819999999999,"Lag",0.99612188056140105,3.08496814552052]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",31.55209,"Lag",0.99607564378451996,2.8035513803201901]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",35.453710000000001,"Lag",0.99606113013918096,3.1560831029458898]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",32.102409999999999,"Lag",0.99600925516551597,2.8766201517717702]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",36.348909999999997,"Lag",0.996022206824554,3.2518174280370298]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",32.869289999999999,"Lag",0.99596518772701104,2.9616539469507299]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",37.180050000000001,"Lag",0.995981582368199,3.3432161962351099]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",33.688459999999999,"Lag",0.99592123344472605,3.0520545438345299]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",38.010199999999998,"Lag",0.99595298269311106,3.4300780499801502]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",34.492269999999998,"Lag",0.99589044909194702,3.1367199203516498]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",38.989759999999997,"Lag",0.99593277018499304,3.5273036670082001]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",35.361130000000003,"Lag",0.99586760614450498,3.2247143289844602]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",39.810549999999999,"Lag",0.99590070547676401,3.6158146877599702]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",36.126930000000002,"Lag",0.99583240704270504,3.30863976572852]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",21.505019999999998,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",21.134039999999999,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",21.584430000000001,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",21.212309999999999,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",21.721340000000001,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",21.348050000000001,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",22.41976,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",21.938479999999998,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",23.32357,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",22.83802,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",24.291820000000001,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",23.80416,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",25.208570000000002,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",24.710059999999999,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",26.119789999999998,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",25.60726,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",27.117000000000001,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",26.578199999999999,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",182.07389000000001,"Lag",0.99601933195891701,16.294470630744001]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",161.77331000000001,"Lag",0.99595131078190502,14.601617112006]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",180.84147999999999,"Lag",0.99592521937739997,16.3755377915959]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",161.36160000000001,"Lag",0.99584751516369097,14.751121966895701]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",179.76722000000001,"Lag",0.99582637626694903,16.475738972859201]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",161.31456,"Lag",0.99574041955918502,14.9369824244712]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",179.62630999999999,"Lag",0.995726138974248,16.6606028205074]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",163.86219,"Lag",0.995643277721735,15.3460420536817]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",181.60625999999999,"Lag",0.99562897776244197,17.0358848204887]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",165.95115999999999,"Lag",0.99553753153961599,15.730415167838601]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",185.19927000000001,"Lag",0.99555068477115405,17.5288677551892]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",168.86878999999999,"Lag",0.99544842884001195,16.167078558492399]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",188.56607,"Lag",0.99547754918658504,17.9946096018585]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",172.15593999999999,"Lag",0.99536888277155999,16.626178438145601]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",191.86246,"Lag",0.99541544419165995,18.4353306093792]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",175.29002,"Lag",0.99530099157134899,17.053364509490802]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",195.82079999999999,"Lag",0.99536353269023903,18.922639323026001]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",178.65521000000001,"Lag",0.99524150231766595,17.491210790801102]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",198.99442999999999,"Lag",0.99529873086148801,19.3641746253546]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",181.51553000000001,"Lag",0.99516925862947003,17.906619355078199]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",125.25749,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",121.86163000000001,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",125.49816,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",122.41078,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",126.03643,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",123.8017,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",130.20001999999999,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",128.12409,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",135.28878,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",133.21136000000001,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",140.65768,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",138.59166999999999,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",145.68161000000001,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",143.57326,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",150.63269,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",148.46265,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",156.05222000000001,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",153.75153,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",325.60539,"Lag",0.99536675403474395,31.453030686566901]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",288,"Lag",0.995274815513991,28.0970172501451]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",323.26276999999999,"Lag",0.99525866839792698,31.591444883368901]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",285.53003000000001,"Lag",0.995150051097768,28.224066365741301]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",321.37473999999997,"Lag",0.99514836559624398,31.772803446477401]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",283.51431000000002,"Lag",0.99502237684375405,28.3940295050635]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",319.96023000000002,"Lag",0.99503498633391996,32.003179787209902]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",284.79144000000002,"Lag",0.99490296790139698,28.864615560573899]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",318.79277000000002,"Lag",0.99491276073659296,32.279477649758299]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",289.06889999999999,"Lag",0.99478886126592103,29.626833784013201]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",320.36833000000001,"Lag",0.99480249692177003,32.791406116276001]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",294.66208999999998,"Lag",0.99468660230202399,30.497307136319101]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",325.80828000000002,"Lag",0.99468785466346898,33.716908543379802]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",300.03642000000002,"Lag",0.99456253194061595,31.4169534454117]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",331.54318000000001,"Lag",0.99460251874800099,34.5871117258636]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",305.57033000000001,"Lag",0.994470185694737,32.269219700753197]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",339.11799000000002,"Lag",0.99454901341732105,35.553679369910498]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",312.22161999999997,"Lag",0.99440956443214901,33.153369757087098]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",345.57506999999998,"Lag",0.994486278520329,36.440266794169197]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",318.24387000000002,"Lag",0.994341016221721,34.001151698340301]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",226.72720000000001,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",222.78458000000001,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",227.46948,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",223.51338999999999,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",228.79026999999999,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",224.82034999999999,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",236.58175,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",231.46055000000001,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",245.97752,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",240.80882,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",256.03519,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",250.84163000000001,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",265.51787000000002,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",260.20749000000001,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",274.95377999999999,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",269.49257999999998,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",285.34429,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",279.60239999999999,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",190.27907999999999,"Lag",0.978972061936905,39.649610107110902]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",167.10693000000001,"Lag",0.978972061936905,34.821088165321598]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",190.50774999999999,"Lag",0.978972061936905,39.697259466899702]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",167.31664000000001,"Lag",0.978972061936905,34.864786714502898]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",190.90640999999999,"Lag",0.978972061936905,39.780330677698601]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",167.69626,"Lag",0.978972061936905,34.943890444607497]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",191.49454,"Lag",0.978972061936905,39.902882905680201]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",168.26759999999999,"Lag",0.978972061936905,35.062944038090201]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",192.31957,"Lag",0.978972061936905,40.074799428645697]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",169.07590999999999,"Lag",0.978972061936905,35.231376512882903]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",193.38541000000001,"Lag",0.978972061936905,40.296894997094697]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",170.12528,"Lag",0.978972061936905,35.450040127180898]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",194.66322,"Lag",0.978972061936905,40.563160044681503]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",171.38637,"Lag",0.978972061936905,35.712821126594903]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",195.94868,"Lag",0.978972061936905,40.831019169332997]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",172.65548000000001,"Lag",0.978972061936905,35.977273302225797]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",197.26308,"Lag",0.978972061936905,41.104908697939003]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",173.95665,"Lag",0.978972061936905,36.248406015202299]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",198.73562999999999,"Lag",0.978972061936905,41.411752904686402]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",175.41666000000001,"Lag",0.978972061936905,36.552637185820103]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",176.8922,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",170.23692,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",177.23587000000001,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",170.57513,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",179.60792000000001,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",172.83331000000001,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",185.17447999999999,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",178.3065,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",191.76168999999999,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",184.7799,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",198.69193999999999,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",191.61355,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",205.12046000000001,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",197.88682,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",211.30452,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",203.89592999999999,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",218.07836,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",210.39164,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",88.072550000000007,"Lag",0.98783193485842602,13.8662205460981]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",80.45326,"Lag",0.98774564011468502,12.7123032758315]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",87.846220000000002,"Lag",0.987714587735114,13.8983578824406]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",80.21369,"Lag",0.98761626024772697,12.742435456226699]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",87.660690000000002,"Lag",0.98757834372907705,13.9471415519522]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",80.01491,"Lag",0.98746598114454598,12.7892124553226]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",87.588419999999999,"Lag",0.98743738394851899,14.0159938263358]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",81.660380000000004,"Lag",0.98734131507962497,13.118210996855501]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",87.925470000000004,"Lag",0.98724080609487397,14.181705664377199]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",83.036519999999996,"Lag",0.98715069283692702,13.4412897150604]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",89.980270000000004,"Lag",0.98710245152867804,14.593140890711499]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",84.862120000000004,"Lag",0.98700127540357196,13.8180133293751]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",92.049679999999995,"Lag",0.98700770951751204,14.984573116363]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",86.999269999999996,"Lag",0.98690446718998903,14.219704562872201]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",94.007800000000003,"Lag",0.98692500912648795,15.352926481360001]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",88.975610000000003,"Lag",0.98681942751753704,14.590817288999199]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",96.354529999999997,"Lag",0.98686999750847404,15.7699138783076]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",91.134280000000004,"Lag",0.98675968466612396,14.979323596259199]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",98.289479999999998,"Lag",0.98677227739344398,16.1475516653983]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",93.013030000000001,"Lag",0.986657075515741,15.3484500718512]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",67.488330000000005,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",66.23603,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",67.629279999999994,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",66.374780000000001,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",67.909369999999996,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",66.652550000000005,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",68.280249999999995,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",67.020960000000002,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",68.880309999999994,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",67.507729999999995,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",71.494410000000002,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",69.960160000000002,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",73.921379999999999,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",72.354960000000005,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",76.316199999999995,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",74.708410000000001,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",78.949160000000006,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",77.264120000000005,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",117.72635,"Lag",0.98806181061679099,18.355817833124899]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",105.08853999999999,"Lag",0.98798078575501302,16.441861648579199]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",117.54485,"Lag",0.98793814428593096,18.423933197177799]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",105.45923999999999,"Lag",0.98784630791443395,16.593605948745701]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",117.46572,"Lag",0.98780337205997604,18.516002895968899]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",106.07598,"Lag",0.98770232308057404,16.791062948828699]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",118.6931,"Lag",0.98768189482609903,18.804152943401]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",108.53496,"Lag",0.98758198717666701,17.265734904477998]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",120.65998999999999,"Lag",0.987522671954153,19.2412398054589]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",110.61715,"Lag",0.98741061872189795,17.720283585322399]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",123.73868,"Lag",0.987400481935926,19.8304151432739]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",113.29395,"Lag",0.98727483046828501,18.248593959112299]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",126.80181,"Lag",0.98731141747003404,20.394394306456]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",116.35975000000001,"Lag",0.98718066661922199,18.812977485313901]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",129.75586999999999,"Lag",0.98723931649527497,20.929874552895502]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",119.26013,"Lag",0.98710436932185097,19.340328066250802]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",133.28735,"Lag",0.98720237865821003,21.5312090465453]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",122.45343,"Lag",0.98706324316058403,19.890446273020999]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",136.25533999999999,"Lag",0.98712422533321897,22.0790770160284]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",125.27059,"Lag",0.98697903549900601,20.415471518067299]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",79.878110000000007,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",78.057670000000002,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",80.181120000000007,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",78.355090000000004,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",80.959490000000002,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",78.852310000000003,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",83.770449999999997,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",81.513900000000007,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",87.122950000000003,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",84.835070000000002,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",90.701130000000006,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",88.389870000000002,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",94.074100000000001,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",91.70881,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",97.419939999999997,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",94.989440000000002,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",101.07977,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",98.537369999999996,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",29.954740000000001,"Lag",0.98783919321336,4.7146680459908898]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",26.871099999999998,"Lag",0.98773545557625697,4.2476605621853398]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",29.871390000000002,"Lag",0.98769187941695502,4.7304706452240204]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",26.930160000000001,"Lag",0.98757639652942797,4.2850307035987401]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",29.792059999999999,"Lag",0.98751569872634104,4.7521914617765404]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",27.029,"Lag",0.98738874732909099,4.3337348007513299]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",30.00592,"Lag",0.98734969069598899,4.8186310025685204]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",27.585560000000001,"Lag",0.98722541245118201,4.4520751680665702]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",30.421779999999998,"Lag",0.98714094443841205,4.9263393844468597]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",28.032440000000001,"Lag",0.98700134507871795,4.5644814304198196]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",31.108160000000002,"Lag",0.98696940728937599,5.0716387134362302]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",28.619450000000001,"Lag",0.98681104497025995,4.69473148852616]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",31.79599,"Lag",0.98683952241769302,5.2100637505044398]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",29.309830000000002,"Lag",0.98667323387883499,4.8335427149951098]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",32.459249999999997,"Lag",0.98673201399013899,5.3408626498162803]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",29.96106,"Lag",0.98655890242857602,4.9625197090163899]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",33.27525,"Lag",0.98666848587790901,5.4884853567550502]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",30.69378,"Lag",0.98648809612133803,5.0975299244674002]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",33.948560000000001,"Lag",0.98656118847908103,5.6224905732029002]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",31.330359999999999,"Lag",0.98637223882426694,5.2259724990763203]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",19.47203,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",18.89254,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",19.458300000000001,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",18.952459999999999,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",19.495439999999999,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",19.057680000000001,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",20.061170000000001,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",19.65052,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",20.845109999999998,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",20.431550000000001,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",21.681930000000001,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",21.267410000000002,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",22.4679,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",22.044540000000001,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",23.247890000000002,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",22.812819999999999,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",24.104399999999998,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",23.646750000000001,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",165.04682,"Lag",0.98765339551585296,26.178616763885302]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",151.24688,"Lag",0.98755328575983004,24.088659681973201]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",164.46431999999999,"Lag",0.98747070776177204,26.282163330359001]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",151.465,"Lag",0.98736010538394803,24.313457604533902]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",163.9589,"Lag",0.98726811841365403,26.416447395692298]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",151.96115,"Lag",0.98714949694556797,24.599426265201]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",164.60571999999999,"Lag",0.98706190986458897,26.738763197614599]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",154.90239,"Lag",0.98695411095319596,25.2692246886334]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",166.77685,"Lag",0.98683075765540595,27.337193185576002]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",157.31021999999999,"Lag",0.98671231856076602,25.903502139793002]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",178.46592999999999,"Lag",0.98674966211598703,29.344950650320101]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",168.80485999999999,"Lag",0.98663204113636604,27.881812284113501]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",182.29642999999999,"Lag",0.98661271357087799,30.132442687329899]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",172.75059999999999,"Lag",0.98649099288886699,28.686757053100401]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",185.98432,"Lag",0.98649934156160002,30.874591426316801]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",176.45589000000001,"Lag",0.98637376918574105,29.4315409668218]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",190.3631,"Lag",0.98641519075709905,31.701864316915898]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",180.44552999999999,"Lag",0.98628235015916199,30.199879840399401]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",193.97751,"Lag",0.98629454759299995,32.449892400379198]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",183.93331000000001,"Lag",0.98615538487987897,30.9287302125623]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",103.88369,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",102.1019,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",104.23859,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",102.45056,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",106.61188,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",104.26609999999999,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",110.21181,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",107.85136,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",122.68103000000001,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",120.2683,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",127.50189,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",125.08345,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",132.01160999999999,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",129.54096000000001,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",136.45886999999999,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",133.91946999999999,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",141.32801000000001,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",138.65656999999999,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",119.11196,"Lag",0.98266440667782096,22.472123119016199]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",107.27547,"Lag",0.98251821830430297,20.3264367882113]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",119.39635,"Lag",0.98249279657946698,22.6399713781611]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",108.08378,"Lag",0.98233543706290105,20.589259823023198]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",119.70685,"Lag",0.98228569804256205,22.836330907074998]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",109.06923,"Lag",0.98211795636702304,20.907972430339299]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",121.32773,"Lag",0.98209032200202195,23.276316301334401]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",111.92033000000001,"Lag",0.98192854534919405,21.570968720386499]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",123.80517999999999,"Lag",0.98187216396767696,23.899822143424899]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",114.50207,"Lag",0.98169708154780699,22.213379966650098]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",127.37452999999999,"Lag",0.98169357408825297,24.713068787074899]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",117.64514,"Lag",0.98149968245187702,22.9493517451081]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",130.89336,"Lag",0.98155170135119496,25.496777863796702]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",121.15152999999999,"Lag",0.98135104453431898,23.730805732867299]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",134.28761,"Lag",0.98143240795824305,26.244782226166301]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",124.47129,"Lag",0.98122557088081497,24.465306753048399]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",138.15463,"Lag",0.98134975532693303,27.062285112656401]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",127.97150999999999,"Lag",0.98113401277476997,25.216317145045601]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",141.48074,"Lag",0.98122452170421304,27.809378398746301]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",131.12644,"Lag",0.980999824405837,25.9323793918572]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",86.990570000000005,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",83.855379999999997,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",87.342320000000001,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",84.185249999999996,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",87.869820000000004,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",84.690479999999994,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",88.551810000000003,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",85.349760000000003,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",89.296229999999994,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",87.013059999999996,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",92.597430000000003,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",90.981520000000003,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",96.38409,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",94.727580000000003,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",100.11564,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",98.406409999999994,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",104.14521999999999,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",102.33704,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",114.22381,"Lag",0.98199140603937296,21.975549414951999]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",102.61823,"Lag",0.98176176765911505,19.871721813436501]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",132.11888999999999,"Lag",0.981977428396555,25.428523456515901]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",121.04428,"Lag",0.98179040585630095,23.420948635264399]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",131.62467000000001,"Lag",0.98162320233987499,25.588093932068901]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",121.34323999999999,"Lag",0.98141819605843295,23.724304598227]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",131.61861999999999,"Lag",0.98126348779859895,25.843253450812998]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",123.71109,"Lag",0.981084368215702,24.409798175521999]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",133.45634999999999,"Lag",0.98088781873395303,26.4731103613776]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",125.72763,"Lag",0.98069070772220901,25.072069270765599]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",136.48845,"Lag",0.98056644016349703,27.307991892012598]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",128.37422000000001,"Lag",0.98034171601101905,25.837066609601401]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",132.70381,"Lag",0.98009168577765304,26.882928709334202]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",124.40586,"Lag",0.979819875114464,25.3786991709574]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",135.62844999999999,"Lag",0.97986344032277295,27.637292782255301]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",127.3115,"Lag",0.97958082478882003,26.129618976170299]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",139.22784999999999,"Lag",0.97971686708155803,28.477023366108401]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",130.59573,"Lag",0.97942020256683904,26.9122164098345]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",142.24029999999999,"Lag",0.97950137697761097,29.252154406879001]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",133.48557,"Lag",0.97919135204609697,27.665121047252299]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",107.16127,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",103.42006000000001,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",125.62352,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",121.86662,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",125.96078,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",122.18804,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",127.60004000000001,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",124.71925,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",132.70631,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",129.79413,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",138.11892,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",135.18763000000001,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",135.99082999999999,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",133.01403999999999,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",140.89177000000001,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",137.82907,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",146.25385,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",143.03815,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",282.23057999999997,"Lag",0.98293166104053098,52.823873835373099]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",251.08020999999999,"Lag",0.98280158243013505,47.1770204938408]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",282.95818000000003,"Lag",0.98278281676955503,53.1965322733138]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",253.01062999999999,"Lag",0.98264051267598296,47.767722830979501]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",283.97304000000003,"Lag",0.98263324045787204,53.624869281464399]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",255.58716999999999,"Lag",0.98248249306464597,48.479156891473501]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",287.01810999999998,"Lag",0.98249866521246398,54.415092200583103]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",262.38515999999998,"Lag",0.98235812349637697,49.949698819403402]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",293.21821999999997,"Lag",0.98237838416986101,55.786394845405198]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",268.80862000000002,"Lag",0.98223104526681204,51.361489737521502]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",301.70051999999998,"Lag",0.98226154484500405,57.5953327785504]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",276.24171000000001,"Lag",0.98210072219739397,52.980229769503097]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",309.86304999999999,"Lag",0.98216174807337098,59.324278836679703]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",284.32713000000001,"Lag",0.98199561886151998,54.695197539054597]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",317.76983000000001,"Lag",0.98208767575744005,60.967698672768798]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",292.01805000000002,"Lag",0.98191768497613496,56.299486868433704]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",326.79694000000001,"Lag",0.98203609553228699,62.792341561966403]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",300.12437,"Lag",0.98185994630692597,57.9572114806301]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",334.85464999999999,"Lag",0.98196986610639603,64.462355812301496]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",307.73808000000002,"Lag",0.98178905724569798,59.546738632942301]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",223.87905000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",216.88541000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",224.74867,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",217.80115000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",226.27814000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",219.28428,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",228.05288999999999,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",221.01509999999999,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",233.42953,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",229.41433000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",242.96234999999999,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",238.9443,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",251.83376000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",247.72183000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",260.57657999999998,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",256.33803,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",270.12009,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",265.63470000000001,"Lag","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",62.891390000000001,"Lead",0.99999503875221896,-0.198108571337689]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",60.562989999999999,"Lead",0.99999500866569302,-0.191351671912732]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",62.421660000000003,"Lead",0.99999512010114699,-0.19501019264487099]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",60.278829999999999,"Lead",0.999995665639412,-0.17747768006859599]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",62.18139,"Lead",0.99999507647450403,-0.19512599162768601]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",60.26285,"Lead",0.99999565829346904,-0.17758092393889199]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",61.746850000000002,"Lead",0.999995637626925,-0.182386474218308]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",60.139290000000003,"Lead",0.99999563353385701,-0.17772141613568401]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",61.623429999999999,"Lead",0.99999561134718895,-0.182569366047032]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",60.01567,"Lead",0.99999560652742003,-0.177903727574489]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",61.630600000000001,"Lead",0.99999560048869296,-0.18281635500350901]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",60.022489999999998,"Lead",0.99999559537120197,-0.17814970084860901]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",61.680869999999999,"Lead",0.99999559396330095,-0.18310111072257601]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",60.072389999999999,"Lead",0.99999558867020499,-0.17843338284632801]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",61.649059999999999,"Lead",0.99999557475614997,-0.18340513960785301]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",60.040140000000001,"Lead",0.99999556893164498,-0.17873613487378601]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",61.606340000000003,"Lead",0.99999555487451697,-0.18368930321034799]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",59.997199999999999,"Lead",0.99999554849777395,-0.17901966004737099]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",61.642249999999997,"Lead",0.99999554565697002,-0.18398684014561201]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",60.032780000000002,"Lead",0.999995539028668,-0.17931623933926999]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",25.28736,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",24.272200000000002,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",25.114560000000001,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",24.0992,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",24.935860000000002,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",23.920290000000001,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",24.334009999999999,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",23.318300000000001,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",24.237459999999999,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",23.062139999999999,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",24.268630000000002,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",22.994070000000001,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",24.302900000000001,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",23.027999999999999,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",24.33784,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",23.06269,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",24.38138,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",23.106020000000001,"Lead","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",61.112560000000002,"Lag",0.92807889298295598,24.520886257735999]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",57.524340000000002,"Lag",0.92758272849956203,23.170029300472301]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",61.752009999999999,"Lag",0.92790935323909196,24.810088413004099]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",58.076459999999997,"Lag",0.92729857212588995,23.443719448609102]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",62.372140000000002,"Lag",0.92768764940469906,25.1022957612368]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",58.595010000000002,"Lag",0.92692606835743796,23.720798255542999]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",62.82734,"Lag",0.92745698200391702,25.3305753670729]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",58.955959999999997,"Lag",0.92653741166760195,23.937929968062399]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",63.28837,"Lag",0.92723563077649895,25.5599848021658]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",59.325319999999998,"Lag",0.92616342856510303,24.1565433173146]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",63.754420000000003,"Lag",0.92699679938048596,25.7954739426104]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",59.69408,"Lag",0.92575877617573199,24.381303996766999]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",64.240129999999994,"Lag",0.92677855429439604,26.035473899575901]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",60.087899999999998,"Lag",0.92538804791192097,24.610842287756899]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",64.707830000000001,"Lag",0.92652279858821796,26.276293565469]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",60.452970000000001,"Lag",0.92495231352348795,24.841449947248002]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",65.093429999999998,"Lag",0.92630570929716505,26.476607864628601]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",60.752549999999999,"Lag",0.92458146333387103,25.033785659948101]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",65.487170000000006,"Lag",0.92615765944860096,26.666741020024201]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",61.081650000000003,"Lag",0.92432823455493396,25.216862485571198]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",54.723210000000002,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",53.571689999999997,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",55.385770000000001,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",54.219729999999998,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",55.967100000000002,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",54.788490000000003,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",56.46584,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",55.27664,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",56.977910000000001,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",55.778120000000001,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",57.499980000000001,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",56.408470000000001,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",59.488329999999998,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",58.38355,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",61.387300000000003,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",60.24785,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",63.392069999999997,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",62.190510000000003,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",257.36205999999999,"Lag",0.98451447589734498,45.8260587725809]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",235.85498999999999,"Lag",0.98435757864603501,42.213769741808299]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",256.08330999999998,"Lag",0.98412562028689898,46.181039162077901]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",234.42303999999999,"Lag",0.98392847563471497,42.543018933168398]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",254.64345,"Lag",0.98367553699631904,46.583853289349797]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",232.83093,"Lag",0.98343033898018895,42.920261422605201]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",253.13971000000001,"Lag",0.98320128369423798,46.993661759463897]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",231.19224,"Lag",0.98290385412729298,43.307403931958397]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",251.71653000000001,"Lag",0.98269853943173102,47.441799376376402]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",229.63497000000001,"Lag",0.98234404986124402,43.733020032172597]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",249.97649000000001,"Lag",0.98211277492462601,47.926252518866796]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",228.13508999999999,"Lag",0.98269793634235902,42.998101078447803]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",248.78763000000001,"Lag",0.98155840554887996,48.452401666602]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",227.4442,"Lag",0.98223421188302995,43.4539772320081]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",248.5891,"Lag",0.98112470492635995,48.996002958872701]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",227.55681000000001,"Lag",0.98187291452301595,43.927496169032899]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",248.74976000000001,"Lag",0.98075759467752299,49.516088974050398]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",227.98514,"Lag",0.98156895015726497,44.3879777678764]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",248.57801000000001,"Lag",0.98034236507504902,50.0288716393014]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",229.21841000000001,"Lag",0.98125137224691605,45.0218930485754]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",197.89102,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",189.28514000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",198.74482,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",190.07441,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",199.83162999999999,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",191.10075000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",201.00476,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",192.21743000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",202.35516000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",193.51137,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",203.82056,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",194.92031,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",205.76876999999999,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",196.81206,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",207.80148,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",201.68001000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",213.06187,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",208.80627999999999,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",69.690110000000004,"Lag",0.98531688083246305,12.0758943859752]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",61.8446,"Lag",0.98520477848645704,10.7581765511508]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",69.882099999999994,"Lag",0.98511921549846504,12.192236189047501]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",62.315170000000002,"Lag",0.98498708110461297,10.9213081530285]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",70.091059999999999,"Lag",0.98488044949280995,12.328655820326601]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",62.890540000000001,"Lag",0.98472739808445298,11.1192693529064]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",71.534260000000003,"Lag",0.98466209258307902,12.675153087856]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",64.489009999999993,"Lag",0.98449104508551,11.4918454920724]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",73.037989999999994,"Lag",0.98444494479325495,13.0350495225307]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",66.012929999999997,"Lag",0.98425393953517804,11.855133003055]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",75.102270000000004,"Lag",0.98422752799942004,13.4990490078709]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",67.776830000000004,"Lag",0.98400856372483403,12.26868120056]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",77.133300000000006,"Lag",0.98403516529322499,13.9504491212818]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",69.749750000000006,"Lag",0.98379896325352301,12.7103212622493]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",79.190089999999998,"Lag",0.98389423431189005,14.387070337991201]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",71.720010000000002,"Lag",0.98364608754296001,13.1324090548414]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",81.500690000000006,"Lag",0.98378774350476705,14.8569346268264]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",73.772739999999999,"Lag",0.98352615584895697,13.558961959449601]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",83.638149999999996,"Lag",0.98369046346585098,15.2933884494976]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",75.775589999999994,"Lag",0.98342046459991295,13.972806927152099]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",63.166420000000002,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",61.199950000000001,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",63.756869999999999,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",61.772930000000002,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",64.444640000000007,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",62.444270000000003,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",66.234560000000002,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",63.90155,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",69.120149999999995,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",66.733670000000004,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",72.192130000000006,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",69.757940000000005,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",75.09778,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",72.593549999999993,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",77.956599999999995,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",75.374880000000005,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",81.039929999999998,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",78.342740000000006,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",39.904620000000001,"Lag",0.97037334306318401,9.9357328981551305]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",34.755020000000002,"Lag",0.97003908010322204,8.7044894674495392]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",39.587260000000001,"Lag",0.96961675966593797,9.9876482756393195]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",34.413400000000003,"Lag",0.96915888029547803,8.7506044010878306]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",39.205539999999999,"Lag",0.96867479430145798,10.050864011621499]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",34.007429999999999,"Lag",0.96805716468966696,8.8080220841737003]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",39.305860000000003,"Lag",0.96837034483592199,10.1278312607499]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",34.083750000000002,"Lag",0.96770155755690002,8.8792510541471099]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",39.565420000000003,"Lag",0.96821805564819197,10.220436404809201]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",34.319420000000001,"Lag",0.96752595846271605,8.9661442194974406]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",39.912269999999999,"Lag",0.968110028988177,10.328409753963101]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",34.642339999999997,"Lag",0.96740368467938698,9.0683960261437893]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",40.233910000000002,"Lag",0.967898203408594,10.4478887673581]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",34.939979999999998,"Lag",0.96716028560326195,9.1821367603837398]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",40.57367,"Lag",0.96770464763234598,10.5694267956455]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",35.759590000000003,"Lag",0.96702136487659596,9.4184045075277592]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",40.980220000000003,"Lag",0.96760509211694801,10.692604021682801]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",36.817819999999998,"Lag",0.96701960062513104,9.6973951402222607]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",41.913640000000001,"Lag",0.96755485986271705,10.9450571230355]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",37.819830000000003,"Lag",0.96698851779900896,9.9662477652102304]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",31.589780000000001,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",30.578959999999999,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",31.69839,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",30.682790000000001,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",31.845549999999999,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",30.82518,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",32.029440000000001,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",31.004339999999999,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",32.241579999999999,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",31.29776,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",33.150700000000001,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",32.608469999999997,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",34.373350000000002,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",33.819229999999997,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",35.578180000000003,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",35.007730000000002,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",36.894489999999998,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",36.291350000000001,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",61.856589999999997,"Lag",0.98881133265851695,9.3316515468166994]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",53.690219999999997,"Lag",0.98878172452693003,8.1105697407303108]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",62.079270000000001,"Lag",0.98871236412396302,9.4072810410050707]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",53.822380000000003,"Lag",0.98867815711788998,8.1686214870156597]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",62.149859999999997,"Lag",0.98852290757259997,9.4980544623422407]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",53.78584,"Lag",0.98847961625852598,8.2355817413320995]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",62.117010000000001,"Lag",0.98826722734226602,9.6000579358415408]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",53.646039999999999,"Lag",0.98821096594508895,8.3110968606390507]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",62.48565,"Lag",0.98813195153753697,9.7135416643723698]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",53.864240000000002,"Lag",0.988067042736408,8.3966041362889605]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",63.133189999999999,"Lag",0.98807720191474402,9.8372242619905901]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",55.207270000000001,"Lag",0.988034530284289,8.6178907998044405]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",63.785119999999999,"Lag",0.98799388651912901,9.9741033471215506]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",56.872100000000003,"Lag",0.98798348857409202,8.8970322870302496]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",64.494290000000007,"Lag",0.98791794790885901,10.117424445674899]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",58.419609999999999,"Lag",0.987935899944689,9.1575339972841796]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",65.211969999999994,"Lag",0.98785856093964997,10.2555834929972]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",60.060830000000003,"Lag",0.98790803838407304,9.4258676014207801]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",65.904330000000002,"Lag",0.98779562463719295,10.3917931750994]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",61.615740000000002,"Lag",0.98787522804641803,9.6832450805602495]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",45.403799999999997,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",43.383270000000003,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",45.533790000000003,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",43.499859999999998,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",45.501260000000002,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",43.74906,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",45.587200000000003,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",44.154339999999998,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",46.239899999999999,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",45.353169999999999,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",48.148260000000001,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",47.257579999999997,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",49.925370000000001,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",49.013089999999998,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",51.673760000000001,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",50.733539999999998,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",53.577660000000002,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",52.585500000000003,"Lag","NA","NA"]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe10",0.50683,"Lead",0.99944954986767498,-1.6823472873778101E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2024,"poe50",0.5,"Lead",0.99944954986767498,-1.6596761116920902E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe10",0.50683,"Lead",0.99944954986767498,-1.6823472873778101E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2025,"poe50",0.5,"Lead",0.99944954986767498,-1.6596761116920902E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe10",0.50683,"Lead",0.99944954986767498,-1.6823472873778101E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2026,"poe50",0.5,"Lead",0.99944954986767498,-1.6596761116920902E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe10",0.50683,"Lead",0.99944954986767498,-1.6823472873778101E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2027,"poe50",0.5,"Lead",0.99944954986767498,-1.6596761116920902E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe10",0.50683,"Lead",0.99944954986767498,-1.6823472873778101E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2028,"poe50",0.5,"Lead",0.99944954986767498,-1.6596761116920902E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe10",0.50683,"Lead",0.99944954986767498,-1.6823472873778101E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2029,"poe50",0.5,"Lead",0.99944954986767498,-1.6596761116920902E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe10",0.50683,"Lead",0.99944954986767498,-1.6823472873778101E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2030,"poe50",0.5,"Lead",0.99944954986767498,-1.6596761116920902E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe10",0.50683,"Lead",0.99944954986767498,-1.6823472873778101E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2031,"poe50",0.5,"Lead",0.99944954986767498,-1.6596761116920902E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe10",0.50683,"Lead",0.99944954986767498,-1.6823472873778101E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2032,"poe50",0.5,"Lead",0.99944954986767498,-1.6596761116920902E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe10",0.50683,"Lead",0.99944954986767498,-1.6823472873778101E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Non-coincident",2033,"poe50",0.5,"Lead",0.99944954986767498,-1.6596761116920902E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe10",0.67073000000000005,"Lag",0.99968919008022095,1.67267444071411E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2024,"poe50",0.65225,"Lag",0.99968919008022095,1.6265887972146401E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe10",0.67073000000000005,"Lag",0.99968919008022095,1.67267444071411E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2025,"poe50",0.65225,"Lag",0.99968919008022095,1.6265887972146401E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe10",0.67073000000000005,"Lag",0.99968919008022095,1.67267444071411E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2026,"poe50",0.65225,"Lag",0.99968919008022095,1.6265887972146401E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe10",0.67073000000000005,"Lag",0.99968919008022095,1.67267444071411E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2027,"poe50",0.65225,"Lag",0.99968919008022095,1.6265887972146401E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe10",0.67073000000000005,"Lag",0.99968919008022095,1.67267444071411E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2028,"poe50",0.65225,"Lag",0.99968919008022095,1.6265887972146401E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe10",0.67073000000000005,"Lag",0.99968919008022095,1.67267444071411E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2029,"poe50",0.65225,"Lag",0.99968919008022095,1.6265887972146401E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe10",0.67073000000000005,"Lag",0.99968919008022095,1.67267444071411E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2030,"poe50",0.65225,"Lag",0.99968919008022095,1.6265887972146401E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe10",0.67073000000000005,"Lag",0.99968919008022095,1.67267444071411E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2031,"poe50",0.65225,"Lag",0.99968919008022095,1.6265887972146401E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe10",0.67073000000000005,"Lag",0.99968919008022095,1.67267444071411E-2]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Non-coincident",2032,"poe50",0.65225,"Lag",0.99968919008022095,1.6265887972146401E-2]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe10",142.53489999999999,"Lag",0.96788907562008097,37.018800173638198]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe50",125.86857000000001,"Lag",0.96768809176683102,32.797544765301303]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe10",143.80323999999999,"Lag",0.96756665591241298,37.544676753797901]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe50",126.94694,"Lag",0.96732122342362303,33.275305660128801]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe10",145.5736,"Lag",0.96717854443968898,38.245185921440999]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe50",128.17768000000001,"Lag",0.96687341698310603,33.839139636326301]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe10",149.29173,"Lag",0.966833288070163,39.438386634306802]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe50",131.50765000000001,"Lag",0.96648091914387602,34.9340270133047]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe10",152.43360999999999,"Lag",0.96647541740203302,40.4963492548261]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe50",134.60452000000001,"Lag",0.96608100765647298,35.980589481185199]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe10",156.83536000000001,"Lag",0.96617163278248497,41.864020465335898]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe50",138.28527,"Lag",0.96572962613201996,37.165645493903298]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe10",161.01611,"Lag",0.96588594689676499,43.170721062981599]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe50",142.24287000000001,"Lag",0.96541157059754301,38.415826561192297]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe10",165.09873999999999,"Lag",0.96566462163271605,44.416370534812501]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe50",146.04611,"Lag",0.96516538561858001,39.590712010677798]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe10",169.48428000000001,"Lag",0.965441694908585,45.751956590373801]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe50",149.78900999999999,"Lag",0.96490760617107396,40.763529923785804]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe10",173.45529999999999,"Lag",0.96522862732983306,46.975870773547697]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe50",153.37738999999999,"Lag",0.96466743320152004,41.890528879105297]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe10",119.11226000000001,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe50",115.41851,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe10",120.96082,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe50",117.20708,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe10",124.39455,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe50",120.59689,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe10",129.08976999999999,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe50",125.22537,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe10",134.52785,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe50",130.58545000000001,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe10",140.22756000000001,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe50",136.21893,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe10",145.57932,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe50",141.45822999999999,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe10",150.79765,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe50",146.54879,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe10",156.40566999999999,"Lag","NA","NA"]
["VIC","ATSBJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe50",151.95738,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",114.39275000000001,"Lag",0.96717684301768903,30.054152616085599]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",110.51972000000001,"Lag",0.96709810862040901,29.073189870589101]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",116.0928,"Lag",0.96693048588151798,30.6209348590262]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",112.20115,"Lag",0.96684374466452905,29.635256031722701]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",118.71728,"Lag",0.96675710640488399,31.399399199634399]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",114.55410999999999,"Lag",0.96665970025153602,30.344949667054301]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",123.22458,"Lag",0.96665572113639198,32.643773477753697]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",119.07688,"Lag",0.96655870716150205,31.5932421935922]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",127.53668,"Lag",0.96653137992568705,33.852324279880797]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",123.67728,"Lag",0.96644044844591603,32.874813746791901]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",133.17755,"Lag",0.96645235762018999,35.393481808831503]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",129.0865,"Lag",0.96635740600221898,34.3572988616393]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",138.97074000000001,"Lag",0.96639840493718698,36.9643325847588]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",135.09371999999999,"Lag",0.96631081818771503,35.982359250303602]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",144.78737000000001,"Lag",0.96635715346511297,38.536350381127001]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",141.05225999999999,"Lag",0.966275205061223,37.590320074020802]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",151.14661000000001,"Lag",0.96633485956808896,40.242941649474602]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",147.23648,"Lag",0.96625205868368502,39.252582199625699]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",157.23924,"Lag",0.96631242828496899,41.879789141482597]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",153.36874,"Lag",0.96623315695410505,40.899467195501302]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",127.34130999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",124.78626,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",129.67064999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",127.06587,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",133.95244,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",131.33139,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",139.78241,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",137.13388,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",146.71839,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",144.03622999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",154.24433999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",151.54230999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",161.54404,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",158.76503,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",168.89022,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",166.01267999999999,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",176.88059000000001,"Lag","NA","NA"]
["VIC","ATSBP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona-Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",173.82458,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",253.02833000000001,"Lag",0.967959184309098,65.6405074095901]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",226.63580999999999,"Lag",0.967710895778368,59.0325502007898]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",256.34928000000002,"Lag",0.96772161304359094,66.760472394696194]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",229.60518999999999,"Lag",0.96744468033228104,60.064491779419399]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",261.19826999999998,"Lag",0.96754778142236098,68.215444732893403]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",233.50202999999999,"Lag",0.96724440293326996,61.281072086224498]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",269.77825999999999,"Lag",0.96743801719818001,70.581315795485395]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",241.46778,"Lag",0.96712478903648103,63.493154437623502]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",277.55874,"Lag",0.96730223108193303,72.775855635797299]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",249.25832,"Lag",0.96698289333784404,65.690213023758901]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",287.90899000000002,"Lag",0.96720676455105603,75.605438899193601]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",258.41012000000001,"Lag",0.96687434233987302,68.219737546387506]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",298.12966,"Lag",0.967131532996657,78.383755202945594]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",268.35804000000002,"Lag",0.96679979525622906,70.929764792152596]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",308.00934999999998,"Lag",0.96706564745468904,81.066595743120004]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",277.84422000000001,"Lag",0.96673355489552004,73.514081309564702]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",319.02893999999998,"Lag",0.96701946296212604,84.028779577097396]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",287.77469000000002,"Lag",0.96668201804300502,76.2035796116093]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",329.25510000000003,"Lag",0.96697215696437999,86.787614992854998]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",297.39064000000002,"Lag",0.96663396424672499,78.809635316737399]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",164.28488999999999,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",160.43199000000001,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",167.35593,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",163.42868999999999,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",172.8287,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",168.86412000000001,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",180.21518,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",176.19373999999999,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",188.90683000000001,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",184.81824,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",198.23864,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",194.10024000000001,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",207.21673000000001,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",202.95751999999999,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",216.21462,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",211.80767,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",225.99623,"Lag","NA","NA"]
["VIC","ATSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ATS_West"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Altona West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",221.33788999999999,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe10",1.243E-2,"Lag",0.98737960137193603,1.9937189106750798E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe50",1.222E-2,"Lag",0.98737960137193603,1.9600358075985099E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe10",1.251E-2,"Lag",0.98737960137193603,2.0065505689899599E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe50",1.23E-2,"Lag",0.98737960137193603,1.97286746591339E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe10",1.268E-2,"Lag",0.98737960137193603,2.03381784290909E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe50",1.2460000000000001E-2,"Lag",0.98737960137193603,1.9985307825431601E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe10",1.337E-2,"Lag",0.98737960137193603,2.1444908958749599E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe50",1.315E-2,"Lag",0.98737960137193603,2.10920383550903E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe10",1.375E-2,"Lag",0.98737960137193603,2.2054412728706599E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe50",1.357E-2,"Lag",0.98737960137193603,2.1765700416621699E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe10",1.426E-2,"Lag",0.98737960137193603,2.2872430946280502E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe50",1.4069999999999999E-2,"Lag",0.98737960137193603,2.2567679061302002E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe10",1.495E-2,"Lag",0.98737960137193603,2.3979161475939201E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe50",1.478E-2,"Lag",0.98737960137193603,2.37064887367479E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe10",1.546E-2,"Lag",0.98737960137193603,2.4797179693513E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe50",1.5310000000000001E-2,"Lag",0.98737960137193603,2.4556586100109002E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe10",1.6029999999999999E-2,"Lag",0.98737960137193603,2.57114353484485E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe50",1.5869999999999999E-2,"Lag",0.98737960137193603,2.5454802182150798E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe10",1.6729999999999998E-2,"Lag",0.98737960137193603,2.6834205451000798E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe50",1.6590000000000001E-2,"Lag",0.98737960137193603,2.66096514304904E-3]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe10",1.223E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe50",1.132E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe10",1.2319999999999999E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe50",1.141E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe10",1.282E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe50",1.188E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe10",1.3480000000000001E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe50",1.2500000000000001E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe10",1.401E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe50",1.3010000000000001E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe10",1.4710000000000001E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe50",1.3679999999999999E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe10",1.5389999999999999E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe50",1.4330000000000001E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe10",1.5939999999999999E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe50",1.485E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe10",1.668E-2,"Lag","NA","NA"]
["VIC","BATS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe50",1.555E-2,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",181.62609,"Lag",0.98619949177892297,30.491053680581]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",169.18584000000001,"Lag",0.98611076621593896,28.495690713684301]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",182.65645000000001,"Lag",0.98603637359873297,30.8485522027065]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",170.13149000000001,"Lag",0.98593497085307502,28.839602113611701]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",184.72202999999999,"Lag",0.98589672657007899,31.356354152238399]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",171.69515000000001,"Lag",0.98578106981527602,29.2668982388759]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",189.45128,"Lag",0.98578264023474804,32.291759510513998]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",176.25301999999999,"Lag",0.98565947254004505,30.174814977126498]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",193.40895,"Lag",0.98563046952700195,33.146139177226999]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",180.4521,"Lag",0.98550079305201399,31.067915776762]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",199.17162999999999,"Lag",0.98551604195214004,34.272367719708903]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",185.63715999999999,"Lag",0.98537548149174303,32.101496538295798]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",204.89465999999999,"Lag",0.98542973537253997,35.364372599500399]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",191.43414000000001,"Lag",0.98528770756736594,33.205362682242203]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",210.19216,"Lag",0.98532669079879198,36.4096321459931]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",196.69657000000001,"Lag",0.985180541446394,34.244997150521101]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",216.04844,"Lag",0.98522001662928904,37.562907729422598]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",202.04854,"Lag",0.985064481228345,35.3173835638908]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",221.43192999999999,"Lag",0.98512401798169502,38.626555516314603]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",207.24387999999999,"Lag",0.98496327081466795,36.3508528943835]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",177.71831,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",172.68862999999999,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",179.85838000000001,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",174.76328000000001,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",184.48527999999999,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",179.35300000000001,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",191.08631,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",185.88618,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",198.87142,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",193.58901,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",207.12676999999999,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",201.77995000000001,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",214.86786000000001,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",209.38668000000001,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",222.51036999999999,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",216.86960999999999,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",230.84103999999999,"Lag","NA","NA"]
["VIC","BATS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BATS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ballarat (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",224.93414999999999,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",73.797600000000003,"Lag",0.99900731004271104,3.2906945912107601]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",66.416079999999994,"Lag",0.99899596068543794,2.9784535018129801]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",74.17398,"Lag",0.99899415986907003,3.3293455741010001]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",66.72945,"Lag",0.99898121186719802,3.01443913785827]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",74.921310000000005,"Lag",0.998981910182696,3.3833366814221102]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",67.239379999999997,"Lag",0.99896715640374001,3.0583881353398001]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",76.726070000000007,"Lag",0.99897178572614698,3.4820489948689599]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",68.902780000000007,"Lag",0.99895589049964895,3.15112086729162]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",78.267420000000001,"Lag",0.99896084761778703,3.57087225178643]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",70.477530000000002,"Lag",0.99894407255912598,3.24135695684868]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",80.51737,"Lag",0.99895275912200099,3.6878155259019301]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",72.420820000000006,"Lag",0.99893481190675004,3.34532839691447]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",82.679029999999997,"Lag",0.99894534663567902,3.8002220708821]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",74.534599999999998,"Lag",0.99892692728857002,3.45570959977535]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",84.683130000000006,"Lag",0.99893737534010196,3.90704288664576]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",76.45438,"Lag",0.99891829893675999,3.55896364762968]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",86.983099999999993,"Lag",0.99893110021779596,4.0250080547688203]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",78.481989999999996,"Lag",0.99891115805474595,3.6654078846832099]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",89.077160000000006,"Lag",0.99892520108379201,4.1332842583134699]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",80.434460000000001,"Lag",0.998904725023253,3.7676947776457799]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",57.252920000000003,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",55.52713,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",57.930750000000003,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",56.18242,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",59.416359999999997,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",57.65325,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",61.546300000000002,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",59.757469999999998,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",64.070899999999995,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",62.251170000000002,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",66.762230000000002,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",64.917259999999999,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",69.283379999999994,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",67.391109999999998,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",71.775710000000004,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",69.828180000000003,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",74.496719999999996,"Lag","NA","NA"]
["VIC","BETS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Bendigo (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",72.459280000000007,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",156.80327,"Lag",0.99655395274326997,13.051350076036799]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",137.90030999999999,"Lag",0.99649265510431895,11.580151365002701]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",157.20284000000001,"Lag",0.99650141269891701,13.184499181164]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",138.16318999999999,"Lag",0.99643199521296999,11.7026620224047]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",158.49516,"Lag",0.99645910385957204,13.373446009043301]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",138.94915,"Lag",0.99638178751022,11.8521993514901]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",161.45797999999999,"Lag",0.99639802493726304,13.7410706761037]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",141.54013,"Lag",0.99631130224461295,12.1908840785247]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",163.92275000000001,"Lag",0.99633916646375997,14.064982062897]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",144.01024000000001,"Lag",0.99624501603045401,12.515211072245]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",168.16627,"Lag",0.99630850371912005,14.489723572227399]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",147.54658000000001,"Lag",0.99620860206268103,12.8849134604817]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",172.11333999999999,"Lag",0.99627644363588697,14.8944330917931]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",151.32186999999999,"Lag",0.99617334546538205,13.2762535122719]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",175.57862,"Lag",0.99623623084676804,15.276601691402499]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",154.54464999999999,"Lag",0.99612801237947302,13.6395485763385]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",179.35989000000001,"Lag",0.99619063914570405,15.700371799874301]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",157.68096,"Lag",0.99607429137877601,14.013122084877301]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",182.94372000000001,"Lag",0.99615703297297298,16.084974660613199]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",160.90304,"Lag",0.99603593540401203,14.369570300327]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",115.21597,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",112.1604,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",116.36552,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",113.27544,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",119.10984000000001,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",116.00615000000001,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",123.11815,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",119.98305000000001,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",127.87269000000001,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",124.69785,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",132.91282000000001,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",129.70987,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",137.58912000000001,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",134.31246999999999,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",142.18695,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",138.82034999999999,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",147.21588,"Lag","NA","NA"]
["VIC","BETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Bendigo (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",143.69203999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe10",3.01206,"Lag",0.97052675246241005,0.74793054699877304]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe50",3,"Lag",0.97052675246241005,0.74493590466203197]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe10",3.2752300000000001,"Lag",0.97052675246241005,0.81327880767540905]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe50",3.2596400000000001,"Lag",0.97052675246241005,0.80940762409084899]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe10",3.2898499999999999,"Lag",0.97052675246241005,0.81690912865079501]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe50",3.27406,"Lag",0.97052675246241005,0.81298828267259104]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe10",3.2898499999999999,"Lag",0.97052675246241005,0.81690912865079501]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe50",3.27406,"Lag",0.97052675246241005,0.81298828267259104]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe10",3.2898499999999999,"Lag",0.97052675246241005,0.81690912865079501]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe50",3.27406,"Lag",0.97052675246241005,0.81298828267259104]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe10",3.2898499999999999,"Lag",0.97052675246241005,0.81690912865079501]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe50",3.27406,"Lag",0.97052675246241005,0.81298828267259104]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe10",3.2898499999999999,"Lag",0.97052675246241005,0.81690912865079501]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe50",3.27406,"Lag",0.97052675246241005,0.81298828267259104]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe10",3.2898499999999999,"Lag",0.97052675246241005,0.81690912865079501]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe50",3.27406,"Lag",0.97052675246241005,0.81298828267259104]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe10",3.2898499999999999,"Lag",0.97052675246241005,0.81690912865079501]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe50",3.27406,"Lag",0.97052675246241005,0.81298828267259104]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe10",3.2898499999999999,"Lag",0.97052675246241005,0.81690912865079501]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe50",3.27406,"Lag",0.97052675246241005,0.81298828267259104]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe10",2.62771,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe50",2.5651299999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe10",2.9016899999999999,"Lag","NA","NA"]
["VIC","BLTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe50",2.8302499999999999,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",53.984830000000002,"Lag",0.96918629488882202,13.720812739411601]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",52.348419999999997,"Lag",0.96914397983622802,13.3144725514956]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",54.238610000000001,"Lag",0.96894892089601403,13.840865277190799]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",52.599409999999999,"Lag",0.96889918284681598,13.4338322988835]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",54.685200000000002,"Lag",0.96867631532300602,14.0189247191413]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",52.918709999999997,"Lag",0.96861371350121706,13.5802841103991]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",55.874450000000003,"Lag",0.96845552267359702,14.3766616593207]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",54.110340000000001,"Lag",0.96838698359193498,13.938612033062901]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",56.827019999999997,"Lag",0.96822355231255597,14.678075743812499]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",55.180430000000001,"Lag",0.968153686955327,14.269207740060001]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",58.220649999999999,"Lag",0.96803303113700001,15.0852945306384]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",56.454030000000003,"Lag",0.96795359991232899,14.646621641340399]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",59.49342,"Lag",0.96784588288843998,15.4623879011037]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",57.794870000000003,"Lag",0.96776558841472005,15.0406176074824]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",60.687269999999998,"Lag",0.96769161565891804,15.8123624605469]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",59.019480000000001,"Lag",0.96760988727625896,15.398230243068101]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",62.008540000000004,"Lag",0.967516530231047,16.202555341049699]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",60.236159999999998,"Lag",0.96742607001900505,15.762452174814699]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",63.173630000000003,"Lag",0.96734531885207098,16.5526419138709]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",61.383679999999998,"Lag",0.96725046610516396,16.108175906354301]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",50.767629999999997,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",49.85483,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",51.241340000000001,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",50.316110000000002,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",52.355699999999999,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",51.432850000000002,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",53.977089999999997,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",53.052970000000002,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",55.856540000000003,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",54.929310000000001,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",57.792700000000004,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",56.867530000000002,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",59.545259999999999,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",58.600250000000003,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",61.23847,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",60.26596,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",63.086019999999998,"Lag","NA","NA"]
["VIC","BLTS22P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brooklyn (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",62.058120000000002,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe10",138.84057000000001,"Lag",0.96824345536258505,35.849891587530401]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe50",124.54982,"Lag",0.96811079308005799,32.230324128666297]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe10",139.50640999999999,"Lag",0.96799213496662795,36.171154198487699]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe50",125.09860999999999,"Lag",0.96782947456740598,32.521940264032096]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe10",140.18897000000001,"Lag",0.96768294486623097,36.532063876601697]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe50",125.66431,"Lag",0.967483139470247,32.853251589838202]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe10",140.95124999999999,"Lag",0.96737746500147903,36.912687372790302]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe50",126.31661,"Lag",0.96714082257548495,33.2060193031515]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe10",141.82498000000001,"Lag",0.96706250846084696,37.329530287470398]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe50",127.08067,"Lag",0.96678782413703601,33.5950849518929]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe10",142.86225999999999,"Lag",0.96676494320933903,37.780792570782602]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe50",128.00828999999999,"Lag",0.96645445356272097,34.018572502070697]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe10",144.04261,"Lag",0.96647972020885298,38.264565828008102]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe50",129.07903999999999,"Lag",0.96613515642774705,34.4745862229884]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe10",145.38801000000001,"Lag",0.96624650628566,38.763144797309401]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe50",130.31542999999999,"Lag",0.96587459009935095,34.945555091441904]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe10",146.58933999999999,"Lag",0.96599729764334497,39.235090003981099]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe50",131.41963999999999,"Lag",0.96559603677556005,35.392901701706499]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe10",147.77493000000001,"Lag",0.96575915215844599,39.6980649408736]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe50",132.51358999999999,"Lag",0.96533002386514,35.832666019007299]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe10",118.49397,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe50",115.57201000000001,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe10",119.57113,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe50",116.62417000000001,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe10",120.79952,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe50",117.82836,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe10",122.11068,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe50",119.11612,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe10",123.58856,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe50",120.5706,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe10",125.21449,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe50",122.17314,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe10",126.91534,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe50",123.85059,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe10",128.59082000000001,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe50",125.50407,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe10",130.2355,"Lag","NA","NA"]
["VIC","BLTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe50",127.12817,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",119.4785,"Lag",0.96938964212269096,30.261567141954998]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",122.20269,"Lag",0.96938964212269096,30.951551185882899]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",120.59965,"Lag",0.96938964212269096,30.5455325081188]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",123.4006,"Lag",0.96938964212269096,31.2549583586799]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",122.20647,"Lag",0.96938964212269096,30.952508585949001]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",124.81765,"Lag",0.96938964212269096,31.613869407266101]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",125.44025999999999,"Lag",0.96938964212269096,31.771564342490901]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",128.25169,"Lag",0.96938964212269096,32.4836445720711]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",128.16825,"Lag",0.96938964212269096,32.4625108520937]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",131.42472000000001,"Lag",0.96938964212269096,33.287311009032102]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",131.86625000000001,"Lag",0.96938964212269096,33.3991419220431]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",135.05277000000001,"Lag",0.96938964212269096,34.206225112150001]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",135.28554,"Lag",0.96938964212269096,34.265181200346902]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",138.83341999999999,"Lag",0.96938964212269096,35.163789810528598]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",138.43682999999999,"Lag",0.96938964212269096,35.063341320525602]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",142.23867000000001,"Lag",0.96938964212269096,36.026273031443999]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",142.01942,"Lag",0.96938964212269096,35.970741294806302]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",145.77520999999999,"Lag",0.96938964212269096,36.922009441427498]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",145.22971999999999,"Lag",0.96938964212269096,36.783847493794497]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",149.1275,"Lag",0.96938964212269096,37.771078930199998]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",122.57736,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",119.47898000000001,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",124.29680999999999,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",121.1534,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",127.56639,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",124.40279,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",132.09684999999999,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",128.89571000000001,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",137.27446,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",134.02786,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",142.60993999999999,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",139.33055999999999,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",147.49901,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",144.13697999999999,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",152.29189,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",148.82881,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",157.52715000000001,"Lag","NA","NA"]
["VIC","BLTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BLTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brooklyn (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",153.8905,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe10",59.423990000000003,"Lag",0.96040964463978096,17.2374655608388]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe50",55.517560000000003,"Lag",0.96022313391117697,16.144561083095098]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe10",59.692540000000001,"Lag",0.959856789282444,17.443428098930902]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe50",55.755870000000002,"Lag",0.95962935408021299,16.342063356596]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe10",60.191769999999998,"Lag",0.95921535169973204,17.738236540545401]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe50",56.0854,"Lag",0.95893074349196605,16.589394718146899]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe10",61.517919999999997,"Lag",0.95860647785306796,18.272630310403901]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe50",57.350200000000001,"Lag",0.958277788504593,17.106624558353499]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe10",62.62003,"Lag",0.95797186778757903,18.751403724160301]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe50",58.524749999999997,"Lag",0.95760876806625095,17.605664558319798]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe10",64.132140000000007,"Lag",0.95727237474189697,19.374041116976599]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe50",59.838000000000001,"Lag",0.95684697006783603,18.1726667587881]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe10",65.630899999999997,"Lag",0.95667483199380199,19.974387377376701]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe50",61.347360000000002,"Lag",0.95621664334488099,18.775978588125501]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe10",67.2179,"Lag",0.95629035918440997,20.554193417227101]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe50",62.917070000000002,"Lag",0.95581380777441005,19.350947393360201]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe10",69.109120000000004,"Lag",0.95603874585552895,21.1974506494727]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe50",64.643180000000001,"Lag",0.95553852848812004,19.948011692846102]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe10",70.750420000000005,"Lag",0.95569818407275198,21.790637796282802]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe50",66.216800000000006,"Lag",0.95517749411304298,20.522263961761599]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe10",56.428620000000002,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe50",55.098410000000001,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe10",57.122149999999998,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe50",55.773589999999999,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe10",58.586449999999999,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe50",57.231879999999997,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe10",60.66977,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe50",59.301990000000004,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe10",63.118450000000003,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe50",61.734070000000003,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe10",65.713650000000001,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe50",64.318399999999997,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe10",68.135149999999996,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe50",66.705659999999995,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe10",70.534570000000002,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe50",69.062160000000006,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe10",73.164069999999995,"Lag","NA","NA"]
["VIC","BTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe50",71.615260000000006,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe10",53.306849999999997,"Lag",0.96002040198453897,15.5436162268416]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe50",48.263379999999998,"Lag",0.95970130016782795,14.1326013241386]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe10",53.527679999999997,"Lag",0.95949330524773502,15.717076512493801]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe50",48.441560000000003,"Lag",0.95911529971905696,14.2941293913777]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe10",53.968000000000004,"Lag",0.95892269947705,15.9647573332742]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe50",48.712449999999997,"Lag",0.95847006715470195,14.494408670171101]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe10",55.157470000000004,"Lag",0.958417432141067,16.423205182036099]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe50",49.806060000000002,"Lag",0.95790977664244303,14.9260377039954]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe10",56.084429999999998,"Lag",0.95779961347044196,16.8310025808677]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe50",50.759149999999998,"Lag",0.95723568387499602,15.341145510028401]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe10",57.429009999999998,"Lag",0.95718264416521903,17.3684920580992]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe50",51.883659999999999,"Lag",0.95653827181909601,15.8170658593304]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe10",58.774169999999998,"Lag",0.95669206282894204,17.883780244456801]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe50",53.19558,"Lag",0.95600511294352097,16.323054469133499]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe10",60.148789999999998,"Lag",0.95636553077884101,18.375655072075901]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe50",54.515180000000001,"Lag",0.955652608811705,16.799536315343499]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe10",61.797260000000001,"Lag",0.95616252965833803,18.926168812830799]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe50",55.974939999999997,"Lag",0.95542233780818397,17.297254535893298]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe10",63.218310000000002,"Lag",0.95586928664343096,19.430535138901899]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe50",57.296660000000003,"Lag",0.95510136434877602,17.773831242855898]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe10",38.499139999999997,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe50",37.33155,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe10",38.960920000000002,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe50",37.778120000000001,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe10",39.96499,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe50",38.77214,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe10",41.398319999999998,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe50",40.188049999999997,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe10",43.095559999999999,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe50",41.864370000000001,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe10",44.904719999999998,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe50",43.656399999999998,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe10",46.609589999999997,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe50",45.329340000000002,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe10",48.303629999999998,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe50",46.985860000000002,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe10",50.160319999999999,"Lag","NA","NA"]
["VIC","BTS22J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Brunswick (Jemena) 22 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe50",48.781410000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe10",181.34448,"Lag",0.93647616839488501,67.917553239496101]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe50",176.57937999999999,"Lag",0.936421489345314,66.164302416724396]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe10",183.71917999999999,"Lag",0.93595922038387502,69.115265230051605]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe50",178.93358000000001,"Lag",0.93589102613536201,67.354471723628606]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe10",186.76069000000001,"Lag",0.93534121258123004,70.633048339930596]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe50",181.53308999999999,"Lag",0.93524970733055801,68.709627215269805]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe10",191.79545999999999,"Lag",0.93471506533787796,72.924603058780804]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe50",186.58769000000001,"Lag",0.934608568746784,71.008478100793397]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe10",196.12477000000001,"Lag",0.93411692167725702,74.947907412337599]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe50",191.33814000000001,"Lag",0.93400617677846198,73.186734932053099]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe10",201.90253000000001,"Lag",0.93351676525679805,77.544264500461097]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe50",196.71754999999999,"Lag",0.93338386833412501,75.636524799079197]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe10",207.35926000000001,"Lag",0.93294505868794597,80.018888380068304]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe50",202.43120999999999,"Lag",0.93280801125644697,78.205682420663507]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe10",212.58046999999999,"Lag",0.93245376094585597,82.366611504338593]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe50",207.78064000000001,"Lag",0.93231202603744301,80.600582271654204]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe10",218.30955,"Lag",0.93210025243550299,84.831865465039002]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe50",213.18214,"Lag",0.93194390248090497,82.945307826964793]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe10",223.44264000000001,"Lag",0.93173857249611503,87.083091422543703]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe50",218.29178999999999,"Lag",0.93157636298749602,85.187909369601797]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe10",159.73084,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe50",155.65842000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe10",162.68026,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe50",158.52651,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe10",167.48969,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe50",163.29257999999999,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe10",173.75744,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe50",169.49997999999999,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe10",180.97148000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe50",176.64257000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe10",188.48475999999999,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe50",184.10073,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe10",195.50623999999999,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe50",191.00093000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe10",202.24939000000001,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe50",197.60239999999999,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe10",209.42993999999999,"Lag","NA","NA"]
["VIC","BTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"BTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Brunswick (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe50",204.54891000000001,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",316.22982999999999,"Lag",0.99022237161362403,44.548969878675798]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",284.89681999999999,"Lag",0.99007288892072598,40.4451421025827]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",318.53667999999999,"Lag",0.99006072763365205,45.248905203480199]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",286.78852000000001,"Lag",0.98989097956263705,41.090703331146699]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",322.90552000000002,"Lag",0.98994103156545299,46.149071747042598]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",290.00745999999998,"Lag",0.98975234468636297,41.840262206957703]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",331.67475000000002,"Lag",0.98985315257034301,47.612141841398604]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",298.07407000000001,"Lag",0.98965486439270201,43.211306943008204]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",339.20197999999999,"Lag",0.98974555431990596,48.954169241646703]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",305.65037000000001,"Lag",0.98953956830699197,44.559761265820498]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",349.91971999999998,"Lag",0.98967064594652698,50.687971026673601]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",314.94484,"Lag",0.98945311263721303,46.107150862587197]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",360.14679999999998,"Lag",0.98959118909940802,52.372851990941903]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",324.86416000000003,"Lag",0.98936896085625903,47.751723090593899]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",369.89316000000002,"Lag",0.98951774815678595,53.982614679924303]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",334.15219000000002,"Lag",0.98929022958843105,49.301456201038697]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",380.83803,"Lag",0.98947672634313899,55.690304188976498]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",343.86842999999999,"Lag",0.98924314691417703,50.848226413778796]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",390.71131000000003,"Lag",0.98942952921145499,57.264115968853602]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",353.08253000000002,"Lag",0.98919242099773397,52.335702371037897]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",243.43806000000001,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",236.57516000000001,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",247.16334000000001,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",240.18232,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",254.19900000000001,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",247.14228,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",263.93713000000002,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",256.76560000000001,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",275.48,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",268.17270000000002,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",287.9128,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",280.49342999999999,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",299.56211000000002,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",291.93329999999997,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",310.93561,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",303.06639999999999,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",323.17971,"Lag","NA","NA"]
["VIC","CBTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",314.92520999999999,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",186.90422000000001,"Lag",0.990429841127625,26.045242239389601]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",170.85535999999999,"Lag",0.99032303519550302,23.943249566402599]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",186.92615000000001,"Lag",0.990254033914578,26.289973312671801]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",170.76293000000001,"Lag",0.99012866016564205,24.173002386894101]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",187.59146999999999,"Lag",0.99005511758846099,26.6554545184562]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",170.87054000000001,"Lag",0.98990454286111396,24.465437760535199]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",190.75890000000001,"Lag",0.98986405617653495,27.368629852733498]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",173.75140999999999,"Lag",0.98969314326167301,25.1410810196139]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",193.29633000000001,"Lag",0.98967379055631399,27.995803958615699]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",176.42721,"Lag",0.98948695294674804,25.786378077915199]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",197.52422999999999,"Lag",0.98951597929323598,28.829374281528501]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",179.95829000000001,"Lag",0.98930824909335502,26.528682695077599]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",201.38543000000001,"Lag",0.98935491728926095,29.621468560456201]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",183.75443999999999,"Lag",0.98913360570338305,27.312257077677501]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",204.9161,"Lag",0.98919647740467798,30.367920485739599]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",187.12385,"Lag",0.98896036645999497,28.0375880424413]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",209.43638999999999,"Lag",0.98908607375714996,31.198617670374801]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",191.03546,"Lag",0.98883494451779497,28.788563620669901]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",213.48134999999999,"Lag",0.98898064389144302,31.9569656774229]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",194.78415000000001,"Lag",0.98871899409651898,29.5081077893627]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",140.27983,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",136.48236,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",141.59782999999999,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",137.75845000000001,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",144.86711,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",141.00971999999999,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",149.69691,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",145.79846000000001,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",155.44906,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",151.49889999999999,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",161.58185,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",157.59393,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",167.27502000000001,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",163.19423,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",172.89887999999999,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",168.70518000000001,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",179.08107000000001,"Lag","NA","NA"]
["VIC","CBTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"CBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Cranbourne (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",174.69195999999999,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",266.85761000000002,"Lag",0.98602841376295003,45.082267214163402]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",240.94058000000001,"Lag",0.98596418881436498,40.799352934921401]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",270.83828,"Lag",0.98595279485313703,45.8810499474938]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",244.55766,"Lag",0.98588031518076202,41.538050666120398]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",276.31531999999999,"Lag",0.98589336046779497,46.909928293603897]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",249.03067999999999,"Lag",0.98581278080023804,42.401009861978899]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",286.26742999999999,"Lag",0.98585221497429598,48.671845236996397]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",258.30605000000003,"Lag",0.98576802581857204,44.051092254524598]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",295.46480000000003,"Lag",0.98580456859312804,50.321951278357297]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",267.48142999999999,"Lag",0.98571807703706305,45.697564342264997]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",307.43738000000002,"Lag",0.98577160932762198,52.423124680914498]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",278.15037000000001,"Lag",0.98568098311917396,47.583304943648997]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",319.26231999999999,"Lag",0.98574645654194704,54.488613968990499]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",289.65717999999998,"Lag",0.98565583709940296,49.596221713976803]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",330.64213999999998,"Lag",0.98571958554989902,56.485136550596401]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",300.57736999999997,"Lag",0.98562813060617405,51.516788219976497]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",343.50258000000002,"Lag",0.98570298796893696,58.716980801339098]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",312.21546999999998,"Lag",0.98560964377901505,53.546634886887702]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",355.53836000000001,"Lag",0.98568918413417095,60.804301766722503]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",323.54284999999999,"Lag",0.98559565932105697,55.5168893336377]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",202.47232,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",196.43733,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",206.20141000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",200.04706999999999,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",212.97805,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",206.72748000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",222.31028000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",215.91928999999999,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",233.17400000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",226.62307000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",244.7885,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",238.09708000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",255.83974000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",248.92544000000001,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",266.97422,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",259.80248999999998,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",279.16636,"Lag","NA","NA"]
["VIC","DPTS",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"DPTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Deer Park (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",271.60203999999999,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",109.12783,"Lag",0.989968824199701,15.574462176395899]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",98.212999999999994,"Lag",0.98985490960997202,14.097305181444099]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",109.42874999999999,"Lag",0.98982841519126097,15.728005333066401]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",98.433310000000006,"Lag",0.98969732837320701,14.239938995013301]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",110.12976,"Lag",0.98966682264794203,15.955954980235701]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",98.792339999999996,"Lag",0.98951238871699099,14.421606826603799]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",112.38294999999999,"Lag",0.98952742990102105,16.3935947121306]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",100.84417999999999,"Lag",0.98935635253532805,14.8319968843459]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",114.30971,"Lag",0.98939392999895803,16.782301542840099]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",102.82687,"Lag",0.98921090458497196,15.2282729938008]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",117.2638,"Lag",0.98929071552352199,17.3009274830737]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",105.34007,"Lag",0.98909252464730102,15.6872311474078]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",120.07071999999999,"Lag",0.98919159142147695,17.798191816563801]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",108.08264,"Lag",0.98898544068168803,16.1757866826275]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",122.69167,"Lag",0.98909407678773698,18.269907838322599]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",110.5883,"Lag",0.98887901336925199,16.631899948324399]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",125.62597,"Lag",0.988996937955819,18.791364612671]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",113.13028,"Lag",0.98876811697922096,17.1002621502187]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",128.36868999999999,"Lag",0.98891922215286698,19.270455807231599]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",115.67334,"Lag",0.98868247806034804,17.552332386540701]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",80.137720000000002,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",77.881249999999994,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",80.980329999999995,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",78.697370000000006,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",82.953109999999995,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",80.65643,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",85.822879999999998,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",83.498729999999995,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",89.237129999999993,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",86.879040000000003,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",92.875600000000006,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",90.491600000000005,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",96.276939999999996,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",93.835729999999998,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",99.635120000000001,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",97.125429999999994,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",103.3056,"Lag","NA","NA"]
["VIC","ERTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",100.67981,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",132.70115999999999,"Lag",0.98955568362949697,19.330920748029801]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",118.80316000000001,"Lag",0.98938431399404603,17.450036857411298]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",132.82973999999999,"Lag",0.98935426598749199,19.5383264717501]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",118.80809000000001,"Lag",0.98915572384723505,17.640708425636198]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",133.68135000000001,"Lag",0.98917206198490903,19.833896240085899]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",119.2255,"Lag",0.98894402878117305,17.877515797562001]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",136.38686000000001,"Lag",0.98901977304881805,20.379464358665398]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",121.65553,"Lag",0.98877183834154503,18.385801868782998]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",138.50658999999999,"Lag",0.98884914435666904,20.8590926580294]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",123.80653,"Lag",0.98858373137079203,18.869662089233501]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",141.68823,"Lag",0.98869492346898702,21.487817494906299]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",126.40797999999999,"Lag",0.98840400857278798,19.419866993422399]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",144.71429000000001,"Lag",0.98855314641416003,22.086304767226501]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",129.30833999999999,"Lag",0.98824760709221604,20.001342673783299]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",147.69969,"Lag",0.98843882627985102,22.656189486068101]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",132.11405999999999,"Lag",0.98812120041269302,20.546910424898201]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",151.15731,"Lag",0.98834020181719695,23.287000736214601]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",135.05534,"Lag",0.98800595625777299,21.107842873196699]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",154.11371,"Lag",0.98822305214112904,23.863559490116]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",137.71886000000001,"Lag",0.98787357244546803,21.644764753167799]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",90.202889999999996,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",88.289829999999995,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",91.238640000000004,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",89.30077,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",93.533590000000004,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",91.593170000000001,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",96.822280000000006,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",94.869950000000003,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",100.70283000000001,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",98.734129999999993,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",104.81178,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",102.8361,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",108.66694,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",106.64601,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",112.47734,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",110.39716,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",116.64979,"Lag","NA","NA"]
["VIC","ERTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",114.45771000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",53.9452,"Lag",0.989404704708303,7.9158387585468404]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",46.786929999999998,"Lag",0.98915535789243303,6.9470752869899597]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",54.373040000000003,"Lag",0.98922598484031699,8.0467211625418305]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",47.12218,"Lag",0.98894527934876997,7.0654270362553104]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",55.133569999999999,"Lag",0.989085078826627,8.2133332830418304]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",47.66142,"Lag",0.98877484254803705,7.2020909054849902]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",56.647770000000001,"Lag",0.98897675240918104,8.4813770310324195]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",49.002099999999999,"Lag",0.98864939413169395,7.4466513484892403]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",57.96837,"Lag",0.98884658543931403,8.7310552189409592]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",50.28302,"Lag",0.98850394864508495,7.6909594491348896]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",59.873220000000003,"Lag",0.98876236880768698,9.0525205683624801]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",51.892040000000001,"Lag",0.98840317100862396,7.9723886867876903]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",61.685319999999997,"Lag",0.98866509643504596,9.3674710655441107]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",53.597329999999999,"Lag",0.98829636303354995,8.2728840675240107]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",63.410449999999997,"Lag",0.98857639533488595,9.6677034745189392]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",55.195509999999999,"Lag",0.988197994046355,8.5559357159639404]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",65.366810000000001,"Lag",0.98853072958101695,9.98622085051705]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",56.892949999999999,"Lag",0.98814442063528996,8.8394121898927605]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",67.142799999999994,"Lag",0.98847887342742002,10.2811103643138]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",58.510770000000001,"Lag",0.98808767288343302,9.1128957888111408]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",34.563630000000003,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",33.110669999999999,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",35.161850000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",33.68477,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",36.256129999999999,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",34.755049999999997,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",37.751840000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",36.216700000000003,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",39.52948,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",37.955120000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",41.45628,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",39.845840000000003,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",43.289589999999997,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",41.631160000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",45.086860000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",43.376860000000001,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",47.017829999999996,"Lag","NA","NA"]
["VIC","ERTS3466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",45.234180000000002,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",156.06542999999999,"Lag",0.989610356611758,22.673930894520801]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",153.57675,"Lag",0.98958764218878004,22.3371257340009]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",156.88323,"Lag",0.98944378249891896,22.977638846059701]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",154.38585,"Lag",0.989418228171564,22.639656272253902]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",158.35532000000001,"Lag",0.98928165581487504,23.3735506456647]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",155.49530999999999,"Lag",0.98924938919312699,22.986491591411699]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",161.89538999999999,"Lag",0.989151148284654,24.043495231884599]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",159.08345,"Lag",0.98911764484532205,23.662941724373699]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",164.73929999999999,"Lag",0.98901267401179105,24.624087145257398]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",162.3031,"Lag",0.98898196706304298,24.294384358214401]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",168.87116,"Lag",0.98890081330966195,25.3720111400124]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",166.12844000000001,"Lag",0.98886501993989295,25.000825511542299]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",172.58680000000001,"Lag",0.98877975469568202,26.073692047592701]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",170.08138,"Lag",0.98874586564470601,25.734621381508799]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",176.11031,"Lag",0.98867461153605796,26.732514925606299]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",173.72784999999999,"Lag",0.98864147680857795,26.410085033964101]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",180.10767999999999,"Lag",0.98859011527930696,27.442851450268002]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",177.46446,"Lag",0.98855273623798301,27.085131640413302]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",183.54338999999999,"Lag",0.98849501300861398,28.084686811774599]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",180.88550000000001,"Lag",0.98845659021343202,27.724981639517001]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",142.24054000000001,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",139.18358000000001,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",144.05157,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",140.94533999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",147.63794999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",144.51871,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",152.65603999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",149.50952000000001,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",158.40478999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",155.22385,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",164.35434000000001,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",161.1534,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",169.81326999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",166.53222,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",175.13285999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",171.75111000000001,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",180.84569999999999,"Lag","NA","NA"]
["VIC","ERTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"ERTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"East Rowville 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",177.28296,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe10",223.79678000000001,"Lag",0.960601235504566,64.751022400831999]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe50",215.08510000000001,"Lag",0.96053161266330001,62.288845077059797]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe10",225.58566999999999,"Lag",0.96016064223299402,65.655272035780598]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe50",216.81603999999999,"Lag",0.96007292483277296,63.176716335402197]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe10",228.06878,"Lag",0.95963480928976697,66.842228922512007]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe50",218.71662000000001,"Lag",0.95951901320569499,64.1990330888393]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe10",233.28791000000001,"Lag",0.95912180884684195,68.832734146714998]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe50",223.86358000000001,"Lag",0.95898554065723796,66.169140945662306]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe10",237.40734,"Lag",0.95856086907933402,70.558331430580296]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe50",228.39395999999999,"Lag",0.95841020174397795,68.010884801854004]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe10",243.38043999999999,"Lag",0.95806832990429602,72.7904139772549]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe50",233.7784,"Lag",0.95789045785063898,70.076594696708099]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe10",248.52925999999999,"Lag",0.95748116174240305,74.883611099368807]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe50",239.11004,"Lag",0.95728638598308402,72.221462134803701]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe10",253.31347,"Lag",0.95693343922763496,76.848372765919706]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe50",243.92314999999999,"Lag",0.95672094322615397,74.194391792448997]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe10",259.71980000000002,"Lag",0.95662480630111901,79.092975222032806]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe50",249.80946,"Lag",0.95639291087253298,76.292021282164299]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe10",265.6123,"Lag",0.95636750942388504,81.143472955275499]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe50",255.55464000000001,"Lag",0.95612675887655096,78.300882044887203]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe10",213.20331999999999,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe50",208.18631999999999,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe10",216.40736999999999,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe50",211.30793,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe10",222.24166,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe50",217.11036999999999,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe10",230.16212999999999,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe50",224.97526999999999,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe10",239.25577000000001,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe50",234.00089,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe10",248.66711000000001,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe50",243.36627999999999,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe10",257.36189000000002,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe50",251.92626000000001,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe10",266.02334000000002,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe50",260.41753999999997,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe10",275.59321999999997,"Lag","NA","NA"]
["VIC","FBTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Citipower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe50",269.68846000000002,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",15.99207,"Lag",0.96196672403212002,4.5412176663629902]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",15.43529,"Lag",0.96195452837705597,4.3838552413967502]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",16.250610000000002,"Lag",0.96189585595640104,4.6191885933971299]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",15.69088,"Lag",0.96188125680951497,4.4609924115544697]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",16.562860000000001,"Lag",0.96178853283855603,4.7149673372781402]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",15.962490000000001,"Lag",0.96176908263295502,4.5452850946024199]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",17.047609999999999,"Lag",0.96169659151603304,4.8591471871467604]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",16.445799999999998,"Lag",0.96167428214153905,4.6890579580635796]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",17.45786,"Lag",0.96161015290825502,4.9820319441429]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",16.890360000000001,"Lag",0.96158674409800304,4.8216397314766004]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",17.99588,"Lag",0.961531280929251,5.1411603911245098]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",17.389320000000001,"Lag",0.96150420520083901,4.9697286721555702]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",18.494309999999999,"Lag",0.96145826398419099,5.2888697091366899]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",17.906580000000002,"Lag",0.96143036886458999,5.1227599027043302]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",18.94613,"Lag",0.96134494617361699,5.4265198617189796]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",18.36523,"Lag",0.96131444402479205,5.2623404144276096]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",19.431000000000001,"Lag",0.96125868960275895,5.57197894364253]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",18.815989999999999,"Lag",0.96122431945444498,5.3981590058242004]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",19.869810000000001,"Lag",0.96120798324109902,5.7017654852237296]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",19.248259999999998,"Lag",0.96117237116140797,5.5260971508047998]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",13.893280000000001,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",13.615410000000001,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",14.15903,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",13.875360000000001,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",14.574070000000001,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",14.288830000000001,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",15.10563,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",14.818049999999999,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",15.70646,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",15.41597,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",16.32038,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",16.028479999999998,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",16.883600000000001,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",16.584219999999998,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",17.417249999999999,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",17.108470000000001,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",17.982379999999999,"Lag","NA","NA"]
["VIC","FBTS66P",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"FBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Fishermans Bend (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",17.656410000000001,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",104.47358,"Lag",0.99242992327686397,12.928504616466499]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",94.430790000000002,"Lag",0.99234005564279704,11.75567691482]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",104.32599,"Lag",0.99227934140813101,13.0394974844438]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",94.221770000000006,"Lag",0.99217153293258098,11.859495799699699]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",105.01656,"Lag",0.99218664257457101,13.2052999361734]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",94.617720000000006,"Lag",0.992065219926895,11.990891627626601]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",106.59335,"Lag",0.99201847258522402,13.548775217318701]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",96.022919999999999,"Lag",0.99187684675090304,12.314328104283801]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",108.43912,"Lag",0.99194730512350104,13.845445268708399]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",97.959649999999996,"Lag",0.99180140922172899,12.621620742398999]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",110.0937,"Lag",0.99172219268953499,14.2542533423713]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",99.196659999999994,"Lag",0.99154523580737097,12.981663715589301]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",111.65551000000001,"Lag",0.99151405380644098,14.6393943536322]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",100.69653,"Lag",0.99131362623042096,13.3595711843943]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",114.29405,"Lag",0.99150073004575101,14.997249982977999]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",103.26961,"Lag",0.99130256397834904,13.709782194929099]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",117.21411000000001,"Lag",0.99148238088674301,15.397217171664799]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",105.86682999999999,"Lag",0.99128121634774802,14.0720471419879]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",119.85612,"Lag",0.99146287834642799,15.7625181267339]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",108.36136,"Lag",0.99126149122438501,14.420124932036201]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",89.803939999999997,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",87.845119999999994,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",90.59057,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",88.611819999999994,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",92.614379999999997,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",90.637240000000006,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",95.609930000000006,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",93.624669999999995,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",99.171999999999997,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",97.174019999999999,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",102.93814999999999,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",100.93671999999999,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",106.4238,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",104.38171,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",109.84175,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",107.74585,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",113.58284999999999,"Lag","NA","NA"]
["VIC","GNTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GNTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Glenrowan (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",111.38231,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",213.81457,"Lag",0.99313082107599304,25.1913332335603]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",190.34751,"Lag",0.99306507508491304,22.534665331691599]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",215.35300000000001,"Lag",0.99305221200509797,25.5188712036902]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",191.64416,"Lag",0.99297607383724795,22.8348317791291]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",218.34164000000001,"Lag",0.99297796070450595,26.0123647087355]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",193.89242999999999,"Lag",0.99289051183606802,23.244509194110002]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",224.84720999999999,"Lag",0.99291914887444399,26.9005517919102]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",199.92214999999999,"Lag",0.99282494879915995,24.078826068528102]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",231.02923000000001,"Lag",0.99285565771171802,27.765139796764601]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",206.16435999999999,"Lag",0.99275642345562398,24.950228085918098]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",239.56057999999999,"Lag",0.99279806370735602,28.907512250316501]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",213.75665000000001,"Lag",0.99269133995964098,25.986291075910099]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",248.42419000000001,"Lag",0.99275559950296099,30.0662858449457]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",222.47053,"Lag",0.99264718490569903,27.1281139794451]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",257.18376000000001,"Lag",0.99271713759917102,31.209865875866701]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",230.99507,"Lag",0.99260712272813101,28.245086644254801]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",266.93184000000002,"Lag",0.99268553783778102,32.463793604006902]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",239.93907999999999,"Lag",0.99257256259985505,29.407986908372798]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",276.08087999999998,"Lag",0.99265346766522899,33.650827892210998]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",248.68648999999999,"Lag",0.99253905717705004,30.5495533139608]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",169.92777000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",166.31502,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",172.22711000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",168.55577,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",177.40835000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",173.71804,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",184.8074,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",181.07957999999999,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",193.85784000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",190.08261999999999,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",203.84954999999999,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",200.04463999999999,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",213.71641,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",209.80698000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",223.67497,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",219.63336000000001,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",234.50518,"Lag","NA","NA"]
["VIC","GTS1266",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 12 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",230.22557,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",299.85685999999998,"Lag",0.99298257756943398,35.711897113051201]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",261.00902000000002,"Lag",0.99288002702238398,31.313995987604201]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",301.75272000000001,"Lag",0.99288173317688999,36.1977492797037]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",262.48595,"Lag",0.99276269460355604,31.7524217666254]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",305.43086,"Lag",0.99278567464001499,36.888039287747901]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",265.03041999999999,"Lag",0.99264876312631001,32.314370827814201]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",313.72559000000001,"Lag",0.99270802926582302,38.095414559891097]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",272.45576,"Lag",0.99255938195112903,33.423323864398]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",321.17493999999999,"Lag",0.99262270420945498,39.230024798490398]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",279.78268000000003,"Lag",0.99246393805366095,34.544074000742199]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",331.55227000000002,"Lag",0.99254590554373601,40.710179498694202]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",288.61428000000001,"Lag",0.99237387254461096,35.849239108046199]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",342.13076000000001,"Lag",0.99248582185068401,42.179961039117302]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",298.72320000000002,"Lag",0.99230832119560097,37.265861388354097]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",352.45866999999998,"Lag",0.99243076890125603,43.613955894063302]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",308.47573999999997,"Lag",0.99224805647070802,38.634719536328703]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",364.03786000000002,"Lag",0.99238529796034103,45.1834462316775]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",318.69078999999999,"Lag",0.99219587896150496,40.049777791199901]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",374.73079000000001,"Lag",0.99233861935481504,46.654612009927199]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",328.57873999999998,"Lag",0.99214446037378201,41.429813085799601]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",212.86181999999999,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",207.27341000000001,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",215.98652999999999,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",210.31451000000001,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",222.55481,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",216.83678,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",231.79656,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",225.99981,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",242.95068000000001,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",237.05893,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",255.13305,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",249.16839999999999,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",267.06007,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",260.93387999999999,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",279.04777999999999,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",272.72732000000002,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",292.07096000000001,"Lag","NA","NA"]
["VIC","GTS3466",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"GTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Geelong 34 (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",285.42216999999999,"Lag","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",92.932460000000006,"Lag",0.99922003832136097,3.6725966130235399]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",80.812330000000003,"Lag",0.99921283785163595,3.20834631390326]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",93.079369999999997,"Lag",0.99921487050364,3.6905826013898801]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",80.937899999999999,"Lag",0.99920686462113395,3.2255148934313098]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",93.619590000000002,"Lag",0.99920951003367697,3.7246675168957202]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",81.233490000000003,"Lag",0.999200521525755,3.2502294844708399]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",95.509169999999997,"Lag",0.999206583623655,3.8068801189164798]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",82.958590000000001,"Lag",0.99919720328091499,3.3261418331775401]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",96.625990000000002,"Lag",0.99919566276958105,3.8778423791273702]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",84.122910000000005,"Lag",0.99918474611782704,3.3989235366789101]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",98.625600000000006,"Lag",0.99918807043992797,3.9767511966399098]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",85.744470000000007,"Lag",0.99917583302046997,3.48335150080272]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",100.59529999999999,"Lag",0.999183613896511,4.0673030318637302]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",87.657820000000001,"Lag",0.99917089570442097,3.5717449017229899]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",102.39270999999999,"Lag",0.99917951985467102,4.1503569423704603]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",89.365359999999995,"Lag",0.999166325173095,3.6513564255241402]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",104.19011999999999,"Lag",0.99917112861142399,4.2447803452902297]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",90.835350000000005,"Lag",0.99915650621566299,3.7332383100824802]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",105.75578,"Lag",0.99916344558778503,4.3285139738351104]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",92.234179999999995,"Lag",0.99914765926653304,3.8105816707505098]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",86.281649999999999,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",82.677139999999994,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",86.797669999999997,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",83.170990000000003,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",88.440119999999993,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",84.791200000000003,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",90.971509999999995,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",87.275199999999998,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",93.976690000000005,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",90.221950000000007,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",97.119860000000003,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",93.315309999999997,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",99.994619999999998,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",96.113259999999997,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",102.73909,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",98.772180000000006,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",105.75057,"Lead","NA","NA"]
["VIC","HOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Horsham (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",101.64794000000001,"Lead","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",397.27291000000002,"Lag",0.99536041587042301,38.4024373583404]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",351.18106999999998,"Lag",0.99529936479516701,34.171156496409502]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",397.73104999999998,"Lag",0.99528064925693904,38.778147603494702]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",351.28874000000002,"Lag",0.99520797473547096,34.514693215757902]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",399.71078,"Lag",0.99519178125252605,39.339017820956499]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",351.96221000000003,"Lag",0.99510430637148495,34.955647349620001]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",407.2867,"Lag",0.99511335677562596,40.412598578147502]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",358.63177000000002,"Lag",0.99501440628237003,35.946023276584597]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",413.32472000000001,"Lag",0.99503240609542998,41.352538551005303]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",364.69896,"Lag",0.99492344193851801,36.888641087054097]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",422.7987,"Lag",0.99496360088296398,42.594547396536001]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",372.37441000000001,"Lag",0.99484273113420996,37.965542929509901]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",431.50087000000002,"Lag",0.99489361689406597,43.774540785780303]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",380.62182000000001,"Lag",0.99476400866451198,39.103788857928699]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",439.64335,"Lag",0.99482667026684801,44.8942532070336]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",388.14843999999999,"Lag",0.99468820561667104,40.1669646637718]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",449.76515999999998,"Lag",0.99478167334412004,46.128714349742097]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",396.68790000000001,"Lag",0.99463531733231603,41.256164361680597]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",458.97654999999997,"Lag",0.99474039585131602,47.260734118290898]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",405.01002999999997,"Lag",0.99458850568897295,42.306549098534397]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",249.60032000000001,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",243.89590000000001,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",251.93474000000001,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",246.16740999999999,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",257.79019,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",252.01575,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",266.42378000000002,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",260.61187999999999,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",276.73576000000003,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",270.87205999999998,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",287.74639999999999,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",281.85633000000001,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",298.05959999999999,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",292.04009000000002,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",308.24315000000001,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",302.05741,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",319.40631999999999,"Lag","NA","NA"]
["VIC","HTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Heatherton (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",312.91030000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",1.2633799999999999,"Lag",0.974193339617211,0.292718105632369]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",1.25,"Lag",0.97417773022684195,0.28970910665237798]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",1.2608699999999999,"Lag",0.97404383889419399,0.293015392529059]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",1.2475099999999999,"Lag",0.97402657842733498,0.29001089130538998]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",1.25943,"Lag",0.97389632075698496,0.29354476513802202]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",1.24607,"Lag",0.97387741310958498,0.290540263914353]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",1.2574099999999999,"Lag",0.97375526299628001,0.29389679836412602]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",1.24407,"Lag",0.97373479362552195,0.29089679489678]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",1.2545299999999999,"Lag",0.97344455574244504,0.29502517794231498]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",1.2412000000000001,"Lag",0.97342060150362997,0.29202742335313098]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",1.2514000000000001,"Lag",0.97316905193309,0.29587482783145203]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",1.2380899999999999,"Lag",0.97314199512205701,0.29288157099859102]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",1.25108,"Lag",0.97305696655759,0.29644209405951]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",1.23777,"Lag",0.97302864639384701,0.293448837226648]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",1.2493099999999999,"Lag",0.97288003810638002,0.297033751640434]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",1.2360199999999999,"Lag",0.97284973326584001,0.29404499256389599]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",1.2488900000000001,"Lag",0.97274906149060902,0.29768025038902801]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",1.2356,"Lag",0.97271727148749199,0.29469149131248901]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",1.24617,"Lag",0.97247636364572299,0.298577479115755]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",1.2329000000000001,"Lag",0.97244147033006501,0.29559321779553899]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",1.3411500000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",1.2997700000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",1.33985,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",1.2985,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",1.33894,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",1.29762,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",1.3381799999999999,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",1.2968999999999999,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",1.3371299999999999,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",1.2958799999999999,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",1.33708,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",1.29586,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",1.3371299999999999,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",1.2959499999999999,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",1.3371599999999999,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",1.2960100000000001,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",1.33727,"Lag","NA","NA"]
["VIC","HYTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"HYTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Heywood (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",1.29616,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",14.328480000000001,"Lag",0.92901179393865296,5.7074147918958804]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",13.54637,"Lag",0.92880330757489604,5.4047182680885504]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",14.35511,"Lag",0.928658584479639,5.73388509321207]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",13.574529999999999,"Lag",0.92843025240948296,5.4317807184393097]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",14.418900000000001,"Lag",0.92805530738210895,5.7865191630214996]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",13.606159999999999,"Lag",0.92778133597509704,5.4719680477574499]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",14.68943,"Lag",0.92759688726552203,5.9160575273340399]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",13.873710000000001,"Lag",0.92729964413926802,5.6003530760418796]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",14.93882,"Lag",0.92740993418551898,6.0251823109425997]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",14.15288,"Lag",0.92711856799340298,5.7210034794212898]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",15.285920000000001,"Lag",0.92705996905503196,6.18179132103878]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",14.465960000000001,"Lag",0.92674222363213798,5.8644458815723999]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",15.620100000000001,"Lag",0.92685151560760004,6.3270379006913]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",14.81631,"Lag",0.92653580130929203,6.0159506637667102]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",15.88974,"Lag",0.92637080169102104,6.4599166180029197]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",15.09198,"Lag",0.92603706313921297,6.1511631449204502]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",16.217099999999999,"Lag",0.92600267150524695,6.6114606598149503]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",15.39059,"Lag",0.92564325262397096,6.2915802032397901]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",16.53415,"Lag",0.92587575207695405,6.7471978522411797]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",15.70316,"Lag",0.92551465921339304,6.42558352136873]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",10.255739999999999,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",9.9360900000000001,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",10.32137,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",9.9995899999999995,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",10.526999999999999,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",10.204359999999999,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",10.843669999999999,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",10.51816,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",11.2232,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",10.89392,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",11.625730000000001,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",11.29373,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",12.0016,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",11.66315,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",12.363329999999999,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",12.01713,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",12.76205,"Lag","NA","NA"]
["VIC","KGTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Kerang (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",12.402189999999999,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",56.036549999999998,"Lag",0.999952156649766,0.548166843077868]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",54.571370000000002,"Lag",0.999952156649766,0.53383399969010004]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",56.316130000000001,"Lag",0.999952156649766,0.55090178100655396]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",54.868070000000003,"Lag",0.999952156649766,0.53673641074754697]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",56.832999999999998,"Lag",0.999952156649766,0.55595796301957301]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",55.274590000000003,"Lag",0.999952156649766,0.54071311497091601]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",58.120269999999998,"Lag",0.999952156649766,0.56855043582685405]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",56.590310000000002,"Lag",0.999952156649766,0.55358389446705603]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",59.187220000000003,"Lag",0.999952156649766,0.57898767033222498]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",57.80668,"Lag",0.999952156649766,0.56548280157169795]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",60.715699999999998,"Lag",0.999952156649766,0.59393973387481702]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",59.238999999999997,"Lag",0.999952156649766,0.57949419828825699]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",62.119300000000003,"Lag",0.999952156649766,0.607670182679108]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",60.743729999999999,"Lag",0.999952156649766,0.59421393199392802]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",63.393630000000002,"Lag",0.999952156649766,0.62013607240892599]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",62.078209999999999,"Lag",0.999952156649766,0.60726822760546295]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",64.858530000000002,"Lag",0.999952156649766,0.63446617675019601]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",63.464100000000002,"Lag",0.999952156649766,0.62082543171872795]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",66.160169999999994,"Lag",0.999952156649766,0.64719922133670005]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",64.776759999999996,"Lag",0.999952156649766,0.63366627734956404]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",35.526000000000003,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",33.360950000000003,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",35.76397,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",33.584629999999997,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",36.464599999999997,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",34.262509999999999,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",37.531289999999998,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",35.289560000000002,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",38.789929999999998,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",36.501190000000001,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",40.102800000000002,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",37.770449999999997,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",41.307070000000003,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",38.92313,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",42.462699999999998,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",40.024419999999999,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",43.735300000000002,"Lag","NA","NA"]
["VIC","KGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Kerang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",41.220120000000001,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe10",267.45915000000002,"Lag",0.98138683711694896,52.337377459219397]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe50",247.49704,"Lag",0.98127776741778305,48.576872582646601]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe10",273.54413,"Lag",0.98117136725353704,53.845938058782899]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe50",253.56488999999999,"Lag",0.98104718858435003,50.082206196258397]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe10",335.29180000000002,"Lag",0.98121991858357005,65.913087411624105]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe50",316.35045000000002,"Lag",0.98112861291355202,62.344875481929698]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe10",342.55662000000001,"Lag",0.981006370009194,67.734114893984795]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe50",323.37427000000002,"Lag",0.98090271443166699,64.120502870049094]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe10",348.48383999999999,"Lag",0.98078847237216205,69.3118180727203]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe50",329.79160999999999,"Lag",0.98067650697091102,65.790535900193404]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe10",356.84703000000002,"Lag",0.98056526769837005,71.398558090754506]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe50",337.15233000000001,"Lag",0.980436150261074,67.688428480576107]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe10",364.72622000000001,"Lag",0.98036261587194395,73.365928989632195]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe50",345.18265000000002,"Lag",0.98022534887641399,69.684269571332095]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe10",372.63904000000002,"Lag",0.98022527289113304,75.227218751760304]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe50",353.06146000000001,"Lag",0.98008276194322297,71.539152457090296]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe10",381.65253000000001,"Lag",0.98010253530508795,77.292854122147702]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe50",361.21141,"Lag",0.97994970294620698,73.442112319672404]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe10",389.69290000000001,"Lag",0.97997976099591499,79.171776709175205]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe50",368.93691999999999,"Lag",0.979820460405462,75.261720908057498]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe10",189.90008,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe50",185.61819,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe10",192.29472000000001,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe50",187.95143999999999,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe10",256.41595999999998,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe50",251.76179999999999,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe10",265.03874000000002,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe50",260.37070999999997,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe10",275.12765999999999,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe50",270.43628000000001,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe10",285.70487000000003,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe50",281.01575000000003,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe10",295.47746999999998,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe50",290.68315999999999,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe10",305.05955,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe50",300.12157999999999,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe10",315.53203000000002,"Lag","NA","NA"]
["VIC","KTSEJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe50",310.31009999999998,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",76.716719999999995,"Lag",0.98067487658206598,15.3049780648986]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",67.338650000000001,"Lag",0.98038254730974395,13.5383172275502]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",77.051360000000003,"Lag",0.98037238794165205,15.495172012313899]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",67.587739999999997,"Lag",0.98003358262144602,13.7123950834205]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",78.043490000000006,"Lag",0.98010876048302997,15.8029387637069]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",68.318870000000004,"Lag",0.97972427923124605,13.9709940978966]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",80.418149999999997,"Lag",0.97988479498294601,16.378014496741699]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",70.507620000000003,"Lag",0.97947138238908904,14.5110477084402]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",82.810720000000003,"Lag",0.97965283048007401,16.9652741619336]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",72.913399999999996,"Lag",0.97921972590482997,15.1007959016193]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",86.281630000000007,"Lag",0.97949591797925595,17.746519110523401]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",76.045060000000007,"Lag",0.97904358071442199,15.818132211323899]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",89.977199999999996,"Lag",0.97937760237961002,18.5616342319342]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",79.689499999999995,"Lag",0.97892731809204003,16.623615354234499]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",93.740889999999993,"Lag",0.97930299697943901,19.3741144778459]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",83.379300000000001,"Lag",0.97885955603705799,17.422176044280999]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",97.860659999999996,"Lag",0.97922011397449704,20.267325539332798]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",87.211039999999997,"Lag",0.97877339724747603,18.261127399774999]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",101.80162,"Lag",0.97914390457105505,21.123377169702401]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",91.013369999999995,"Lag",0.97870049967668105,19.091063614938601]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",72.599450000000004,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",70.945639999999997,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",73.592100000000002,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",71.915270000000007,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",75.879710000000003,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",74.194680000000005,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",79.174539999999993,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",77.471770000000006,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",83.220889999999997,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",81.495810000000006,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",87.718170000000001,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",85.978480000000005,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",92.169749999999993,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",90.383920000000003,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",96.695819999999998,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",94.851650000000006,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",101.64245,"Lag","NA","NA"]
["VIC","KTSEP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor East (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",99.693430000000006,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe10",143.68262999999999,"Lag",0.98155069348129098,27.988791788986401]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe50",134.43530000000001,"Lag",0.98146934041468104,26.246760031808499]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe10",145.33327,"Lag",0.98140163524426205,28.427712003410502]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe50",135.98848000000001,"Lag",0.98130978082186004,26.667320523474299]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe10",147.70283000000001,"Lag",0.981275330492408,28.991950357829001]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe50",137.92411999999999,"Lag",0.98117127261599502,27.1498161024025]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe10",152.17419000000001,"Lag",0.98118475124493099,29.943852799108001]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe50",142.23157,"Lag",0.98107557389157396,28.070840828133399]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe10",156.09056000000001,"Lag",0.98108215041375502,30.8005442735755]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe50",146.31626,"Lag",0.98097068435472301,28.959240783359]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe10",161.32073,"Lag",0.98100364244226002,31.9004906949062]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe50",151.04936000000001,"Lag",0.98088460261803301,29.965548097451101]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe10",166.34523999999999,"Lag",0.98093429441478897,32.955805898027599]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe50",156.09641999999999,"Lag",0.98081460135833398,31.025111317689301]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe10",171.05894000000001,"Lag",0.98085457841483903,33.962520745577699]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe50",160.74194,"Lag",0.98073221663694798,32.018982271358198]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe10",176.43561,"Lag",0.98080244399002203,35.0790850374377]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe50",165.67060000000001,"Lag",0.98067501157163095,33.0511494834629]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe10",181.37524999999999,"Lag",0.98075513025398897,36.106909565970803]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe50",170.41821999999999,"Lag",0.98062584595678404,34.0428008746674]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe10",118.05571,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe50",115.34506,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe10",119.98567,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe50",117.22629000000001,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe10",123.50864,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe50",120.72743,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe10",128.32812000000001,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe50",125.51069,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe10",133.89521999999999,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe50",131.03469000000001,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe10",139.74109000000001,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe50",136.84971999999999,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe10",145.21889999999999,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe50",142.24638999999999,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe10",150.64471,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe50",147.57227,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe10",156.55659,"Lag","NA","NA"]
["VIC","KTSWJ",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe50",153.31254999999999,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",149.00532999999999,"Lag",0.98151123698703702,29.057532031285401]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",138.68186,"Lag",0.98142015924223003,27.112774724660301]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",150.04369,"Lag",0.981338391332091,29.400371161806099]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",139.65403000000001,"Lag",0.98123406290426796,27.443144841746101]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",151.99136999999999,"Lag",0.98118554358140397,29.907230753502802]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",141.19354999999999,"Lag",0.98106615204397296,27.8731143817187]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",156.26820000000001,"Lag",0.98105207573409203,30.860809574462099]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",145.32876999999999,"Lag",0.98092409098463795,28.800016408713301]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",160.16649000000001,"Lag",0.98090908175548996,31.753279284557902]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",149.43592000000001,"Lag",0.98077626389142503,29.7318316112706]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",165.63994,"Lag",0.98080334943047798,32.931880809744598]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",154.44322,"Lag",0.98066121537668305,30.822618804795201]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",171.10050000000001,"Lag",0.98071473775653395,34.098267843869301]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",159.98036999999999,"Lag",0.98057199934509798,32.003434026546202]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",176.48356999999999,"Lag",0.98064960940734403,35.232147448449801]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",165.36062000000001,"Lag",0.98050687709378503,33.136782393509399]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",182.47307000000001,"Lag",0.98057916595864203,36.496074868226003]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",170.9502,"Lag",0.98043113124686698,34.3253720303439]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",188.04993999999999,"Lag",0.98051217212949804,37.678246690294202]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",176.39254,"Lag",0.98036236129524801,35.482200803954498]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",118.98851000000001,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",116.40845,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",120.53231,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",117.9165,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",123.94891,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",121.32447999999999,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",128.84123,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",126.19427,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",134.70374000000001,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",132.02780000000001,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",141.05189999999999,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",138.35954000000001,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",147.17671000000001,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",144.41663,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",153.33342999999999,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",150.48622,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",160.06862000000001,"Lag","NA","NA"]
["VIC","KTSWP",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"KTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Keilor West (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",157.06143,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",10.143599999999999,"Lag",0.98271480931916499,1.91087301222187]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",10,"Lag",0.98271480931916499,1.8838213378109101]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",10.143599999999999,"Lag",0.98271480931916499,1.91087301222187]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",10,"Lag",0.98271480931916499,1.8838213378109101]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",10.143599999999999,"Lag",0.98271480931916499,1.91087301222187]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",10,"Lag",0.98271480931916499,1.8838213378109101]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",10.143599999999999,"Lag",0.98271480931916499,1.91087301222187]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",10,"Lag",0.98271480931916499,1.8838213378109101]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",10.143599999999999,"Lag",0.98271480931916499,1.91087301222187]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",10,"Lag",0.98271480931916499,1.8838213378109101]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",10.143599999999999,"Lag",0.98271480931916499,1.91087301222187]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",10,"Lag",0.98271480931916499,1.8838213378109101]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",10.143599999999999,"Lag",0.98271480931916499,1.91087301222187]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",10,"Lag",0.98271480931916499,1.8838213378109101]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",10.143599999999999,"Lag",0.98271480931916499,1.91087301222187]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",10,"Lag",0.98271480931916499,1.8838213378109101]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",10.143599999999999,"Lag",0.98271480931916499,1.91087301222187]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",10,"Lag",0.98271480931916499,1.8838213378109101]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",10.143599999999999,"Lag",0.98271480931916499,1.91087301222187]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",10,"Lag",0.98271480931916499,1.8838213378109101]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",10.43905,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",10,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",10.43905,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",10,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",10.43905,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",10,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",10.43905,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",10,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",10.43905,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",10,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",10.43905,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",10,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",10.43905,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",10,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",10.43905,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",10,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",10.43905,"Lag","NA","NA"]
["VIC","LY66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"LY"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Loy Yang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",10,"Lag","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",16.98828,"Lead",0.95219942067486596,-5.4500459932932896]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",13.461959999999999,"Lead",0.94832110422019,-4.5044291508441603]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",16.581240000000001,"Lead",0.94730799622047601,-5.60680540018698]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",13.02054,"Lead",0.94170121134434703,-4.6519692279426597]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",16.291060000000002,"Lead",0.94245933809230797,-5.7789656921739798]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",12.656280000000001,"Lead",0.93490916020347303,-4.8042642508421496]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",16.623010000000001,"Lead",0.94185832587954599,-5.9302994277243899]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",12.91742,"Lead",0.93410981216998401,-4.9366095994583601]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",16.841809999999999,"Lead",0.94052179882181397,-6.0835638899321198]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",13.1068,"Lead",0.93236715393149305,-5.0819848038832296]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",17.267600000000002,"Lead",0.940035231887423,-6.2652836335839499]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",13.426220000000001,"Lead",0.93167910959589295,-5.2351804023833797]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",17.504349999999999,"Lead",0.93790969400968704,-6.4738648911621404]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",13.605,"Lead",0.92880081607518905,-5.4282164433173596]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",17.756779999999999,"Lead",0.93619854689426896,-6.6663249762134296]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",13.79954,"Lead",0.92648788848209895,-5.6051527644988504]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",18.190429999999999,"Lead",0.93582517797210296,-6.8511526389231099]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",14.139150000000001,"Lead",0.92599236668825302,-5.7647626909100902]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",18.53734,"Lead",0.93501833005968005,-7.0301609239946004]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",14.420719999999999,"Lead",0.92494194959613496,-5.9262494224964604]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",29.121569999999998,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",28.03002,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",29.364360000000001,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",28.263269999999999,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",30.004159999999999,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",28.89489,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",30.956150000000001,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",29.831209999999999,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",32.084820000000001,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",30.940860000000001,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",33.272640000000003,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",32.112540000000003,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",34.36739,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",33.181229999999999,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",35.438490000000002,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",34.222769999999997,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",36.609229999999997,"Lead","NA","NA"]
["VIC","MBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Mt Beauty (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",35.346620000000001,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",43.600659999999998,"Lead",0.95073541786482296,-14.216738549067401]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",40.347360000000002,"Lead",0.95033842865459495,-13.213018702269901]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",43.605840000000001,"Lead",0.94979562073857304,-14.3641469771116]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",40.326450000000001,"Lead",0.949315383620979,-13.3523777494384]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",43.791800000000002,"Lead",0.94881390276933897,-14.577160991021699]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",40.384590000000003,"Lead",0.94822850325088603,-13.525956276053201]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",44.495199999999997,"Lead",0.94775574949182495,-14.976255290223]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",41.03,"Lead",0.94707510986192101,-13.9071592913534]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",45.027439999999999,"Lead",0.946679178096964,-15.3239258037321]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",41.601010000000002,"Lead",0.94592091493957298,-14.266791265059901]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",45.99738,"Lead",0.94588157389717697,-15.780730802311099]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",42.417909999999999,"Lead",0.94503250079157297,-14.6763798110049]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",46.88823,"Lead",0.94509465865603903,-16.2131051225691]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",43.303260000000002,"Lead",0.94419157691725797,-15.107057251431]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",47.776899999999998,"Lead",0.944466780043692,-16.622945154828201]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",44.165289999999999,"Lead",0.943519294600212,-15.5086782148311]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",48.807400000000001,"Lead",0.94389641923561096,-17.076276754624701]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",45.061540000000001,"Lead",0.94288181230100598,-15.920590520547]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",49.65437,"Lead",0.94320985823583403,-17.488214592137101]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",45.843609999999998,"Lead",0.94213321904681802,-16.312505176041999]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",36.0824,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",35.189509999999999,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",36.466529999999999,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",35.562829999999998,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",37.337980000000002,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",36.430819999999997,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",38.595669999999998,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",37.68009,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",40.073430000000002,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",39.147109999999998,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",41.628680000000003,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",40.695279999999997,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",43.072290000000002,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",42.117190000000001,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",44.49409,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",43.511980000000001,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",46.053609999999999,"Lead","NA","NA"]
["VIC","MTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Malvern (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",45.023420000000002,"Lead","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",216.18565000000001,"Lag",0.95385302312848297,68.055460290722607]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",197.11190999999999,"Lag",0.95355242076944902,62.267634859106899]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",216.91061999999999,"Lag",0.95329510938597695,68.725603418142796]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",197.70514,"Lag",0.95293744788862,62.897802180924202]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",218.29852,"Lag",0.95259683183696697,69.719077643088497]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",198.44265999999999,"Lag",0.95215598776126997,63.693922037811198]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",222.57548,"Lag",0.95190262276744497,71.643132479768497]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",202.38005999999999,"Lag",0.95139075719338895,65.514939190033004]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",226.18809999999999,"Lag",0.95124512352956003,73.340227809192399]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",206.15412000000001,"Lag",0.950679735628852,67.261022632835804]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",231.87151,"Lag",0.95073604818650903,75.605137473010004]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",211.02461,"Lag",0.95010836290297496,69.279256026038993]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",237.25360000000001,"Lag",0.95025359900446704,77.767773459314299]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",216.3398,"Lag",0.94959016344427505,71.421591561494395]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",242.54513,"Lag",0.94988195325750802,79.822284056611295]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",221.46532999999999,"Lag",0.94919129948787295,73.425730337551897]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",248.47761,"Lag",0.94951505673902603,82.097444424489595]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",226.68637000000001,"Lag",0.94878008183708495,75.485008003607206]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",253.82678000000001,"Lag",0.94916492303911504,84.178618982316294]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",231.69397000000001,"Lag",0.94839898828963298,77.462534953116105]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",136.02296000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",132.96360999999999,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",137.47290000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",134.37629999999999,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",140.87073000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",137.76783,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",145.80685,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",142.68154000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",151.69156000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",148.53618,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",157.98946000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",154.81798000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",163.93116000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",160.68672000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",169.81807000000001,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",166.4802,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",176.25570999999999,"Lag","NA","NA"]
["VIC","MTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Malvern (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",172.74494000000001,"Lag","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",392.40758,"Lag",0.99829971440230003,22.9122475167947]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",334.51823999999999,"Lag",0.99824723283948302,19.832086691136698]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",392.13824,"Lag",0.99825991164860195,23.1636610907529]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",333.73926,"Lag",0.99819911388372196,20.056383473589101]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",394.46926999999999,"Lag",0.99822741518682101,23.5185017723276]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",334.63513,"Lag",0.99815876730564301,20.3348625381449]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",402.42660000000001,"Lag",0.99819991113436901,24.178847329073299]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",341.34813000000003,"Lag",0.99812565494188898,20.929000110481301]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",409.22908000000001,"Lag",0.99817231600035605,24.775817332143799]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",347.87736000000001,"Lag",0.99809360455234097,21.511431099190698]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",418.68069000000003,"Lag",0.998140993513009,25.5649269668504]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",355.18184000000002,"Lag",0.99805477655004204,22.186296803778401]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",427.52791999999999,"Lag",0.998109481038011,26.326095963221899]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",363.20787000000001,"Lag",0.99801764865140996,22.903771605846799]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",436.65501,"Lag",0.998086993162137,27.0480218744081]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",371.42487999999997,"Lag",0.99799134590861704,23.577274218992098]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",447.58595000000003,"Lag",0.99807169548128705,27.836078277337901]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",380.48484000000002,"Lag",0.99797249731886495,24.265780008603599]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",456.44511999999997,"Lag",0.99804770703217804,28.563583304754399]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",388.13959999999997,"Lag",0.99794377941951595,24.929201104504799]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",327.40514999999999,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",319.62533000000002,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",330.83274999999998,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",322.95972999999998,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",339.00171,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",331.10419000000002,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",350.91397000000001,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",342.94864999999999,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",365.11487,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",357.06150000000002,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",380.27584000000002,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",372.16800000000001,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",394.54498999999998,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",386.24775,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",408.62993,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",400.09554000000003,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",423.98126000000002,"Lead","NA","NA"]
["VIC","MWTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"MWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Morwell (Ausnet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",415.01841999999999,"Lead","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",0.51878000000000002,"Lag",0.91195318247211699,0.233402841979893]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",0.47276000000000001,"Lag",0.91195318247211699,0.212698113987459]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",0.52148000000000005,"Lag",0.91195318247211699,0.23461759134059601]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",0.47543000000000002,"Lag",0.91195318247211699,0.213899366133044]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",0.52607999999999999,"Lag",0.91195318247211699,0.236687164325498]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",0.47876000000000002,"Lag",0.91195318247211699,0.21539755701124499]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",0.53737999999999997,"Lag",0.91195318247211699,0.241771115353627]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",0.48954999999999999,"Lag",0.91195318247211699,0.22025205538235201]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",0.54615999999999998,"Lag",0.91195318247211699,0.245721300311767]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",0.49901000000000001,"Lag",0.91195318247211699,0.22450817721652]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",0.55871000000000004,"Lag",0.91195318247211699,0.25136763530318401]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",0.50987000000000005,"Lag",0.91195318247211699,0.229394169089572]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",0.56976000000000004,"Lag",0.91195318247211699,0.25633910953865602]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",0.52100000000000002,"Lag",0.91195318247211699,0.23440163589869301]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",0.57952999999999999,"Lag",0.91195318247211699,0.26073470259571901]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",0.53058000000000005,"Lag",0.91195318247211699,0.23871174659333699]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",0.59087000000000001,"Lag",0.91195318247211699,0.26583664991067402]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",0.54042999999999997,"Lag",0.91195318247211699,0.24314333222405199]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",0.60065000000000002,"Lag",0.91195318247211699,0.27023674203944398]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",0.54959000000000002,"Lag",0.91195318247211699,0.24726448190702999]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",0.47087000000000001,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",0.45399,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",0.47384999999999999,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",0.45684999999999998,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",0.48236000000000001,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",0.46527000000000002,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",0.49525000000000002,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",0.47796,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",0.51004000000000005,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",0.49249999999999999,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",0.52488000000000001,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",0.50714000000000004,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",0.53774999999999995,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",0.51964999999999995,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",0.54991999999999996,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",0.53141000000000005,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",0.56333,"Lag","NA","NA"]
["VIC","NKHN",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"NKHN"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Khancoban (Essential Energy) 11 kV","Essential Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",0.54413,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",37.602809999999998,"Lag",0.93081226377620296,14.7653174458388]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",35.851660000000003,"Lag",0.93046218639739697,14.117302028472]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",37.698450000000001,"Lag",0.930118405935774,14.8853356929715]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",35.944029999999998,"Lag",0.92973343496560701,14.236110207698101]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",37.984029999999997,"Lag",0.92960220790558601,15.059734196695601]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",36.140909999999998,"Lag",0.92917257430438804,14.3776851568892]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",38.748489999999997,"Lag",0.92912123488252996,15.42127313074]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",36.895530000000001,"Lag",0.928672969661124,14.735582785673101]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",39.365720000000003,"Lag",0.92867625351768002,15.7217396063505]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",37.58502,"Lag",0.92823138381791104,15.062789171661899]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",40.279299999999999,"Lag",0.928343730449531,16.128442427166899]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",38.404409999999999,"Lag",0.92786833238872601,15.4346368560469]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",41.053429999999999,"Lag",0.92784696676717604,16.502003335683501]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",39.212209999999999,"Lag",0.92736531316567905,15.8206573934375]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",41.732259999999997,"Lag",0.927311126752146,16.844429880427899]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",39.89913,"Lag",0.92681402475418195,16.1660776535841]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",42.581209999999999,"Lag",0.92699567518148696,17.2287970302989]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",40.665489999999998,"Lag",0.92647033514987798,16.5198822626561]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",43.345820000000003,"Lag",0.92676104586992403,17.5697041173744]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",41.409129999999998,"Lag",0.92622795373732303,16.853029372972099]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",18.757739999999998,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",18.161200000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",18.93019,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",18.3278,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",19.346029999999999,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",18.740030000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",19.956700000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",19.343229999999998,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",20.669160000000002,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",20.046530000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",21.40992,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",20.78,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",22.091989999999999,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",21.447859999999999,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",22.749610000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",22.088840000000001,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",23.47017,"Lag","NA","NA"]
["VIC","RCTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Red Cliffs (Powercor) 22 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",22.781829999999999,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",129.96870999999999,"Lag",0.98954619398369104,18.941613371039001]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",126.44141999999999,"Lag",0.98953408327126102,18.438387433766501]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",130.70496,"Lag",0.98950528254120396,19.0867451707696]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",127.20088,"Lag",0.98949217243237697,18.586830521767698]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",132.03120000000001,"Lag",0.98947271465054298,19.310785455889199]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",128.25496999999999,"Lag",0.98945772123723497,18.772044132916999]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",135.13525000000001,"Lag",0.98944557759970497,19.790647565946699]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",131.4057,"Lag",0.98943033585213203,19.258565912792299]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",137.72228000000001,"Lag",0.98941760444899596,20.1966595227182]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",134.32059000000001,"Lag",0.98940327831733699,19.711352491382399]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",141.38615999999999,"Lag",0.98939669355363802,20.7547638908575]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",137.73996,"Lag",0.98938115040855201,20.234573486188999]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",144.77947,"Lag",0.98937742509378901,21.272497414726999]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",141.34773000000001,"Lag",0.98936268932164595,20.782903256612499]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",147.85570000000001,"Lag",0.989353511246439,21.749323574355699]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",144.54275999999999,"Lag",0.98933903666660905,21.2766781903278]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",151.38320999999999,"Lag",0.98933411340673105,22.288819720700701]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",147.86416,"Lag",0.98931860830264196,21.7867693549642]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",154.54238000000001,"Lag",0.98931777470011795,22.771662189572801]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",151.02868000000001,"Lag",0.98930222611478402,22.270375089336]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",84.081590000000006,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",81.225790000000003,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",84.866150000000005,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",81.982919999999993,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",86.775899999999993,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",83.872810000000001,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",89.582989999999995,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",86.641099999999994,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",92.881439999999998,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",89.892269999999996,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",96.343459999999993,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",93.315349999999995,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",99.569190000000006,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",96.471869999999996,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",102.69131,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",99.514129999999994,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",106.10771,"Lag","NA","NA"]
["VIC","RCTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RCTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Red Cliffs (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",102.80077,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe10",42.250360000000001,"Lag",0.99414365260267601,4.5927510545809902]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe50",40.734229999999997,"Lag",0.99413668182069204,4.43060062878404]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe10",42.5428,"Lag",0.99409545715690395,4.6436993273484104]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe50",41.022689999999997,"Lag",0.99408669888099099,4.4811232397053997]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe10",43.006329999999998,"Lag",0.99404616056581896,4.7140262198837499]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe50",41.384799999999998,"Lag",0.99403492491810497,4.5406032416809996]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe10",44.016590000000001,"Lag",0.99399443017106304,4.84586738160601]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe50",42.39029,"Lag",0.99398139174851097,4.6719342508892696]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe10",44.825629999999997,"Lag",0.99393757220451895,4.95845484083548]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe50",43.285719999999998,"Lag",0.99392339722011303,4.7937611389834096]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe10",45.999079999999999,"Lag",0.99389460971756505,5.1064210964686501]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe50",44.358029999999999,"Lag",0.99387822377584301,4.9309104501163699]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe10",47.077480000000001,"Lag",0.99385271969061895,5.2441997203052999]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe50",45.483539999999998,"Lag",0.99383567452838895,5.0737274984676004]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe10",48.102679999999999,"Lag",0.99382067459869305,5.3724802362804498]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe50",46.527500000000003,"Lag",0.99380307903397502,5.2040144004307303]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe10",49.293340000000001,"Lag",0.99379583897879897,5.5166184170702701]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe50",47.630499999999998,"Lag",0.993776789431004,5.3387773255858999]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe10",50.331600000000002,"Lag",0.99376529158173499,5.6467947390362498]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe50",48.649630000000002,"Lag",0.99374532264301596,5.4669076899852396]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe10",36.682070000000003,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe50",35.768410000000003,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe10",37.126660000000001,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe50",36.200479999999999,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe10",38.038440000000001,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe50",37.107329999999997,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe10",39.32244,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe50",38.381369999999997,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe10",40.799199999999999,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe50",39.845820000000003,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe10",42.323729999999998,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe50",41.36177,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe10",43.7224,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe50",42.736960000000003,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe10",45.089219999999997,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe50",44.074849999999998,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe10",46.584119999999999,"Lag","NA","NA"]
["VIC","RTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Richmond (CitiPower) 22kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe50",45.519399999999997,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe10",390.18540000000002,"Lag",0.988163220923019,60.573841670992103]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe50",367.94268,"Lag",0.98811934903592702,57.228466453394297]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe10",391.57584000000003,"Lag",0.98797189529193696,61.287939131361099]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe50",369.17194000000001,"Lag",0.98791583972291996,57.918321933575101]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe10",394.62232999999998,"Lag",0.98777043230675599,62.289421908922598]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe50",371.15253999999999,"Lag",0.98769873936994601,58.759491494466801]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe10",402.56909999999999,"Lag",0.98755620530270405,64.108371137805406]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe50",378.78525999999999,"Lag",0.98747088643133396,60.5312066131739]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe10",408.87450999999999,"Lag",0.98733284819299005,65.705427262781399]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe50",385.63452999999998,"Lag",0.98723671634138599,62.210060996898903]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe10",418.90033,"Lag",0.98715935524566201,67.784937538233095]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe50",394.47824000000003,"Lag",0.98704914367479701,64.1117782012481]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe10",428.18538000000001,"Lag",0.986986522819148,69.761329754163398]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe50",403.92923000000002,"Lag",0.98686850110207702,66.113128316374599]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe10",437.37148999999999,"Lag",0.98685007749007503,71.637997296688994]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe50",413.06234999999998,"Lag",0.98672576682095303,67.981825995826796]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe10",448.32934999999998,"Lag",0.98674213689269397,73.739640054003502]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe50",422.99034999999998,"Lag",0.98660860206254097,69.928574562071205]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe10",457.67664000000002,"Lag",0.98660807691110097,75.664410277667798]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe50",431.93547999999998,"Lag",0.98646655971069797,71.7928586537559]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe10",309.06286,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe50",301.70114000000001,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe10",312.90875999999997,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe50",305.44711999999998,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe10",320.97924,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe50",313.48469999999998,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe10",332.39647000000002,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe50",324.82963000000001,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe10",345.77497,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe50",338.11711000000003,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe10",359.88882999999998,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe50",352.17180999999999,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe10",373.12182999999999,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe50",365.21767999999997,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe10",386.25549999999998,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe50",378.11574000000002,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe10",400.67689999999999,"Lag","NA","NA"]
["VIC","RTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (Citipower Total)","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe50",392.11700000000002,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",76.035430000000005,"Lag",0.98834570054661197,11.711058832095899]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",69.853309999999993,"Lag",0.988298042473998,10.7812484923436]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",76.488389999999995,"Lag",0.98823434672543597,11.8379740739596]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",70.26585,"Lag",0.98817653942838601,10.902084438766099]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",77.257980000000003,"Lag",0.98809928310214601,12.0267521490555]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",70.815160000000006,"Lag",0.98802721713962904,11.057731707336]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",79.072370000000006,"Lag",0.98795313585619804,12.3859262355582]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",72.528090000000006,"Lag",0.98786798609732795,11.401645889943101]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",80.725520000000003,"Lag",0.98782721557124797,12.7120076539801]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",74.25976,"Lag",0.98773362201302795,11.739536963932499]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",83.145820000000001,"Lag",0.98773137378696096,13.1455386340524]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",76.414079999999998,"Lag",0.98762783364356099,12.1330637133902]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",85.482810000000001,"Lag",0.987637688819616,13.5674922632474]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",78.754059999999996,"Lag",0.98752886463211298,12.5554670480124]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",87.757549999999995,"Lag",0.98755753666992696,13.974462803160201]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",80.992990000000006,"Lag",0.98744410612687294,12.957051651019]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",90.464780000000005,"Lag",0.98749333610391998,14.443383334528299]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",83.460830000000001,"Lag",0.98737366880392796,13.3899671716088]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",93.036050000000003,"Lag",0.98744795138409902,14.8813468276058]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",85.928070000000005,"Lag",0.98732602208320897,13.8122842246876]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",57.7121,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",56.458419999999997,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",58.373629999999999,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",57.10371,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",59.883459999999999,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",58.610860000000002,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",62.064239999999998,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",60.78246,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",64.670320000000004,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",63.376249999999999,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",67.473330000000004,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",66.17295,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",70.142840000000007,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",68.811629999999994,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",72.851020000000005,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",71.479050000000001,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",75.860309999999998,"Lag","NA","NA"]
["VIC","RTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Richmond 66kV (United Energy Total)","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",74.412310000000005,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",189.06958,"Lag",0.98735172848573105,30.3600670952206]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",175.62079,"Lag",0.98723645500797697,28.331213188224599]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",189.17889,"Lag",0.98714024542907897,30.635460598770401]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",175.64851999999999,"Lag",0.98700695392850402,28.594299718304399]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",190.15754999999999,"Lag",0.98692769666186497,31.052411063308501]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",176.10792000000001,"Lag",0.986771461090311,28.9329157988759]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",193.77065999999999,"Lag",0.98673648644019696,31.877647053780201]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",179.52656999999999,"Lag",0.98656473574844505,29.728815995513798]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",196.49943999999999,"Lag",0.98650946828547603,32.607680911041399]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",182.47790000000001,"Lag",0.98632420515346897,30.492423240194999]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",201.13754,"Lag",0.98634630761480502,33.582749641366298]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",186.50588999999999,"Lag",0.98614315795847196,31.375452161942601]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",205.4393,"Lag",0.98618013168205998,34.5134637491566]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",190.84479999999999,"Lag",0.98596816860496805,32.311770634337101]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",209.51702,"Lag",0.98602976775347395,35.393537539319297]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",194.85778999999999,"Lag",0.98580878462019905,33.182079403750699]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",214.43906999999999,"Lag",0.98591572384911197,36.375736490346199]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",199.25310999999999,"Lag",0.98568221578066495,34.084817063580999]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",218.63511,"Lag",0.98577855440205697,37.271581388667698]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",203.22824,"Lag",0.98553473414727399,34.947335981156598]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",126.50038000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",124.34119,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",127.71634,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",125.53194999999999,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",130.75914,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",128.58667,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",135.24537000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",133.07632000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",140.61681999999999,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",138.44702000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",146.36832999999999,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",144.21108000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",151.76697999999999,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",149.56657000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",157.12287000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",154.85918000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",162.99950000000001,"Lag","NA","NA"]
["VIC","RWTS1366A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",160.60048,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",109.88318,"Lag",0.98773473642078102,17.370349171869599]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",104.11575000000001,"Lag",0.98767371872316101,16.5002877842781]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",110.12981000000001,"Lag",0.98754530639958205,17.545789037401899]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",104.32868000000001,"Lag",0.98747301526369502,16.6706437443687]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",110.87688,"Lag",0.98734987415152298,17.805513804237101]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",104.7897,"Lag",0.98726236324997596,16.8872156580404]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",113.00512000000001,"Lag",0.98714061914351503,18.299677157903901]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",106.85095,"Lag",0.98704104138271398,17.371273052492299]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",114.71387,"Lag",0.98692479854404902,18.734701562782799]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",108.73367,"Lag",0.98681701333134397,17.8325421763534]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",117.5206,"Lag",0.98676886655070495,19.309488035288599]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",111.23390000000001,"Lag",0.98664860690576806,18.361090755153199]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",120.16637,"Lag",0.98661840409041601,19.858430100456001]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",113.95392,"Lag",0.98649353475095203,18.9212340066425]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",122.78498999999999,"Lag",0.98650123558851899,20.381637556636999]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",116.58461,"Lag",0.98637265807656804,19.446262315603398]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",125.7443,"Lag",0.98639233251355096,20.9586342650957]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",119.2825,"Lag",0.98625492810269699,19.9838217967452]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",128.31286,"Lag",0.98626714984383701,21.486950720905298]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",121.76715,"Lag",0.98612344292131804,20.499479780578099]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",80.185850000000002,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",78.28537,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",80.973299999999995,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",79.050079999999994,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",82.873180000000005,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",80.944450000000003,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",85.652010000000004,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",83.707430000000002,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",88.954560000000001,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",86.989189999999994,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",92.466160000000002,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",90.488079999999997,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",95.742230000000006,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",93.718599999999995,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",98.974959999999996,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",96.893950000000004,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",102.5184,"Lag","NA","NA"]
["VIC","RWTS1366U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 13 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",100.3335,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",58.596850000000003,"Lag",0.99836544053673104,3.3544594672132702]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",54.733199999999997,"Lag",0.998350923466236,3.1471967909864]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",58.63673,"Lag",0.99833683920482197,3.3860558153001099]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",54.747839999999997,"Lag",0.99832005504335397,3.1774391577478198]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",58.908230000000003,"Lag",0.99830632464242497,3.4328771909444602]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",54.857529999999997,"Lag",0.99828644188243898,3.2155803543800299]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",59.889310000000002,"Lag",0.99827363049162599,3.5236605746087899]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",55.778739999999999,"Lag",0.99825116309865902,3.3031520557165801]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",60.616129999999998,"Lag",0.99823859718297003,3.6025238331632798]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",56.573770000000003,"Lag",0.99821406563367499,3.38567438979433]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",61.914499999999997,"Lag",0.99821240414208701,3.70701977636155]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",57.683390000000003,"Lag",0.99818509203310601,3.48004497739936]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",63.124940000000002,"Lag",0.99818743493286299,3.8058686387255198]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",58.904910000000001,"Lag",0.99815876958177296,3.5794882182532599]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",64.318870000000004,"Lag",0.99816718978866403,3.8995076365236101]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",60.079219999999999,"Lag",0.99813735655842495,3.6720747155123301]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",65.700289999999995,"Lag",0.99814817329243499,4.0039282563632304]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",61.295549999999999,"Lag",0.99811625451045805,3.7676392031406198]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",66.875349999999997,"Lag",0.998126928102407,4.0989163547943903]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",62.399470000000001,"Lag",0.99809334651283599,3.8588110483431599]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",40.706159999999997,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",39.980220000000003,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",41.122500000000002,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",40.38776,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",42.101059999999997,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",41.369210000000002,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",43.525080000000003,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",42.793140000000001,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",45.205730000000003,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",44.472320000000003,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",46.980319999999999,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",46.24971,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",48.630589999999998,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",47.885019999999997,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",50.263109999999998,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",49.496119999999998,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",52.056600000000003,"Lag","NA","NA"]
["VIC","RWTS22A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",51.24503,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",35.696190000000001,"Lag",0.99835225700567198,2.0517234398303201]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",32.323169999999998,"Lag",0.99832930089592997,1.8707802508337099]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",35.732199999999999,"Lag",0.99832142148311098,2.0729692900560299]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",32.331029999999998,"Lag",0.99829478286234197,1.8905160149139899]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",35.941740000000003,"Lag",0.99829103379032702,2.1039626965407798]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",32.428849999999997,"Lag",0.99826002119382595,1.9155162837729001]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",36.538739999999997,"Lag",0.99825336547439503,2.1624151773434099]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",32.958889999999997,"Lag",0.99821778056282395,1.9703767443873299]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",37.024259999999998,"Lag",0.99821597731580602,2.21453867839565]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",33.459820000000001,"Lag",0.99817666757014101,2.02332690361012]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",37.926079999999999,"Lag",0.99819243315344897,2.2834395663302902]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",34.219059999999999,"Lag",0.99814960722269896,2.0845791918071002]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",38.775010000000002,"Lag",0.99816901214518305,2.3496689445652099]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",35.047080000000001,"Lag",0.99812417033819201,2.1496868683972301]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",39.62659,"Lag",0.99815127534260994,2.4129072845752702]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",35.862870000000001,"Lag",0.99810493727026295,2.2110052800540001]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",40.529789999999998,"Lag",0.99812933852566299,2.4825438691850601]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",36.638570000000001,"Lag",0.99807980185024403,2.2738022204882302]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",41.340049999999998,"Lag",0.998108265801947,2.5464368535636601]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",37.382280000000002,"Lag",0.99805634534061605,2.3341251788285202]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",27.031469999999999,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",26.148289999999999,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",27.32264,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",26.428930000000001,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",27.999379999999999,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",27.097899999999999,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",28.981310000000001,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",28.066230000000001,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",30.151499999999999,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",29.220050000000001,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",31.40278,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",30.457619999999999,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",32.580179999999999,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",31.611249999999998,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",33.748330000000003,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",32.751939999999998,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",35.027929999999998,"Lag","NA","NA"]
["VIC","RWTS22U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Ringwood (United Energy) 22 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",33.987560000000002,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",200.23273,"Lag",0.98755171174740097,31.8925510300915]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",183.77619999999999,"Lag",0.98743579966422401,29.409956299554601]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",200.55992000000001,"Lag",0.98736459164294998,32.188446280719297]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",184.00054,"Lag",0.98723029762061099,29.690335832832702]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",201.78801999999999,"Lag",0.98717037174514899,32.638324399061801]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",184.65758,"Lag",0.98701275473705097,30.054065136885601]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",205.82884999999999,"Lag",0.986996233078271,33.521532316322599]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",188.43686,"Lag",0.98682220714858804,30.897816215324902]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",208.94943000000001,"Lag",0.98679287428491003,34.300119946113]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",191.74614,"Lag",0.986604060094044,31.704870698434501]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",213.81862000000001,"Lag",0.98661751150253496,35.336397511611501]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",195.9025,"Lag",0.98640764143075899,32.633612349510599]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",218.57076000000001,"Lag",0.98646667689160294,36.3289219548655]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",200.63676000000001,"Lag",0.98624687733164096,33.623439456583597]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",223.14775,"Lag",0.98633403030748101,37.274760617063997]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",205.09690000000001,"Lag",0.98610484437888002,34.551650393237203]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",228.49135000000001,"Lag",0.98622026413193897,38.329220974811498]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",209.82121000000001,"Lag",0.98597742076725703,35.512686068462102]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",233.12734,"Lag",0.98608991224639797,39.295342647104299]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",214.16928999999999,"Lag",0.98583561288820698,36.435374292216899]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",138.1045,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",135.52670000000001,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",139.48788999999999,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",136.87984,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",142.84715,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",140.24673999999999,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",147.76544000000001,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",145.16135,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",153.62338,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",151.01023000000001,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",159.86580000000001,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",157.25807,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",165.71702999999999,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",163.05485999999999,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",171.52723,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",168.78874999999999,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",177.90563,"Lag","NA","NA"]
["VIC","RWTS2466A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",175.01147,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",7.0939199999999998,"Lag",0.98826356590064601,1.0965250595334699]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",6.5154500000000004,"Lag",0.98821431075324495,1.0092583894776499]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",7.1220699999999999,"Lag",0.98814783366374803,1.10638816393992]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",6.5404999999999998,"Lag",0.98808793776031301,1.0186538349265499]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",7.1842100000000002,"Lag",0.988069113899948,1.1198085618542399]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",6.5832800000000002,"Lag",0.98800021634072199,1.02915362722212]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",7.3391500000000001,"Lag",0.98799287282678405,1.1476749939152699]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",6.72959,"Lag",0.987917364303732,1.05571815708843]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",7.4545000000000003,"Lag",0.98789429110623395,1.17057649613481]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",6.8521299999999998,"Lag",0.98781201826161502,1.07970432637402]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",7.61463,"Lag",0.98778176773445103,1.20136877387482]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",6.98672,"Lag",0.98768711825159505,1.10664369773474]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",7.7595599999999996,"Lag",0.98768584686433603,1.2291203602784999]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",7.1304999999999996,"Lag",0.98758408684327703,1.1342217977509399]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",7.8922100000000004,"Lag",0.98761292001913503,1.2538981058557599]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",7.2584999999999997,"Lag",0.98750553620790504,1.15829805489188]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",8.0535200000000007,"Lag",0.98754936228536405,1.28286716220644]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",7.3969699999999996,"Lag",0.98743425181672295,1.18382152072953]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",8.1812799999999992,"Lag",0.98746061491144799,1.3079431243978901]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",7.5136099999999999,"Lag",0.98733705132963701,1.2072199449829299]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",8.5770700000000009,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",7.9319100000000002,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",8.6604100000000006,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",8.0088299999999997,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",8.8464299999999998,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",8.1848899999999993,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",9.1171600000000002,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",8.4402200000000001,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",9.4260699999999993,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",8.7313200000000002,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",9.7394099999999995,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",9.0275700000000008,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",10.015790000000001,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",9.2855600000000003,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",10.28375,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",9.53444,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",10.57987,"Lag","NA","NA"]
["VIC","RWTS2466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"RWTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Ringwood 24 (United Energy) 66kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",9.8054799999999993,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",291.62797,"Lag",0.99183161237175499,37.5047010693578]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",268.34634,"Lag",0.99179131296489298,34.596657506104698]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",293.29771,"Lag",0.99180011843305405,37.7929839577439]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",269.94619,"Lag",0.99175712979439201,34.876210629236603]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",296.18349999999998,"Lag",0.99176735440115904,38.241953335916399]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",272.07441999999998,"Lag",0.99172031867469501,35.230555297636698]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",303.25447000000003,"Lag",0.99174897992438904,39.199143002132899]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",278.86340000000001,"Lag",0.99170089115955795,36.1525223783039]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",309.36626000000001,"Lag",0.991736602628008,40.019520052036597]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",285.37392,"Lag",0.99168930454543702,37.0227036820325]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",318.00015000000002,"Lag",0.99173119978431301,41.150011531849103]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",293.07778000000002,"Lag",0.99168288315533804,38.037027704706702]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",326.08447999999999,"Lag",0.99172653111217302,42.208203767171803]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",301.25630000000001,"Lag",0.99167930728049503,39.106984950607398]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",333.03811000000002,"Lag",0.99169703778250795,43.186010580746597]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",308.12392999999997,"Lag",0.99164823511639799,40.0740497436948]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",341.03426999999999,"Lag",0.99167271502293997,44.288437556013101]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",315.29467,"Lag",0.99162137944264594,41.073375805581101]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",347.81614999999999,"Lag",0.99163321583073005,45.277521074877903]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",321.73667999999998,"Lag",0.99157891333484305,42.020007109294198]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",197.15714,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",190.80709999999999,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",199.01621,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",192.60395,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",203.57638,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",197.12366,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",210.31124,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",203.77668,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",218.29132000000001,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",211.65622999999999,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",226.76183,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",220.04584,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",234.72274999999999,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",227.85300000000001,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",242.42193,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",235.37298000000001,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",250.85865999999999,"Lag","NA","NA"]
["VIC","SHTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SHTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Shepparton (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",243.51342,"Lag","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",272.31700000000001,"Lag",0.99620083915208502,23.805308180888499]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",254.47487000000001,"Lag",0.99618215085870898,22.300551889563199]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",275.12045000000001,"Lag",0.996156940208481,24.189729970123299]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",257.07301000000001,"Lag",0.99613502349514604,22.6676583967004]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",279.57941,"Lag",0.99612263311007498,24.691895728669198]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",260.69733000000002,"Lag",0.996097424000013,23.0994329076211]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",288.63583,"Lag",0.99610194091964799,25.560069022117901]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",269.41775999999999,"Lag",0.99607556672178899,23.939269726314599]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",296.76218999999998,"Lag",0.99607604591699295,26.367355282726798]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",277.84282000000002,"Lag",0.99604901706473603,24.771747525390001]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",307.76587999999998,"Lag",0.99606005825795196,27.401014826130801]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",287.89202,"Lag",0.99603149293190596,25.724908000997299]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",318.31321000000003,"Lag",0.99604012665292196,28.412085247218101]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",298.47284000000002,"Lag",0.99601122289510102,26.738802876799198]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",328.31135999999998,"Lag",0.99601802491457503,29.3866588213534]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",308.33551999999997,"Lag",0.99598834003066705,27.701951282819198]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",339.93718000000001,"Lag",0.99601051136174201,30.456133949098401]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",319.11829,"Lag",0.99598009880758098,28.700325886613101]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",350.67804000000001,"Lag",0.99600217538227698,31.4514489315311]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",329.50796000000003,"Lag",0.99597165728716197,29.666022467994502]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",206.03638000000001,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",198.99544,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",209.33869000000001,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",202.17366999999999,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",215.68988999999999,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",208.41385,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",224.59960000000001,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",217.15948,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",235.08423999999999,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",227.45590000000001,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",246.37139999999999,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",238.57365999999999,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",257.02692999999999,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",248.98129,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",267.63837000000001,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",259.31509,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",279.19893000000002,"Lead","NA","NA"]
["VIC","SMTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",270.46429999999998,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe10",83.639449999999997,"Lag",0.99632284548309002,7.1925420200470498]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe50",77.769440000000003,"Lag",0.99631219851860697,6.6974814820035196]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe10",84.748769999999993,"Lag",0.99631230346098598,7.2984349216936604]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe50",78.827560000000005,"Lag",0.99630089932255805,6.7990563161259097]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe10",86.335250000000002,"Lag",0.996307677453379,7.4397480559029097]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe50",80.168300000000002,"Lag",0.99629563472738802,6.9196444129640504]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe10",89.067689999999999,"Lag",0.99630634332319701,7.6766042063010698]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe50",82.815690000000004,"Lag",0.996294421988137,7.1493276797111402]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe10",91.533619999999999,"Lag",0.99630292207447502,7.8928119881296697]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe50",85.396119999999996,"Lag",0.99629132164926304,7.3751920773897899]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe10",94.811700000000002,"Lag",0.99630074152984405,8.1779001304848205]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe50",88.399940000000001,"Lag",0.99628887262162102,7.6371498838232297]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe10",98.011300000000006,"Lag",0.99629928795465705,8.4555488411090298]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe50",91.632900000000006,"Lag",0.99628779419438995,7.91761208531869]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe10",101.07111,"Lag",0.99629800772499799,8.7210387100828406]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe50",94.677199999999999,"Lag",0.99628676825487805,8.1817938834467796]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe10",104.4464,"Lag",0.99629769572087401,9.01266143567962]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe50",97.815529999999995,"Lag",0.99628639200465696,8.4534320527830502]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe10",107.55361000000001,"Lag",0.99629653805501495,9.2822410136896192]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe50",100.83704,"Lag",0.99628535253963302,8.7157839279253704]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe10",77.787989999999994,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe50",74.963930000000005,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe10",79.007689999999997,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe50",76.137190000000004,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe10",81.249549999999999,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe50",78.339359999999999,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe10",84.297529999999995,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe50",81.330150000000003,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe10",87.858729999999994,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe50",84.824849999999998,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe10",91.618750000000006,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe50",88.525769999999994,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe10",95.150689999999997,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe50",91.970290000000006,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe10",98.621960000000001,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe50",95.344269999999995,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe10",102.38306,"Lead","NA","NA"]
["VIC","SMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"South Morang (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe50",98.959559999999996,"Lead","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",228.09896000000001,"Lag",0.99608097030394105,20.2538232783429]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",205.44014999999999,"Lag",0.99602848905795005,18.364318336173]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",228.15900999999999,"Lag",0.995998408407056,20.472715704375702]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",205.29214999999999,"Lag",0.99593555277444001,18.5658615941243]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",229.43986000000001,"Lag",0.99592173903609305,20.785138231147801]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",205.83273,"Lag",0.995847500310717,18.8165534376195]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",233.97143,"Lag",0.99585756027440697,21.362814793931001]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",209.91499999999999,"Lag",0.99577536084124496,19.3567631356152]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",237.29839999999999,"Lag",0.99578032117752002,21.868920042957299]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",213.3082,"Lag",0.99569011589920797,19.8683912656895]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",242.49319,"Lag",0.99571158510448499,22.530108004950002]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",217.52609000000001,"Lag",0.99561078112726398,20.448116106803099]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",247.53353999999999,"Lag",0.99565186036998998,23.1590465052202]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",222.37155000000001,"Lag",0.99554495969326795,21.060802843711599]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",252.50137000000001,"Lag",0.99560269640836296,23.7578940357043]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",227.04836,"Lag",0.99549061761070101,21.635382386235602]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",258.33040999999997,"Lag",0.995562095699977,24.4190503014607]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",232.01609999999999,"Lag",0.99544351469324999,22.224715347648502]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",263.22559999999999,"Lag",0.99551239017558202,25.0216655051073]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",236.42784,"Lag",0.99538751664493896,22.7870159379376]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",171.86815999999999,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",168.82789,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",173.81421,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",170.73330000000001,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",178.10765000000001,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",175.03613000000001,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",184.26837,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",181.19417999999999,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",191.50904,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",188.42639,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",199.15231,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",196.07929999999999,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",206.27202,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",203.13319999999999,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",213.28547,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",210.05360999999999,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",220.96356,"Lag","NA","NA"]
["VIC","SVTS1266U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 12 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",217.54061999999999,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe10",33.946649999999998,"Lag",0.99627654345576699,2.93765312936844]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe50",30.745239999999999,"Lag",0.99624844155978198,2.6706894178181901]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe10",34.043689999999998,"Lag",0.99623175900977901,2.9638147818337699]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe50",30.82349,"Lag",0.996198686666246,2.6952841831494001]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe10",34.291289999999996,"Lag",0.99618460314448398,3.0040987700840098]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe50",30.97214,"Lag",0.99614537597410202,2.7273167886470699]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe10",34.926819999999999,"Lag",0.99612188056140105,3.08496814552052]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe50",31.55209,"Lag",0.99607564378451996,2.8035513803201901]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe10",35.453710000000001,"Lag",0.99606113013918096,3.1560831029458898]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe50",32.102409999999999,"Lag",0.99600925516551597,2.8766201517717702]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe10",36.348909999999997,"Lag",0.996022206824554,3.2518174280370298]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe50",32.869289999999999,"Lag",0.99596518772701104,2.9616539469507299]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe10",37.180050000000001,"Lag",0.995981582368199,3.3432161962351099]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe50",33.688459999999999,"Lag",0.99592123344472605,3.0520545438345299]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe10",38.010199999999998,"Lag",0.99595298269311106,3.4300780499801502]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe50",34.492269999999998,"Lag",0.99589044909194702,3.1367199203516498]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe10",38.989759999999997,"Lag",0.99593277018499304,3.5273036670082001]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe50",35.361130000000003,"Lag",0.99586760614450498,3.2247143289844602]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe10",39.810549999999999,"Lag",0.99590070547676401,3.6158146877599702]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe50",36.126930000000002,"Lag",0.99583240704270504,3.30863976572852]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe10",20.937660000000001,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe50",20.465389999999999,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe10",21.14809,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe50",20.67051,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe10",21.664400000000001,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe50",21.186219999999999,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe10",22.41976,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe50",21.938479999999998,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe10",23.32357,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe50",22.83802,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe10",24.291820000000001,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe50",23.80416,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe10",25.208570000000002,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe50",24.710059999999999,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe10",26.119789999999998,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe50",25.60726,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe10",27.117000000000001,"Lag","NA","NA"]
["VIC","SVTS3466C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe50",26.578199999999999,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",176.5814,"Lag",0.99600252434157999,15.8364550950729]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",161.77331000000001,"Lag",0.99595131078190502,14.601617112006]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",176.30144000000001,"Lag",0.99590870448160496,15.996946505573]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",161.36160000000001,"Lag",0.99584751516369097,14.751121966895701]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",176.79816,"Lag",0.99581381078890296,16.228150792209]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",161.31456,"Lag",0.99574041955918502,14.9369824244712]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",179.62630999999999,"Lag",0.995726138974248,16.6606028205074]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",163.86219,"Lag",0.995643277721735,15.3460420536817]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",181.60625999999999,"Lag",0.99562897776244197,17.0358848204887]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",165.95115999999999,"Lag",0.99553753153961599,15.730415167838601]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",185.19927000000001,"Lag",0.99555068477115405,17.5288677551892]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",168.86878999999999,"Lag",0.99544842884001195,16.167078558492399]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",188.56607,"Lag",0.99547754918658504,17.9946096018585]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",172.15593999999999,"Lag",0.99536888277155999,16.626178438145601]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",191.86246,"Lag",0.99541544419165995,18.4353306093792]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",175.29002,"Lag",0.99530099157134899,17.053364509490802]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",195.82079999999999,"Lag",0.99536353269023903,18.922639323026001]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",178.65521000000001,"Lag",0.99524150231766595,17.491210790801102]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",198.99442999999999,"Lag",0.99529873086148801,19.3641746253546]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",181.51553000000001,"Lag",0.99516925862947003,17.906619355078199]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",121.55784,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",119.49648999999999,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",122.87872,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",120.79076999999999,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",125.87984,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",123.8017,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",130.20001999999999,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",128.12409,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",135.28878,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",133.21136000000001,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",140.65768,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",138.59166999999999,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",145.68161000000001,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",143.57326,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",150.63269,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",148.46265,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",156.05222000000001,"Lag","NA","NA"]
["VIC","SVTS3466U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"SVTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Springvale 34 (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",153.75153,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",303.84546999999998,"Lag",0.99531643868331299,29.511112682380201]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",280.38252,"Lag",0.99525305993392899,27.4172113704116]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",303.40746999999999,"Lag",0.99520503115370296,29.8195006598364]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",279.76452999999998,"Lag",0.99513074913379596,27.709536521277801]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",304.43522000000002,"Lag",0.99509606135841699,30.261071837616601]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",279.91034000000002,"Lag",0.99500851158103398,28.072400830438401]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",309.70963,"Lag",0.99499976907501897,31.0883866862373]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",284.79144000000002,"Lag",0.99490296790139698,28.864615560573899]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",313.70600000000002,"Lag",0.99489331923663704,31.825519627570898]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",289.06889999999999,"Lag",0.99478886126592103,29.626833784013201]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",320.36833000000001,"Lag",0.99480249692177003,32.791406116276001]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",294.66208999999998,"Lag",0.99468660230202399,30.497307136319101]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",325.80828000000002,"Lag",0.99468785466346898,33.716908543379802]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",300.03642000000002,"Lag",0.99456253194061595,31.4169534454117]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",331.54318000000001,"Lag",0.99460251874800099,34.5871117258636]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",305.57033000000001,"Lag",0.994470185694737,32.269219700753197]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",339.11799000000002,"Lag",0.99454901341732105,35.553679369910498]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",312.22161999999997,"Lag",0.99440956443214901,33.153369757087098]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",345.57506999999998,"Lag",0.994486278520329,36.440266794169197]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",318.24387000000002,"Lag",0.994341016221721,34.001151698340301]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",221.26795000000001,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",216.24654000000001,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",223.39855,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",218.31998999999999,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",228.73057,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",223.64418000000001,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",236.58175,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",231.46055000000001,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",245.97752,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",240.80882,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",256.03519,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",250.84163000000001,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",265.51787000000002,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",260.20749000000001,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",274.95377999999999,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",269.49257999999998,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",285.34429,"Lag","NA","NA"]
["VIC","TBTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TBTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Tyabb (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",279.60239999999999,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",144.73150999999999,"Lag",0.978972061936905,30.158585703238799]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",131.25056000000001,"Lag",0.978972061936905,27.349478094701599]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",145.66166000000001,"Lag",0.978972061936905,30.3524067204579]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",132.15871999999999,"Lag",0.978972061936905,27.538716921770099]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",147.25246000000001,"Lag",0.978972061936905,30.683891399479901]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",133.38524000000001,"Lag",0.978972061936905,27.794294359860299]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",150.87604999999999,"Lag",0.978972061936905,31.438960904167601]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",136.85391000000001,"Lag",0.978972061936905,28.517082241167302]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",153.99805000000001,"Lag",0.978972061936905,32.0895110474329]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",140.16540000000001,"Lag",0.978972061936905,29.2071175691371]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",158.40504999999999,"Lag",0.978972061936905,33.007824462349802]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",144.09763000000001,"Lag",0.978972061936905,30.026500269282]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",162.59891999999999,"Lag",0.978972061936905,33.881726681868102]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",148.32903999999999,"Lag",0.978972061936905,30.908224927102101]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",166.47334000000001,"Lag",0.978972061936905,34.689063160430003]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",152.16781,"Lag",0.978972061936905,31.7081327981664]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",170.86279999999999,"Lag",0.978972061936905,35.603721658782803]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",156.15401,"Lag",0.978972061936905,32.538761555720697]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",174.98045999999999,"Lag",0.978972061936905,36.461743536719403]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",160.12581,"Lag",0.978972061936905,33.366389697623703]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",174.48034999999999,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",167.80856,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",175.88497000000001,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",169.15816000000001,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",179.60792000000001,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",172.83331000000001,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",185.17447999999999,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",178.3065,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",191.76168999999999,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",184.7799,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",198.69193999999999,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",191.61355,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",205.12046000000001,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",197.88682,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",211.30452,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",203.89592999999999,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",218.07836,"Lag","NA","NA"]
["VIC","TGTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TGTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Terang (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",210.39164,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",84.152799999999999,"Lag",0.98778952811723097,13.272586858428101]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",79.37912,"Lag",0.98773211621230295,12.5496281844931]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",84.374570000000006,"Lag",0.98767211449845804,13.372587516524501]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",79.590479999999999,"Lag",0.98760738067131504,12.6480522811536]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",84.938159999999996,"Lag",0.98754070565638596,13.534823030696399]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",79.948670000000007,"Lag",0.98746491148976101,12.7791806177128]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",86.689499999999995,"Lag",0.98742368243171896,13.8798552474672]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",81.660380000000004,"Lag",0.98734131507962497,13.118210996855501]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",87.925470000000004,"Lag",0.98724080609487397,14.181705664377199]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",83.036519999999996,"Lag",0.98715069283692702,13.4412897150604]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",89.980270000000004,"Lag",0.98710245152867804,14.593140890711499]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",84.862120000000004,"Lag",0.98700127540357196,13.8180133293751]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",92.049679999999995,"Lag",0.98700770951751204,14.984573116363]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",86.999269999999996,"Lag",0.98690446718998903,14.219704562872201]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",94.007800000000003,"Lag",0.98692500912648795,15.352926481360001]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",88.975610000000003,"Lag",0.98681942751753704,14.590817288999199]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",96.354529999999997,"Lag",0.98686999750847404,15.7699138783076]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",91.134280000000004,"Lag",0.98675968466612396,14.979323596259199]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",98.289479999999998,"Lag",0.98677227739344398,16.1475516653983]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",93.013030000000001,"Lag",0.986657075515741,15.3484500718512]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",62.409619999999997,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",60.920900000000003,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",62.936109999999999,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",61.432899999999997,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",64.331590000000006,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",62.82705,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",66.409400000000005,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",64.895319999999998,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",68.880309999999994,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",67.352959999999996,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",71.494410000000002,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",69.960160000000002,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",73.921379999999999,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",72.354960000000005,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",76.316199999999995,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",74.708410000000001,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",78.949160000000006,"Lag","NA","NA"]
["VIC","TSTS66A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",77.264120000000005,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe10",114.73446,"Lag",0.98804426335305096,17.9027055954049]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe50",105.08853999999999,"Lag",0.98798078575501302,16.441861648579199]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe10",115.1554,"Lag",0.98792154051831804,18.062058584000098]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe50",105.45923999999999,"Lag",0.98784630791443395,16.593605948745701]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe10",116.09173,"Lag",0.98779225310226904,18.307916474507898]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe50",106.07598,"Lag",0.98770232308057404,16.791062948828699]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe10",118.6931,"Lag",0.98768189482609903,18.804152943401]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe50",108.53496,"Lag",0.98758198717666701,17.265734904477998]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe10",120.65998999999999,"Lag",0.987522671954153,19.2412398054589]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe50",110.61715,"Lag",0.98741061872189795,17.720283585322399]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe10",123.73868,"Lag",0.987400481935926,19.8304151432739]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe50",113.29395,"Lag",0.98727483046828501,18.248593959112299]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe10",126.80181,"Lag",0.98731141747003404,20.394394306456]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe50",116.35975000000001,"Lag",0.98718066661922199,18.812977485313901]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe10",129.75586999999999,"Lag",0.98723931649527497,20.929874552895502]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe50",119.26013,"Lag",0.98710436932185097,19.340328066250802]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe10",133.28735,"Lag",0.98720237865821003,21.5312090465453]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe50",122.45343,"Lag",0.98706324316058403,19.890446273020999]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe10",136.25533999999999,"Lag",0.98712422533321897,22.0790770160284]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe50",125.27059,"Lag",0.98697903549900601,20.415471518067299]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe10",78.241249999999994,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe50",76.045360000000002,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe10",79.035550000000001,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe50",76.815749999999994,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe10",80.959490000000002,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe50",78.728059999999999,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe10",83.770449999999997,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe50",81.513900000000007,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe10",87.122950000000003,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe50",84.835070000000002,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe10",90.701130000000006,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe50",88.389870000000002,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe10",94.074100000000001,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe50",91.70881,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe10",97.419939999999997,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe50",94.989440000000002,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe10",101.07977,"Lag","NA","NA"]
["VIC","TSTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe50",98.537369999999996,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe10",29.16639,"Lag",0.98781479668007999,4.59527494243207]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe50",26.871099999999998,"Lag",0.98773545557625697,4.2476605621853398]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe10",29.237010000000001,"Lag",0.98766897725002001,4.63439580912884]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe50",26.930160000000001,"Lag",0.98757639652942797,4.2850307035987401]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe10",29.416260000000001,"Lag",0.98749986660548805,4.6952777453848302]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe50",27.029,"Lag",0.98738874732909099,4.3337348007513299]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe10",30.00592,"Lag",0.98734969069598899,4.8186310025685204]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe50",27.585560000000001,"Lag",0.98722541245118201,4.4520751680665702]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe10",30.421779999999998,"Lag",0.98714094443841205,4.9263393844468597]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe50",28.032440000000001,"Lag",0.98700134507871795,4.5644814304198196]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe10",31.108160000000002,"Lag",0.98696940728937599,5.0716387134362302]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe50",28.619450000000001,"Lag",0.98681104497025995,4.69473148852616]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe10",31.79599,"Lag",0.98683952241769302,5.2100637505044398]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe50",29.309830000000002,"Lag",0.98667323387883499,4.8335427149951098]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe10",32.459249999999997,"Lag",0.98673201399013899,5.3408626498162803]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe50",29.96106,"Lag",0.98655890242857602,4.9625197090163899]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe10",33.27525,"Lag",0.98666848587790901,5.4884853567550502]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe50",30.69378,"Lag",0.98648809612133803,5.0975299244674002]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe10",33.948560000000001,"Lag",0.98656118847908103,5.6224905732029002]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe50",31.330359999999999,"Lag",0.98637223882426694,5.2259724990763203]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe10",18.779219999999999,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe50",18.374829999999999,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe10",18.957979999999999,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe50",18.54918,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe10",19.404669999999999,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe50",18.99596,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe10",20.061170000000001,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe50",19.65052,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe10",20.845109999999998,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe50",20.431550000000001,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe10",21.681930000000001,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe50",21.267410000000002,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe10",22.4679,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe50",22.044540000000001,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe10",23.247890000000002,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe50",22.812819999999999,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe10",24.104399999999998,"Lag","NA","NA"]
["VIC","TSTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe50",23.646750000000001,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe10",160.37215,"Lag",0.98762145483019803,25.4706528399768]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2024,"poe50",151.24688,"Lag",0.98755328575983004,24.088659681973201]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe10",160.64012,"Lag",0.98744007457806005,25.703000386705]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2025,"poe50",151.465,"Lag",0.98736010538394803,24.313457604533902]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe10",161.55735999999999,"Lag",0.98724582437901598,26.052741790414601]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2026,"poe50",151.96115,"Lag",0.98714949694556797,24.599426265201]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe10",164.60571999999999,"Lag",0.98706190986458897,26.738763197614599]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2027,"poe50",154.90239,"Lag",0.98695411095319596,25.2692246886334]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe10",166.77685,"Lag",0.98683075765540595,27.337193185576002]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2028,"poe50",157.31021999999999,"Lag",0.98671231856076602,25.903502139793002]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe10",178.46592999999999,"Lag",0.98674966211598703,29.344950650320101]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2029,"poe50",168.80485999999999,"Lag",0.98663204113636604,27.881812284113501]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe10",182.29642999999999,"Lag",0.98661271357087799,30.132442687329899]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2030,"poe50",172.75059999999999,"Lag",0.98649099288886699,28.686757053100401]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe10",185.98432,"Lag",0.98649934156160002,30.874591426316801]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2031,"poe50",176.45589000000001,"Lag",0.98637376918574105,29.4315409668218]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe10",190.3631,"Lag",0.98641519075709905,31.701864316915898]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2032,"poe50",180.44552999999999,"Lag",0.98628235015916199,30.199879840399401]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe10",193.97751,"Lag",0.98629454759299995,32.449892400379198]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Summer","Coincident",2033,"poe50",183.93331000000001,"Lag",0.98615538487987897,30.9287302125623]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe10",103.14216,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2024,"poe50",100.82583,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe10",104.15011,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2025,"poe50",101.80714999999999,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe10",106.61188,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2026,"poe50",104.26609999999999,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe10",110.21181,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2027,"poe50",107.85136,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe10",122.68103000000001,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2028,"poe50",120.2683,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe10",127.50189,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2029,"poe50",125.08345,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe10",132.01160999999999,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2030,"poe50",129.54096000000001,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe10",136.45886999999999,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2031,"poe50",133.91946999999999,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe10",141.32801000000001,"Lag","NA","NA"]
["VIC","TSTS66U",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TSTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Templestowe (United Energy) 66 kV","United Energy","MAX_DEMAND","Winter","Coincident",2032,"poe50",138.65656999999999,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",116.09484999999999,"Lag",0.98263002504651697,21.9251897219082]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",107.27547,"Lag",0.98251821830430297,20.3264367882113]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",116.97935,"Lag",0.98246178370575699,22.201824270229999]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",108.08378,"Lag",0.98233543706290105,20.589259823023198]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",118.31685,"Lag",0.98226553113552195,22.584355532633801]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",109.06923,"Lag",0.98211795636702304,20.907972430339299]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",121.32773,"Lag",0.98209032200202195,23.276316301334401]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",111.92033000000001,"Lag",0.98192854534919405,21.570968720386499]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",123.80517999999999,"Lag",0.98187216396767696,23.899822143424899]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",114.50207,"Lag",0.98169708154780699,22.213379966650098]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",127.37452999999999,"Lag",0.98169357408825297,24.713068787074899]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",117.64514,"Lag",0.98149968245187702,22.9493517451081]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",130.89336,"Lag",0.98155170135119496,25.496777863796702]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",121.15152999999999,"Lag",0.98135104453431898,23.730805732867299]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",134.28761,"Lag",0.98143240795824305,26.244782226166301]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",124.47129,"Lag",0.98122557088081497,24.465306753048399]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",138.15463,"Lag",0.98134975532693303,27.062285112656401]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",127.97150999999999,"Lag",0.98113401277476997,25.216317145045601]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",141.48074,"Lag",0.98122452170421304,27.809378398746301]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",131.12644,"Lag",0.980999824405837,25.9323793918572]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",78.301230000000004,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",76.745429999999999,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",79.426100000000005,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",77.846159999999998,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",81.699749999999995,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",80.115930000000006,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",84.882469999999998,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",83.287440000000004,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",88.622739999999993,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",87.013059999999996,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",92.597430000000003,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",90.981520000000003,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",96.38409,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",94.727580000000003,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",100.11564,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",98.406409999999994,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",104.14521999999999,"Lag","NA","NA"]
["VIC","TTS1266A",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",102.33704,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe10",110.52264,"Lag",0.98192354806895399,21.304611503714298]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe50",102.53066,"Lag",0.98175983165752201,19.855847364846699]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe10",128.50501,"Lag",0.98192003646658998,24.773409236238699]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe50",121.04428,"Lag",0.98179040585630095,23.420948635264399]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe10",129.15222,"Lag",0.98157697483796302,25.139895000747401]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe50",121.34323999999999,"Lag",0.98141819605843295,23.724304598227]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe10",131.61861999999999,"Lag",0.98126348779859895,25.843253450812998]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe50",123.71109,"Lag",0.981084368215702,24.409798175521999]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe10",133.45634999999999,"Lag",0.98088781873395303,26.4731103613776]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe50",125.72763,"Lag",0.98069070772220901,25.072069270765599]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe10",136.48845,"Lag",0.98056644016349703,27.307991892012598]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe50",128.37422000000001,"Lag",0.98034171601101905,25.837066609601401]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe10",132.70381,"Lag",0.98009168577765304,26.882928709334202]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe50",124.40586,"Lag",0.979819875114464,25.3786991709574]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe10",135.62844999999999,"Lag",0.97986344032277295,27.637292782255301]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe50",127.3115,"Lag",0.97958082478882003,26.129618976170299]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe10",139.22784999999999,"Lag",0.97971686708155803,28.477023366108401]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe50",130.59573,"Lag",0.97942020256683904,26.9122164098345]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe10",142.24029999999999,"Lag",0.97950137697761097,29.252154406879001]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe50",133.48557,"Lag",0.97919135204609697,27.665121047252299]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe10",100.81831,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe50",98.103139999999996,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe10",120.30346,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe50",117.45574999999999,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe10",123.28863,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe50",120.43204,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe10",127.60004000000001,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe50",124.71925,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe10",132.70631,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe50",129.79413,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe10",138.11892,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe50",135.18763000000001,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe10",135.99082999999999,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe50",133.01403999999999,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe10",140.89177000000001,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe50",137.82907,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe10",146.25385,"Lag","NA","NA"]
["VIC","TTS1266J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 12 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe50",143.03815,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe10",274.22467999999998,"Lag",0.98290109231045497,51.372586317216097]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe50",251.08020999999999,"Lag",0.98280158243013505,47.1770204938408]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe10",276.36640999999997,"Lag",0.982754184623992,52.001594349587201]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe50",253.01062999999999,"Lag",0.98264051267598296,47.767722830979501]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe10",279.80119000000002,"Lag",0.98261303738470196,52.868607795232599]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe50",255.58716999999999,"Lag",0.98248249306464597,48.479156891473501]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe10",287.01810999999998,"Lag",0.98249866521246398,54.415092200583103]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe50",262.38515999999998,"Lag",0.98235812349637697,49.949698819403402]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe10",293.21821999999997,"Lag",0.98237838416986101,55.786394845405198]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe50",268.80862000000002,"Lag",0.98223104526681204,51.361489737521502]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe10",301.70051999999998,"Lag",0.98226154484500405,57.5953327785504]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe50",276.24171000000001,"Lag",0.98210072219739397,52.980229769503097]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe10",309.86304999999999,"Lag",0.98216174807337098,59.324278836679703]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe50",284.32713000000001,"Lag",0.98199561886151998,54.695197539054597]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe10",317.76983000000001,"Lag",0.98208767575744005,60.967698672768798]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe50",292.01805000000002,"Lag",0.98191768497613496,56.299486868433704]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe10",326.79694000000001,"Lag",0.98203609553228699,62.792341561966403]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe50",300.12437,"Lag",0.98185994630692597,57.9572114806301]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe10",334.85464999999999,"Lag",0.98196986610639603,64.462355812301496]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe50",307.73808000000002,"Lag",0.98178905724569798,59.546738632942301]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe10",208.58038999999999,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe50",204.66744,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe10",211.26727,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe50",207.29402999999999,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe10",216.73166000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe50",212.75755000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe10",224.41319999999999,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe50",220.42266000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe10",233.42953,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe50",229.41433000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe10",242.96234999999999,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe50",238.9443,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe10",251.83376000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe50",247.72183000000001,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe10",260.57657999999998,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe50",256.33803,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe10",270.12009,"Lag","NA","NA"]
["VIC","TTS3466J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"TTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Thomastown 34 (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe50",265.63470000000001,"Lag","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe10",39.513449999999999,"Lead",0.99999561628382805,-0.116999118576258]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2024,"poe50",39.743510000000001,"Lead",0.999995617295795,-0.117666741098894]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe10",39.683160000000001,"Lead",0.99999560071618099,-0.11771008395985]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2025,"poe50",39.93047,"Lead",0.99999560189734005,-0.118427765112911]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe10",40.022669999999998,"Lead",0.99999559124036796,-0.11884494188983399]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2026,"poe50",40.199159999999999,"Lead",0.99999559212019296,-0.11935710697294299]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe10",40.800139999999999,"Lead",0.99999555867838097,-0.121600177725549]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2027,"poe50",41.020209999999999,"Lead",0.99999555993244105,-0.122238809771783]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe10",41.382860000000001,"Lead",0.99999552293264704,-0.123832252237634]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2028,"poe50",41.725990000000003,"Lead",0.99999552515700696,-0.124827998200392]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe10",42.337449999999997,"Lead",0.99999551304072398,-0.12682860627450601]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2029,"poe50",42.636830000000003,"Lead",0.99999551501162498,-0.12769739194270899]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe10",43.208300000000001,"Lead",0.99999550906954204,-0.129494643787995]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2030,"poe50",43.602130000000002,"Lead",0.99999551164174305,-0.13063751859495701]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe10",43.924999999999997,"Lead",0.99999548664707605,-0.131970810960755]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2031,"poe50",44.377929999999999,"Lead",0.99999548978981001,-0.13328519098847599]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe10",44.751750000000001,"Lead",0.99999546491037605,-0.134778132673118]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2032,"poe50",45.167499999999997,"Lead",0.99999546795182104,-0.13598461821509]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe10",45.51717,"Lead",0.99999545767334497,-0.13719267085365699]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Summer","Coincident",2033,"poe50",45.958080000000002,"Lead",0.999995460915303,-0.138472169447309]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe10",14.01929,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2024,"poe50",13.015650000000001,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe10",14.118449999999999,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2025,"poe50",13.10772,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe10",14.394030000000001,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2026,"poe50",13.371079999999999,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe10",14.808400000000001,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2027,"poe50",13.76524,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe10",15.292899999999999,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2028,"poe50",14.22597,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe10",15.79288,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2029,"poe50",14.70341,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe10",16.24484,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2030,"poe50",15.13034,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe10",16.67643,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2031,"poe50",15.536160000000001,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe10",17.15006,"Lead","NA","NA"]
["VIC","WETS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WETS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wemen (Powercor) 66 kV","Powercor","MAX_DEMAND","Winter","Coincident",2032,"poe50",15.97489,"Lead","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe10",51.698050000000002,"Lag",0.92794296196029202,20.7652982740426]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe50",48.649079999999998,"Lag",0.92788763741256597,19.549018818750501]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe10",52.511600000000001,"Lag",0.927748038626386,21.123951507270199]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe50",49.430639999999997,"Lag",0.927680811100284,19.894910765453599]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe10",53.506219999999999,"Lag",0.92749881847965299,21.565548483217299]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe50",50.269860000000001,"Lag",0.92741324162731598,20.274516371412599]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe10",55.053400000000003,"Lag",0.92726329083058801,22.2294351431044]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe50",51.771239999999999,"Lag",0.92716398555437196,20.920132730492501]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe10",56.362110000000001,"Lag",0.92703967291488598,22.796996730780599]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe50",53.153170000000003,"Lag",0.926931501277659,21.516902864568401]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe10",58.080080000000002,"Lag",0.92681749502812305,23.531895368750401]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe50",54.70288,"Lag",0.92669303677716097,22.184680087389001]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe10",59.67765,"Lag",0.92662141575548496,24.215432807278901]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe50",56.318170000000002,"Lag",0.92648935073620098,22.875286297321502]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe10",61.140749999999997,"Lag",0.92638781996406505,24.853332329581701]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe50",57.76473,"Lag",0.92624462906073701,23.506587767760799]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe10",62.706189999999999,"Lag",0.92620928457039098,25.5243023428126]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe50",59.183,"Lag",0.92605267876199604,24.118849480340799]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe10",64.127099999999999,"Lag",0.926100769719019,26.1241888798723]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe50",60.548310000000001,"Lag",0.92593878671502505,24.6965563509183]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe10",48.88897,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe50",47.869210000000002,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe10",49.82808,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe50",48.787019999999998,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe10",51.296880000000002,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe50",50.248980000000003,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe10",53.177250000000001,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe50",52.119480000000003,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe10",55.305810000000001,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe50",54.235959999999999,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe10",57.485210000000002,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe50",56.408470000000001,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe10",59.488329999999998,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe50",58.38355,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe10",61.387300000000003,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe50",60.24785,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe10",63.392069999999997,"Lag","NA","NA"]
["VIC","WMTS22C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"West Melbourne (CitiPower) 22 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe50",62.190510000000003,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe10",204.25093000000001,"Lag",0.98498598341244603,35.798197530897397]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2024,"poe50",196.34155999999999,"Lag",0.98493664088419997,34.4697538846303]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe10",205.19981000000001,"Lag",0.98472361316863699,36.284650482962597]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2025,"poe50",197.22704999999999,"Lag",0.98466303114184495,34.945559965612603]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe10",206.86229,"Lag",0.98443230397210602,36.933952569684898]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2026,"poe50",198.35249999999999,"Lag",0.98435485893596497,35.504663453539401]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe10",211.12117000000001,"Lag",0.98416079843994297,38.029515908507001]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2027,"poe50",202.5385,"Lag",0.98407211083202395,36.587985997843198]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe10",214.48453000000001,"Lag",0.98387659574320097,38.988905362467001]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2028,"poe50",206.2681,"Lag",0.98378114865365496,37.608888467505899]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe10",219.21198000000001,"Lag",0.98357475516037296,40.228804217911403]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2029,"poe50",210.4477,"Lag",0.983461438743372,38.7567714162969]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe10",223.69275999999999,"Lag",0.98330287136292405,41.398064562716897]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2030,"poe50",215.09302,"Lag",0.98318231759771402,39.953667605367698]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe10",228.27030999999999,"Lag",0.98310741663071899,42.498109482861203]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2031,"poe50",219.71395999999999,"Lag",0.98298171032881498,41.061000232347197]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe10",233.70638,"Lag",0.98296783951621003,43.694217397572103]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2032,"poe50",224.69917000000001,"Lag",0.98283232217582395,42.181382507423699]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe10",238.35214999999999,"Lag",0.98280159739321504,44.785446232162897]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Summer","Coincident",2033,"poe50",229.21841000000001,"Lag",0.98265962059504197,43.251359589401801]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe10",164.68081000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2024,"poe50",161.02529000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe10",166.96608000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2025,"poe50",163.25366,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe10",171.38951,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2026,"poe50",167.66095000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe10",177.50006999999999,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2027,"poe50",173.73844,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe10",184.59829999999999,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2028,"poe50",180.79481999999999,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe10",192.02399,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2029,"poe50",188.19577000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe10",198.95052000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2030,"poe50",195.02798000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe10",205.72129000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2031,"poe50",201.68001000000001,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe10",213.06187,"Lag","NA","NA"]
["VIC","WMTS66C",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (CitiPower) 66 kV","Citipower","MAX_DEMAND","Winter","Coincident",2032,"poe50",208.80627999999999,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe10",68.431190000000001,"Lag",0.98530064852643995,11.8644484332434]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2024,"poe50",61.8446,"Lag",0.98520477848645704,10.7581765511508]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe10",68.977819999999994,"Lag",0.98510497632595495,12.040354936754801]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2025,"poe50",62.315170000000002,"Lag",0.98498708110461297,10.9213081530285]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe10",69.793599999999998,"Lag",0.98487476501398796,12.2786949704715]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2026,"poe50",62.890540000000001,"Lag",0.98472739808445298,11.1192693529064]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe10",71.534260000000003,"Lag",0.98466209258307902,12.675153087856]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2027,"poe50",64.489009999999993,"Lag",0.98449104508551,11.4918454920724]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe10",73.037989999999994,"Lag",0.98444494479325495,13.0350495225307]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2028,"poe50",66.012929999999997,"Lag",0.98425393953517804,11.855133003055]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe10",75.102270000000004,"Lag",0.98422752799942004,13.4990490078709]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2029,"poe50",67.776830000000004,"Lag",0.98400856372483403,12.26868120056]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe10",77.133300000000006,"Lag",0.98403516529322499,13.9504491212818]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2030,"poe50",69.749750000000006,"Lag",0.98379896325352301,12.7103212622493]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe10",79.190089999999998,"Lag",0.98389423431189005,14.387070337991201]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2031,"poe50",71.720010000000002,"Lag",0.98364608754296001,13.1324090548414]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe10",81.500690000000006,"Lag",0.98378774350476705,14.8569346268264]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2032,"poe50",73.772739999999999,"Lag",0.98352615584895697,13.558961959449601]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe10",83.638149999999996,"Lag",0.98369046346585098,15.2933884494976]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Summer","Coincident",2033,"poe50",75.775589999999994,"Lag",0.98342046459991295,13.972806927152099]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe10",61.023260000000001,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2024,"poe50",58.804340000000003,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe10",61.983840000000001,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2025,"poe50",59.728619999999999,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe10",63.777540000000002,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2026,"poe50",61.490609999999997,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe10",66.234560000000002,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2027,"poe50",63.90155,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe10",69.120149999999995,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2028,"poe50",66.733670000000004,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe10",72.192130000000006,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2029,"poe50",69.757940000000005,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe10",75.09778,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2030,"poe50",72.593549999999993,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe10",77.956599999999995,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2031,"poe50",75.374880000000005,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe10",81.039929999999998,"Lag","NA","NA"]
["VIC","WMTS66J",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WMTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"West Melbourne (Jemena) 66 kV","Jemena","MAX_DEMAND","Winter","Coincident",2032,"poe50",78.342740000000006,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",34.931319999999999,"Lag",0.97005218345989397,8.7466419097428094]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",31.415510000000001,"Lag",0.96976252316403,7.9060294415687702]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",34.834359999999997,"Lag",0.96920134097799104,8.8512538174677005]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",31.282689999999999,"Lag",0.96880628249004297,8.0020674038561399]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",34.802410000000002,"Lag",0.96816393992398897,8.9980977992860094]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",31.129930000000002,"Lag",0.96762353539673795,8.1200263229776297]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",35.640279999999997,"Lag",0.96792205930603803,9.2514095396986402]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",31.902439999999999,"Lag",0.96735505476652495,8.3577108164912897]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",36.460900000000002,"Lag",0.96783331910880199,9.4781613047054893]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",32.743029999999997,"Lag",0.96727308788990396,8.5892373079450905]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",37.624569999999999,"Lag",0.96782849542945604,9.7814322030027903]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",33.768749999999997,"Lag",0.96726452326316403,8.8595250558489909]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",38.676389999999998,"Lag",0.967702770392877,10.0754935777914]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",34.801049999999996,"Lag",0.96713778590982002,9.1489192969248396]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",39.670389999999998,"Lag",0.96758950691398804,10.353457095846]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",35.759590000000003,"Lag",0.96702136487659596,9.4184045075277592]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",40.850360000000002,"Lag",0.96758868974509804,10.6615551495545]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",36.817819999999998,"Lag",0.96701960062513104,9.6973951402222607]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",41.913640000000001,"Lag",0.96755485986271705,10.9450571230355]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",37.819830000000003,"Lag",0.96698851779900896,9.9662477652102304]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",28.532109999999999,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",27.999279999999999,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",28.85107,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",28.311240000000002,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",29.570319999999999,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",29.031410000000001,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",30.60914,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",30.06887,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",31.840499999999999,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",31.29776,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",33.150700000000001,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",32.608469999999997,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",34.373350000000002,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",33.819229999999997,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",35.578180000000003,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",35.007730000000002,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",36.894489999999998,"Lag","NA","NA"]
["VIC","WOTS22",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"22 kV"},"Wodonga (AusNet) 22 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",36.291350000000001,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",54.150579999999998,"Lag",0.98878952877589599,8.1772184623338102]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",50.588349999999998,"Lag",0.98872536101094899,7.6614958201458299]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",54.588410000000003,"Lag",0.98869254966402897,8.2795236509958805]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",50.999760000000002,"Lag",0.98862130801217996,7.7599760474194897]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",55.069760000000002,"Lag",0.98850836437262202,8.4214615454879205]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",51.3217,"Lag",0.98842030535716197,7.8788353236327602]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",56.153930000000003,"Lag",0.98827864443367097,8.6741771943392401]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",52.341119999999997,"Lag",0.98817310565359295,8.1221767768028208]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",57.314720000000001,"Lag",0.98816741135699304,8.8961481473204707]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",53.568339999999999,"Lag",0.98805781346827604,8.3537651478397503]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",59.125900000000001,"Lag",0.98814729186494799,9.1852113314256698]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",55.207270000000001,"Lag",0.988034530284289,8.6178907998044405]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",60.775210000000001,"Lag",0.98809625076048502,9.4621059071924396]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",56.872100000000003,"Lag",0.98798348857409202,8.8970322870302496]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",62.338549999999998,"Lag",0.98804947355140005,9.7248994092245002]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",58.419609999999999,"Lag",0.987935899944689,9.1575339972841796]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",64.132499999999993,"Lag",0.98802462217626996,10.015344533151101]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",60.060830000000003,"Lag",0.98790803838407304,9.4258676014207801]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",65.747630000000001,"Lag",0.98799283461006404,10.281440376212201]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",61.615740000000002,"Lag",0.98787522804641803,9.6832450805602495]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",41.236710000000002,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",40.379460000000002,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",41.777369999999998,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",40.907389999999999,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",42.877600000000001,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",42.005420000000001,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",44.42794,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",43.549460000000003,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",46.239899999999999,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",45.353169999999999,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",48.148260000000001,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",47.257579999999997,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",49.925370000000001,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",49.013089999999998,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",51.673760000000001,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",50.733539999999998,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",53.577660000000002,"Lag","NA","NA"]
["VIC","WOTS66",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"WOTS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"66 kV"},"Wodonga (AusNet) 66 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",52.585500000000003,"Lag","NA","NA"]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe10",0.28971000000000002,"Lead",0.99944954986767498,-9.6164953263663307E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2024,"poe50",0.28498000000000001,"Lead",0.99944954986767498,-9.4594899662002602E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe10",0.28971000000000002,"Lead",0.99944954986767498,-9.6164953263663307E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2025,"poe50",0.28498000000000001,"Lead",0.99944954986767498,-9.4594899662002602E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe10",0.28971000000000002,"Lead",0.99944954986767498,-9.6164953263663307E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2026,"poe50",0.28498000000000001,"Lead",0.99944954986767498,-9.4594899662002602E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe10",0.28971000000000002,"Lead",0.99944954986767498,-9.6164953263663307E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2027,"poe50",0.28498000000000001,"Lead",0.99944954986767498,-9.4594899662002602E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe10",0.28971000000000002,"Lead",0.99944954986767498,-9.6164953263663307E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2028,"poe50",0.28498000000000001,"Lead",0.99944954986767498,-9.4594899662002602E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe10",0.28971000000000002,"Lead",0.99944954986767498,-9.6164953263663307E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2029,"poe50",0.28498000000000001,"Lead",0.99944954986767498,-9.4594899662002602E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe10",0.28971000000000002,"Lead",0.99944954986767498,-9.6164953263663307E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2030,"poe50",0.28498000000000001,"Lead",0.99944954986767498,-9.4594899662002602E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe10",0.28971000000000002,"Lead",0.99944954986767498,-9.6164953263663307E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2031,"poe50",0.28498000000000001,"Lead",0.99944954986767498,-9.4594899662002602E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe10",0.28971000000000002,"Lead",0.99944954986767498,-9.6164953263663307E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2032,"poe50",0.28498000000000001,"Lead",0.99944954986767498,-9.4594899662002602E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe10",0.28971000000000002,"Lead",0.99944954986767498,-9.6164953263663307E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Summer","Coincident",2033,"poe50",0.28498000000000001,"Lead",0.99944954986767498,-9.4594899662002602E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe10",0.35905999999999999,"Lag",0.99968919008022095,8.9542809279860303E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2024,"poe50",0.35085,"Lag",0.99968919008022095,8.7495389728287701E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe10",0.35905999999999999,"Lag",0.99968919008022095,8.9542809279860303E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2025,"poe50",0.35085,"Lag",0.99968919008022095,8.7495389728287701E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe10",0.35905999999999999,"Lag",0.99968919008022095,8.9542809279860303E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2026,"poe50",0.35085,"Lag",0.99968919008022095,8.7495389728287701E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe10",0.35905999999999999,"Lag",0.99968919008022095,8.9542809279860303E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2027,"poe50",0.35085,"Lag",0.99968919008022095,8.7495389728287701E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe10",0.35905999999999999,"Lag",0.99968919008022095,8.9542809279860303E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2028,"poe50",0.35085,"Lag",0.99968919008022095,8.7495389728287701E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe10",0.35905999999999999,"Lag",0.99968919008022095,8.9542809279860303E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2029,"poe50",0.35085,"Lag",0.99968919008022095,8.7495389728287701E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe10",0.35905999999999999,"Lag",0.99968919008022095,8.9542809279860303E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2030,"poe50",0.35085,"Lag",0.99968919008022095,8.7495389728287701E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe10",0.35905999999999999,"Lag",0.99968919008022095,8.9542809279860303E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2031,"poe50",0.35085,"Lag",0.99968919008022095,8.7495389728287701E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe10",0.35905999999999999,"Lag",0.99968919008022095,8.9542809279860303E-3]
["VIC","YPS11",{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$B$76,2,FALSE)","v":"YPS"},{"$f":"VLOOKUP(AEMO_DATA_2024[[#This Row],[CP_NAME]],'2024 Lookup'!$A$3:$C$76,3,FALSE)","v":"11 kV"},"Yallourn (AusNet) 11 kV","AusNet","MAX_DEMAND","Winter","Coincident",2032,"poe50",0.35085,"Lag",0.99968919008022095,8.7495389728287701E-3]

{"sheet":"2024 Lookup","index":12,"n_rows":76,"n_cols":40,"rows_kept":76,"cut":false,"hidden":false,"merged":[[1,0,1,2]]}
["Manually update the station acronym and voltage"]
["TO BE AUTOMATED"]
[{"$f":"_xlfn.UNIQUE(AEMO_DATA_2024[CP_NAME])","v":"Altona-Brooklyn (Jemena) 66 kV"},"ATS_BLTS","66 kV",null,"ATS_BLTS","ATS_West","BATS","BETS","BLTS","BTS","CBTS","DPTS","ERTS","FBTS","GNTS","GTS","HOTS","HTS","HYTS","KGTS","KTS","LY","MBTS","MTS","MWTS","NKHN","RCTS","RTS","RWTS","SHTS","SMTS","SVTS","TBTS","TGTS","TSTS","TTS","WETS","WMTS","WOTS","YPS"]
["Altona-Brooklyn (Powercor) 66 kV","ATS_BLTS","66 kV",null,{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=E$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=F$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=G$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=H$3))","v":"22 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=I$3))","v":"22 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=J$3))","v":"22 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=K$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=L$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=M$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=N$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=O$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=P$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=Q$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=R$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=S$3))","v":"22 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=T$3))","v":"22 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=U$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=V$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=W$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=X$3))","v":"22 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=Y$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=Z$3))","v":"11 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AA$3))","v":"22 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AB$3))","v":"22 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AC$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AD$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AE$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AF$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AG$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AH$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AI$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AJ$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AK$3))","v":"66 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AL$3))","v":"22 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AM$3))","v":"22 kV"},{"$f":"_xlfn.UNIQUE(_xlfn._xlws.FILTER(AEMO_DATA_2024[[Voltage]:[Voltage]],AEMO_DATA_2024[[Station]:[Station]]=AN$3))","v":"11 kV"}]
["Altona West (Powercor) 66 kV","ATS_West","66 kV",null,null,null,null,"66 kV","66 kV","66 kV",null,null,null,null,null,null,null,null,null,"66 kV",null,null,null,"66 kV",null,null,"66 kV","66 kV","22 kV",null,null,null,null,null,null,null,null,"66 kV","66 kV"]
["Ballarat (CitiPower) 66 kV","BATS","66 kV"]
["Ballarat (Powercor) 66 kV","BATS","66 kV"]
["Bendigo (Powercor) 22 kV","BETS","22 kV"]
["Bendigo (Powercor) 66 kV","BETS","66 kV"]
["Brooklyn (Jemena) 22 kV","BLTS","22 kV"]
["Brooklyn (Powercor) 22 kV","BLTS","22 kV"]
["Brooklyn (Jemena) 66 kV","BLTS","66 kV"]
["Brooklyn (Powercor) 66 kV","BLTS","66 kV"]
["Brunswick (CitiPower) 22 kV","BTS","22 kV"]
["Brunswick (Jemena) 22 kV","BTS","22 kV"]
["Brunswick (CitiPower) 66 kV","BTS","66 kV"]
["Cranbourne (AusNet) 66 kV","CBTS","66 kV"]
["Cranbourne (United Energy) 66 kV","CBTS","66 kV"]
["Deer Park (Powercor) 66 kV","DPTS","66 kV"]
["East Rowville 12 (AusNet) 66 kV","ERTS","66 kV"]
["East Rowville 12 (United Energy) 66 kV","ERTS","66 kV"]
["East Rowville 34 (AusNet) 66 kV","ERTS","66 kV"]
["East Rowville 34 (United Energy) 66 kV","ERTS","66 kV"]
["Fishermans Bend (Citipower) 66 kV","FBTS","66 kV"]
["Fishermans Bend (Powercor) 66 kV","FBTS","66 kV"]
["Glenrowan (AusNet) 66 kV","GNTS","66 kV"]
["Geelong 12 (Powercor) 66 kV","GTS","66 kV"]
["Geelong 34 (Powercor) 66 kV","GTS","66 kV"]
["Horsham (Powercor) 66 kV","HOTS","66 kV"]
["Heatherton (United Energy) 66 kV","HTS","66 kV"]
["Heywood (Powercor) 22 kV","HYTS","22 kV"]
["Kerang (Powercor) 22 kV","KGTS","22 kV"]
["Kerang (Powercor) 66 kV","KGTS","66 kV"]
["Keilor East (Jemena) 66 kV","KTS","66 kV"]
["Keilor East (Powercor) 66 kV","KTS","66 kV"]
["Keilor West (Jemena) 66 kV","KTS","66 kV"]
["Keilor West (Powercor) 66 kV","KTS","66 kV"]
["Loy Yang (AusNet) 66 kV","LY","66 kV"]
["Mt Beauty (AusNet) 66 kV","MBTS","66 kV"]
["Malvern (United Energy) 22 kV","MTS","22 kV"]
["Malvern (United Energy) 66 kV","MTS","66 kV"]
["Morwell (Ausnet) 66 kV","MWTS","66 kV"]
["Khancoban (Essential Energy) 11 kV","NKHN","11 kV"]
["Red Cliffs (Powercor) 22 kV","RCTS","22 kV"]
["Red Cliffs (Powercor) 66 kV","RCTS","66 kV"]
["Richmond (CitiPower) 22kV","RTS","22 kV"]
["Richmond 66kV (Citipower Total)","RTS","66 kV"]
["Richmond 66kV (United Energy Total)","RTS","66 kV"]
["Ringwood 13 (AusNet) 66 kV","RWTS","66 kV"]
["Ringwood 13 (United Energy) 66 kV","RWTS","66 kV"]
["Ringwood (AusNet) 22 kV","RWTS","22 kV"]
["Ringwood (United Energy) 22 kV","RWTS","22 kV"]
["Ringwood 24 (AusNet) 66 kV","RWTS","66 kV"]
["Ringwood 24 (United Energy) 66kV","RWTS","66 kV"]
["Shepparton (Powercor) 66 kV","SHTS","66 kV"]
["South Morang (AusNet) 66 kV","SMTS","66 kV"]
["South Morang (Jemena) 66 kV","SMTS","66 kV"]
["Springvale 12 (United Energy) 66 kV","SVTS","66 kV"]
["Springvale 34 (CitiPower) 66 kV","SVTS","66 kV"]
["Springvale 34 (United Energy) 66 kV","SVTS","66 kV"]
["Tyabb (United Energy) 66 kV","TBTS","66 kV"]
["Terang (Powercor) 66 kV","TGTS","66 kV"]
["Templestowe (AusNet) 66 kV","TSTS","66 kV"]
["Templestowe (CitiPower) 66 kV","TSTS","66 kV"]
["Templestowe (Jemena) 66 kV","TSTS","66 kV"]
["Templestowe (United Energy) 66 kV","TSTS","66 kV"]
["Thomastown 12 (AusNet) 66 kV","TTS","66 kV"]
["Thomastown 12 (Jemena) 66 kV","TTS","66 kV"]
["Thomastown 34 (Jemena) 66 kV","TTS","66 kV"]
["Wemen (Powercor) 66 kV","WETS","66 kV"]
["West Melbourne (CitiPower) 22 kV","WMTS","22 kV"]
["West Melbourne (CitiPower) 66 kV","WMTS","66 kV"]
["West Melbourne (Jemena) 66 kV","WMTS","66 kV"]
["Wodonga (AusNet) 22 kV","WOTS","22 kV"]
["Wodonga (AusNet) 66 kV","WOTS","66 kV"]
["Yallourn (AusNet) 11 kV","YPS","11 kV"]