{"text_format":"1","workbook":"xlsx","n_sheets":4,"sheets":["B Tx MTTR Calc","Cleaned up","Metro B Tx POFs","Country B & L Tx POFs"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":2,"defined_names":131,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"B Tx MTTR Calc","index":0,"n_rows":36,"n_cols":22,"rows_kept":36,"cut":false,"hidden":true,"merged":[]}
[]
[null,"Assumptions",null,null,null,null,null,null,"Power Transformer Failure Rates","AGE","2019/20","2020/21","2021/22","2022/23","2023/24","2024/25","2025/26","2026/27","2027/28","2028/29","2029/30","2030/31"]
[null,"Transformer Failure Rate = ",2.3287860133643826E-2,"Use average failure rate (C3)",null,null,null,null,1,2.5,3.9131189606246301E-5,9.0749269969515515E-5,1.7010000000000018E-4,2.8091811974310254E-4,4.2653671588738999E-4,6.0999487702766858E-4,8.3410426806245354E-4,1.1014937630327291E-3,1.4146411170328681E-3,1.7758964130827005E-3,2.1875000000000024E-3,2.6515965813071951E-3]
[null,"Number of transformers = ",60,"51 Metro and 30 Country Transformers",null,null,null,null,2,15,3.4506521122825489E-3,4.0548331260361406E-3,4.7184062733088197E-3,5.4432000000000031E-3,6.2309896742010415E-3,7.0835019587771704E-3,8.0024186143940294E-3,8.9893798317792848E-3,1.0045987171005152E-2,1.1173806169788348E-2,1.2374368670764585E-2,1.3649174908396487E-2]
[null,"Time to replace with spare trfr (months) = ",1,null,null,null,null,null,3,27.5,1.5703800296425076E-2,1.7170588456136286E-2,1.8716647843831462E-2,2.0343357330834089E-2,2.2052072602592246E-2,2.3844127290592959E-2,2.5720834015054799E-2,2.7683485347947085E-2,2.9733354704607442E-2,3.1871697171158044E-2,3.4099750274012283E-2,3.6418734696993596E-2]
[null,"Time to repair or procure trfr (months) = ",12,null,null,null,null,null,4,37.5,3.4099750274012283E-2,3.6418734696993596E-2,3.8829854950926612E-2,4.1334300000000039E-2,4.3933243848707532E-2,4.6627846092758822E-2,4.9419252436980483E-2,5.2308595182914343E-2,5.5296993688536161E-2,5.8385554802279666E-2,6.1575373273330611E-2,6.4867532139969653E-2]
[null,null,null,null,null,null,null,null,5,42.5,4.6627846092758822E-2,4.9419252436980483E-2,5.2308595182914343E-2,5.5296993688536161E-2,5.8385554802279666E-2,6.1575373273330611E-2,6.4867532139969653E-2,6.8263103097573954E-2,7.1763146847738046E-2,7.5368713429844456E-2,7.9080842536293203E-2,8.2900563812497732E-2]
[null,"Two spare transformers calculation"]
[null,"State","1st Spare","2nd Spare","Percentage of Time"]
[null,"No spare transformers available",0,0,{"$f":"1-SUM(E11:E13)","v":0.40883828558498791},{"$f":"SUM(E10:E12)","v":0.75678231849406763},0.15,{"$f":"E10*12","v":4.906059427019855},null,{"$f":"G10*12","v":1.7999999999999998}]
[null,"One spare transformer available",0,1,{"$f":"C4*(C3*((1-C3)^(C4-1)))/2","v":0.17397201645453983},null,{"$f":"1-G10","v":0.85},{"$f":"SUM(E11:E13)*1","v":0.59116171441501209},null,{"$f":"SUM(G11:G13)*1","v":0.85}]
[null,"One spare transformer available",1,0,{"$f":"E11","v":0.17397201645453983},{"$f":"SUM(E11:E12)","v":0.34794403290907966},null,{"$f":"SUM(H10:H11)","v":5.4972211414348671},null,{"$f":"SUM(J10:J11)","v":2.65}]
[null,"Both spare transformers available",1,1,{"$f":"(1-C3)^C4","v":0.24321768150593243},{"$f":"SUM(E11:E13)","v":0.59116171441501209}]
[]
[null,"N-1 Contingency"]
[null,"MTTR N-1 = ",{"$f":"E10*$C$6+(1-E10)*$C$5","v":5.4972211414348671},"Months"]
[null,"Factor = ",{"$f":"C16/12","v":0.4581017617862389},{"$f":"C17*12","v":5.4972211414348671}]
[]
[null,"N-2 Contingency"]
[null,"MTTR N-2 = ",{"$f":"(E10+E11+E12)*$C$6+E13*$C$5","v":9.3246055034347428},"Months",{"$f":"C20/12","v":0.7770504586195619},null,null,30,1.8165421383103046]
[null,"Factor = ",{"$f":"(C20/12)*C17","v":0.35596818409042624},null,null,null,null,51,2.9584631070922223]
[null,null,null,null,null,null,null,{"$f":"SUM(H20:H21)","v":81},{"$f":"(H20*I20+H21*I21)/H22","v":2.535529414950771}]
[null,"N-3 Contingency"]
[null,"MTTR N-3 = ",{"$f":"C6","v":12},"Months"]
[null,"Factor = ",{"$f":"(C24/12)*C21","v":0.35596818409042624}]
[]
[]
[]
[]
[]
[null,"Power Transformer Failure Rates","AGE","2020/21","2021/22"]
[null,1,2.5,3.9131189606246301E-5,9.0749269969515515E-5]
[null,2,15,3.4506521122825489E-3,4.0548331260361406E-3]
[null,3,27.5,1.5703800296425076E-2,1.7170588456136286E-2]
[null,4,37.5,3.4099750274012283E-2,3.6418734696993596E-2]
[null,5,42.5,4.6627846092758822E-2,4.9419252436980483E-2]

{"sheet":"Cleaned up","index":1,"n_rows":40,"n_cols":12,"rows_kept":40,"cut":false,"hidden":false,"merged":[[28,4,28,5],[27,3,27,5],[1,1,1,5],[1,7,1,11],[27,9,27,11],[28,10,28,11]]}
[]
[null,"Metro B Transformer - MTTR Calculation",null,null,null,null,null,"Country B Transformer - MTTR Calculation"]
[]
[null,"Assumptions ",null,null,null,null,null,"Assumptions "]
[null,"Transformer Failure Rate",{"$f":"MEDIAN('Metro B Tx POFs'!K2:K61)","v":1.9204861937895057E-2},"Using median failure rate of metro B Tx fleet",null,null,null,"Transformer Failure Rate",{"$f":"MEDIAN('Country B & L Tx POFs'!K:K)","v":2.4747248876740569E-2},"Using median failure rate of country B Tx fleet"]
[null,"Number of transformers",{"$f":"COUNT('Metro B Tx POFs'!K2:K61)","v":60},null,null,null,null,"Number of transformers",{"$f":"COUNT('Country B & L Tx POFs'!K2:K103)","v":30}]
[null,"Time to replace with spare transformer (% of the year)  ",{"$f":"1/12","v":8.3333333333333329E-2},null,null,null,null,"Time to replace with spare transformer (% of the year)  ",{"$f":"1/12","v":8.3333333333333329E-2}]
[null,"Time to repair or procure transformer (% of the year) ",1,null,null,null,null,"Time to repair or procure transformer (% of the year) ",1]
[]
[]
[null,"Two spare transformers calculation",null,null,null,null,null,"Two spare transformers calculation"]
[null,"State","1st Spare","2nd Spare","Percentage of Time","Comments",null,"State","1st Spare","2nd Spare","Percentage of Time","Comments"]
[null,"No spare transformers available",0,0,{"$f":"1-SUM(E14:E16)","v":0.32059538240352559},null,null,"No spare transformers available",0,0,{"$f":"1-SUM(K14:K16)","v":0.16950289202202373}]
[null,"One spare transformer available",0,1,{"$f":"C6*(C5*((1-C5)^(C6-1)))/2","v":0.18350690016752463},null,null,"One spare transformer available",0,1,{"$f":"I6*(I5*((1-I5)^(I6-1)))/2","v":0.17948019137238108}]
[null,"One spare transformer available",1,0,{"$f":"E14","v":0.18350690016752463},"Same as above",null,"One spare transformer available",1,0,{"$f":"K14","v":0.17948019137238108},"Same as above"]
[null,"Both spare transformers available",1,1,{"$f":"(1-C5)^C6","v":0.31239081726142515},null,null,"Both spare transformers available",1,1,{"$f":"(1-I5)^I6","v":0.4715367252332141}]
[]
[]
[null,"N-1 Contingency",null,null,null,null,null,"N-1 Contingency"]
[null,"MTTR N-1 - Failure of one metro B transformer",{"$f":"E13*$C$8+(1-E13)*$C$7","v":0.37721243386989844},null,null,null,null,"MTTR N-1",{"$f":"K13*$I$8+(1-K13)*$I$7","v":0.23871098435352175}]
[null,"MTTR associated with the first metro B transformer",{"$f":"C20*12","v":4.5265492064387818},"months",null,null,null,"Factor",{"$f":"I20*12","v":2.8645318122422609},"months"]
[]
[null,"N-2 Contingency",null,null,null,null,null,"N-2 Contingency"]
[null,"MTTR N-2 - Failure of a second metro B transformer",{"$f":"((E13+E14+E15)*$C$8+(E16)*$C$7)*C20","v":0.26919454174692531},null,null,null,null,"MTTR N-2",{"$f":"((K13+K14+K15)*$I$8+(K16)*$I$7)*I20","v":0.13553007150086982}]
[null,"MTTR associated with the second metro B transformer",{"$f":"C24/C20*12","v":8.5637010101243227},"months",null,null,null,"Factor",{"$f":"I24/I20*12","v":6.8130960224346442},"months"]
[]
[null,"N-3 Contingency",null,null,null,null,null,"N-3 Contingency"]
[null,"MTTR N-3 - Failure of a third metro B transformer",{"$f":"C24*C8","v":0.26919454174692531},"MTTR N-1 x MTTR N-2 x MTTR N-3",null,null,null,"MTTR N-3",{"$f":"I24*I8","v":0.13553007150086982},"MTTR N-1 x MTTR N-2 x MTTR N-3"]
[null,"MTTR associated with the third metro B transformer",{"$f":"C28/C24*12","v":12},"months","Procuring a new transformer",null,null,"Factor",{"$f":"I28/I24*12","v":12},"months","Procuring a new transformer"]
[]
[null,"N-4 Contingency",null,null,null,null,null,"N-4 Contingency"]
[null,"MTTR N-4 - Failure of a fourth metro B transformer",{"$f":"C24*C8","v":0.26919454174692531},null,null,null,null,"MTTR N-3",{"$f":"I24*I8","v":0.13553007150086982}]
[null,"MTTR associated with the fourth metro B transformer",{"$f":"C32/C28*12","v":12},"months",null,null,null,"Factor",{"$f":"I32/I28*12","v":12},"months"]
[]
[]
[null,null,"Input"]
[null,null,"Calculation"]
[null,null,"Output"]
[null,null,"Note"]
[null,null,"Explanation"]

{"sheet":"Metro B Tx POFs","index":2,"n_rows":61,"n_cols":36,"rows_kept":61,"cut":false,"hidden":false,"merged":[]}
["Station","FLOC","FLOC Description","Equipment ID","Start-Up Date","Age","Object Type","Nominal Voltage (kV)","Manufacturer","User Status","PoF '25","PoF '26","PoF '27","PoF '28","PoF '29","PoF '30","PoF '31","PoF '32","PoF '33","PoF '34","PoF '35","PoF '36","PoF '37","PoF '38","PoF '39","PoF '40","Safety CoF ($)","Environment CoF ($)","Total Risk '26 ($)","Total Risk '27 ($)","Total Risk '28 ($)","Total Risk '29 ($)","Total Risk '30 ($)","Total Risk '31 ($)","Total Risk '32 ($)","Likelihood"]
["ATS","TS-ATSX-TRNFMR-9000100001","B2 TR","30418395","1/01/1992","33","PT",220,"WILSON","SERV",3.4206684268950238E-2,3.511074706808448E-2,3.6024295945642049E-2,3.6947265589859835E-2,3.7879591220282061E-2,3.882120856809701E-2,3.9772053857473622E-2,4.0732063787836448E-2,4.1701175517012801E-2,4.2679326645216675E-2,4.3666455199811383E-2,4.4662499620801044E-2,4.566739874703285E-2,4.6681091803034924E-2,4.7703518386489785E-2,4.8734618456285239E-2,109557.3,500,72636.672084472521,77586.769461097414,82826.233509525555,88368.168421615963,94226.063880184782,100413.79950895833,106945.65074238319,"3"]
["ATS","TS-ATSX-TRNFMR-9000102131","B4 TR","30289167","17/01/2008","17","PT",220,"AREVA","SERV",1.9957226012379148E-2,2.0683475554232333E-2,2.1420472117498868E-2,2.2168136330492527E-2,2.2926389961281823E-2,2.369515586267501E-2,2.4474357920729717E-2,2.5263921006501433E-2,2.6063770930786601E-2,2.6873834401624941E-2,2.7694038984356295E-2,2.8524313064041906E-2,2.9364585810077948E-2,3.0214787142847421E-2,3.1074847702262209E-2,3.1944698818065276E-2,109557.3,500,49138.982067257639,53015.369620278536,57137.176298757069,61516.153727103927,66164.425143231943,71094.490247596113,76319.23086903822,"1"]
["ATS","TS-ATSX-TRNFMR-9000102027","B3 TR","30253033","30/10/2004","20","PT",220,"ALSTOM","SERV",1.8955861948624642E-2,1.9666886401553896E-2,2.038877135080619E-2,2.1121435724226867E-2,2.1864799673203872E-2,2.261878451217525E-2,2.3383312662103473E-2,2.4158307597598183E-2,2.4943693797386257E-2,2.573939669787384E-2,2.6545342649562209E-2,2.7361458876093758E-2,2.8187673435740801E-2,2.9023915185154014E-2,2.9870113745207649E-2,3.0726199468793514E-2,109557.3,500,41004.012772802955,44449.382004729989,48123.581321141784,52037.944741522639,56204.174394952679,60634.345454877977,65340.912289577238,"1"]
["BLTS","TS-BLTS-TRNFMR-9000102191","B3 TR","30166749","16/12/2013","11","PT",220,"WILSON","SERV",2.046592596249952E-2,2.1199728276112939E-2,2.194422177035793E-2,2.2699327879578401E-2,2.3464969138870417E-2,2.4241069131572868E-2,2.502755244007715E-2,2.5824344599703619E-2,2.6631372055403335E-2,2.7448562121075937E-2,2.8275842941303808E-2,2.9113143455328783E-2,2.9960393363114513E-2,3.0817523093336519E-2,3.1684463773175353E-2,3.2561147199786533E-2,109557.3,500,6426.2777526740101,6919.4680532644488,7446.3206848671471,8008.75696211168,8608.7806533996536,9248.4804938554826,9930.0321619822062,"1"]
["BLTS","TS-BLTS-TRNFMR-9000103745","B5 TR","30439978","22/02/2013","12","PT",220,"WILSON","SERV",1.9957226012379148E-2,2.0683475554232333E-2,2.1420472117498868E-2,2.2168136330492527E-2,2.2926389961281823E-2,2.369515586267501E-2,2.4474357920729717E-2,2.5263921006501433E-2,2.6063770930786601E-2,2.6873834401624941E-2,2.7694038984356295E-2,2.8524313064041906E-2,2.9364585810077948E-2,3.0214787142847421E-2,3.1074847702262209E-2,3.1944698818065276E-2,109557.3,500,6303.7428832095975,6791.2171706055051,7312.1033893197573,7868.3147943639688,8461.8472182886999,9094.7809856827207,9769.2836913702104,"1"]
["BLTS","TS-BLTS-TRNFMR-9000100867","B1 TR","30422361","5/08/2012","13","PT",220,"WILSON","SERV",2.1499222011051922E-2,2.2248012412092399E-2,2.3007384002693088E-2,2.3777259747570723E-2,2.4557563639425295E-2,2.5348220651022046E-2,2.6149156690234765E-2,2.6960298557827778E-2,2.7781573907774582E-2,2.8612911209917269E-2,2.945423971480432E-2,3.0305489420549225E-2,3.1166591041564051E-2,3.2037475979044605E-2,3.2918076293083631E-2,3.380832467630368E-2,109557.3,500,6664.1682123582741,7168.2987428157048,7706.5769271189365,8280.9403342894693,8893.4085420068623,9546.0865464369581,10241.166335781865,"1"]
["BTS","TS-BTSX-TRNFMR-8000000911","B1 TR","32541179","28/06/2016","9","PT",220,"ABB","SERV",1.3409015528344947E-2,1.402513563365404E-2,1.4652858069281072E-2,1.5292088338107024E-2,1.5942733895813466E-2,1.6604704037614604E-2,1.7277909793742219E-2,1.796226383283428E-2,1.8657680372478724E-2,1.9364075096251154E-2,2.0081365076655144E-2,2.0809468703440248E-2,2.1548305616830521E-2,2.2297796645245893E-2,2.305786374713481E-2,2.3828429956587516E-2,109557.3,500,2060.1332476404518,2188.8775226907283,2324.8409134773042,2468.5168459194047,2620.4334609729103,2781.1565728794767,2951.290910642751,"1"]
["BTS","TS-BTSX-TRNFMR-8000000912","B2 TR","32541183","28/06/2016","9","PT",220,"ABB","SERV",1.3409015528344947E-2,1.402513563365404E-2,1.4652858069281072E-2,1.5292088338107024E-2,1.5942733895813466E-2,1.6604704037614604E-2,1.7277909793742219E-2,1.796226383283428E-2,1.8657680372478724E-2,1.9364075096251154E-2,2.0081365076655144E-2,2.0809468703440248E-2,2.1548305616830521E-2,2.2297796645245893E-2,2.305786374713481E-2,2.3828429956587516E-2,109557.3,500,2060.1332476404518,2188.8775226907283,2324.8409134773042,2468.5168459194047,2620.4334609729103,2781.1565728794767,2951.290910642751,"1"]
["BTS","TS-BTSX-TRNFMR-8000000913","B3 TR","32541184","28/06/2016","9","PT",220,"ABB","SERV",9.7909725810378934E-3,1.0331459139145904E-2,1.0884199109630899E-2,1.1449082310122205E-2,1.202600150404054E-2,1.2614852203121085E-2,1.3215532487678816E-2,1.3827942842613239E-2,1.4451986007416595E-2,1.5087566838684396E-2,1.5734592183820895E-2,1.6392970764789738E-2,1.7062613070913835E-2,1.7743431259833908E-2,1.843533906585626E-2,1.9138251714989285E-2,109557.3,500,1535.7567749746609,1647.8834204822067,1766.8366360886143,1893.0901838567036,2027.1519655910533,2169.5678868055402,2320.9219037570729,"1"]
["CBTS","TS-CBTS-TRNFMR-9000103954","B3 TR","30342890","20/12/2009","15","PT",220,"ABB","SERV",1.7018079311710177E-2,1.769816270097424E-2,1.8389341352980204E-2,1.9091530397796763E-2,1.9804646383347113E-2,2.0528607201720672E-2,2.1263332020569292E-2,2.2008741219148198E-2,2.2764756328612079E-2,2.3531299976216835E-2,2.4308295833101679E-2,2.5095668565375706E-2,2.5893343788247147E-2,2.6701248022955371E-2,2.7519308656304586E-2,2.8347453902599518E-2,109557.3,500,1683013.2706302949,1777617.024393769,1875511.9523689239,1976758.8671728289,2081419.752243632,2189557.7860934488,2301237.366339115,"1"]
["CBTS","TS-CBTS-TRNFMR-9000102025","B1 TR","30112314","22/01/2005","20","PT",220,"WILSON","SERV",2.5279823020006975E-2,2.607987800250855E-2,2.6890145074086602E-2,2.7710551816841678E-2,2.8541026631866084E-2,2.9381498703903164E-2,3.0231897968033161E-2,3.1092155078253692E-2,3.1962201377819688E-2,3.2841968871219041E-2,3.373139019767879E-2,3.4630398606101953E-2,3.5538927931334507E-2,3.6456912571684597E-2,3.738428746761302E-2,3.8320988081517404E-2,109557.3,500,2413272.2410512203,2528861.6310152751,2647945.5935201407,2770585.704829515,2896844.7918575485,3026786.9530731039,3160477.579200923,"2"]
["CBTS","TS-CBTS-TRNFMR-9000102026","B2 TR","30290613","31/03/2005","20","PT",220,"WILSON","SERV",2.6406001680960522E-2,2.7220373865510905E-2,2.8044856698618559E-2,2.8879378902107677E-2,2.9723869967760108E-2,3.0578260124780599E-2,3.1442480309103682E-2,3.231646213440853E-2,3.3200137864725643E-2,3.4093440388532237E-2,3.4996303194237854E-2,3.5908660346967491E-2,3.6830446466561084E-2,3.7761596706717304E-2,3.8702046735200502E-2,3.9651732715054733E-2,109557.3,500,2560640.3565896912,2680066.0559536703,2803019.5497231069,2929562.5714702257,3059758.1187395342,3193670.4723640862,3331365.2171025663,"2"]
["ERTS","TS-ERTS-TRNFMR-2602337129","B1 TR","33408512","14/12/2023","1","PT",220,"WILSON","SERV",6.3517535608215159E-3,6.8028173892564769E-3,7.2670128136598233E-3,7.7442012982888997E-3,8.2342493978838638E-3,8.7370283410821425E-3,9.2524136598247653E-3,9.7802848583715685E-3,1.0320525116605195E-2,1.0873021023153018E-2,1.1437662334559007E-2,1.2014341757305869E-2,1.2602954749961315E-2,1.3203399343107769E-2,1.3815575975050343E-2,1.4439387341560916E-2,109557.3,500,3704.399899675474,4111.6725833224964,4552.0403646690038,5027.6123808206721,5540.610012577732,6093.3698637719262,6688.3471845758977,"1"]
["ERTS","TS-ERTS-TRNFMR-9000106033","B3 TR","33155766","18/09/2019","6","PT",220,"ABB","SERV",1.0553297925527505E-2,1.1110956872436684E-2,1.1680715382524354E-2,1.2262467352260553E-2,1.2856109351800149E-2,1.3461540451832565E-2,1.4078662065437175E-2,1.470737780331377E-2,1.5347593340962029E-2,1.5999216296575081E-2,1.6662156118560145E-2,1.7336323981733903E-2,1.8021632691354816E-2,1.8717996594251773E-2,1.9425331496389808E-2,2.0143554586293022E-2,109557.3,500,6653.1878593610381,7229.1688793221028,7845.0704083829105,8503.285158683293,9206.324381467186,9956.8218682346651,10757.537208718661,"1"]
["ERTS","TS-ERTS-TRNFMR-9000101309","B2 TR","30068367","24/11/2011","13","PT",220,"WILSON","SERV",1.749433390860744E-2,1.8182215123493606E-2,1.8881131870590373E-2,1.959100028325178E-2,2.031173786040319E-2,2.1043263396472556E-2,2.1785496916087888E-2,2.2538359613145986E-2,2.3301773793882985E-2,2.407566282362239E-2,2.4859951076904307E-2,2.5654563890732951E-2,2.6459427520697409E-2,2.7274469099752063E-2,2.8099616599451926E-2,2.8934798793471606E-2,109557.3,500,11411.304225224656,12191.67487776455,13019.645405685611,13897.967354032029,14829.519200827901,15817.31060511571,16864.484920393341,"1"]
["ERTS","TS-ERTS-TRNFMR-9000105193","B4 TR","33408511","3/07/2024","1","PT",220,"WILSON","SERV",6.3517535608215159E-3,6.8028173892564769E-3,7.2670128136598233E-3,7.7442012982888997E-3,8.2342493978838638E-3,8.7370283410821425E-3,9.2524136598247653E-3,9.7802848583715685E-3,1.0320525116605195E-2,1.0873021023153018E-2,1.1437662334559007E-2,1.2014341757305869E-2,1.2602954749961315E-2,1.3203399343107769E-2,1.3815575975050343E-2,1.4439387341560916E-2,109557.3,500,3704.399899675474,4111.6725833224964,4552.0403646690038,5027.6123808206721,5540.610012577732,6093.3698637719262,6688.3471845758977,"1"]
["FBTS","TS-FBTS-TRNFMR-9000102306","B3 TR","30192651","1/06/1989","36","PT",220,"WILSON","SERV",4.0751363806001972E-2,4.1720656996895089E-2,4.2698988342790511E-2,4.3686295879445391E-2,4.4682518054979359E-2,4.5687593716080999E-2,4.6701462094863921E-2,4.772406279635355E-2,4.875533578654867E-2,4.9795221381033872E-2,5.0843660234134558E-2,5.190059332854724E-2,5.2965961965455777E-2,5.4039707755081712E-2,5.5121772607680808E-2,5.6212098724906401E-2,109557.3,500,11669.053985370945,12509.158324295939,13407.23990349847,14366.415651283352,15389.9136248424,16481.076608596781,17643.364369934621,"3"]
["FBTS","TS-FBTS-TRNFMR-9000101877","B1 220/66KV 150MVA TR","30258017","23/12/2016","8","PT",220,"WILSON","SERV",1.3409015528344947E-2,1.402513563365404E-2,1.4652858069281072E-2,1.5292088338107024E-2,1.5942733895813466E-2,1.6604704037614604E-2,1.7277909793742219E-2,1.796226383283428E-2,1.8657680372478724E-2,1.9364075096251154E-2,2.0081365076655144E-2,2.0809468703440248E-2,2.1548305616830521E-2,2.2297796645245893E-2,2.305786374713481E-2,2.3828429956587516E-2,109557.3,500,6813.6271417253975,7420.9698316159629,8072.4315485734496,8770.5397447893592,9517.9256636227892,10317.328077043005,11171.595279369962,"1"]
["FBTS","TS-FBTS-TRNFMR-2602058480","B2 TR","33252644","28/03/2021","4","PT",220,"ABB","SERV",7.9925289442848158E-3,8.4890856299505435E-3,8.9983091640517543E-3,9.5200771435124398E-3,1.0054270982274072E-2,1.0600775630318138E-2,1.1159479320505761E-2,1.1730273339772279E-2,1.2313051821725596E-2,1.2907711558133861E-2,1.3514151827134668E-2,1.4132274236302367E-2,1.4761982578958333E-2,1.5403182702319884E-2,1.6055782386260375E-2,1.6719691231611766E-2,109557.3,500,3929.9431082713036,4360.3147718818282,4827.0894009506446,5332.5824319025533,5879.2113726581492,6469.4993783524606,7106.0785828486305,"1"]
["GTS","TS-GTSX-TRNFMR-9000100730","B4 TR","30134344","1/01/1968","57","PT",220,"TOSHIBA","SERV",4.9195207778246597E-2,5.0238727254030557E-2,5.1290774925080607E-2,5.2351291910316511E-2,5.3420219643082856E-2,5.4497499861900778E-2,5.5583074601602833E-2,5.6676886184905961E-2,5.777887721431596E-2,5.888899056441943E-2,6.0007169374492686E-2,6.113335704145928E-2,6.2267497213115086E-2,6.340953378169889E-2,6.455941087768502E-2,6.5717072863891612E-2,109557.3,500,22688.496565177789,24137.480042678722,25671.462075887728,27294.459699726762,29010.63019256543,30824.275229734012,32739.84402458461,"4"]
["GTS","TS-GTSX-TRNFMR-9000105993","B1 TR","30329521","1/07/2014","11","PT",220,"ABB","SERV",1.7976068879081208E-2,1.8671705881307177E-2,1.9378319395160548E-2,2.009582652018449E-2,2.0824145671785366E-2,2.1563196514556626E-2,2.2312899900083227E-2,2.3073177808854872E-2,2.3843953295952236E-2,2.4625150440196197E-2,2.541669429649196E-2,2.6218510851119592E-2,2.7030526979741176E-2,2.7852670407924718E-2,2.8684869674002078E-2,2.952705409408396E-2,109557.3,500,10588.418702135783,11436.251782148145,12340.67623209603,13304.740772330129,14331.617138136571,15424.604542565381,16587.132921691558,"1"]
["GTS","TS-GTSX-TRNFMR-9000100729","B3 TR","30070869","16/09/2013","12","PT",220,"ABB","SERV",1.8463254636218895E-2,1.9166605889889277E-2,1.9880875318230684E-2,2.0605980951710401E-2,2.1341842089366403E-2,2.208837923531537E-2,2.2845514039479986E-2,2.3613169242183707E-2,2.4391268622298012E-2,2.5179736948660714E-2,2.5978499934514288E-2,2.6787484194724542E-2,2.760661720557589E-2,2.8435827266950486E-2,2.9275043466718942E-2,3.0124195647180163E-2,109557.3,500,10888.814442993409,11752.606054459959,12673.672311602731,13655.083233838819,14700.03295302641,15811.84298091627,16993.966159134718,"1"]
["GTS","TS-GTSX-TRNFMR-9000103966","B2 TR","30140360","16/11/2010","14","PT",220,"WILSON","SERV",1.5622499262757383E-2,1.627893162019145E-2,1.6946642976288229E-2,1.7625545208476256E-2,1.8315551786118989E-2,1.901657768444498E-2,1.972853930466667E-2,2.0451354399724786E-2,2.1184942005167295E-2,2.1929222374716506E-2,2.2684116920133612E-2,2.3449548155019206E-2,2.4225439642231672E-2,2.5011715944636692E-2,2.5808302578922637E-2,2.661512597225002E-2,109557.3,500,9114.6757975767359,9882.0002112704551,10702.430430321447,11578.903780925633,12514.479271544909,13512.341132090049,14575.802135111731,"1"]
["HTS","TS-HTSX-TRNFMR-9000101836","B1 TR","33213393","30/04/2017","8","PT",220,"ABB","SERV",1.2983481922033024E-2,1.3591399618810507E-2,1.4210987215310777E-2,1.4842148770694896E-2,1.548479038218098E-2,1.6138820065064841E-2,1.6804147642152989E-2,1.7480684641689725E-2,1.8168344202949216E-2,1.8867040988782668E-2,1.9576691104473132E-2,2.0297212022329147E-2,2.1028522511513548E-2,2.1770542572654095E-2,2.2523193376824735E-2,2.328639720854031E-2,109557.3,500,25244.22375216311,27376.840597454739,29656.70550897238,32092.30398701477,34692.483340680366,37466.45915975664,40423.822342163883,"1"]
["HTS","TS-HTSX-TRNFMR-9000103663","B2 TR","33213569","30/11/2016","8","PT",220,"ABB","SERV",1.4720074182648535E-2,1.5360518848109184E-2,1.6012369102284763E-2,1.6675534429112737E-2,1.7349926036945962E-2,1.8035456762734103E-2,1.8732040983287068E-2,1.9439594532961735E-2,2.0158034627200339E-2,2.0887279791387381E-2,2.1627249794574088E-2,2.2377865587653312E-2,2.3139049245607834E-2,2.3910723913505127E-2,2.4692813755934684E-2,2.5485243909612487E-2,109557.3,500,28580.256485953141,30857.05109687155,33286.039702612128,35875.919014439569,38635.751775739474,41574.974230938904,44703.401254120399,"1"]
["HTS","TS-HTSX-TRNFMR-9000103664","B3 TR","32697712","31/05/2016","9","PT",220,"ABB","SERV",6.3517535608215159E-3,6.8028173892564769E-3,7.2670128136598233E-3,7.7442012982888997E-3,8.2342493978838638E-3,8.7370283410821425E-3,9.2524136598247653E-3,9.7802848583715685E-3,1.0320525116605195E-2,1.0873021023153018E-2,1.1437662334559007E-2,1.2014341757305869E-2,1.2602954749961315E-2,1.3203399343107769E-2,1.3815575975050343E-2,1.4439387341560916E-2,109557.3,500,11338.331075169992,12682.3295399566,14143.111528308962,15728.11136456199,17445.105897334652,19302.221186372179,21307.939505107421,"1"]
["KTS","TS-KTSX-TRNFMR-9000102175","B5 TR","30089713","12/02/2010","15","PT",220,"ABB","SERV",2.5840390717448036E-2,2.6647622206427357E-2,2.746501485974695E-2,2.8292496838233094E-2,2.9129997096675186E-2,2.9977445349922749E-2,3.0834772040916225E-2,3.1701908310515781E-2,3.2578785969000656E-2,3.3465337469129941E-2,3.4361495880665505E-2,3.526719486624863E-2,3.6182368658556618E-2,3.710695203865233E-2,3.8040880315447834E-2,3.8984089306222436E-2,109557.3,500,4249.1681682349417,4459.2219495779373,4679.6709402864572,4911.1089216161763,5154.161904915657,5409.4895213257842,5677.7865558123258,"2"]
["KTS","TS-KTSX-TRNFMR-9000105084","B4 TR","30360363","19/03/1971","54","PT",220,"ENGLISH ELECTRIC","SERV",5.5930023139499685E-2,5.7026442049365134E-2,5.8131022209946592E-2,5.9243706580795363E-2,6.0364438383865071E-2,6.1493161096580318E-2,6.2629818445155472E-2,6.3774354398247302E-2,6.4926713160847527E-2,6.6086839168461031E-2,6.7254677081516667E-2,6.8430171780043847E-2,6.9613268358530767E-2,7.0803912121063184E-2,7.200204857661352E-2,7.3207623434563329E-2,109557.3,500,8486.7254581841953,8794.3184977274141,9115.87353923513,9452.1545190384404,9803.9640016437043,10172.144246211117,10557.579319929077,"4"]
["KTS","TS-KTSX-TRNFMR-9000101786","B2 TR","30177594","20/10/2012","12","PT",220,"WILSON","SERV",1.9957226012379148E-2,2.0683475554232333E-2,2.1420472117498868E-2,2.2168136330492527E-2,2.2926389961281823E-2,2.369515586267501E-2,2.4474357920729717E-2,2.5263921006501433E-2,2.6063770930786601E-2,2.6873834401624941E-2,2.7694038984356295E-2,2.8524313064041906E-2,2.9364585810077948E-2,3.0214787142847421E-2,3.1074847702262209E-2,3.1944698818065276E-2,109557.3,500,3292.4324063198719,3473.034671728009,3662.9510479525211,3862.7232382961738,4072.923870851791,4294.1572401134472,4527.0608922859783,"1"]
["KTS","TS-KTSX-TRNFMR-9000101991","B3 TR","30396377","24/01/2001","24","PT",220,"ABB","SERV",2.1499222011051922E-2,2.2248012412092399E-2,2.3007384002693088E-2,2.3777259747570723E-2,2.4557563639425295E-2,2.5348220651022046E-2,2.6149156690234765E-2,2.6960298557827778E-2,2.7781573907774582E-2,2.8612911209917269E-2,2.945423971480432E-2,3.0305489420549225E-2,3.1166591041564051E-2,3.2037475979044605E-2,3.2918076293083631E-2,3.380832467630368E-2,109557.3,500,3546.3661886343543,3735.1412833514723,3933.532683006054,4142.0969891612358,4361.4214332151232,4592.126131349989,4834.8644833527133,"1"]
["KTS","TS-KTSX-TRNFMR-9000102355","B1 TR","30308721","24/04/2013","12","PT",220,"WILSON","SERV",1.9957226012379148E-2,2.0683475554232333E-2,2.1420472117498868E-2,2.2168136330492527E-2,2.2926389961281823E-2,2.369515586267501E-2,2.4474357920729717E-2,2.5263921006501433E-2,2.6063770930786601E-2,2.6873834401624941E-2,2.7694038984356295E-2,2.8524313064041906E-2,2.9364585810077948E-2,3.0214787142847421E-2,3.1074847702262209E-2,3.1944698818065276E-2,109557.3,500,3292.4324063198719,3473.034671728009,3662.9510479525211,3862.7232382961738,4072.923870851791,4294.1572401134472,4527.0608922859783,"1"]
["MTS","TS-MTSX-TRNFMR-9000105415","B3 TR","30376616","2/05/2007","18","PT",220,"AREVA","SERV",1.654733504477468E-2,1.7219578048082274E-2,1.7902976782321556E-2,1.8597445335227558E-2,1.9302899267416906E-2,2.001925553484174E-2,2.0746432416666516E-2,2.1484349448089524E-2,2.2232927357693E-2,2.2992088008938261E-2,2.3761754345463793E-2,2.4541850339883764E-2,2.5332300945804742E-2,2.6133032052814142E-2,2.6943970444210708E-2,2.7765043757269625E-2,109557.3,500,74191.462591297823,81952.756415548662,90341.725232255092,99394.403032602466,109148.05754814121,119641.20325319791,130913.6153074975,"1"]
["MTS","TS-MTSX-TRNFMR-9000102379","B1 TR","30006289","3/12/2007","17","PT",220,"AREVA","SERV",1.8463254636218895E-2,1.9166605889889277E-2,1.9880875318230684E-2,2.0605980951710401E-2,2.1341842089366403E-2,2.208837923531537E-2,2.2845514039479986E-2,2.3613169242183707E-2,2.4391268622298012E-2,2.5179736948660714E-2,2.5978499934514288E-2,2.6787484194724542E-2,2.760661720557589E-2,2.8435827266950486E-2,2.9275043466718942E-2,3.0124195647180163E-2,109557.3,500,74640.851286332705,82412.394447563231,90811.62949589215,99874.589904080844,109638.5429088297,120142.00271180909,131424.74402100409,"1"]
["RTS","TS-RTSX-TRNFMR-9000104969","B1 220/66/11KV TR","32950096","11/12/2017","7","PT",220,"ALSTOM","SERV",1.2983481922033024E-2,1.3591399618810507E-2,1.4210987215310777E-2,1.4842148770694896E-2,1.548479038218098E-2,1.6138820065064841E-2,1.6804147642152989E-2,1.7480684641689725E-2,1.8168344202949216E-2,1.8867040988782668E-2,1.9576691104473132E-2,2.0297212022329147E-2,2.1028522511513548E-2,2.1770542572654095E-2,2.2523193376824735E-2,2.328639720854031E-2,109557.3,500,9381.340105905474,10491.639380584078,11708.682807121939,13040.035145340609,14493.595891881891,16077.605585588119,17800.65273355828,"1"]
["RTS","TS-RTSX-TRNFMR-9000100334","B2 TR","33034376","5/08/2018","7","PT",220,"ALSTOM","SERV",1.1741815860679794E-2,1.2324833054356832E-2,1.2919729463515939E-2,1.3526404414391902E-2,1.4144759559655995E-2,1.4774698734978053E-2,1.5416127827396431E-2,1.6068954654281153E-2,1.673308885181779E-2,1.7408441772070682E-2,1.8094926387801191E-2,1.879245720430911E-2,1.9500950177644527E-2,2.0220322638621169E-2,2.0950493222111177E-2,2.1691381801168697E-2,109557.3,500,8761.0310673051099,9819.1387219196786,10980.40270134407,12252.229774815769,13642.3584087863,15158.86681471267,16810.17811683294,"1"]
["RTS","TS-RTSX-TRNFMR-8000002864","B5 TR","32789210","9/04/2017","8","PT",220,"ALSTOM","SERV",1.1339689458706781E-2,1.1914305962636318E-2,1.2500873828635295E-2,1.3099290657039186E-2,1.3709456483116833E-2,1.433127362451625E-2,1.4964646541479554E-2,1.56094817084933E-2,1.6265687496191616E-2,1.6933174062492173E-2,1.7611853252050391E-2,1.8301638503244178E-2,1.9002444761977544E-2,1.9714188401678934E-2,2.0436787148939151E-2,2.1170160014291395E-2,109557.3,500,8534.9210003525841,9574.0786372685779,10715.12918827654,11965.42518331805,13332.65088509497,14824.82895067869,16450.326412896458,"1"]
["RWTS","TS-RWTS-TRNFMR-9000105420","B1 TR","30092200","18/12/2007","17","PT",220,"AREVA","SERV",1.9453861927165472E-2,2.0172518993128996E-2,2.0901979511879221E-2,2.1642163276705761E-2,2.2392991261543149E-2,2.3154385563301405E-2,2.3926269347930074E-2,2.4708566799922504E-2,2.5501203074981271E-2,2.6304104255605698E-2,2.7117197309378782E-2,2.7940410049744235E-2,2.8773671099100895E-2,2.9616909854038975E-2,3.0470056452568617E-2,3.1333041743199619E-2,109557.3,500,7434.4380720092568,8002.1565791896664,8607.4448987350206,9252.3824050927669,9939.1374330792059,10669.969657408694,11447.233243127856,"1"]
["RWTS","TS-RWTS-TRNFMR-9000103449","B4 TR","32936197","26/07/2018","7","PT",220,"ABB","SERV",9.7909725810378934E-3,1.0331459139145904E-2,1.0884199109630899E-2,1.1449082310122205E-2,1.202600150404054E-2,1.2614852203121085E-2,1.3215532487678816E-2,1.3827942842613239E-2,1.4451986007416595E-2,1.5087566838684396E-2,1.5734592183820895E-2,1.6392970764789738E-2,1.7062613070913835E-2,1.7743431259833908E-2,1.843533906585626E-2,1.9138251714989285E-2,109557.3,500,3584.9387928494452,3935.3087069908324,4313.2411933277144,4720.4694060789479,5158.8075280012799,5630.1553493864903,6136.4990165208419,"1"]
["RWTS","TS-RWTS-TRNFMR-9000103450","B3 TR","30182680","29/11/1984","40","PT",220,"WILSON","SERV",4.0751363806001972E-2,4.1720656996895089E-2,4.2698988342790511E-2,4.3686295879445391E-2,4.4682518054979359E-2,4.5687593716080999E-2,4.6701462094863921E-2,4.772406279635355E-2,4.875533578654867E-2,4.9795221381033872E-2,5.0843660234134558E-2,5.190059332854724E-2,5.2965961965455777E-2,5.4039707755081712E-2,5.5121772607680808E-2,5.6212098724906401E-2,109557.3,500,13131.651021910091,13969.581165751322,14857.966553822782,15799.35040038093,16796.37286171595,17851.774946025831,18968.401097144648,"3"]
["RWTS","TS-RWTS-TRNFMR-9000100293","B2 TR","30055996","31/03/2009","16","PT",220,"WILSON","SERV",2.5279823020006975E-2,2.607987800250855E-2,2.6890145074086602E-2,2.7710551816841678E-2,2.8541026631866084E-2,2.9381498703903164E-2,3.0231897968033161E-2,3.1092155078253692E-2,3.1962201377819688E-2,3.2841968871219041E-2,3.373139019767879E-2,3.4630398606101953E-2,3.5538927931334507E-2,3.6456912571684597E-2,3.738428746761302E-2,3.8320988081517404E-2,109557.3,500,9481.1995058591674,10148.827530396176,10858.433992358947,11612.250377581649,12412.599663561443,13261.899243178803,14162.66422018198,"2"]
["SMTS","TS-SMTS-TRNFMR-9000103942","B1 TR","30255860","26/03/2009","16","PT",220,"AREVA","SERV",2.6406001680960522E-2,2.7220373865510905E-2,2.8044856698618559E-2,2.8879378902107677E-2,2.9723869967760108E-2,3.0578260124780599E-2,3.1442480309103682E-2,3.231646213440853E-2,3.3200137864725643E-2,3.4093440388532237E-2,3.4996303194237854E-2,3.5908660346967491E-2,3.6830446466561084E-2,3.7761596706717304E-2,3.8702046735200502E-2,3.9651732715054733E-2,109557.3,500,914200.7432841789,961406.20247294812,1010526.253985582,1061626.4735533081,1114774.2498445869,1170038.8014716869,1227491.195389777,"2"]
["SMTS","TS-SMTS-TRNFMR-9000101249","B3 TR","30018608","28/09/2009","16","PT",220,"AREVA","SERV",1.7976068879081208E-2,1.8671705881307177E-2,1.9378319395160548E-2,2.009582652018449E-2,2.0824145671785366E-2,2.1563196514556626E-2,2.2312899900083227E-2,2.3073177808854872E-2,2.3843953295952236E-2,2.4625150440196197E-2,2.541669429649196E-2,2.6218510851119592E-2,2.7030526979741176E-2,2.7852670407924718E-2,2.8684869674002078E-2,2.952705409408396E-2,109557.3,500,622663.96175346093,662459.13708576933,704129.62744350662,747741.73229076003,793363.54559132503,841064.97564129904,890917.76312992629,"1"]
["SVTS","TS-SVTS-TRNFMR-9000101602","B1 TR","30123334","18/12/2001","23","PT",220,"WILSON","SERV",2.5279823020006975E-2,2.607987800250855E-2,2.6890145074086602E-2,2.7710551816841678E-2,2.8541026631866084E-2,2.9381498703903164E-2,3.0231897968033161E-2,3.1092155078253692E-2,3.1962201377819688E-2,3.2841968871219041E-2,3.373139019767879E-2,3.4630398606101953E-2,3.5538927931334507E-2,3.6456912571684597E-2,3.738428746761302E-2,3.8320988081517404E-2,109557.3,500,5507.0446442662123,5846.9654490412413,6207.7524664119001,6590.6689113463644,6997.0440001895113,7428.2757642841534,7885.8342419050659,"2"]
["SVTS","TS-SVTS-TRNFMR-9000105387","B4 TR","30027808","31/10/2012","12","PT",220,"WILSON","SERV",1.8463254636218895E-2,1.9166605889889277E-2,1.9880875318230684E-2,2.0605980951710401E-2,2.1341842089366403E-2,2.208837923531537E-2,2.2845514039479986E-2,2.3613169242183707E-2,2.4391268622298012E-2,2.5179736948660714E-2,2.5978499934514288E-2,2.6787484194724542E-2,2.760661720557589E-2,2.8435827266950486E-2,2.9275043466718942E-2,3.0124195647180163E-2,109557.3,500,4103.3072922636456,4386.8963982762034,4688.9279751618997,5010.5621701475629,5353.0224243783487,5717.5978135216219,6105.6460659779541,"1"]
["SVTS","TS-SVTS-TRNFMR-9000103413","B2 TR","30461961","4/02/1999","26","PT",220,"ALSTOM","SERV",2.7552252878867534E-2,2.8380800168900322E-2,2.9219358253074867E-2,3.0067856924902436E-2,3.0926226702704618E-2,3.1794398799622425E-2,3.2672305095289844E-2,3.3559878109053476E-2,3.4457050974639469E-2,3.5363757416176589E-2,3.6279931725478276E-2,3.7205508740512871E-2,3.8140423824987724E-2,3.9084612848967248E-2,4.0038012170479309E-2,4.10005586180342E-2,109557.3,500,5938.2703315812178,6293.9450684833482,6671.1562206857525,7071.1955837250853,7495.4216276320385,7945.262732053021,8422.2197999250275,"2"]
["SVTS","TS-SVTS-TRNFMR-9000102974","B3 TR","30107571","5/06/2003","22","PT",220,"AREVA","SERV",3.1109466372648331E-2,3.1979707828761028E-2,3.2859669124880919E-2,3.3749282912675871E-2,3.4648482452999341E-2,3.5557201592186449E-2,3.6475374739598387E-2,3.7402936846332335E-2,3.8339823385028393E-2,3.928597033070913E-2,4.0241314142572926E-2,4.1205791746714127E-2,4.2179340519680419E-2,4.3161898272844446E-2,4.415340323752992E-2,4.5153794050857732E-2,109557.3,500,6574.3297677513692,6952.1004912761309,7352.3534984331054,7776.4207330238678,8225.7024540227849,8701.6700020572134,9205.8685448220112,"2"]
["TBTS","TS-TBTS-TRNFMR-9000106334","B3 TR","30230878","30/11/2013","11","PT",220,"WILSON","SERV",1.7018079311710177E-2,1.769816270097424E-2,1.8389341352980204E-2,1.9091530397796763E-2,1.9804646383347113E-2,2.0528607201720672E-2,2.1263332020569292E-2,2.2008741219148198E-2,2.2764756328612079E-2,2.3531299976216835E-2,2.4308295833101679E-2,2.5095668565375706E-2,2.5893343788247147E-2,2.6701248022955371E-2,2.7519308656304586E-2,2.8347453902599518E-2,109557.3,500,20154.747163411019,21766.91509669946,23480.69268172446,25300.944062772563,27232.699662587089,29281.159858475359,31451.699221200382,"1"]
["TBTS","TS-TBTS-TRNFMR-9000104894","B1 TR","30119127","4/12/1985","39","PT",220,"WILSON","SERV",4.2114819612163235E-2,4.3096784788184239E-2,4.4087701239064581E-2,4.5087507575570784E-2,4.6096142801648865E-2,4.7113546301547071E-2,4.8139657827523386E-2,4.9174417488153765E-2,5.02177657371502E-2,5.126964336272577E-2,5.2329991477404358E-2,5.3398751508340503E-2,5.4475865188027717E-2,5.5561274545463668E-2,5.6654921897679844E-2,5.7756749841665234E-2,109557.3,500,44986.657184087679,47655.725396801026,50461.279281671261,53408.941195757485,56504.504306227813,59753.93563463696,63163.380464620765,"3"]
["TBTS","TS-TBTS-TRNFMR-9000101593","B2 TR","30218602","4/12/1985","39","PT",220,"WILSON","SERV",4.1430860119579305E-2,4.2406504601988138E-2,4.3391143696683288E-2,4.4384715730373503E-2,4.538715943237781E-2,4.6398413921291626E-2,4.741841869228447E-2,4.8447113605002978E-2,4.9484438872012038E-2,5.053033504779969E-2,5.1584743018262658E-2,5.2647603990683578E-2,5.3718859484151782E-2,5.4798451320434483E-2,5.5886321615223999E-2,5.6982412769810753E-2,109557.3,500,44590.262937560845,47244.372097429339,50034.396817753863,52965.94349507687,56044.789308562045,59276.885067285977,62668.359920943571,"3"]
["TSTS","TS-TSTS-TRNFMR-9000101577","B3 TR","30136974","1/01/1968","57","PT",220,"TOSHIBA","SERV",6.219241354166849E-2,6.3333930766589441E-2,6.4483292198409425E-2,6.5640442184796144E-2,6.6805325300453355E-2,6.79778863417001E-2,6.9158070321262866E-2,7.0345822463315444E-2,7.1541088198686986E-2,7.2743813160326964E-2,7.3953943178920234E-2,7.5171424278710597E-2,7.6396202673493785E-2,7.7628224762789744E-2,7.8867437128160911E-2,8.0113786529705244E-2,109557.3,500,377284.89429802232,395776.724074292,415009.59342559933,435006.20381201949,455789.73516529106,477383.85294385848,499812.71303497429,"4"]
["TSTS","TS-TSTS-TRNFMR-9000100149","B2 TR","30300684","17/04/1966","59","PT",220,"ASEA","SERV",6.9534964925391352E-2,7.0725112345303986E-2,7.1922756047767877E-2,7.3127841729076826E-2,7.4340315281908209E-2,7.5560122791219486E-2,7.6787210530267824E-2,7.8021524956860433E-2,7.9263012709704594E-2,8.0511620604962753E-2,8.176729563292473E-2,8.3029984954829272E-2,8.4299635899822256E-2,8.5576195962058899E-2,8.6859612797892782E-2,8.814983422323841E-2,109557.3,500,398990.52661240502,418252.83032483089,438279.54666988074,459093.83292835817,480719.32658270036,503180.15189748642,526500.92544692021,"4"]
["TSTS","TS-TSTS-TRNFMR-9000103388","B1 TR","30082161","5/06/1984","41","PT",220,"FUJI","SERV",3.1719356747126337E-2,3.2596428610447203E-2,3.3483172970372177E-2,3.4379522908756122E-2,3.5285412099865687E-2,3.6200774787557566E-2,3.7125545763653234E-2,3.8059660347423696E-2,3.9003054366125611E-2,3.9955664136524405E-2,4.0917426447336314E-2,4.1888278542543178E-2,4.2868158105531018E-2,4.3857003243988446E-2,4.485475247555093E-2,4.5861344714112739E-2,109557.3,500,208879.3772274236,221424.2855340376,234557.20355867429,248298.4829620111,262668.95019657217,277689.91292318451,293383.16577371716,"3"]
["TTS","TS-TTSX-TRNFMR-9000101733","B5 TR","30223933","12/02/1999","26","PT",220,"ABB","SERV",3.8739870541487087E-2,3.9689924767590479E-2,4.064914905996897E-2,4.1617480537671114E-2,4.2594856763476741E-2,4.3581215728596079E-2,4.4576495838103303E-2,4.5580635897070065E-2,4.6593575097360063E-2,4.7615253005043989E-2,4.864560954840369E-2,4.9684585006490534E-2,5.0732119998226133E-2,5.1788155471970243E-2,5.2852632695603141E-2,5.3925493247025336E-2,109557.3,500,5578.3098922925692,5792.5995381379471,6016.4195421058803,6250.3367786063627,6494.9501438181951,6750.8921719432874,7018.8305956543991,"3"]
["TTS","TS-TTSX-TRNFMR-9000100136","B3 TR","30149640","15/10/2010","14","PT",220,"ABB","SERV",1.5622499262757383E-2,1.627893162019145E-2,1.6946642976288229E-2,1.7625545208476256E-2,1.8315551786118989E-2,1.901657768444498E-2,1.972853930466667E-2,2.0451354399724786E-2,2.1184942005167295E-2,2.1929222374716506E-2,2.2684116920133612E-2,2.3449548155019206E-2,2.4225439642231672E-2,2.5011715944636692E-2,2.5808302578922637E-2,2.661512597225002E-2,109557.3,500,2317.9957172759314,2450.1400294722348,2588.9754492429652,2734.9112143399684,2888.3828182458647,3049.8532539726084,3219.8139998793285,"1"]
["TTS","TS-TTSX-TRNFMR-9000101558","B2 TR","30325104","24/12/2007","17","PT",220,"AREVA","SERV",2.7552252878867534E-2,2.8380800168900322E-2,2.9219358253074867E-2,3.0067856924902436E-2,3.0926226702704618E-2,3.1794398799622425E-2,3.2672305095289844E-2,3.3559878109053476E-2,3.4457050974639469E-2,3.5363757416176589E-2,3.6279931725478276E-2,3.7205508740512871E-2,3.8140423824987724E-2,3.9084612848967248E-2,4.0038012170479309E-2,4.10005586180342E-2,109557.3,500,4054.461794862812,4235.5979934211719,4425.147296440613,4623.6145165715034,4831.5337864973626,5049.4704029371569,5278.0220138979048,"2"]
["TTS","TS-TTSX-TRNFMR-9000103370","B1 TR","30272015","27/04/2013","12","PT",220,"WILSON","SERV",1.8463254636218895E-2,1.9166605889889277E-2,1.9880875318230684E-2,2.0605980951710401E-2,2.1341842089366403E-2,2.208837923531537E-2,2.2845514039479986E-2,2.3613169242183707E-2,2.4391268622298012E-2,2.5179736948660714E-2,2.5978499934514288E-2,2.6787484194724542E-2,2.760661720557589E-2,2.8435827266950486E-2,2.9275043466718942E-2,3.0124195647180163E-2,109557.3,500,2739.9206585813608,2885.3272278415411,3037.8996777171633,3198.0738579116451,3366.3128830727542,3543.1081036873661,3728.9807193193701,"1"]
["TTS","TS-TTSX-TRNFMR-9000101569","B4 TR","30302932","30/03/1967","58","PT",220,"ASEA","SERV",5.0662732587327675E-2,5.1718208944089183E-2,5.2782130916702918E-2,5.3854440062895859E-2,5.4935078241938329E-2,5.6023987605971381E-2,5.712111059169156E-2,5.8226389912439447E-2,5.9339768550606964E-2,6.0461189750392719E-2,6.159059701086389E-2,6.2727934079341741E-2,6.3873144945032045E-2,6.502617383298126E-2,6.6186965198248515E-2,6.7355463720360498E-2,109557.3,500,7096.6888062779453,7337.4855238783393,7588.6795422647228,7850.8876746835003,8124.7605362623563,8410.9843243318664,8710.2827438236855,"4"]
["WMTS","TS-WMTS-TRNFMR-9000101546","B3 TR","33094675","20/12/2018","6","PT",220,"TOSHIBA","SERV",2.4173919215689676E-2,2.4959512549772245E-2,2.5755421102227394E-2,2.6561571241417781E-2,2.7377890208053479E-2,2.820430607672908E-2,2.9040747719712878E-2,2.9887144772833829E-2,3.0743427603313389E-2,3.1609527279409466E-2,3.2485375541743799E-2,3.3370904776203969E-2,3.4266047988313453E-2,3.5170738778971478E-2,3.6084911321476287E-2,3.700850033975267E-2,109557.3,500,2871.2034466782029,2977.9339333066673,3088.3211714157646,3202.6373223819473,3321.179859323559,3444.2724097533046,3572.2673669926317,"2"]
["WMTS","TS-WMTS-TRNFMR-9000104095","B2 TR","33096331","30/10/2019","5","PT",220,"TOSHIBA","SERV",1.2983481922033024E-2,1.3591399618810507E-2,1.4210987215310777E-2,1.4842148770694896E-2,1.548479038218098E-2,1.6138820065064841E-2,1.6804147642152989E-2,1.7480684641689725E-2,1.8168344202949216E-2,1.8867040988782668E-2,1.9576691104473132E-2,2.0297212022329147E-2,2.1028522511513548E-2,2.1770542572654095E-2,2.2523193376824735E-2,2.328639720854031E-2,109557.3,500,1607.0448093378275,1693.0415877751018,1782.747416091006,1876.4284297120942,1974.3757218582778,2076.9068871856998,2184.3682341786666,"1"]
["WMTS","TS-WMTS-TRNFMR-9000102453","B1 TR","33096330","4/03/2021","4","PT",220,"TOSHIBA","SERV",1.0169107776935138E-2,1.0718207902754573E-2,1.1279483775289534E-2,1.1852827301632729E-2,1.2438133194085155E-2,1.3035298785357585E-2,1.3644223860076243E-2,1.4264810500786429E-2,1.4896962946882142E-2,1.554058746510123E-2,1.6195592230394684E-2,1.6861887216126248E-2,1.7539384092686294E-2,1.8227996133712954E-2,1.8927638129203506E-2,1.9638226304882878E-2,109557.3,500,1282.0400177194492,1360.8985768555456,1443.4798327411677,1530.0470667146215,1620.8887037721354,1716.3203564786145,1816.6855376257349,"1"]

{"sheet":"Country B & L Tx POFs","index":3,"n_rows":31,"n_cols":36,"rows_kept":31,"cut":false,"hidden":false,"merged":[]}
["Station","FLOC","FLOC Description","Equipment ID","Start-Up Date","Age","Object Type","Nominal Voltage (kV)","Manufacturer","User Status","PoF '25","PoF '26","PoF '27","PoF '28","PoF '29","PoF '30","PoF '31","PoF '32","PoF '33","PoF '34","PoF '35","PoF '36","PoF '37","PoF '38","PoF '39","PoF '40","Safety CoF ($)","Environment CoF ($)","Total Risk '26 ($)","Total Risk '27 ($)","Total Risk '28 ($)","Total Risk '29 ($)","Total Risk '30 ($)","Total Risk '31 ($)","Total Risk '32 ($)","Likelihood"]
["RCTS","TS-RCTS-TRNFMR-9000121025","L1A 220/66/22KV TR","30216946","16/11/1962","62","PT",220,"BRUCE PEEBLES","SERV",6.4605584460227683E-2,6.5763556796895051E-2,6.6929256400716786E-2,6.8102628091199269E-2,6.9283616903709877E-2,7.0472168084550035E-2,7.166822708619125E-2,7.2871739562744509E-2,7.408265136560388E-2,7.5300908539300826E-2,7.6526457317490304E-2,7.7759244119161686E-2,7.8999215544967916E-2,8.0246318373732639E-2,8.150049955909322E-2,8.2761706226316956E-2,109557.3,500,70343.987486423677,74152.933728811768,78136.889398477055,82302.337348450659,86655.947251406746,91204.578809290673,95955.28662554537,"4"]
["RCTS","TS-RCTS-TRNFMR-9000118320","L2A 220/66/22KV TR","30221515","20/12/1962","62","PT",220,"BRUCE PEEBLES","SERV",5.7471714654521278E-2,5.8579575779707294E-2,5.9695518145552406E-2,6.0819485078049462E-2,6.195142015591204E-2,6.3091267204057111E-2,6.4238970287337271E-2,6.5394473704561418E-2,6.6557721982757778E-2,6.7728659871710728E-2,6.8907232338686231E-2,7.0093384563438499E-2,7.128706193336809E-2,7.2488210038951784E-2,7.3696774669301246E-2,7.4912701807973825E-2,109557.3,500,63995.414082443618,67528.406470486196,71226.604723732584,75096.244570712181,79143.743913972125,83375.706989057508,87798.928585995149,"4"]
["KGTS","TS-KGTS-TRNFMR-9000103626","B2 TR","30264148","15/09/1962","63","PT",220,"BRUCE PEEBLES","SERV",5.5165242674795611E-2,5.6255898159987217E-2,5.7354755099005894E-2,5.8461756262854991E-2,5.9576844690024888E-2,6.0699963679316182E-2,6.1831056782970406E-2,6.297006780011094E-2,6.41169407704405E-2,6.5271619968243599E-2,6.6434049896627378E-2,6.7604175282008905E-2,6.8781941068844721E-2,6.9967292414597537E-2,7.1160174684877564E-2,7.2360533448848852E-2,109557.3,500,137354.53271264117,144112.30475845016,151147.97578418598,158470.32103312048,166088.295524835,174011.03448588451,182247.85597749066,"4"]
["KGTS","TS-KGTS-TRNFMR-9000101035","B3 TR","30287689","5/09/1962","63","PT",220,"BRUCE PEEBLES","SERV",5.440453225979669E-2,5.5489395982218026E-2,5.658250149709354E-2,5.7683791383179472E-2,5.879320849195524E-2,5.9910695940225467E-2,6.1036197103016443E-2,6.2169655606817087E-2,6.3311015323085029E-2,6.4460220362049681E-2,6.5617215066769208E-2,6.6781944007469174E-2,6.7954351976074689E-2,6.9134383981047209E-2,7.0321985242360885E-2,7.151710118676935E-2,109557.3,500,136191.20982986499,142912.416747182,149910.42628694291,157193.9897683069,164772.03715024632,172653.67956649189,180848.2098574987,"4"]
["SHTS","TS-SHTS-TRNFMR-9000100271","B3 TR","30319072","5/10/1971","54","PT",220,"TOSHIBA","SERV",5.440453225979669E-2,5.5489395982218026E-2,5.658250149709354E-2,5.7683791383179472E-2,5.879320849195524E-2,5.9910695940225467E-2,6.1036197103016443E-2,6.2169655606817087E-2,6.3311015323085029E-2,6.4460220362049681E-2,6.5617215066769208E-2,6.6781944007469174E-2,6.7954351976074689E-2,6.9134383981047209E-2,7.0321985242360885E-2,7.151710118676935E-2,109557.3,500,65084.839445187681,68960.412691035614,73027.35100865706,77292.995315803579,81764.891706351424,86450.796631456105,91358.680147100997,"4"]
["BATS","TS-BATS-TRNFMR-9000103776","B2 TR","30024480","29/05/1969","56","PT",220,"TOSHIBA","SERV",5.3647911870894793E-2,5.4726955395021148E-2,5.5814281188436787E-2,5.6909831633839336E-2,5.8013549392046393E-2,5.9125377394366962E-2,6.024525883528109E-2,6.1373137165448566E-2,6.2508956085018386E-2,6.3652659537245415E-2,6.4804191702344749E-2,6.59634969916576E-2,6.7130520042030239E-2,6.8305205710454286E-2,6.9487499068924263E-2,7.0677345399536406E-2,109557.3,500,617622.46349684044,647295.48519500636,678267.19920979277,710583.83775317681,744292.66575700371,779441.98607723485,816081.14532812219,"4"]
["RCTS","TS-RCTS-TRNFMR-9000118319","B2B TR","30009162","5/11/1974","50","PT",220,"HAWKER SIDDLEY BRUSH","SERV",4.6311106260509938E-2,4.7330360918864556E-2,4.8358310876684629E-2,4.9394896316632519E-2,5.0440057764210566E-2,5.1493736077216967E-2,5.2555872435675277E-2,5.3626408332235087E-2,5.4705285562973605E-2,5.5792446218647096E-2,5.6887832676303041E-2,5.7991387591275534E-2,5.9103053889529744E-2,6.0222774760354647E-2,6.1350493649345972E-2,6.2486154251731651E-2,109557.3,500,52495.021481832424,55536.766541254197,58726.624330489809,62070.399538613907,65574.071991769044,69243.800225982734,73085.926522350041,"3"]
["SHTS","TS-SHTS-TRNFMR-9000101629","B2 TR","30098829","10/07/1969","56","PT",220,"TOSHIBA","SERV",4.6311106260509938E-2,4.7330360918864556E-2,4.8358310876684629E-2,4.9394896316632519E-2,5.0440057764210566E-2,5.1493736077216967E-2,5.2555872435675277E-2,5.3626408332235087E-2,5.4705285562973605E-2,5.5792446218647096E-2,5.6887832676303041E-2,5.7991387591275534E-2,5.9103053889529744E-2,6.0222774760354647E-2,6.1350493649345972E-2,6.2486154251731651E-2,109557.3,500,61102.452096994981,64783.457003944437,68647.989645362206,72703.200223426,76956.44348478422,81415.282534188271,86087.494114498622,"3"]
["RCTS","TS-RCTS-TRNFMR-9000121024","B1B TR","30115227","1/06/1987","38","PT",220,"WILSON","SERV",4.5600815732727451E-2,4.661393035973993E-2,4.7635782488780198E-2,4.8666312055254068E-2,4.970545934512316E-2,5.0753164983994736E-2,5.1809369926723026E-2,5.2874015447477052E-2,5.3947043130271766E-2,5.502839485989397E-2,5.611801281327633E-2,5.7215839451214889E-2,5.8321817510478602E-2,5.9435889996251268E-2,6.0558000174921522E-2,6.1688091567160042E-2,109557.3,500,51707.004587178431,54714.933787292197,57869.803704300328,61177.38914923057,64643.639876955043,68274.684053198303,72076.832583867508,"3"]
["GNTS","TS-GNTS-TRNFMR-9000101867","B2 TR","30000089","12/05/1981","44","PT",220,"FUJI","SERV",3.8739870541487087E-2,3.9689924767590479E-2,4.064914905996897E-2,4.1617480537671114E-2,4.2594856763476741E-2,4.3581215728596079E-2,4.4576495838103303E-2,4.5580635897070065E-2,4.6593575097360063E-2,4.7615253005043989E-2,4.864560954840369E-2,4.9684585006490534E-2,5.0732119998226133E-2,5.1788155471970243E-2,5.2852632695603141E-2,5.3925493247025336E-2,109557.3,500,3477926.4835731611,3599298.8143286668,3723414.265455544,3850313.9214771613,3980039.653192637,4112634.1262012725,4248140.8091056468,"3"]
["TGTS","TS-TGTS-TRNFMR-9000105719","B2 TR","30215049","26/04/1978","47","PT",220,"FUJI","SERV",3.7421589957426282E-2,3.8358662395287957E-2,3.9304993964182855E-2,4.0260521132821081E-2,4.1225180836464648E-2,4.2198910460512384E-2,4.3181647824881764E-2,4.4173331169153118E-2,4.517389913842329E-2,4.6183290769842733E-2,4.7201445479777115E-2,4.8228303051585097E-2,4.9263803623946334E-2,5.0307887679756136E-2,5.1360496035504077E-2,5.2421569831151649E-2,109557.3,500,724382.49834093032,755702.45968382817,788154.20102964016,821774.68535846868,856601.82234191289,892674.47530391498,930032.46989740804,"3"]
["BETS","TS-BETS-TRNFMR-9000100900","B4 TR","30303085","23/04/1981","44","PT",220,"FUJI","SERV",3.2334047044198844E-2,3.3217916033845496E-2,3.4111410480481386E-2,3.5014463884277758E-2,3.5927010321668118E-2,3.6848984423376252E-2,3.7780321353575452E-2,3.872095679011911E-2,3.9670826905776502E-2,4.0629868350406273E-2,4.159801823401732E-2,4.2575214110666115E-2,4.3561393963134187E-2,4.4556496188354555E-2,4.5560459583528057E-2,4.6573223332904923E-2,109557.3,500,197649.9387459369,210696.50195739241,224498.33894413061,239090.031561012,254507.16056863908,270786.31437781133,287965.09740492865,"3"]
["MWTS","TS-MWTS-TRNFMR-9000104229","B3 TR","30114668","9/06/1983","42","PT",220,"FUJI","SERV",3.0504399472171539E-2,3.1367777019483012E-2,3.2240922062724997E-2,3.3123766811040456E-2,3.4016244100189663E-2,3.4918287367921352E-2,3.5829830630646264E-2,3.6750808461338491E-2,3.768115596857935E-2,3.8620808776677285E-2,3.9569703006800627E-2,4.0527775259052046E-2,4.1494962595441942E-2,4.2471202523695295E-2,4.3456432981850979E-2,4.4450592323611593E-2,109557.3,500,472658.2575223716,497814.16684719513,524108.81446748273,551586.56755600753,580293.04893194593,610275.14985043521,641581.04240644851,"2"]
["KGTS","TS-KGTS-TRNFMR-9000103625","B1 TR","30139189","3/09/2004","21","PT",220,"ABB","SERV",2.7552252878867534E-2,2.8380800168900322E-2,2.9219358253074867E-2,3.0067856924902436E-2,3.0926226702704618E-2,3.1794398799622425E-2,3.2672305095289844E-2,3.3559878109053476E-2,3.4457050974639469E-2,3.5363757416176589E-2,3.6279931725478276E-2,3.7205508740512871E-2,3.8140423824987724E-2,3.9084612848967248E-2,4.0038012170479309E-2,4.10005586180342E-2,109557.3,500,65487.088898438189,69689.294831504332,74100.341999632583,78727.789424425238,83579.370640146226,88662.995928394375,93986.753849019966,"2"]
["MBTS","TS-MBTS-TRNFMR-9000104603","B2 TR","30320144","31/12/2005","19","PT",220,"AREVA","SERV",2.6406001680960522E-2,2.7220373865510905E-2,2.8044856698618559E-2,2.8879378902107677E-2,2.9723869967760108E-2,3.0578260124780599E-2,3.1442480309103682E-2,3.231646213440853E-2,3.3200137864725643E-2,3.4093440388532237E-2,3.4996303194237854E-2,3.5908660346967491E-2,3.6830446466561084E-2,3.7761596706717304E-2,3.8702046735200502E-2,3.9651732715054733E-2,109557.3,500,22913.362595318849,24874.525735342104,26970.896441085672,29209.22144903582,31596.448761493251,34139.728441523752,36846.415170065935,"2"]
["SHTS","TS-SHTS-TRNFMR-9000102874","B4 TR","30122588","1/06/2001","24","PT",220,"WILSON","SERV",2.3088496072520615E-2,2.38594808068745E-2,2.4640885689531156E-2,2.543263579446009E-2,2.6234657126137373E-2,2.7046876577607626E-2,2.7869221891057561E-2,2.8701621620715656E-2,2.9544005097910442E-2,3.0396302398133623E-2,3.1258444309967826E-2,3.2130362305747284E-2,3.3011988513837021E-2,3.3903255692423362E-2,3.4804097204709006E-2,3.5714446995429583E-2,109557.3,500,34375.763655263472,36893.107380312722,39556.754683645529,42373.147997515138,45348.931917718917,48490.957324381285,51806.285969141783,"2"]
["BATS","TS-BATS-TRNFMR-9000104470","B1 TR","30131526","22/07/2015","10","PT",220,"WILSON","SERV",1.5168469644279203E-2,1.5816930589472311E-2,1.6476733396138199E-2,1.7147788769116046E-2,1.7830009069624175E-2,1.8523308224483226E-2,1.9227601641954917E-2,1.9942806133591451E-2,2.0668839841559095E-2,2.1405622170959093E-2,2.2153073726713268E-2,2.2911116254639596E-2,null,null,null,null,109557.3,500,358340.55083926389,383072.3022503049,409084.33758682804,436423.22910052765,465136.57572814077,495273.00935583166,526882.19999789982,"2"]
["MWTS","TS-MWTS-TRNFMR-9000100442","B1 TR","30162364","16/04/2010","15","PT",220,"WILSON","SERV",2.255353007298877E-2,2.3317154572073617E-2,2.4091252397387519E-2,2.4875747943175375E-2,2.5670566565240582E-2,2.6475634537121429E-2,2.7290879008921354E-2,2.8116227968594809E-2,2.8951610205506961E-2,2.9796955276104042E-2,3.0652193471548683E-2,3.1517255787173459E-2,3.2392073893638518E-2,3.3276580109671938E-2,3.4170707376287135E-2,3.5074389232381598E-2,109557.3,500,349284.49793122389,370720.38271572063,393207.82280173083,416788.65285481676,441505.92783855571,467403.93690933404,494528.21620849479,"2"]
["RCTS","TS-RCTS-TRNFMR-9000101142","B3 TR","30188337","30/06/2006","19","PT",220,"WILSON","SERV",2.1499222011051922E-2,2.2248012412092399E-2,2.3007384002693088E-2,2.3777259747570723E-2,2.4557563639425295E-2,2.5348220651022046E-2,2.6149156690234765E-2,2.6960298557827778E-2,2.7781573907774582E-2,2.8612911209917269E-2,2.945423971480432E-2,3.0305489420549225E-2,3.1166591041564051E-2,3.2037475979044605E-2,3.2918076293083631E-2,3.380832467630368E-2,109557.3,500,22643.48918256769,24313.17126921095,26081.638578069156,27953.42168102333,29933.204514414923,32025.8290068387,34236.297869473063,"1"]
["HOTS","TS-HOTS-TRNFMR-9000103910","B2 TR","30403050","5/07/2007","18","PT",220,"AREVA","SERV",2.046592596249952E-2,2.1199728276112939E-2,2.194422177035793E-2,2.2699327879578401E-2,2.3464969138870417E-2,2.4241069131572868E-2,2.502755244007715E-2,2.5824344599703619E-2,2.6631372055403335E-2,2.7448562121075937E-2,2.8275842941303808E-2,2.9113143455328783E-2,2.9960393363114513E-2,3.0817523093336519E-2,3.1684463773175353E-2,3.2561147199786533E-2,109557.3,500,47886.512652580714,52638.881784178018,57758.377896070408,63265.171302763563,69180.09187614503,75524.635812828405,82320.971667983686,"1"]
["MBTS","TS-MBTS-TRNFMR-9000102766","B1 TR (HOT SPARE)","30197453","31/12/2005","19","PT",220,"AREVA","SERV",1.8463254636218895E-2,1.9166605889889277E-2,1.9880875318230684E-2,2.0605980951710401E-2,2.1341842089366403E-2,2.208837923531537E-2,2.2845514039479986E-2,2.3613169242183707E-2,2.4391268622298012E-2,2.5179736948660714E-2,2.5978499934514288E-2,2.6787484194724542E-2,2.760661720557589E-2,2.8435827266950486E-2,2.9275043466718942E-2,3.0124195647180163E-2,109557.3,500,22026.986595318849,23976.019935342101,26060.34854108567,28286.71814903582,30662.075461493252,33193.569641523747,35888.55437006594,"1"]
["WETS","TS-WETS-TRNFMR-9000105463","B1 TR","30093526","30/09/2011","14","PT",220,"WILSON","SERV",1.8463254636218895E-2,1.9166605889889277E-2,1.9880875318230684E-2,2.0605980951710401E-2,2.1341842089366403E-2,2.208837923531537E-2,2.2845514039479986E-2,2.3613169242183707E-2,2.4391268622298012E-2,2.5179736948660714E-2,2.5978499934514288E-2,2.6787484194724542E-2,2.760661720557589E-2,2.8435827266950486E-2,2.9275043466718942E-2,3.0124195647180163E-2,109557.3,500,2260665.265701286,2376096.0463856542,2494847.8891589539,2616948.5431320569,2742425.7428442282,2871307.2218331317,3003620.7261815965,"1"]
["BETS","TS-BETS-TRNFMR-9000101413","L4 TR","30437067","31/10/2013","11","PT",220,"WILSON","SERV",1.8463254636218895E-2,1.9166605889889277E-2,1.9880875318230684E-2,2.0605980951710401E-2,2.1341842089366403E-2,2.208837923531537E-2,2.2845514039479986E-2,2.3613169242183707E-2,2.4391268622298012E-2,2.5179736948660714E-2,2.5978499934514288E-2,2.6787484194724542E-2,2.760661720557589E-2,2.8435827266950486E-2,2.9275043466718942E-2,3.0124195647180163E-2,109557.3,500,22991.821669239587,25354.2293789143,27908.475831896758,30665.742225707618,33637.599580319111,36836.01278904669,40273.345186508886,"1"]
["GNTS","TS-GNTS-TRNFMR-9000104776","B3 TR","30268304","26/03/2014","11","PT",220,"WILSON","SERV",1.749433390860744E-2,1.8182215123493606E-2,1.8881131870590373E-2,1.959100028325178E-2,2.031173786040319E-2,2.1043263396472556E-2,2.1785496916087888E-2,2.2538359613145986E-2,2.3301773793882985E-2,2.407566282362239E-2,2.4859951076904307E-2,2.5654563890732951E-2,2.6459427520697409E-2,2.7274469099752063E-2,2.8099616599451926E-2,2.8934798793471606E-2,109557.3,500,1305021.635042964,1377814.3454445871,1453126.6283437118,1531003.6316563049,1611491.2050275952,1694635.91327203,1780485.0475126349,"1"]
["HOTS","TS-HOTS-TRNFMR-9000101170","B3 TR","30120436","30/11/2006","18","PT",220,"AREVA","SERV",1.749433390860744E-2,1.8182215123493606E-2,1.8881131870590373E-2,1.959100028325178E-2,2.031173786040319E-2,2.1043263396472556E-2,2.1785496916087888E-2,2.2538359613145986E-2,2.3301773793882985E-2,2.407566282362239E-2,2.4859951076904307E-2,2.5654563890732951E-2,2.6459427520697409E-2,2.7274469099752063E-2,2.8099616599451926E-2,2.8934798793471606E-2,109557.3,500,47554.413252580714,52301.766384178016,57416.283696070408,62918.135202763566,68828.149976145025,75167.823812828399,81959.324967983674,"1"]
["TGTS","TS-TGTS-TRNFMR-9000101176","B1 TR","30321868","4/05/2007","18","PT",220,"ABB","SERV",1.654733504477468E-2,1.7219578048082274E-2,1.7902976782321556E-2,1.8597445335227558E-2,1.9302899267416906E-2,2.001925553484174E-2,2.0746432416666516E-2,2.1484349448089524E-2,2.2232927357693E-2,2.2992088008938261E-2,2.3761754345463793E-2,2.4541850339883764E-2,2.5332300945804742E-2,2.6133032052814142E-2,2.6943970444210708E-2,2.7765043757269625E-2,109557.3,500,330891.24693910778,353211.7307929722,376621.5028305825,401158.30331661471,426860.80221367377,453768.60730572266,481922.2732799541,"1"]
["BETS","TS-BETS-TRNFMR-9000101412","L2 TR","30149749","31/10/2013","11","PT",220,"WILSON","SERV",1.5622499262757383E-2,1.627893162019145E-2,1.6946642976288229E-2,1.7625545208476256E-2,1.8315551786118989E-2,1.901657768444498E-2,1.972853930466667E-2,2.0451354399724786E-2,2.1184942005167295E-2,2.1929222374716506E-2,2.2684116920133612E-2,2.3449548155019206E-2,2.4225439642231672E-2,2.5011715944636692E-2,2.5808302578922637E-2,2.661512597225002E-2,109557.3,500,22674.01206923959,25031.295678914303,27580.457131896757,30332.676925707619,33299.525380319108,36492.96698904669,39925.364386508889,"1"]
["BETS","TS-BETS-TRNFMR-9000106322","B3 TR","30046037","30/11/2013","11","PT",220,"WILSON","SERV",1.5168469644279203E-2,1.5816930589472311E-2,1.6476733396138199E-2,1.7147788769116046E-2,1.7830009069624175E-2,1.8523308224483226E-2,1.9227601641954917E-2,1.9942806133591451E-2,2.0668839841559095E-2,2.1405622170959093E-2,2.2153073726713268E-2,2.2911116254639596E-2,2.367967258636039E-2,2.4458666587742983E-2,2.524802311059049E-2,2.6047667947323161E-2,109557.3,500,136118.83972446548,147668.58643890379,159966.15515230809,173046.26680123253,186944.63753845991,201697.98835961361,217344.05342800712,"1"]
["MWTS","TS-MWTS-TRNFMR-9000101711","B2 TR","32495378","30/11/2015","9","PT",220,"TOSHIBA","SERV",1.1741815860679794E-2,1.2324833054356832E-2,1.2919729463515939E-2,1.3526404414391902E-2,1.4144759559655995E-2,1.4774698734978053E-2,1.5416127827396431E-2,1.6068954654281153E-2,1.673308885181779E-2,1.7408441772070682E-2,1.8094926387801191E-2,1.879245720430911E-2,1.9500950177644527E-2,2.0220322638621169E-2,2.0950493222111177E-2,2.1691381801168697E-2,109557.3,500,164416.57766903532,178212.12836399837,192852.60744161939,208375.21834074441,224818.32696143581,242221.4786887409,260625.41223673942,"1"]
["WETS","TS-WETS-TRNFMR-8000030801","B2 TR","33097043","31/10/2018","6","PT",220,"WILSON","SERV",1.1339689458706781E-2,1.1914305962636318E-2,1.2500873828635295E-2,1.3099290657039186E-2,1.3709456483116833E-2,1.433127362451625E-2,1.4964646541479554E-2,1.56094817084933E-2,1.6265687496191616E-2,1.6933174062492173E-2,1.7611853252050391E-2,1.8301638503244178E-2,1.9002444761977544E-2,1.9714188401678934E-2,2.0436787148939151E-2,2.1170160014291395E-2,109557.3,500,1198985.227423741,1280292.1316585368,1364682.6908500681,1452189.4947006139,1542844.9560447009,1636681.335432664,1733730.7635016749,"1"]