## Cover
CitiPower
Revised regulatory proposal 2026-31
CBD security of supply
| Model number: | 3.3.08
2025-12-01
12
2025-05-12

## Summary
CitiPower
CBD security of supply
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Construct new feeders from MG to JA |  | -10.5138 | 5.8708 | -4.643
| Option 3 | Construct new feeders from MG to JA and rebuild J |  | -38.5808 | 6.1928 | -32.388
| Option 4 | Rebuild J zone substation |  | -35.3106 | 6.105 | -29.2056
| Option 5 | `
NPV
| Preferred option: |  |  | 2026-06-30
| Option 3 | Construct new feeders from MG to JA and rebuild J |  | -32.388
PREFERRED OPTION
Preferred Option
Option 3
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 8.7638 | 10.2589 | 0.55335 | 16.6004 | 20.5846 |  | 56.761
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  |  | -4.643 | -32.388 | -29.2056 |  |  | Option 2
| Capex 10% higher |  |  | -5.6944 | -36.2461 | -32.7367 |  |  | Option 2
| Capex 10% lower |  |  | -3.5916 | -28.5299 | -25.6746 |  |  | Option 2
| Total benefits 10% higher |  |  | -4.0559 | -31.7687 | -28.5951 |  |  | Option 2
| Total benefits 10% lower |  |  | -5.2301 | -33.0073 | -29.8161 |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  |  | -6.2815 | -36.8653 | -33.3472 |  |  | Option 2
0
| 0 | [6 empty] | 0
0
0

## Assumptions
CitiPower
CBD security of supply
Project
|  | Business: |  | CitiPower
|  | Descripton: |  | CBD security of supply
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Construct new feeders from MG to JA
|  | Option 3 |  | Construct new feeders from MG to JA and rebuild J
|  | Option 4 |  | Rebuild J zone substation
Option 5
|  | Compliance project |  | Yes
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2024-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | JA |  | Little Bourke Street | 35717.9798 | 2024 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | #REF! |  |  |  | 0 | 2023-12-31 | per MWh
|  | #REF! |  |  |  | 0 | 2023-12-31 | per MWh
|  | #REF! |  |  |  | 0 | 2023-12-31 | per MWh
|  | #REF! |  |  |  | 0 | 2023-12-31 | per customer
|  | #REF! |  |  |  | 0 | 2023-12-31 | per customer minute
|  | #REF! |  |  |  | 0 | 2023-12-31 | per customer minute
|  | #REF! |  |  |  | 0 | 2023-12-31 | per customer
|  | #REF! |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
CitiPower
CBD security of supply
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk 10% PoE |  | 30% | MWh |  | 0.11902 | 1.1632 | 2.4742 | 4.3101 | 6.6085 | 9.8496 | 15.2992 | 23.5231 | 32.4442 | 40.8192 | 36.4836 | 36.4836 | 36.4836 | 36.4836 | 36.4836 | 36.4836 | 36.4836 | 36.4836 | 36.4836 | 36.4836 | 36.4836 | 36.4836 | 36.4836 | 36.4836 | 36.4836
| Energy at risk 50% PoE |  | 70% | MWh |  | 0 | 0.065696 | 0.28731 | 0.73936 | 1.3599 | 2.3265 | 4.0737 | 6.8817 | 10.0481 | 13.2145 | 11.55 | 11.55 | 11.55 | 11.55 | 11.55 | 11.55 | 11.55 | 11.55 | 11.55 | 11.55 | 11.55 | 11.55 | 11.55 | 11.55 | 11.55
| Energy at risk (weighted) |  |  | MWh |  | 0.035706 | 0.39496 | 0.94339 | 1.8106 | 2.9344 | 4.5835 | 7.4413 | 11.8741 | 16.7669 | 21.4959 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03
| Energy at risk value | $/MWh | 33720.0512 | 2023-12-31 |  | 1204.0067 | 13318.0724 | 31811.1238 | 61053.1649 | 98949.6014 | 154554.9547 | 250921.3303 | 400395.7797 | 565380.871 | 724843.0667 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145
| Safety consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 1204.0067 | 13318.0724 | 31811.1238 | 61053.1649 | 98949.6014 | 154554.9547 | 250921.3303 | 400395.7797 | 565380.871 | 724843.0667 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer |  | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min |  | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min |  | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer |  | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer |  | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
CitiPower
CBD security of supply
OPTION 2 | Construct new feeders from MG to JA
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
[5 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Construct new feeders from MG to JA |  | 50 | 2023-12-31 | 7918867.3 | 9269805.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 7918867.3 | 9269805.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Const end date |  | 2028
| Energy at risk 10% PoE |  | 30% | MWh | 0.11902 | 1.1632 | 0 | 0.21536 | 0.0014263 | 0.0247 | 0.22077 | 1.1762 | 2.5993 | 3.9718 | 3.2345 | 3.2345 | 3.2345 | 3.2345 | 3.2345 | 3.2345 | 3.2345 | 3.2345 | 3.2345 | 3.2345 | 3.2345 | 3.2345 | 3.2345 | 3.2345 | 3.2345
| Energy at risk 50% PoE |  | 70% | MWh | 0 | 0.065696 | 0 | 0 | 0 | 0 | 0 | 0.019701 | 0.12891 | 0.3124 | 0.20492 | 0.20492 | 0.20492 | 0.20492 | 0.20492 | 0.20492 | 0.20492 | 0.20492 | 0.20492 | 0.20492 | 0.20492 | 0.20492 | 0.20492 | 0.20492 | 0.20492
| Energy at risk (weighted) |  |  | MWh | 0.035706 | 0.39496 | 0 | 0.064608 | 0.00042788 | 0.0074099 | 0.066232 | 0.36664 | 0.87003 | 1.4102 | 1.1138 | 1.1138 | 1.1138 | 1.1138 | 1.1138 | 1.1138 | 1.1138 | 1.1138 | 1.1138 | 1.1138 | 1.1138 | 1.1138 | 1.1138 | 1.1138 | 1.1138
| Energy at risk value | $/MWh | 33720.0512 | 2023-12-31 | 1204.0067 | 13318.0724 | 0 | 2178.5773 | 14.428 | 249.8638 | 2233.361 | 12363.2134 | 29337.3284 | 47553.0633 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 1204.0067 | 13318.0724 | 0 | 2178.5773 | 14.428 | 249.8638 | 2233.361 | 12363.2134 | 29337.3284 | 47553.0633 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578 | 37556.6578
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - residential | $/customer min |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - business | $/customer min |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 31811.1238 | 58874.5876 | 98935.1734 | 154305.0909 | 248687.9693 | 388032.5663 | 536043.5426 | 677290.0033 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872
Capital expenditure
| Construct new feeders from MG to JA |  |  | 2023-12-31 | -7918867.3 | -9269805.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Construct new feeders from MG to JA |  |  | 2023-12-31 | -7918867.3 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Construct new feeders from MG to JA |  |  | 2023-12-31 | 0 | -337610.6886 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -337610.6886 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929
| Annualised capex |  |  | 2023-12-31 | 0 | -337610.6886 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 31811.1238 | 58874.5876 | 98935.1734 | 154305.0909 | 248687.9693 | 388032.5663 | 536043.5426 | 677290.0033 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | -337610.6886 | -701005.7692 | -673942.3054 | -633881.7196 | -578511.8021 | -484128.9237 | -344784.3267 | -196773.3504 | -55526.8896 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | -337610.6886 | -701005.7692 | -673942.3054 | -633881.7196 | -578511.8021 | -484128.9237 | -344784.3267 | -196773.3504 | -55526.8896 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058
| Total annualised capex |  |  |  | 0 | -337610.6886 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929
| Total benefits |  |  |  | 0 | 0 | 31811.1238 | 58874.5876 | 98935.1734 | 154305.0909 | 248687.9693 | 388032.5663 | 536043.5426 | 677290.0033 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872 | 604137.4872
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | -371371.7574 | -774287.4584 | -747223.9947 | -707163.4089 | -651793.4914 | -557410.6129 | -418066.016 | -270055.0397 | -128808.5789 | -201961.0951 | -201961.0951 | -201961.0951 | -201961.0951 | -201961.0951 | -201961.0951 | -201961.0951 | -201961.0951 | -201961.0951 | -201961.0951 | -201961.0951 | -201961.0951 | -201961.0951 | -201961.0951 | -201961.0951
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | -303849.6197 | -627724.0799 | -600660.6161 | -560600.0303 | -505230.1128 | -410847.2344 | -271502.6374 | -123491.6611 | 17754.7997 | -55397.7165 | -55397.7165 | -55397.7165 | -55397.7165 | -55397.7165 | -55397.7165 | -55397.7165 | -55397.7165 | -55397.7165 | -55397.7165 | -55397.7165 | -55397.7165 | -55397.7165 | -55397.7165 | -55397.7165
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | -337610.6886 | -697824.6568 | -668054.8466 | -623988.2022 | -563081.293 | -459260.1267 | -305981.0701 | -143168.9961 | 12202.1107 | -68265.6571 | -68265.6571 | -68265.6571 | -68265.6571 | -68265.6571 | -68265.6571 | -68265.6571 | -68265.6571 | -68265.6571 | -68265.6571 | -68265.6571 | -68265.6571 | -68265.6571 | -68265.6571 | -68265.6571
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | -337610.6886 | -704186.8815 | -679829.7641 | -643775.2369 | -593942.3112 | -508997.7206 | -383587.5833 | -250377.7046 | -123255.8899 | -189093.1545 | -189093.1545 | -189093.1545 | -189093.1545 | -189093.1545 | -189093.1545 | -189093.1545 | -189093.1545 | -189093.1545 | -189093.1545 | -189093.1545 | -189093.1545 | -189093.1545 | -189093.1545 | -189093.1545
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | -371371.7574 | -777468.5708 | -753111.4534 | -717056.9262 | -667224.0005 | -582279.4099 | -456869.2726 | -323659.3939 | -196537.5792 | -262374.8438 | -262374.8438 | -262374.8438 | -262374.8438 | -262374.8438 | -262374.8438 | -262374.8438 | -262374.8438 | -262374.8438 | -262374.8438 | -262374.8438 | -262374.8438 | -262374.8438 | -262374.8438 | -262374.8438
sens | 0 | 0% | 0% | Option 2sens | 0 | -337610.6886 | -701005.7692 | -673942.3054 | -633881.7196 | -578511.8021 | -484128.9237 | -344784.3267 | -196773.3504 | -55526.8896 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058
sens | 0 | 0% | 0% | Option 2sens | 0 | -337610.6886 | -701005.7692 | -673942.3054 | -633881.7196 | -578511.8021 | -484128.9237 | -344784.3267 | -196773.3504 | -55526.8896 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058
sens | 0 | 0% | 0% | Option 2sens | 0 | -337610.6886 | -701005.7692 | -673942.3054 | -633881.7196 | -578511.8021 | -484128.9237 | -344784.3267 | -196773.3504 | -55526.8896 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058 | -128679.4058

## Option3
CitiPower
CBD security of supply
OPTION 3 | Construct new feeders from MG to JA and rebuild J
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
[5 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Construct new feeders from MG to JA |  | 50 | 2023-12-31 | 7918867.3 | 9269805.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rebuild J zone substation |  | 50 | 2023-12-31 | 0 | 0 | 500000 | 15000000 | 18600000 | 18600000 | 9300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 7918867.3 | 9269805.7099 | 500000 | 15000000 | 18600000 | 18600000 | 9300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Const end date |  | 2033
| Energy at risk 10% PoE |  | 30% | MWh | 0.11902 | 1.1632 | 0 | 0.21536 | 0.0014263 | 0.0247 | 0.22077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk 50% PoE |  | 70% | MWh | 0 | 0.065696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0.035706 | 0.39496 | 0 | 0.064608 | 0.00042788 | 0.0074099 | 0.066232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 33720.0512 | 2023-12-31 | 1204.0067 | 13318.0724 | 0 | 2178.5773 | 14.428 | 249.8638 | 2233.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 1204.0067 | 13318.0724 | 0 | 2178.5773 | 14.428 | 249.8638 | 2233.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 31811.1238 | 58874.5876 | 98935.1734 | 154305.0909 | 248687.9693 | 400395.7797 | 565380.871 | 724843.0667 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145
Capital expenditure
| Construct new feeders from MG to JA |  |  | 2023-12-31 | -7918867.3 | -9269805.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rebuild J zone substation |  |  | 2023-12-31 | 0 | 0 | -500000 | -15000000 | -18600000 | -18600000 | -9300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Construct new feeders from MG to JA |  |  | 2023-12-31 | -7918867.3 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099
| Rebuild J zone substation |  |  | 2023-12-31 | 0 | 0 | -500000 | -15500000 | -34100000 | -52700000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Construct new feeders from MG to JA |  |  | 2023-12-31 | 0 | -337610.6886 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929
| Annualised capex - Rebuild J zone substation |  |  | 2023-12-31 | 0 | 0 | 0 | -21316.8548 | -660822.4983 | -1453809.4962 | -2246796.4942 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -337610.6886 | -732816.8929 | -754133.7477 | -1393639.3912 | -2186626.3892 | -2979613.3871 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861
| Annualised capex |  |  | 2023-12-31 | 0 | -337610.6886 | -732816.8929 | -754133.7477 | -1393639.3912 | -2186626.3892 | -2979613.3871 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 31811.1238 | 58874.5876 | 98935.1734 | 154305.0909 | 248687.9693 | 400395.7797 | 565380.871 | 724843.0667 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | -337610.6886 | -701005.7692 | -695259.1602 | -1294704.2179 | -2032321.2983 | -2730925.4178 | -2975711.1064 | -2810726.0151 | -2651263.8194 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | -337610.6886 | -701005.7692 | -695259.1602 | -1294704.2179 | -2032321.2983 | -2730925.4178 | -2975711.1064 | -2810726.0151 | -2651263.8194 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411
| Total annualised capex |  |  |  | 0 | -337610.6886 | -732816.8929 | -754133.7477 | -1393639.3912 | -2186626.3892 | -2979613.3871 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861
| Total benefits |  |  |  | 0 | 0 | 31811.1238 | 58874.5876 | 98935.1734 | 154305.0909 | 248687.9693 | 400395.7797 | 565380.871 | 724843.0667 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | -371371.7574 | -774287.4584 | -770672.5349 | -1434068.157 | -2250983.9372 | -3028886.7565 | -3313321.795 | -3148336.7037 | -2988874.508 | -3072023.4297 | -3072023.4297 | -3072023.4297 | -3072023.4297 | -3072023.4297 | -3072023.4297 | -3072023.4297 | -3072023.4297 | -3072023.4297 | -3072023.4297 | -3072023.4297 | -3072023.4297 | -3072023.4297 | -3072023.4297 | -3072023.4297
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | -303849.6197 | -627724.0799 | -619845.7854 | -1155340.2787 | -1813658.6594 | -2432964.0791 | -2638100.4178 | -2473115.3265 | -2313653.1308 | -2396802.0525 | -2396802.0525 | -2396802.0525 | -2396802.0525 | -2396802.0525 | -2396802.0525 | -2396802.0525 | -2396802.0525 | -2396802.0525 | -2396802.0525 | -2396802.0525 | -2396802.0525 | -2396802.0525 | -2396802.0525 | -2396802.0525
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | -337610.6886 | -697824.6568 | -689371.7014 | -1284810.7005 | -2016890.7892 | -2706056.6209 | -2935671.5284 | -2754187.928 | -2578779.5127 | -2670243.3266 | -2670243.3266 | -2670243.3266 | -2670243.3266 | -2670243.3266 | -2670243.3266 | -2670243.3266 | -2670243.3266 | -2670243.3266 | -2670243.3266 | -2670243.3266 | -2670243.3266 | -2670243.3266 | -2670243.3266 | -2670243.3266
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | -337610.6886 | -704186.8815 | -701146.6189 | -1304597.7352 | -2047751.8074 | -2755794.2147 | -3015750.6844 | -2867264.1022 | -2723748.1261 | -2798582.1556 | -2798582.1556 | -2798582.1556 | -2798582.1556 | -2798582.1556 | -2798582.1556 | -2798582.1556 | -2798582.1556 | -2798582.1556 | -2798582.1556 | -2798582.1556 | -2798582.1556 | -2798582.1556 | -2798582.1556 | -2798582.1556
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | -371371.7574 | -777468.5708 | -776559.9937 | -1443961.6743 | -2266414.4463 | -3053755.5534 | -3353361.373 | -3204874.7908 | -3061358.8147 | -3136192.8442 | -3136192.8442 | -3136192.8442 | -3136192.8442 | -3136192.8442 | -3136192.8442 | -3136192.8442 | -3136192.8442 | -3136192.8442 | -3136192.8442 | -3136192.8442 | -3136192.8442 | -3136192.8442 | -3136192.8442 | -3136192.8442
sens | 0 | 0% | 0% | Option 3sens | 0 | -337610.6886 | -701005.7692 | -695259.1602 | -1294704.2179 | -2032321.2983 | -2730925.4178 | -2975711.1064 | -2810726.0151 | -2651263.8194 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411
sens | 0 | 0% | 0% | Option 3sens | 0 | -337610.6886 | -701005.7692 | -695259.1602 | -1294704.2179 | -2032321.2983 | -2730925.4178 | -2975711.1064 | -2810726.0151 | -2651263.8194 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411
sens | 0 | 0% | 0% | Option 3sens | 0 | -337610.6886 | -701005.7692 | -695259.1602 | -1294704.2179 | -2032321.2983 | -2730925.4178 | -2975711.1064 | -2810726.0151 | -2651263.8194 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411 | -2734412.7411

## Option4
CitiPower
CBD security of supply
OPTION 4 | Rebuild J zone substation
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
[5 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Rebuild J zone substation |  | 50 | 2023-12-31 | 6000000 | 24800000 | 25200000 | 6000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 6000000 | 24800000 | 25200000 | 6000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Const end date |  | 2029
| Energy at risk 10% PoE |  | 30% | MWh | 0.11902 | 1.1632 | 2.4742 | 4.3101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk 50% PoE |  | 70% | MWh | 0 | 0.065696 | 0.28731 | 0.73936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0.035706 | 0.39496 | 0.94339 | 1.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 33720.0512 | 2023-12-31 | 1204.0067 | 13318.0724 | 31811.1238 | 61053.1649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 1204.0067 | 13318.0724 | 31811.1238 | 61053.1649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 98949.6014 | 154554.9547 | 250921.3303 | 400395.7797 | 565380.871 | 724843.0667 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145
Capital expenditure
| Rebuild J zone substation |  |  | 2023-12-31 | -6000000 | -24800000 | -25200000 | -6000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Rebuild J zone substation |  |  | 2023-12-31 | -6000000 | -30800000 | -56000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Rebuild J zone substation |  |  | 2023-12-31 | 0 | -255802.2574 | -1313118.2546 | -2387487.7357 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -255802.2574 | -1313118.2546 | -2387487.7357 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931
| Annualised capex |  |  | 2023-12-31 | 0 | -255802.2574 | -1313118.2546 | -2387487.7357 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 98949.6014 | 154554.9547 | 250921.3303 | 400395.7797 | 565380.871 | 724843.0667 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | -255802.2574 | -1313118.2546 | -2387487.7357 | -2544340.3918 | -2488735.0384 | -2392368.6628 | -2242894.2134 | -2077909.1221 | -1918446.9265 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | -255802.2574 | -1313118.2546 | -2387487.7357 | -2544340.3918 | -2488735.0384 | -2392368.6628 | -2242894.2134 | -2077909.1221 | -1918446.9265 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482
| Total annualised capex |  |  |  | 0 | -255802.2574 | -1313118.2546 | -2387487.7357 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 98949.6014 | 154554.9547 | 250921.3303 | 400395.7797 | 565380.871 | 724843.0667 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145 | 641694.145
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | -281382.4831 | -1444430.0801 | -2626236.5093 | -2808669.3911 | -2753064.0378 | -2656697.6621 | -2507223.2128 | -2342238.1214 | -2182775.9258 | -2265924.8475 | -2265924.8475 | -2265924.8475 | -2265924.8475 | -2265924.8475 | -2265924.8475 | -2265924.8475 | -2265924.8475 | -2265924.8475 | -2265924.8475 | -2265924.8475 | -2265924.8475 | -2265924.8475 | -2265924.8475 | -2265924.8475
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | -230222.0317 | -1181806.4292 | -2148738.9622 | -2280011.3925 | -2224406.0391 | -2128039.6635 | -1978565.2141 | -1813580.1228 | -1654117.9272 | -1737266.8489 | -1737266.8489 | -1737266.8489 | -1737266.8489 | -1737266.8489 | -1737266.8489 | -1737266.8489 | -1737266.8489 | -1737266.8489 | -1737266.8489 | -1737266.8489 | -1737266.8489 | -1737266.8489 | -1737266.8489 | -1737266.8489
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | -255802.2574 | -1313118.2546 | -2387487.7357 | -2534445.4316 | -2473279.543 | -2367276.5298 | -2202854.6355 | -2021371.035 | -1845962.6198 | -1937426.4337 | -1937426.4337 | -1937426.4337 | -1937426.4337 | -1937426.4337 | -1937426.4337 | -1937426.4337 | -1937426.4337 | -1937426.4337 | -1937426.4337 | -1937426.4337 | -1937426.4337 | -1937426.4337 | -1937426.4337 | -1937426.4337
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | -255802.2574 | -1313118.2546 | -2387487.7357 | -2554235.3519 | -2504190.5339 | -2417460.7958 | -2282933.7914 | -2134447.2092 | -1990931.2331 | -2065765.2627 | -2065765.2627 | -2065765.2627 | -2065765.2627 | -2065765.2627 | -2065765.2627 | -2065765.2627 | -2065765.2627 | -2065765.2627 | -2065765.2627 | -2065765.2627 | -2065765.2627 | -2065765.2627 | -2065765.2627 | -2065765.2627
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | -281382.4831 | -1444430.0801 | -2626236.5093 | -2818564.3512 | -2768519.5332 | -2681789.7951 | -2547262.7907 | -2398776.2085 | -2255260.2324 | -2330094.262 | -2330094.262 | -2330094.262 | -2330094.262 | -2330094.262 | -2330094.262 | -2330094.262 | -2330094.262 | -2330094.262 | -2330094.262 | -2330094.262 | -2330094.262 | -2330094.262 | -2330094.262 | -2330094.262
sens | 0 | 0% | 0% | Option 4sens | 0 | -255802.2574 | -1313118.2546 | -2387487.7357 | -2544340.3918 | -2488735.0384 | -2392368.6628 | -2242894.2134 | -2077909.1221 | -1918446.9265 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482
sens | 0 | 0% | 0% | Option 4sens | 0 | -255802.2574 | -1313118.2546 | -2387487.7357 | -2544340.3918 | -2488735.0384 | -2392368.6628 | -2242894.2134 | -2077909.1221 | -1918446.9265 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482
sens | 0 | 0% | 0% | Option 4sens | 0 | -255802.2574 | -1313118.2546 | -2387487.7357 | -2544340.3918 | -2488735.0384 | -2392368.6628 | -2242894.2134 | -2077909.1221 | -1918446.9265 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482 | -2001595.8482

## Option5
CitiPower
CBD security of supply
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
[5 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Const end date |  | 2027
| Energy at risk 10% PoE |  | 30% | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk 50% PoE |  | 70% | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 33720.0512 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
CitiPower
CBD security of supply
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 7851881.3347 | 2026-06-30 |  | 1332.4698 | 14739.0629 | 35205.2565 | 67567.3184 | 109507.1686 | 171045.4136 | 277693.7356 | 443116.5721 | 625704.9805 | 802181.22 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 6212490.3232 | 2026-06-30 |  | 1332.4698 | 14739.0629 | 35205.2565 | 67567.3184 | 109507.1686 | 171045.4136 | 277693.7356 | 443116.5721 | 625704.9805 | 802181.22 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 437678.5245 | 2026-06-30 |  | 1332.4698 | 14739.0629 | 0 | 2411.0237 | 15.9674 | 276.5234 | 2471.6527 | 13682.3239 | 32467.5161 | 52626.8045 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184
Option 2 | Capital expenditure | Option 2Capital expenditure | -18357235.9082 | 2026-06-30 |  | -8763782.016 | -10258860.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 341729.313 | 2026-06-30 |  | 1332.4698 | 14739.0629 | 0 | 2411.0237 | 15.9674 | 276.5234 | 2471.6527 | 13682.3239 | 32467.5161 | 52626.8045 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 41563.8184 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -10513766.5519 | 2026-06-30 |  | 0 | -373632.5372 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | -811005.825 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 5870761.0102 | 2026-06-30 |  | 0 | 0 | 35205.2565 | 65156.2947 | 109491.2012 | 170768.8902 | 275222.0829 | 429434.2482 | 593237.4644 | 749554.4155 | 668596.7885 | 668596.7885 | 668596.7885 | 668596.7885 | 668596.7885 | 668596.7885 | 668596.7885 | 668596.7885 | 668596.7885 | 668596.7885 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | -373632.5372 | -775800.5684 | -745849.5302 | -701514.6237 | -640236.9348 | -535783.742 | -381571.5767 | -217768.3605 | -61451.4094 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | -4643005.5417 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -10513766.5519 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 5870761.0102 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 19663.9862 | 2026-06-30 |  | 1332.4698 | 14739.0629 | 0 | 2411.0237 | 15.9674 | 276.5234 | 2471.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Capital expenditure | Option 3Capital expenditure | -76480694.958 | 2026-06-30 |  | -8763782.016 | -10258860.705 | -553348.2052 | -16600446.1572 | -20584553.2349 | -20584553.2349 | -10292276.6175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 19663.9862 | 2026-06-30 |  | 1332.4698 | 14739.0629 | 0 | 2411.0237 | 15.9674 | 276.5234 | 2471.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -38580801.6576 | 2026-06-30 |  | 0 | -373632.5372 | -811005.825 | -834597.1116 | -1542335.7118 | -2419931.5759 | -3297527.4401 | -3736325.3722 | -3736325.3722 | -3736325.3722 | -3736325.3722 | -3736325.3722 | -3736325.3722 | -3736325.3722 | -3736325.3722 | -3736325.3722 | -3736325.3722 | -3736325.3722 | -3736325.3722 | -3736325.3722 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 6192826.3369 | 2026-06-30 |  | 0 | 0 | 35205.2565 | 65156.2947 | 109491.2012 | 170768.8902 | 275222.0829 | 443116.5721 | 625704.9805 | 802181.22 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | -373632.5372 | -775800.5684 | -769440.8169 | -1432844.5105 | -2249162.6858 | -3022305.3572 | -3293208.8001 | -3110620.3917 | -2934144.1522 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | -32387975.3207 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -38580801.6576 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 6192826.3369 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 107514.1279 | 2026-06-30 |  | 1332.4698 | 14739.0629 | 35205.2565 | 67567.3184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | -64070045.0033 | 2026-06-30 |  | -6640178.4629 | -27446070.9799 | -27888749.5441 | -6640178.4629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 107514.1279 | 2026-06-30 |  | 1332.4698 | 14739.0629 | 35205.2565 | 67567.3184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | -35310607.0615 | 2026-06-30 |  | 0 | -283095.4401 | -1453223.259 | -2642224.1072 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | -2925319.5473 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 6104976.1953 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 109507.1686 | 171045.4136 | 277693.7356 | 443116.5721 | 625704.9805 | 802181.22 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 710160.6068 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | -283095.4401 | -1453223.259 | -2642224.1072 | -2815812.3786 | -2754274.1337 | -2647625.8117 | -2482202.9751 | -2299614.5668 | -2123138.3272 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | -29205630.8662 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -35310607.0615 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 6104976.1953 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 3 | Annualised capex | -1 |  |  | Option 3 annualised capex | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.0013325 | 0.014739 | 0.035205 | 0.067567 | 0.10951 | 0.17105 | 0.27769 | 0.44312 | 0.6257 | 0.80218 | 0.71016 | 0.71016 | 0.71016 | 0.71016 | 0.71016 | 0.71016 | 0.71016 | 0.71016 | 0.71016 | 0.71016 | 0.71016 | 0.71016 | 0.71016 | 0.71016 | 0.71016
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 21.4959 |  |  | Energy at risk energy at risk (weighted) | 0.035706 | 0.39496 | 0.94339 | 1.8106 | 2.9344 | 4.5835 | 7.4413 | 11.8741 | 16.7669 | 21.4959 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03
Option 1 (base case) | Energy at risk value | 0.72484 |  |  | Option 1 (base case) risk cost | 0.001204 | 0.013318 | 0.031811 | 0.061053 | 0.09895 | 0.15455 | 0.25092 | 0.4004 | 0.56538 | 0.72484 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169 | 0.64169

## Sensitivity_calcs
CitiPower
CBD security of supply
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | -142409.0365 | -142409.0365 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | -4643005.5417 |  | 0 | 0 | -373632.5372 | -775800.5684 | -745849.5302 | -701514.6237 | -640236.9348 | -535783.742 | -381571.5767 | -217768.3605 | -61451.4094 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | -5694382.1969 |  | 0 | 0 | -410995.7909 | -856901.1509 | -826950.1127 | -782615.2062 | -721337.5173 | -616884.3245 | -462672.1592 | -298868.943 | -142551.9919 | -223509.619 | -223509.619 | -223509.619 | -223509.619 | -223509.619 | -223509.619 | -223509.619 | -223509.619 | -223509.619 | -223509.619 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | -3591628.8865 |  | 0 | 0 | -336269.2835 | -694699.986 | -664748.9477 | -620414.0412 | -559136.3523 | -454683.1595 | -300470.9942 | -136667.7781 | 19649.1731 | -61308.454 | -61308.454 | -61308.454 | -61308.454 | -61308.454 | -61308.454 | -61308.454 | -61308.454 | -61308.454 | -61308.454 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | -4055929.4407 |  | 0 | 0 | -373632.5372 | -772280.0428 | -739333.9008 | -690565.5036 | -623160.0458 | -508261.5337 | -338628.1519 | -158444.6141 | 13504.0321 | -75549.3576 | -75549.3576 | -75549.3576 | -75549.3576 | -75549.3576 | -75549.3576 | -75549.3576 | -75549.3576 | -75549.3576 | -75549.3576 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | -5230081.6427 |  | 0 | 0 | -373632.5372 | -779321.0941 | -752365.1597 | -712463.7438 | -657313.8238 | -563305.9503 | -424515.0016 | -277092.107 | -136406.851 | -209268.7153 | -209268.7153 | -209268.7153 | -209268.7153 | -209268.7153 | -209268.7153 | -209268.7153 | -209268.7153 | -209268.7153 | -209268.7153 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | -6281458.2979 |  | 0 | 0 | -410995.7909 | -860421.6766 | -833465.7422 | -793564.3263 | -738414.4063 | -644406.5328 | -505615.5841 | -358192.6895 | -217507.4335 | -290369.2978 | -290369.2978 | -290369.2978 | -290369.2978 | -290369.2978 | -290369.2978 | -290369.2978 | -290369.2978 | -290369.2978 | -290369.2978 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | -4643005.5417 |  | 0 | 0 | -373632.5372 | -775800.5684 | -745849.5302 | -701514.6237 | -640236.9348 | -535783.742 | -381571.5767 | -217768.3605 | -61451.4094 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | -4643005.5417 |  | 0 | 0 | -373632.5372 | -775800.5684 | -745849.5302 | -701514.6237 | -640236.9348 | -535783.742 | -381571.5767 | -217768.3605 | -61451.4094 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | -4643005.5417 |  | 0 | 0 | -373632.5372 | -775800.5684 | -745849.5302 | -701514.6237 | -640236.9348 | -535783.742 | -381571.5767 | -217768.3605 | -61451.4094 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | -142409.0365 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | -373632.5372 | -775800.5684 | -769440.8169 | -1432844.5105 | -2249162.6858 | -3022305.3572 | -3293208.8001 | -3110620.3917 | -2934144.1522 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | -32387975.3207 |  | 0 | 0 | -373632.5372 | -775800.5684 | -769440.8169 | -1432844.5105 | -2249162.6858 | -3022305.3572 | -3293208.8001 | -3110620.3917 | -2934144.1522 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | -36246055.4865 |  | 0 | 0 | -410995.7909 | -856901.1509 | -852900.5281 | -1587078.0817 | -2491155.8434 | -3352058.1012 | -3666841.3373 | -3484252.9289 | -3307776.6894 | -3399797.3026 | -3399797.3026 | -3399797.3026 | -3399797.3026 | -3399797.3026 | -3399797.3026 | -3399797.3026 | -3399797.3026 | -3399797.3026 | -3399797.3026 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | -28529895.1549 |  | 0 | 0 | -336269.2835 | -694699.986 | -685981.1057 | -1278610.9394 | -2007169.5282 | -2692552.6132 | -2919576.2628 | -2736987.8545 | -2560511.615 | -2652532.2281 | -2652532.2281 | -2652532.2281 | -2652532.2281 | -2652532.2281 | -2652532.2281 | -2652532.2281 | -2652532.2281 | -2652532.2281 | -2652532.2281 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | -31768692.687 |  | 0 | 0 | -373632.5372 | -772280.0428 | -762925.1874 | -1421895.3904 | -2232085.7968 | -2994783.1489 | -3248897.1428 | -3048049.8937 | -2853926.0302 | -2955148.7047 | -2955148.7047 | -2955148.7047 | -2955148.7047 | -2955148.7047 | -2955148.7047 | -2955148.7047 | -2955148.7047 | -2955148.7047 | -2955148.7047 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | -33007257.9544 |  | 0 | 0 | -373632.5372 | -779321.0941 | -775956.4464 | -1443793.6307 | -2266239.5748 | -3049827.5655 | -3337520.4573 | -3173190.8898 | -3014362.2742 | -3097180.826 | -3097180.826 | -3097180.826 | -3097180.826 | -3097180.826 | -3097180.826 | -3097180.826 | -3097180.826 | -3097180.826 | -3097180.826 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | -36865338.1202 |  | 0 | 0 | -410995.7909 | -860421.6766 | -859416.1575 | -1598027.2018 | -2508232.7324 | -3379580.3095 | -3711152.9945 | -3546823.427 | -3387994.8114 | -3470813.3633 | -3470813.3633 | -3470813.3633 | -3470813.3633 | -3470813.3633 | -3470813.3633 | -3470813.3633 | -3470813.3633 | -3470813.3633 | -3470813.3633 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -32387975.3207 |  | 0 | 0 | -373632.5372 | -775800.5684 | -769440.8169 | -1432844.5105 | -2249162.6858 | -3022305.3572 | -3293208.8001 | -3110620.3917 | -2934144.1522 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -32387975.3207 |  | 0 | 0 | -373632.5372 | -775800.5684 | -769440.8169 | -1432844.5105 | -2249162.6858 | -3022305.3572 | -3293208.8001 | -3110620.3917 | -2934144.1522 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -32387975.3207 |  | 0 | 0 | -373632.5372 | -775800.5684 | -769440.8169 | -1432844.5105 | -2249162.6858 | -3022305.3572 | -3293208.8001 | -3110620.3917 | -2934144.1522 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | -3026164.7654 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | -29205630.8662 |  | 0 | 0 | -283095.4401 | -1453223.259 | -2642224.1072 | -2815812.3786 | -2754274.1337 | -2647625.8117 | -2482202.9751 | -2299614.5668 | -2123138.3272 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | -32736691.5724 |  | 0 | 0 | -311404.9841 | -1598545.5849 | -2906446.5179 | -3108344.3333 | -3046806.0884 | -2940157.7664 | -2774734.9298 | -2592146.5215 | -2415670.2819 | -2507690.8951 | -2507690.8951 | -2507690.8951 | -2507690.8951 | -2507690.8951 | -2507690.8951 | -2507690.8951 | -2507690.8951 | -2507690.8951 | -2507690.8951 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | -25674570.1601 |  | 0 | 0 | -254785.8961 | -1307900.9331 | -2378001.6965 | -2523280.4239 | -2461742.179 | -2355093.8569 | -2189671.0204 | -2007082.612 | -1830606.3725 | -1922626.9857 | -1922626.9857 | -1922626.9857 | -1922626.9857 | -1922626.9857 | -1922626.9857 | -1922626.9857 | -1922626.9857 | -1922626.9857 | -1922626.9857 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | -28595133.2467 |  | 0 | 0 | -283095.4401 | -1453223.259 | -2642224.1072 | -2804861.6618 | -2737169.5923 | -2619856.4381 | -2437891.3179 | -2237044.0687 | -2042920.2052 | -2144142.8797 | -2144142.8797 | -2144142.8797 | -2144142.8797 | -2144142.8797 | -2144142.8797 | -2144142.8797 | -2144142.8797 | -2144142.8797 | -2144142.8797 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | -29816128.4857 |  | 0 | 0 | -283095.4401 | -1453223.259 | -2642224.1072 | -2826763.0955 | -2771378.675 | -2675395.1852 | -2526514.6323 | -2362185.0648 | -2203356.4492 | -2286175.0011 | -2286175.0011 | -2286175.0011 | -2286175.0011 | -2286175.0011 | -2286175.0011 | -2286175.0011 | -2286175.0011 | -2286175.0011 | -2286175.0011 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | -33347189.1919 |  | 0 | 0 | -311404.9841 | -1598545.5849 | -2906446.5179 | -3119295.0502 | -3063910.6298 | -2967927.1399 | -2819046.587 | -2654717.0195 | -2495888.4039 | -2578706.9558 | -2578706.9558 | -2578706.9558 | -2578706.9558 | -2578706.9558 | -2578706.9558 | -2578706.9558 | -2578706.9558 | -2578706.9558 | -2578706.9558 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -29205630.8662 |  | 0 | 0 | -283095.4401 | -1453223.259 | -2642224.1072 | -2815812.3786 | -2754274.1337 | -2647625.8117 | -2482202.9751 | -2299614.5668 | -2123138.3272 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -29205630.8662 |  | 0 | 0 | -283095.4401 | -1453223.259 | -2642224.1072 | -2815812.3786 | -2754274.1337 | -2647625.8117 | -2482202.9751 | -2299614.5668 | -2123138.3272 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -29205630.8662 |  | 0 | 0 | -283095.4401 | -1453223.259 | -2642224.1072 | -2815812.3786 | -2754274.1337 | -2647625.8117 | -2482202.9751 | -2299614.5668 | -2123138.3272 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | -2215158.9404 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | TRUE | FALSE | FALSE | FALSE | TRUE |  | 2028-29: FALSE
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None |  | -4.643 | -32.388 | -29.2056 |  |  | 2026-27: -4.643; 2028-29: Option 2
sens1 | Capex 10% higher |  | -5.6944 | -36.2461 | -32.7367 |  |  | 2026-27: -5.6944; 2028-29: Option 2
sens2 | Capex 10% lower |  | -3.5916 | -28.5299 | -25.6746 |  |  | 2026-27: -3.5916; 2028-29: Option 2
sens3 | Total benefits 10% higher |  | -4.0559 | -31.7687 | -28.5951 |  |  | 2026-27: -4.0559; 2028-29: Option 2
sens4 | Total benefits 10% lower |  | -5.2301 | -33.0073 | -29.8161 |  |  | 2026-27: -5.2301; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower |  | -6.2815 | -36.8653 | -33.3472 |  |  | 2026-27: -6.2815; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: 0
sens | 0 | [6 empty] | 2026-27: 0
sens | 0 | [6 empty] | 2026-27: 0

## Misc_calcs
CitiPower
CBD security of supply
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 2.425%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 2.425% | 2.425%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1854 | 1.1997
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.1997
| Conversion from input dollars to output dollars |  | 1.1067
| Convert from VCR date | 2024-12-31 | 1.1482
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 0.94406
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | 1 | TRUE
| Option 5 | Not used | FALSE
| First year | 1

## Data
CitiPower
CBD security of supply
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | TRUE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | TRUE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | FALSE | June | 6 | CY | Not used | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | TRUE | December | 12 | FY |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [5 empty] | 2024 |  | 2024-25
2023
2022
2021
2020