## Cover
CitiPower
Revised proposal 2026-31
Transformer refurbishment
| Model number: | 3.4.04
2025-12-01
5
2025-06-30

## Summary
CitiPower
Transformer refurbishment
| Number where option 2 is preferred |  |  |  |  | 9
| Total for 2026-31 regulatory period |  |  |  |  | 6
| Cost per ZSS refurbishment |  |  |  | 2026-06-30 | 586549.0976
| Total capital cost for where option 2 is preferred for 2026-31 |  |  |  | 2026-06-30 | 3519294.5853
|  |  | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | Total
| Number refurbished |  | 1 | 1 | 1 | 1 | 2 | 6
| Capital expenditure | 2026-06-30 | 586549.0976 | 586549.0976 | 586549.0976 | 586549.0976 | 1173098.1951 | 3519294.5853

## Assumptions
CitiPower
Transformer refurbishment
Project
| Business: |  | CitiPower
| Descripton: |  | Transformer refurbishment
| Date of cost inputs: |  | December |  | 2023
| Option |  | Description
| Option 1 (base case) |  | No change to existing practices
| Option 2 |  | Refurbish transformer
| Option 3 |  | Replace transformer
Timing & WACC
| Input dollars |  |  |  | 2023-12-31 | [input_dollars]
| Output dollars |  |  |  | 2026-06-30 | [output_dollars]
Costs
| Oil Value $/L |  | 2023-12-31 |  | 117.5
[5 empty] | Cost | Life (years) | Annual cost
| Replacement Cost |  | 2023-12-31 |  | 6120000 | 40 | 153000
| Refurbishment Cost |  | 2023-12-31 |  | 530000 | 20 | 26500
| Leak Cleanup Cost Savings |  | 2023-12-31 |  | 100000 | 20 | 5000
Other
Capped leak rate
| >300 | 300
Modifiers
PCB Modifier
| 2 |  | 5
| NO |  | 1
| Unknown |  | 1
| Depth to ground water score |  | Factor
| >5m |  | 1
| 1-5m |  | 3
| Distance (m) |  | Distance Modifier
| 0-40m | 0 | 2.5
| 41-80m | 40 | 1.5
| 81-120m | 80 | 1.2
| >120m | 120 | 1
| Unknown | 100000 | 1
| Bund Y / N |  | Bunding Modifier
| Y |  | 0.1 | Modern, concrete bund or equivalent
| Earthen |  | 1 | SEC brick wall, gravel base
| N |  | 2 | zero containment
| Unknown |  | 1

## Calcs
CitiPower
Transformer refurbishment
| Transformers |  | 97 | [11 empty] | 9 |  | 6
Option 2 preferred
| Equipment ID | Transformer | ZSS | Leak Rate/Y (L) | Name of Waterway | Dist to Waterway (m) | Bund | Depth to ground | PCB | Distance | Bunding | GW depth | PCB | Risk | Refurbishment | Refurbishment | Refurbishment
|  | description | [5 empty] | water score |  | modifier | modifier | modifier | modifier | ($ 2023) | benefit-cost ratio | before June 2026 | 2026-31
| 10266753 | NR NO2 66/11KV TRANS | NR | >300 | YARRA RIVER | 715.4652 | Earthen | 1-5m | NO | 1 | 1 | 3 | 1 | 110750 | 4.1792 | TRUE | FALSE
| 10266737 | CW No3 66/11KV TRANS | CW | >300 | YARRA RIVER | 1205.7683 | Earthen | 1-5m | NO | 1 | 1 | 3 | 1 | 110750 | 4.1792 | TRUE | FALSE
| 10266737 | CW No1 66/11KV TRANS | CW | >300 | YARRA RIVER | 1205.7683 | Earthen | 1-5m | NO | 1 | 1 | 3 | 1 | 110750 | 4.1792 | TRUE | FALSE
| 10266826 | AP No2 66/11KV TRANS | AP | >300 | YARRA RIVER | 1371.6927 | Earthen | 1-5m | NO | 1 | 1 | 3 | 1 | 110750 | 4.1792 |  | TRUE
| 10266769 | SO NO1 66/11KV TRANS | SO | 66.6667 | YARRA RIVER | 905.4524 | N | 1-5m | NO | 1 | 2 | 3 | 1 | 52000 | 1.9623 |  | TRUE
| 10266792 | FB NO3 66/11KV TRANS | FB | 105 | YARRA RIVER | 384.3759 | Earthen | 1-5m | NO | 1 | 1 | 3 | 1 | 42012.5 | 1.5854 |  | TRUE
| 10266753 | NR NO1 66/11KV TRANS | NR | 99 | YARRA RIVER | 715.4652 | Earthen | 1-5m | NO | 1 | 1 | 3 | 1 | 39897.5 | 1.5056 |  | TRUE
| 10266769 | SO NO2 66/11KV TRANS | SO | 33.4 | YARRA RIVER | 905.4524 | N | 1-5m | NO | 1 | 2 | 3 | 1 | 28547 | 1.0772 |  | TRUE
| 10266769 | SO NO3 66/11KV TRANS | SO | 33.2 | YARRA RIVER | 905.4524 | N | 1-5m | NO | 1 | 2 | 3 | 1 | 28406 | 1.0719 |  | TRUE
| 10266745 | B No2 66/11KV TRANS | B | >300 | YARRA RIVER | 813.8737 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 15575 | 0.58774 |  | FALSE
| 10266604 | VM NO3 66/11KV TRANS | VM | >300 | YARRA RIVER | 1392.4743 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 15575 | 0.58774 |  | FALSE
| 10266826 | AP No1 66/11KV TRANS | AP | 25 | YARRA RIVER | 1371.6927 | Earthen | 1-5m | NO | 1 | 1 | 3 | 1 | 13812.5 | 0.52123 |  | FALSE
| 10266745 | B No3 66/11KV TRANS | B | 237.9 | YARRA RIVER | 813.8737 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 13385.975 | 0.50513 |  | FALSE
| 10266723 | WB NO1 66/6.6KV TRANS | WB | 33.6 | MOONEE PONDS CREEK | 1710.3448 | N | >5m | NO | 1 | 2 | 1 | 1 | 12896 | 0.48664 |  | FALSE
| 10266723 | WB NO2 66/6.6KV TRANS | WB | 33.5 | MOONEE PONDS CREEK | 1710.3448 | N | >5m | NO | 1 | 2 | 1 | 1 | 12872.5 | 0.48575 |  | FALSE
| 10266777 | MG NO2 66/11KV TRANS | MG | 200 | YARRA RIVER | 575.9209 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 12050 | 0.45472 |  | FALSE
| 10266683 | R NO1 22/11KV TRANS | R | 150.1 | YARRA RIVER | 113.9822 | Y | 1-5m | NO | 1.2 | 0.1 | 3 | 1 | 11349.23 | 0.42827 |  | FALSE
| 10266683 | R NO2 22/11KV TRANS | R | 150 | YARRA RIVER | 113.9822 | Y | 1-5m | NO | 1.2 | 0.1 | 3 | 1 | 11345 | 0.42811 |  | FALSE
| 10266629 | E NO1 66/6.6KV TRANS | E | 116.8 | YARRA RIVER | 576.4338 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 9117.2 | 0.34405 |  | FALSE
| 10266777 | MG NO1 66/11KV TRANS | MG | 116.6667 | YARRA RIVER | 575.9209 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 9112.5 | 0.34387 |  | FALSE
| 10266581 | WA NO2 66/11KV TRANS | WA | 73.3333 | YARRA RIVER | 777.3757 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 7585 | 0.28623 |  | FALSE
| 10266614 | JA NO2 66/11/11KV TRANS | JA | 66.78 | YARRA RIVER | 768.4477 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 7353.995 | 0.27751 |  | FALSE
| 10266643 | AR No1 66/11KV TRANS | AR | 200.1 | GARDINERS CREEK | 1994.2207 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 7351.175 | 0.2774 |  | FALSE
| 10266624 | LQ NO1 66/11KV TRANS | LQ | 66.6667 | YARRA RIVER | 601.2774 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 7350 | 0.27736 |  | FALSE
| 10266643 | AR No2 66/11KV TRANS | AR | 183.3333 | GARDINERS CREEK | 1994.2207 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 7154.1667 | 0.26997 |  | FALSE
| 10266581 | WA NO1 66/11KV TRANS | WA | 58.3333 | YARRA RIVER | 777.3757 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 7056.25 | 0.26627 |  | FALSE
| 10266581 | WA NO3 66/11KV TRANS | WA | 50 | YARRA RIVER | 777.3757 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 6762.5 | 0.25519 |  | FALSE
| 10266871 | NC NO1 66/11KV TRANS | NC | 136.6667 | MERRI CREEK | 1203.1552 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 6605.8333 | 0.24928 |  | FALSE
| 10266651 | BC No1 66/11KV TRANS | BC | 133.3333 | ELSTER CREEK | 2093.8728 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 6566.6667 | 0.2478 |  | FALSE
| 10266566 | FR NO3 66/11KV TRANS | FR | 33.39 | YARRA RIVER | 346.469 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 6176.9975 | 0.23309 |  | FALSE
| 10266777 | MG NO3 66/11KV TRANS | MG | 33.3333 | YARRA RIVER | 575.9209 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 6175 | 0.23302 |  | FALSE
| 10266604 | VM NO1 66/11KV TRANS | VM | 33.3333 | YARRA RIVER | 1392.4743 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 6175 | 0.23302 |  | FALSE
| 10266635 | PM NO2 66/6.6KV TRANS | PM | 84.1667 | OCEAN - BAY | 918.9858 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 5988.9583 | 0.226 |  | FALSE
| 10266691 | CL No2 66/11KV TRANS | CL | 83.4 | HAWTHORN MAIN DRAIN | 298.7864 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 5979.95 | 0.22566 |  | FALSE
| 10266691 | CL No1 66/11KV TRANS | CL | 83.3333 | HAWTHORN MAIN DRAIN | 298.7864 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 5979.1667 | 0.22563 |  | FALSE
| 10266707 | L NO3 66/11KV TRANS | L | 75 | GLASS CREEK | 1839.1727 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 5881.25 | 0.22193 |  | FALSE
| 10266707 | L NO1 66/11KV TRANS | L | 58.39 | GLASS CREEK | 1839.1727 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 5686.0825 | 0.21457 |  | FALSE
| 10266635 | PM NO3 66/6.6KV TRANS | PM | 53.33 | OCEAN - BAY | 918.9858 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 5626.6275 | 0.21233 |  | FALSE
| 10266604 | VM NO2 66/11KV TRANS | VM | 16.6667 | YARRA RIVER | 1392.4743 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 5587.5 | 0.21085 |  | FALSE
| 10266842 | BK No1 22/6.6KV TRANS | BK | 38.3333 | MERRI CREEK | 730.0057 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 5450.4167 | 0.20568 |  | FALSE
| 10266871 | NC NO2 66/11KV TRANS | NC | 33.4 | MERRI CREEK | 1203.1552 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 5392.45 | 0.20349 |  | FALSE
| 10266842 | BK No2 22/6.6KV TRANS | BK | 33.3333 | MERRI CREEK | 730.0057 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 5391.6667 | 0.20346 |  | FALSE
| 10266715 | C NO1 22/6.6KV TRANS (EX ZSS C) | C | 0 | MERRI CREEK | 1629.9889 | N | >5m | NO | 1 | 2 | 1 | 1 | 0 | 0 |  | FALSE
| 10266715 | C NO3 22/6.6KV TRANS (EX ZSS C) | C | 0 | MERRI CREEK | 1629.9889 | N | >5m | NO | 1 | 2 | 1 | 1 | 0 | 0 |  | FALSE
| 10266593 | DA No1 66/11/11KV TRANS | DA | 0 | MOONEE PONDS CREEK | 254.7963 | Earthen | >5m | NO | 1 | 1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266715 | C NO2 22/6.6KV TRANS (EX ZSS C) | C | 0 | MERRI CREEK | 1629.9889 | N | >5m | NO | 1 | 2 | 1 | 1 | 0 | 0 |  | FALSE
| 10266593 | DA No3 66/11/11KV TRANS | DA | 0 | MOONEE PONDS CREEK | 254.7963 | Earthen | >5m | NO | 1 | 1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266826 | AP No3 66/11KV TRANS | AP | 0 | YARRA RIVER | 1371.6927 | Earthen | 1-5m | NO | 1 | 1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266651 | BC No2 66/11KV TRANS | BC | 0 | ELSTER CREEK | 2093.8728 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266651 | BC No3 66/11KV TRANS | BC | 0 | ELSTER CREEK | 2093.8728 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266842 | BK No3 22/6.6KV TRANS | BK | 0 | MERRI CREEK | 730.0057 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266842 | BK BK3 6.6KV FDR 11/6.6KV AUTO TRANS | BK | 0 | MERRI CREEK | 730.0057 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266842 | BK BK4 6.6KV FDR 11/6.6KV AUTO TRANS | BK | 0 | MERRI CREEK | 730.0057 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266842 | BK BK11 6.6KV FDR 11/6.6KV AUTO TRANS | BK | 0 | MERRI CREEK | 730.0057 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266609 | BQ No1 66/11/11KV TRANS | BQ | 0 | YARRA RIVER | 1485.569 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266609 | BQ No3 66/11/11KV TRANS | BQ | 0 | YARRA RIVER | 1485.569 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266691 | CL No3 66/11KV TRANS | CL | 0 | HAWTHORN MAIN DRAIN | 298.7864 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266737 | CW CW9-F32 11/6.6KV AUTO TRANS @CW | CW | 0 | YARRA RIVER | 1205.7683 | UNKNOWN | 1-5m | UNKNOWN | 1 | 1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266729 | F NO3 22/6.6KV TRANS | F | 0 | MERRI CREEK | 533.1668 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266729 | F NO1 22/6.6KV TRANS | F | 0 | MERRI CREEK | 533.1668 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266792 | FB NO1 66/11KV TRANS | FB | 0 | YARRA RIVER | 384.3759 | Earthen | 1-5m | NO | 1 | 1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266792 | FB NO2 66/11KV TRANS | FB | 0 | YARRA RIVER | 384.3759 | Earthen | 1-5m | NO | 1 | 1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266566 | FR NO1 66/11KV TRANS | FR | 0 | YARRA RIVER | 346.469 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266566 | FR NO2 66/11KV TRANS | FR | 0 | YARRA RIVER | 346.469 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266614 | JA NO1 66/11/11KV TRANS | JA | 0 | YARRA RIVER | 768.4477 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266614 | JA NO3 66/11/11KV TRANS | JA | 0 | YARRA RIVER | 768.4477 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266624 | LQ NO2 66/11KV TRANS | LQ | 0 | YARRA RIVER | 601.2774 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266624 | LQ NO3 66/11KV TRANS | LQ | 0 | YARRA RIVER | 601.2774 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266598 | LS NO1 22/6.6KV TRANS (EX ZSS LS) | LS | 0 | MOONEE PONDS CREEK | 559.8358 | UNKNOWN | >5m | UNKNOWN | 1 | 1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266598 | LS NO2 22/6.6KV TRANS (EX ZSS LS) | LS | 0 | MOONEE PONDS CREEK | 559.8358 | UNKNOWN | >5m | UNKNOWN | 1 | 1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266598 | LS NO3 22/6.6KV TRANS (EX ZSS LS) | LS | 0 | MOONEE PONDS CREEK | 559.8358 | UNKNOWN | >5m | UNKNOWN | 1 | 1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266576 | MP NO1 66/11/11KV TRANS | MP | 0 | YARRA RIVER | 670.1667 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266576 | MP N02 66/11/11KV TRANS | MP | 0 | YARRA RIVER | 670.1667 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266576 | MP NO3 66/11/11KV TRANS | MP | 0 | YARRA RIVER | 670.1667 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266753 | NR NO3 66/11KV TRANS | NR | 0 | YARRA RIVER | 715.4652 | Earthen | 1-5m | NO | 1 | 1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266761 | Q NO1 66/11KV TRANS | Q | 0 | YARRA RIVER | 949.4634 | N | 1-5m | NO | 1 | 2 | 3 | 1 | 0 | 0 |  | FALSE
| 10266761 | Q NO3 66/11KV TRANS | Q | 0 | YARRA RIVER | 949.4634 | N | 1-5m | NO | 1 | 2 | 3 | 1 | 0 | 0 |  | FALSE
| 10266683 | R NO3 22/11KV TRANS | R | 0 | YARRA RIVER | 113.9822 | Y | 1-5m | NO | 1.2 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266699 | RD NO1 66/11KV TRANS | RD | 0 | NICHOLLSDALE RD DRAIN | 112.7444 | N | >5m | NO | 1.2 | 2 | 1 | 1 | 0 | 0 |  | FALSE
| 10266699 | RD NO2 66/11KV TRANS | RD | 0 | NICHOLLSDALE RD DRAIN | 112.7444 | N | >5m | NO | 1.2 | 2 | 1 | 1 | 0 | 0 |  | FALSE
| 54413343 | SB NO1 66/11/11KV TRANS | SB | 0 | YARRA RIVER | 574.3836 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 54413343 | SB NO2 66/11/11KV TRANS | SB | 0 | YARRA RIVER | 574.3836 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266675 | SK NO1 66/11KV TRANS | SK | 0 | OCEAN - BAY | 1312.577 | N | >5m | NO | 1 | 2 | 1 | 1 | 0 | 0 |  | FALSE
| 10266675 | SK NO2 66/11KV TRANS | SK | 0 | OCEAN - BAY | 1312.577 | N | >5m | NO | 1 | 2 | 1 | 1 | 0 | 0 |  | FALSE
| 10266675 | SK NO3 66/11KV TRANS | SK | 0 | OCEAN - BAY | 1312.577 | N | >5m | NO | 1 | 2 | 1 | 1 | 0 | 0 |  | FALSE
| 10266659 | TK NO1 66/11KV TRANS | TK | 0 | YARRA RIVER | 932.6422 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266659 | TK NO2 66/11KV TRANS | TK | 0 | YARRA RIVER | 932.6422 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266659 | TK NO3 66/11KV TRANS | TK | 0 | YARRA RIVER | 932.6422 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266723 | WB NO3 66/6.6KV TRANS | WB | 0 | MOONEE PONDS CREEK | 1710.3448 | Y | >5m | NO | 1 | 0.1 | 1 | 1 | 0 | 0 |  | FALSE
| 10266930 | WG NO2 66/11 KV TRANS | WG | 0 | YARRA RIVER | 559.1629 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266930 | WG NO1 66/11 KV TRANS | WG | 0 | YARRA RIVER | 559.1629 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266930 | WG AUTO TRANS NO 3 | WG | 0 | YARRA RIVER | 559.1629 | UNKNOWN | 1-5m | UNKNOWN | 1 | 1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266930 | WG AUTO TRANS NO 4 | WG | 0 | YARRA RIVER | 559.1629 | UNKNOWN | 1-5m | UNKNOWN | 1 | 1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266930 | WG AUTO TRANS NO 2 | WG | 0 | YARRA RIVER | 559.1629 | UNKNOWN | 1-5m | UNKNOWN | 1 | 1 | 3 | 1 | 0 | 0 |  | FALSE
| 10266930 | WG NO3 66/11 KV TRANS | WG | 0 | YARRA RIVER | 559.1629 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 181629913 | WP No1 66/11/11KV TRANS | WP | 0 | YARRA RIVER | 794.4251 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE
| 181629913 | WP No2 66/11/11KV TRANS | WP | 0 | YARRA RIVER | 794.4251 | Y | 1-5m | NO | 1 | 0.1 | 3 | 1 | 0 | 0 |  | FALSE

## Misc_calcs
CitiPower
Transformer refurbishment
DROPDOWN LISTS
| Dollar inputs - month |  |  | Not used options | Conversions |  | Dollar inputs - year
| June | 6 | CY | Not used |  |  | 2023
| December | 12 | FY |  |  |  | 2022
2021
2020
ESCALATION & OTHER
| Year end |  |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 2.425%
| HY ending |  |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 2.425% | 2.425%
| Actual cumulative HY escalation |  |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1854 | 1.1997
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.1997
| Conversion from input dollars to output dollars |  | 1.1067