## Expected Design Life Relays
Expected Design Life Relays
| CN | CS | NH
Digital | 20 Years | 20 Years | 20 Years

## NH Relay Failure Scenarios
NH Relay Failure Scenarios - Do Nothing
Consequence Duration (Min) | 90
[9 empty] | Asset PoFailure (Ergon Weibull Paper) | [25 empty] | Scenario (LoC - Likelihood of Consequence)
Item | Scenarios | Asset Age @ year 2026 | Asset Type | Consequence | N-# based on Consequence | Consequence Duration (Hr) | Probability of Fault | X (PoFX) | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | Failure (malop) of NEI/TTS PW Relay during a line fault on NH-NEL or NEL-WT or WT-TTS 66kV line | 54 | Electromechanical | Station Black | 3 | 1.5 | 0.2 | 1 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 1 | 0.16771 | 0.17299 | 0.17772 | 0.18188 | 0.18549 | 0.18857 | 0.19114 | 0.19326 | 0.19497 | 0.19632 | 0.19736 | 0.19815 | 0.19873 | 0.19915 | 0.19944 | 0.19965 | 0.19978 | 0.19987 | 0.19992 | 0.19996 | 0.19998 | 0.19999 | 0.19999 | 0.2 | 0.2 | 0.2
2 | Failure (malop) of NEI/TTS Dir OC Y Relay during a line fault on NH-NEL or NEL-WT or WT-TTS 66kV line | 22 | Digital | Station Black | 3 | 1.5 | 0.2 | 1 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.17695 | 0.18112 | 0.18467 | 0.18765 | 0.19013 | 0.19218 | 0.19386 | 0.19521 | 0.1963 | 0.19716 | 0.19784 | 0.19837 | 0.19878 | 0.19909 | 0.19933 | 0.19951 | 0.19965 | 0.19975 | 0.19982 | 0.19987 | 0.19991 | 0.19994 | 0.19996 | 0.19997 | 0.19998 | 0.19999
3 | Failure (malop for FDR Fault) of No1 22kV Bus OC Protection (R Ph) | 53 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 0.5399 | 0.5593 | 0.57692 | 0.59268 | 0.60657 | 0.61861 | 0.62887 | 0.63747 | 0.64453 | 0.65022 | 0.65472 | 0.65819 | 0.66082 | 0.66276 | 0.66416 | 0.66515 | 0.66582 | 0.66627 | 0.66656 | 0.66674 | 0.66686 | 0.66692 | 0.66696 | 0.66698 | 0.66699 | 0.667
4 | Failure (malop for FDR Fault)) of No1 22kV Bus OC Protection (W Ph) | 53 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 0.5399 | 0.5593 | 0.57692 | 0.59268 | 0.60657 | 0.61861 | 0.62887 | 0.63747 | 0.64453 | 0.65022 | 0.65472 | 0.65819 | 0.66082 | 0.66276 | 0.66416 | 0.66515 | 0.66582 | 0.66627 | 0.66656 | 0.66674 | 0.66686 | 0.66692 | 0.66696 | 0.66698 | 0.66699 | 0.667
5 | Failure (malop for FDR Fault)) of No1 22kV Bus OC Protection (B Ph) | 53 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 0.5399 | 0.5593 | 0.57692 | 0.59268 | 0.60657 | 0.61861 | 0.62887 | 0.63747 | 0.64453 | 0.65022 | 0.65472 | 0.65819 | 0.66082 | 0.66276 | 0.66416 | 0.66515 | 0.66582 | 0.66627 | 0.66656 | 0.66674 | 0.66686 | 0.66692 | 0.66696 | 0.66698 | 0.66699 | 0.667
6 | Failure (malop for FDR Fault)) of No1 22kV Bus Diff Protection | 21 | Digital | No1 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.57392 | 0.59012 | 0.60404 | 0.61586 | 0.62581 | 0.63409 | 0.64093 | 0.64651 | 0.65103 | 0.65465 | 0.65753 | 0.6598 | 0.66157 | 0.66293 | 0.66398 | 0.66477 | 0.66537 | 0.66582 | 0.66615 | 0.66639 | 0.66657 | 0.6667 | 0.66679 | 0.66685 | 0.6669 | 0.66693
7 | Failure (malop for FDR Fault) of No2 22kV Bus OC Protection (R Ph) | 53 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 0.32378 | 0.33541 | 0.34598 | 0.35543 | 0.36376 | 0.37098 | 0.37714 | 0.38229 | 0.38652 | 0.38994 | 0.39263 | 0.39472 | 0.39629 | 0.39746 | 0.3983 | 0.39889 | 0.39929 | 0.39956 | 0.39974 | 0.39985 | 0.39991 | 0.39995 | 0.39997 | 0.39999 | 0.39999 | 0.4
8 | Failure (malop for FDR Fault)) of No2 22kV Bus OC Protection (W Ph) | 53 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 0.32378 | 0.33541 | 0.34598 | 0.35543 | 0.36376 | 0.37098 | 0.37714 | 0.38229 | 0.38652 | 0.38994 | 0.39263 | 0.39472 | 0.39629 | 0.39746 | 0.3983 | 0.39889 | 0.39929 | 0.39956 | 0.39974 | 0.39985 | 0.39991 | 0.39995 | 0.39997 | 0.39999 | 0.39999 | 0.4
9 | Failure (malop for FDR Fault)) of No2 22kV Bus OC Protection (B Ph) | 53 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 0.32378 | 0.33541 | 0.34598 | 0.35543 | 0.36376 | 0.37098 | 0.37714 | 0.38229 | 0.38652 | 0.38994 | 0.39263 | 0.39472 | 0.39629 | 0.39746 | 0.3983 | 0.39889 | 0.39929 | 0.39956 | 0.39974 | 0.39985 | 0.39991 | 0.39995 | 0.39997 | 0.39999 | 0.39999 | 0.4
10 | Failure (malop for FDR Fault)) of No2 22kV Bus Diff Protection | 21 | Digital | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.34418 | 0.3539 | 0.36224 | 0.36933 | 0.3753 | 0.38027 | 0.38436 | 0.38771 | 0.39042 | 0.3926 | 0.39432 | 0.39568 | 0.39674 | 0.39756 | 0.39819 | 0.39867 | 0.39902 | 0.39929 | 0.39949 | 0.39964 | 0.39974 | 0.39982 | 0.39987 | 0.39991 | 0.39994 | 0.39996
11 | Failure (malop for FDR Fault)) of No3 22kV Bus OC Protection | 22 | Digital | No3 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.59012 | 0.60404 | 0.61586 | 0.62581 | 0.63409 | 0.64093 | 0.64651 | 0.65103 | 0.65465 | 0.65753 | 0.6598 | 0.66157 | 0.66293 | 0.66398 | 0.66477 | 0.66537 | 0.66582 | 0.66615 | 0.66639 | 0.66657 | 0.6667 | 0.66679 | 0.66685 | 0.6669 | 0.66693 | 0.66695
12 | Failure (malop for FDR Fault)) of No3 22kV Bus Diff Protection | 22 | Digital | No3 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.59012 | 0.60404 | 0.61586 | 0.62581 | 0.63409 | 0.64093 | 0.64651 | 0.65103 | 0.65465 | 0.65753 | 0.6598 | 0.66157 | 0.66293 | 0.66398 | 0.66477 | 0.66537 | 0.66582 | 0.66615 | 0.66639 | 0.66657 | 0.6667 | 0.66679 | 0.66685 | 0.6669 | 0.66693 | 0.66695
13 | Failure of NH02 feeder protection for a feeder fault | 20 | Digital | No1 Bus Outage | 1 | 1.5 | 1 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985
14 | Failure of NH03 feeder protection for a feeder fault | 22 | Digital | No1 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.3539 | 0.36224 | 0.36933 | 0.3753 | 0.38027 | 0.38436 | 0.38771 | 0.39042 | 0.3926 | 0.39432 | 0.39568 | 0.39674 | 0.39756 | 0.39819 | 0.39867 | 0.39902 | 0.39929 | 0.39949 | 0.39964 | 0.39974 | 0.39982 | 0.39987 | 0.39991 | 0.39994 | 0.39996 | 0.39997
15 | Failure of NH05 feeder protection for a feeder fault | 22 | Digital | No1 Bus Outage | 1 | 1.5 | 0.6 | 1 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.53085 | 0.54336 | 0.554 | 0.56295 | 0.5704 | 0.57655 | 0.58157 | 0.58563 | 0.58889 | 0.59148 | 0.59352 | 0.59511 | 0.59634 | 0.59728 | 0.598 | 0.59854 | 0.59894 | 0.59924 | 0.59946 | 0.59961 | 0.59973 | 0.59981 | 0.59987 | 0.59991 | 0.59994 | 0.59996
16 | Failure of NH08 feeder protection for a feeder fault | 20 | Digital | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.33298 | 0.34418 | 0.3539 | 0.36224 | 0.36933 | 0.3753 | 0.38027 | 0.38436 | 0.38771 | 0.39042 | 0.3926 | 0.39432 | 0.39568 | 0.39674 | 0.39756 | 0.39819 | 0.39867 | 0.39902 | 0.39929 | 0.39949 | 0.39964 | 0.39974 | 0.39982 | 0.39987 | 0.39991 | 0.39994
17 | Failure of NH09 feeder protection for a feeder fault | 20 | Digital | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.33298 | 0.34418 | 0.3539 | 0.36224 | 0.36933 | 0.3753 | 0.38027 | 0.38436 | 0.38771 | 0.39042 | 0.3926 | 0.39432 | 0.39568 | 0.39674 | 0.39756 | 0.39819 | 0.39867 | 0.39902 | 0.39929 | 0.39949 | 0.39964 | 0.39974 | 0.39982 | 0.39987 | 0.39991 | 0.39994
18 | Failure of NH12 feeder protection for a feeder fault | 20 | Digital | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.33298 | 0.34418 | 0.3539 | 0.36224 | 0.36933 | 0.3753 | 0.38027 | 0.38436 | 0.38771 | 0.39042 | 0.3926 | 0.39432 | 0.39568 | 0.39674 | 0.39756 | 0.39819 | 0.39867 | 0.39902 | 0.39929 | 0.39949 | 0.39964 | 0.39974 | 0.39982 | 0.39987 | 0.39991 | 0.39994
19 | Failure of NH13 feeder protection for a feeder fault | 20 | Digital | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.33298 | 0.34418 | 0.3539 | 0.36224 | 0.36933 | 0.3753 | 0.38027 | 0.38436 | 0.38771 | 0.39042 | 0.3926 | 0.39432 | 0.39568 | 0.39674 | 0.39756 | 0.39819 | 0.39867 | 0.39902 | 0.39929 | 0.39949 | 0.39964 | 0.39974 | 0.39982 | 0.39987 | 0.39991 | 0.39994
20 | Failure of NH16 feeder protection for a feeder fault | 22 | Digital | No3 Bus Outage | 1 | 1.5 | 0.6 | 1 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.53085 | 0.54336 | 0.554 | 0.56295 | 0.5704 | 0.57655 | 0.58157 | 0.58563 | 0.58889 | 0.59148 | 0.59352 | 0.59511 | 0.59634 | 0.59728 | 0.598 | 0.59854 | 0.59894 | 0.59924 | 0.59946 | 0.59961 | 0.59973 | 0.59981 | 0.59987 | 0.59991 | 0.59994 | 0.59996
21 | Failure of NH17 feeder protection for a feeder fault | 20 | Digital | No3 Bus Outage | 1 | 1.5 | 0.8 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.66596 | 0.68836 | 0.70779 | 0.72448 | 0.73867 | 0.7506 | 0.76053 | 0.76873 | 0.77543 | 0.78085 | 0.78519 | 0.78864 | 0.79136 | 0.79348 | 0.79512 | 0.79638 | 0.79733 | 0.79805 | 0.79859 | 0.79898 | 0.79927 | 0.79949 | 0.79964 | 0.79975 | 0.79983 | 0.79988
22 | Failure of NH20 feeder protection for a feeder fault | 15 | Digital | No3 Bus Outage | 1 | 1.5 | 0.6 | 1 | 0.63212 | 0.6802 | 0.7244 | 0.76452 | 0.80052 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.37927 | 0.40812 | 0.43464 | 0.45871 | 0.48031 | 0.49947 | 0.51627 | 0.53085 | 0.54336 | 0.554 | 0.56295 | 0.5704 | 0.57655 | 0.58157 | 0.58563 | 0.58889 | 0.59148 | 0.59352 | 0.59511 | 0.59634 | 0.59728 | 0.598 | 0.59854 | 0.59894 | 0.59924 | 0.59946
23 | Failure of No1 Cap Bank Prot (Current Balance) | 40 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.1 | 1 | 0.32524 | 0.36013 | 0.39659 | 0.43439 | 0.47323 | 0.5128 | 0.55273 | 0.59264 | 0.63212 | 0.67077 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.032524 | 0.036013 | 0.039659 | 0.043439 | 0.047323 | 0.05128 | 0.055273 | 0.059264 | 0.063212 | 0.067077 | 0.070819 | 0.0744 | 0.077785 | 0.080944 | 0.083853 | 0.086494 | 0.088858 | 0.09094 | 0.092745 | 0.094284 | 0.095572 | 0.096631 | 0.097484 | 0.098158 | 0.09868 | 0.099074
24 | Failure of No1 Cap Bank Prot (OC & EF) | 20 | Digital | No1 Bus Outage | 1 | 1.5 | 0.1 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.083244 | 0.086045 | 0.088474 | 0.09056 | 0.092333 | 0.093824 | 0.095067 | 0.096091 | 0.096928 | 0.097606 | 0.098149 | 0.098581 | 0.09892 | 0.099185 | 0.09939 | 0.099547 | 0.099666 | 0.099756 | 0.099823 | 0.099873 | 0.099909 | 0.099936 | 0.099955 | 0.099969 | 0.099978 | 0.099985
25 | Failure of No2 Cap Bank Prot (Current Balance) | 20 | Digital | No2 Bus Outage | 1 | 1.5 | 0.1 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.083244 | 0.086045 | 0.088474 | 0.09056 | 0.092333 | 0.093824 | 0.095067 | 0.096091 | 0.096928 | 0.097606 | 0.098149 | 0.098581 | 0.09892 | 0.099185 | 0.09939 | 0.099547 | 0.099666 | 0.099756 | 0.099823 | 0.099873 | 0.099909 | 0.099936 | 0.099955 | 0.099969 | 0.099978 | 0.099985
26 | Failure of No2 Cap Bank Prot (OC & EF) | 20 | Digital | No2 Bus Outage | 1 | 1.5 | 0.1 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.083244 | 0.086045 | 0.088474 | 0.09056 | 0.092333 | 0.093824 | 0.095067 | 0.096091 | 0.096928 | 0.097606 | 0.098149 | 0.098581 | 0.09892 | 0.099185 | 0.09939 | 0.099547 | 0.099666 | 0.099756 | 0.099823 | 0.099873 | 0.099909 | 0.099936 | 0.099955 | 0.099969 | 0.099978 | 0.099985
27 | Failure of MEF protection for a NH02 feeder fault | 20 | Analogue Electronic | No1 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.036914 | 0.045705 | 0.055915 | 0.067649 | 0.080999 | 0.096038 | 0.11282 | 0.13137 | 0.15167 | 0.17369 | 0.19734 | 0.2225 | 0.24899 | 0.27661 | 0.3051 | 0.33417 | 0.36351 | 0.39278 | 0.42162 | 0.4497 | 0.47667 | 0.50223 | 0.52612 | 0.54812 | 0.56806 | 0.58586
28 | Failure of MEF protection for a NH03 feeder fault | 20 | Analogue Electronic | No1 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.036914 | 0.045705 | 0.055915 | 0.067649 | 0.080999 | 0.096038 | 0.11282 | 0.13137 | 0.15167 | 0.17369 | 0.19734 | 0.2225 | 0.24899 | 0.27661 | 0.3051 | 0.33417 | 0.36351 | 0.39278 | 0.42162 | 0.4497 | 0.47667 | 0.50223 | 0.52612 | 0.54812 | 0.56806 | 0.58586
29 | Failure of MEF protection for a NH05 feeder fault | 20 | Analogue Electronic | No1 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.036914 | 0.045705 | 0.055915 | 0.067649 | 0.080999 | 0.096038 | 0.11282 | 0.13137 | 0.15167 | 0.17369 | 0.19734 | 0.2225 | 0.24899 | 0.27661 | 0.3051 | 0.33417 | 0.36351 | 0.39278 | 0.42162 | 0.4497 | 0.47667 | 0.50223 | 0.52612 | 0.54812 | 0.56806 | 0.58586
30 | Failure of MEF protection for a NH08 feeder fault | 20 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.022138 | 0.027409 | 0.033532 | 0.040569 | 0.048575 | 0.057594 | 0.067658 | 0.078781 | 0.090958 | 0.10416 | 0.11835 | 0.13343 | 0.14932 | 0.16588 | 0.18297 | 0.2004 | 0.218 | 0.23555 | 0.25285 | 0.26968 | 0.28586 | 0.30119 | 0.31552 | 0.32871 | 0.34067 | 0.35134
31 | Failure of MEF protection for a NH09 feeder fault | 20 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.022138 | 0.027409 | 0.033532 | 0.040569 | 0.048575 | 0.057594 | 0.067658 | 0.078781 | 0.090958 | 0.10416 | 0.11835 | 0.13343 | 0.14932 | 0.16588 | 0.18297 | 0.2004 | 0.218 | 0.23555 | 0.25285 | 0.26968 | 0.28586 | 0.30119 | 0.31552 | 0.32871 | 0.34067 | 0.35134
32 | Failure of MEF protection for a NH12 feeder fault | 20 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.022138 | 0.027409 | 0.033532 | 0.040569 | 0.048575 | 0.057594 | 0.067658 | 0.078781 | 0.090958 | 0.10416 | 0.11835 | 0.13343 | 0.14932 | 0.16588 | 0.18297 | 0.2004 | 0.218 | 0.23555 | 0.25285 | 0.26968 | 0.28586 | 0.30119 | 0.31552 | 0.32871 | 0.34067 | 0.35134
33 | Failure of MEF protection for a NH13 feeder fault | 20 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.022138 | 0.027409 | 0.033532 | 0.040569 | 0.048575 | 0.057594 | 0.067658 | 0.078781 | 0.090958 | 0.10416 | 0.11835 | 0.13343 | 0.14932 | 0.16588 | 0.18297 | 0.2004 | 0.218 | 0.23555 | 0.25285 | 0.26968 | 0.28586 | 0.30119 | 0.31552 | 0.32871 | 0.34067 | 0.35134
34 | Failure of MEF protection for a NH16 feeder fault | 20 | Analogue Electronic | No3 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.036914 | 0.045705 | 0.055915 | 0.067649 | 0.080999 | 0.096038 | 0.11282 | 0.13137 | 0.15167 | 0.17369 | 0.19734 | 0.2225 | 0.24899 | 0.27661 | 0.3051 | 0.33417 | 0.36351 | 0.39278 | 0.42162 | 0.4497 | 0.47667 | 0.50223 | 0.52612 | 0.54812 | 0.56806 | 0.58586
35 | Failure of MEF protection for a NH17 feeder fault | 20 | Analogue Electronic | No3 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.036914 | 0.045705 | 0.055915 | 0.067649 | 0.080999 | 0.096038 | 0.11282 | 0.13137 | 0.15167 | 0.17369 | 0.19734 | 0.2225 | 0.24899 | 0.27661 | 0.3051 | 0.33417 | 0.36351 | 0.39278 | 0.42162 | 0.4497 | 0.47667 | 0.50223 | 0.52612 | 0.54812 | 0.56806 | 0.58586
36 | Failure of MEF protection for a NH20 feeder fault | 20 | Analogue Electronic | No3 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.036914 | 0.045705 | 0.055915 | 0.067649 | 0.080999 | 0.096038 | 0.11282 | 0.13137 | 0.15167 | 0.17369 | 0.19734 | 0.2225 | 0.24899 | 0.27661 | 0.3051 | 0.33417 | 0.36351 | 0.39278 | 0.42162 | 0.4497 | 0.47667 | 0.50223 | 0.52612 | 0.54812 | 0.56806 | 0.58586
37 | Failure (malop) of BUEF protection (No1 Stage 2) | 20 | Digital | No1 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.55524 | 0.57392 | 0.59012 | 0.60404 | 0.61586 | 0.62581 | 0.63409 | 0.64093 | 0.64651 | 0.65103 | 0.65465 | 0.65753 | 0.6598 | 0.66157 | 0.66293 | 0.66398 | 0.66477 | 0.66537 | 0.66582 | 0.66615 | 0.66639 | 0.66657 | 0.6667 | 0.66679 | 0.66685 | 0.6669
38 | Failure (malop) of BUEF protection (No2 Stage 2) | 20 | Digital | No2 Bus Outage | 1 | 1.5 | 0.4 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.33298 | 0.34418 | 0.3539 | 0.36224 | 0.36933 | 0.3753 | 0.38027 | 0.38436 | 0.38771 | 0.39042 | 0.3926 | 0.39432 | 0.39568 | 0.39674 | 0.39756 | 0.39819 | 0.39867 | 0.39902 | 0.39929 | 0.39949 | 0.39964 | 0.39974 | 0.39982 | 0.39987 | 0.39991 | 0.39994
39 | Failure (malop) of BUEF protection (No3 Stage 2) | 20 | Digital | No3 Bus Outage | 1 | 1.5 | 0.667 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.55524 | 0.57392 | 0.59012 | 0.60404 | 0.61586 | 0.62581 | 0.63409 | 0.64093 | 0.64651 | 0.65103 | 0.65465 | 0.65753 | 0.6598 | 0.66157 | 0.66293 | 0.66398 | 0.66477 | 0.66537 | 0.66582 | 0.66615 | 0.66639 | 0.66657 | 0.6667 | 0.66679 | 0.66685 | 0.6669
40 | Failure (malop) of BUEF protection (No1 Stage 3 & No2 Stage 3 & No3 Stage 3) | 20 | Digital | Station Black | 3 | 1.5 | 0.56 | 3 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.32304 | 0.35675 | 0.38783 | 0.41591 | 0.44082 | 0.46253 | 0.48114 | 0.49687 | 0.50997 | 0.52073 | 0.52948 | 0.53649 | 0.54205 | 0.54642 | 0.54982 | 0.55243 | 0.55441 | 0.55591 | 0.55703 | 0.55787 | 0.55848 | 0.55892 | 0.55924 | 0.55947 | 0.55963 | 0.55975
41 | Failure (malop) 1-2 66KV BUS TIE CB FAIL RELAY during a 66kV line fault | 20 | Digital | Station Black | 3 | 1.5 | 0.2 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.16649 | 0.17209 | 0.17695 | 0.18112 | 0.18467 | 0.18765 | 0.19013 | 0.19218 | 0.19386 | 0.19521 | 0.1963 | 0.19716 | 0.19784 | 0.19837 | 0.19878 | 0.19909 | 0.19933 | 0.19951 | 0.19965 | 0.19975 | 0.19982 | 0.19987 | 0.19991 | 0.19994 | 0.19996 | 0.19997
42 | Failure (malop) 2-3 66KV BUS TIE CB FAIL RELAY during a 66kV line fault | 20 | Digital | Station Black | 3 | 1.5 | 0.2 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.16649 | 0.17209 | 0.17695 | 0.18112 | 0.18467 | 0.18765 | 0.19013 | 0.19218 | 0.19386 | 0.19521 | 0.1963 | 0.19716 | 0.19784 | 0.19837 | 0.19878 | 0.19909 | 0.19933 | 0.19951 | 0.19965 | 0.19975 | 0.19982 | 0.19987 | 0.19991 | 0.19994 | 0.19996 | 0.19997
43 | Failure (malop) 1-2 22KV BUS TIE CB FAIL RELAY | 20 | Digital | No1 and No2 Bus Outage | 2 | 1.5 | 0.56 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.46617 | 0.48185 | 0.49546 | 0.50714 | 0.51707 | 0.52542 | 0.53237 | 0.53811 | 0.5428 | 0.54659 | 0.54963 | 0.55205 | 0.55395 | 0.55544 | 0.55658 | 0.55746 | 0.55813 | 0.55863 | 0.55901 | 0.55929 | 0.55949 | 0.55964 | 0.55975 | 0.55982 | 0.55988 | 0.55992
44 | Failure (malop) 2-3 22KV BUS TIE CB FAIL RELAY | 20 | Digital | No2 and No3 Bus Outage | 2 | 1.5 | 0.56 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.46617 | 0.48185 | 0.49546 | 0.50714 | 0.51707 | 0.52542 | 0.53237 | 0.53811 | 0.5428 | 0.54659 | 0.54963 | 0.55205 | 0.55395 | 0.55544 | 0.55658 | 0.55746 | 0.55813 | 0.55863 | 0.55901 | 0.55929 | 0.55949 | 0.55964 | 0.55975 | 0.55982 | 0.55988 | 0.55992
45 | Failure (malop) No1 TRANSFORMER 22KV CB FAIL RELAY | 20 | Digital | No1 Bus Outage | 1 | 1.5 | 0.56 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.46617 | 0.48185 | 0.49546 | 0.50714 | 0.51707 | 0.52542 | 0.53237 | 0.53811 | 0.5428 | 0.54659 | 0.54963 | 0.55205 | 0.55395 | 0.55544 | 0.55658 | 0.55746 | 0.55813 | 0.55863 | 0.55901 | 0.55929 | 0.55949 | 0.55964 | 0.55975 | 0.55982 | 0.55988 | 0.55992
46 | Failure (malop) No2 TRANSFORMER 22KV CB FAIL RELAY | 20 | Digital | No2 Bus Outage | 1 | 1.5 | 0.56 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.46617 | 0.48185 | 0.49546 | 0.50714 | 0.51707 | 0.52542 | 0.53237 | 0.53811 | 0.5428 | 0.54659 | 0.54963 | 0.55205 | 0.55395 | 0.55544 | 0.55658 | 0.55746 | 0.55813 | 0.55863 | 0.55901 | 0.55929 | 0.55949 | 0.55964 | 0.55975 | 0.55982 | 0.55988 | 0.55992
47 | Failure (malop) No3 TRANSFORMER 22KV CB FAIL RELAY | 20 | Digital | No3 Bus Outage | 1 | 1.5 | 0.56 | 1 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.46617 | 0.48185 | 0.49546 | 0.50714 | 0.51707 | 0.52542 | 0.53237 | 0.53811 | 0.5428 | 0.54659 | 0.54963 | 0.55205 | 0.55395 | 0.55544 | 0.55658 | 0.55746 | 0.55813 | 0.55863 | 0.55901 | 0.55929 | 0.55949 | 0.55964 | 0.55975 | 0.55982 | 0.55988 | 0.55992
Total

## CS Relay Failure Scenarios
CS Relay Failure Scenarios - Do Nothing
Consequence Duration (Min) | 90
[9 empty] | Asset PoFailure (Ergon Weibull Paper) | [25 empty] | Scenario (LoC - Likelihood of Consequence)
Item | Scenarios | Asset Age @ year 2026 | Asset Type | Consequence | N-# based on Consequence | Consequence Duration (Hr) | Probability of Fault | X (PoFX) | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | Failure (malop) of No1 and No2 Transformer DIFF Prot | 23 | Digital | Station Black | 2 | 1.5 | 0.28571 | 2 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.23432 | 0.24358 | 0.25151 | 0.25822 | 0.26382 | 0.26843 | 0.2722 | 0.27524 | 0.27766 | 0.27958 | 0.28108 | 0.28224 | 0.28313 | 0.28381 | 0.28432 | 0.2847 | 0.28499 | 0.2852 | 0.28535 | 0.28546 | 0.28553 | 0.28559 | 0.28563 | 0.28566 | 0.28568 | 0.28569
2 | Failure (malop) of No1 and No2 Transformer HTOC Prot (R PH) | 51 | Electromechanical | Station Black | 2 | 1.5 | 0.28571 | 2 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.15815 | 0.17287 | 0.1872 | 0.20089 | 0.21375 | 0.22559 | 0.23629 | 0.24576 | 0.25398 | 0.26097 | 0.26679 | 0.27152 | 0.27529 | 0.27822 | 0.28045 | 0.2821 | 0.28329 | 0.28413 | 0.28471 | 0.28509 | 0.28534 | 0.2855 | 0.28559 | 0.28565 | 0.28568 | 0.2857
3 | Failure (malop) of No1 and No2 Transformer HTOC Prot (W PH) | 51 | Electromechanical | Station Black | 2 | 1.5 | 0.28571 | 2 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.15815 | 0.17287 | 0.1872 | 0.20089 | 0.21375 | 0.22559 | 0.23629 | 0.24576 | 0.25398 | 0.26097 | 0.26679 | 0.27152 | 0.27529 | 0.27822 | 0.28045 | 0.2821 | 0.28329 | 0.28413 | 0.28471 | 0.28509 | 0.28534 | 0.2855 | 0.28559 | 0.28565 | 0.28568 | 0.2857
4 | Failure (malop) of No1 and No2 Transformer HTOC Prot (B PH) | 51 | Electromechanical | Station Black | 2 | 1.5 | 0.28571 | 2 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.15815 | 0.17287 | 0.1872 | 0.20089 | 0.21375 | 0.22559 | 0.23629 | 0.24576 | 0.25398 | 0.26097 | 0.26679 | 0.27152 | 0.27529 | 0.27822 | 0.28045 | 0.2821 | 0.28329 | 0.28413 | 0.28471 | 0.28509 | 0.28534 | 0.2855 | 0.28559 | 0.28565 | 0.28568 | 0.2857
5 | Failure (malop for FDR Fault) of No1 22kV Bus Protection (R Ph) | 50 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.17705 | 0.186 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998
6 | Failure (malop for FDR Fault)) of No1 22kV Bus Protection (W Ph) | 50 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.17705 | 0.186 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998
7 | Failure (malop for FDR Fault)) of No1 22kV Bus Protection (B Ph) | 50 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.17705 | 0.186 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998
8 | Failure (malop for FDR Fault)) of No1 22kV Bus Overload Protection (R Ph) | 50 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.17705 | 0.186 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998
9 | Failure (malop for FDR Fault)) of No1 22kV Bus Overload Protection (W Ph) | 50 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.17705 | 0.186 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998
10 | Failure (malop for FDR Fault)) of No1 22kV Bus Overload Protection (B Ph) | 50 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.17705 | 0.186 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998
11 | Failure (malop for FDR Fault) of No2 22kV Bus Protection (R Ph) | 50 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.22131 | 0.2325 | 0.24308 | 0.25295 | 0.26204 | 0.2703 | 0.27768 | 0.28419 | 0.28983 | 0.29464 | 0.29866 | 0.30197 | 0.30464 | 0.30675 | 0.30837 | 0.30961 | 0.31052 | 0.31117 | 0.31163 | 0.31195 | 0.31216 | 0.31229 | 0.31238 | 0.31243 | 0.31246 | 0.31248
12 | Failure (malop for FDR Fault)) of No2 22kV Bus Protection (W Ph) | 50 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.22131 | 0.2325 | 0.24308 | 0.25295 | 0.26204 | 0.2703 | 0.27768 | 0.28419 | 0.28983 | 0.29464 | 0.29866 | 0.30197 | 0.30464 | 0.30675 | 0.30837 | 0.30961 | 0.31052 | 0.31117 | 0.31163 | 0.31195 | 0.31216 | 0.31229 | 0.31238 | 0.31243 | 0.31246 | 0.31248
13 | Failure (malop for FDR Fault)) of No2 22kV Bus Protection (B Ph) | 50 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.22131 | 0.2325 | 0.24308 | 0.25295 | 0.26204 | 0.2703 | 0.27768 | 0.28419 | 0.28983 | 0.29464 | 0.29866 | 0.30197 | 0.30464 | 0.30675 | 0.30837 | 0.30961 | 0.31052 | 0.31117 | 0.31163 | 0.31195 | 0.31216 | 0.31229 | 0.31238 | 0.31243 | 0.31246 | 0.31248
14 | Failure (malop for FDR Fault)) of No2 22kV Bus Overload Protection (R Ph) | 50 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.22131 | 0.2325 | 0.24308 | 0.25295 | 0.26204 | 0.2703 | 0.27768 | 0.28419 | 0.28983 | 0.29464 | 0.29866 | 0.30197 | 0.30464 | 0.30675 | 0.30837 | 0.30961 | 0.31052 | 0.31117 | 0.31163 | 0.31195 | 0.31216 | 0.31229 | 0.31238 | 0.31243 | 0.31246 | 0.31248
15 | Failure (malop for FDR Fault)) of No2 22kV Bus Overload Protection (W Ph) | 50 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.22131 | 0.2325 | 0.24308 | 0.25295 | 0.26204 | 0.2703 | 0.27768 | 0.28419 | 0.28983 | 0.29464 | 0.29866 | 0.30197 | 0.30464 | 0.30675 | 0.30837 | 0.30961 | 0.31052 | 0.31117 | 0.31163 | 0.31195 | 0.31216 | 0.31229 | 0.31238 | 0.31243 | 0.31246 | 0.31248
16 | Failure (malop for FDR Fault)) of No2 22kV Bus Overload Protection (B Ph) | 50 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.22131 | 0.2325 | 0.24308 | 0.25295 | 0.26204 | 0.2703 | 0.27768 | 0.28419 | 0.28983 | 0.29464 | 0.29866 | 0.30197 | 0.30464 | 0.30675 | 0.30837 | 0.30961 | 0.31052 | 0.31117 | 0.31163 | 0.31195 | 0.31216 | 0.31229 | 0.31238 | 0.31243 | 0.31246 | 0.31248
17 | Failure of CS02 feeder protection for a feeder fault | 22 | Digital | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.22119 | 0.2264 | 0.23083 | 0.23456 | 0.23767 | 0.24023 | 0.24232 | 0.24401 | 0.24537 | 0.24645 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998
18 | Failure of CS03 feeder protection for a feeder fault | 22 | Digital | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.22119 | 0.2264 | 0.23083 | 0.23456 | 0.23767 | 0.24023 | 0.24232 | 0.24401 | 0.24537 | 0.24645 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998
19 | Failure of CS05 feeder protection for a feeder fault | 22 | Digital | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.22119 | 0.2264 | 0.23083 | 0.23456 | 0.23767 | 0.24023 | 0.24232 | 0.24401 | 0.24537 | 0.24645 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998
20 | Failure of CS08 feeder protection for a feeder fault | 22 | Digital | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.27648 | 0.283 | 0.28854 | 0.2932 | 0.29708 | 0.30029 | 0.3029 | 0.30502 | 0.30672 | 0.30806 | 0.30913 | 0.30995 | 0.31059 | 0.31108 | 0.31146 | 0.31174 | 0.31195 | 0.3121 | 0.31222 | 0.3123 | 0.31236 | 0.3124 | 0.31243 | 0.31245 | 0.31247 | 0.31248
21 | Failure of CS09 feeder protection for a feeder fault | 17 | Digital | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.7244 | 0.76452 | 0.80052 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.22637 | 0.23891 | 0.25016 | 0.26014 | 0.26889 | 0.27648 | 0.283 | 0.28854 | 0.2932 | 0.29708 | 0.30029 | 0.3029 | 0.30502 | 0.30672 | 0.30806 | 0.30913 | 0.30995 | 0.31059 | 0.31108 | 0.31146 | 0.31174 | 0.31195 | 0.3121 | 0.31222 | 0.3123 | 0.31236
22 | Failure of CS12 feeder protection for a feeder fault | 17 | Digital | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.7244 | 0.76452 | 0.80052 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.22637 | 0.23891 | 0.25016 | 0.26014 | 0.26889 | 0.27648 | 0.283 | 0.28854 | 0.2932 | 0.29708 | 0.30029 | 0.3029 | 0.30502 | 0.30672 | 0.30806 | 0.30913 | 0.30995 | 0.31059 | 0.31108 | 0.31146 | 0.31174 | 0.31195 | 0.3121 | 0.31222 | 0.3123 | 0.31236
23 | Failure of CS13 feeder protection for a feeder fault | 22 | Digital | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.27648 | 0.283 | 0.28854 | 0.2932 | 0.29708 | 0.30029 | 0.3029 | 0.30502 | 0.30672 | 0.30806 | 0.30913 | 0.30995 | 0.31059 | 0.31108 | 0.31146 | 0.31174 | 0.31195 | 0.3121 | 0.31222 | 0.3123 | 0.31236 | 0.3124 | 0.31243 | 0.31245 | 0.31247 | 0.31248
24 | Failure of No2 Cap Bank Prot (Current Balance R PH) | 50 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.22131 | 0.2325 | 0.24308 | 0.25295 | 0.26204 | 0.2703 | 0.27768 | 0.28419 | 0.28983 | 0.29464 | 0.29866 | 0.30197 | 0.30464 | 0.30675 | 0.30837 | 0.30961 | 0.31052 | 0.31117 | 0.31163 | 0.31195 | 0.31216 | 0.31229 | 0.31238 | 0.31243 | 0.31246 | 0.31248
25 | Failure of No2 Cap Bank Prot (Current Balance W PH) | 50 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.22131 | 0.2325 | 0.24308 | 0.25295 | 0.26204 | 0.2703 | 0.27768 | 0.28419 | 0.28983 | 0.29464 | 0.29866 | 0.30197 | 0.30464 | 0.30675 | 0.30837 | 0.30961 | 0.31052 | 0.31117 | 0.31163 | 0.31195 | 0.31216 | 0.31229 | 0.31238 | 0.31243 | 0.31246 | 0.31248
26 | Failure of No2 Cap Bank Prot (Current Balance B PH) | 50 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.70819 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.22131 | 0.2325 | 0.24308 | 0.25295 | 0.26204 | 0.2703 | 0.27768 | 0.28419 | 0.28983 | 0.29464 | 0.29866 | 0.30197 | 0.30464 | 0.30675 | 0.30837 | 0.30961 | 0.31052 | 0.31117 | 0.31163 | 0.31195 | 0.31216 | 0.31229 | 0.31238 | 0.31243 | 0.31246 | 0.31248
27 | Failure of No2 Cap Bank Prot (OC & OV) | 22 | Digital | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.27648 | 0.283 | 0.28854 | 0.2932 | 0.29708 | 0.30029 | 0.3029 | 0.30502 | 0.30672 | 0.30806 | 0.30913 | 0.30995 | 0.31059 | 0.31108 | 0.31146 | 0.31174 | 0.31195 | 0.3121 | 0.31222 | 0.3123 | 0.31236 | 0.3124 | 0.31243 | 0.31245 | 0.31247 | 0.31248
28 | Failure of MEF protection for a CS02 feeder fault | 22 | Analogue Electronic | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 0.18824 | 0.1972 | 0.20544 | 0.21292 | 0.21959 | 0.22544 | 0.23049
29 | Failure of MEF protection for a CS03 feeder fault | 22 | Analogue Electronic | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 0.18824 | 0.1972 | 0.20544 | 0.21292 | 0.21959 | 0.22544 | 0.23049
30 | Failure of MEF protection for a CS05 feeder fault | 22 | Analogue Electronic | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 0.18824 | 0.1972 | 0.20544 | 0.21292 | 0.21959 | 0.22544 | 0.23049
31 | Failure of MEF protection for a CS08 feeder fault | 22 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.026197 | 0.031695 | 0.037949 | 0.044995 | 0.052858 | 0.061547 | 0.071061 | 0.081377 | 0.092458 | 0.10424 | 0.11666 | 0.1296 | 0.14294 | 0.15657 | 0.17031 | 0.18402 | 0.19754 | 0.21069 | 0.22333 | 0.2353 | 0.2465 | 0.2568 | 0.26615 | 0.27448 | 0.2818 | 0.28811
32 | Failure of MEF protection for a CS09 feeder fault | 22 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.026197 | 0.031695 | 0.037949 | 0.044995 | 0.052858 | 0.061547 | 0.071061 | 0.081377 | 0.092458 | 0.10424 | 0.11666 | 0.1296 | 0.14294 | 0.15657 | 0.17031 | 0.18402 | 0.19754 | 0.21069 | 0.22333 | 0.2353 | 0.2465 | 0.2568 | 0.26615 | 0.27448 | 0.2818 | 0.28811
33 | Failure of MEF protection for a CS12 feeder fault | 22 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.026197 | 0.031695 | 0.037949 | 0.044995 | 0.052858 | 0.061547 | 0.071061 | 0.081377 | 0.092458 | 0.10424 | 0.11666 | 0.1296 | 0.14294 | 0.15657 | 0.17031 | 0.18402 | 0.19754 | 0.21069 | 0.22333 | 0.2353 | 0.2465 | 0.2568 | 0.26615 | 0.27448 | 0.2818 | 0.28811
34 | Failure of MEF protection for a CS13 feeder fault | 22 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.026197 | 0.031695 | 0.037949 | 0.044995 | 0.052858 | 0.061547 | 0.071061 | 0.081377 | 0.092458 | 0.10424 | 0.11666 | 0.1296 | 0.14294 | 0.15657 | 0.17031 | 0.18402 | 0.19754 | 0.21069 | 0.22333 | 0.2353 | 0.2465 | 0.2568 | 0.26615 | 0.27448 | 0.2818 | 0.28811
35 | Failure (malop) of BUEF protection (No1 Stage 2) | 22 | Analogue Electronic | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 0.18824 | 0.1972 | 0.20544 | 0.21292 | 0.21959 | 0.22544 | 0.23049
36 | Failure (malop) of BUEF protection (No2 Stage 2) | 22 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.3125 | 1 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.026197 | 0.031695 | 0.037949 | 0.044995 | 0.052858 | 0.061547 | 0.071061 | 0.081377 | 0.092458 | 0.10424 | 0.11666 | 0.1296 | 0.14294 | 0.15657 | 0.17031 | 0.18402 | 0.19754 | 0.21069 | 0.22333 | 0.2353 | 0.2465 | 0.2568 | 0.26615 | 0.27448 | 0.2818 | 0.28811
37 | Failure (malop) of BUEF protection (No1 Stage 3 & No2 Stage 3) | 22 | Analogue Electronic | Station Black | 2 | 1.5 | 0.28571 | 2 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.0020079 | 0.002939 | 0.0042134 | 0.0059234 | 0.0081743 | 0.011083 | 0.014774 | 0.019375 | 0.025011 | 0.031794 | 0.039816 | 0.049138 | 0.059781 | 0.071718 | 0.084864 | 0.099078 | 0.11416 | 0.12987 | 0.14592 | 0.16199 | 0.17777 | 0.19294 | 0.20724 | 0.22043 | 0.23233 | 0.24285
Total

## CN Relay Failure Scenarios
CN Relay Failure Scenarios - Do Nothing
Consequence Duration (Min) | 90
[9 empty] | Asset PoFailure (Ergon Weibull Paper) | [25 empty] | Scenario (LoC - Likelihood of Consequence)
Item | Scenarios | Asset Age @ year 2026 | Asset Type | Consequence | N-# based on Consequence | Consequence Duration (Hr) | Probability of Fault | X (PoFX) | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | Failure (malop) of No1 Transformer DIFF Prot (R PH) | 59 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.295 | 1 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 1 | 1 | 1 | 1 | 1 | 1 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295
2 | Failure (malop) of No1 Transformer DIFF Prot (W PH) | 59 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.295 | 1 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 1 | 1 | 1 | 1 | 1 | 1 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295
3 | Failure (malop) of No1 Transformer DIFF Prot (B PH) | 59 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.295 | 1 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 1 | 1 | 1 | 1 | 1 | 1 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295
4 | Failure (malop) of No1 Transformer HTOC Prot (R PH) | 51 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.295 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.21948 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499
5 | Failure (malop) of No1 Transformer HTOC Prot (W PH) | 51 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.295 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.21948 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499
6 | Failure (malop) of No1 Transformer HTOC Prot (B PH) | 51 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.295 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.21948 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499
7 | Failure (malop) of No2 and No3 Transformer HTOC Prot (R PH) | 51 | Electromechanical | No2 and No3 Bus Outage | 2 | 1.5 | 0.295 | 2 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.16329 | 0.17849 | 0.19328 | 0.20742 | 0.2207 | 0.23292 | 0.24397 | 0.25375 | 0.26224 | 0.26945 | 0.27546 | 0.28034 | 0.28423 | 0.28726 | 0.28956 | 0.29126 | 0.2925 | 0.29336 | 0.29396 | 0.29436 | 0.29461 | 0.29477 | 0.29487 | 0.29493 | 0.29496 | 0.29498
8 | Failure (malop) of No2 and No3 Transformer HTOC Prot (W PH) | 51 | Electromechanical | No2 and No3 Bus Outage | 2 | 1.5 | 0.295 | 2 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.16329 | 0.17849 | 0.19328 | 0.20742 | 0.2207 | 0.23292 | 0.24397 | 0.25375 | 0.26224 | 0.26945 | 0.27546 | 0.28034 | 0.28423 | 0.28726 | 0.28956 | 0.29126 | 0.2925 | 0.29336 | 0.29396 | 0.29436 | 0.29461 | 0.29477 | 0.29487 | 0.29493 | 0.29496 | 0.29498
9 | Failure (malop) of No2 and No3 Transformer HTOC Prot (B PH) | 51 | Electromechanical | No2 and No3 Bus Outage | 2 | 1.5 | 0.295 | 2 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.16329 | 0.17849 | 0.19328 | 0.20742 | 0.2207 | 0.23292 | 0.24397 | 0.25375 | 0.26224 | 0.26945 | 0.27546 | 0.28034 | 0.28423 | 0.28726 | 0.28956 | 0.29126 | 0.2925 | 0.29336 | 0.29396 | 0.29436 | 0.29461 | 0.29477 | 0.29487 | 0.29493 | 0.29496 | 0.29498
10 | Failure (malop) of No1 22kV Bus Protection (R Ph) | 51 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.295 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.21948 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499
11 | Failure (malop) of No1 22kV Bus Protection (W Ph) | 51 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.295 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.21948 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499
12 | Failure (malop) of No1 22kV Bus Protection (B Ph) | 51 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.295 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.21948 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499
13 | Failure (malop) of No1 22kV Bus Overload Protection (R Ph) | 51 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.186 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998 | 0.24999
14 | Failure (malop) of No1 22kV Bus Overload Protection (W Ph) | 51 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.186 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998 | 0.24999
15 | Failure (malop) of No1 22kV Bus Overload Protection (B Ph) | 51 | Electromechanical | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.186 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998 | 0.24999
16 | Failure (malop for FDR faut) of No2 22kV Bus Protection (R Ph) | 51 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.295 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.21948 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499
17 | Failure (malop for FDR faut) of No2 22kV Bus Protection (W Ph) | 51 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.295 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.21948 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499
18 | Failure (malop for FDR faut) of No2 22kV Bus Protection (B Ph) | 51 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.295 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.21948 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499
19 | Failure (malop for FDR faut) of No2 22kV Bus Overload Protection (R Ph) | 51 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.186 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998 | 0.24999
20 | Failure (malop for FDR fau) of No2 22kV Bus Overload Protection (W Ph) | 51 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.186 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998 | 0.24999
21 | Failure (malop for FDR fau) of No2 22kV Bus Overload Protection (B Ph) | 51 | Electromechanical | No2 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.186 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998 | 0.24999
22 | Failure (malop for FDR fau) of No3 22kV Bus Overload Protection (R Ph) | 51 | Electromechanical | No3 Bus Outage | 1 | 1.5 | 0.417 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.31025 | 0.32436 | 0.33754 | 0.34967 | 0.36068 | 0.37054 | 0.37922 | 0.38675 | 0.39316 | 0.39854 | 0.40295 | 0.40651 | 0.40932 | 0.41149 | 0.41314 | 0.41435 | 0.41523 | 0.41584 | 0.41626 | 0.41654 | 0.41673 | 0.41684 | 0.41691 | 0.41695 | 0.41697 | 0.41699
23 | Failure (malop for FDR fau) of No3 22kV Bus Overload Protection (W Ph) | 51 | Electromechanical | No3 Bus Outage | 1 | 1.5 | 0.417 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.31025 | 0.32436 | 0.33754 | 0.34967 | 0.36068 | 0.37054 | 0.37922 | 0.38675 | 0.39316 | 0.39854 | 0.40295 | 0.40651 | 0.40932 | 0.41149 | 0.41314 | 0.41435 | 0.41523 | 0.41584 | 0.41626 | 0.41654 | 0.41673 | 0.41684 | 0.41691 | 0.41695 | 0.41697 | 0.41699
24 | Failure (malop for FDR fau) of No3 22kV Bus Overload Protection (B Ph) | 51 | Electromechanical | No3 Bus Outage | 1 | 1.5 | 0.417 | 1 | 0.744 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.31025 | 0.32436 | 0.33754 | 0.34967 | 0.36068 | 0.37054 | 0.37922 | 0.38675 | 0.39316 | 0.39854 | 0.40295 | 0.40651 | 0.40932 | 0.41149 | 0.41314 | 0.41435 | 0.41523 | 0.41584 | 0.41626 | 0.41654 | 0.41673 | 0.41684 | 0.41691 | 0.41695 | 0.41697 | 0.41699
25 | Failure of CN01 feeder protection for a feeder fault | 32 | Digital | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
26 | Failure of CN02 feeder protection for a feeder fault | 32 | Digital | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
27 | Failure of CN03 feeder protection for a feeder fault | 32 | Digital | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
28 | Failure of CN04 feeder protection for a feeder fault | 32 | Digital | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
29 | Failure of CN05 feeder protection for a feeder fault | 32 | Digital | No2 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
30 | Failure of CN06 feeder protection for a feeder fault | 32 | Digital | No2 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
31 | Failure of CN07 feeder protection for a feeder fault | 32 | Digital | No2 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
32 | Failure of CN08 feeder protection for a feeder fault | 32 | Digital | No2 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
33 | Failure of CN09 feeder protection for a feeder fault | 32 | Digital | No3 Bus Outage | 1 | 1.5 | 0.5 | 1 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.4946 | 0.49593 | 0.49695 | 0.49774 | 0.49833 | 0.49878 | 0.49912 | 0.49936 | 0.49955 | 0.49968 | 0.49977 | 0.49984 | 0.49989 | 0.49993 | 0.49995 | 0.49997 | 0.49998 | 0.49998 | 0.49999 | 0.49999 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
34 | Failure of CN10 feeder protection for a feeder fault | 32 | Digital | No3 Bus Outage | 1 | 1.5 | 0.5 | 1 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.4946 | 0.49593 | 0.49695 | 0.49774 | 0.49833 | 0.49878 | 0.49912 | 0.49936 | 0.49955 | 0.49968 | 0.49977 | 0.49984 | 0.49989 | 0.49993 | 0.49995 | 0.49997 | 0.49998 | 0.49998 | 0.49999 | 0.49999 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
35 | Failure of CN11 feeder protection for a feeder fault | 15 | Digital | No3 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.63212 | 0.6802 | 0.7244 | 0.76452 | 0.80052 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.15803 | 0.17005 | 0.1811 | 0.19113 | 0.20013 | 0.20811 | 0.21511 | 0.22119 | 0.2264 | 0.23083 | 0.23456 | 0.23767 | 0.24023 | 0.24232 | 0.24401 | 0.24537 | 0.24645 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977
36 | Failure of MEF protection for a CN01 feeder fault | 15 | Analogue Electronic | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.015197 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.0037993 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866
37 | Failure of MEF protection for a CN02 feeder fault | 15 | Analogue Electronic | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.015197 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.0037993 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866
38 | Failure of MEF protection for a CN03 feeder fault | 15 | Analogue Electronic | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.015197 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.0037993 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866
39 | Failure of MEF protection for a CN04 feeder fault | 15 | Analogue Electronic | No1 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.015197 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.0037993 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866
40 | Failure of MEF protection for a CN05 feeder fault | 15 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.015197 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.0037993 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866
41 | Failure of MEF protection for a CN06 feeder fault | 15 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.015197 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.0037993 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866
42 | Failure of MEF protection for a CN07 feeder fault | 15 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.015197 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.0037993 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866
43 | Failure of MEF protection for a CN08 feeder fault | 15 | Analogue Electronic | No2 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.015197 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.0037993 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866
44 | Failure of MEF protection for a CN09 feeder fault | 15 | Analogue Electronic | No3 Bus Outage | 1 | 1.5 | 0.5 | 1 | 0.015197 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.0075986 | 0.010196 | 0.013413 | 0.017338 | 0.02206 | 0.027672 | 0.034262 | 0.041915 | 0.050711 | 0.060719 | 0.071993 | 0.084572 | 0.098476 | 0.1137 | 0.1302 | 0.14793 | 0.16679 | 0.18665 | 0.20735 | 0.22871 | 0.25051 | 0.2725 | 0.29444 | 0.31606 | 0.33711 | 0.35732
45 | Failure of MEF protection for a CN10 feeder fault | 15 | Analogue Electronic | No3 Bus Outage | 1 | 1.5 | 0.5 | 1 | 0.015197 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.0075986 | 0.010196 | 0.013413 | 0.017338 | 0.02206 | 0.027672 | 0.034262 | 0.041915 | 0.050711 | 0.060719 | 0.071993 | 0.084572 | 0.098476 | 0.1137 | 0.1302 | 0.14793 | 0.16679 | 0.18665 | 0.20735 | 0.22871 | 0.25051 | 0.2725 | 0.29444 | 0.31606 | 0.33711 | 0.35732
46 | Failure of MEF protection for a CN11 feeder fault | 15 | Analogue Electronic | No3 Bus Outage | 1 | 1.5 | 0.25 | 1 | 0.015197 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.0037993 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866
47 | Failure (malop) of BUEF protection | 34 | Analogue Electronic | Station Black | 3 | 1.5 | 0.501 | 1 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.93903 | 0.95323 | 0.96479 | 0.97401 | 0.98121 | 0.98671 | 0.99081 | 0.99379 | 0.99591 | 0.99737 | 0.99836 | 0.999 | 0.22917 | 0.25101 | 0.27304 | 0.29503 | 0.31669 | 0.33778 | 0.35804 | 0.37724 | 0.39518 | 0.41171 | 0.42669 | 0.44005 | 0.45178 | 0.46189 | 0.47045 | 0.47757 | 0.48336 | 0.48798 | 0.49159 | 0.49434 | 0.49639 | 0.49789 | 0.49895 | 0.49968 | 0.50018 | 0.5005
Total

## Fault Data CN CS NH (hidden)
Outage CASE Number | Customer SubGroup | ZSS | Feeder | Bus | Date Out | Time Out | Date On | Time On | Duration | Customers Effected
J.25.0121485 | 1 | CS | CS No2 TRANSFORMER |  | 2025-07-25 | 14:46:17 | 2025-07-25 | 14:51:42 | 5.4167 | 13269
J.25.0121485 | 2 | CS | CS No2 TRANSFORMER |  | 2025-07-25 | 14:46:17 | 2025-07-25 | 14:52:59 | 6.7 | 6713
J.24.0098206 | 1 | NH | NH 02 | No1 Bus | 2024-06-01 | 9:09 | 2024-06-01 | 9:10 | 0.86667 | 4446
J.24.0097978 | 1 | NH | NH 02 | No1 Bus | 2024-05-28 | 18:55 | 2024-05-28 | 18:56 | 0.26667 | 4447
J.21.0036628 | 3 | NH | NH 02 | No1 Bus | 2021-01-22 | 22:31 | 2021-01-22 | 23:08 | 36.95 | 72
J.21.0036628 | 4 | NH | NH 02 | No1 Bus | 2021-01-22 | 22:31 | 2021-01-22 | 23:10 | 38.5833 | 2459
J.21.0036628 | 2 | NH | NH 02 | No1 Bus | 2021-01-22 | 22:31 | 2021-01-22 | 22:54 | 22.2333 | 1799
J.24.0098206 | 2 | NH | NH 03 | No1 Bus | 2024-06-01 | 9:09 | 2024-06-01 | 9:10 | 0.86667 | 264
J.24.0097978 | 2 | NH | NH 03 | No1 Bus | 2024-05-28 | 18:55 | 2024-05-28 | 18:56 | 0.26667 | 264
J.24.0098206 | 3 | NH | NH 05 | No1 Bus | 2024-06-01 | 9:09 | 2024-06-01 | 9:10 | 0.86667 | 779
J.24.0097978 | 3 | NH | NH 05 | No1 Bus | 2024-05-28 | 18:55 | 2024-05-28 | 18:56 | 0.26667 | 779
J.21.0036628 | 1 | NH | NH 05 | No1 Bus | 2021-01-22 | 22:31 | 2021-01-22 | 22:46 | 14.7833 | 3764
J.24.0098206 | 4 | NH | NH 08 | No2 Bus | 2024-06-01 | 9:09 | 2024-06-01 | 9:10 | 0.86667 | 2441
J.24.0097978 | 4 | NH | NH 08 | No2 Bus | 2024-05-28 | 18:55 | 2024-05-28 | 18:56 | 0.26667 | 2440
J.24.0098206 | 5 | NH | NH 09 | No2 Bus | 2024-06-01 | 9:09 | 2024-06-01 | 9:10 | 0.86667 | 302
J.24.0097978 | 5 | NH | NH 09 | No2 Bus | 2024-05-28 | 18:55 | 2024-05-28 | 18:56 | 0.26667 | 302
J.24.0098206 | 6 | NH | NH 12 | No2 Bus | 2024-06-01 | 9:09 | 2024-06-01 | 9:10 | 0.86667 | 18
J.24.0097978 | 6 | NH | NH 12 | No2 Bus | 2024-05-28 | 18:55 | 2024-05-28 | 18:56 | 0.26667 | 18
J.24.0098206 | 7 | NH | NH 13 | No2 Bus | 2024-06-01 | 9:09 | 2024-06-01 | 9:10 | 0.86667 | 1
J.24.0097978 | 7 | NH | NH 13 | No2 Bus | 2024-05-28 | 18:55 | 2024-05-28 | 18:56 | 0.26667 | 1
J.24.0098206 | 8 | NH | NH 16 | No3 Bus | 2024-06-01 | 9:09 | 2024-06-01 | 9:10 | 0.86667 | 2910
J.24.0097978 | 8 | NH | NH 16 | No3 Bus | 2024-05-28 | 18:55 | 2024-05-28 | 18:56 | 0.26667 | 2910
J.24.0094260 | 1 | CN | CN 09 | No3 Bus | 2024-03-15 | 18:28 | 2024-03-15 | 18:59 | 31.15 | 70
J.24.0094260 | 2 | CN | CN 10 | No3 Bus | 2024-03-15 | 18:28 | 2024-03-15 | 18:59 | 31.3667 | 2068
J.24.0094260 | 3 | CN | CN 11 | No3 Bus | 2024-03-15 | 18:28 | 2024-03-15 | 18:34 | 5.7333 | 4634
J.23.0085582 | 2 | CN | CN 06 | No2 Bus | 2023-10-01 | 14:48 | 2023-10-01 | 14:48 | 0.033333 | 2300
J.23.0085582 | 3 | CN | CN 07 | No2 Bus | 2023-10-01 | 14:48 | 2023-10-01 | 14:48 | 0.033333 | 2900
J.23.0085582 | 4 | CN | CN 08 | No2 Bus | 2023-10-01 | 14:48 | 2023-10-01 | 14:48 | 0.033333 | 2646
J.23.0085580 | 1 | CN | CN 10 | No3 Bus | 2023-10-01 | 14:48 | 2023-10-01 | 15:11 | 23.05 | 2070
J.23.0085580 | 2 | CN | CN 09 | No3 Bus | 2023-10-01 | 14:48 | 2023-10-01 | 15:11 | 23.2333 | 70
J.23.0085582 | 1 | CN | CN 05 | No2 Bus | 2023-10-01 | 14:48 | 2023-10-01 | 14:48 | 0.033333 | 4438
J.21.0047703 | 1 | CS | CS 03 |  | 2021-09-22 | 9:17 | 2021-09-22 | 9:44 | 27.1667 | 2434
J.21.0047703 | 2 | CS | CS 02 |  | 2021-09-22 | 9:17 | 2021-09-22 | 9:47 | 30.2333 | 5861
J.21.0047703 | 3 | CS | CS 08 |  | 2021-09-22 | 9:17 | 2021-09-22 | 9:53 | 36.5833 | 2234
J.21.0047703 | 4 | CS | CS 05 |  | 2021-09-22 | 9:17 | 2021-09-22 | 10:02 | 45 | 4988
J.21.0047703 | 5 | CS | CS 09 |  | 2021-09-22 | 9:17 | 2021-09-22 | 10:02 | 45 | 1964
J.21.0047703 | 6 | CS | CS 12 |  | 2021-09-22 | 9:17 | 2021-09-22 | 10:02 | 45 | 2188
J.21.0047703 | 7 | CS | CS 13 |  | 2021-09-22 | 9:17 | 2021-09-22 | 10:02 | 45 | 1965
J.21.0047704 | 1 | CN | CN 01 | No1 Bus | 2021-09-22 | 9:17 | 2021-09-22 | 9:17 | 0.033333 | 98
J.21.0047704 | 2 | CN | CN 02 | No1 Bus | 2021-09-22 | 9:17 | 2021-09-22 | 9:17 | 0.033333 | 517
J.21.0047704 | 3 | CN | CN 03 | No1 Bus | 2021-09-22 | 9:17 | 2021-09-22 | 9:17 | 0.033333 | 1322
J.21.0047704 | 4 | CN | CN 04 | No1 Bus | 2021-09-22 | 9:17 | 2021-09-22 | 9:17 | 0.033333 | 1521
202328 | 1 | NH | NH 16 | No3 Bus | 2020-09-18 | 16:46 | 2020-09-18 | 17:13 | 27.15 | 2703
J.24.0098206 | 9 | NH | NH 17 | No3 Bus | 2024-06-01 | 9:09 | 2024-06-01 | 9:10 | 0.86667 | 2575
J.24.0097978 | 9 | NH | NH 17 | No3 Bus | 2024-05-28 | 18:55 | 2024-05-28 | 18:56 | 0.26667 | 2575
202328 | 2 | NH | NH 17 | No3 Bus | 2020-09-18 | 16:46 | 2020-09-18 | 16:46 | 0.15 | 8
202328 | 3 | NH | NH 17 | No3 Bus | 2020-09-18 | 16:46 | 2020-09-18 | 17:35 | 49.2833 | 2972
J.24.0098206 | 10 | NH | NH 20 | No3 Bus | 2024-06-01 | 9:09 | 2024-06-01 | 9:10 | 0.86667 | 2227
J.24.0097978 | 10 | NH | NH 20 | No3 Bus | 2024-05-28 | 18:55 | 2024-05-28 | 18:56 | 0.26667 | 2231
202328 | 4 | NH | NH 20 | No3 Bus | 2020-09-18 | 16:46 | 2020-09-18 | 17:45 | 59.2167 | 2085
[11 empty] | ZSS | No of FDRs | Number of Year | Number of Fault | Prob of Fault / Year
[11 empty] | CN | 11 | 4 | 13 | 0.29545
[11 empty] | CN Bus 1 | 4 | 4 | 4 | 0.25
[11 empty] | CN Bus 2 | 4 | 4 | 4 | 0.25
[11 empty] | CN Bus 3 | 3 | 4 | 5 | 0.41667
[11 empty] | CN1 | 1 | 4 | 1 | 0.25
[11 empty] | CN2 | 1 | 4 | 1 | 0.25
[11 empty] | CN3 | 1 | 4 | 1 | 0.25
[11 empty] | CN4 | 1 | 4 | 1 | 0.25
[11 empty] | CN5 | 1 | 4 | 1 | 0.25
[11 empty] | CN6 | 1 | 4 | 1 | 0.25
[11 empty] | CN7 | 1 | 4 | 1 | 0.25
[11 empty] | CN8 | 1 | 4 | 1 | 0.25
[11 empty] | CN9 | 1 | 4 | 2 | 0.5
[11 empty] | CN10 | 1 | 4 | 2 | 0.5
[11 empty] | CN11 | 1 | 4 | 1 | 0.25
[11 empty] | ZSS | No of FDRs | Number of Year | Number of Fault | Prob of Fault / Year
[11 empty] | CS | 7 | 4 | 8 | 0.28571
[11 empty] | CS Bus 1 | 3 | 4 | 3 | 0.25
[11 empty] | CS Bus 2 | 4 | 4 | 5 | 0.3125
[11 empty] | CS2 | 1 | 4 | 1 | 0.25
[11 empty] | CS3 | 1 | 4 | 1 | 0.25
[11 empty] | CS5 | 1 | 4 | 1 | 0.25
[11 empty] | CS8 | 1 | 4 | 1 | 0.25
[11 empty] | CS9 | 1 | 4 | 1 | 0.25
[11 empty] | CS12 | 1 | 4 | 1 | 0.25
[11 empty] | CS13 | 1 | 4 | 1 | 0.25
[11 empty] | ZSS | No of FDRs | Number of Year | Number of Fault | Prob of Fault / Year
[11 empty] | NH | 10 | 5 | 28 | 0.56
[11 empty] | NH Bus 1 | 3 | 5 | 10 | 0.66667
[11 empty] | NH Bus 2 | 4 | 5 | 8 | 0.4
[11 empty] | NH Bus 3 | 3 | 5 | 10 | 0.66667
[11 empty] | NH2 | 1 | 5 | 5 | 1
[11 empty] | NH3 | 1 | 5 | 2 | 0.4
[11 empty] | NH5 | 1 | 5 | 3 | 0.6
[11 empty] | NH8 | 1 | 5 | 2 | 0.4
[11 empty] | NH9 | 1 | 5 | 2 | 0.4
[11 empty] | NH12 | 1 | 5 | 2 | 0.4
[11 empty] | NH13 | 1 | 5 | 2 | 0.4
[11 empty] | NH16 | 1 | 5 | 3 | 0.6
[11 empty] | NH17 | 1 | 5 | 4 | 0.8
[11 empty] | NH20 | 1 | 5 | 3 | 0.6

## Customer Numbers (hidden)
NMI Count
HV Feeder¦Premise Type | Commercial | Industrial | Residential | NCONUML | Residential2 | Not assigned
CN0-001 | 58 | 4 | 56 | 4 | 52
CN0-002 | 327 | 20 | 279 | 4 | 275
CN0-003 | 54 | 1 | 1313 | 7 | 1306
CN0-004 | 285 | 32 | 1979 | 20 | 1959
CN0-005 | 412 | 13 | 4138 | 23 | 4115
CN0-006 | 107 | 4 | 1632 | 5 | 1627
CN0-007 | 151 | 3 | 2779 | 20 | 2759
CN0-008 | 246 | 10 | 2705 | 23 | 2682
CN0-009 | 67 | 5 | 0
CN0-010 | 84 | 4 | 2020 | 3 | 2017
CN0-011 | 317 | 20 | 4259 | 44 | 4215
CS0-002 | 186 | 4 | 5795 | 30 | 5765
CS0-003 | 305 | 5 | 1945 | 36 | 1909 | 1
CS0-005 | 254 | 10 | 4863 | 47 | 4816
CS0-008 | 226 | 3 | 2066 | 37 | 2029
CS0-009 | 143 | 1 | 1819 | 15 | 1804
CS0-012 | 340 | 6 | 1877 | 12 | 1865
CS0-013 | 204 | 2 | 1803 | 36 | 1767 | 1
NH0-002 | 113 | 2 | 4285 | 23 | 4262
NH0-003 | 8 |  | 255 |  | 255
NH0-005 | 40 |  | 777 | 3 | 774
NH0-008 | 36 |  | 2457 | 5 | 2452
NH0-009 | 14 | 4 | 289 | 3 | 286
NH0-012 | 11 | 1 | 0
NH0-013 |  | 1 | 0
NH0-016 | 72 |  | 2940 | 20 | 2920
NH0-017 | 253 | 7 | 2440 | 22 | 2418
NH0-020 | 113 |  | 2150 | 14 | 2136

## Notes (hidden)
http://www.eaes-seari.com/Jwk_dqynxgljs/EN/10.16628/j.cnki.2095-8188.2022.11.011

## Restoration Time (hidden)
Asset Type | Failure Scenario | Average Duration | Comments
Primary | CB failure leading to bus failure (only applicable to switchgear) | 1.5 hrs | Approximately 1 hr to restore supply to most customers (i.e 70%).
|  | Days/Weeks | Remaining ~x% may experience prolonged outage (days or weeks) due to limited transfer capacity from adjacent ZSS.
Primary | CB failure causing a bus outage | 1.5 hrs | Average 30 min response time for HV Operator/Tester.
Restoration delayed by condition assessment of ageing equipment and old drawings.
Isolation of failed circuit required before restoration can begin.
Secondary | Bus outage due to protection maloperation | 1.5 hrs | Average 30 min response time for HV Operator/Tester.
Condition assessment and isolation of failed circuit required.
Feeder patrol to confirm fault location outside ZSS using Fault indicators.
Tester to interrogate feeder and bus protection to confirm maloperation prior to restoration.

## Weibull Data
User Input Cell
Weibull Curve Profile | ErgonE-AN |  |  | Vendor | Original | ErgonE-DI | ErgonE-AN | ErgonE-ElecM | VenX-ModA | VenX-ModB | VenX-ModC | VenX-ModD | VenX-ModE | VenY-ModC | VenZ-ModA | VenZ-ModB | VenZ-ModC
Beta (β) | 4.3 |  |  | Beta (β) | 1.681 | 1.9 | 4.3 | 5 | 2.5126 | 2.5642 | 2.9954 | 4.9533 | 7.2322 | 2.2715 | 1.8462 | 1.9263 | 2.3065
Eta (η) | 37 |  |  | Eta (η) | 19.99 | 14 | 37 | 47 | 28.6766 | 23.0924 | 26.3703 | 22.1097 | 24.0032 | 32.6647 | 16.7257 | 22.0107 | 24.0321
Relay Average Age | 20 | 0.068523
Time (years) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90
Probability Density Function (PDF) | 0 | 7.7661e-07 | 7.6489e-06 | 2.9154e-05 | 7.533e-05 | 0.0001573 | 0.00028703 | 0.00047719 | 0.00074097 | 0.001092 | 0.001544 | 0.0021108 | 0.0028059 | 0.0036423 | 0.004632 | 0.0057857 | 0.0071119 | 0.008617 | 0.010304 | 0.012172 | 0.014216 | 0.016425 | 0.018782 | 0.021266 | 0.023844 | 0.026481 | 0.029131 | 0.031744 | 0.034262 | 0.036624 | 0.038766 | 0.040621 | 0.042128 | 0.043227 | 0.04387 | 0.044019 | 0.043649 | 0.042754 | 0.041345 | 0.039454 | 0.037131 | 0.034443 | 0.031471 | 0.028306 | 0.025045 | 0.021782 | 0.018609 | 0.015604 | 0.012832 | 0.01034 | 0.0081581 | 0.0062961 | 0.0047488 | 0.0034972 | 0.0025122 | 0.0017586 | 0.0011984 | 0.00079412 | 0.00051118 | 0.00031928 | 0.00019329 | 0.00011328 | 6.4191e-05 | 3.513e-05 | 1.8545e-05 | 9.4303e-06 | 4.6136e-06 | 2.1687e-06 | 9.7809e-07 | 4.2268e-07 | 1.7477e-07 | 6.9041e-08 | 2.6021e-08 | 9.3419e-09 | 3.1901e-09 | 1.0345e-09 | 3.1808e-10 | 9.2583e-11 | 2.5468e-11 | 6.6099e-12 | 1.6158e-12 | 3.7141e-13 | 8.0131e-14 | 1.6198e-14 | 3.0623e-15 | 5.4046e-16 | 8.8875e-17 | 1.3592e-17 | 1.9295e-18 | 2.5373e-19 | 3.0849e-20
Cumulative Failure Probability (CDF) | 0 | 1.8061e-07 | 3.5576e-06 | 2.034e-05 | 7.0077e-05 | 0.00018292 | 0.00040059 | 0.00077712 | 0.0013795 | 0.0022881 | 0.0035971 | 0.0054143 | 0.0078614 | 0.011073 | 0.015197 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.93903 | 0.95323 | 0.96479 | 0.97401 | 0.98121 | 0.98671 | 0.99081 | 0.99379 | 0.99591 | 0.99737 | 0.99836 | 0.999 | 0.99941 | 0.99966 | 0.99981 | 0.9999 | 0.99995 | 0.99997 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Reliability Function R(t) | 1 | 1 | 1 | 0.99998 | 0.99993 | 0.99982 | 0.9996 | 0.99922 | 0.99862 | 0.99771 | 0.9964 | 0.99459 | 0.99214 | 0.98893 | 0.9848 | 0.97961 | 0.97317 | 0.96532 | 0.95588 | 0.94466 | 0.93148 | 0.91617 | 0.89858 | 0.87856 | 0.85601 | 0.83086 | 0.80305 | 0.77261 | 0.73959 | 0.70413 | 0.66642 | 0.6267 | 0.58529 | 0.54258 | 0.49899 | 0.455 | 0.41112 | 0.36788 | 0.32579 | 0.28535 | 0.24702 | 0.21121 | 0.17823 | 0.14833 | 0.12165 | 0.098243 | 0.078058 | 0.060969 | 0.046773 | 0.035211 | 0.025989 | 0.018788 | 0.013292 | 0.009192 | 0.0062081 | 0.0040904 | 0.0026265 | 0.0016417 | 0.00099784 | 0.00058907 | 0.00033736 | 0.00018722 | 0.00010055 | 5.2199e-05 | 2.6159e-05 | 1.2639e-05 | 5.8796e-06 | 2.6299e-06 | 1.1295e-06 | 4.6516e-07 | 1.8342e-07 | 6.9144e-08 | 2.4884e-08 | 8.5363e-09 | 2.787e-09 | 8.6462e-10 | 2.5448e-10 | 7.0943e-11 | 1.8702e-11 | 4.654e-12 | 1.0914e-12 | 2.408e-13 | 4.989e-14 | 9.6896e-15 | 1.7609e-15 | 2.9887e-16 | 4.7286e-17 | 6.961e-18 | 9.5157e-19 | 1.2055e-19 | 1.4127e-20

## CN Relay Failure Scenarios-Old (hidden)
CN Relay Failure Scenarios
VCR | 44.96 | ($k/MWh)
Energy At Risk | To keep the calculation simple, energy at risk is assumed to be constant for the 20 year period using 2026 Energy from 2024 DAPR Also PF is assumed to be unity (1).
[9 empty] | Asset PoF (Ergon Weibull Paper) | [24 empty] | Scenario (LoC - Likelihood of Consequence) | [25 empty] | Annual Asset Risk Cost ($k) - Reliability & Security { Annual Asset Risk = PoF * Asset No * Loc * CoC} OLD
Item | Scenarios | Asset Age @ year 2026 | Asset Type | Asset Type Failure | Consequence | Consequence Duration (Hr) | Probability of Fault | Power of Factor | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Energy at Risk @ 2026 (MVA) CoC - Consequence of Cost of Failure Event | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | Failure (malop) of No1 Transformer DIFF Prot (R PH) | 59 | Electromechanical | Secondary | No1 Bus Outage | 0.33333 | 0.295 | 1 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 1 | 1 | 1 | 1 | 1 | 1 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 20.9667 | 88.5906 | 89.572 | 90.3632 | 90.988 | 91.4711 | 91.8364 | 92.1063 | 92.3009 | 92.4377 | 92.5314 | 92.5938 | 92.6342 | 92.6595 | 92.6749 | 92.684 | 92.6892 | 92.6921 | 92.6936 | 92.6943 | 92.6947 | 92.6949 | 92.695 | 92.695 | 92.695 | 92.695
2 | Failure (malop) of No1 Transformer DIFF Prot (W PH) | 59 | Electromechanical | Secondary | No1 Bus Outage | 0.33333 | 0.295 | 1 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 1 | 1 | 1 | 1 | 1 | 1 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 20.9667 | 88.5906 | 89.572 | 90.3632 | 90.988 | 91.4711 | 91.8364 | 92.1063 | 92.3009 | 92.4377 | 92.5314 | 92.5938 | 92.6342 | 92.6595 | 92.6749 | 92.684 | 92.6892 | 92.6921 | 92.6936 | 92.6943 | 92.6947 | 92.6949 | 92.695 | 92.695 | 92.695 | 92.695
3 | Failure (malop) of No1 Transformer DIFF Prot (B PH) | 59 | Electromechanical | Secondary | No1 Bus Outage | 0.33333 | 0.295 | 1 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.99998 | 0.99999 | 1 | 1 | 1 | 1 | 1 | 1 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 0.295 | 20.9667 | 88.5906 | 89.572 | 90.3632 | 90.988 | 91.4711 | 91.8364 | 92.1063 | 92.3009 | 92.4377 | 92.5314 | 92.5938 | 92.6342 | 92.6595 | 92.6749 | 92.684 | 92.6892 | 92.6921 | 92.6936 | 92.6943 | 92.6947 | 92.6949 | 92.695 | 92.695 | 92.695 | 92.695
4 | Failure (malop) of No1 Transformer HTOC Prot (R PH) | 51 | Electromechanical | Secondary | No1 Bus Outage | 0.33333 | 0.295 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 20.9667 | 72.1027 | 75.031 | 77.7275 | 80.1761 | 82.3669 | 84.2971 | 85.9703 | 87.3964 | 88.5906 | 89.572 | 90.3632 | 90.988 | 91.4711 | 91.8364 | 92.1063 | 92.3009 | 92.4377 | 92.5314 | 92.5938 | 92.6342 | 92.6595 | 92.6749 | 92.684 | 92.6892 | 92.6921
5 | Failure (malop) of No1 Transformer HTOC Prot (W PH) | 51 | Electromechanical | Secondary | No1 Bus Outage | 0.33333 | 0.295 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 20.9667 | 72.1027 | 75.031 | 77.7275 | 80.1761 | 82.3669 | 84.2971 | 85.9703 | 87.3964 | 88.5906 | 89.572 | 90.3632 | 90.988 | 91.4711 | 91.8364 | 92.1063 | 92.3009 | 92.4377 | 92.5314 | 92.5938 | 92.6342 | 92.6595 | 92.6749 | 92.684 | 92.6892 | 92.6921
6 | Failure (malop) of No1 Transformer HTOC Prot (B PH) | 51 | Electromechanical | Secondary | No1 Bus Outage | 0.33333 | 0.295 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 20.9667 | 72.1027 | 75.031 | 77.7275 | 80.1761 | 82.3669 | 84.2971 | 85.9703 | 87.3964 | 88.5906 | 89.572 | 90.3632 | 90.988 | 91.4711 | 91.8364 | 92.1063 | 92.3009 | 92.4377 | 92.5314 | 92.5938 | 92.6342 | 92.6595 | 92.6749 | 92.684 | 92.6892 | 92.6921
7 | Failure (malop) of No2 and No3 Transformer HTOC Prot (R PH) | 51 | Electromechanical | Secondary | No2 and No3 Bus Outage | 0.33333 | 0.295 | 2 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.17849 | 0.19328 | 0.20742 | 0.2207 | 0.23292 | 0.24397 | 0.25375 | 0.26224 | 0.26945 | 0.27546 | 0.28034 | 0.28423 | 0.28726 | 0.28956 | 0.29126 | 0.2925 | 0.29336 | 0.29396 | 0.29436 | 0.29461 | 0.29477 | 0.29487 | 0.29493 | 0.29496 | 0.29498 | 41.9333 | 112.1698 | 121.4659 | 130.3537 | 138.6958 | 146.379 | 153.3198 | 159.4669 | 164.8015 | 169.3358 | 173.1085 | 176.1799 | 178.6248 | 180.5267 | 181.9716 | 183.0427 | 183.817 | 184.3623 | 184.7361 | 184.9853 | 185.1466 | 185.248 | 185.3097 | 185.3461 | 185.3668 | 185.3782
8 | Failure (malop) of No2 and No3 Transformer HTOC Prot (W PH) | 51 | Electromechanical | Secondary | No2 and No3 Bus Outage | 0.33333 | 0.295 | 2 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.17849 | 0.19328 | 0.20742 | 0.2207 | 0.23292 | 0.24397 | 0.25375 | 0.26224 | 0.26945 | 0.27546 | 0.28034 | 0.28423 | 0.28726 | 0.28956 | 0.29126 | 0.2925 | 0.29336 | 0.29396 | 0.29436 | 0.29461 | 0.29477 | 0.29487 | 0.29493 | 0.29496 | 0.29498 | 41.9333 | 112.1698 | 121.4659 | 130.3537 | 138.6958 | 146.379 | 153.3198 | 159.4669 | 164.8015 | 169.3358 | 173.1085 | 176.1799 | 178.6248 | 180.5267 | 181.9716 | 183.0427 | 183.817 | 184.3623 | 184.7361 | 184.9853 | 185.1466 | 185.248 | 185.3097 | 185.3461 | 185.3668 | 185.3782
9 | Failure (malop) of No2 and No3 Transformer HTOC Prot (B PH) | 51 | Electromechanical | Secondary | No2 and No3 Bus Outage | 0.33333 | 0.295 | 2 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.17849 | 0.19328 | 0.20742 | 0.2207 | 0.23292 | 0.24397 | 0.25375 | 0.26224 | 0.26945 | 0.27546 | 0.28034 | 0.28423 | 0.28726 | 0.28956 | 0.29126 | 0.2925 | 0.29336 | 0.29396 | 0.29436 | 0.29461 | 0.29477 | 0.29487 | 0.29493 | 0.29496 | 0.29498 | 41.9333 | 112.1698 | 121.4659 | 130.3537 | 138.6958 | 146.379 | 153.3198 | 159.4669 | 164.8015 | 169.3358 | 173.1085 | 176.1799 | 178.6248 | 180.5267 | 181.9716 | 183.0427 | 183.817 | 184.3623 | 184.7361 | 184.9853 | 185.1466 | 185.248 | 185.3097 | 185.3461 | 185.3668 | 185.3782
10 | Failure (malop) of No1 22kV Bus Protection (R Ph) | 51 | Electromechanical | Secondary | No1 Bus Outage | 0.33333 | 0.295 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 20.9667 | 72.1027 | 75.031 | 77.7275 | 80.1761 | 82.3669 | 84.2971 | 85.9703 | 87.3964 | 88.5906 | 89.572 | 90.3632 | 90.988 | 91.4711 | 91.8364 | 92.1063 | 92.3009 | 92.4377 | 92.5314 | 92.5938 | 92.6342 | 92.6595 | 92.6749 | 92.684 | 92.6892 | 92.6921
11 | Failure (malop) of No1 22kV Bus Protection (W Ph) | 51 | Electromechanical | Secondary | No1 Bus Outage | 0.33333 | 0.295 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 20.9667 | 72.1027 | 75.031 | 77.7275 | 80.1761 | 82.3669 | 84.2971 | 85.9703 | 87.3964 | 88.5906 | 89.572 | 90.3632 | 90.988 | 91.4711 | 91.8364 | 92.1063 | 92.3009 | 92.4377 | 92.5314 | 92.5938 | 92.6342 | 92.6595 | 92.6749 | 92.684 | 92.6892 | 92.6921
12 | Failure (malop) of No1 22kV Bus Protection (B Ph) | 51 | Electromechanical | Secondary | No1 Bus Outage | 0.33333 | 0.295 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 20.9667 | 72.1027 | 75.031 | 77.7275 | 80.1761 | 82.3669 | 84.2971 | 85.9703 | 87.3964 | 88.5906 | 89.572 | 90.3632 | 90.988 | 91.4711 | 91.8364 | 92.1063 | 92.3009 | 92.4377 | 92.5314 | 92.5938 | 92.6342 | 92.6595 | 92.6749 | 92.684 | 92.6892 | 92.6921
13 | Failure (malop) of No1 22kV Bus Overload Protection (R Ph) | 51 | Electromechanical | Secondary | No1 Bus Outage | 0.33333 | 0.25 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998 | 0.24999 | 20.9667 | 61.1039 | 63.5856 | 65.8708 | 67.9458 | 69.8024 | 71.4382 | 72.8562 | 74.0648 | 75.0768 | 75.9085 | 76.579 | 77.1085 | 77.5179 | 77.8275 | 78.0562 | 78.2211 | 78.3371 | 78.4164 | 78.4693 | 78.5035 | 78.525 | 78.5381 | 78.5458 | 78.5502 | 78.5526
14 | Failure (malop) of No1 22kV Bus Overload Protection (W Ph) | 51 | Electromechanical | Secondary | No1 Bus Outage | 0.33333 | 0.25 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998 | 0.24999 | 20.9667 | 61.1039 | 63.5856 | 65.8708 | 67.9458 | 69.8024 | 71.4382 | 72.8562 | 74.0648 | 75.0768 | 75.9085 | 76.579 | 77.1085 | 77.5179 | 77.8275 | 78.0562 | 78.2211 | 78.3371 | 78.4164 | 78.4693 | 78.5035 | 78.525 | 78.5381 | 78.5458 | 78.5502 | 78.5526
15 | Failure (malop) of No1 22kV Bus Overload Protection (B Ph) | 51 | Electromechanical | Secondary | No1 Bus Outage | 0.33333 | 0.25 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998 | 0.24999 | 20.9667 | 61.1039 | 63.5856 | 65.8708 | 67.9458 | 69.8024 | 71.4382 | 72.8562 | 74.0648 | 75.0768 | 75.9085 | 76.579 | 77.1085 | 77.5179 | 77.8275 | 78.0562 | 78.2211 | 78.3371 | 78.4164 | 78.4693 | 78.5035 | 78.525 | 78.5381 | 78.5458 | 78.5502 | 78.5526
16 | Failure (malop for FDR faut) of No2 22kV Bus Protection (R Ph) | 51 | Electromechanical | Secondary | No2 Bus Outage | 0.33333 | 0.295 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 20.9667 | 72.1027 | 75.031 | 77.7275 | 80.1761 | 82.3669 | 84.2971 | 85.9703 | 87.3964 | 88.5906 | 89.572 | 90.3632 | 90.988 | 91.4711 | 91.8364 | 92.1063 | 92.3009 | 92.4377 | 92.5314 | 92.5938 | 92.6342 | 92.6595 | 92.6749 | 92.684 | 92.6892 | 92.6921
17 | Failure (malop for FDR faut) of No2 22kV Bus Protection (W Ph) | 51 | Electromechanical | Secondary | No2 Bus Outage | 0.33333 | 0.295 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 20.9667 | 72.1027 | 75.031 | 77.7275 | 80.1761 | 82.3669 | 84.2971 | 85.9703 | 87.3964 | 88.5906 | 89.572 | 90.3632 | 90.988 | 91.4711 | 91.8364 | 92.1063 | 92.3009 | 92.4377 | 92.5314 | 92.5938 | 92.6342 | 92.6595 | 92.6749 | 92.684 | 92.6892 | 92.6921
18 | Failure (malop for FDR faut) of No2 22kV Bus Protection (B Ph) | 51 | Electromechanical | Secondary | No2 Bus Outage | 0.33333 | 0.295 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.22947 | 0.23878 | 0.24737 | 0.25516 | 0.26213 | 0.26827 | 0.2736 | 0.27814 | 0.28194 | 0.28506 | 0.28758 | 0.28957 | 0.2911 | 0.29227 | 0.29313 | 0.29375 | 0.29418 | 0.29448 | 0.29468 | 0.29481 | 0.29489 | 0.29494 | 0.29496 | 0.29498 | 0.29499 | 20.9667 | 72.1027 | 75.031 | 77.7275 | 80.1761 | 82.3669 | 84.2971 | 85.9703 | 87.3964 | 88.5906 | 89.572 | 90.3632 | 90.988 | 91.4711 | 91.8364 | 92.1063 | 92.3009 | 92.4377 | 92.5314 | 92.5938 | 92.6342 | 92.6595 | 92.6749 | 92.684 | 92.6892 | 92.6921
19 | Failure (malop for FDR faut) of No2 22kV Bus Overload Protection (R Ph) | 51 | Electromechanical | Secondary | No2 Bus Outage | 0.33333 | 0.25 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998 | 0.24999 | 20.9667 | 61.1039 | 63.5856 | 65.8708 | 67.9458 | 69.8024 | 71.4382 | 72.8562 | 74.0648 | 75.0768 | 75.9085 | 76.579 | 77.1085 | 77.5179 | 77.8275 | 78.0562 | 78.2211 | 78.3371 | 78.4164 | 78.4693 | 78.5035 | 78.525 | 78.5381 | 78.5458 | 78.5502 | 78.5526
20 | Failure (malop for FDR fau) of No2 22kV Bus Overload Protection (W Ph) | 51 | Electromechanical | Secondary | No2 Bus Outage | 0.33333 | 0.25 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998 | 0.24999 | 20.9667 | 61.1039 | 63.5856 | 65.8708 | 67.9458 | 69.8024 | 71.4382 | 72.8562 | 74.0648 | 75.0768 | 75.9085 | 76.579 | 77.1085 | 77.5179 | 77.8275 | 78.0562 | 78.2211 | 78.3371 | 78.4164 | 78.4693 | 78.5035 | 78.525 | 78.5381 | 78.5458 | 78.5502 | 78.5526
21 | Failure (malop for FDR fau) of No2 22kV Bus Overload Protection (B Ph) | 51 | Electromechanical | Secondary | No2 Bus Outage | 0.33333 | 0.25 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.19446 | 0.20236 | 0.20963 | 0.21624 | 0.22214 | 0.22735 | 0.23186 | 0.23571 | 0.23893 | 0.24158 | 0.24371 | 0.2454 | 0.2467 | 0.24768 | 0.24841 | 0.24894 | 0.24931 | 0.24956 | 0.24973 | 0.24984 | 0.2499 | 0.24995 | 0.24997 | 0.24998 | 0.24999 | 20.9667 | 61.1039 | 63.5856 | 65.8708 | 67.9458 | 69.8024 | 71.4382 | 72.8562 | 74.0648 | 75.0768 | 75.9085 | 76.579 | 77.1085 | 77.5179 | 77.8275 | 78.0562 | 78.2211 | 78.3371 | 78.4164 | 78.4693 | 78.5035 | 78.525 | 78.5381 | 78.5458 | 78.5502 | 78.5526
22 | Failure (malop for FDR fau) of No3 22kV Bus Overload Protection (R Ph) | 51 | Electromechanical | Secondary | No3 Bus Outage | 0.33333 | 0.417 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.32436 | 0.33754 | 0.34967 | 0.36068 | 0.37054 | 0.37922 | 0.38675 | 0.39316 | 0.39854 | 0.40295 | 0.40651 | 0.40932 | 0.41149 | 0.41314 | 0.41435 | 0.41523 | 0.41584 | 0.41626 | 0.41654 | 0.41673 | 0.41684 | 0.41691 | 0.41695 | 0.41697 | 0.41699 | 20.9667 | 101.9214 | 106.0607 | 109.8725 | 113.3336 | 116.4305 | 119.1589 | 121.5241 | 123.5401 | 125.228 | 126.6154 | 127.7337 | 128.6169 | 129.2999 | 129.8163 | 130.1978 | 130.4728 | 130.6662 | 130.7986 | 130.8868 | 130.9439 | 130.9797 | 131.0015 | 131.0144 | 131.0217 | 131.0257
23 | Failure (malop for FDR fau) of No3 22kV Bus Overload Protection (W Ph) | 51 | Electromechanical | Secondary | No3 Bus Outage | 0.33333 | 0.417 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.32436 | 0.33754 | 0.34967 | 0.36068 | 0.37054 | 0.37922 | 0.38675 | 0.39316 | 0.39854 | 0.40295 | 0.40651 | 0.40932 | 0.41149 | 0.41314 | 0.41435 | 0.41523 | 0.41584 | 0.41626 | 0.41654 | 0.41673 | 0.41684 | 0.41691 | 0.41695 | 0.41697 | 0.41699 | 20.9667 | 101.9214 | 106.0607 | 109.8725 | 113.3336 | 116.4305 | 119.1589 | 121.5241 | 123.5401 | 125.228 | 126.6154 | 127.7337 | 128.6169 | 129.2999 | 129.8163 | 130.1978 | 130.4728 | 130.6662 | 130.7986 | 130.8868 | 130.9439 | 130.9797 | 131.0015 | 131.0144 | 131.0217 | 131.0257
24 | Failure (malop for FDR fau) of No3 22kV Bus Overload Protection (B Ph) | 51 | Electromechanical | Secondary | No3 Bus Outage | 0.33333 | 0.417 | 1 | 0.77785 | 0.80944 | 0.83853 | 0.86494 | 0.88858 | 0.9094 | 0.92745 | 0.94284 | 0.95572 | 0.96631 | 0.97484 | 0.98158 | 0.9868 | 0.99074 | 0.99365 | 0.99575 | 0.99722 | 0.99823 | 0.99891 | 0.99934 | 0.99962 | 0.99978 | 0.99988 | 0.99994 | 0.99997 | 0.32436 | 0.33754 | 0.34967 | 0.36068 | 0.37054 | 0.37922 | 0.38675 | 0.39316 | 0.39854 | 0.40295 | 0.40651 | 0.40932 | 0.41149 | 0.41314 | 0.41435 | 0.41523 | 0.41584 | 0.41626 | 0.41654 | 0.41673 | 0.41684 | 0.41691 | 0.41695 | 0.41697 | 0.41699 | 20.9667 | 101.9214 | 106.0607 | 109.8725 | 113.3336 | 116.4305 | 119.1589 | 121.5241 | 123.5401 | 125.228 | 126.6154 | 127.7337 | 128.6169 | 129.2999 | 129.8163 | 130.1978 | 130.4728 | 130.6662 | 130.7986 | 130.8868 | 130.9439 | 130.9797 | 131.0015 | 131.0144 | 131.0217 | 131.0257
25 | Failure of CN01 feeder protection for a feeder fault | 32 | Digital | Secondary | No1 Bus Outage | 0.33333 | 0.25 | 1 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 20.9667 | 77.915 | 78.076 | 78.1993 | 78.293 | 78.3635 | 78.4162 | 78.4552 | 78.4838 | 78.5046 | 78.5196 | 78.5304 | 78.538 | 78.5434 | 78.5471 | 78.5497 | 78.5515 | 78.5527 | 78.5535 | 78.5541 | 78.5544 | 78.5547 | 78.5548 | 78.5549 | 78.555 | 78.555
26 | Failure of CN02 feeder protection for a feeder fault | 32 | Digital | Secondary | No1 Bus Outage | 0.33333 | 0.25 | 1 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 20.9667 | 77.915 | 78.076 | 78.1993 | 78.293 | 78.3635 | 78.4162 | 78.4552 | 78.4838 | 78.5046 | 78.5196 | 78.5304 | 78.538 | 78.5434 | 78.5471 | 78.5497 | 78.5515 | 78.5527 | 78.5535 | 78.5541 | 78.5544 | 78.5547 | 78.5548 | 78.5549 | 78.555 | 78.555
27 | Failure of CN03 feeder protection for a feeder fault | 32 | Digital | Secondary | No1 Bus Outage | 0.33333 | 0.25 | 1 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 20.9667 | 77.915 | 78.076 | 78.1993 | 78.293 | 78.3635 | 78.4162 | 78.4552 | 78.4838 | 78.5046 | 78.5196 | 78.5304 | 78.538 | 78.5434 | 78.5471 | 78.5497 | 78.5515 | 78.5527 | 78.5535 | 78.5541 | 78.5544 | 78.5547 | 78.5548 | 78.5549 | 78.555 | 78.555
28 | Failure of CN04 feeder protection for a feeder fault | 32 | Digital | Secondary | No1 Bus Outage | 0.33333 | 0.25 | 1 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 20.9667 | 77.915 | 78.076 | 78.1993 | 78.293 | 78.3635 | 78.4162 | 78.4552 | 78.4838 | 78.5046 | 78.5196 | 78.5304 | 78.538 | 78.5434 | 78.5471 | 78.5497 | 78.5515 | 78.5527 | 78.5535 | 78.5541 | 78.5544 | 78.5547 | 78.5548 | 78.5549 | 78.555 | 78.555
29 | Failure of CN05 feeder protection for a feeder fault | 32 | Digital | Secondary | No2 Bus Outage | 0.33333 | 0.25 | 1 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 20.9667 | 77.915 | 78.076 | 78.1993 | 78.293 | 78.3635 | 78.4162 | 78.4552 | 78.4838 | 78.5046 | 78.5196 | 78.5304 | 78.538 | 78.5434 | 78.5471 | 78.5497 | 78.5515 | 78.5527 | 78.5535 | 78.5541 | 78.5544 | 78.5547 | 78.5548 | 78.5549 | 78.555 | 78.555
30 | Failure of CN06 feeder protection for a feeder fault | 32 | Digital | Secondary | No2 Bus Outage | 0.33333 | 0.25 | 1 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 20.9667 | 77.915 | 78.076 | 78.1993 | 78.293 | 78.3635 | 78.4162 | 78.4552 | 78.4838 | 78.5046 | 78.5196 | 78.5304 | 78.538 | 78.5434 | 78.5471 | 78.5497 | 78.5515 | 78.5527 | 78.5535 | 78.5541 | 78.5544 | 78.5547 | 78.5548 | 78.5549 | 78.555 | 78.555
31 | Failure of CN07 feeder protection for a feeder fault | 32 | Digital | Secondary | No2 Bus Outage | 0.33333 | 0.25 | 1 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 20.9667 | 77.915 | 78.076 | 78.1993 | 78.293 | 78.3635 | 78.4162 | 78.4552 | 78.4838 | 78.5046 | 78.5196 | 78.5304 | 78.538 | 78.5434 | 78.5471 | 78.5497 | 78.5515 | 78.5527 | 78.5535 | 78.5541 | 78.5544 | 78.5547 | 78.5548 | 78.5549 | 78.555 | 78.555
32 | Failure of CN08 feeder protection for a feeder fault | 32 | Digital | Secondary | No2 Bus Outage | 0.33333 | 0.25 | 1 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 0.24984 | 0.24989 | 0.24992 | 0.24995 | 0.24996 | 0.24997 | 0.24998 | 0.24999 | 0.24999 | 0.24999 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 20.9667 | 77.915 | 78.076 | 78.1993 | 78.293 | 78.3635 | 78.4162 | 78.4552 | 78.4838 | 78.5046 | 78.5196 | 78.5304 | 78.538 | 78.5434 | 78.5471 | 78.5497 | 78.5515 | 78.5527 | 78.5535 | 78.5541 | 78.5544 | 78.5547 | 78.5548 | 78.5549 | 78.555 | 78.555
33 | Failure of CN09 feeder protection for a feeder fault | 32 | Digital | Secondary | No3 Bus Outage | 0.33333 | 0.5 | 1 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.49593 | 0.49695 | 0.49774 | 0.49833 | 0.49878 | 0.49912 | 0.49936 | 0.49955 | 0.49968 | 0.49977 | 0.49984 | 0.49989 | 0.49993 | 0.49995 | 0.49997 | 0.49998 | 0.49998 | 0.49999 | 0.49999 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 20.9667 | 155.8301 | 156.1519 | 156.3986 | 156.586 | 156.7271 | 156.8324 | 156.9104 | 156.9676 | 157.0092 | 157.0393 | 157.0608 | 157.076 | 157.0867 | 157.0942 | 157.0994 | 157.103 | 157.1054 | 157.107 | 157.1081 | 157.1089 | 157.1093 | 157.1097 | 157.1099 | 157.11 | 157.1101
34 | Failure of CN10 feeder protection for a feeder fault | 32 | Digital | Secondary | No3 Bus Outage | 0.33333 | 0.5 | 1 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.99936 | 0.99955 | 0.99969 | 0.99978 | 0.99985 | 0.9999 | 0.99993 | 0.99995 | 0.99997 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 0.49593 | 0.49695 | 0.49774 | 0.49833 | 0.49878 | 0.49912 | 0.49936 | 0.49955 | 0.49968 | 0.49977 | 0.49984 | 0.49989 | 0.49993 | 0.49995 | 0.49997 | 0.49998 | 0.49998 | 0.49999 | 0.49999 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 20.9667 | 155.8301 | 156.1519 | 156.3986 | 156.586 | 156.7271 | 156.8324 | 156.9104 | 156.9676 | 157.0092 | 157.0393 | 157.0608 | 157.076 | 157.0867 | 157.0942 | 157.0994 | 157.103 | 157.1054 | 157.107 | 157.1081 | 157.1089 | 157.1093 | 157.1097 | 157.1099 | 157.11 | 157.1101
35 | Failure of CN11 feeder protection for a feeder fault | 15 | Digital | Secondary | No3 Bus Outage | 0.33333 | 0.25 | 1 | 0.6802 | 0.7244 | 0.76452 | 0.80052 | 0.83244 | 0.86045 | 0.88474 | 0.9056 | 0.92333 | 0.93824 | 0.95067 | 0.96091 | 0.96928 | 0.97606 | 0.98149 | 0.98581 | 0.9892 | 0.99185 | 0.9939 | 0.99547 | 0.99666 | 0.99756 | 0.99823 | 0.99873 | 0.99909 | 0.17005 | 0.1811 | 0.19113 | 0.20013 | 0.20811 | 0.21511 | 0.22119 | 0.2264 | 0.23083 | 0.23456 | 0.23767 | 0.24023 | 0.24232 | 0.24401 | 0.24537 | 0.24645 | 0.2473 | 0.24796 | 0.24848 | 0.24887 | 0.24917 | 0.24939 | 0.24956 | 0.24968 | 0.24977 | 20.9667 | 53.4334 | 56.9052 | 60.0571 | 62.8848 | 65.3928 | 67.5925 | 69.5011 | 71.1398 | 72.5324 | 73.7039 | 74.6797 | 75.4846 | 76.1422 | 76.6744 | 77.1011 | 77.44 | 77.7069 | 77.915 | 78.076 | 78.1993 | 78.293 | 78.3635 | 78.4162 | 78.4552 | 78.4838
36 | Failure of MEF protection for a CN01 feeder fault | 15 | Analogue Electronic | Secondary | No1 Bus Outage | 0.33333 | 0.25 | 1 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 20.9667 | 1.6019 | 2.1073 | 2.7239 | 3.4659 | 4.3475 | 5.3829 | 6.5853 | 7.9673 | 9.5395 | 11.3108 | 13.2872 | 15.4715 | 17.863 | 20.4564 | 23.2418 | 26.2046 | 29.3248 | 32.5775 | 35.9329 | 39.357 | 42.8124 | 46.2592 | 49.6563 | 52.9628 | 56.1394
37 | Failure of MEF protection for a CN02 feeder fault | 15 | Analogue Electronic | Secondary | No1 Bus Outage | 0.33333 | 0.25 | 1 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 20.9667 | 1.6019 | 2.1073 | 2.7239 | 3.4659 | 4.3475 | 5.3829 | 6.5853 | 7.9673 | 9.5395 | 11.3108 | 13.2872 | 15.4715 | 17.863 | 20.4564 | 23.2418 | 26.2046 | 29.3248 | 32.5775 | 35.9329 | 39.357 | 42.8124 | 46.2592 | 49.6563 | 52.9628 | 56.1394
38 | Failure of MEF protection for a CN03 feeder fault | 15 | Analogue Electronic | Secondary | No1 Bus Outage | 0.33333 | 0.25 | 1 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 20.9667 | 1.6019 | 2.1073 | 2.7239 | 3.4659 | 4.3475 | 5.3829 | 6.5853 | 7.9673 | 9.5395 | 11.3108 | 13.2872 | 15.4715 | 17.863 | 20.4564 | 23.2418 | 26.2046 | 29.3248 | 32.5775 | 35.9329 | 39.357 | 42.8124 | 46.2592 | 49.6563 | 52.9628 | 56.1394
39 | Failure of MEF protection for a CN04 feeder fault | 15 | Analogue Electronic | Secondary | No1 Bus Outage | 0.33333 | 0.25 | 1 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 20.9667 | 1.6019 | 2.1073 | 2.7239 | 3.4659 | 4.3475 | 5.3829 | 6.5853 | 7.9673 | 9.5395 | 11.3108 | 13.2872 | 15.4715 | 17.863 | 20.4564 | 23.2418 | 26.2046 | 29.3248 | 32.5775 | 35.9329 | 39.357 | 42.8124 | 46.2592 | 49.6563 | 52.9628 | 56.1394
40 | Failure of MEF protection for a CN05 feeder fault | 15 | Analogue Electronic | Secondary | No2 Bus Outage | 0.33333 | 0.25 | 1 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 20.9667 | 1.6019 | 2.1073 | 2.7239 | 3.4659 | 4.3475 | 5.3829 | 6.5853 | 7.9673 | 9.5395 | 11.3108 | 13.2872 | 15.4715 | 17.863 | 20.4564 | 23.2418 | 26.2046 | 29.3248 | 32.5775 | 35.9329 | 39.357 | 42.8124 | 46.2592 | 49.6563 | 52.9628 | 56.1394
41 | Failure of MEF protection for a CN06 feeder fault | 15 | Analogue Electronic | Secondary | No2 Bus Outage | 0.33333 | 0.25 | 1 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 20.9667 | 1.6019 | 2.1073 | 2.7239 | 3.4659 | 4.3475 | 5.3829 | 6.5853 | 7.9673 | 9.5395 | 11.3108 | 13.2872 | 15.4715 | 17.863 | 20.4564 | 23.2418 | 26.2046 | 29.3248 | 32.5775 | 35.9329 | 39.357 | 42.8124 | 46.2592 | 49.6563 | 52.9628 | 56.1394
42 | Failure of MEF protection for a CN07 feeder fault | 15 | Analogue Electronic | Secondary | No2 Bus Outage | 0.33333 | 0.25 | 1 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 20.9667 | 1.6019 | 2.1073 | 2.7239 | 3.4659 | 4.3475 | 5.3829 | 6.5853 | 7.9673 | 9.5395 | 11.3108 | 13.2872 | 15.4715 | 17.863 | 20.4564 | 23.2418 | 26.2046 | 29.3248 | 32.5775 | 35.9329 | 39.357 | 42.8124 | 46.2592 | 49.6563 | 52.9628 | 56.1394
43 | Failure of MEF protection for a CN08 feeder fault | 15 | Analogue Electronic | Secondary | No2 Bus Outage | 0.33333 | 0.25 | 1 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 20.9667 | 1.6019 | 2.1073 | 2.7239 | 3.4659 | 4.3475 | 5.3829 | 6.5853 | 7.9673 | 9.5395 | 11.3108 | 13.2872 | 15.4715 | 17.863 | 20.4564 | 23.2418 | 26.2046 | 29.3248 | 32.5775 | 35.9329 | 39.357 | 42.8124 | 46.2592 | 49.6563 | 52.9628 | 56.1394
44 | Failure of MEF protection for a CN09 feeder fault | 15 | Analogue Electronic | Secondary | No3 Bus Outage | 0.33333 | 0.5 | 1 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.010196 | 0.013413 | 0.017338 | 0.02206 | 0.027672 | 0.034262 | 0.041915 | 0.050711 | 0.060719 | 0.071993 | 0.084572 | 0.098476 | 0.1137 | 0.1302 | 0.14793 | 0.16679 | 0.18665 | 0.20735 | 0.22871 | 0.25051 | 0.2725 | 0.29444 | 0.31606 | 0.33711 | 0.35732 | 20.9667 | 3.2038 | 4.2147 | 5.4479 | 6.9318 | 8.6951 | 10.7657 | 13.1706 | 15.9345 | 19.079 | 22.6216 | 26.5744 | 30.9431 | 35.726 | 40.9127 | 46.4837 | 52.4092 | 58.6497 | 65.155 | 71.8657 | 78.714 | 85.6248 | 92.5184 | 99.3126 | 105.9255 | 112.2787
45 | Failure of MEF protection for a CN10 feeder fault | 15 | Analogue Electronic | Secondary | No3 Bus Outage | 0.33333 | 0.5 | 1 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.010196 | 0.013413 | 0.017338 | 0.02206 | 0.027672 | 0.034262 | 0.041915 | 0.050711 | 0.060719 | 0.071993 | 0.084572 | 0.098476 | 0.1137 | 0.1302 | 0.14793 | 0.16679 | 0.18665 | 0.20735 | 0.22871 | 0.25051 | 0.2725 | 0.29444 | 0.31606 | 0.33711 | 0.35732 | 20.9667 | 3.2038 | 4.2147 | 5.4479 | 6.9318 | 8.6951 | 10.7657 | 13.1706 | 15.9345 | 19.079 | 22.6216 | 26.5744 | 30.9431 | 35.726 | 40.9127 | 46.4837 | 52.4092 | 58.6497 | 65.155 | 71.8657 | 78.714 | 85.6248 | 92.5184 | 99.3126 | 105.9255 | 112.2787
46 | Failure of MEF protection for a CN11 feeder fault | 15 | Analogue Electronic | Secondary | No3 Bus Outage | 0.33333 | 0.25 | 1 | 0.020392 | 0.026826 | 0.034675 | 0.044121 | 0.055344 | 0.068523 | 0.083831 | 0.10142 | 0.12144 | 0.14399 | 0.16914 | 0.19695 | 0.22739 | 0.26041 | 0.29587 | 0.33358 | 0.3733 | 0.41471 | 0.45742 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.005098 | 0.0067065 | 0.0086689 | 0.01103 | 0.013836 | 0.017131 | 0.020958 | 0.025356 | 0.030359 | 0.035996 | 0.042286 | 0.049238 | 0.056849 | 0.065102 | 0.073967 | 0.083396 | 0.093326 | 0.10368 | 0.11436 | 0.12525 | 0.13625 | 0.14722 | 0.15803 | 0.16855 | 0.17866 | 20.9667 | 1.6019 | 2.1073 | 2.7239 | 3.4659 | 4.3475 | 5.3829 | 6.5853 | 7.9673 | 9.5395 | 11.3108 | 13.2872 | 15.4715 | 17.863 | 20.4564 | 23.2418 | 26.2046 | 29.3248 | 32.5775 | 35.9329 | 39.357 | 42.8124 | 46.2592 | 49.6563 | 52.9628 | 56.1394
47 | Failure (malop) of BUEF protection | 34 | Analogue Electronic | Secondary | Station Black | 0.33333 | 0.501 | 1 | 0.50101 | 0.545 | 0.58888 | 0.63212 | 0.67421 | 0.71465 | 0.75298 | 0.78879 | 0.82177 | 0.85167 | 0.87835 | 0.90176 | 0.92194 | 0.93903 | 0.95323 | 0.96479 | 0.97401 | 0.98121 | 0.98671 | 0.99081 | 0.99379 | 0.99591 | 0.99737 | 0.99836 | 0.999 | 0.25101 | 0.27304 | 0.29503 | 0.31669 | 0.33778 | 0.35804 | 0.37724 | 0.39518 | 0.41171 | 0.42669 | 0.44005 | 0.45178 | 0.46189 | 0.47045 | 0.47757 | 0.48336 | 0.48798 | 0.49159 | 0.49434 | 0.49639 | 0.49789 | 0.49895 | 0.49968 | 0.50018 | 0.5005 | 62.9 | 236.6142 | 257.3881 | 278.1103 | 298.5337 | 318.4122 | 337.5099 | 355.6103 | 372.5245 | 388.0987 | 402.22 | 414.82 | 425.8758 | 435.4085 | 443.4794 | 450.1838 | 455.6439 | 459.9995 | 463.4001 | 465.9961 | 467.9322 | 469.3414 | 470.3415 | 471.0329 | 471.498 | 471.8021
| Total | [58 empty] | 3169.4455 | 3286.6882 | 3398.5109 | 3504.3032 | 3603.644 | 3696.3223 | 3782.3448 | 3861.9285 | 3935.4807 | 4003.5655 | 4066.862 | 4126.1172 | 4182.0957 | 4235.533 | 4287.093 | 4337.3344 | 4386.6856 | 4435.4311 | 4483.7075 | 4531.5097 | 4578.705 | 4625.0543 | 4670.2376 | 4713.8836 | 4755.599