## Revision
Revision History
Revision | Date | Comments
0.1 | 2025-10-30 | First Issue
0.2 | 2025-11-13 | Transformer, 66kV and 22kV CB PoF's updated
Transformer, 66kV and 22kV CB PoF's tabs added
Modified asset quantities for Failure of Feeder Circuit Breaker and 66kV Circuit Breaker
Added Summary tab with transformer and switchgear quantified risk splits
Quantities and Cost of Consequences cells linked to cells in Notes tab
Content in Notes tab have been reorganised
Safety risk event probability accounts for likelihood of fault and explosion
VCR rates updated
PoF for 40% increase in scale factors for 22kV switchgear have been calculated

## Summary
Summary of quantified risks - CN ZSS
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Option 1 - Do Nothing
Transformers Risks | 40985.7898 | 52157.2261 | 62372.3959 | 73034.5144 | 83998.7491 | 95702.8647 | 108686.5532 | 123977.2102 | 140891.821 | 158062.0146 | 176012.5948 | 196790.3974 | 220410.4275 | 246794.7312 | 274057.341 | 302049.3495 | 332282.9965 | 364824.1107 | 399583.6662 | 437591.5495
Switchgear Risks | 1818973.9924 | 2062352.7471 | 2199722.9354 | 2300117.5766 | 2365330.9676 | 2412918.2216 | 2457188.4353 | 2517364.4181 | 2573726.5482 | 2602293.5945 | 2616657.5148 | 2646942.2842 | 2687922.5476 | 2734634.4113 | 2765400.1106 | 2781985.5631 | 2800164.4286 | 2819861.9498 | 2839944.4014 | 2867120.114
Total | 1859959.7821 | 2114509.9732 | 2262095.3312 | 2373152.091 | 2449329.7167 | 2508621.0863 | 2565874.9885 | 2641341.6283 | 2714618.3691 | 2760355.6092 | 2792670.1096 | 2843732.6816 | 2908332.9751 | 2981429.1425 | 3039457.4516 | 3084034.9126 | 3132447.4251 | 3184686.0605 | 3239528.0675 | 3304711.6635
Option 2 - Transformer Refurbishment with Deferred ZSS Redevelopment;
Transformers Risks | 40985.7898 | 52157.2261 | 45161.7653 | 38663.3545 | 44911.534 | 51691.8931 | 59317.6751 | 68384.7222 | 78561.5157 | 1.0532 | 2.7573 | 4.9552 | 7.6302 | 10.7941 | 14.379 | 18.3738 | 22.8959 | 28.0187 | 33.8244 | 40.5186
Switchgear Risks | 1818973.9924 | 2062352.7471 | 2199722.9354 | 2300117.5766 | 2365330.9676 | 2412918.2216 | 2457188.4353 | 2517364.4181 | 2573726.5482 | 2602293.5945 | 2616657.5148 | 2646942.2842 | 2687922.5476 | 2734634.4113 | 2765400.1106 | 2781985.5631 | 2800164.4286 | 2819861.9498 | 2839944.4014 | 2867120.114
Total | 1859959.7821 | 2114509.9732 | 2244884.7007 | 2338780.9311 | 2410242.5016 | 2464610.1146 | 2516506.1104 | 2585749.1403 | 2652288.0639 | 2602294.6477 | 2616660.272 | 2646947.2394 | 2687930.1777 | 2734645.2054 | 2765414.4896 | 2782003.9369 | 2800187.3244 | 2819889.9685 | 2839978.2258 | 2867160.6326
Option 3 - ZSS Redevelopment
Transformers Risks | 40985.7898 | 52157.2261 | 62372.3959 | 73034.5144 | 0.9927 | 2.6292 | 4.7447 | 7.3539 | 10.4333 | 13.871 | 17.6879 | 22.1202 | 27.2627 | 33.2105 | 39.8111 | 47.1254 | 55.5128 | 65.1734 | 76.3205 | 89.4394
Switchgear Risks | 1818973.9924 | 2062352.7471 | 2199722.9354 | 2300117.5766 | 112.5763 | 45430.4943 | 91878.5714 | 139495.8648 | 187702.1938 | 234081.0792 | 278785.2238 | 324588.1111 | 371663.9598 | 419754.6661 | 465573.4059 | 508506.5082 | 551186.2236 | 593681.6135 | 635943.3529 | 679379.9677
Total | 1859959.7821 | 2114509.9732 | 2262095.3312 | 2373152.091 | 113.569 | 45433.1235 | 91883.3161 | 139503.2187 | 187712.6271 | 234094.9502 | 278802.9116 | 324610.2313 | 371691.2224 | 419787.8766 | 465613.2169 | 508553.6336 | 551241.7365 | 593746.7869 | 636019.6734 | 679469.4071
Option 4 - Staged ZSS Redevelopment, Prioritising Transformer Replacement
Transformers Risks | 40985.7898 | 52157.2261 | 62372.3959 | 73034.5144 | 0.9927 | 2.6292 | 4.7447 | 7.3539 | 10.4333 | 13.871 | 17.6879 | 22.1202 | 27.2627 | 33.2105 | 39.8111 | 47.1254 | 55.5128 | 65.1734 | 76.3205 | 89.4394
Switchgear Risks | 1818973.9924 | 2062352.7471 | 2199722.9354 | 2300117.5766 | 2365330.9676 | 2412918.2216 | 2457188.4353 | 2517364.4181 | 118.8507 | 47651.3081 | 95360.3116 | 143234.3751 | 191758.7757 | 240994.2146 | 289046.5144 | 335081.3181 | 380703.6242 | 425983.4928 | 470937.2876 | 516562.4142
Total | 1859959.7821 | 2114509.9732 | 2262095.3312 | 2373152.091 | 2365331.9603 | 2412920.8508 | 2457193.18 | 2517371.772 | 129.284 | 47665.1791 | 95377.9995 | 143256.4954 | 191786.0384 | 241027.4252 | 289086.3255 | 335128.4436 | 380759.137 | 426048.6662 | 471013.6081 | 516651.8537
Option 5 - Staged ZSS Redevelopment, Prioritising Switchgear and Protection Relay Replacement
Transformers Risks | 40985.7898 | 52157.2261 | 62372.3959 | 73034.5144 | 83998.7491 | 95702.8647 | 108686.5532 | 123977.2102 | 1.048 | 2.7577 | 4.9245 | 7.551 | 10.6587 | 14.2807 | 18.3389 | 22.8353 | 27.9258 | 33.7033 | 40.2697 | 47.872
Switchgear Risks | 1818973.9924 | 2062352.7471 | 2199722.9354 | 2300117.5766 | 112.5763 | 45430.4943 | 91878.5714 | 139495.8648 | 187702.1938 | 234081.0792 | 278785.2238 | 324588.1111 | 371663.9598 | 419754.6661 | 465573.4059 | 508506.5082 | 551186.2236 | 593681.6135 | 635943.3529 | 679379.9677
Total | 1859959.7821 | 2114509.9732 | 2262095.3312 | 2373152.091 | 84111.3254 | 141133.359 | 200565.1246 | 263473.0749 | 187703.2419 | 234083.8369 | 278790.1482 | 324595.6621 | 371674.6185 | 419768.9468 | 465591.7448 | 508529.3435 | 551214.1494 | 593715.3169 | 635983.6226 | 679427.8397

## Option 1
|  |  | Items | Probability of Failure |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
|  |  | 1 | Failure of Transformers No.1 |  |  | 10.63% | 18.72% | 19.95% | 21.24% | 22.59% | 24.01% | 25.48% | 27.01% | 28.6% | 30.26% | 31.97% | 33.74% | 35.56% | 37.44% | 39.37% | 41.35% | 43.37% | 45.42% | 47.52% | 49.64% | 51.79%
|  |  | 2 | Failure of Transformers No.2 |  |  | 10.63% | 18.72% | 19.95% | 21.24% | 22.59% | 24.01% | 25.48% | 27.01% | 28.6% | 30.26% | 31.97% | 33.74% | 35.56% | 37.44% | 39.37% | 41.35% | 43.37% | 45.42% | 47.52% | 49.64% | 51.79%
|  |  | 3 | Failure of Transformers No.1 and No.2 |  |  | 1.13% | 3.506% | 3.982% | 4.513% | 5.105% | 5.762% | 6.491% | 7.296% | 8.182% | 9.155% | 10.22% | 11.38% | 12.65% | 14.02% | 15.5% | 17.1% | 18.81% | 20.63% | 22.58% | 24.64% | 26.82%
|  |  | 4 | Failure of 22kV Circuit Breaker |  |  | 74.33% | 75.25% | 75.8% | 76.34% | 76.87% | 77.39% | 77.89% | 78.38% | 78.87% | 79.34% | 79.8% | 80.25% | 80.69% | 81.12% | 81.54% | 81.96% | 82.36% | 82.75% | 83.14% | 83.52% | 83.89%
|  |  | 5 | Failure of 66kV Circuit Breaker |  |  | 55.24% | 92.43% | 93.52% | 94.5% | 95.36% | 96.11% | 96.76% | 97.33% | 97.81% | 98.22% | 98.56% | 98.85% | 99.09% | 99.28% | 99.44% | 99.56% | 99.67% | 99.75% | 99.81% | 99.86% | 99.89%
Option 1 - Do Nothing | [6 empty] | 2024: Years
Item | Fault Scenario | Risk | Assets Quantities | Event Probability | CoC | LoC | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
1 | Failure of Transformer No.1 and No.2 | Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 19.617 | 21.9811 | 23.1912 | 24.0071 | 24.4605 | 24.7413 | 24.9987 | 25.4267 | 25.8239 | 25.9507 | 25.9461 | 26.1082 | 26.382 | 26.7171 | 26.9011 | 26.9522 | 27.0236 | 27.1136 | 27.211 | 27.3792
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 40985.7898 | 52157.2261 | 62372.3959 | 73034.5144 | 83998.7491 | 95702.8647 | 108686.5532 | 123977.2102 | 140891.821 | 158062.0146 | 176012.5948 | 196790.3974 | 220410.4275 | 246794.7312 | 274057.341 | 302049.3495 | 332282.9965 | 364824.1107 | 399583.6662 | 437591.5495
2 | Failure of Feeder Circuit Breaker | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 564030.8044 | 574219.2817 | 583865.9158 | 597523.1587 | 610482.0213 | 617044.9656 | 620418.8944 | 627723.6245 | 637703.653 | 649160.4976 | 656933.4607 | 661418.1533 | 666344.463 | 671684.6253 | 677153.03 | 684343.8651
3 | Failure of Transformer Incomer Circuit Breakers | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 564030.8044 | 574219.2817 | 583865.9158 | 597523.1587 | 610482.0213 | 617044.9656 | 620418.8944 | 627723.6245 | 637703.653 | 649160.4976 | 656933.4607 | 661418.1533 | 666344.463 | 671684.6253 | 677153.03 | 684343.8651
4 | Failure of 22kV Bus Tie Circuit Breakers | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 564030.8044 | 574219.2817 | 583865.9158 | 597523.1587 | 610482.0213 | 617044.9656 | 620418.8944 | 627723.6245 | 637703.653 | 649160.4976 | 656933.4607 | 661418.1533 | 666344.463 | 671684.6253 | 677153.03 | 684343.8651
5 | Failure of 66kV Bus Tie Circuit Breakers | Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 499350.8009 | 572876.6019 | 617073.1634 | 650452.4173 | 673238.5544 | 690260.3766 | 705590.688 | 724794.9419 | 742280.4842 | 751158.6978 | 755400.8315 | 763771.4108 | 774811.5887 | 787152.9185 | 794599.7284 | 797731.1032 | 801131.0396 | 804808.0738 | 808485.3113 | 814088.5188
[5 empty] | Transformers Risks |  |  | 40985.7898 | 52157.2261 | 62372.3959 | 73034.5144 | 83998.7491 | 95702.8647 | 108686.5532 | 123977.2102 | 140891.821 | 158062.0146 | 176012.5948 | 196790.3974 | 220410.4275 | 246794.7312 | 274057.341 | 302049.3495 | 332282.9965 | 364824.1107 | 399583.6662 | 437591.5495
[5 empty] | Switchgear Risks |  |  | 1818973.9924 | 2062352.7471 | 2199722.9354 | 2300117.5766 | 2365330.9676 | 2412918.2216 | 2457188.4353 | 2517364.4181 | 2573726.5482 | 2602293.5945 | 2616657.5148 | 2646942.2842 | 2687922.5476 | 2734634.4113 | 2765400.1106 | 2781985.5631 | 2800164.4286 | 2819861.9498 | 2839944.4014 | 2867120.114
[5 empty] | Total |  |  | 1859959.7821 | 2114509.9732 | 2262095.3312 | 2373152.091 | 2449329.7167 | 2508621.0863 | 2565874.9885 | 2641341.6283 | 2714618.3691 | 2760355.6092 | 2792670.1096 | 2843732.6816 | 2908332.9751 | 2981429.1425 | 3039457.4516 | 3084034.9126 | 3132447.4251 | 3184686.0605 | 3239528.0675 | 3304711.6635

## Option 2
|  |  | Items | Probability of Failure |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
|  |  | 1 | Failure of Transformers No.1 |  |  | 10.63% | 18.72% | 19.95% | 15.38% | 16.44% | 17.55% | 18.72% | 19.95% | 21.24% | 22.59% | 0.08252% | 0.1335% | 0.1785% | 0.2203% | 0.2604% | 0.2995% | 0.3382% | 0.3771% | 0.4164% | 0.4567% | 0.4983%
|  |  | 2 | Failure of Transformers No.2 |  |  | 10.63% | 18.72% | 19.95% | 21.24% | 16.44% | 17.55% | 18.72% | 19.95% | 21.24% | 22.59% | 0.08252% | 0.1335% | 0.1785% | 0.2203% | 0.2604% | 0.2995% | 0.3382% | 0.3771% | 0.4164% | 0.4567% | 0.4983%
|  |  | 3 | Failure of Transformers No.1 and No.2 |  |  | 1.13% | 3.506% | 3.982% | 3.268% | 2.702% | 3.081% | 3.506% | 3.982% | 4.513% | 5.105% | 6.81e-05% | 0.0001783% | 0.0003185% | 0.0004853% | 0.000678% | 0.0008969% | 0.001144% | 0.001422% | 0.001734% | 0.002086% | 0.002483%
|  |  | 4 | Failure of 22kV Circuit Breaker |  |  | 74.33% | 75.25% | 75.8% | 76.34% | 76.87% | 77.39% | 77.89% | 78.38% | 78.87% | 79.34% | 79.8% | 80.25% | 80.69% | 81.12% | 81.54% | 81.96% | 82.36% | 82.75% | 83.14% | 83.52% | 83.89%
|  |  | 5 | Failure of 66kV Circuit Breaker |  |  | 55.24% | 92.43% | 93.52% | 94.5% | 95.36% | 96.11% | 96.76% | 97.33% | 97.81% | 98.22% | 98.56% | 98.85% | 99.09% | 99.28% | 99.44% | 99.56% | 99.67% | 99.75% | 99.81% | 99.86% | 99.89%
Option 2 - Transformer Refurbishment with Deferred ZSS Redevelopment; | [6 empty] | 2024: Years
Item | Fault Scenario | Risk | Assets Quantities | Event Probability | CoC | LoC | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
1 | Failure of Transformer No.1 and No.2 | Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 19.617 | 21.9811 | 23.1912 | 24.0071 | 24.4605 | 24.7413 | 24.9987 | 25.4267 | 25.8239 | 25.9507 | 25.9461 | 26.1082 | 26.382 | 26.7171 | 26.9011 | 26.9522 | 27.0236 | 27.1136 | 27.211 | 27.3792
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 40985.7898 | 52157.2261 | 45161.7653 | 38663.3545 | 44911.534 | 51691.8931 | 59317.6751 | 68384.7222 | 78561.5157 | 1.0532 | 2.7573 | 4.9552 | 7.6302 | 10.7941 | 14.379 | 18.3738 | 22.8959 | 28.0187 | 33.8244 | 40.5186
2 | Failure of Feeder Circuit Breaker | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 564030.8044 | 574219.2817 | 583865.9158 | 597523.1587 | 610482.0213 | 617044.9656 | 620418.8944 | 627723.6245 | 637703.653 | 649160.4976 | 656933.4607 | 661418.1533 | 666344.463 | 671684.6253 | 677153.03 | 684343.8651
3 | Failure of Transformer Incomer Circuit Breakers | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 564030.8044 | 574219.2817 | 583865.9158 | 597523.1587 | 610482.0213 | 617044.9656 | 620418.8944 | 627723.6245 | 637703.653 | 649160.4976 | 656933.4607 | 661418.1533 | 666344.463 | 671684.6253 | 677153.03 | 684343.8651
4 | Failure of 22kV Bus Tie Circuit Breakers | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 564030.8044 | 574219.2817 | 583865.9158 | 597523.1587 | 610482.0213 | 617044.9656 | 620418.8944 | 627723.6245 | 637703.653 | 649160.4976 | 656933.4607 | 661418.1533 | 666344.463 | 671684.6253 | 677153.03 | 684343.8651
5 | Failure of 66kV Bus Tie Circuit Breakers | Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 499350.8009 | 572876.6019 | 617073.1634 | 650452.4173 | 673238.5544 | 690260.3766 | 705590.688 | 724794.9419 | 742280.4842 | 751158.6978 | 755400.8315 | 763771.4108 | 774811.5887 | 787152.9185 | 794599.7284 | 797731.1032 | 801131.0396 | 804808.0738 | 808485.3113 | 814088.5188
[5 empty] | Transformers Risks |  |  | 40985.7898 | 52157.2261 | 45161.7653 | 38663.3545 | 44911.534 | 51691.8931 | 59317.6751 | 68384.7222 | 78561.5157 | 1.0532 | 2.7573 | 4.9552 | 7.6302 | 10.7941 | 14.379 | 18.3738 | 22.8959 | 28.0187 | 33.8244 | 40.5186
[5 empty] | Switchgear Risks |  |  | 1818973.9924 | 2062352.7471 | 2199722.9354 | 2300117.5766 | 2365330.9676 | 2412918.2216 | 2457188.4353 | 2517364.4181 | 2573726.5482 | 2602293.5945 | 2616657.5148 | 2646942.2842 | 2687922.5476 | 2734634.4113 | 2765400.1106 | 2781985.5631 | 2800164.4286 | 2819861.9498 | 2839944.4014 | 2867120.114
[5 empty] | Total |  |  | 1859959.7821 | 2114509.9732 | 2244884.7007 | 2338780.9311 | 2410242.5016 | 2464610.1146 | 2516506.1104 | 2585749.1403 | 2652288.0639 | 2602294.6477 | 2616660.272 | 2646947.2394 | 2687930.1777 | 2734645.2054 | 2765414.4896 | 2782003.9369 | 2800187.3244 | 2819889.9685 | 2839978.2258 | 2867160.6326

## Option 3
|  |  | Items | Probability of Failure |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
|  |  | 1 | Failure of Transformers No.1 |  |  | 10.63% | 18.72% | 19.95% | 21.24% | 22.59% | 0.08252% | 0.1335% | 0.1785% | 0.2203% | 0.2604% | 0.2995% | 0.3382% | 0.3771% | 0.4164% | 0.4567% | 0.4983% | 0.5417% | 0.5871% | 0.6351% | 0.686% | 0.7404%
|  |  | 2 | Failure of Transformers No.2 |  |  | 10.63% | 18.72% | 19.95% | 21.24% | 22.59% | 0.08252% | 0.1335% | 0.1785% | 0.2203% | 0.2604% | 0.2995% | 0.3382% | 0.3771% | 0.4164% | 0.4567% | 0.4983% | 0.5417% | 0.5871% | 0.6351% | 0.686% | 0.7404%
|  |  | 3 | Failure of Transformers No.1 and No.2 |  |  | 1.13% | 3.506% | 3.982% | 4.513% | 5.105% | 6.81e-05% | 0.0001783% | 0.0003185% | 0.0004853% | 0.000678% | 0.0008969% | 0.001144% | 0.001422% | 0.001734% | 0.002086% | 0.002483% | 0.002934% | 0.003447% | 0.004034% | 0.004707% | 0.005482%
|  |  | 4 | Failure of 22kV Circuit Breaker |  |  | 74.33% | 75.25% | 75.8% | 76.34% | 76.87% | 0.005149% | 2.054% | 4.112% | 6.137% | 8.131% | 10.09% | 12.02% | 13.91% | 15.76% | 17.58% | 19.36% | 21.1% | 22.81% | 24.49% | 26.13% | 27.74%
|  |  | 5 | Failure of 66kV Circuit Breaker |  |  | 55.24% | 92.43% | 93.52% | 94.5% | 95.36% | 0.0001636% | 0.001851% | 0.00765% | 0.02094% | 0.04571% | 0.08652% | 0.1483% | 0.2366% | 0.3571% | 0.516% | 0.7196% | 0.9745% | 1.287% | 1.666% | 2.116% | 2.645%
Option 3 - ZSS Redevelopment | [6 empty] | 2024: Years
Item | Fault Scenario | Risk | Assets Quantities | Event Probability | CoC | LoC | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
1 | Failure of Transformer No.1 and No.2 | Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 19.617 | 21.9811 | 23.1912 | 24.0071 | 24.4605 | 24.7413 | 24.9987 | 25.4267 | 25.8239 | 25.9507 | 25.9461 | 26.1082 | 26.382 | 26.7171 | 26.9011 | 26.9522 | 27.0236 | 27.1136 | 27.211 | 27.3792
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 40985.7898 | 52157.2261 | 62372.3959 | 73034.5144 | 0.9927 | 2.6292 | 4.7447 | 7.3539 | 10.4333 | 13.871 | 17.6879 | 22.1202 | 27.2627 | 33.2105 | 39.8111 | 47.1254 | 55.5128 | 65.1734 | 76.3205 | 89.4394
2 | Failure of Feeder Circuit Breaker | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 37.5254 | 15143.498 | 30626.189 | 46498.6105 | 62567.3443 | 78026.8335 | 92927.8408 | 108194.5851 | 123884.6446 | 139911.1572 | 155177.3015 | 169476.7497 | 183684.2491 | 197819.165 | 211860.1496 | 226269.7923
3 | Failure of Transformer Incomer Circuit Breakers | Unserved Energy (N-1)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 37.5254 | 15143.498 | 30626.189 | 46498.6105 | 62567.3443 | 78026.8335 | 92927.8408 | 108194.5851 | 123884.6446 | 139911.1572 | 155177.3015 | 169476.7497 | 183684.2491 | 197819.165 | 211860.1496 | 226269.7923
4 | Failure of 22kV Bus Tie Circuit Breakers | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 37.5254 | 15143.498 | 30626.189 | 46498.6105 | 62567.3443 | 78026.8335 | 92927.8408 | 108194.5851 | 123884.6446 | 139911.1572 | 155177.3015 | 169476.7497 | 183684.2491 | 197819.165 | 211860.1496 | 226269.7923
5 | Failure of 66kV Bus Tie Circuit Breakers | Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 499350.8009 | 572876.6019 | 617073.1634 | 650452.4173 | 1.9505e-06 | 0.00025252 | 0.0043593 | 0.033212 | 0.1608 | 0.57878 | 1.7013 | 4.3557 | 10.0261 | 21.1945 | 41.5014 | 76.2592 | 133.4762 | 224.1185 | 362.9042 | 570.5907
[5 empty] | Transformers Risks |  |  | 40985.7898 | 52157.2261 | 62372.3959 | 73034.5144 | 0.9927 | 2.6292 | 4.7447 | 7.3539 | 10.4333 | 13.871 | 17.6879 | 22.1202 | 27.2627 | 33.2105 | 39.8111 | 47.1254 | 55.5128 | 65.1734 | 76.3205 | 89.4394
[5 empty] | Switchgear Risks |  |  | 1818973.9924 | 2062352.7471 | 2199722.9354 | 2300117.5766 | 112.5763 | 45430.4943 | 91878.5714 | 139495.8648 | 187702.1938 | 234081.0792 | 278785.2238 | 324588.1111 | 371663.9598 | 419754.6661 | 465573.4059 | 508506.5082 | 551186.2236 | 593681.6135 | 635943.3529 | 679379.9677
[5 empty] | Total |  |  | 1859959.7821 | 2114509.9732 | 2262095.3312 | 2373152.091 | 113.569 | 45433.1235 | 91883.3161 | 139503.2187 | 187712.6271 | 234094.9502 | 278802.9116 | 324610.2313 | 371691.2224 | 419787.8766 | 465613.2169 | 508553.6336 | 551241.7365 | 593746.7869 | 636019.6734 | 679469.4071

## Option 4
|  |  | Items | Probability of Failure |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
|  |  | 1 | Failure of Transformers No.1 |  |  | 10.63% | 18.72% | 19.95% | 21.24% | 22.59% | 0.08252% | 0.1335% | 0.1785% | 0.2203% | 0.2604% | 0.2995% | 0.3382% | 0.3771% | 0.4164% | 0.4567% | 0.4983% | 0.5417% | 0.5871% | 0.6351% | 0.686% | 0.7404%
|  |  | 2 | Failure of Transformers No.2 |  |  | 10.63% | 18.72% | 19.95% | 21.24% | 22.59% | 0.08252% | 0.1335% | 0.1785% | 0.2203% | 0.2604% | 0.2995% | 0.3382% | 0.3771% | 0.4164% | 0.4567% | 0.4983% | 0.5417% | 0.5871% | 0.6351% | 0.686% | 0.7404%
|  |  | 3 | Failure of Transformers No.1 and No.2 |  |  | 1.13% | 3.506% | 3.982% | 4.513% | 5.105% | 6.81e-05% | 0.0001783% | 0.0003185% | 0.0004853% | 0.000678% | 0.0008969% | 0.001144% | 0.001422% | 0.001734% | 0.002086% | 0.002483% | 0.002934% | 0.003447% | 0.004034% | 0.004707% | 0.005482%
|  |  | 4 | Failure of 22kV Circuit Breaker |  |  | 74.33% | 75.25% | 75.8% | 76.34% | 76.87% | 77.39% | 77.89% | 78.38% | 78.87% | 0.005149% | 2.054% | 4.112% | 6.137% | 8.131% | 10.09% | 12.02% | 13.91% | 15.76% | 17.58% | 19.36% | 21.1%
|  |  | 5 | Failure of 66kV Circuit Breaker |  |  | 55.24% | 92.43% | 93.52% | 94.5% | 95.36% | 96.11% | 96.76% | 97.33% | 97.81% | 0.0001636% | 0.001851% | 0.00765% | 0.02094% | 0.04571% | 0.08652% | 0.1483% | 0.2366% | 0.3571% | 0.516% | 0.7196% | 0.9745%
Option 4 - Staged ZSS Redevelopment, Prioritising Transformer Replacement | [6 empty] | 2024: Years
Item | Fault Scenario | Risk | Assets Quantities | Event Probability | CoC | LoC | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
1 | Failure of Transformer No.1 and No.2 | Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 19.617 | 21.9811 | 23.1912 | 24.0071 | 24.4605 | 24.7413 | 24.9987 | 25.4267 | 25.8239 | 25.9507 | 25.9461 | 26.1082 | 26.382 | 26.7171 | 26.9011 | 26.9522 | 27.0236 | 27.1136 | 27.211 | 27.3792
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 40985.7898 | 52157.2261 | 62372.3959 | 73034.5144 | 0.9927 | 2.6292 | 4.7447 | 7.3539 | 10.4333 | 13.871 | 17.6879 | 22.1202 | 27.2627 | 33.2105 | 39.8111 | 47.1254 | 55.5128 | 65.1734 | 76.3205 | 89.4394
2 | Failure of Feeder Circuit Breaker | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 564030.8044 | 574219.2817 | 583865.9158 | 597523.1587 | 39.6169 | 15883.7693 | 31786.769 | 47744.7803 | 63919.5371 | 80331.2063 | 96348.2501 | 111692.2739 | 126897.7848 | 141987.3279 | 156965.1027 | 172161.649
3 | Failure of Transformer Incomer Circuit Breakers | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 564030.8044 | 574219.2817 | 583865.9158 | 597523.1587 | 39.6169 | 15883.7693 | 31786.769 | 47744.7803 | 63919.5371 | 80331.2063 | 96348.2501 | 111692.2739 | 126897.7848 | 141987.3279 | 156965.1027 | 172161.649
4 | Failure of 22kV Bus Tie Circuit Breakers | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 564030.8044 | 574219.2817 | 583865.9158 | 597523.1587 | 39.6169 | 15883.7693 | 31786.769 | 47744.7803 | 63919.5371 | 80331.2063 | 96348.2501 | 111692.2739 | 126897.7848 | 141987.3279 | 156965.1027 | 172161.649
5 | Failure of 66kV Bus Tie Circuit Breakers | Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 499350.8009 | 572876.6019 | 617073.1634 | 650452.4173 | 673238.5544 | 690260.3766 | 705590.688 | 724794.9419 | 2.0592e-06 | 0.00026487 | 0.0045245 | 0.034102 | 0.16428 | 0.59587 | 1.764 | 4.4965 | 10.2699 | 21.509 | 41.9795 | 77.4673
[5 empty] | Transformers Risks |  |  | 40985.7898 | 52157.2261 | 62372.3959 | 73034.5144 | 0.9927 | 2.6292 | 4.7447 | 7.3539 | 10.4333 | 13.871 | 17.6879 | 22.1202 | 27.2627 | 33.2105 | 39.8111 | 47.1254 | 55.5128 | 65.1734 | 76.3205 | 89.4394
[5 empty] | Switchgear Risks |  |  | 1818973.9924 | 2062352.7471 | 2199722.9354 | 2300117.5766 | 2365330.9676 | 2412918.2216 | 2457188.4353 | 2517364.4181 | 118.8507 | 47651.3081 | 95360.3116 | 143234.3751 | 191758.7757 | 240994.2146 | 289046.5144 | 335081.3181 | 380703.6242 | 425983.4928 | 470937.2876 | 516562.4142
[5 empty] | Total |  |  | 1859959.7821 | 2114509.9732 | 2262095.3312 | 2373152.091 | 2365331.9603 | 2412920.8508 | 2457193.18 | 2517371.772 | 129.284 | 47665.1791 | 95377.9995 | 143256.4954 | 191786.0384 | 241027.4252 | 289086.3255 | 335128.4436 | 380759.137 | 426048.6662 | 471013.6081 | 516651.8537

## Option 5
|  |  | Items | Probability of Failure |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
|  |  | 1 | Failure of Transformers No.1 |  |  | 10.63% | 18.72% | 19.95% | 21.24% | 22.59% | 24.01% | 25.48% | 27.01% | 28.6% | 0.08252% | 0.1335% | 0.1785% | 0.2203% | 0.2604% | 0.2995% | 0.3382% | 0.3771% | 0.4164% | 0.4567% | 0.4983% | 0.5417%
|  |  | 2 | Failure of Transformers No.2 |  |  | 10.63% | 18.72% | 19.95% | 21.24% | 22.59% | 24.01% | 25.48% | 27.01% | 28.6% | 0.08252% | 0.1335% | 0.1785% | 0.2203% | 0.2604% | 0.2995% | 0.3382% | 0.3771% | 0.4164% | 0.4567% | 0.4983% | 0.5417%
|  |  | 3 | Failure of Transformers No.1 and No.2 |  |  | 1.13% | 3.506% | 3.982% | 4.513% | 5.105% | 5.762% | 6.491% | 7.296% | 8.182% | 6.81e-05% | 0.0001783% | 0.0003185% | 0.0004853% | 0.000678% | 0.0008969% | 0.001144% | 0.001422% | 0.001734% | 0.002086% | 0.002483% | 0.002934%
|  |  | 4 | Failure of 22kV Circuit Breaker |  |  | 74.33% | 75.25% | 75.8% | 76.34% | 76.87% | 0.005149% | 2.054% | 4.112% | 6.137% | 8.131% | 10.09% | 12.02% | 13.91% | 15.76% | 17.58% | 19.36% | 21.1% | 22.81% | 24.49% | 26.13% | 27.74%
|  |  | 5 | Failure of 66kV Circuit Breaker |  |  | 55.24% | 92.43% | 93.52% | 94.5% | 95.36% | 0.0001636% | 0.001851% | 0.00765% | 0.02094% | 0.04571% | 0.08652% | 0.1483% | 0.2366% | 0.3571% | 0.516% | 0.7196% | 0.9745% | 1.287% | 1.666% | 2.116% | 2.645%
Option 5 - Staged ZSS Redevelopment, Prioritising Switchgear and Protection Relay Replacement | [6 empty] | 2024: Years
Item | Fault Scenario | Risk | Assets Quantities | Event Probability | CoC | LoC | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
1 | Failure of Transformer No.1 and No.2 | Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 19.617 | 21.9811 | 23.1912 | 24.0071 | 24.4605 | 24.7413 | 24.9987 | 25.4267 | 25.8239 | 25.9507 | 25.9461 | 26.1082 | 26.382 | 26.7171 | 26.9011 | 26.9522 | 27.0236 | 27.1136 | 27.211 | 27.3792
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 40985.7898 | 52157.2261 | 62372.3959 | 73034.5144 | 83998.7491 | 95702.8647 | 108686.5532 | 123977.2102 | 1.048 | 2.7577 | 4.9245 | 7.551 | 10.6587 | 14.2807 | 18.3389 | 22.8353 | 27.9258 | 33.7033 | 40.2697 | 47.872
2 | Failure of Feeder Circuit Breaker | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 37.5254 | 15143.498 | 30626.189 | 46498.6105 | 62567.3443 | 78026.8335 | 92927.8408 | 108194.5851 | 123884.6446 | 139911.1572 | 155177.3015 | 169476.7497 | 183684.2491 | 197819.165 | 211860.1496 | 226269.7923
3 | Failure of Transformer Incomer Circuit Breakers | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 37.5254 | 15143.498 | 30626.189 | 46498.6105 | 62567.3443 | 78026.8335 | 92927.8408 | 108194.5851 | 123884.6446 | 139911.1572 | 155177.3015 | 169476.7497 | 183684.2491 | 197819.165 | 211860.1496 | 226269.7923
4 | Failure of 22kV Bus Tie Circuit Breakers | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 439874.3971 | 496492.0484 | 527549.924 | 549888.3864 | 37.5254 | 15143.498 | 30626.189 | 46498.6105 | 62567.3443 | 78026.8335 | 92927.8408 | 108194.5851 | 123884.6446 | 139911.1572 | 155177.3015 | 169476.7497 | 183684.2491 | 197819.165 | 211860.1496 | 226269.7923
5 | Failure of 66kV Bus Tie Circuit Breakers | Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39728.7588
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 9.8085 | 10.9905 | 11.5956 | 12.0035 | 12.2303 | 12.3706 | 12.4994 | 12.7134 | 12.9119 | 12.9754 | 12.973 | 13.0541 | 13.191 | 13.3586 | 13.4505 | 13.4761 | 13.5118 | 13.5568 | 13.6055 | 13.6896
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 499350.8009 | 572876.6019 | 617073.1634 | 650452.4173 | 1.9505e-06 | 0.00025252 | 0.0043593 | 0.033212 | 0.1608 | 0.57878 | 1.7013 | 4.3557 | 10.0261 | 21.1945 | 41.5014 | 76.2592 | 133.4762 | 224.1185 | 362.9042 | 570.5907
[5 empty] | Transformers Risks |  |  | 40985.7898 | 52157.2261 | 62372.3959 | 73034.5144 | 83998.7491 | 95702.8647 | 108686.5532 | 123977.2102 | 1.048 | 2.7577 | 4.9245 | 7.551 | 10.6587 | 14.2807 | 18.3389 | 22.8353 | 27.9258 | 33.7033 | 40.2697 | 47.872
[5 empty] | Switchgear Risks |  |  | 1818973.9924 | 2062352.7471 | 2199722.9354 | 2300117.5766 | 112.5763 | 45430.4943 | 91878.5714 | 139495.8648 | 187702.1938 | 234081.0792 | 278785.2238 | 324588.1111 | 371663.9598 | 419754.6661 | 465573.4059 | 508506.5082 | 551186.2236 | 593681.6135 | 635943.3529 | 679379.9677
[5 empty] | Total |  |  | 1859959.7821 | 2114509.9732 | 2262095.3312 | 2373152.091 | 84111.3254 | 141133.359 | 200565.1246 | 263473.0749 | 187703.2419 | 234083.8369 | 278790.1482 | 324595.6621 | 371674.6185 | 419768.9468 | 465591.7448 | 508529.3435 | 551214.1494 | 593715.3169 | 635983.6226 | 679427.8397

## Transformer PoF
Failures
| β | 0.96
| η | 5930
| β | 3.49
| η | 112
Retirements
| β | 0.57
| η | 467000
| β | 5.86
| η | 90.3
Asset Age | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150
Year start Actual | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116
Aust failures | 0% | 0.02388% | 0.0465% | 0.06884% | 0.09118% | 0.1138% | 0.1369% | 0.1607% | 0.1856% | 0.2116% | 0.2392% | 0.2686% | 0.3001% | 0.3339% | 0.3705% | 0.4102% | 0.4532% | 0.4999% | 0.5507% | 0.606% | 0.6661% | 0.7314% | 0.8023% | 0.8791% | 0.9624% | 1.052% | 1.15% | 1.255% | 1.368% | 1.489% | 1.62% | 1.759% | 1.909% | 2.069% | 2.239% | 2.421% | 2.614% | 2.819% | 3.037% | 3.267% | 3.511% | 3.769% | 4.041% | 4.327% | 4.628% | 4.945% | 5.278% | 5.626% | 5.992% | 6.374% | 6.773% | 7.19% | 7.625% | 8.079% | 8.55% | 9.041% | 9.551% | 10.08% | 10.63% | 11.2% | 11.78% | 12.39% | 13.02% | 13.67% | 14.34% | 15.03% | 15.74% | 16.47% | 17.22% | 17.99% | 18.78% | 19.59% | 20.42% | 21.27% | 22.14% | 23.03% | 23.94% | 24.87% | 25.81% | 26.77% | 27.75% | 28.75% | 29.76% | 30.79% | 31.83% | 32.89% | 33.96% | 35.05% | 36.15% | 37.25% | 38.38% | 39.51% | 40.65% | 41.79% | 42.95% | 44.11% | 45.28% | 46.46% | 47.64% | 48.82% | 50% | 51.19% | 52.37% | 53.56% | 54.74% | 55.92% | 57.09% | 58.27% | 59.43% | 60.59% | 61.74% | 62.88% | 64.02% | 65.14% | 66.25% | 67.35% | 68.44% | 69.51% | 70.57% | 71.61% | 72.63% | 73.64% | 74.64% | 75.61% | 76.56% | 77.5% | 78.42% | 79.31% | 80.19% | 81.04% | 81.87% | 82.68% | 83.47% | 84.24% | 84.99% | 85.71% | 86.41% | 87.09% | 87.74% | 88.38% | 88.99% | 89.58% | 90.14% | 90.69% | 91.21% | 91.72% | 92.2% | 92.66% | 93.1% | 93.52% | 93.93%
Aust retirement | 0% | 0.05866% | 0.08707% | 0.1097% | 0.1292% | 0.1468% | 0.1628% | 0.1778% | 0.1919% | 0.2052% | 0.218% | 0.2304% | 0.2423% | 0.254% | 0.2656% | 0.277% | 0.2885% | 0.3002% | 0.3122% | 0.3246% | 0.3377% | 0.3516% | 0.3665% | 0.3828% | 0.4007% | 0.4206% | 0.4427% | 0.4676% | 0.4956% | 0.5272% | 0.5631% | 0.6038% | 0.65% | 0.7023% | 0.7617% | 0.829% | 0.905% | 0.9908% | 1.088% | 1.196% | 1.318% | 1.455% | 1.608% | 1.778% | 1.968% | 2.178% | 2.411% | 2.669% | 2.953% | 3.266% | 3.61% | 3.986% | 4.398% | 4.847% | 5.337% | 5.869% | 6.447% | 7.072% | 7.748% | 8.476% | 9.261% | 10.1% | 11.01% | 11.97% | 13% | 14.1% | 15.27% | 16.51% | 17.82% | 19.2% | 20.66% | 22.2% | 23.81% | 25.5% | 27.26% | 29.09% | 31% | 32.97% | 35.01% | 37.12% | 39.28% | 41.5% | 43.76% | 46.07% | 48.41% | 50.78% | 53.18% | 55.58% | 57.99% | 60.39% | 62.78% | 65.14% | 67.48% | 69.77% | 72% | 74.18% | 76.29% | 78.33% | 80.28% | 82.14% | 83.9% | 85.57% | 87.13% | 88.59% | 89.94% | 91.18% | 92.32% | 93.36% | 94.29% | 95.13% | 95.87% | 96.53% | 97.1% | 97.6% | 98.03% | 98.4% | 98.71% | 98.97% | 99.18% | 99.36% | 99.5% | 99.62% | 99.71% | 99.78% | 99.84% | 99.88% | 99.91% | 99.94% | 99.96% | 99.97% | 99.98% | 99.99% | 99.99% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Aust both |  | 0.08252% | 0.1335% | 0.1785% | 0.2203% | 0.2604% | 0.2995% | 0.3382% | 0.3771% | 0.4164% | 0.4567% | 0.4983% | 0.5417% | 0.5871% | 0.6351% | 0.686% | 0.7404% | 0.7986% | 0.8612% | 0.9286% | 1.001% | 1.08% | 1.166% | 1.259% | 1.359% | 1.469% | 1.587% | 1.716% | 1.856% | 2.009% | 2.174% | 2.353% | 2.547% | 2.757% | 2.984% | 3.23% | 3.495% | 3.782% | 4.091% | 4.425% | 4.783% | 5.169% | 5.584% | 6.028% | 6.505% | 7.016% | 7.562% | 8.145% | 8.768% | 9.432% | 10.14% | 10.89% | 11.69% | 12.53% | 13.43% | 14.38% | 15.38% | 16.44% | 17.55% | 18.72% | 19.95% | 21.24% | 22.59% | 24.01% | 25.48% | 27.01% | 28.6% | 30.26% | 31.97% | 33.74% | 35.56% | 37.44% | 39.37% | 41.35% | 43.37% | 45.42% | 47.52% | 49.64% | 51.79% | 53.95% | 56.13% | 58.32% | 60.5% | 62.67% | 64.83% | 66.97% | 69.08% | 71.15% | 73.17% | 75.15% | 77.06% | 78.91% | 80.7% | 82.4% | 84.03% | 85.57% | 87.03% | 88.4% | 89.67% | 90.86% | 91.95% | 92.95% | 93.87% | 94.7% | 95.45% | 96.11% | 96.71% | 97.23% | 97.68% | 98.08% | 98.42% | 98.71% | 98.96% | 99.16% | 99.34% | 99.48% | 99.59% | 99.68% | 99.76% | 99.82% | 99.86% | 99.9% | 99.93% | 99.95% | 99.96% | 99.97% | 99.98% | 99.99% | 99.99% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%

## 66kV CB PoF
| β | 3.5
| η | 45
Asset Age | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82
Year start Actual | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
Probability of Failures | 0% | 0.0001636% | 0.001851% | 0.00765% | 0.02094% | 0.04571% | 0.08652% | 0.1483% | 0.2366% | 0.3571% | 0.516% | 0.7196% | 0.9745% | 1.287% | 1.666% | 2.116% | 2.645% | 3.26% | 3.967% | 4.773% | 5.685% | 6.707% | 7.845% | 9.104% | 10.49% | 12% | 13.64% | 15.41% | 17.31% | 19.33% | 21.49% | 23.76% | 26.16% | 28.66% | 31.27% | 33.96% | 36.74% | 39.59% | 42.5% | 45.45% | 48.43% | 51.42% | 54.41% | 57.38% | 60.32% | 63.21% | 66.04% | 68.79% | 71.45% | 74% | 76.45% | 78.77% | 80.96% | 83.02% | 84.94% | 86.71% | 88.35% | 89.85% | 91.2% | 92.43% | 93.52% | 94.5% | 95.36% | 96.11% | 96.76% | 97.33% | 97.81% | 98.22% | 98.56% | 98.85% | 99.09% | 99.28% | 99.44% | 99.56% | 99.67% | 99.75% | 99.81% | 99.86% | 99.89% | 99.92% | 99.94% | 99.96% | 99.97%

## 22kV CB PoF
Year | 1962 | 1963 | 1964 | 1965 | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Asset Age in Days in A1 year | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 365 | 366 | 365 | 365 | 365
days in service | 1 | 366 | 732 | 1097 | 1462 | 1827 | 2193 | 2558 | 2923 | 3288 | 3654 | 4019 | 4384 | 4749 | 5115 | 5480 | 5845 | 6210 | 6576 | 6941 | 7306 | 7671 | 8037 | 8402 | 8767 | 9132 | 9498 | 9863 | 10228 | 10593 | 10959 | 11324 | 11689 | 12054 | 12420 | 12785 | 13150 | 13515 | 13881 | 14246 | 14611 | 14976 | 15342 | 15707 | 16072 | 16437 | 16803 | 17168 | 17533 | 17898 | 18264 | 18629 | 18994 | 19359 | 19725 | 20090 | 20455 | 20820 | 21186 | 21551 | 21916 | 22281 | 22647 | 23012 | 23377 | 23742 | 24108 | 24473 | 24838 | 25203 | 25569 | 25934 | 26299 | 26664 | 27029 | 27395 | 27760 | 28125 | 28490 | 28855 | 29221 | 29586 | 29951 | 30316
failures per year | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Failure time (t) | 0.2 | 73.2 | 146.4 | 219.4 | 292.4 | 365.4 | 438.6 | 511.6 | 584.6 | 657.6 | 730.8 | 803.8 | 876.8 | 949.8 | 1023 | 1096 | 1169 | 1242 | 1315.2 | 1388.2 | 1461.2 | 1534.2 | 1607.4 | 1680.4 | 1753.4 | 1826.4 | 1899.6 | 1972.6 | 2045.6 | 2118.6 | 2191.8 | 2264.8 | 2337.8 | 2410.8 | 2484 | 2557 | 2630 | 2703 | 2776.2 | 2849.2 | 2922.2 | 2995.2 | 3068.4 | 3141.4 | 3214.4 | 3287.4 | 3360.6 | 3433.6 | 3506.6 | 3579.6 | 3652.8 | 3725.8 | 3798.8 | 3871.8 | 3945 | 4018 | 4091 | 4164 | 4237.2 | 4310.2 | 4383.2 | 4456.2 | 4529.4 | 4602.4 | 4675.4 | 4748.4 | 4821.6 | 4894.6 | 4967.6 | 5040.6 | 5113.8 | 5186.8 | 5259.8 | 5332.8 | 5405.8 | 5479 | 5552 | 5625 | 5698 | 5771 | 5844.2 | 5917.2 | 5990.2 | 6063.2
Median Rank | 7.5008e-06 | 0.0027453 | 0.0054905 | 0.0082283 | 0.010966 | 0.013704 | 0.016449 | 0.019187 | 0.021925 | 0.024662 | 0.027408 | 0.030146 | 0.032883 | 0.035621 | 0.038366 | 0.041104 | 0.043842 | 0.04658 | 0.049325 | 0.052063 | 0.0548 | 0.057538 | 0.060284 | 0.063021 | 0.065759 | 0.068497 | 0.071242 | 0.07398 | 0.076718 | 0.079455 | 0.082201 | 0.084938 | 0.087676 | 0.090414 | 0.093159 | 0.095897 | 0.098635 | 0.10137 | 0.10412 | 0.10686 | 0.10959 | 0.11233 | 0.11508 | 0.11781 | 0.12055 | 0.12329 | 0.12604 | 0.12877 | 0.13151 | 0.13425 | 0.13699 | 0.13973 | 0.14247 | 0.14521 | 0.14795 | 0.15069 | 0.15343 | 0.15617 | 0.15891 | 0.16165 | 0.16439 | 0.16712 | 0.16987 | 0.17261 | 0.17535 | 0.17808 | 0.18083 | 0.18357 | 0.1863 | 0.18904 | 0.19179 | 0.19452 | 0.19726 | 0.2 | 0.20274 | 0.20548 | 0.20822 | 0.21096 | 0.2137 | 0.21643 | 0.21918 | 0.22192 | 0.22465 | 0.22739
1/1-MR | 1 | 1.0028 | 1.0055 | 1.0083 | 1.0111 | 1.0139 | 1.0167 | 1.0196 | 1.0224 | 1.0253 | 1.0282 | 1.0311 | 1.034 | 1.0369 | 1.0399 | 1.0429 | 1.0459 | 1.0489 | 1.0519 | 1.0549 | 1.058 | 1.0611 | 1.0642 | 1.0673 | 1.0704 | 1.0735 | 1.0767 | 1.0799 | 1.0831 | 1.0863 | 1.0896 | 1.0928 | 1.0961 | 1.0994 | 1.1027 | 1.1061 | 1.1094 | 1.1128 | 1.1162 | 1.1196 | 1.1231 | 1.1265 | 1.13 | 1.1335 | 1.1371 | 1.1406 | 1.1442 | 1.1478 | 1.1514 | 1.1551 | 1.1587 | 1.1624 | 1.1661 | 1.1699 | 1.1736 | 1.1774 | 1.1812 | 1.1851 | 1.1889 | 1.1928 | 1.1967 | 1.2007 | 1.2046 | 1.2086 | 1.2126 | 1.2167 | 1.2207 | 1.2248 | 1.229 | 1.2331 | 1.2373 | 1.2415 | 1.2457 | 1.25 | 1.2543 | 1.2586 | 1.263 | 1.2674 | 1.2718 | 1.2762 | 1.2807 | 1.2852 | 1.2897 | 1.2943
ln(days in service) | 0 | 5.9026 | 6.5958 | 7.0003 | 7.2876 | 7.5104 | 7.693 | 7.847 | 7.9804 | 8.098 | 8.2036 | 8.2988 | 8.3857 | 8.4657 | 8.5399 | 8.6089 | 8.6733 | 8.7339 | 8.7912 | 8.8452 | 8.8965 | 8.9452 | 8.9918 | 9.0362 | 9.0787 | 9.1195 | 9.1588 | 9.1965 | 9.2329 | 9.2679 | 9.3019 | 9.3347 | 9.3664 | 9.3972 | 9.4271 | 9.456 | 9.4842 | 9.5116 | 9.5383 | 9.5642 | 9.5895 | 9.6142 | 9.6383 | 9.6619 | 9.6848 | 9.7073 | 9.7293 | 9.7508 | 9.7718 | 9.7924 | 9.8127 | 9.8325 | 9.8519 | 9.8709 | 9.8896 | 9.908 | 9.926 | 9.9437 | 9.9611 | 9.9782 | 9.995 | 10.0115 | 10.0278 | 10.0438 | 10.0595 | 10.075 | 10.0903 | 10.1053 | 10.1201 | 10.1347 | 10.1491 | 10.1633 | 10.1773 | 10.1911 | 10.2047 | 10.2181 | 10.2314 | 10.2444 | 10.2573 | 10.27 | 10.2826 | 10.2951 | 10.3073 | 10.3194
ln(ln(1/(1-MR))) | -11.8005 | -5.8965 | -5.202 | -4.796 | -4.5074 | -4.2832 | -4.0992 | -3.9439 | -3.8091 | -3.69 | -3.5831 | -3.4865 | -3.3981 | -3.3167 | -3.2411 | -3.1707 | -3.1048 | -3.0428 | -2.9841 | -2.9287 | -2.876 | -2.8258 | -2.7778 | -2.7319 | -2.6879 | -2.6457 | -2.6049 | -2.5658 | -2.528 | -2.4914 | -2.456 | -2.4218 | -2.3886 | -2.3563 | -2.3249 | -2.2945 | -2.2649 | -2.236 | -2.2078 | -2.1803 | -2.1535 | -2.1273 | -2.1017 | -2.0766 | -2.0521 | -2.0281 | -2.0046 | -1.9816 | -1.959 | -1.9369 | -1.9151 | -1.8937 | -1.8728 | -1.8522 | -1.8319 | -1.812 | -1.7924 | -1.7731 | -1.7541 | -1.7355 | -1.7171 | -1.699 | -1.6811 | -1.6635 | -1.6462 | -1.6291 | -1.6121 | -1.5955 | -1.5791 | -1.5628 | -1.5468 | -1.531 | -1.5154 | -1.4999 | -1.4847 | -1.4696 | -1.4547 | -1.44 | -1.4254 | -1.411 | -1.3967 | -1.3826 | -1.3687 | -1.3549
Beta(β) =@LINEST(G2:G75,F2:F75,True,False) | 1.0164
Intercept =@index(LINEST(G2:G75,F2:F75),2) | -11.8965
45.3894 | 16567.1279
total Failures in 75 years = 15 in a population of 158 | 15
PoF = 1-(1-Weibull.Dist( C2,$J$2,$L$2,TRUE)) | 0.005149% | 2.054% | 4.112% | 6.137% | 8.131% | 10.09% | 12.02% | 13.91% | 15.76% | 17.58% | 19.36% | 21.1% | 22.81% | 24.49% | 26.13% | 27.74% | 29.31% | 30.85% | 32.36% | 33.84% | 35.28% | 36.7% | 38.09% | 39.44% | 40.77% | 42.07% | 43.34% | 44.58% | 45.8% | 46.99% | 48.16% | 49.3% | 50.42% | 51.51% | 52.58% | 53.63% | 54.65% | 55.65% | 56.63% | 57.59% | 58.53% | 59.44% | 60.34% | 61.22% | 62.08% | 62.92% | 63.74% | 64.54% | 65.33% | 66.1% | 66.85% | 67.59% | 68.31% | 69.01% | 69.7% | 70.37% | 71.03% | 71.67% | 72.31% | 72.92% | 73.52% | 74.11% | 74.69% | 75.25% | 75.8% | 76.34% | 76.87% | 77.39% | 77.89% | 78.38% | 78.87% | 79.34% | 79.8% | 80.25% | 80.69% | 81.12% | 81.54% | 81.96% | 82.36% | 82.75% | 83.14% | 83.52% | 83.89% | 84.25%
Note: - The data here has been derived from available Jemena SAP data and based on existing fleet of 22kV Switchboards and total number of CBs in those boards. 158 Items and failure rate (based on industry norms) is 15 units in 75 years or 0.2 failures per annum ie 1 every 5 years on average. - The Weibull distribution scale factor values in the report, Review of Assets for Replacement of Substations within Jemena’s Network (VIC-JEM-008-R1¦V1.0), differ from this spreadsheet. The report’s calculation includes operating years up to year 2035, while this spreadsheet includes operating years up to year 2045. This affects the asset’s ‘characteristic life’ and decreases the Probability of Failure. These lower values have been used in the cost-benefits analysis and business case.