## Home
|  | Cost Benefit Analysis |  |  |  |  | Overall check: | Ok
|  | Home | Home | Home | Home | Home
Copyright Jemena Limited. Jemena is not liable for any loss caused by reliance on this document.
Project Details
| Project Name: |  | Distribution Transformer Replacement Model
| Project No: |  | [Please insert project number here]
| Start Date: |  | 2024-01-01
Table Of Contents & Checks
| Worksheet |  | Ref | Check | Description
| Home |  | 1 | Ok | Outlines project details, model checks and model structure
| Input¦Costs |  | 2 | Ok | Inputs project cost and benefit information
| Input¦Benefits |  | 3 | Ok | Outputs the summary of costs and benefits of each option
| Input¦Transf_Failures |  | 4 | Ok | Outputs the summary of costs and benefits of each option
| Output¦Tables |  | 4 | Ok | Outputs the options analysis for the business case
Model Key Legend
| Model key |  |  | Description
| Input |  | ---------> | Input assumption (hardcode)
| Internal link |  | ---------> | Internal link (different sheet within the model)
| Drop-down |  | ---------> | Choose from a drop-down list
| Calculation |  | ---------> | Calculation (general formula driven)
Version control
| Version | Person |  | Date | Sheet | Comment
| v1.0 | George Tziokas |  | 2025-11-18 | All | Initial model development
v2.0
v3.0
v4.0
v4.1
End

## Input¦Costs
|  | Cost Benefit Analysis | [5 empty] | Section Check: | Ok |  | Overall Check: | Ok |  | Legend: | Input | Internal | Select | Calculation
Input¦Costs
[8 empty] | Year Display | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total
|  |  | Option | Unit | Basis | Asset |  | Start Year | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Copyright Jemena Limited. All rights reserved. Jemena is not liable for any loss caused by reliance on this document.
Input ¦ Options
|  | Option | Option | Unit | Basis |  | Short description | Detailed Description / Objectives | 2028: Benefits Delivered
|  | Option 1 - Do nothing | Option 1 | n/a | n/a |  | Do nothing | [Insert description of status quo] | 2028: n/a
|  | Option 2 - Replacement based on historical trend | Option 2 | n/a | n/a |  | Replacement based on historical trend | Replacement levels to maintain network performance and reliability and meet compliance obligations | 2028: Replacement levels to maintain network performance and reliability and meet compliance obligations
|  | Option 3 - Option 2 plus additional 20% opportunistic replacement | Option 3 | n/a | n/a |  | Option 2 plus additional 20% opportunistic replacement | Replacement levels to increase network performance and reliability | 2028: Replacement levels to increase network performance and reliability
|  | Option 4 - [Insert short option description] | Option 4 | n/a | n/a |  | [Insert short option description] | [Insert detailed option description or objectives] | 2028: [Describe benefits delivered through this option]
|  | Option 5 - [Insert short option description] | Option 5 | n/a | n/a |  | [Insert short option description] | [Insert detailed option description or objectives] | 2028: [Describe benefits delivered through this option]
Summary
Forecast Capex
|  | Forecast Capex | Option | Unit | Basis | Code | Source |  | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total
|  | Option 1 - Do nothing | Option 1 | Volume | n/a | n/a | Calculated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Option 2 - Replacement based on historical trend | Option 2 | Volume | n/a | n/a | Capex model submitted to the AER |  | 1552366.0509 | 1495364.2608 | 1954659.0913 | 2056981.2975 | 2056981.2975 | 2056981.2975 | 2056981.2975 | 10182584.2813
|  | Option 3 - Option 2 plus additional 20% opportunistic replacement | Option 3 | Volume | n/a | n/a | Capex model submitted to the AER |  | 1862839.2611 | 1794437.113 | 2345590.9095 | 2468377.557 | 2468377.557 | 2468377.557 | 2468377.557 | 12219101.1375
Option 2 - Replacement based on historical trend
Unit Costs
|  | Unit Costs | Option | Unit | Basis | MATT code |  | Unit Costs
|  | Kiosk Refurbishment | Option 2 | Dollars | Real 2024 | RHM |  | 11367.0465
|  | Trans Ground/Indoor Repl | Option 2 | Dollars | Real 2024 | RHD |  | 44600.0408
|  | Trans Pole Mounted Repl | Option 2 | Dollars | Real 2024 | RHA |  | 25280.9308
|  | Transformer/Subs Kiosk Repl | Option 2 | Dollars | Real 2024 | RHK |  | 118945.7045
|  | Indoor/Kiosk Switch Repl | Option 2 | Dollars | Real 2024 | RHE |  | 102322.2062
|  | [Spare] | Option 2 | Dollars | Real 2024 | [Spare] |  | 0
Historical Volumes
|  | Historical Volumes | Option | Unit | Basis | Code | Source | Unique code | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total
|  | Kiosk Refurbishment | Option 2 | Volume | n/a | RHM | Capex model submitted to the AER | A108 | 6.0729 | 6 | 6 | 6 | 6 | 6 | 6 | 30
|  | Trans Ground/Indoor Repl | Option 2 | Volume | n/a | RHD | Capex model submitted to the AER | A243 | 9.6093 | 8.302 | 9 | 9 | 9 | 9 | 9 | 45
|  | Trans Pole Mounted Repl | Option 2 | Volume | n/a | RHA | Capex model submitted to the AER | A140 | 28.2643 | 32.396 | 32 | 32 | 32 | 32 | 32 | 160
|  | Transformer/Subs Kiosk Repl | Option 2 | Volume | n/a | RHK | Capex model submitted to the AER | A148 | 2 | 2 | 3.9633 | 3.9633 | 3.9633 | 3.9633 | 3.9633 | 19.8167
|  | Indoor/Kiosk Switch Repl | Option 2 | Volume | n/a | RHE | Capex model submitted to the AER | A143 | 1 | 0 | 2 | 3 | 3 | 3 | 3 | 14
|  | [Spare] | Option 2 | Volume | n/a | [Spare] | Capex model submitted to the AER | [Spare] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | Option 2 | Volume | n/a | n/a | Calculated |  | 46.9464 | 48.698 | 52.9633 | 53.9633 | 53.9633 | 53.9633 | 53.9633 | 268.8167
Replacement Expenditure
|  | Replacement Expenditure | Option | Unit | Basis | Code | Source |  | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total
|  | Replace Metal Trifurcating Boxes | Option 2 | Dollars | Real 2024 | n/a | Capex model submitted to the AER |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Option 2 plus additional 20% opportunistic replacement
Historical Volumes
|  | Option 3 Adjustment Factor | Option | Unit | Basis | Code | Source
|  | Option 3 Adjustment Factor | Option 3 | % | n/a | n/a | Source | 20%
|  | Volumes | Option | Unit | Basis | Code | Source | Unique code | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total
|  | Kiosk Refurbishment | Option 3 | Volume | n/a | n/a | Capex model submitted to the AER | A108 | 7.2874 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 36
|  | Trans Ground/Indoor Repl | Option 3 | Volume | n/a | n/a | Capex model submitted to the AER | A243 | 11.5311 | 9.9624 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 54
|  | Trans Pole Mounted Repl | Option 3 | Volume | n/a | n/a | Capex model submitted to the AER | A140 | 33.9171 | 38.8752 | 38.4 | 38.4 | 38.4 | 38.4 | 38.4 | 192
|  | Transformer/Subs Kiosk Repl | Option 3 | Volume | n/a | n/a | Capex model submitted to the AER | A148 | 2.4 | 2.4 | 4.756 | 4.756 | 4.756 | 4.756 | 4.756 | 23.78
|  | Indoor/Kiosk Switch Repl | Option 3 | Volume | n/a | n/a | Capex model submitted to the AER | A143 | 1.2 | 0 | 2.4 | 3.6 | 3.6 | 3.6 | 3.6 | 16.8
|  | [Spare] | Option 3 | Volume | n/a | n/a | Capex model submitted to the AER | [Spare] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | Option 3 | Volume | n/a | n/a | Calculated |  | 56.3357 | 58.4376 | 63.556 | 64.756 | 64.756 | 64.756 | 64.756 | 322.58
Replacement Expenditure
|  | Replacement Expenditure | Option | Unit | Basis | Code | Source |  | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total
|  | Replace Metal Trifurcating Boxes | Option 2 | Dollars | Real 2024 | n/a | Capex model submitted to the AER |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
End

## Input¦Benefits
|  |  | Cost Benefit Analysis | [5 empty] | Section Check: | Ok |  | Overall Check: | Ok |  | Legend: | Input | Internal | Select | Calculation
Input¦Benefits
[9 empty] | Year Display | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total
|  |  |  | Option | Unit | Basis | Asset |  | Start Year | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Copyright Jemena Limited. All rights reserved. Jemena is not liable for any loss caused by reliance on this document.
Benefits
Option 2 - Replacement based on historical trend
|  |  | Category | Option | Unit | Basis | Source
|  |  | Average of Outage Duration (minutes) | Option 2 | Minutes | n/a | Source |  | 333.2384
|  |  | Minutes in Hour | Option 2 | Minutes | n/a | n/a |  | 60
|  |  | Average of Outage Duration (Hours) | Option 2 | Minutes | n/a | Source |  | 5.554
|  |  | Average number of customers per outage caused by S/S fault | Option 2 | # | n/a | Source |  | 436.2727
|  |  | Total Duration (Hours) | Option 2 | Hours | n/a | Source |  | 2423.0473
|  |  | % Split between Categories | Option | Unit | Basis | Source |  | % Split
|  |  | Residential | Option 2 | % | n/a | Source |  | 80%
|  |  | Commercial | Option 2 | % | n/a | Source |  | 15%
|  |  | Industrial | Option 2 | % | n/a | Source |  | 5%
0 |  |  | Total % | Option 2 | % | n/a | Source |  | 100%
|  |  | kW per Hour | Option | Unit | Basis | Source |  | kWh p.a. | 2024: Hours per Year; 2025: kW per Hour
|  |  | Residential | Option 2 | Mixed | n/a | Source |  | 6100 | 2024: 8760; 2025: 0.69635
|  |  | Commercial | Option 2 | Mixed | n/a | Source |  | 14600 | 2024: 8760; 2025: 1.6667
|  |  | Industrial | Option 2 | Mixed | n/a | Source |  | 146000 | 2024: 8760; 2025: 16.6667
|  |  | 2025 VCR - $/kWh | Option | Unit | Basis | Source |  | $/kWh
|  |  | Residential | Option 2 | $/kWh | Real 2024 | AER VCR Final Report |  | 54.4084 | 2025: Check Dollar Basis
|  |  | Commercial | Option 2 | $/kWh | Real 2024 | AER VCR Final Report |  | 34.39 | 2025: Check Dollar Basis
|  |  | Industrial | Option 2 | $/kWh | Real 2024 | AER VCR Final Report |  | 33.49 | 2025: Check Dollar Basis
|  |  | VCR Calculation | Option | Unit | Basis | Source |  | kWh | 2024: VCR per Outage
|  |  | Residential | Option 2 | Mixed | n/a | Source |  | 1349.8254 | 2024: 73441.865
|  |  | Commercial | Option 2 | Mixed | n/a | Source |  | 605.7618 | 2024: 20832.1489
|  |  | Industrial | Option 2 | Mixed | n/a | Source |  | 2019.2061 | 2024: 67623.2109
|  |  | Total VCR per Outage | Option 2 | $ | Real 2024 | Calculated |  |  | 2024: 161897.2248
|  |  | Historical Fault Levels | Option | Unit | Basis | Source |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2023
|  |  | Pole Transformer Failures | Option 2 | # | n/a | Source |  | 12 | 15 | 15 | 7 | 14 | 20
|  |  | Non-pole Sub Failures | Option 2 | # | n/a | Source |  | 7 | 4 | 9 | 0 | 1 | 10
|  |  | Total Fault Levels | Option 2 | # | n/a | Calculated |  | 19 | 19 | 24 | 7 | 15 | 30
|  |  | Average Fault Levels 2020-2023 | Option 2 | # | n/a | Calculated |  | 19 | 2024: Fault levels based on historical inspection / condition replacement
|  |  | Estimated Fault Levels & Savings | Option | Unit | Basis | Source
|  |  | Option 2 2027-28 Volume | Option 2 | Volume | n/a | Source |  | 53.9633
|  |  | % Averted | Option 2 | % | n/a | Source |  | 40% | 2024: Option 2: Assume that we will avert 2/5 of faults due to continuing replacement at historical inspection / condition replacement levels
|  |  | Estimated number of faults averted pa | Option 2 | # | n/a | Calculated |  | 13.9853 | 2024: Estimated Fault Levels
|  |  | Cost of expected unserved energy pa | Option 2 | $ | Real 2024 | Calculated |  | 2264187.0741
|  |  | Reg Period | Option 2 | Years | n/a | Input |  | 5
|  |  | Cost of expected unserved energy over 5 years | Option 2 | $ | Real 2024 | Calculated |  | 11320935.3706
Option 3 - Option 2 plus additional 20% opportunistic replacement
|  |  | Historical Volume | Option | Unit | Basis | Source |  | Unique code | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total |  | Risks identified and quantified per scenario (include the assumptions used and show formula in calculating the risks)
|  |  | Kiosk Refurbishment | Option 2 | Volume | n/a | Capex model submitted to the AER |  | A108 | 6.0729 | 6 | 6 | 6 | 6 | 6 | 6 | 30 |  | Sometimes kiosks are taken out of service before end of life,e.g. due to customer request for capacity increase. In this case they may be refurbished and returned to the store to be used for other projects. The alternative option is to scrap these and buy new ones instead, which is a higher cost option. Need to know refurbishment cost vs cost of new kiosk to compare these options.
|  |  | Trans Ground/Indoor Repl | Option 2 | Volume | n/a | Capex model submitted to the AER |  | A243 | 9.6093 | 8.302 | 9 | 9 | 9 | 9 | 9 | 45 |  | These often supply single large customers like factories or apartment towers and can't be back-fed. These customers would be permanently off supply. Not an option, this is a loss of licence situation.
|  |  | Trans Pole Mounted Repl | Option 2 | Volume | n/a | Capex model submitted to the AER |  | A140 | 28.2643 | 32.396 | 32 | 32 | 32 | 32 | 32 | 160 |  | Typically these are run to failure and replaced once they have failed. LV networks are designed without redundancy. We may be able to backfeed some customers at times of lower demand but many customers would be off supply during high demand periods. This would assume we had the resources for the switching required to change network configuration depending on the weather. Not replacing failed pole mounted tx is not really a feasible option. Absolute best case scenario assume 100 customers per sub off for 12 hours per day on the 10 hottest days of the year. 4.5kW per cust. $2.6M cost of unserved energy per year, every year for each failed transformer. Plus GSL penalty costs. And likely loss of licence.
|  |  | Transformer/Subs Kiosk Repl | Option 2 | Volume | n/a | Capex model submitted to the AER |  | A148 | 2 | 2 | 3.9633 | 3.9633 | 3.9633 | 3.9633 | 3.9633 | 19.8167 |  | Same as pole subs above
|  |  | Indoor/Kiosk Switch Repl | Option 2 | Volume | n/a | Capex model submitted to the AER |  | A143 | 1 | 0 | 2 | 3 | 3 | 3 | 3 | 14 |  | Same as for subs above, if this is failed then we can't supply customers from the sub. Must be replaced.
|  |  | [Spare] | Option 2 | Volume | n/a | Capex model submitted to the AER |  | [Spare] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Total | Option 2 | Volume | n/a | Capex model submitted to the AER |  |  | 46.9464 | 48.698 | 52.9633 | 53.9633 | 53.9633 | 53.9633 | 53.9633 | 268.8167
|  |  | Volume for option 3 (20% more than option 2) | Option | Unit | Basis | Source |  | Unique code | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total
|  |  | Kiosk Refurbishment | Option 3 | Volume | n/a | Calculated |  | A108 | 7.2874 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 36
|  |  | Trans Ground/Indoor Repl | Option 3 | Volume | n/a | Calculated |  | A243 | 11.5311 | 9.9624 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 54
|  |  | Trans Pole Mounted Repl | Option 3 | Volume | n/a | Calculated |  | A140 | 33.9171 | 38.8752 | 38.4 | 38.4 | 38.4 | 38.4 | 38.4 | 192
|  |  | Transformer/Subs Kiosk Repl | Option 3 | Volume | n/a | Calculated |  | A148 | 2.4 | 2.4 | 4.756 | 4.756 | 4.756 | 4.756 | 4.756 | 23.78
|  |  | Indoor/Kiosk Switch Repl | Option 3 | Volume | n/a | Calculated |  | A143 | 1.2 | 0 | 2.4 | 3.6 | 3.6 | 3.6 | 3.6 | 16.8
|  |  | [Spare] | Option 3 | Volume | n/a | Calculated |  | [Spare] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Total | Option 3 | Volume | n/a | Calculated |  |  | 56.3357 | 58.4376 | 63.556 | 64.756 | 64.756 | 64.756 | 64.756 | 322.58
|  |  | Estimated Fault Levels & Savings | Option | Unit | Basis | Source |  | % Averted
|  |  | Option 2 2027-28 Volume | Option 3 | Volume | n/a | Source |  | 64.756
|  |  | % Averted | Option 3 | % | n/a | Source |  | 40% | 2024: Option 3: Assume that we will avert 2/5 of transformer failures due to continuing replacement at historical inspection / condition replacement levels
|  |  | Estimated number of faults averted pa | Option 3 | # | n/a | Calculated |  | 18.3024 | 2024: Estimated Fault Levels
|  |  | Cost of expected unserved energy pa | Option 3 | $ | Real 2024 | Calculated |  | 2963108.2706
|  |  | Period | Option 3 | Years | n/a | Input |  | 4
|  |  | Cost of expected unserved energy over 5 years | Option 3 | $ | Real 2024 | Calculated |  | 11852433.0823 | 2024: Cost of expected unserved energy is captured over 4 years to refelect the additional time required for replacement
End
|  |  | Option 2 - Replacement based on historical trend | Option | Unit | Basis | MATT code |  | Option 2 - Replacement based on historical trend
|  |  | HV U/G Cable Replacement | #REF! | Dollars | Real 2024 | RUA |  | 495.7045
|  |  | LV U/G Cable Replacement | #REF! | Dollars | Real 2024 | RUC |  | 620.9524
|  |  | Pillar to Pillar | #REF! | Dollars | Real 2024 | RUF |  | 6511.7807
|  |  | HV U/G Termination Replacement | #REF! | Dollars | Real 2024 | RUH |  | 16991.4222
|  |  | LV U/G Termination Replacement | #REF! | Dollars | Real 2024 | RUL |  | 10501.5786
|  |  | Replace Metal Trifurcating Boxes | #REF! | Dollars | Real 2024 | RUA |  | 0
|  |  | [Spare] | #REF! | Dollars | Real 2024 | [Select from list] |  | 0
|  |  | [Spare] | #REF! | Dollars | Real 2024 | [Select from list] |  | 0
|  |  | [Spare] | #REF! | Dollars | Real 2024 | [Select from list] |  | 0
|  |  | [Spare] | #REF! | Dollars | Real 2024 | [Select from list] |  | 0
Historical Volumes
|  |  | Historical Volumes | Option | Unit | Basis | Code | Source | Unique code | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total
|  |  | HV U/G Cable Replacement | #REF! | Volume | n/a | RUA | Capex model submitted to the AER | A208 | 37.6857 | 42.8 | 327.9 | 321.3 | 327.9 | 321.3 | 327.9 | 1626.3
|  |  | LV U/G Cable Replacement | #REF! | Volume | n/a | RUC | Capex model submitted to the AER | A210 | 179.0071 | 203.9 | 200 | 200 | 200 | 200 | 200 | 1000
|  |  | Pillar to Pillar | #REF! | Volume | n/a | RUF | Capex model submitted to the AER | A211 | 5 | 5.39 | 5 | 5 | 5 | 5 | 5 | 25
|  |  | HV U/G Termination Replacement | #REF! | Volume | n/a | RUH | Capex model submitted to the AER | A239 | 23.5536 | 23.81 | 20 | 20 | 20 | 20 | 20 | 100
|  |  | LV U/G Termination Replacement | #REF! | Volume | n/a | RUL | Capex model submitted to the AER | A213 | 42.3964 | 47.16 | 45 | 45 | 45 | 45 | 45 | 225
|  |  | Replace Metal Trifurcating Boxes | #REF! | Volume | n/a | RUA | Capex model submitted to the AER | A209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | [Spare] | #REF! | Volume | n/a | [Select from list] | Capex model submitted to the AER | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | [Spare] | #REF! | Volume | n/a | [Select from list] | Capex model submitted to the AER | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | [Spare] | #REF! | Volume | n/a | [Select from list] | Capex model submitted to the AER | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | [Spare] | #REF! | Volume | n/a | [Select from list] | Capex model submitted to the AER | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 287.6429 | 323.06 | 597.9 | 591.3 | 597.9 | 591.3 | 597.9 | 2976.3
Replacement Expenditure
|  |  | Replacement Expenditure | Option | Unit | Basis | Code | Source |  | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total
|  |  | Replace Metal Trifurcating Boxes | #REF! | Dollars | Real 2024 | n/a | Capex model submitted to the AER |  | 387979.1732 | 0 | 0 | 1216459.3501 | 853666.7401 | 883175.2626 | 394408.1723 | 3347709.5251
|  |  | [Spare] | #REF! | Dollars | Real 2024 | n/a | Capex model submitted to the AER |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | [Spare] | #REF! | Dollars | Real 2024 | n/a | Capex model submitted to the AER |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | [Spare] | #REF! | Dollars | Real 2024 | n/a | Capex model submitted to the AER |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | [Spare] | #REF! | Dollars | Real 2024 | n/a | Capex model submitted to the AER |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs ¦ Sensitivity (Apply to all options)
Customer ¦ Customer benefits overestimate
|  |  | Customer benefits overestimate (%) | Option | Unit | Basis |  | Sensitivity
|  |  | Overestimate by | All | #NAME? | #NAME? |  | 10%
End

## Input¦Transf_Failures
|  | Cost Benefit Analysis | [5 empty] | Section Check: | Ok |  | Overall Check: | Ok |  | Legend: | Input | Internal | Select | Calculation
Input¦Transf_Failures
[8 empty] | Year Display | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total
|  |  | Option | Unit | Basis | Asset |  | Start Year | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Copyright Jemena Limited. All rights reserved. Jemena is not liable for any loss caused by reliance on this document.
Transformer Failures
Transformer Failures
|  | displayID | feeder | Feeder with no space | jcf_primary_cause | Average of CMOS | Average of Outage Duration (minutes) | Sum of voltage | Average of totalAffected | substation | nominalFeeder | jobtypeText | addr | jcf_deviceAffected | jcf_equipment | jcf_interrupting_device | networkModelExternalID | networkModelName | nominalSubstation | notes | Sum of totalAffectedLoads
|  | J.21.0036662 | SBY23 | SBY23 | Asset - Electrical Failure | 2576.4 | 286.2667 | 22 | 9 | Sunbury (SBY) | SBY23 | Outage | 105 SPAVIN DRIVE SUNBURY VIC 3429 |  | Distr - Transformer | HV Fuse Operation | HVSW_36440610 | 595570 | Sunbury (SBY) | SUSPECT SPAVIN DVE P12 TX HAS FAILED, REPLACED WITH 100KVA S/STN (LIKE FOR LIKE). OSI PM NUMBER DID NOT WORK OUT SO RAISED IN SAP PM # 5174596 a/p 81373 issued by kevin karash @ 2050 CANCELLED 2215. see OIW 75274 | 7
|  | J.22.0065283 | PTN11 | PTN11 | Asset - Electrical Failure | 43837 | 185.75 | 22 | 236 | Preston (PTN) | PTN11 | Outage | U 1 , 27 SYLVESTER GROVE PRESTON VIC 3072 |  | Distr - Transformer | HV Fuse Operation | HVSW_30193724 | 680590 | Preston (PTN) | REPLACING 500KVA 22KV KITCHENER-MURRAY S/STN- LEAKING SIGNIFICANT AMOUNT OF OIL. @ 09:30 SUB PLACED UNDER LV // 1. SYLVERSTER EAST PLENTY 2. KITCHENER NTH SYLVESTER 3. MURRAY WEST DEAN. 4. HILL NTH GOWER IN HAND WITH M.BODDY TO CLEAN UP. SAFE TO REPLACE WITH OUT ISOLATING HV LV EAP #95001 ISSUED BY TIM SCHIPPER @10:45 @10:40 KITCHENER-MURRY S/STN - KITCHENER N GREGORY E & KITCHENER S MURRY S CCT LV BUS FUSE OPEN TO ALLOW ACCESS TO BUS FOR TX REPLACEMENT LV EAP #95001 CANCELLED BY PAUL JORDAN @13:00 HV FUSES @ KITCHENER-MURRY S/STN CLOSED @ 13:15 TEST VLOTS @ 13:20 POL @ 13:22 REMOVE LV // @ 13:46 CR-001680 TX CHANGED LIKE FOR LIKE | 221
|  | J.22.0066040 | FW 05 | FW05 | Asset - Electrical Failure | 24799.429633333333 | 164.2346 | 22 | 151 | Footscray West (FW) | FW 05 | Outage | 37 URWIN STREET YARRAVILLE VIC 3013 |  | Distr - Transformer | Emergency Switching | HVSW_10673104 | 300130 | Footscray West (FW) | Crew found blue phase LV lead at Angliss-Adeney burnt out. White phase is showing signs of heat also. Sub has an oil leak and in need of some TLC. LV //s installed and substation isolated LV and HV to confirm damage. Crew to split bus and install //'s. LV //'s - 1. Francis West Urwin, 2.Adeney West Urwin, 3. Urwin Nth Adeney, 4. Ballard Nth Adeney. Tie bus again. DAO contacted and substation will be replaced in next couple of days. OI 79562 WRITTEN FOR THIS. | 144
|  | J.22.0070222 | NH 08 | NH08 | Asset - Electrical Failure | 36593.70341666667 | 323.8381 | 22 | 113 | North Heidelberg (NH) | NH 08 | Outage | 14 FAIRBANK WAY VIEW BANK VIC 3084 |  | Distr - Transformer |  | HVSW_11081236 | 17222 | North Heidelberg (NH) | Operator Sam Sozzi reports 3 x HV 15A BA fuses operated at #17222 to The Glade 15-Sherlowe s/stn. Also found LV fuses operated on the blue & white phases on the "Fairbank S Martins SW" street cct. D/O arranging U/G Crew & bucket for earthing to issue SFT on cable. **We will need to organise Testers** LV //'s installed (customers on @ 10:56am) & dressed in GIS - 1. Eugene sth Lower Plenty 2. Castleton cnr Bannockburn 3. Martins east Henderson 4. Rainsford west Eugene Transformer kiosk appears ok, so potential HV cable fault. Sub isolated LV & HV. Tester will organise another tested to be in attendance Mon 21/11 to be done under faults teester to attend 23/11/22 to do SFT on cable. A/P# 91563 @ 2235. CANCELLED 2320 M.BLESZCZ OPENED 10439 AT 1700 23/11/22 FOR EARTHING AND WILL CALL WITH A SFT# 6124 @ 18:00. Cancelled @ 20:00. M.Bleszcz advised that the HV cable & TX needs replacing. In hand with D/O. 24/11/22 - M. Bleszcz has issued AP 91565 @17:40. Cancelled AT 1525 3x Xarms replaced line still isolated due to u/g cable fault and tx fault job with maintenace planners to replace kiosk | 54
|  | J.23.0072354 | FF 96 | FF96 | Asset - Electrical Failure | 17394.5232 | 187.0379 | 6.6 | 93 | Fairfield (FF) | FF 96 | Outage | 116A FULHAM ROAD ALPHINGTON VIC 3078 |  | Distr - Transformer | HV Fuse Operation | HVSW_10659546 | 401180 | Fairfield (FF) | 40E - Crew found 2x HV fuses blown, // installed to restore customers @14:00 Operator inspected transformer and it looked okay. Changed 2 x blown fuses and activated substation. Substation failed and fuses operated again. Substation was isolated HV and DAO advised. OI 80464 PM1334415 | 93
|  | J.23.0073166 | KLO22 | KLO22 | Asset - Electrical Failure | 1892.1511333333333 | 473.0378 | 22 | 4 | Kalkallo (KLO) | KLO22 | Outage | 10 KINLOCH COURT CRAIGIEBURN VIC 3064 |  | Distr - Transformer | HV Fuse Operation | HVSW_10588102 | 103750 |  | CREW FOUND SPUR FUSE 17337 OPERATED AS WELL AS BLUE PH HV FUSE @ KINLOCH CRT-P3 S/STN. @10:15 CREW REPLACED 15E BA SPUR FUSE 17337 AND TESTED TX. TX REQUIRES REPLACEMENT POSSIBLY CAUSE FROM COO STRESS TESTING YESTERDAY 20/01/23 @10:20 KINLOCH CRT-P3 S/STN ISOLATED HV & LV TO REPLACE TX @13:40 EAP #88922 ISSUED BY GEORGE TIOULIS TO REPLACE TX @15:00 EAP #88922 CANCELLED @15:15 KINLOCH SRT-P3 S/STN - ACTIVATED, PH ROTATION & POL NOTE: KINLOCH SRT-P3 S/STN UPGRADED FROM 63KVA TO 100KVA AS NO 63KVA TX AVAILABLE...... CR--001942 PM ORDER #5189178 | 3
|  | J.23.0075727 | PV 22 | PV22 | Asset - Electrical Failure | 12273.391883333334 | 88.2978 | 11 | 139 | Pascoe Vale (PV) | PV 22 | Outage | 31 LEBANON STREET ESSENDON NORTH VIC 3041 |  | Distr - Transformer | Emergency Switching | HVSW_10549960 | 224270 | Pascoe Vale (PV) | LV leads on transformer are melted and need replacing. LV//'s installed to restore customers while making repairs. 1. Lebanon cnr Roslyn 2. Roslyn anr Peck 3. Wilonga N/W Lebanon. 4. Melissa S/W Mascoma @2214 LV Bus was isolated as it needs to be rehashed. Cust at #48 Lebanon is shown as being connected pole to pit outside bus, but is actually inside the bus and was off supply from approx. 2303 to 0119 East side bus isols closed to energise. LEBANON-FENACRE S/STN needs to be replaced. HV earth has been left on and connected to the bottom contacts of the hv fuse units. INSTRUCTION 81006 Crew replaced S/stn with New 500 KVA sub and installed N 40 E ba fuses. Change Request raised CR-002031 | 114
|  | J.24.0090571 | COO12 | COO12 | Asset - Electrical Failure | 47917.643533333336 | 118.0435 | 22 | 957 | Coolaroo (COO) | COO12 | Outage | COO12 FDR CB - COO12 - - MICKLEHAM, SUNBURY, BULLA, YUROKE, DIGGERS REST, OAKLANDS JUNCTION, CLARKEFIELD, ATTWOOD, WILDWOOD, GREENVALE, MELBOURNE AIRPORT, WESTMEADOWS, |  | Distr - Transformer | CB Reclose & Open to Lockout | STSW_10328609 | COO12 FDR CB | Coolaroo (COO) | COO12 OPENED TO LOCKOUT AT 1808. ALL CUSTOMERS RESTORED AT 1858 SEE INSTR 83349 CAUSE = AT OAKLANDS RD-P32E2 THE S/STN HAD FAILED. WHEN THE CREW ATTEMPTED TO CLOSE IN THE HV FUSES COO12 OPENED TO LOCKOUT. IN HAND TO HAVE S/STN REPLACED BY KEITH FRASER 5198282 | 834
|  | J.24.0093890 | SHM21 | SHM21 | Asset - Electrical Failure | 597603.2333333333 | 266.7 | 22 | 4526 | Sydenham (SHM) | SHM21 | Outage | SHM21 FDR CB - SHM21 - - TAYLORS LAKES, HILLSIDE, CAROLINE SPRINGS, SYDENHAM, TAYLORS HILL, |  | Distr - Transformer | CB Reclose & Open to Lockout | STSW_20344369 | SHM21 FDR CB | Sydenham (SHM) | SUSPECT CABLE FAULT. THIS PROVED TO BE WRONG AND DUNDEE-MEADE TRANSFORMER HAS FAILED. SECTION ISOLATED AND CUSTOMERS RESTORED VIA LV // FOR DUNDEE-MEADE. ALL OTHER CUSTOMERS OFF SHM21 RESTORED VIA FAULT SWITCHING. SEE OI 83833 | 4208
|  | J.24.0094045 | FW 13 | FW13 | Asset - Electrical Failure | 1311.6658 | 1311.6658 | 22 | 1 | Footscray West (FW) | FW 13 | Outage | 11302 - FW 13 - - YARRAVILLE, |  | Distr - Transformer | Emergency Switching | HVSW_20705690 | 11302 | Footscray West (FW) | UGC was repaired and pressure tested, but Transformer need replacing. Blew two 31.5A PF fuses on energising Trans a/p 95162 issued @1407 by M Bleszcz gas swich 11302 checked open and tagged. A/P 95162 cancelled at 2135, SFT 7752 issued at 2140 and cancelled at 2305. A/P 95164 issued at 2310 and cancelled at 2340.. | 1
|  | J.24.0094391 | COO12 | COO12 | Asset - Electrical Failure | 2307.733333333333 | 42.7667 | 22 | 54 | Coolaroo (COO) | COO12 | Outage | 11293 - COO12 - - BULLA, GREENVALE, OAKLANDS JUNCTION, |  | Distr - Transformer | Emergency Switching | HVSW_30871084 | 11293 | Coolaroo (COO) | emergency switching to repair VT leads at ACR 18077 in somerton rd. | 35
|  | J.24.0095711 | BD 16 | BD16 | Asset - Electrical Failure | 12870.605966666666 | 114.4919 | 22 | 115 | Broadmeadows (BD) | BD 16 | Outage | 54 BLACKWOOD CRESCENT CAMPBELLFIELD VIC 3061 |  | Distr - Transformer | HV Fuse Operation | HVSW_10597184 | 135560 | Broadmeadows (BD) | x3 BA FUSES AT BLACKWOOD-SYCAMORE HAVE OPERATED. CREW SUSPECT THE TRANSFORMER MAY BE FAULTY, BUT HARD TO TELL IN THE DARK. CREW HAVE INSTALLED X5 LV //S TO GET THE CUSTOMERS BACK ON. DAY CREW TO INSEPCT TRANSFORMER TO CONFIRM IF FAULTY LV //S 1. LV ISOLS CHESTNUT ST [~48M N OF MYRTLE ST, A155733] 2. LV ISOLS SYCAMORE CRES [~46M NW OF CHESTNUT ST, A032647 3. LV ISOLS WARATAH ST [~25M W OF GUMTREE CT, A086388] 4. LV ISOLS BLACKWOOD CRES [~38M S OF POPLAR ST, A086398] 5. LV ISOLS SYCAMORE CRES [~35M N OF MYRTLE ST, A032654] 16/4/24 UPDATE Spoke to and emailed Martin Boddy. OI 84098 | 114
|  | J.24.0097006 | CS 09 | CS09 | Asset - Electrical Failure | 8870.033333333333 | 38.6333 | 22 | 259 | Coburg South (CS) | CS 09 | Outage | 44 COBURG STREET COBURG VIC 3058 |  | Distr - Transformer | HV Fuse Operation | HVSW_23220712 | 14093 | Coburg South (CS) | Crew found transformer has failed catastrophically. All 3 HV fuses had operated. Crew to isolate trans LV and open East and West Bus isols. then install LV parallels to restore customers. 1. Sheffield West Coburg. 2. Coburg N Hardwick. 3. Barrow N Hardwick. 4. Barrow N Harding. 5. Harding East Patterson. West CCT @2059 and East CCT @2107. Crew tested volts, Red phase was low, so CCTs tied at LV parallel point 6. Barrow cnr Walsh. EAP #J73425 on issue at 0020 by B Hawtin. EAP cancelled at 01:45 (10/05) by Damien. Sub act & POL with LV //'s removed. CR-002767 | 210
|  | J.24.0097089 | SHM11 | SHM11 | Asset - Electrical Failure | 84463.18565000001 | 702.8344 | 22 | 1429 | Sydenham (SHM) | SHM11 | Outage | SHM11 FDR CB - SHM11 - - PLUMPTON, CALDER PARK, DIGGERS REST, BULLA, KEILOR NORTH, SYDENHAM, SUNBURY, |  | Distr - Transformer | CB Reclose & Open to Lockout | STSW_10329678 | SHM11 FDR CB | Sydenham (SHM) | PATROL FOUND FAILED TRANSFORMER A150617 AT PLUMTON S-HOLDEN P3 10KVA S/S. ISOLATED SUB RESTORED SHM11 FDR | 1328
|  | J.24.0097663 | SBY13 | SBY13 | Asset - Electrical Failure | 720.1 | 360.05 | 22 | 2 | Sunbury (SBY) | SBY13 | Outage | 504220 - SBY13 - - GISBORNE SOUTH, |  | Distr - Transformer | Emergency Switching | HVSW_10553164 | 504220 | Sunbury (SBY) | faulty trans being replaced under AP #94203 issued 2200 PERMIT CANCELLED 23 45 TX PLACED ON LOAD AT 00:00 , VOLTS TESTED ALL OKAY. 71 DUGGAN HAS BEEN RECONNECTED NO ACCCESS TO 28 6001204254 AND 38 6001204253 | 2
|  | J.24.0101246 | YVE22 | YVE22 | Asset - Electrical Failure | 15068.866666666667 | 101.8167 | 22 | 148 | Yarraville (YVE) | YVE22 | Outage | 301160 - YVE22 - - MARIBYRNONG, |  | Distr - Transformer | LV Fuse Operation | HVSW_10666326 | 301160 | Yarraville (YVE) | Crew have advised HV fuse footpath side has operated, crew observe of oil on TX and on Ground. PFF. LV// installed Nth cct Cust on 2025. Sth CCt Cust On 2031. Upon Closer Look Crew have observed that HV Fuse has not operated but significant damage Blue Ph HV dropper insulator falling off , Subsidary Arm is rotten, Top of Tx covered in oil, no oil in TX and Oil all over ground oil contained. Old fuse units, LV bushings white ph Hot spot and bushing cover melted off. TX to be replaced. Tx isolated HV and LV. Burnt out Bus Fuse on Blue Ph. replaced 355 Amp LV fuse. all other fuses OK. PM# 5203856 | 23
|  | J.24.0101876 | COO12 | COO12 | Asset - Electrical Failure | 2886.3166666666666 | 47.3167 | 22 | 61 | Coolaroo (COO) | COO12 | Outage | 95 BULLA ROAD BULLA VIC 3428 |  | Distr - Transformer | HV Fuse Operation | HVSW_30913369 | 580320 | Coolaroo (COO) | TRANSFORMER AT GREEN-BOURKE S/STN FAULTED DURING REFCL TESTING. S/STN ISOLATED HV AND LV AND 4 LV //'S CLOSED. ASR AT 12:02. CUSTOMER'S WERE OFF AT 11:07. REFER TO SWITCHING INSTRUCTION 84809 FOR DETIALS. Keith Fraser has created job number 5204036 for this job and for the week, | 51
|  | J.24.0102975 | SHM14 | SHM14 | Asset - Electrical Failure | 6199.216666666666 | 918.8667 | 22 | 54 | Sydenham (SHM) | SHM14 | Outage | 53412 - SHM14 - - SYDENHAM, FRASER RISE, |  | Distr - Transformer | Emergency Switching | HVSW_36333207 | 53412 | Sydenham (SHM) | Transformer Beattys rd-P8 replaced Change request raised CR-002945 This outage has been created due to the outage for Tx replacement BEATTYS RD - P8 refer to J.24.012924 Large EPV required to replace 2X HV fuses - shift to attend 25kVA Tx, 6K Fuses required. No Cause found, New fuses installed and both operated. LAs cut away, reinstated fuses. Fuses held , red ph faulty giving wrong readings. Closed HV fuses LV isols tested - White and blue phase testing Faulty. Rob advises transformer faulty to be replaced. isolated HV and LV 20:09 | 51
|  | J.24.0103384 | SBY13 | SBY13 | Asset - Electrical Failure | 168569.55936666668 | 676.1299 | 22 | 788 | Sunbury (SBY) | SBY13 | Outage | 51070 - SBY13 - - GISBORNE SOUTH, DIGGERS REST, TOOLERN VALE, GISBORNE, SUNBURY, |  | Distr - Transformer | ACR Reclose & Lockout | HVSW_11087477 | 51070 | Sunbury (SBY) | UNSUCC RECLOSE ACR 51070. HV FUSE OPERATED AT WATERSONS RD P6E1 & GISB-MELTON RD P24E2N2. WATERSONS RD RESTORED OKAY, GISB-MELTON RD P24E2N2 HAS FAILED AND NEEDS TO BE REPLACED. 63KVA 3 PHASE. SEE INSTRUCTION 85018 DEBROAH - 0419 117 681. CREW TO CALL WHEN ATTENDING IF THEY HAVE ACCESS ISSUES EAP ISSUE 96907 ISSUED BY MARK AT 1400. CANCELLATION - 1435 Cust on 1448 | 984
|  | J.24.0109184 | CS 02 | CS02 | Asset - Electrical Failure | 13167.952066666667 | 53.967 | 22 | 244 | Coburg South (CS) | CS 02 | Outage | 5 OBERON STREET COBURG VIC 3058 |  | Distr - Transformer | HV Fuse Operation | HVSW_22054654 | 11985 | Coburg South (CS) | Crew found all 3x HV BA fuses operated. Sub isolated HV and LV , bus split and 5 LV //'s installed. Suspect faulty transformer. All supply restored 04:49. PM ORDER: 5207653 | 205
|  | J.25.0110341 | SHM14 | SHM14 | Asset - Electrical Failure | 26104.433333333334 | 124.4833 | 22 | 214 | Sydenham (SHM) | SHM14 | Outage | 59797 - SHM14 - - FRASER RISE, |  | Distr - Transformer | Emergency Switching | HVSW_35262633 | 59797 | Sydenham (SHM) | EMERGENCY SWITCHING TO REPLACE MODEN-FLORESTA S/STN. REFER TO INSTR 85689 | 214
|  | J.25.0110997 | ST 24 | ST24 | Asset - Electrical Failure | 745.0166666666667 | 745.0167 | 22 | 1 | Somerton (ST) | ST 24 | Outage | L4, CLIFFORDS ROAD SOMERTON VIC 3062 |  | Distr - Transformer | Emergency Switching | HVSW_10784014 | 106480 | Somerton (ST) | boral. Mick found 2 x 15E B/Acid fuses have operated. Crew to isolate LV and replace fuses. 2 X HV BUSHINGS HAVE SUSTAINED DAMAGE AND TRANSFORMER NEEDS TO BE REPLACED. TRANS REPLACED AND SUPPLY RESTORED. | 1
|  | Average |  |  |  |  | 333.2384 |  | 2024: 436.2727
End

## Output¦Tables
|  | Cost Benefit Analysis |  |  |  |  | Section Check: | Ok |  | Overall Check: | Ok |  | Legend: | Input | Internal | Select | Calculation
Output¦Tables
[7 empty] | Year Display | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | EDPR Total
|  |  | Option | Unit | Basis | Asset | Start Year | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Copyright Jemena Limited. All rights reserved. Jemena is not liable for any loss caused by reliance on this document.
Underground Cable Replacement Business Case
Table 1: Credible options and summary of economic analysis & Table 8: Costs of Options
|  | Option | Total capital expenditure ($m) | Value of Customer Reliability ($m over 5 years) | Ranking
|  | Option 1 – Do nothing | 0 | 0 | 3
|  | Option 2 - Replacement levels to maintain network performance and reliability and meet compliance obligations | 10.1826 | 11.3209 | 1
|  | Option 3 - Replacement levels to increase network performance and reliability | 12.2191 | 11.8524 | 2
End