## Main page
AFAP REVIEW
Risk Title | ED - Potential for injury or damage caused by bushfire
Risk Description | The risk of bushfires caused by JEN assets and operational activities, which is increased during bushfire risk periods.
Causes | - Failure of assets including deterioration of assets / age (in the vicinity of fuels such as grass, bracken, scrub or trees) - Contact of vegetation with assets (failure of trees, failure to maintain clearances from overhead electrical assets) - Fire initiated by arcing at pole's HV crossarms - Environmental Factors (e.g. lightning, debris blown onto overhead) - Human intervention (e.g. arson or accidents operating machinery) - Clashing of conductors - Bird or animal contact - Fault on the network
Consequence | Potential to result in Intense bushfires leading to multiple fatalities, damage to property and the environment, and business interruption costs.
Consequence category | Health, safety and environment
Consequence rating | Catastrophic |  |  | Overall Consequence rating assigned based on: | Safety
Residual Likelihood | Rare
Residual Risk rating | Significant
Participants | Paul Garnish, Michael Ciavarella, Vincent Marziale, Tom Ruzeu, Dalibor Balicevic, Peter Wong, Brian Polifrone, Kopeeswaran Vaikundan, Kit Lui, Alan Shu, Harj Kooner, Ian Russom, Gef Formston
AFAP Workshop Date | 14 / 15 October 2020
[5 empty] | Risk mitigation |  |  | Responsible party
Controls (key controls listed first) | Strength of control | Reason for rating | Further actions to strengthen control | Assumptions | Does the action reduce consequence level? (Y/N) | Does the action reduce likelihood level? (Y/N) | Does the action reduce risk? |  | Initiative No.
Key Control - Asset Class Strategies -Key control - JEN distribution asset class strategy -Key control - JEN primary plant asset class strategy -Key control - JEN secondary plant asset class strategy |  | Refer to Key Control assessment | 24*7 monitoring of critical assets | Technology exists, needs to be evaluated | No | Yes | Yes | P Wong | 1
|  |  | Better alignment of project timing ACS review (solutions) across different teams | Only efficiency gains involved | No | No | No
|  |  | Document evidence why a project has been rejected in the business case process | Documentation in investment framework is the evidence | No | No | No
|  |  | Document reasons for implementing a strategy (level of treatment) for performance/failure of assets which are not investigated (e.g. perfrormance of crossarms) | Some ACS may not explain this adequately | No | No | No
Key control - JEN secondary plant asset class strategy |  |  | consider speeding up further protection settings where appropriate | Currently setting as fast as possible according to standard, but can we push for more and optimise? | No | Yes | Yes | M.Ciavarella | 3
|  |  | review standards to set-up new scheme appropriately |  | No | Yes | Yes | M.Ciavarella | 4
|  |  | Simultaneously updating all protection equipments to latest technology | Replace all old protection systems in poor condition | No | Yes | Yes | M.Ciavarella | 5
|  |  | Implement logic blocking scheme |  | No | Yes | Yes | M.Ciavarella | 6
|  |  | REFCL sub asset class (ACS) to be developed by 2022 | Still being implemented ( the mandated one installation) | No | Yes | Yes | ACS Managers | 7
|  |  | Faulted phase earthing | ZSS will detect ground fault in the distribution network (LV and HV). We are trying to incorporate into the REFCL solution | No | Yes | Yes | M.Ciavarella | 8
|  |  | High impedance (pattern recognition) protection | technology is still being developed anf commerciallay available | No | Yes | Yes | M.Ciavarella | 9
|  |  | REFCL for all HBRA areas |  |  |  |  | M.Ciavarella | 31
|  |  | Manning ZSS feeding into HBRA during TFB days |  |  |  |  | M.Ciavarella | 32
|  |  | Allocate budget to purchase sufficient spares for secondary assets (P&C and Comms) |  |  |  |  | M.Ciavarella | 33
|  |  | Duplication for ZSS feeder protection |  |  |  |  | M.Ciavarella | 34
Key control - JEN primary plant asset class strategy |  |  | Proactively install dual power supply battery systems at HBRA ZSS |  |  |  |  | M.Ciavarella | 35
|  |  | On TFB days run HBRA station buses open to reduce the fault level |  |  |  |  | M.Ciavarella | 36
Key control - JEN distribution asset class strategy |  |  | Early fault detection (EFD) technology in the HBRA for detection of partial discharge between phase to gnd |  |  |  |  | P Garnish | 37
|  |  | Smart distribution ZSS |  |  |  |  | P Garnish | 38
|  |  | All future and augmentation OH construction in HBRA to utilise insulated OH cables only (not currently in Stds) |  |  |  |  | P Garnish | 39
|  |  | Install composite cross arms in future and augmentation construction in HBRA |  |  |  |  | P Garnish | 40
|  |  | Proactively replace all OH POELS with underground at JEN cost |  |  |  |  | P Garnish | 41
|  |  | Inspect all poles annually rather than 3yrly. Visual inpection of each pole, crossarm and span |  |  |  |  | P Garnish | 42
|  |  | Routine HV cable and transformer testing in the HBRA |  |  |  |  | P Garnish | 43
Key control - JEN maintenance programs |  |  | Train back-up person for routine reporting of maintenance notification status | NIP has developed a documented procedure; Service Delivery to execute as a backup; there area a lot duplicates in the system (~7000) | No | Yes | Yes | P Garnish | 10
|  |  | Prioritisation model has been developed to execute high risk maintenance orders | Sufficient budget exists to address defects in backlog ( High Risk) Resource availability | No | Yes | Yes | P Garnish | 12
|  |  | Re-evaluate existing notifications using new criteria through routine asset inspection |  | No | Yes | Yes | P Garnish | 13
|  |  | Should be tracking in MRC a) trend or b) completion of high risk notifications |  | No | Yes | Yes | P Garnish | 14
|  |  | Increase frequency of asset inpection program from 3 yr to annual |  |  |  |  | M.Ciavarella / P.Garnish | 44
|  |  | Inspection and patrol program for all OH conductors in HBRA |  |  |  |  | M.Ciavarella / P.Garnish | 45
Key control - JEN internal technical standards |  |  | Check if alerts can be created for changes to published standards |  | No | Yes | Yes | M.Ciavarella / P.Garnish | 15
Key control - JEN asset inspection manual |  |  | Drone technology - more efficient, which may be able to enable reduction in cycle time and more frequent inspections | May be able to apply in area that is non-sensitive area except airport. May be able to trial. Ask counterpart about details. Requires special license in urban area, more applicable to rural area. Select Solutions uses drone for AusNet services. May introduce new risk as Drones may crash on to lines | No | Yes | Yes | P. Wong | 17
|  |  | Consider emerging/evolving technologies attached to the pole (multisensor transmitter devices) - realtime measurement of pollution, smoke, lean, vibration, etc. | Unproven at this moment, but some claims (e.g. WA) are present. For example, vibration measurements can complement asset inspector's pole assessment. | No | Yes | Yes | P. Wong | 18
|  |  | LiDAR (light detection and ranging) and other similar technologies (e.g. dual vision cameras) | A 3D model at a point in time, can be done in 2 weeks for the whole network. We have trialed it 5 years ago. Why did it drop out after the trial? Cost has allegedly dropped recently. Future exploration/research of spatial technology - the thinking is how you integrate back to GIS, to forecast tree growth earlier and provide to council so they have no excuse not to have tree cutting budget ESV are considering legislating LiDAR | No | Yes | Yes | P. Wong | 19
|  |  | Pole top detection of tracking/electrical leakage, vegetation contact (can also detect tree species). Its an ongoing/ eveloving technology | JEN has trialed RMIT technology for 2 years Makes no sense for HBRA which does not have wooden arms Also does not make sense for feeders with sections of UG cables | Yes | Yes | Yes | P. Wong | 20
|  |  | Mechanical digging around base of poles |  | No | Yes | No
|  |  | Review wood pole serviceability criteria | ** Please check with Tom** | No | Yes | Yes | P. Garnish | 21
Key control - JEN bushfire mitigation plan |  |  | Accelerate replacement all open LV conductors with LV ABC conductor and remove wooden LV crossarms in HBRA | The risk is that protection may not operate for covered conductor | No | Yes | Yes | P. Garnish | 22
|  |  | Targeted replacement of wooden crossarms in LBRA with steel crossarms, timber poles with concrete poles, update the policy | Cons: concrete pole is conductive | Yes | Yes | Yes | P Garnish | 23
|  |  | Undergrounding the network selectively - higher risk areas (e.g. HBRA) | Royal Commission also thought this was too expensive; but consider Undergrounding certain section | Yes | Yes | Yes | P Garnish | 24
|  |  | Asphalting/concreting the conductor path in HBRA - remove grass (fuel) for fire |  | No | Yes | Yes | P Garnish | 25
|  |  | Improved methodology or technology for conductor assessment and expand beyond steel conductor (first one would be copper conductor) | Currently we do a visual inspection by camera between poles in middle of span ONLY for steel conductor (extent of corrosion) | No | Yes | Yes | P. Wong | 26
Key control - JEN electric line clearance management plan |  |  | Explore methods to remove vegetation | Implement vegetation corridors under and above all overhead lines | No | Yes | Yes | P. Garnish | 27
|  |  | Expand the clearance space to ensure failed tree/branch cannot contact the line | Current legislation deals with hazardous trees - we have a register and a formal program in HBRA to identify within 2 year cycle |  |  |  | P. Garnish | 28
|  |  | Better prevent council trees from becoming "natural" spreaders | Councils have improved and we are pushing ESV to push councils to do better |  |  |  | P. Garnish | 29
|  |  | Reinforce standard to install LV spreaders for vegetated spans |  |  |  |  | P. Garnish | 30
|  |  | Annual vegetation assessment and clearance in HBRA |  |  |  |  | M.Ciavarella / P.Garnish | 46
Key control - emergency management capability (all assets) |  |  | SCADA system to prioritize HBRA alarms for controllers |  |  |  |  | T.Pullens | 47
Key control - (Electricity) - sufficient trained and competent personnel – field operators and operator technicians |  |  | Introduction of video headset monitoring between operators and controllers |  |  |  |  | V.Marziale | 48
Key control - (Electricity) sufficient trained and competent personnel – engineers
Audits (internal and external) |  |  | Internal audits to ensure compliance with JEN stds for construction (field side) |  |  |  |  | V.Marziale | 49
|  |  | Internal audits to ensure accurate delivery of project scope (project side) |  |  |  |  | V.Marziale | 50
|  |  | Analysis and trending of observations and Non-conformances |  |  |  |  | V.Marziale | 51
|  |  | Auditing end-to-end turnkey developments |  |  |  |  | V.Marziale | 52
BFM KPIs
Early fire detection (technologies)
Thermal surveying
Line Design (was Bird / Animal cover)
No go zone procedures, industry rules & information on Jemena website
Asset Investigations
Industry review of Technology/process/procedures
Other Controls considered but not implemented
Drone technology
LiDAR technology
Underground assets
Corona assessments
Previously completed actions
Capital programs in HBRA • Non tension connector, surge divertor • HV crossarm replacement (wooden --> steel) • Vibration dampers and armour rods • Undersized pole replacement / staking
Proactive replacement of non-preferred services (including use of breakaway devices)
Installation of a pilot REFCL
AFAP Statement
Risk Ratings Matrix
[5 empty] | Likelihood |  | Consequence
1
Minor
[5 empty] | 5 | Almost Certain | Moderate
[5 empty] | 4 | Likely | Moderate
[5 empty] | 3 | Possible | Moderate
[5 empty] | 2 | Unlikely | Low
[5 empty] | 1 | Rare | Low

## Initiatives
Initiative No. | Year | Initial | Final | Main Control/s Strengthened | Name of initiative | Comment | Reason for rejection | Scenario (SC#) | Responsible party:
1 | 2018 | Eliminate | Reject | Key control - JEN primary plant asset class strategy | 24*7 monitoring of critical assets using robotic inspection | Reviewed 2020 - Rejected | Risk reduction too low | 1 | P. Wong
3 | 2018 | Requires Further analysis | Reject | Key control - JEN secondary plant asset class strategy | Consider speeding up further protection settings on TFB day where appropriate at Sunbury | Reviewed 2020 - Rejected | Costs outweigh benefits | 1 | M.Ciavarella
4 | 2018 | Removed | Duplicate | Key control - JEN secondary plant asset class strategy | Review standards to set-up new protection scheme appropriately |  |  | 1 | M.Ciavarella | Removed, covered by #3
5 | 2018 | Eliminate | Reject | Key control - JEN secondary plant asset class strategy | Simultaneously updating all protection equipments to latest technology | Reviewed 2020 - Rejected | Risk reduction too low | 1 | M.Ciavarella
6 | 2018 | Removed | Duplicate | Key control - JEN secondary plant asset class strategy | Implement logic blocking scheme |  |  | 1 | M.Ciavarella | Removed, covered by #3
7 | 2018 | Implement | Accept | Key control - JEN secondary plant asset class strategy | Develop REFCL sub asset class (ACS) by 2022 | Reviewed 2020 - Implemented. Project team in place for implementation in Summer 2022 | - | 1 | All asset class managers
8 | 2018 | Implement | Accept | Key control - JEN secondary plant asset class strategy | Faulted phase earthing | Reviewed 2020 - Implemented. To be delivered as part of REFCL program | - | 1 | P. Wong
9 | 2018 | Eliminate | Reject | Key control - JEN secondary plant asset class strategy | High impedance (pattern recognition) protection | Reviewed 2020 - Rejected | Risk reduction too low | 1 | M.Ciavarella
10 | 2018 | Eliminate | Reject | Key control - JEN maintenance programs | Train back-up person / automation for routine reporting of maintenance notification status | Reviewed 2020 - Rejected | Risk reduction too low | 1 | P. Garnish
12 | 2018 | Implement | Accept | Key control - JEN maintenance programs | Execute high risk maintenance notifications using prioritisation model which has been developed | Reviewed 2020 - Implemented | - | 1 | P. Garnish
13 | 2018 | Implement | Accept | Key control - JEN maintenance programs | Re-evaluate existing notifications using new criteria through routine asset inspection | Reviewed 2020 - Implemented | - | 1 | P. Garnish
14 | 2018 | Implement | Accept | Key control - JEN maintenance programs | Tracking in Management Risk Committee a) trend or b) completion of high risk notifications | Reviewed 2020 - Implemented | - | 1 | P. Garnish
15 | 2018 | Implement | Accept | Key control - JEN internal technical standards | Create alerts for changes to published standards | Reviewed 2020 - Implemented | - | 1 | M.Ciavarella / P.Garnish
17 | 2018 | Eliminate | Reject | Key control - JEN asset inspection manual | Drone technology for asset inspection in HBRA | Reviewed 2020 - Rejected | Other reason | 1 | P. Garnish
18 | 2018 | Eliminate | Reject | Key control - JEN asset inspection manual | Emerging/evolving technologies attached to the pole (multisensor transmitter devices) | Reviewed 2020 - Rejected | Other reason | 1 | P. Wong
19 | 2018 | Implement | Accept | Key control - JEN asset inspection manual | LiDAR (light detection and ranging) and other similar technologies (e.g. dual vision cameras) | Reviewed 2020 - Trial ongoing with PowerCor, results in 2021 | - | 1 | P. Garnish
20 | 2018 | Eliminate | Reject | Key control - JEN asset inspection manual | Pole top detection (EFD on feeders supplying the HBRA) of tracking/electrical leakage, vegetation contact | Reviewed 2020 - Rejected | Other reason | 1 | P. Wong
21 | 2018 | Implement | Accept | Key control - JEN asset inspection manual | Review wood pole serviceability criteria | Reviewed 2020 - Implemented 2020 | - | 1 | P. Garnish
22 | 2018 | Requires further analysis | Reject | Key control - JEN bushfire mitigation plan | Accelerate replacement all open LV conductors with LV ABC conductor | Reviewed 2020 - Rejected | Costs outweigh benefits | 1 | P. Garnish
23 | 2018 | Implement | Accept | Key control - JEN bushfire mitigation plan | Targeted replacement of timber poles with concrete poles, update the policy | Reviewed 2020 - Starting in 2021 | - | 1 | P. Garnish
24 | 2018 | Eliminate | Reject | Key control - JEN bushfire mitigation plan | Undergrounding the network selectively - higher risk areas (e.g. HBRA) | Reviewed 2020 - Rejected | Financially not viable | 1 | P. Garnish
25 | 2018 | Eliminate | Reject | Key control - JEN bushfire mitigation plan | Asphalting/concreting the conductor path in HBRA - remove grass (fuel) for fire | Reviewed 2020 - Rejected | Financially not viable | 1 | P. Garnish | Grossly disproportionate costs $4.6B
26 | 2018 | Removed | Duplicate | Key control - JEN bushfire mitigation plan | Improved methodology or technology for conductor assessment and expand beyond steel conductor (first one would be copper conductor) |  |  | 1 | P.Garnish | Removed, covered by #19
27 | 2018 | Requires further analysis | Reject | Key control - JEN electric line clearance management plan | Remove vegetation in HBRA under and in vicinity of conductors | Reviewed 2020 - Rejected | Costs outweigh benefits | 1 | P. Garnish
28 | 2018 | Requires further analysis | Reject | Key control - JEN electric line clearance management plan | Expand the clearance space to ensure failed tree/branch cannot contact the line | Reviewed 2020 - Rejected | Costs outweigh benefits | 1 | P. Garnish | Regulations do not allow this
29 | 2018 | Implement | Accept | Key control - JEN electric line clearance management plan | Better prevent council trees from becoming "natural" spreaders | Reviewed 2020 - Implemented | Other reason | 1 | P. Garnish
30 | 2018 | Implement | Accept | Key control - JEN electric line clearance management plan | Reinforce standard to install LV spreaders for vegetated spans in HBRA | Reviewed 2020 - Implemented | - | 1 | P. Garnish
31 | 2020 | Requires Further analysis | Reject | Key control - JEN secondary plant asset class strategy | REFCL for all HBRA areas | New Initiative 2020 - Rejected | Costs outweigh benefits | 1 | M.Ciavarella
32 | 2020 | Eliminate | Reject | Key control - JEN secondary plant asset class strategy | Manning ZSS feeding into HBRA during TFB days | New Initiative 2020 - Rejected | Other reason | 1 | M.Ciavarella
33 | 2020 | Eliminate | Reject | Key control - JEN secondary plant asset class strategy | Allocate budget to purchase additional spares for secondary assets (Protection & Control and Comms) | New Initiative 2020 - Rejected | Other reason | 1 | M.Ciavarella
34 | 2020 | Eliminate | Reject | Key control - JEN secondary plant asset class strategy | Duplication for ZSS feeder protection | New Initiative 2020 - Rejected | Risk reduction too low | 1 | M.Ciavarella
35 | 2020 | Implement | Accept | Key control - JEN primary plant asset class strategy | Review the benefits of proactively installing dual power supply battery systems in HBRA ZSS | New Initiative 2020 - Accepted. Action to review in detail | - | 1 | M.Ciavarella
36 | 2020 | Eliminate | Reject | Key control - JEN primary plant asset class strategy | On TFB days run HBRA station buses open to reduce the fault level | New Initiative 2020 - Rejected | Risk reduction too low | 1 | T.Bui
38 | 2020 | Eliminate | Reject | Key control - JEN distribution asset class strategy | Smart distribution substations | New Initiative 2020 - Rejected | Risk reduction too low | 1 | P. Garnish
39 | 2020 | Implement | Accept | Key control - JEN distribution asset class strategy | Further investigate all future OH construction in HBRA to utilise insulated OH cables only (not currently in Stds) | New initiative 2020 - Accepted. Action - a paper in being considered to investigate further | - | 1 | P. Garnish
40 | 2020 | Eliminate | Reject | Key control - JEN distribution asset class strategy | Install LV composite crossarms in future and augmentation construction in HBRA | New Initiative 2020 - Rejected | Other reason | 1 | P. Garnish
41 | 2020 | Requires further analysis | Reject | Key control - JEN distribution asset class strategy | Proactively replace all OH POELS with underground at JEN cost | New Initiative 2020 - Rejected | Costs outweigh benefits | 1 | P. Garnish
42 | 2020 | Requires further analysis | Reject | Key control - JEN distribution asset class strategy | Asset Inspection of all poles annually rather than 3yrly. Visual inspection of each pole, crossarm and span | New Initiative 2020 - Rejected | Costs outweigh benefits | 1 | P. Garnish
43 | 2020 | Eliminate | Reject | Key control - JEN distribution asset class strategy | Routine HV cable testing in the HBRA | New Initiative 2020 - Rejected | Risk reduction too low | 1 | P. Garnish
44 | 2020 | Eliminate | Reject | Key control - JEN maintenance programs | Increase frequency of asset inspection program from 3 yrs to annual (visual and structural) | New Initiative 2020 - Rejected | Risk reduction too low | 1 | M.Ciavarella / P.Garnish
45 | 2020 | Implement | Accept | Key control - JEN maintenance programs | Review requirement for inspection program of all OH conductors in HBRA (expanding to include Aluminium and Copper). Perform AFAP analysis | New initiative 2020 - Accepted. Action to review requirement and determine AFAP assessment criteria | - | 1 | M.Ciavarella / P.Garnish
46 | 2020 | Implement | Accept | Key control - JEN electric line clearance management plan | Annual vegetation assessment and clearance in HBRA | New initiative 2020 - Accepted. Already implemented | - | 1 | M.Ciavarella / P.Garnish
47 | 2020 | Eliminate | Reject | Key control - emergency management capability (all assets) | SCADA system to prioritize HBRA alarms for controllers | New Initiative 2020 - Rejected | Risk reduction too low | 1 | Tim Pullens
48 | 2020 | Implement | Accept | Key control - (Electricity) - sufficient trained and competent personnel – field operators and operator technicians | Introduction of video headset monitoring between operators and controllers | New initiative 2020 - Accepted. Action to review other DBs, barriers, costs, does it sit on our roadmap for use of technology | - | 1 | V.Marziale
49 | 2020 | Implement | Accept | Audits (internal and external) | Internal audits to ensure compliance with JEN stds for construction (field side) (including building to project scope) | New initiative 2020 - Accepted. Action to update 2021 audit plan to ensure adequate level of auditing of quality to JEN construction standards including projects | - | 1 | V.Marziale
51 | 2020 | Implement | Accept | Audits (internal and external) | Analysis and trending of observations and Non-conformances | New initiative 2020 - Accepted. Action to update 2021 audit plan to ensure trending analysis of observations and non-conformances is fed back to AM on a quarterly basis | - | 1 | V.Marziale
52 | 2020 | Implement | Accept | Audits (internal and external) | Auditing end-to-end turnkey developments | New initiative 2020 - Accepted. Action to to review feasibility/cost of implementing the auditing of end-to-end turnkey developments against current process | - | 1 | V.Marziale
53 | 2020 | Implement | Accept | Audits (internal and external) | Routine transformer testing in the HBRA | New initiative 2020 - Accepted. Action to explore parameters available in smart meter data to identify potential electrical faults | - | 1 | M.Ciavarella

## SC1. CBA-Bushfire
AFAP COST-BENEFIT CALCULATION:
Refer to guidance in Appendix 2 - ALARP/AFAP Review Procedure (JEM AM PR 0017) | [5 empty] | Reviewed Date: | 2022-04-06
Notes: |  | Cells highlighted in yellow require user input / entries in red are mandatory for the calculation
SCENARIO:
SC1 - Potential for a fatality caused by a bushfire start
STEP 1 |  | LAYERS OF PROTECTION (LOPA) CALCULATION - INITIATING EVENT FREQUENCY |  |  |  |  | Comments
Number of events |  | Major consequence bushfires in extreme conditions leading to fatality | 29 | events per | 20 | years | 29 major consequence fatality bushfires from 2000 - 2020. http://royalcommission.vic.gov.au/Commission-Reports/Final-Report/Volume-2/Chapters/Electricity-Caused-Fire.html https://www.ffm.vic.gov.au/history-and-incidents/past-bushfires
Events per year |  |  | 1.45 | events / year | 1 | event in | 0.68966 | years
STEP 2 |  | LAYERS OF PROTECTION (LOPA) CALCULATION - RISK REDUCTION FACTORS |  |  | Comments
- LIKELIHOOD MODIFIERS - |  |  | RRF | Risk factor %
Likelihood modifier - (100% = no risk reduction, 1% = large reduction) |  |  | 3.0303 | 33% | Historical proportion (1-4%) of all bushfires (in "normal circumstances") caused by Electricity assets. ESV Powerline Bushfire Safety Taskforce: Final Report 2011 - https://esv.vic.gov.au/safety-education/bushfire-and-powerline-safety/powerline-bushfire-safety-taskforce/ However, disproportionately for major consequence fires in extreme conditions, Royal Commission report highlights 5 out of 15 major fires in Black Saturday(2009) caused by electricity (33%).
Likelihood modifier - (100% = no risk reduction, 1% = large reduction) |  |  | 126 | 0.7937% | JEN ground/veg fires in HBRA - ESV DB Qtly report 2020 (10 JEN fires out of 1260 total of all DBs in 10yrs = 0.8%)
Likelihood modifier - (100% = no risk reduction, 1% = large reduction) |  |  | 1.0526 | 95% | Royal Comm recomm 27 - All JEN HBRA SWERS removed. Assume each Royal Comm element reduces risk by 5% (compared to VIC average of all DBs over past 20yrs)
Likelihood modifier - (100% = no risk reduction, 1% = large reduction) |  |  | 1.0526 | 95% | Royal Comm recomm - Increased ESV regulatory enforcement - Assume each Royal Comm element reduces risk by 5%
Likelihood modifier - (100% = no risk reduction, 1% = large reduction) |  |  | 1.0526 | 95% | Royal Comm recomm 33 - Installation of armour rods /spreaders / spacers / vibration dampers in HBRA - Assume each Royal Comm element reduces risk by 5%
Likelihood modifier - (100% = no risk reduction, 1% = large reduction) |  |  | 5 | 20% | No JEN line construction areas so lower contact risk from JEN (no extreme consequence areas - closest = 100km) - 80% reduction in risk
ALL Likelihood modifiers RRF (Risk Reduction Factor) |  |  | 2226.6697
Residual Likelihood of Hazardous event |  |  | 0.0006512 |  | 1 | event in | 1535.6343 | years
Residual Likelihood |  |  | Rare
Initiating event Consequence rating |  |  | Catastrophic
Residual risk rating |  |  | Significant
STEP 3 |  | TOTAL COST CALCULATION – BENEFITS |  |  | Comments
1 - BENEFIT COST CALCULATION -
Total cost of lives
Value of statistical life |  |  | 5700000 | VoL | Value of statistical life (Australian Government Best Practice Regulation Guidance Note) |  |  | https://www.pmc.gov.au/sites
Value of life year |  |  | 213000 | VLY | Value of statistical life year (Australian Govt)
Value of permanent incapacitating injury (modifies VoL) |  | Injury = internal permanent | 1185600 |  | 0.208 * VoL (AIHW 1999 for unintentional internal injury) |  |  | http://dro.deakin.edu.au/view/DU:30046704
Value of serious injury (modifies VLY) |  | Injury = burn <20% < 6mth recovery | 16827 |  | 0.158 * VLY * 0.5 (AIHW 1999 for burn injury)
Value of minor injury (modifies VLY) |  | Injury = slight/minor <1 wk recovery | 1100 |  | Slight injury - UK Health and Safety Executive – Cost Benefit Analysis (CBA) checklist |  |  | https://www.hse.gov.uk/risk/theory/alarpcheck.htm
Possible Number of Fatalities |  |  | 9.15 | N | 183 bushfire fatalities in 20 years = 9.2 per year 2005 (4), 2006 (1), 2009 (173), 2013 (5) |  |  | Fatalities from 1926 - 2013, Forest Fire Management Victoria https://www.ffm.vic.gov.au/history-and-incidents/past-bushfires
Possible Number of permanent incapacitating injuries |  |  | 0
Possible Number of serious injuries |  |  | 0
Possible Number of minor injuries |  |  | 0
Cost of lives |  |  | 52155000 | CoL | Total cost of loss of N lives / injury
Other benefits cost
Asset damage |  |  | 0 | $
Legal costs (managing the incident and any prosecution / regulatory / coronial inquest consequences) |  |  | 50000000 | $ | Assume $50m worst case if 100% Jemena at fault and insurance does not pay. Need to consider excess
Damage to Reputation |  |  | 10000000 | $ | Assume loss of reputation causes loss of new project work
Other benefits cost |  |  | 60000000 | OC | Total cost of 'other benefits' cost savings to the business and society of avoidance of an incident
TOTAL BENEFIT COST (= Cost of Lives + Other Benefits cost) |  |  | 112155000 | CoB | Total benefit cost savings to the business and society of avoidance of an incident
STEP 4 |  | MAX JUSTIFIABLE SPEND CALCULATION (MJS)
Key inputs for Max Justifiable spend:
Number of years considered (yrs) |  |  | 1 | T |  | For comparison purposes, all values are calculated on a per annum basis
Gross Disproportion value |  |  | 10 | Gd | Factor 1 - 10 | Value depending on level of risk, the higher the risk, the higher the factor to be adopted. This is a subjective value. Suggest using 10 for fatality risks for conservatism, 5 for incapacitating injury, 3 for serious injury, 1 for minor injury/property damage/legal/reputation damage. Examples from the UK HSE include 10 for worst case fatality aversion.
Frequency of hazardous event (before further risk reduction) - copied from RESIDUAL LIKELIHOOD |  |  | 0.0006512 | F0 | per year
Initiative No. | Applicable to Scenario (Y/N) | Cost (1yrs) | Frequency Hazardous event F0 (before control) | %Effectivess Estimation of % reduction in risk - Eliminates the risk completely = 100% - Reduces the risk by half = 50% - Reduces the risk by factor of 10 = 10% - Reduces the risk by factor of 100 = 1% | Assumption for %Effectiveness | Frequency Hazardous event F1 (after control) = F0 * %effectiveness | MJS (1yrs) = CoB * (F0 - F1) * T * Gd | Justified on pure cost/benefit?
1 |  | 60000 | 0.0006512 | 100% |  | 0 | 730349.6883 | Justified
Hazardous trees | Y | NA | 0.0006512 | 50% |  | 0.0003256 | 365174.8441 | NA
5 |  | 100000 | 0.0006512 | 100% |  | 0 | 730349.6883 | Justified
7 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
8 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
9 |  | 1000000 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
10 |  | 150000 | 0.0006512 | 100% |  | 0 | 730349.6883 | Justified
12 |  | 69000 | 0.0006512 | 100% |  | 0 | 730349.6883 | Justified
13 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
14 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
15 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
17 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
18 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
19 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
20 |  | 150000 | 0.0006512 | 100% |  | 0 | 730349.6883 | Justified
21 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
23 |  | 2400000 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
24 |  | 1400000000 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
25 |  | 462000000 | 0.0006512 | 20% |  | 0.00052096 | 146069.9377 | Not justified
29 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
30 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
32 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
33 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
34 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
35 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
36 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
38 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
39 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
40 |  | 0 | 0.0006512 | 100% |  | 0 | 730349.6883 | Not justified
[5 empty] | 25% Scale Factor Applied to HBRA |  | 91293.711

## Do not delete
-
Financially not viable
Technically not viable
Risk reduction too low
Risk is already low (within risk appetite)
Benefits too low
Costs outweigh benefits
Other reason

## matrix
Risk Ratings Matrix
Likelihood |  | Consequence
|  | 1 | 2 | 3 | 4 | 5
|  | Minor | Serious | Severe | Major | Catastrophic
5 | Almost Certain | Moderate | High | Extreme | Extreme | Extreme
4 | Likely | Moderate | Significant | High | Extreme | Extreme
3 | Possible | Moderate | Moderate | Significant | High | Extreme
2 | Unlikely | Low | Low | Moderate | Significant | High
1 | Rare | Low | Low | Moderate | Moderate | Significant

## 1
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 1 |  | Reviewed 2020 - Rejected
Name of initiative: | 24*7 monitoring of critical assets using robotic inspection
2. Main Control/s Strengthened | Key control - JEN primary plant asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Remote sensing of ZSS indoor switchboard equipment for partial discharge monitoring
5. Responsible party: | P. Wong
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 300000 | $300k for partial discharge monitoring of indoor switchboard using inspection robot. (We have quotes from two suppliers).
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 5
| Cost to implement control divided by the design life of the control (cost pa) | 60000
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 60000
8. Financial viability | Is the control financially viable? (Y/N) | Yes
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Risk reduction too low | A 24/7 system would add benefits but we cannot prioritize the cost above other controls and the actual risk reduction is difficult to quantify given our capital constraints. Our existing controls are considered to adequately manage the risk. | K
Further explanation/commentary: |  |  | Comment owner:
Currently under Jemena consideration |  |  | P. Wong
24*7 monitoring can be justifiable if it is applied to critical assets that have displayed signs of impeding failure (e.g. end-of-life). The effectiveness of such monitoring techniques should be ascertained via pilot projects |  |  | P. Wong
JEN is currently considering a trial of a substation robotic system for an aged 22kV indoor switchboard |  |  | D. Mafaakher

## 3
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 3 |  | Reviewed 2020 - Rejected
Name of initiative: | Consider speeding up further protection settings on TFB day where appropriate at Sunbury
2. Main Control/s Strengthened | Key control - JEN secondary plant asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Faster non-RECFL protection may reduce available energy for ignition. This option could potentially reduce the stress on Assets . Even though some existing Feeder P&C settings could be designed to legacy standard for historical reasons, the fundamental principle has always been to isolate the fault as fast as possible. With this in mind, it maybe worthwhile targeting particular feeders prone to fire start.
5. Responsible party: | M.Ciavarella
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes | Small % reduction in Risk only - assume 1% because the fault energy still exists.
7. Costs to implement control | Cost to implement control | 190000 | For a complete review of all JEN feeders it will cost approximately $190K. This is based on $19K per feeder (10 feeders) settings review assuming 2 ACR's per feeder. Note this excludes 66kV Line Protection schemes. | 190000 | Man HRs | Cost
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1 |  | Project Initiation & Scoping (average derived from ZSS consisting multiple feeder protection review) | 15
| Cost to implement control divided by the design life of the control (cost pa) | 190000 |  | Man hours for detail design | 22.5
| Cost of upkeep / maintenance / testing (cost pa) | 0 |  | Secondary Plant to review P&C Settings Report and Check and ISSUE RESIS | 11.25
| Total cost (pa) | 190000 | One year implementation costs only | Testers to Test and Commission Feeder & 2xACR | 22.5
8. Financial viability | Is the control financially viable? (Y/N) | Yes |  | JEN CoC Switching | 7.5
9. Technical viability | Is the control technically viable? (Y/N) | Yes |  | PM Cost (average derived from ZSS consisting multiple feeder protection review) | 15
| Is this control viable from a volume perspective? (Y/N?) | Yes |  | Total Man Hrs | 93.75 | 14062.5
| Is this control viable considering our network traits? (Y/N) | Yes |  | Total Cost including Over Heads (Assume 35%) |  | 18984.375
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Requires Further analysis |  | Cost to review all feeders & assocaitee ACR's across JEN (assuming 300 feeders) |  | 5695312.5
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | Yes
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Costs outweigh benefits | Calculated max justifiable spend ($7K pa) grossly disproportionate to costs ($190K pa). Very small cost justified as estimated risk reduction of only 1%.
Further explanation/commentary: |  |  | Comment owner:
Currently setting as fast as possible according to standard, but can we push for more and optimise? |  |  | C. Lee
Why are we then not implementing it now? There is a fair bit of secondary damage (e.g. connections) because protection is too slow |  |  | C. Lee
All existing feeder protection settings are designed to isolate the fault as fast as possible. It's not technically and economically viable to speed up the protections further. |  |  | K. Vaikundan
Economically it's not viable to review all Feeder & ACR Protection schemes (approx. 400) across JEN. Maybe consider targeting particular feeders prone to fire start (Network Performance to confirm any potential feeders). |  |  | K. Vaikundan

## 5
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 5 |  | Reviewed 2020 - Rejected
Name of initiative: | Simultaneously updating all protection equipments to latest technology
2. Main Control/s Strengthened | Key control - JEN secondary plant asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Newer technology could have advanced self monitoring capabilities
5. Responsible party: | M.Ciavarella
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | No
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | No
7. Costs to implement control | Cost to implement control | 100000 | To replace a single feeder protection relay it will cost approximately $100k.
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 100000
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 100000
8. Financial viability | Is the control financially viable? (Y/N) | No
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Risk reduction too low | No risk reduction. It is not financially viable to update all equipment at the same time. Instead, the P&C ACS has a replacement program, so there is always a mix of old and new equipment. Improving protection systems are only one contributor to overall risk reduction. No old relays in HBRA - they utilise more modern relays.
Further explanation/commentary: |  |  | Comment owner:
Replace all old protection systems which are in poor condition across the JEN network. |  |  | Assumption
It is not financially viable to update all equipment at the same time. Instead, the P&C ACS has a replacement program, so there is always a mix of old and new equipment. |  |  | K. Vaikundan
New Protection relays brings advance monitoring features. But the basic protection principles remains the same (OC or EF elements). If the intention of this option is to improve fault clearance time, then it’s not necessary to upgrade the protection relay to a new technology. |  |  | K. Vaikundan

## 7
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 7 |  | Reviewed 2020 - Implemented. Project team in place for implementation in Summer 2022
Name of initiative: | Develop REFCL sub asset class (ACS) by 2022
2. Main Control/s Strengthened | Key control - JEN secondary plant asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk
5. Responsible party: | All asset class managers
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 0
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N) | Yes
9. Technical viability | Is the control technically viable? (Y/N) | Yes
Is this control viable from a volume perspective? (Y/N?)
Is this control viable considering our network traits? (Y/N)
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:
Still being implemented by Peter Wong's team. Next mandated ZSS is COO. |  |  | K. Vaikundan
Why do we require a separate ACS for REFCL? All Primary Plant equipment associated with REFCL (e.g. Peterson coil, CB's) will be coved in the relevant Primary Plant ACS. Similarly all Protection relays associated with the REFCL will be covered in the existing P&C ACS document. |  |  | K. Vaikundan

## 8
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 8 |  | Reviewed 2020 - Implemented. To be delivered as part of REFCL program
Name of initiative: | Faulted phase earthing
2. Main Control/s Strengthened | Key control - JEN secondary plant asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk
5. Responsible party: | P. Wong
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 0
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | No
| Is this control viable from a volume perspective? (Y/N?) | No
Is this control viable considering our network traits? (Y/N)
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | - | Feasibility being investigated as a part of REFCL program
Further explanation/commentary: |  |  | Comment owner:
This should be assigned to Peter Wong's team as they are exploring this technology as part of REFCL. |  |  | Kopee Vaikundan

## 9
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 9 |  | Reviewed 2020 - Rejected
Name of initiative: | High impedance (pattern recognition) protection
2. Main Control/s Strengthened | Key control - JEN secondary plant asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | High Impedance faults are likely to be detected and isolated in a matter of seconds (subject to available technology). Only applicable to ZSS without REFCLs installed (approx 5-6)
5. Responsible party: | M.Ciavarella
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | No | Unproven technology not yet showing benefit. Unlikely to reduce Likelihood of ignition
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | No
7. Costs to implement control | Cost to implement control | 1000000 | $150-200k per feeder to bench test the relay, design, test, commission and monitor and analysis for a period of time (e.g. one year window).
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 1000000
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 1000000
8. Financial viability | Is the control financially viable? (Y/N) | No
9. Technical viability | Is the control technically viable? (Y/N) | No
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Risk reduction too low | Subject to commercial availability of technology which is still under development. This scheme is in development for down conductor (human safety). Hence this protection is not suitable for reduction of fire start.
Further explanation/commentary: |  |  | Comment owner:
Subject to commercial availability of technology which is still under development. This scheme is in development for down conductor (human safety). Hence this protection is not suitable for reduction of fire start. |  |  | K. Vaikundan
Maybe worthwhile conducting a pilot project on a feeder to evaluate this technology. |  |  | K. Vaikundan
Most of the solutions available to detect these faults are very slow in terms of fault confirmation time (5-10 seconds). This is because they use multiple of fault detecting algorithms such as fault signature detections to identify these faults. |  |  | K. Vaikundan

## 10
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 10 |  | Reviewed 2020 - Rejected
Name of initiative: | Train back-up person / automation for routine reporting of maintenance notification status
2. Main Control/s Strengthened | Key control - JEN maintenance programs
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Providing redundancy additional to existing redundancy. Assists during leave periods
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | No
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | No | Notifications are prioritised and maintainance planners work on most important first. Multiple planners (5) already.
7. Costs to implement control | Cost to implement control | 0
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 150000
| Total cost (pa) | 150000
8. Financial viability | Is the control financially viable? (Y/N) | Yes
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Risk reduction too low | Notifications are prioritised and maintainance planners work on most important first. Multiple planners (5) already. Insufficient benefit
Further explanation/commentary: |  |  | Comment owner:
NIP has developed a documented procedure; Service Delivery to execute as a backup; there area a lot duplicates in the system (~7000) |  |  | P. Garnish

## 12
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 12 |  | Reviewed 2020 - Implemented
Name of initiative: | Execute high risk maintenance notifications using prioritisation model which has been developed
2. Main Control/s Strengthened | Key control - JEN maintenance programs
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 54000 | $50K ( 3 people * 3 weeks @$150/hr)
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 54000
| Cost of upkeep / maintenance / testing (cost pa) | 15000 | Cost for maintaining the model ($15k for annual refresher + $50 for weekly upkeep of the data)
| Total cost (pa) | 69000
8. Financial viability | Is the control financially viable? (Y/N) | Yes
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:
Sufficient budget exists to address defects in backlog (i.e. high risk maintenance orders) |  |  | Assumption
Resource availability |  |  | Assumption
Under the assumptions made of funds and resource being available; this can be implemented

## 13
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 13 |  | Reviewed 2020 - Implemented
Name of initiative: | Re-evaluate existing notifications using new criteria through routine asset inspection
2. Main Control/s Strengthened | Key control - JEN maintenance programs
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Confirmed Implemented
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 0
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N) | Yes
9. Technical viability | Is the control technically viable? (Y/N)
Is this control viable from a volume perspective? (Y/N?)
Is this control viable considering our network traits? (Y/N)
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:
Already being done - new asset inspection manual update 2018 |  |  | Paul Garnish

## 14
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 14 |  | Reviewed 2020 - Implemented
Name of initiative: | Tracking in Management Risk Committee a) trend or b) completion of high risk notifications
2. Main Control/s Strengthened | Key control - JEN maintenance programs
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | KPI already implemented
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 0
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N) | Yes
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:
This will not make a direct change/provide benefit as it is purely reporting of a position |  |  | Paul Garnish

## 15
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 15 |  | Reviewed 2020 - Implemented
Name of initiative: | Create alerts for changes to published standards
2. Main Control/s Strengthened | Key control - JEN internal technical standards
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Confirmed Implemented
5. Responsible party: | M.Ciavarella / P.Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 0
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N) | Yes
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:
Process involves raising proposed changes through Standards Committee and then using the FTC process to communicate the changes
Document control to alert all stakeholders has been implemented

## 17
16 | AFAP INITIATIVE ASSESSMENT: |  |  | Comments
| 1. Initiative ID: | 17 |  | Reviewed 2020 - Rejected
| Name of initiative: | Drone technology for asset inspection in HBRA
| 2. Main Control/s Strengthened | Key control - JEN asset inspection manual
| 3. Applicable Scenario (SC#) | 1
| 4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Potential for inspections to be cheaper, faster and safer. May allow greater precision and better access to hard-to-reach places. Possible use of predictive maintenance, focused on minimising network failures.
| 5. Responsible party: | P. Garnish
| 6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
|  | Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
|  | Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
| 7. Costs to implement control | Cost to implement control | 0
|  | Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
|  | Cost to implement control divided by the design life of the control (cost pa) | 0
|  | Cost of upkeep / maintenance / testing (cost pa) | 0
|  | Total cost (pa) | 0
| 8. Financial viability | Is the control financially viable? (Y/N)
| 9. Technical viability | Is the control technically viable? (Y/N) | Yes
|  | Is this control viable from a volume perspective? (Y/N?) | No
Is this control viable considering our network traits? (Y/N)
| 10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
| Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
| 11. Final consideration / justification statement | Accept / Reject | Reject
|  | If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Other reason | JEN insurers have excluded cover for use of drones
| Further explanation/commentary: |  |  | Comment owner:
| Technology is more efficient than current asset inspection practices and may be able to enable reduction in cycle time and more frequent inspections |  |  | T. Ruzeu
| May be able to apply in area that is non-sensitive area except airport. May be able to trial. Ask DB counterpart's about details. Requires special license in urban area, more applicable to rural area. Select Solutions uses drone for AusNet services. May introduce new risk as Drones may crash on to lines |  |  | T. Ruzeu
| Drone coupled with big data analytics technology may prove to deliver more accurate results compared with current inspection approach. We are in regular contact with service providers to understand development of the technology and potential pilot projects |  |  | P. Wong

## 18
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 18 |  | Reviewed 2020 - Rejected
Name of initiative: | Emerging/evolving technologies attached to the pole (multisensor transmitter devices)
2. Main Control/s Strengthened | Key control - JEN asset inspection manual
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Improved fire start detection
5. Responsible party: | P. Wong
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 0
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N)
Is this control viable from a volume perspective? (Y/N?)
Is this control viable considering our network traits? (Y/N)
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Other reason | Accepted for review in a trial with developers but the product has not become commercially available
Further explanation/commentary: |  |  | Comment owner:
Technology enables realtime measurement of pollution, smoke, lean, vibration, etc. |  |  | T. Ruzeu
Technology unproven at this moment, but there are some claims that it works (e.g. in WA). For example, vibration measurements can complement asset inspector's pole assessment. |  |  | T. Ruzeu
Jemena is partnering with a developer ( start-up) of Pole sensors for a Victorian govt. grant |  |  | P. Wong

## 19
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 19 |  | Reviewed 2020 - Trial ongoing with PowerCor, results in 2021
Name of initiative: | LiDAR (light detection and ranging) and other similar technologies (e.g. dual vision cameras)
2. Main Control/s Strengthened | Key control - JEN asset inspection manual
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Advanced LiDAR detection to detect/map asset and vegetation clearances to reduce the risk of fire starts
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 0
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N)
Is this control viable from a volume perspective? (Y/N?)
Is this control viable considering our network traits? (Y/N)
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | - | Jemena is currently evaluating the option with service providers
Further explanation/commentary: |  |  | Comment owner:
Technology is a 3D model at a point in time, can be done in 2 weeks for the whole network. |  |  | C. Lee
We have trialed it 5 years ago. Why did it drop out after the trial? Cost has allegedly dropped recently. |  |  | C. Lee
Future exploration/research of spatial technology - the thinking is how you integrate back to GIS, to forecast tree growth earlier and provide to council so they have no excuse not to have tree cutting budget |  |  | T. Ruzeu
ESV are considering legislating LiDAR |  |  | C. Mukherjee
We'll continue to monitor the technology development and the cost |  |  | P. Wong

## 20
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 20 |  | Reviewed 2020 - Rejected
Name of initiative: | Pole top detection (EFD on feeders supplying the HBRA) of tracking/electrical leakage, vegetation contact
2. Main Control/s Strengthened | Key control - JEN asset inspection manual
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Looks for partial discharge signature which is a precursor to a poletop fire
5. Responsible party: | P. Wong
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 90000 | Trial costs only - covering one circuit. Installation + Ongoing Opex cost; Upfront Capex $ 90k+ $60K Opex. Actual costs for network would be significantly higher for all circuits
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 90000
| Cost of upkeep / maintenance / testing (cost pa) | 60000
| Total cost (pa) | 150000
8. Financial viability | Is the control financially viable? (Y/N) | No
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Other reason | The initial trial is inconclusive based on the selected area; no fire starts were detected. The technology requires overhead line between 2 detectors whereas JEN has a mixture of OH and UG. Our existing controls are considered to adequately manage the risk. Pole top detection system would add benefits but we cannot prioritize above other controls the cost as the actual risk reduction is difficult to quantify given our capital constraints
Further explanation/commentary: |  |  | Comment owner:
Technology can also detect tree species |  |  | T. Ruzeu
It is an ongoing/ evolving technology |  |  | T. Ruzeu
JEN has trialed RMIT technology for 2 years |  |  | T. Ruzeu
Makes no sense for HBRA which does not have wooden arms |  |  | T. Ruzeu
Also does not make sense for feeders with sections of UG cables |  |  | T. Ruzeu
The technology has been developed into an early bushfire detection device for SWER networks. Rollout of the technology in JEN is not expected to be viable as JEN has no SWER networks. |  |  | D. Mafaakher

## 21
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 21 |  | Reviewed 2020 - Implemented 2020
Name of initiative: | Review wood pole serviceability criteria
2. Main Control/s Strengthened | Key control - JEN asset inspection manual
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Reduces the risk of pole failures causing fire starts
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 0 | No inspection cost increase, additional staking and replacement costs to bring forward pole replacements. (100 poles per year @$10k)
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N) | No
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement | F- Factor Fire start $25k average cost (AER), $3k Savings ( approrx. For cross-arm replacement); assumption of reducing 3 fire starts; reliability STPIS
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:
Tom to provide details |  |  | P. Garnish

## 22
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 22 |  | Reviewed 2020 - Rejected
Name of initiative: | Accelerate replacement all open LV conductors with LV ABC conductor
2. Main Control/s Strengthened | Key control - JEN bushfire mitigation plan
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Potential to reduce conductor clashing, animal/bird fire start, Vegetation contact F- Factor
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 8968000 | $236K/km ($9 M for 38 Kms in HBRA); $28k/span
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 5
| Cost to implement control divided by the design life of the control (cost pa) | 1793600
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 1793600
8. Financial viability | Is the control financially viable? (Y/N) | No
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Requires further analysis
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | Yes
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Costs outweigh benefits | Calculated max justifiable spend ($688K pa - very conservative assumption control 100% effective) grossly disproportionate to costs ($1.8M pa).
Further explanation/commentary: |  |  | Comment owner:
The risk is that protection may not operate for covered conductor |  |  | T. Ruzeu
As JEN HBRA is only 38 Kms, it can be feasible provided funding is available |  |  | P. Garnish
Can be viable if its targeted to high fire consequence area |  |  | P. Garnish

## 23
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 23 |  | Reviewed 2020 - Starting in 2021
Name of initiative: | Targeted replacement of timber poles with concrete poles, update the policy
2. Main Control/s Strengthened | Key control - JEN bushfire mitigation plan
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Reduces the risk of pole failures causing fire starts
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 2400000 | wood pole is approx $600 per unit and concrete $3000 per unit. (increase of $2400 per unit x 1000 units per year = $2,400,000)
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 2400000
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 2400000
8. Financial viability | Is the control financially viable? (Y/N) | No
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement | F- Factor Fire start $25k average cost (AER), $3k Savings ( approrx. For cross-arm replacement); assumption of reducing 3 fire starts; reliability STPIS
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept | Rejected in 2018. Decided to implement in HBRA only from 2021. Policy changed after St Pats day fire. Rating changed to accepted 10.09.20
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:
The negative side efect of this initiative is that concrete poles are conductive |  |  | T. Ruzeu

## 24
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 24 |  | Reviewed 2020 - Rejected
Name of initiative: | Undergrounding the network selectively - higher risk areas (e.g. HBRA)
2. Main Control/s Strengthened | Key control - JEN bushfire mitigation plan
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Removes risk from OH conductors causing firestarts
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 7000000000 | $7b cost to replace HBRA underground
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 5
| Cost to implement control divided by the design life of the control (cost pa) | 1400000000
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 1400000000
8. Financial viability | Is the control financially viable? (Y/N) | No
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Financially not viable | $1.4B annual costs. Also not technically viable unless over the long term
Further explanation/commentary: |  |  | Comment owner:
Royal Commission also thought that undergrounding the entire network was too expensive; therefore consider undergrounding certain high risk sections |  |  | T. Ruzeu

## 25
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 25 |  | Reviewed 2020 - Rejected
Name of initiative: | Asphalting/concreting the conductor path in HBRA - remove grass (fuel) for fire
2. Main Control/s Strengthened | Key control - JEN bushfire mitigation plan
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes | Assume risk reduction of 80%
7. Costs to implement control | Cost to implement control | 462000000 | $300 per sq m and 700km route length (x 2.2m width) = $462m
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 462000000
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 462000000
8. Financial viability | Is the control financially viable? (Y/N) | No
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Financially not viable | Customer complaints would also not allow
Further explanation/commentary: |  |  | Comment owner:

## 27
16 | AFAP INITIATIVE ASSESSMENT: |  |  | Comments
| 1. Initiative ID: | 27 |  | Reviewed 2020 - Rejected
| Name of initiative: | Remove vegetation in HBRA under and in vicinity of conductors |  | Already have existing process for individual problem trees
| 2. Main Control/s Strengthened | Key control - JEN electric line clearance management plan
| 3. Applicable Scenario (SC#) | 1
| 4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Completely remove trees from under or in vicinity of conductors in HBRA to reduce risk of vegetation caused fire starts
| 5. Responsible party: | P. Garnish
| 6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
|  | Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
|  | Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes | Assume trees contribute to 80% of risk
| 7. Costs to implement control | Cost to implement control | 30000000 | $1100 to remove per tree (25000 trees to be removed) = $27.5m - not including cost to maintain annually (estimate $300k) and cost of offset planting new trees ($2.5m)
|  | Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 5 | Five year EDPR cycle considered
|  | Cost to implement control divided by the design life of the control (cost pa) | 6000000
|  | Cost of upkeep / maintenance / testing (cost pa) | 300000
|  | Total cost (pa) | 6300000
| 8. Financial viability | Is the control financially viable? (Y/N) | No
| 9. Technical viability | Is the control technically viable? (Y/N) | Yes
|  | Is this control viable from a volume perspective? (Y/N?) | Yes
|  | Is this control viable considering our network traits? (Y/N) | Yes
| 10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Requires further analysis
| Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | Yes
| 11. Final consideration / justification statement | Accept / Reject | Reject
|  | If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Costs outweigh benefits | Calculated max justifiable spend ($137K pa) grossly disproportionate to costs ($30M pa) . Also highly unlikely to be accepted due to potential for damage to reputation from tree removal
| Further explanation/commentary: |  |  | Comment owner:
| This initiaive would involve implement vegetation corridors under and above all overhead lines |  |  | T. Ruzeu

## 28
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 28 |  | Reviewed 2020 - Rejected
Name of initiative: | Expand the clearance space to ensure failed tree/branch cannot contact the line
2. Main Control/s Strengthened | Key control - JEN electric line clearance management plan
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Reduces risk of vegetation caused fire starts
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 25000000 | $500 per span x 50000 spans to establish and maintain @$100 extra per span ongoing
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 5
| Cost to implement control divided by the design life of the control (cost pa) | 5000000
| Cost of upkeep / maintenance / testing (cost pa) | 5000000
| Total cost (pa) | 10000000
8. Financial viability | Is the control financially viable? (Y/N) | No
9. Technical viability | Is the control technically viable? (Y/N) | No
Is this control viable from a volume perspective? (Y/N?)
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Requires further analysis
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | Yes
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Costs outweigh benefits | Calculated max justifiable spend ($688K pa - very conservative assumption control 100% effective) grossly disproportionate to costs ($10M pa).Regulations do not allow this
Further explanation/commentary: |  |  | Comment owner:
Current legislation deals with hazardous trees - we have a register and a formal program in HBRA to identify within 2 year cycle |  |  | T. Ruzeu

## 29
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 29 |  | Reviewed 2020 - Implemented
Name of initiative: | Better prevent council trees from becoming "natural" spreaders
2. Main Control/s Strengthened | Key control - JEN electric line clearance management plan
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major
Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare
Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant
7. Costs to implement control | Cost to implement control | 0
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N)
Is this control viable from a volume perspective? (Y/N?)
Is this control viable considering our network traits? (Y/N)
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Other reason | Already doing this
Further explanation/commentary: |  |  | Comment owner:
Councils have improved and we are pushing ESV to push councils to do better |  |  | T. Ruzeu

## 30
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 30 |  | Reviewed 2020 - Implemented
Name of initiative: | Reinforce standard to install LV spreaders for vegetated spans in HBRA |  | Already implemented
2. Main Control/s Strengthened | Key control - JEN electric line clearance management plan
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Reduces clashing between open LBRA conductors
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N) | No
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:

## 31
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 31 |  | New Initiative 2020 - Rejected
Name of initiative: | REFCL for all HBRA areas
2. Main Control/s Strengthened | Key control - JEN secondary plant asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Reducing fault energy to minimise firestart. (Only 1.5 REFCLs on JEN network planned).
5. Responsible party: | M.Ciavarella
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes | Assume reduces risk by 50% based on JEN analysis of REFCLs
7. Costs to implement control | Cost to implement control | 22000000 | Estimate $15-30M for 5-6
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 5
| Cost to implement control divided by the design life of the control (cost pa) | 4400000
| Cost of upkeep / maintenance / testing (cost pa) | 200000
| Total cost (pa) | 4600000
8. Financial viability | Is the control financially viable? (Y/N) | No
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Requires Further analysis
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | Yes
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Costs outweigh benefits | Calculated max justifiable spend ($344K p.a.) grossly disproportionate to costs ($4.6M p.a.)
Further explanation/commentary: |  |  | Comment owner:

## 32
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 32 |  | New Initiative 2020 - Rejected
Name of initiative: | Manning ZSS feeding into HBRA during TFB days
2. Main Control/s Strengthened | Key control - JEN secondary plant asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Immediate response in event of SCADA comms failures for monitoring / control.
5. Responsible party: | M.Ciavarella
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | No
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | No
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N) | Yes
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Other reason | Acts as an insurance / contigency only in event of TFB failures. (No history of comms SCADA failure on TFB days). Will not improve bushfire risk, only affects customer supply availability. Operator would not trigger a protection event
Further explanation/commentary: |  |  | Comment owner:

## 33
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 33 |  | New Initiative 2020 - Rejected
Name of initiative: | Allocate budget to purchase additional spares for secondary assets (Protection & Control and Comms)
2. Main Control/s Strengthened | Key control - JEN secondary plant asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk
5. Responsible party: | M.Ciavarella
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | No
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | No | Only reduces reliability risk
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Other reason | Acts as a reliability risk reduction rather than preventing a TFB issue. (The protection does not prevent the fire in any case)
Further explanation/commentary: |  |  | Comment owner:

## 34
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 34 |  | New Initiative 2020 - Rejected
Name of initiative: | Duplication for ZSS feeder protection
2. Main Control/s Strengthened | Key control - JEN secondary plant asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Possible reduction in duration of fault event
5. Responsible party: | M.Ciavarella
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control |  | $100K per feeder
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N) | Yes
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Risk reduction too low | Reduces the duration of fault event but does not stop the fault event. Risk reduction considered too low
Further explanation/commentary: |  |  | Comment owner:

## 35
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 35 |  | New Initiative 2020 - Accepted. Action to review in detail
Name of initiative: | Review the benefits of proactively installing dual power supply battery systems in HBRA ZSS
2. Main Control/s Strengthened | Key control - JEN primary plant asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | The battery systems operate the control and protection systems. Some ZSS do have dual protection. Sydenham and COO do not. Part of new standard and we upgrade for new builds. The battery system does not "stop" the event from happening but does affect time fault is active.
5. Responsible party: | M.Ciavarella
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:

## 36
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 36 |  | New Initiative 2020 - Rejected
Name of initiative: | On TFB days run HBRA station buses open to reduce the fault level
2. Main Control/s Strengthened | Key control - JEN primary plant asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Running buses open marginally reduces the energy of the fault. However introduces more of a reliability risk affecting customer supply. A no cost initiative
5. Responsible party: | T.Bui
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Risk reduction too low | Running 22kV buses open for zone substations supplying HBRA supply areas would only reduce the fault level or energy slightly due to the significant impedance in the 22kV line. This is unlikely to be effective to reduce a bushfire start where there would be a trade off with the increase in reliability risk. It is recommended that this proposal would not be adopted.
Further explanation/commentary: |  |  | Comment owner:

## 38
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 38 |  | New Initiative 2020 - Rejected
Name of initiative: | Smart distribution substations
2. Main Control/s Strengthened | Key control - JEN distribution asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Adding smart systems to detect faults rather than relying on fuses. Potentially reduces duration of fault. Fuses are considered high speed but smart systems could cooordinate a response. Some smart systems being installed in kiosk subs.
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Risk reduction too low | Risk reduction considered too small because the smart electronic protection is no faster than a conventional fuse.
Further explanation/commentary: |  |  | Comment owner:

## 39
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 39 |  | New initiative 2020 - Accepted. Action - a paper in being considered to investigate further
Name of initiative: | Further investigate all future OH construction in HBRA to utilise insulated OH cables only (not currently in Stds)
2. Main Control/s Strengthened | Key control - JEN distribution asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Insulated conductors reduce risk by 80-90% during contact with ground/vegetation. Mandated in 33 sites in VIC but not within JEN area.
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control |  | $600K per Km compared to $200K. For re-conductering, $30K per km.
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:

## 40
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 40 |  | New Initiative 2020 - Rejected
Name of initiative: | Install LV composite crossarms in future and augmentation construction in HBRA
2. Main Control/s Strengthened | Key control - JEN distribution asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Inherently non-conductive, increased strength, durability and resistance to environmental degradation
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Other reason | Superseded by requirement all LV to be either LV ABC or underground removing need for crossarms
Further explanation/commentary: |  |  | Comment owner:

## 41
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 41 |  | New Initiative 2020 - Rejected
Name of initiative: | Proactively replace all OH POELS with underground at JEN cost
2. Main Control/s Strengthened | Key control - JEN distribution asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Reduces risk by 80-90%. (The risk is essentially owned by customer but we have an inspection responsibility). Bushfire Royal Commission indicated 15 funded sites for replacement considered higher risk. We have about 400 sites.
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | Yes
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 8500000 | $10K per site for 350 sites plus $100K per site for approx 50 sites
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 5
| Cost to implement control divided by the design life of the control (cost pa) | 1700000
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 1700000
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Requires further analysis
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | Yes
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Costs outweigh benefits | Calculated max justifiable spend ($620K pa) grossly disproportionate to costs ($1.7M pa)
Further explanation/commentary: |  |  | Comment owner:

## 42
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 42 |  | New Initiative 2020 - Rejected
Name of initiative: | Asset Inspection of all poles annually rather than 3yrly. Visual inspection of each pole, crossarm and span
2. Main Control/s Strengthened | Key control - JEN distribution asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Condition assessment of electrical assets. Other DBs assess assets with "known" faults. We inspect one third each year normally.
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes | Reduces risk by only 0.1% because many other control measures in place already
7. Costs to implement control | Cost to implement control | 150000 | Visual inspection $30 per pole x 5000 poles
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 150000
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 150000
8. Financial viability | Is the control financially viable? (Y/N) | Yes
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Requires further analysis
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | Yes
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Costs outweigh benefits | Calculated max justifiable spend ($1K pa) grossly disproportionate to costs ($150K pa) and risk reduction too low
Further explanation/commentary: |  |  | Comment owner:

## 43
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 43 |  | New Initiative 2020 - Rejected
Name of initiative: | Routine HV cable testing in the HBRA
2. Main Control/s Strengthened | Key control - JEN distribution asset class strategy
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Identifies insulation failures above ground reducing flashover fires.
5. Responsible party: | P. Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Risk reduction too low | Some history of cable head failures occassionaly in LBRA but not in HBRA. Considered minimal risk reduction
Further explanation/commentary: |  |  | Comment owner:

## 44
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 44 |  | New Initiative 2020 - Rejected
Name of initiative: | Increase frequency of asset inspection program from 3 yrs to annual (visual and structural) |  | In contrast to #42 which is only visual
2. Main Control/s Strengthened | Key control - JEN maintenance programs
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Considered no risk reduction
5. Responsible party: | M.Ciavarella / P.Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control | 300000 | 5000 poles x $60
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 300000
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 300000
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Risk reduction too low | Decay occurs slower than inspection cycle. Considered excessive inspection. Few failures in HBRA
Further explanation/commentary: |  |  | Comment owner:

## 45
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 45 |  | New initiative 2020 - Accepted. Action to review requirement and determine AFAP assessment criteria
Name of initiative: | Review requirement for inspection program of all OH conductors in HBRA (expanding to include Aluminium and Copper). Perform AFAP analysis
2. Main Control/s Strengthened | Key control - JEN maintenance programs
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Captures aluminium corrosion issues and annealing issues for copper, reducing failure rates. Already performed for steel conductors but expanding for aluminium and copper
5. Responsible party: | M.Ciavarella / P.Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:

## 46
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 46 |  | New initiative 2020 - Accepted. Already implemented
Name of initiative: | Annual vegetation assessment and clearance in HBRA
2. Main Control/s Strengthened | Key control - JEN electric line clearance management plan
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Reduces risk of vegetation caused fire starts
5. Responsible party: | M.Ciavarella / P.Garnish
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:

## 47
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 47 |  | New Initiative 2020 - Rejected
Name of initiative: | SCADA system to prioritize HBRA alarms for controllers
2. Main Control/s Strengthened | Key control - emergency management capability (all assets)
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | If alarms occur in the HBRA area it is clearly visible? Is there anything in SCADA that would allow us to delineate between alarms in HBRA areas vs others? Is there any value in considering assigning higher priority to HBRA alarms? Answer - Not certain if would reduce risk.
5. Responsible party: | Tim Pullens
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | No
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | No
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N) | Yes
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | Yes
| Is this control viable considering our network traits? (Y/N) | Yes
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Eliminate
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Reject
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | Risk reduction too low | Network Operations Manager (T.Pullens) post workshop discussed issue with SCADA & RTS Manager (P.Rogers) and reported the control room are very aware of which components of the network are part of the HBRA area when dealing with faults and there is little value in introducing additional specific alarms
Further explanation/commentary: |  |  | Comment owner:
If alarms occur in the HBRA area it is clearly visible. Is there anything in SCADA that would allow us to delineate between alarms in HBRA areas vs others? Is there any value in considering assigning higher priority to HBRA alarms? |  |  | P.Garnish/T.Ruzeu

## 48
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 48 |  | New initiative 2020 - Accepted. Action to review other DBs, barriers, costs, does it sit on our roadmap for use of technology
Name of initiative: | Introduction of video headset monitoring between operators and controllers
2. Main Control/s Strengthened | Key control - (Electricity) - sufficient trained and competent personnel – field operators and operator technicians
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Controller can monitor progress of switching actions and identify potential errors. Expectation is that operators are already skilled. Not a high frequency of operator errors in the field.
5. Responsible party: | V.Marziale
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:
(Raised by Tom Ruzeu)

## 49
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 49 |  | New initiative 2020 - Accepted. Action to update 2021 audit plan to ensure adequate level of auditing of quality to JEN construction standards including projects
Name of initiative: | Internal audits to ensure compliance with JEN stds for construction (field side) (including building to project scope)
2. Main Control/s Strengthened | Audits (internal and external)
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Evidence of compliance issues, eg with bird covers and non-tension connectors. Possibly requires more detailed auditing to capture
5. Responsible party: | V.Marziale
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:

## 51
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 51 |  | New initiative 2020 - Accepted. Action to update 2021 audit plan to ensure trending analysis of observations and non-conformances is fed back to AM on a quarterly basis
Name of initiative: | Analysis and trending of observations and Non-conformances
2. Main Control/s Strengthened | Audits (internal and external)
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | 49 about finding errors. This one about trending. Minimal feedback supplied to Asset Management.
5. Responsible party: | V.Marziale
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:

## 52
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 52 |  | New initiative 2020 - Accepted. Action to to review feasibility/cost of implementing the auditing of end-to-end turnkey developments against current process
Name of initiative: | Auditing end-to-end turnkey developments
2. Main Control/s Strengthened | Audits (internal and external)
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | Focus on contractor compliance
5. Responsible party: | V.Marziale
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:

## 53
AFAP INITIATIVE ASSESSMENT: |  |  | Comments
1. Initiative ID: | 53 |  | New initiative 2020 - Accepted. Action to explore parameters available in smart meter data to identify potential electrical faults
Name of initiative: | Routine transformer testing in the HBRA
2. Main Control/s Strengthened | Audits (internal and external)
3. Applicable Scenario (SC#) | 1
4. Function of control /initiative: | Describe clearly how the control function acts to minimise the risk |  | A verification of smart meter loading data to gain spot checks of transformers and determine if overloaded (possible overheat, loss of oil and cooling resulting in possible flashover). Smart meter data suggest we do have some issues although data is not inline with actual failures. Option to explore parameters available in smart meter data to identify potential electrical faults
5. Responsible party: | M.Ciavarella
6. Risk reduction | Does the control reduce Consequence level? (Y/N) List any change - eg Catastrophic > Major | No
| Does the control reduce Likelihood level? (Y/N) List any change - eg Unlikely > Rare | Yes
| Does the control reduce Risk ? (Y/N) (A reduction in risk can be possible even if the L/C/R ratings are unchanged). List any change - eg High > Significant | Yes
7. Costs to implement control | Cost to implement control
| Estimated design life of control (years) (How long is the control expected to defend against the risk?) | 1
| Cost to implement control divided by the design life of the control (cost pa) | 0
| Cost of upkeep / maintenance / testing (cost pa) | 0
| Total cost (pa) | 0
8. Financial viability | Is the control financially viable? (Y/N)
9. Technical viability | Is the control technically viable? (Y/N) | Yes
| Is this control viable from a volume perspective? (Y/N?) | No
| Is this control viable considering our network traits? (Y/N) | No
10. Decide: - Eliminate - Implement - Further analysis | Decide: (a) whether the initiative is easily eliminated (based on our technical/financial requirements, (b) Implement (easy to justify / relatively inexpensive), (c) Requires further detailed AFAP analysis | Implement
Detailed Cost-benefit analysis? | Refer to CBA tab if detailed analysis required | No
11. Final consideration / justification statement | Accept / Reject | Accept
| If control is rejected, state the main reason reason (select from list and provide overall statement of justification why implementation of measure is not practicable) | -
Further explanation/commentary: |  |  | Comment owner:
99