## Summary
Summary of quantified risks - NH ZSS
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Option 1 - Do Nothing | 1998128.7842 | 2090160.1562 | 2206242.8161 | 2298020.0016 | 2354242.898 | 2402918.4171 | 2460415.7565 | 2536046.0679 | 2606739.6456 | 2641695.667 | 2658873.6812 | 2695565.9826 | 2747363.9337 | 2803924.9914 | 2841823.2486 | 2866268.8801 | 2889564.4378 | 2911794.1278 | 2931709.7188 | 2957447.6519
Option 3 - develop the zone substation | 1998128.7842 | 2090160.1562 | 2206242.8161 | 2298020.0016 | 2354242.898 | 2402918.4171 | 2460415.7565 | 2536046.0679 | 29.9428 | 12182.9734 | 26140.0021 | 41939.251 | 59810.9103 | 79740.158 | 101060.3677 | 123491.1197 | 147400.2482 | 172763.7102 | 199538.9311 | 228172.591
Option 4 - Staged replacement | 1998128.7842 | 2090160.1562 | 2206242.8161 | 2298020.0016 | 2354242.898 | 2402918.4171 | 967598.1367 | 1008415.9752 | 1048789.0539 | 1075898.4116 | 1096583.2434 | 77288.5347 | 97982.3937 | 120472.9033 | 143726.5256 | 167616.8278 | 192697.7527 | 218806.1522 | 245872.4511 | 274605.6308

## Option 1
|  |  | Items | Probability of Failure |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
|  |  | 1 | Failure of 22kV Circuit Breaker |  |  | 74.33% | 68.31% | 69.01% | 69.7% | 70.37% | 71.03% | 71.67% | 72.31% | 72.92% | 73.52% | 74.11% | 74.69% | 75.25% | 75.8% | 76.34% | 76.87% | 77.39% | 77.89% | 78.38% | 78.87% | 79.34%
|  |  | 2 | Failure of 66kV Circuit Breaker |  |  | 55.24% | 80.96% | 83.02% | 84.94% | 86.71% | 88.35% | 89.85% | 91.2% | 92.43% | 93.52% | 94.5% | 95.36% | 96.11% | 96.76% | 97.33% | 97.81% | 98.22% | 98.56% | 98.85% | 99.09% | 99.28%
Option 1 - Do Nothing | [6 empty] | 2024: Years
Item | Fault Scenario | Risk | Assets Quantities | Event Probability | CoC | LoC | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
1 | Failure of Feeder and Transformer Circuit Breaker | Initial Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39440.4168
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 8.1022 | 8.3024 | 8.5948 | 8.7903 | 8.852 | 8.8905 | 8.9662 | 9.1113 | 9.2411 | 9.2484 | 9.1993 | 9.2234 | 9.3029 | 9.4013 | 9.4398 | 9.4373 | 9.4346 | 9.4316 | 9.424 | 9.4377
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 327412.2701 | 338960.2337 | 354404.2386 | 365965.2425 | 371983.4711 | 376985.8015 | 383543.9188 | 393072.1135 | 401964.4662 | 405502.0389 | 406491.9104 | 410631.4611 | 417205.22 | 424614.5686 | 429303.9426 | 432067.9771 | 434756.2425 | 437369.1979 | 439707.48 | 442981.3985
2 | Failure of 22kV Transformer Incomer Circuit Breakers | Initial Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39440.4168
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 16.2043 | 16.6048 | 17.1896 | 17.5806 | 17.7041 | 17.781 | 17.9324 | 18.2227 | 18.4823 | 18.4968 | 18.3985 | 18.4468 | 18.6059 | 18.8026 | 18.8796 | 18.8746 | 18.8692 | 18.8633 | 18.8479 | 18.8754
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 447286.9688 | 467831.886 | 494037.894 | 515079.3607 | 528446.4707 | 540406.6043 | 554650.5087 | 573270.2364 | 591080.7429 | 601059.5272 | 607222.6896 | 618032.9706 | 632524.1857 | 648333.3024 | 660030.0944 | 668732.602 | 677275.2548 | 685656.8008 | 693572.4118 | 702912.0262
3 | Failure of 22kV Bus Tie Circuit Breaker | Initial Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39440.4168
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 16.2043 | 16.6048 | 17.1896 | 17.5806 | 17.7041 | 17.781 | 17.9324 | 18.2227 | 18.4823 | 18.4968 | 18.3985 | 18.4468 | 18.6059 | 18.8026 | 18.8796 | 18.8746 | 18.8692 | 18.8633 | 18.8479 | 18.8754
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 447286.9688 | 467831.886 | 494037.894 | 515079.3607 | 528446.4707 | 540406.6043 | 554650.5087 | 573270.2364 | 591080.7429 | 601059.5272 | 607222.6896 | 618032.9706 | 632524.1857 | 648333.3024 | 660030.0944 | 668732.602 | 677275.2548 | 685656.8008 | 693572.4118 | 702912.0262
4 | Failure of 66kV Bus Tie Circuit Breaker | Initial Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39440.4168
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 16.2043 | 16.6048 | 17.1896 | 17.5806 | 17.7041 | 17.781 | 17.9324 | 18.2227 | 18.4823 | 18.4968 | 18.3985 | 18.4468 | 18.6059 | 18.8026 | 18.8796 | 18.8746 | 18.8692 | 18.8633 | 18.8479 | 18.8754
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 776142.5766 | 815536.1505 | 863762.7895 | 901896.0378 | 925366.4855 | 945119.407 | 967570.8203 | 996433.4816 | 1022613.6935 | 1034074.5737 | 1037936.3916 | 1048868.5803 | 1065110.3423 | 1082643.818 | 1092459.1172 | 1096735.6991 | 1100257.6857 | 1103111.3284 | 1104857.4151 | 1108642.2011
[5 empty] | Total |  |  | 1998128.7842 | 2090160.1562 | 2206242.8161 | 2298020.0016 | 2354242.898 | 2402918.4171 | 2460415.7565 | 2536046.0679 | 2606739.6456 | 2641695.667 | 2658873.6812 | 2695565.9826 | 2747363.9337 | 2803924.9914 | 2841823.2486 | 2866268.8801 | 2889564.4378 | 2911794.1278 | 2931709.7188 | 2957447.6519

## Option 3
|  |  | Items | Probability of Failure |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
|  |  | 1 | Failure of 22kV Circuit Breaker |  |  | 74.33% | 68.31% | 69.01% | 69.7% | 70.37% | 71.03% | 71.67% | 72.31% | 72.92% | 0.005149% | 2.054% | 4.112% | 6.137% | 8.131% | 10.09% | 12.02% | 13.91% | 15.76% | 17.58% | 19.36% | 21.1%
|  |  | 2 | Failure of 66kV Circuit Breaker - AEI |  |  | 55.24% | 80.96% | 83.02% | 84.94% | 86.71% | 88.35% | 89.85% | 91.2% | 92.43% | 0.0001636% | 0.001851% | 0.00765% | 0.02094% | 0.04571% | 0.08652% | 0.1483% | 0.2366% | 0.3571% | 0.516% | 0.7196% | 0.9745%
Option 3 - develop the zone substation | [6 empty] | 2024: Years
Item | Fault Scenario | Risk | Assets Quantities | Event Probability | CoC | LoC | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
1 | Failure of Feeder and Transformer Circuit Breaker | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39440.4168
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 8.1022 | 8.3024 | 8.5948 | 8.7903 | 8.852 | 8.8905 | 8.9662 | 9.1113 | 9.2411 | 9.2484 | 9.1993 | 9.2234 | 9.3029 | 9.4013 | 9.4398 | 9.4373 | 9.4346 | 9.4316 | 9.424 | 9.4377
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 327412.2701 | 338960.2337 | 354404.2386 | 365965.2425 | 371983.4711 | 376985.8015 | 383543.9188 | 393072.1135 | 28.1483 | 11239.2263 | 22376.6079 | 33489.2935 | 44752.0216 | 56124.1373 | 67128.0305 | 77650.5397 | 87963.1209 | 98065.419 | 107933.9697 | 117828.3552
2 | Failure of 22kV Transformer Incomer Circuit Breakers | Initial Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39440.4168
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 16.2043 | 16.6048 | 17.1896 | 17.5806 | 17.7041 | 17.781 | 17.9324 | 18.2227 | 18.4823 | 18.4968 | 18.3985 | 18.4468 | 18.6059 | 18.8026 | 18.8796 | 18.8746 | 18.8692 | 18.8633 | 18.8479 | 18.8754
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 447286.9688 | 467831.886 | 494037.894 | 515079.3607 | 528446.4707 | 540406.6043 | 554650.5087 | 573270.2364 | 0.0028985 | 461.7472 | 1840.063 | 4110.7321 | 7277.8481 | 11326.8176 | 16137.7058 | 21599.1815 | 27725.2081 | 34470.0708 | 41790.7729 | 49731.2786
3 | Failure of 22kV Bus Tie Circuit Breaker | Initial Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39440.4168
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 16.2043 | 16.6048 | 17.1896 | 17.5806 | 17.7041 | 17.781 | 17.9324 | 18.2227 | 18.4823 | 18.4968 | 18.3985 | 18.4468 | 18.6059 | 18.8026 | 18.8796 | 18.8746 | 18.8692 | 18.8633 | 18.8479 | 18.8754
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 447286.9688 | 467831.886 | 494037.894 | 515079.3607 | 528446.4707 | 540406.6043 | 554650.5087 | 573270.2364 | 0.0028985 | 461.7472 | 1840.063 | 4110.7321 | 7277.8481 | 11326.8176 | 16137.7058 | 21599.1815 | 27725.2081 | 34470.0708 | 41790.7729 | 49731.2786
4 | Failure of 66kV Bus Tie Circuit Breaker | Initial Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39440.4168
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 16.2043 | 16.6048 | 17.1896 | 17.5806 | 17.7041 | 17.781 | 17.9324 | 18.2227 | 18.4823 | 18.4968 | 18.3985 | 18.4468 | 18.6059 | 18.8026 | 18.8796 | 18.8746 | 18.8692 | 18.8633 | 18.8479 | 18.8754
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 776142.5766 | 815536.1505 | 863762.7895 | 901896.0378 | 925366.4855 | 945119.407 | 967570.8203 | 996433.4816 | 1.7887 | 20.2528 | 83.2683 | 228.4933 | 503.1926 | 962.3855 | 1656.9256 | 2642.217 | 3986.7111 | 5758.1495 | 8023.4157 | 10881.6786
[5 empty] | Total |  |  | 1998128.7842 | 2090160.1562 | 2206242.8161 | 2298020.0016 | 2354242.898 | 2402918.4171 | 2460415.7565 | 2536046.0679 | 29.9428 | 12182.9734 | 26140.0021 | 41939.251 | 59810.9103 | 79740.158 | 101060.3677 | 123491.1197 | 147400.2482 | 172763.7102 | 199538.9311 | 228172.591

## Option 4
|  |  | Items | Probability of Failure |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
|  |  | 1 | Failure of 22kV Circuit Breaker |  |  | 74.33% | 68.31% | 69.01% | 69.7% | 70.37% | 71.03% | 71.67% | 0.005149% | 2.054% | 4.112% | 6.137% | 8.131% | 10.09% | 12.02% | 13.91% | 15.76% | 17.58% | 19.36% | 21.1% | 22.81% | 24.49%
|  |  | 2 | Failure of 66kV Circuit Breaker - AEI |  |  | 55.24% | 80.96% | 83.02% | 84.94% | 86.71% | 88.35% | 89.85% | 91.2% | 92.43% | 93.52% | 94.5% | 95.36% | 0.0001636% | 0.001851% | 0.00765% | 0.02094% | 0.04571% | 0.08652% | 0.1483% | 0.2366% | 0.3571%
Option 4 - Staged replacement | [6 empty] | 2024: Years
Item | Fault Scenario | Risk | Assets Quantities | Event Probability | CoC | LoC | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
1 | Failure of Feeder and Transformer Circuit Breaker | Unserved Energy (N-1 Bus Outage)
|  | VCR ($/MWh) | 39440.4168
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 8.1022 | 8.3024 | 8.5948 | 8.7903 | 8.852 | 8.8905 | 8.9662 | 9.1113 | 9.2411 | 9.2484 | 9.1993 | 9.2234 | 9.3029 | 9.4013 | 9.4398 | 9.4373 | 9.4346 | 9.4316 | 9.424 | 9.4377
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 327412.2701 | 338960.2337 | 354404.2386 | 365965.2425 | 371983.4711 | 376985.8015 | 27.3108 | 11072.6836 | 22478.4802 | 33580.0848 | 44253.3498 | 55061.8785 | 66154.6263 | 77354.2656 | 88011.6577 | 98124.6115 | 108055.9529 | 117752.303 | 127182.6761 | 136714.6553
2 | Failure of 22kV Transformer Incomer Circuit Breakers | Initial Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39440.4168
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 16.2043 | 16.6048 | 17.1896 | 17.5806 | 17.7041 | 17.781 | 17.9324 | 18.2227 | 18.4823 | 18.4968 | 18.3985 | 18.4468 | 18.6059 | 18.8026 | 18.8796 | 18.8746 | 18.8692 | 18.8633 | 18.8479 | 18.8754
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 447286.9688 | 467831.886 | 494037.894 | 515079.3607 | 528446.4707 | 540406.6043 | 0.0028123 | 454.905 | 1848.4401 | 4121.8765 | 7196.751 | 11112.4354 | 15903.6976 | 21516.7703 | 27740.5065 | 34490.8771 | 41838.0034 | 49699.1795 | 58025.6508 | 66951.4732
3 | Failure of 22kV Bus Tie Circuit Breaker | Initial Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39440.4168
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 16.2043 | 16.6048 | 17.1896 | 17.5806 | 17.7041 | 17.781 | 17.9324 | 18.2227 | 18.4823 | 18.4968 | 18.3985 | 18.4468 | 18.6059 | 18.8026 | 18.8796 | 18.8746 | 18.8692 | 18.8633 | 18.8479 | 18.8754
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 447286.9688 | 467831.886 | 494037.894 | 515079.3607 | 528446.4707 | 540406.6043 | 0.0028123 | 454.905 | 1848.4401 | 4121.8765 | 7196.751 | 11112.4354 | 15903.6976 | 21516.7703 | 27740.5065 | 34490.8771 | 41838.0034 | 49699.1795 | 58025.6508 | 66951.4732
4 | Failure of 66kV Bus Tie Circuit Breaker | Initial Unserved Energy (N-2 Bus Outage)
|  | VCR ($/MWh) | 39440.4168
|  | Duration in minutes | 90
|  | Unserved Energy at risk (MWh) | [5 empty] | 16.2043 | 16.6048 | 17.1896 | 17.5806 | 17.7041 | 17.781 | 17.9324 | 18.2227 | 18.4823 | 18.4968 | 18.3985 | 18.4468 | 18.6059 | 18.8026 | 18.8796 | 18.8746 | 18.8692 | 18.8633 | 18.8479 | 18.8754
|  | Cost Expected Unserved Energy at risk ($) | [5 empty] | 776142.5766 | 815536.1505 | 863762.7895 | 901896.0378 | 925366.4855 | 945119.407 | 967570.8203 | 996433.4816 | 1022613.6935 | 1034074.5737 | 1037936.3916 | 1.7853 | 20.3723 | 85.0972 | 233.855 | 510.4622 | 965.7931 | 1655.4902 | 2638.4734 | 3988.0292
[5 empty] | Total |  |  | 1998128.7842 | 2090160.1562 | 2206242.8161 | 2298020.0016 | 2354242.898 | 2402918.4171 | 967598.1367 | 1008415.9752 | 1048789.0539 | 1075898.4116 | 1096583.2434 | 77288.5347 | 97982.3937 | 120472.9033 | 143726.5256 | 167616.8278 | 192697.7527 | 218806.1522 | 245872.4511 | 274605.6308

## 66kV CB PoF
| β | 3.5
| η | 45
Asset Age | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82
Year start Actual | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
Probability of Failures | 0% | 0.0001636% | 0.001851% | 0.00765% | 0.02094% | 0.04571% | 0.08652% | 0.1483% | 0.2366% | 0.3571% | 0.516% | 0.7196% | 0.9745% | 1.287% | 1.666% | 2.116% | 2.645% | 3.26% | 3.967% | 4.773% | 5.685% | 6.707% | 7.845% | 9.104% | 10.49% | 12% | 13.64% | 15.41% | 17.31% | 19.33% | 21.49% | 23.76% | 26.16% | 28.66% | 31.27% | 33.96% | 36.74% | 39.59% | 42.5% | 45.45% | 48.43% | 51.42% | 54.41% | 57.38% | 60.32% | 63.21% | 66.04% | 68.79% | 71.45% | 74% | 76.45% | 78.77% | 80.96% | 83.02% | 84.94% | 86.71% | 88.35% | 89.85% | 91.2% | 92.43% | 93.52% | 94.5% | 95.36% | 96.11% | 96.76% | 97.33% | 97.81% | 98.22% | 98.56% | 98.85% | 99.09% | 99.28% | 99.44% | 99.56% | 99.67% | 99.75% | 99.81% | 99.86% | 99.89% | 99.92% | 99.94% | 99.96% | 99.97%

## 22kV CB PoF
Year | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Asset Age in Days in A1 year | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 365 | 366 | 365 | 365 | 365 | 365 | 366 | 365 | 365 | 365
days in service | 1 | 366 | 732 | 1097 | 1462 | 1827 | 2193 | 2558 | 2923 | 3288 | 3654 | 4019 | 4384 | 4749 | 5115 | 5480 | 5845 | 6210 | 6576 | 6941 | 7306 | 7671 | 8037 | 8402 | 8767 | 9132 | 9498 | 9863 | 10228 | 10593 | 10959 | 11324 | 11689 | 12054 | 12420 | 12785 | 13150 | 13515 | 13881 | 14246 | 14611 | 14976 | 15342 | 15707 | 16072 | 16437 | 16803 | 17168 | 17533 | 17898 | 18264 | 18629 | 18994 | 19359 | 19725 | 20090 | 20455 | 20820 | 21186 | 21551 | 21916 | 22281 | 22647 | 23012 | 23377 | 23742 | 24108 | 24473 | 24838 | 25203 | 25569 | 25934 | 26299 | 26664 | 27029 | 27395 | 27760 | 28125 | 28490 | 28855 | 29221 | 29586 | 29951 | 30316
failures per year | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Failure time (t) | 0.2 | 73.2 | 146.4 | 219.4 | 292.4 | 365.4 | 438.6 | 511.6 | 584.6 | 657.6 | 730.8 | 803.8 | 876.8 | 949.8 | 1023 | 1096 | 1169 | 1242 | 1315.2 | 1388.2 | 1461.2 | 1534.2 | 1607.4 | 1680.4 | 1753.4 | 1826.4 | 1899.6 | 1972.6 | 2045.6 | 2118.6 | 2191.8 | 2264.8 | 2337.8 | 2410.8 | 2484 | 2557 | 2630 | 2703 | 2776.2 | 2849.2 | 2922.2 | 2995.2 | 3068.4 | 3141.4 | 3214.4 | 3287.4 | 3360.6 | 3433.6 | 3506.6 | 3579.6 | 3652.8 | 3725.8 | 3798.8 | 3871.8 | 3945 | 4018 | 4091 | 4164 | 4237.2 | 4310.2 | 4383.2 | 4456.2 | 4529.4 | 4602.4 | 4675.4 | 4748.4 | 4821.6 | 4894.6 | 4967.6 | 5040.6 | 5113.8 | 5186.8 | 5259.8 | 5332.8 | 5405.8 | 5479 | 5552 | 5625 | 5698 | 5771 | 5844.2 | 5917.2 | 5990.2 | 6063.2
Median Rank | 7.5008e-06 | 0.0027453 | 0.0054905 | 0.0082283 | 0.010966 | 0.013704 | 0.016449 | 0.019187 | 0.021925 | 0.024662 | 0.027408 | 0.030146 | 0.032883 | 0.035621 | 0.038366 | 0.041104 | 0.043842 | 0.04658 | 0.049325 | 0.052063 | 0.0548 | 0.057538 | 0.060284 | 0.063021 | 0.065759 | 0.068497 | 0.071242 | 0.07398 | 0.076718 | 0.079455 | 0.082201 | 0.084938 | 0.087676 | 0.090414 | 0.093159 | 0.095897 | 0.098635 | 0.10137 | 0.10412 | 0.10686 | 0.10959 | 0.11233 | 0.11508 | 0.11781 | 0.12055 | 0.12329 | 0.12604 | 0.12877 | 0.13151 | 0.13425 | 0.13699 | 0.13973 | 0.14247 | 0.14521 | 0.14795 | 0.15069 | 0.15343 | 0.15617 | 0.15891 | 0.16165 | 0.16439 | 0.16712 | 0.16987 | 0.17261 | 0.17535 | 0.17808 | 0.18083 | 0.18357 | 0.1863 | 0.18904 | 0.19179 | 0.19452 | 0.19726 | 0.2 | 0.20274 | 0.20548 | 0.20822 | 0.21096 | 0.2137 | 0.21643 | 0.21918 | 0.22192 | 0.22465 | 0.22739
1/1-MR | 1 | 1.0028 | 1.0055 | 1.0083 | 1.0111 | 1.0139 | 1.0167 | 1.0196 | 1.0224 | 1.0253 | 1.0282 | 1.0311 | 1.034 | 1.0369 | 1.0399 | 1.0429 | 1.0459 | 1.0489 | 1.0519 | 1.0549 | 1.058 | 1.0611 | 1.0642 | 1.0673 | 1.0704 | 1.0735 | 1.0767 | 1.0799 | 1.0831 | 1.0863 | 1.0896 | 1.0928 | 1.0961 | 1.0994 | 1.1027 | 1.1061 | 1.1094 | 1.1128 | 1.1162 | 1.1196 | 1.1231 | 1.1265 | 1.13 | 1.1335 | 1.1371 | 1.1406 | 1.1442 | 1.1478 | 1.1514 | 1.1551 | 1.1587 | 1.1624 | 1.1661 | 1.1699 | 1.1736 | 1.1774 | 1.1812 | 1.1851 | 1.1889 | 1.1928 | 1.1967 | 1.2007 | 1.2046 | 1.2086 | 1.2126 | 1.2167 | 1.2207 | 1.2248 | 1.229 | 1.2331 | 1.2373 | 1.2415 | 1.2457 | 1.25 | 1.2543 | 1.2586 | 1.263 | 1.2674 | 1.2718 | 1.2762 | 1.2807 | 1.2852 | 1.2897 | 1.2943
ln(days in service) | 0 | 5.9026 | 6.5958 | 7.0003 | 7.2876 | 7.5104 | 7.693 | 7.847 | 7.9804 | 8.098 | 8.2036 | 8.2988 | 8.3857 | 8.4657 | 8.5399 | 8.6089 | 8.6733 | 8.7339 | 8.7912 | 8.8452 | 8.8965 | 8.9452 | 8.9918 | 9.0362 | 9.0787 | 9.1195 | 9.1588 | 9.1965 | 9.2329 | 9.2679 | 9.3019 | 9.3347 | 9.3664 | 9.3972 | 9.4271 | 9.456 | 9.4842 | 9.5116 | 9.5383 | 9.5642 | 9.5895 | 9.6142 | 9.6383 | 9.6619 | 9.6848 | 9.7073 | 9.7293 | 9.7508 | 9.7718 | 9.7924 | 9.8127 | 9.8325 | 9.8519 | 9.8709 | 9.8896 | 9.908 | 9.926 | 9.9437 | 9.9611 | 9.9782 | 9.995 | 10.0115 | 10.0278 | 10.0438 | 10.0595 | 10.075 | 10.0903 | 10.1053 | 10.1201 | 10.1347 | 10.1491 | 10.1633 | 10.1773 | 10.1911 | 10.2047 | 10.2181 | 10.2314 | 10.2444 | 10.2573 | 10.27 | 10.2826 | 10.2951 | 10.3073 | 10.3194
ln(ln(1/(1-MR))) | -11.8005 | -5.8965 | -5.202 | -4.796 | -4.5074 | -4.2832 | -4.0992 | -3.9439 | -3.8091 | -3.69 | -3.5831 | -3.4865 | -3.3981 | -3.3167 | -3.2411 | -3.1707 | -3.1048 | -3.0428 | -2.9841 | -2.9287 | -2.876 | -2.8258 | -2.7778 | -2.7319 | -2.6879 | -2.6457 | -2.6049 | -2.5658 | -2.528 | -2.4914 | -2.456 | -2.4218 | -2.3886 | -2.3563 | -2.3249 | -2.2945 | -2.2649 | -2.236 | -2.2078 | -2.1803 | -2.1535 | -2.1273 | -2.1017 | -2.0766 | -2.0521 | -2.0281 | -2.0046 | -1.9816 | -1.959 | -1.9369 | -1.9151 | -1.8937 | -1.8728 | -1.8522 | -1.8319 | -1.812 | -1.7924 | -1.7731 | -1.7541 | -1.7355 | -1.7171 | -1.699 | -1.6811 | -1.6635 | -1.6462 | -1.6291 | -1.6121 | -1.5955 | -1.5791 | -1.5628 | -1.5468 | -1.531 | -1.5154 | -1.4999 | -1.4847 | -1.4696 | -1.4547 | -1.44 | -1.4254 | -1.411 | -1.3967 | -1.3826 | -1.3687 | -1.3549
Beta(β) =@LINEST(G2:G75,F2:F75,True,False) | 1.0164
Intercept =@index(LINEST(G2:G75,F2:F75),2) | -11.8965
45.3894 | 16567.1279
total Failures in 75 years = 15 in a population of 158 | 15
PoF = 1-(1-Weibull.Dist( C2,$J$2,$L$2,TRUE)) | 0.005149% | 2.054% | 4.112% | 6.137% | 8.131% | 10.09% | 12.02% | 13.91% | 15.76% | 17.58% | 19.36% | 21.1% | 22.81% | 24.49% | 26.13% | 27.74% | 29.31% | 30.85% | 32.36% | 33.84% | 35.28% | 36.7% | 38.09% | 39.44% | 40.77% | 42.07% | 43.34% | 44.58% | 45.8% | 46.99% | 48.16% | 49.3% | 50.42% | 51.51% | 52.58% | 53.63% | 54.65% | 55.65% | 56.63% | 57.59% | 58.53% | 59.44% | 60.34% | 61.22% | 62.08% | 62.92% | 63.74% | 64.54% | 65.33% | 66.1% | 66.85% | 67.59% | 68.31% | 69.01% | 69.7% | 70.37% | 71.03% | 71.67% | 72.31% | 72.92% | 73.52% | 74.11% | 74.69% | 75.25% | 75.8% | 76.34% | 76.87% | 77.39% | 77.89% | 78.38% | 78.87% | 79.34% | 79.8% | 80.25% | 80.69% | 81.12% | 81.54% | 81.96% | 82.36% | 82.75% | 83.14% | 83.52% | 83.89% | 84.25%
Note: - The data here has been derived from available Jemena SAP data and based on existing fleet of 22kV Switchboards and total number of CBs in those boards. 158 Items and failure rate (based on industry norms) is 15 units in 75 years or 0.2 failures per annum ie 1 every 5 years on average. - The Weibull distribution scale factor values in the report, Review of Assets for Replacement of Substations within Jemena’s Network (VIC-JEM-008-R1¦V1.0), differ from this spreadsheet. The report’s calculation includes operating years up to year 2035, while this spreadsheet includes operating years up to year 2045. This affects the asset’s ‘characteristic life’ and decreases the Probability of Failure. These lower values have been used in the cost-benefits analysis and business case.