## INTRO
PTS Replacement Volume - Model
|  |  |  | Version | 1.0
|  |  |  | Date | 4598700%
|  |  |  | Planning Year-Start (Y0) | 2025
Structure Overview
Parameters | --> | Refers to tabs containing required inputs. Cells/Inputs to be updated as per the periodicity/base of the model are highlighted in green.
Note: These are the only tabs that should be updated/manipulated.
INPUT
Data | --> | PTS in service and historical
OUTPUT (WOOD & STEEL)
Forecast LV | --> | Refers to tab containing formulated and calculated cells. Includes PoF and Replacement volumes as outputs for LV
Forecast HV | --> | Refers to tab containing formulated and calculated cells. Includes PoF and Replacement volumes as outputs for HV
Forecast ST | --> | Refers to tab containing formulated and calculated cells. Includes PoF and Replacement volumes as outputs for ST
High Level - Data Model
High Level - Process Flow

## Parameters
Model Parameters--> | Weibull Cumulative Distribution Function (CDF)
PTS In Service Volumes
Exclude | NO
User Status List Desc | INSV
Row Labels | Count of SAP ID | Count of SAP ID2 | Average of Age (Years) | Min of Age (Years) | Max of Age (Years) | StdDev of Age (Years)
steel | 66442 | 52.64% | 18.625 | 0 | 86.863 | 10.5002
HV | 33273 | 26.36% | 18.5263 | 0 | 73.9123 | 11.1066
LV | 26257 | 20.8% | 17.6011 | 0 | 68.4932 | 8.6
ST | 6912 | 5.476% | 22.9894 | 0.47397 | 86.863 | 12.7285
wood | 59771 | 47.36% | 35.7362 | 0 | 94.5123 | 18.9725
HV | 5582 | 4.423% | 45.0707 | 2.5041 | 94.5123 | 11.0435
LV | 53950 | 42.75% | 34.6939 | 0 | 94.5123 | 19.3385
ST | 239 | 0.1894% | 53.003 | 5.2164 | 87.9205 | 13.2458
Grand Total | 126213 | 100% | 26.7284 | 0 | 94.5123 | 17.3637
Health Index Threshold
WOOD | STEEL
0.3 | 0.3
Scale Parameter (η – Eta)
Exclude | NO
User Status List Desc | ASRT RMVD
Bushfire Area | no
Row Labels | Number of Xarms | Average of Age (Years) | Min of Age (Years) | Max of Age (Years) | StdDev of Age (Years) | Coeficient of VAR
steel | 390 | 25.3951 | 0.024658 | 60.9671 | 14.4354 | 0.56843
HV | 296 | 27.3529 | 0.1863 | 60.9671 | 14.9401 | 0.5462
LV | 45 | 16.243 | 0.024658 | 46.4548 | 10.6831 | 0.6577
ST | 49 | 21.9736 | 1.8164 | 38.0493 | 9.9113 | 0.45105
wood | 17694 | 41.8241 | 0 | 81.2247 | 15.3681 | 0.36745
HV | 4423 | 42.5823 | 0.49315 | 81.2247 | 12.151 | 0.28535
LV | 12981 | 41.4238 | 0 | 81.2137 | 16.3409 | 0.39448
ST | 290 | 48.1784 | 5.6959 | 69.8877 | 12.2682 | 0.25464
Grand Total | 18084 | 41.4698 | 0 | 81.2247 | 15.5327 | 0.37455
Wood
LV | HV | ST
52 | 55 | 59
Steel
LV | HV | ST
70 | 70 | 70
Shape Parameter (β – Beta)
Wood
LV | HV | ST
3 | 3 | 3
Steel
LV | HV | ST
3 | 3 | 3

## OUTPUT<Forecast-LV-WOOD>
Exclude | NO
User Status List Desc | INSV
Crossarm Material | wood
Count of SAP ID | Voltage |  |  | Age | [6 empty] | Failure Probability | [6 empty] | Volumes
Years (Date Installed) | LV | Grand Total | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
1931 | 1 | 1 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 0.99728 | 0.99775 | 0.99815 | 0.99848 | 0.99876 | 0.99899 | 0.99918 | 0.99728 | 0.00047189 | 0.00039755 | 0.00033348 | 0.00027852 | 0.00023161 | 0.00019176
1934 | 1 | 1 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 0.9953 | 0.99607 | 0.99672 | 0.99728 | 0.99775 | 0.99815 | 0.99848 | 0.9953 | 0.00076948 | 0.0006565 | 0.00055777 | 0.00047189 | 0.00039755 | 0.00033348
1949 | 1 | 1 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 0.95593 | 0.9611 | 0.96578 | 0.97 | 0.97378 | 0.97717 | 0.98018 | 0.95593 | 0.0051731 | 0.0046784 | 0.0042158 | 0.0037849 | 0.0033855 | 0.0030169
1950 | 61 | 61 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 0.95023 | 0.95593 | 0.9611 | 0.96578 | 0.97 | 0.97378 | 0.97717 | 57.9641 | 0.34766 | 0.31556 | 0.28539 | 0.25716 | 0.23088 | 0.20651
1951 | 24 | 24 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 0.94397 | 0.95023 | 0.95593 | 0.9611 | 0.96578 | 0.97 | 0.97378 | 22.6554 | 0.15017 | 0.13679 | 0.12415 | 0.11228 | 0.10118 | 0.090837
1952 | 23 | 23 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 0.93713 | 0.94397 | 0.95023 | 0.95593 | 0.9611 | 0.96578 | 0.97 | 21.554 | 0.15743 | 0.14391 | 0.13109 | 0.11898 | 0.1076 | 0.096962
1953 | 91 | 91 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 0.92967 | 0.93713 | 0.94397 | 0.95023 | 0.95593 | 0.9611 | 0.96578 | 84.5998 | 0.67899 | 0.62286 | 0.56938 | 0.51864 | 0.47075 | 0.42574
1954 | 62 | 62 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 0.92156 | 0.92967 | 0.93713 | 0.94397 | 0.95023 | 0.95593 | 0.9611 | 57.1369 | 0.50255 | 0.46261 | 0.42437 | 0.38793 | 0.35336 | 0.32073
1955 | 90 | 90 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 0.91279 | 0.92156 | 0.92967 | 0.93713 | 0.94397 | 0.95023 | 0.95593 | 82.1509 | 0.78976 | 0.7295 | 0.67153 | 0.61602 | 0.56312 | 0.51295
1956 | 83 | 83 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 0.90332 | 0.91279 | 0.92156 | 0.92967 | 0.93713 | 0.94397 | 0.95023 | 74.9755 | 0.78581 | 0.72833 | 0.67276 | 0.6193 | 0.56811 | 0.51932
1957 | 174 | 174 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 0.89314 | 0.90332 | 0.91279 | 0.92156 | 0.92967 | 0.93713 | 0.94397 | 155.4063 | 1.7714 | 1.6474 | 1.5269 | 1.4104 | 1.2983 | 1.191
1958 | 202 | 202 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 0.88223 | 0.89314 | 0.90332 | 0.91279 | 0.92156 | 0.92967 | 0.93713 | 178.2104 | 2.2038 | 2.0564 | 1.9125 | 1.7726 | 1.6373 | 1.5072
1959 | 324 | 324 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.91279 | 0.92156 | 0.92967 | 282.0667 | 3.7757 | 3.5348 | 3.2984 | 3.0675 | 2.8431 | 2.6262
1960 | 412 | 412 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.91279 | 0.92156 | 353.566 | 5.1114 | 4.8012 | 4.4949 | 4.1943 | 3.9006 | 3.6153
1961 | 570 | 570 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.91279 | 481.6527 | 7.5041 | 7.0716 | 6.6424 | 6.2187 | 5.8027 | 5.3965
1962 | 510 | 510 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 423.8505 | 7.1019 | 6.7142 | 6.3273 | 5.9432 | 5.5641 | 5.1919
1963 | 502 | 502 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 409.8315 | 7.3704 | 6.9905 | 6.6089 | 6.228 | 5.85 | 5.4768
1964 | 767 | 767 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 614.3413 | 11.8355 | 11.2611 | 10.6806 | 10.0977 | 9.5157 | 8.9381
1965 | 966 | 966 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 758.1164 | 15.6172 | 14.9063 | 14.1829 | 13.4518 | 12.7175 | 11.9846
1966 | 766 | 766 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 588.2225 | 12.934 | 12.3838 | 11.8201 | 11.2465 | 10.6667 | 10.0845
1967 | 955 | 955 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 716.5689 | 16.7895 | 16.1253 | 15.4394 | 14.7365 | 14.0214 | 13.2986
1968 | 957 | 957 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 700.6058 | 17.4638 | 16.8246 | 16.1591 | 15.4717 | 14.7674 | 14.0507
1969 | 769 | 769 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 548.4521 | 14.5217 | 14.0331 | 13.5195 | 12.9847 | 12.4323 | 11.8664
1970 | 501 | 501 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 347.5535 | 9.7605 | 9.4608 | 9.1425 | 8.8079 | 8.4594 | 8.0996
1971 | 1004 | 1004 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 0.67368 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 676.3756 | 20.1189 | 19.56 | 18.9594 | 18.3214 | 17.6509 | 16.9527
1972 | 1109 | 1109 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 0.65313 | 0.67368 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 724.3226 | 22.7895 | 22.2229 | 21.6056 | 20.9422 | 20.2375 | 19.4969
1973 | 849 | 849 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 0.63212 | 0.65313 | 0.67368 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 536.6704 | 17.8381 | 17.4466 | 17.0129 | 16.5403 | 16.0324 | 15.4929
1974 | 845 | 845 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 0.6107 | 0.63212 | 0.65313 | 0.67368 | 0.69372 | 0.7132 | 0.73209 | 516.0432 | 18.0987 | 17.7541 | 17.3644 | 16.9327 | 16.4623 | 15.9568
1975 | 814 | 814 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 0.58893 | 0.6107 | 0.63212 | 0.65313 | 0.67368 | 0.69372 | 0.7132 | 479.3906 | 17.7208 | 17.4347 | 17.1027 | 16.7274 | 16.3115 | 15.8584
1976 | 917 | 917 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 0.56687 | 0.58893 | 0.6107 | 0.63212 | 0.65313 | 0.67368 | 0.69372 | 519.8194 | 20.2312 | 19.9632 | 19.6409 | 19.2668 | 18.844 | 18.3755
1977 | 757 | 757 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 0.54458 | 0.56687 | 0.58893 | 0.6107 | 0.63212 | 0.65313 | 0.67368 | 412.2443 | 16.876 | 16.7012 | 16.4799 | 16.2139 | 15.9051 | 15.556
1978 | 1097 | 1097 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 0.52212 | 0.54458 | 0.56687 | 0.58893 | 0.6107 | 0.63212 | 0.65313 | 572.7607 | 24.6395 | 24.4557 | 24.2024 | 23.8818 | 23.4962 | 23.0488
1979 | 703 | 703 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 0.49955 | 0.52212 | 0.54458 | 0.56687 | 0.58893 | 0.6107 | 0.63212 | 351.1848 | 15.8624 | 15.79 | 15.6721 | 15.5098 | 15.3044 | 15.0573
1980 | 1174 | 1174 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 0.47695 | 0.49955 | 0.52212 | 0.54458 | 0.56687 | 0.58893 | 0.6107 | 559.9394 | 26.5342 | 26.49 | 26.369 | 26.1722 | 25.9012 | 25.5581
1981 | 843 | 843 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 0.45438 | 0.47695 | 0.49955 | 0.52212 | 0.54458 | 0.56687 | 0.58893 | 383.0394 | 19.0295 | 19.0531 | 19.0213 | 18.9345 | 18.7932 | 18.5986
1982 | 817 | 817 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 0.4319 | 0.45438 | 0.47695 | 0.49955 | 0.52212 | 0.54458 | 0.56687 | 352.8594 | 18.3663 | 18.4426 | 18.4655 | 18.4347 | 18.3505 | 18.2136
1983 | 1176 | 1176 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 0.40957 | 0.4319 | 0.45438 | 0.47695 | 0.49955 | 0.52212 | 0.54458 | 481.6595 | 26.2506 | 26.4366 | 26.5465 | 26.5794 | 26.5351 | 26.4139
1984 | 1258 | 1258 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 0.38747 | 0.40957 | 0.4319 | 0.45438 | 0.47695 | 0.49955 | 0.52212 | 487.4425 | 27.8021 | 28.081 | 28.28 | 28.3975 | 28.4327 | 28.3853
1985 | 1468 | 1468 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 0.36566 | 0.38747 | 0.40957 | 0.4319 | 0.45438 | 0.47695 | 0.49955 | 536.7851 | 32.027 | 32.4432 | 32.7686 | 33.0008 | 33.138 | 33.1791
1986 | 1939 | 1939 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 0.34418 | 0.36566 | 0.38747 | 0.40957 | 0.4319 | 0.45438 | 0.47695 | 667.3728 | 41.637 | 42.3026 | 42.8524 | 43.2823 | 43.589 | 43.7701
1987 | 1229 | 1229 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 0.32311 | 0.34418 | 0.36566 | 0.38747 | 0.40957 | 0.4319 | 0.45438 | 397.1035 | 25.8986 | 26.3909 | 26.8128 | 27.1612 | 27.4337 | 27.6281
1988 | 1616 | 1616 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 0.30249 | 0.32311 | 0.34418 | 0.36566 | 0.38747 | 0.40957 | 0.4319 | 488.8286 | 33.3189 | 34.0539 | 34.7011 | 35.2558 | 35.714 | 36.0723
1989 | 960 | 960 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 0.28238 | 0.30249 | 0.32311 | 0.34418 | 0.36566 | 0.38747 | 0.40957 | 0 | 290.3932 | 19.7934 | 20.23 | 20.6145 | 20.9441 | 21.2163
1990 | 1505 | 1505 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 0.26282 | 0.28238 | 0.30249 | 0.32311 | 0.34418 | 0.36566 | 0.38747 | 0 | 0 | 455.2519 | 31.0303 | 31.7148 | 32.3175 | 32.8342
1991 | 915 | 915 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 0.24386 | 0.26282 | 0.28238 | 0.30249 | 0.32311 | 0.34418 | 0.36566 | 0 | 0 | 0 | 276.7811 | 18.8656 | 19.2817 | 19.6482
1992 | 747 | 747 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 0.22554 | 0.24386 | 0.26282 | 0.28238 | 0.30249 | 0.32311 | 0.34418 | 0 | 0 | 0 | 0 | 225.9622 | 15.4017 | 15.7415
1993 | 850 | 850 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 0.20788 | 0.22554 | 0.24386 | 0.26282 | 0.28238 | 0.30249 | 0.32311 | 0 | 0 | 0 | 0 | 0 | 257.119 | 17.5254
1994 | 621 | 621 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 0.19093 | 0.20788 | 0.22554 | 0.24386 | 0.26282 | 0.28238 | 0.30249 | 0 | 0 | 0 | 0 | 0 | 0 | 187.8481
1995 | 283 | 283 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 0.17471 | 0.19093 | 0.20788 | 0.22554 | 0.24386 | 0.26282 | 0.28238 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1996 | 447 | 447 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 0.15924 | 0.17471 | 0.19093 | 0.20788 | 0.22554 | 0.24386 | 0.26282 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1997 | 531 | 531 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 0.14455 | 0.15924 | 0.17471 | 0.19093 | 0.20788 | 0.22554 | 0.24386 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1998 | 499 | 499 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 0.13063 | 0.14455 | 0.15924 | 0.17471 | 0.19093 | 0.20788 | 0.22554 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1999 | 316 | 316 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 0.1175 | 0.13063 | 0.14455 | 0.15924 | 0.17471 | 0.19093 | 0.20788 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2000 | 323 | 323 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 0.10517 | 0.1175 | 0.13063 | 0.14455 | 0.15924 | 0.17471 | 0.19093 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 475 | 475 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 0.093637 | 0.10517 | 0.1175 | 0.13063 | 0.14455 | 0.15924 | 0.17471 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2002 | 413 | 413 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 0.082893 | 0.093637 | 0.10517 | 0.1175 | 0.13063 | 0.14455 | 0.15924 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 392 | 392 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 0.072932 | 0.082893 | 0.093637 | 0.10517 | 0.1175 | 0.13063 | 0.14455 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 288 | 288 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 0.063742 | 0.072932 | 0.082893 | 0.093637 | 0.10517 | 0.1175 | 0.13063 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 315 | 315 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 0.055307 | 0.063742 | 0.072932 | 0.082893 | 0.093637 | 0.10517 | 0.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 429 | 429 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 0.04761 | 0.055307 | 0.063742 | 0.072932 | 0.082893 | 0.093637 | 0.10517 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 497 | 497 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 0.040629 | 0.04761 | 0.055307 | 0.063742 | 0.072932 | 0.082893 | 0.093637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 526 | 526 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0.034338 | 0.040629 | 0.04761 | 0.055307 | 0.063742 | 0.072932 | 0.082893 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 514 | 514 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 0.02871 | 0.034338 | 0.040629 | 0.04761 | 0.055307 | 0.063742 | 0.072932 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 606 | 606 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 0.023717 | 0.02871 | 0.034338 | 0.040629 | 0.04761 | 0.055307 | 0.063742 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011 | 528 | 528 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 0.019326 | 0.023717 | 0.02871 | 0.034338 | 0.040629 | 0.04761 | 0.055307 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012 | 639 | 639 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 0.015504 | 0.019326 | 0.023717 | 0.02871 | 0.034338 | 0.040629 | 0.04761 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013 | 613 | 613 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 0.012214 | 0.015504 | 0.019326 | 0.023717 | 0.02871 | 0.034338 | 0.040629 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014 | 800 | 800 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 0.0094214 | 0.012214 | 0.015504 | 0.019326 | 0.023717 | 0.02871 | 0.034338 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015 | 1111 | 1111 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 0.0070867 | 0.0094214 | 0.012214 | 0.015504 | 0.019326 | 0.023717 | 0.02871 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016 | 1052 | 1052 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 0.0051712 | 0.0070867 | 0.0094214 | 0.012214 | 0.015504 | 0.019326 | 0.023717 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017 | 765 | 765 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 0.0036347 | 0.0051712 | 0.0070867 | 0.0094214 | 0.012214 | 0.015504 | 0.019326 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018 | 893 | 893 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 0.0024364 | 0.0036347 | 0.0051712 | 0.0070867 | 0.0094214 | 0.012214 | 0.015504 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019 | 777 | 777 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 0.001535 | 0.0024364 | 0.0036347 | 0.0051712 | 0.0070867 | 0.0094214 | 0.012214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020 | 2848 | 2848 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 0.0008886 | 0.001535 | 0.0024364 | 0.0036347 | 0.0051712 | 0.0070867 | 0.0094214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 1381 | 1381 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0.00045506 | 0.0008886 | 0.001535 | 0.0024364 | 0.0036347 | 0.0051712 | 0.0070867 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 1270 | 1270 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 0.000192 | 0.00045506 | 0.0008886 | 0.001535 | 0.0024364 | 0.0036347 | 0.0051712 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 | 392 | 392 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 5.6894e-05 | 0.000192 | 0.00045506 | 0.0008886 | 0.001535 | 0.0024364 | 0.0036347 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 1 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 7.1119e-06 | 5.6894e-05 | 0.000192 | 0.00045506 | 0.0008886 | 0.001535 | 0.0024364 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 1 | 1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 0 | 7.1119e-06 | 5.6894e-05 | 0.000192 | 0.00045506 | 0.0008886 | 0.001535 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grand Total | 53950 | 53950 | [14 empty] | 16106.2709
[18 empty] | 1657.9256 | 1836.3374 | 1681.8513 | 1642.2915 | 2485.6985 | 2424.559

## OUTPUT<Forecast-HV-WOOD>
Exclude | NO
User Status List Desc | INSV
Crossarm Material | wood
Count of SAP ID | Voltage |  |  | Age | [6 empty] | Failure Probability | [6 empty] | Volumes
Years (Date Installed) | HV | Grand Total | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
1931 | 1 | 1 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 0.99321 | 0.99422 | 0.9951 | 0.99585 | 0.99651 | 0.99707 | 0.99755 | 0.99321 | 0.00101 | 0.00087657 | 0.00075802 | 0.00065309 | 0.00056059 | 0.00047939
1934 | 1 | 1 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 0.98921 | 0.99072 | 0.99205 | 0.99321 | 0.99422 | 0.9951 | 0.99585 | 0.98921 | 0.0015116 | 0.0013262 | 0.0011594 | 0.00101 | 0.00087657 | 0.00075802
1949 | 1 | 1 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 0.92853 | 0.93569 | 0.94229 | 0.94836 | 0.95392 | 0.959 | 0.96363 | 0.92853 | 0.0071577 | 0.0066014 | 0.0060692 | 0.0055624 | 0.0050817 | 0.0046277
1950 | 9 | 9 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 0.92079 | 0.92853 | 0.93569 | 0.94229 | 0.94836 | 0.95392 | 0.959 | 8.2871 | 0.069633 | 0.064419 | 0.059412 | 0.054623 | 0.050062 | 0.045736
1951 | 18 | 18 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 0.91246 | 0.92079 | 0.92853 | 0.93569 | 0.94229 | 0.94836 | 0.95392 | 16.4242 | 0.15007 | 0.13927 | 0.12884 | 0.11882 | 0.10925 | 0.10012
1952 | 13 | 13 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 0.9035 | 0.91246 | 0.92079 | 0.92853 | 0.93569 | 0.94229 | 0.94836 | 11.7455 | 0.11644 | 0.10839 | 0.10058 | 0.09305 | 0.085818 | 0.0789
1953 | 11 | 11 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 0.8939 | 0.9035 | 0.91246 | 0.92079 | 0.92853 | 0.93569 | 0.94229 | 9.8329 | 0.10553 | 0.098528 | 0.091711 | 0.085106 | 0.078735 | 0.072615
1954 | 7 | 7 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 0.88366 | 0.8939 | 0.9035 | 0.91246 | 0.92079 | 0.92853 | 0.93569 | 6.1856 | 0.071717 | 0.067157 | 0.0627 | 0.058362 | 0.054159 | 0.050104
1955 | 4 | 4 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 0.87275 | 0.88366 | 0.8939 | 0.9035 | 0.91246 | 0.92079 | 0.92853 | 3.491 | 0.043633 | 0.040981 | 0.038376 | 0.035829 | 0.03335 | 0.030948
1956 | 5 | 5 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 0.86117 | 0.87275 | 0.88366 | 0.8939 | 0.9035 | 0.91246 | 0.92079 | 4.3059 | 0.057901 | 0.054542 | 0.051226 | 0.047969 | 0.044786 | 0.041687
1957 | 11 | 11 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 0.84891 | 0.86117 | 0.87275 | 0.88366 | 0.8939 | 0.9035 | 0.91246 | 9.338 | 0.13483 | 0.12738 | 0.11999 | 0.1127 | 0.10553 | 0.098528
1958 | 15 | 15 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 0.83598 | 0.84891 | 0.86117 | 0.87275 | 0.88366 | 0.8939 | 0.9035 | 12.5396 | 0.19406 | 0.18386 | 0.1737 | 0.16362 | 0.15368 | 0.14391
1959 | 41 | 41 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 0.82236 | 0.83598 | 0.84891 | 0.86117 | 0.87275 | 0.88366 | 0.8939 | 33.7168 | 0.55822 | 0.53042 | 0.50256 | 0.47479 | 0.44724 | 0.42005
1960 | 41 | 41 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 0.80807 | 0.82236 | 0.83598 | 0.84891 | 0.86117 | 0.87275 | 0.88366 | 33.131 | 0.58581 | 0.55822 | 0.53042 | 0.50256 | 0.47479 | 0.44724
1961 | 76 | 76 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 0.79312 | 0.80807 | 0.82236 | 0.83598 | 0.84891 | 0.86117 | 0.87275 | 60.2772 | 1.1363 | 1.0859 | 1.0348 | 0.98322 | 0.93158 | 0.88009
1962 | 45 | 45 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 0.77752 | 0.79312 | 0.80807 | 0.82236 | 0.83598 | 0.84891 | 0.86117 | 34.9883 | 0.70211 | 0.67283 | 0.64296 | 0.61268 | 0.58217 | 0.55159
1963 | 65 | 65 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 0.76128 | 0.77752 | 0.79312 | 0.80807 | 0.82236 | 0.83598 | 0.84891 | 49.4834 | 1.0553 | 1.0142 | 0.97186 | 0.92872 | 0.88499 | 0.84091
1964 | 85 | 85 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 0.74443 | 0.76128 | 0.77752 | 0.79312 | 0.80807 | 0.82236 | 0.83598 | 63.2769 | 1.4322 | 1.3801 | 1.3262 | 1.2709 | 1.2145 | 1.1573
1965 | 89 | 89 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 0.727 | 0.74443 | 0.76128 | 0.77752 | 0.79312 | 0.80807 | 0.82236 | 64.7027 | 1.5519 | 1.4996 | 1.445 | 1.3886 | 1.3307 | 1.2716
1966 | 84 | 84 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 0.709 | 0.727 | 0.74443 | 0.76128 | 0.77752 | 0.79312 | 0.80807 | 59.5561 | 1.5117 | 1.4647 | 1.4153 | 1.3638 | 1.3106 | 1.2559
1967 | 120 | 120 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 0.69048 | 0.709 | 0.727 | 0.74443 | 0.76128 | 0.77752 | 0.79312 | 82.8573 | 2.2228 | 2.1595 | 2.0924 | 2.0219 | 1.9483 | 1.8723
1968 | 140 | 140 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 0.67146 | 0.69048 | 0.709 | 0.727 | 0.74443 | 0.76128 | 0.77752 | 94.0048 | 2.662 | 2.5933 | 2.5195 | 2.4412 | 2.3588 | 2.2731
1969 | 64 | 64 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 0.652 | 0.67146 | 0.69048 | 0.709 | 0.727 | 0.74443 | 0.76128 | 41.7278 | 1.2458 | 1.2169 | 1.1855 | 1.1518 | 1.116 | 1.0783
1970 | 62 | 62 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 0.63212 | 0.652 | 0.67146 | 0.69048 | 0.709 | 0.727 | 0.74443 | 39.1915 | 1.2323 | 1.2069 | 1.1789 | 1.1484 | 1.1158 | 1.0811
1971 | 139 | 139 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 0.61188 | 0.63212 | 0.652 | 0.67146 | 0.69048 | 0.709 | 0.727 | 85.0513 | 2.8135 | 2.7628 | 2.7058 | 2.643 | 2.5747 | 2.5015
1972 | 131 | 131 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 0.59132 | 0.61188 | 0.63212 | 0.652 | 0.67146 | 0.69048 | 0.709 | 77.4632 | 2.6931 | 2.6515 | 2.6038 | 2.5501 | 2.4909 | 2.4265
1973 | 112 | 112 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 0.5705 | 0.59132 | 0.61188 | 0.63212 | 0.652 | 0.67146 | 0.69048 | 63.8957 | 2.3324 | 2.3025 | 2.267 | 2.2261 | 2.1802 | 2.1296
1974 | 121 | 121 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 0.54946 | 0.5705 | 0.59132 | 0.61188 | 0.63212 | 0.652 | 0.67146 | 66.4843 | 2.5459 | 2.5198 | 2.4875 | 2.4491 | 2.405 | 2.3554
1975 | 119 | 119 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 0.52825 | 0.54946 | 0.5705 | 0.59132 | 0.61188 | 0.63212 | 0.652 | 62.8622 | 2.5231 | 2.5038 | 2.4782 | 2.4464 | 2.4086 | 2.3653
1976 | 149 | 149 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 0.50694 | 0.52825 | 0.54946 | 0.5705 | 0.59132 | 0.61188 | 0.63212 | 75.5346 | 3.1753 | 3.1592 | 3.135 | 3.1029 | 3.0631 | 3.0159
1977 | 175 | 175 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 0.48558 | 0.50694 | 0.52825 | 0.54946 | 0.5705 | 0.59132 | 0.61188 | 84.9765 | 3.7386 | 3.7294 | 3.7105 | 3.6821 | 3.6444 | 3.5976
1978 | 208 | 208 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 0.46422 | 0.48558 | 0.50694 | 0.52825 | 0.54946 | 0.5705 | 0.59132 | 96.5576 | 4.4431 | 4.4436 | 4.4326 | 4.4102 | 4.3764 | 4.3316
1979 | 112 | 112 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 0.44292 | 0.46422 | 0.48558 | 0.50694 | 0.52825 | 0.54946 | 0.5705 | 49.6066 | 2.3859 | 2.3924 | 2.3927 | 2.3868 | 2.3747 | 2.3565
1980 | 258 | 258 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 0.42173 | 0.44292 | 0.46422 | 0.48558 | 0.50694 | 0.52825 | 0.54946 | 108.8055 | 5.467 | 5.4961 | 5.5111 | 5.5118 | 5.4981 | 5.4703
1981 | 230 | 230 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 0.4007 | 0.42173 | 0.44292 | 0.46422 | 0.48558 | 0.50694 | 0.52825 | 92.162 | 4.8351 | 4.8736 | 4.8996 | 4.913 | 4.9136 | 4.9014
1982 | 151 | 151 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 0.3799 | 0.4007 | 0.42173 | 0.44292 | 0.46422 | 0.48558 | 0.50694 | 57.3653 | 3.1411 | 3.1744 | 3.1996 | 3.2167 | 3.2255 | 3.2259
1983 | 208 | 208 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 0.35937 | 0.3799 | 0.4007 | 0.42173 | 0.44292 | 0.46422 | 0.48558 | 74.7495 | 4.2702 | 4.3268 | 4.3727 | 4.4075 | 4.431 | 4.4431
1984 | 269 | 269 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 0.33916 | 0.35937 | 0.3799 | 0.4007 | 0.42173 | 0.44292 | 0.46422 | 91.2354 | 5.4359 | 5.5225 | 5.5957 | 5.655 | 5.7 | 5.7305
1985 | 284 | 284 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 0.31933 | 0.33916 | 0.35937 | 0.3799 | 0.4007 | 0.42173 | 0.44292 | 90.6889 | 5.634 | 5.739 | 5.8304 | 5.9077 | 5.9704 | 6.0179
1986 | 348 | 348 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 0.2999 | 0.31933 | 0.33916 | 0.35937 | 0.3799 | 0.4007 | 0.42173 | 0 | 111.1258 | 6.9036 | 7.0323 | 7.1443 | 7.2391 | 7.3158
1987 | 267 | 267 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 0.28094 | 0.2999 | 0.31933 | 0.33916 | 0.35937 | 0.3799 | 0.4007 | 0 | 0 | 85.2603 | 5.2967 | 5.3955 | 5.4814 | 5.5541
1988 | 340 | 340 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 0.26247 | 0.28094 | 0.2999 | 0.31933 | 0.33916 | 0.35937 | 0.3799 | 0 | 0 | 0 | 108.5712 | 6.7449 | 6.8706 | 6.9801
1989 | 100 | 100 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 0.24454 | 0.26247 | 0.28094 | 0.2999 | 0.31933 | 0.33916 | 0.35937 | 0 | 0 | 0 | 0 | 31.9327 | 1.9838 | 2.0208
1990 | 184 | 184 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 0.22717 | 0.24454 | 0.26247 | 0.28094 | 0.2999 | 0.31933 | 0.33916 | 0 | 0 | 0 | 0 | 0 | 58.7562 | 3.6502
1991 | 124 | 124 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 0.21041 | 0.22717 | 0.24454 | 0.26247 | 0.28094 | 0.2999 | 0.31933 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5965
1992 | 87 | 87 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 0.19426 | 0.21041 | 0.22717 | 0.24454 | 0.26247 | 0.28094 | 0.2999 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1993 | 82 | 82 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 0.17877 | 0.19426 | 0.21041 | 0.22717 | 0.24454 | 0.26247 | 0.28094 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1994 | 47 | 47 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 0.16394 | 0.17877 | 0.19426 | 0.21041 | 0.22717 | 0.24454 | 0.26247 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1995 | 8 | 8 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 0.1498 | 0.16394 | 0.17877 | 0.19426 | 0.21041 | 0.22717 | 0.24454 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1996 | 26 | 26 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 0.13635 | 0.1498 | 0.16394 | 0.17877 | 0.19426 | 0.21041 | 0.22717 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1997 | 20 | 20 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 0.12361 | 0.13635 | 0.1498 | 0.16394 | 0.17877 | 0.19426 | 0.21041 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1998 | 29 | 29 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 0.11157 | 0.12361 | 0.13635 | 0.1498 | 0.16394 | 0.17877 | 0.19426 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1999 | 20 | 20 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 0.10025 | 0.11157 | 0.12361 | 0.13635 | 0.1498 | 0.16394 | 0.17877 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2000 | 31 | 31 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 0.089639 | 0.10025 | 0.11157 | 0.12361 | 0.13635 | 0.1498 | 0.16394 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 34 | 34 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 0.079731 | 0.089639 | 0.10025 | 0.11157 | 0.12361 | 0.13635 | 0.1498 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2002 | 11 | 11 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 0.07052 | 0.079731 | 0.089639 | 0.10025 | 0.11157 | 0.12361 | 0.13635 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 6 | 6 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 0.061995 | 0.07052 | 0.079731 | 0.089639 | 0.10025 | 0.11157 | 0.12361 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 6 | 6 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 0.054143 | 0.061995 | 0.07052 | 0.079731 | 0.089639 | 0.10025 | 0.11157 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 7 | 7 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 0.046946 | 0.054143 | 0.061995 | 0.07052 | 0.079731 | 0.089639 | 0.10025 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 7 | 7 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 0.040388 | 0.046946 | 0.054143 | 0.061995 | 0.07052 | 0.079731 | 0.089639 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 16 | 16 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 0.034446 | 0.040388 | 0.046946 | 0.054143 | 0.061995 | 0.07052 | 0.079731 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 2 | 2 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0.029098 | 0.034446 | 0.040388 | 0.046946 | 0.054143 | 0.061995 | 0.07052 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 12 | 12 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 0.024319 | 0.029098 | 0.034446 | 0.040388 | 0.046946 | 0.054143 | 0.061995 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 2 | 2 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 0.020081 | 0.024319 | 0.029098 | 0.034446 | 0.040388 | 0.046946 | 0.054143 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011 | 5 | 5 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 0.016358 | 0.020081 | 0.024319 | 0.029098 | 0.034446 | 0.040388 | 0.046946 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012 | 23 | 23 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 0.013118 | 0.016358 | 0.020081 | 0.024319 | 0.029098 | 0.034446 | 0.040388 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013 | 13 | 13 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 0.010332 | 0.013118 | 0.016358 | 0.020081 | 0.024319 | 0.029098 | 0.034446 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014 | 5 | 5 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 0.0079681 | 0.010332 | 0.013118 | 0.016358 | 0.020081 | 0.024319 | 0.029098 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015 | 5 | 5 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 0.0059925 | 0.0079681 | 0.010332 | 0.013118 | 0.016358 | 0.020081 | 0.024319 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016 | 6 | 6 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 0.0043721 | 0.0059925 | 0.0079681 | 0.010332 | 0.013118 | 0.016358 | 0.020081 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017 | 4 | 4 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 0.0030727 | 0.0043721 | 0.0059925 | 0.0079681 | 0.010332 | 0.013118 | 0.016358 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018 | 3 | 3 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 0.0020595 | 0.0030727 | 0.0043721 | 0.0059925 | 0.0079681 | 0.010332 | 0.013118 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019 | 3 | 3 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 0.0012974 | 0.0020595 | 0.0030727 | 0.0043721 | 0.0059925 | 0.0079681 | 0.010332 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020 | 16 | 16 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 0.00075103 | 0.0012974 | 0.0020595 | 0.0030727 | 0.0043721 | 0.0059925 | 0.0079681 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 3 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0.0003846 | 0.00075103 | 0.0012974 | 0.0020595 | 0.0030727 | 0.0043721 | 0.0059925 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 5 | 5 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 0.00016227 | 0.0003846 | 0.00075103 | 0.0012974 | 0.0020595 | 0.0030727 | 0.0043721 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 4.8083e-05 | 0.00016227 | 0.0003846 | 0.00075103 | 0.0012974 | 0.0020595 | 0.0030727 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grand Total | 5582 | 5582
[17 empty] | 1919.4129 | 471.3217 | 451.949 | 480.1142 | 409.7035 | 437.937 | 421.6963

## OUTPUT<Forecast-ST-WOOD>
Exclude | NO
User Status List Desc | INSV
Crossarm Material | wood
Count of SAP ID | Voltage |  |  | Age | [6 empty] | Failure Probability | [6 empty] | Volumes
Years (Date Installed) | ST | Grand Total | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
1938 | 2 | 2 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 0.95949 | 0.96378 | 0.96769 | 0.97126 | 0.9745 | 0.97744 | 0.98009 | 1.919 | 0.0085721 | 0.0078314 | 0.0071344 | 0.0064809 | 0.0058702 | 0.0053017
1944 | 1 | 1 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 0.9248 | 0.93175 | 0.93821 | 0.9442 | 0.94972 | 0.95481 | 0.95949 | 0.9248 | 0.0069535 | 0.0064587 | 0.0059829 | 0.0055271 | 0.005092 | 0.0046782
1952 | 2 | 2 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 0.84955 | 0.86097 | 0.8718 | 0.88204 | 0.8917 | 0.9008 | 0.90934 | 1.6991 | 0.022832 | 0.021654 | 0.020485 | 0.01933 | 0.018193 | 0.017079
1953 | 5 | 5 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 0.83755 | 0.84955 | 0.86097 | 0.8718 | 0.88204 | 0.8917 | 0.9008 | 4.1877 | 0.060032 | 0.057079 | 0.054135 | 0.051213 | 0.048325 | 0.045483
1954 | 8 | 8 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 0.82495 | 0.83755 | 0.84955 | 0.86097 | 0.8718 | 0.88204 | 0.8917 | 6.5996 | 0.10077 | 0.096051 | 0.091327 | 0.086617 | 0.081941 | 0.077321
1956 | 1 | 1 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 0.79801 | 0.81177 | 0.82495 | 0.83755 | 0.84955 | 0.86097 | 0.8718 | 0.79801 | 0.013761 | 0.013182 | 0.012596 | 0.012006 | 0.011416 | 0.010827
1958 | 1 | 1 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 0.76879 | 0.78368 | 0.79801 | 0.81177 | 0.82495 | 0.83755 | 0.84955 | 0.76879 | 0.014887 | 0.01433 | 0.013761 | 0.013182 | 0.012596 | 0.012006
1959 | 2 | 2 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 0.75336 | 0.76879 | 0.78368 | 0.79801 | 0.81177 | 0.82495 | 0.83755 | 1.5067 | 0.030857 | 0.029775 | 0.028661 | 0.027522 | 0.026363 | 0.025192
1960 | 8 | 8 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 0.73741 | 0.75336 | 0.76879 | 0.78368 | 0.79801 | 0.81177 | 0.82495 | 5.8993 | 0.12761 | 0.12343 | 0.1191 | 0.11464 | 0.11009 | 0.10545
1962 | 3 | 3 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 0.70403 | 0.72096 | 0.73741 | 0.75336 | 0.76879 | 0.78368 | 0.79801 | 2.1121 | 0.050789 | 0.049358 | 0.047854 | 0.046286 | 0.044662 | 0.042991
1963 | 7 | 7 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 0.68665 | 0.70403 | 0.72096 | 0.73741 | 0.75336 | 0.76879 | 0.78368 | 4.8065 | 0.12166 | 0.11851 | 0.11517 | 0.11166 | 0.108 | 0.10421
1964 | 28 | 28 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 0.66885 | 0.68665 | 0.70403 | 0.72096 | 0.73741 | 0.75336 | 0.76879 | 18.7278 | 0.49839 | 0.48662 | 0.47403 | 0.46067 | 0.44664 | 0.432
1965 | 23 | 23 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 0.65066 | 0.66885 | 0.68665 | 0.70403 | 0.72096 | 0.73741 | 0.75336 | 14.9652 | 0.41831 | 0.40939 | 0.39973 | 0.38938 | 0.37841 | 0.36688
1966 | 19 | 19 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 0.63212 | 0.65066 | 0.66885 | 0.68665 | 0.70403 | 0.72096 | 0.73741 | 12.0103 | 0.35228 | 0.34556 | 0.33819 | 0.33021 | 0.32166 | 0.3126
1967 | 2 | 2 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 0.61326 | 0.63212 | 0.65066 | 0.66885 | 0.68665 | 0.70403 | 0.72096 | 1.2265 | 0.037716 | 0.037082 | 0.036375 | 0.035599 | 0.034759 | 0.033859
1968 | 7 | 7 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 0.59413 | 0.61326 | 0.63212 | 0.65066 | 0.66885 | 0.68665 | 0.70403 | 4.1589 | 0.13395 | 0.13201 | 0.12979 | 0.12731 | 0.1246 | 0.12166
1969 | 8 | 8 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 0.57475 | 0.59413 | 0.61326 | 0.63212 | 0.65066 | 0.66885 | 0.68665 | 4.598 | 0.155 | 0.15309 | 0.15086 | 0.14833 | 0.1455 | 0.1424
1970 | 3 | 3 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 0.55518 | 0.57475 | 0.59413 | 0.61326 | 0.63212 | 0.65066 | 0.66885 | 1.6655 | 0.058713 | 0.058123 | 0.057409 | 0.056574 | 0.055623 | 0.054563
1971 | 5 | 5 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 0.53546 | 0.55518 | 0.57475 | 0.59413 | 0.61326 | 0.63212 | 0.65066 | 2.6773 | 0.098623 | 0.097855 | 0.096872 | 0.095681 | 0.09429 | 0.092705
1972 | 1 | 1 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 0.51562 | 0.53546 | 0.55518 | 0.57475 | 0.59413 | 0.61326 | 0.63212 | 0.51562 | 0.019835 | 0.019725 | 0.019571 | 0.019374 | 0.019136 | 0.018858
1974 | 15 | 15 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 0.4758 | 0.49572 | 0.51562 | 0.53546 | 0.55518 | 0.57475 | 0.59413 | 7.137 | 0.29881 | 0.2985 | 0.29752 | 0.29587 | 0.29356 | 0.29062
1975 | 4 | 4 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 0.4559 | 0.4758 | 0.49572 | 0.51562 | 0.53546 | 0.55518 | 0.57475 | 1.8236 | 0.079585 | 0.079683 | 0.0796 | 0.079338 | 0.078899 | 0.078284
1976 | 3 | 3 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 0.43608 | 0.4559 | 0.4758 | 0.49572 | 0.51562 | 0.53546 | 0.55518 | 1.3082 | 0.059482 | 0.059689 | 0.059762 | 0.0597 | 0.059504 | 0.059174
1977 | 2 | 2 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 0.41636 | 0.43608 | 0.4559 | 0.4758 | 0.49572 | 0.51562 | 0.53546 | 0.83273 | 0.039427 | 0.039654 | 0.039793 | 0.039841 | 0.0398 | 0.039669
1980 | 1 | 1 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 0.35834 | 0.37745 | 0.39681 | 0.41636 | 0.43608 | 0.4559 | 0.4758 | 0.35834 | 0.019114 | 0.019356 | 0.019556 | 0.019714 | 0.019827 | 0.019896
1981 | 3 | 3 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 0.3395 | 0.35834 | 0.37745 | 0.39681 | 0.41636 | 0.43608 | 0.4559 | 1.0185 | 0.056497 | 0.057343 | 0.058069 | 0.058669 | 0.059141 | 0.059482
1982 | 14 | 14 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 0.32099 | 0.3395 | 0.35834 | 0.37745 | 0.39681 | 0.41636 | 0.43608 | 4.4939 | 0.25917 | 0.26365 | 0.2676 | 0.27099 | 0.27379 | 0.27599
1983 | 14 | 14 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 0.30284 | 0.32099 | 0.3395 | 0.35834 | 0.37745 | 0.39681 | 0.41636 | 4.2397 | 0.25416 | 0.25917 | 0.26365 | 0.2676 | 0.27099 | 0.27379
1984 | 4 | 4 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 0.28508 | 0.30284 | 0.32099 | 0.3395 | 0.35834 | 0.37745 | 0.39681 | 0 | 1.2114 | 0.072617 | 0.074047 | 0.07533 | 0.076458 | 0.077425
1985 | 3 | 3 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 0.26774 | 0.28508 | 0.30284 | 0.32099 | 0.3395 | 0.35834 | 0.37745 | 0 | 0 | 0.90852 | 0.054463 | 0.055535 | 0.056497 | 0.057343
1986 | 3 | 3 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 0.25086 | 0.26774 | 0.28508 | 0.30284 | 0.32099 | 0.3395 | 0.35834 | 0 | 0 | 0 | 0.90852 | 0.054463 | 0.055535 | 0.056497
1987 | 1 | 1 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 0.23446 | 0.25086 | 0.26774 | 0.28508 | 0.30284 | 0.32099 | 0.3395 | 0 | 0 | 0 | 0 | 0.30284 | 0.018154 | 0.018512
1988 | 6 | 6 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 0.21857 | 0.23446 | 0.25086 | 0.26774 | 0.28508 | 0.30284 | 0.32099 | 0 | 0 | 0 | 0 | 0 | 1.817 | 0.10893
1989 | 8 | 8 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 0.20321 | 0.21857 | 0.23446 | 0.25086 | 0.26774 | 0.28508 | 0.30284 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4227
1990 | 3 | 3 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 0.18841 | 0.20321 | 0.21857 | 0.23446 | 0.25086 | 0.26774 | 0.28508 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1993 | 8 | 8 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 0.14747 | 0.16053 | 0.17418 | 0.18841 | 0.20321 | 0.21857 | 0.23446 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1995 | 1 | 1 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 0.12319 | 0.13502 | 0.14747 | 0.16053 | 0.17418 | 0.18841 | 0.20321 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1997 | 1 | 1 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 0.10137 | 0.11197 | 0.12319 | 0.13502 | 0.14747 | 0.16053 | 0.17418 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1998 | 1 | 1 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 0.091388 | 0.10137 | 0.11197 | 0.12319 | 0.13502 | 0.14747 | 0.16053 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2000 | 1 | 1 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 0.073257 | 0.082019 | 0.091388 | 0.10137 | 0.11197 | 0.12319 | 0.13502 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 2 | 2 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 0.065094 | 0.073257 | 0.082019 | 0.091388 | 0.10137 | 0.11197 | 0.12319 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 1 | 1 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 0.050525 | 0.057521 | 0.065094 | 0.073257 | 0.082019 | 0.091388 | 0.10137 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012 | 2 | 2 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 0.01064 | 0.013272 | 0.016299 | 0.019746 | 0.023638 | 0.027997 | 0.032845 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013 | 1 | 1 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 0.0083784 | 0.01064 | 0.013272 | 0.016299 | 0.019746 | 0.023638 | 0.027997 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020 | 1 | 1 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 0.00060845 | 0.0010512 | 0.0016687 | 0.0024898 | 0.0035432 | 0.0048572 | 0.0064597 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grand Total | 239 | 239
[17 empty] | 112.9789 | 27.2049 | 26.9311 | 26.9374 | 26.3333 | 27.8081 | 5.8644

## OUTPUT<Forecast-LV-STEEL>
Exclude | NO
User Status List Desc | INSV
Crossarm Material | steel
Count of SAP ID | Voltage |  |  | Age | [6 empty] | Failure Probability | [6 empty] | Volumes
Years (Date Installed) | LV | Grand Total | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
1957 | 1 | 1 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 0.89314 | 0.90332 | 0.91279 | 0.92156 | 0.92967 | 0.93713 | 0.94397 | 0.89314 | 0.01018 | 0.0094676 | 0.0087751 | 0.0081056 | 0.0074614 | 0.0068446
1960 | 1 | 1 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.91279 | 0.92156 | 0.85817 | 0.012406 | 0.011653 | 0.01091 | 0.01018 | 0.0094676 | 0.0087751
1961 | 1 | 1 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.91279 | 0.845 | 0.013165 | 0.012406 | 0.011653 | 0.01091 | 0.01018 | 0.0094676
1962 | 1 | 1 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.83108 | 0.013925 | 0.013165 | 0.012406 | 0.011653 | 0.01091 | 0.01018
1964 | 1 | 1 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 0.80097 | 0.015431 | 0.014682 | 0.013925 | 0.013165 | 0.012406 | 0.011653
1965 | 2 | 2 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 1.5696 | 0.032334 | 0.030862 | 0.029364 | 0.02785 | 0.02633 | 0.024813
1967 | 1 | 1 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 0.75033 | 0.017581 | 0.016885 | 0.016167 | 0.015431 | 0.014682 | 0.013925
1970 | 4 | 4 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 2.7749 | 0.077928 | 0.075535 | 0.072994 | 0.070322 | 0.06754 | 0.064668
1971 | 1 | 1 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 0.67368 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 0.67368 | 0.020039 | 0.019482 | 0.018884 | 0.018248 | 0.017581 | 0.016885
1972 | 2 | 2 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 0.65313 | 0.67368 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 1.3063 | 0.041099 | 0.040077 | 0.038964 | 0.037768 | 0.036497 | 0.035161
1974 | 1 | 1 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 0.6107 | 0.63212 | 0.65313 | 0.67368 | 0.69372 | 0.7132 | 0.73209 | 0.6107 | 0.021419 | 0.021011 | 0.02055 | 0.020039 | 0.019482 | 0.018884
1975 | 2 | 2 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 0.58893 | 0.6107 | 0.63212 | 0.65313 | 0.67368 | 0.69372 | 0.7132 | 1.1779 | 0.04354 | 0.042837 | 0.042021 | 0.041099 | 0.040077 | 0.038964
1978 | 8 | 8 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 0.52212 | 0.54458 | 0.56687 | 0.58893 | 0.6107 | 0.63212 | 0.65313 | 4.1769 | 0.17969 | 0.17835 | 0.1765 | 0.17416 | 0.17135 | 0.16809
1979 | 1 | 1 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 0.49955 | 0.52212 | 0.54458 | 0.56687 | 0.58893 | 0.6107 | 0.63212 | 0.49955 | 0.022564 | 0.022461 | 0.022293 | 0.022062 | 0.02177 | 0.021419
1980 | 15 | 15 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 0.47695 | 0.49955 | 0.52212 | 0.54458 | 0.56687 | 0.58893 | 0.6107 | 7.1543 | 0.33902 | 0.33846 | 0.33691 | 0.3344 | 0.33094 | 0.32655
1981 | 15 | 15 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 0.45438 | 0.47695 | 0.49955 | 0.52212 | 0.54458 | 0.56687 | 0.58893 | 6.8156 | 0.3386 | 0.33902 | 0.33846 | 0.33691 | 0.3344 | 0.33094
1982 | 17 | 17 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 0.20689 | 0.21991 | 0.23331 | 0.24707 | 0.26117 | 0.27561 | 0.29036 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1983 | 4 | 4 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 0.19426 | 0.20689 | 0.21991 | 0.23331 | 0.24707 | 0.26117 | 0.27561 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1984 | 9 | 9 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 0.18204 | 0.19426 | 0.20689 | 0.21991 | 0.23331 | 0.24707 | 0.26117 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1985 | 135 | 135 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 0.17022 | 0.18204 | 0.19426 | 0.20689 | 0.21991 | 0.23331 | 0.24707 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1986 | 101 | 101 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 0.15881 | 0.17022 | 0.18204 | 0.19426 | 0.20689 | 0.21991 | 0.23331 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1987 | 75 | 75 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 0.14784 | 0.15881 | 0.17022 | 0.18204 | 0.19426 | 0.20689 | 0.21991 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1988 | 104 | 104 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 0.13729 | 0.14784 | 0.15881 | 0.17022 | 0.18204 | 0.19426 | 0.20689 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1989 | 108 | 108 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 0.12718 | 0.13729 | 0.14784 | 0.15881 | 0.17022 | 0.18204 | 0.19426 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1990 | 187 | 187 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 0.1175 | 0.12718 | 0.13729 | 0.14784 | 0.15881 | 0.17022 | 0.18204 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1991 | 162 | 162 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 0.10827 | 0.1175 | 0.12718 | 0.13729 | 0.14784 | 0.15881 | 0.17022 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1992 | 412 | 412 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 0.099471 | 0.10827 | 0.1175 | 0.12718 | 0.13729 | 0.14784 | 0.15881 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1993 | 208 | 208 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 0.091112 | 0.099471 | 0.10827 | 0.1175 | 0.12718 | 0.13729 | 0.14784 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1994 | 137 | 137 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 0.083189 | 0.091112 | 0.099471 | 0.10827 | 0.1175 | 0.12718 | 0.13729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1995 | 283 | 283 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 0.075699 | 0.083189 | 0.091112 | 0.099471 | 0.10827 | 0.1175 | 0.12718 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1996 | 390 | 390 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 0.068636 | 0.075699 | 0.083189 | 0.091112 | 0.099471 | 0.10827 | 0.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1997 | 522 | 522 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 0.061995 | 0.068636 | 0.075699 | 0.083189 | 0.091112 | 0.099471 | 0.10827 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1998 | 701 | 701 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 0.055769 | 0.061995 | 0.068636 | 0.075699 | 0.083189 | 0.091112 | 0.099471 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1999 | 608 | 608 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 0.049951 | 0.055769 | 0.061995 | 0.068636 | 0.075699 | 0.083189 | 0.091112 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2000 | 676 | 676 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 0.044532 | 0.049951 | 0.055769 | 0.061995 | 0.068636 | 0.075699 | 0.083189 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 1159 | 1159 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 0.039502 | 0.044532 | 0.049951 | 0.055769 | 0.061995 | 0.068636 | 0.075699 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2002 | 765 | 765 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 0.034851 | 0.039502 | 0.044532 | 0.049951 | 0.055769 | 0.061995 | 0.068636 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 1171 | 1171 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 0.030567 | 0.034851 | 0.039502 | 0.044532 | 0.049951 | 0.055769 | 0.061995 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 1517 | 1517 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 0.026639 | 0.030567 | 0.034851 | 0.039502 | 0.044532 | 0.049951 | 0.055769 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 862 | 862 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 0.023054 | 0.026639 | 0.030567 | 0.034851 | 0.039502 | 0.044532 | 0.049951 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 897 | 897 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 0.019798 | 0.023054 | 0.026639 | 0.030567 | 0.034851 | 0.039502 | 0.044532 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 870 | 870 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 0.016859 | 0.019798 | 0.023054 | 0.026639 | 0.030567 | 0.034851 | 0.039502 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 951 | 951 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0.014222 | 0.016859 | 0.019798 | 0.023054 | 0.026639 | 0.030567 | 0.034851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 1145 | 1145 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 0.011871 | 0.014222 | 0.016859 | 0.019798 | 0.023054 | 0.026639 | 0.030567 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 1022 | 1022 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 0.0097914 | 0.011871 | 0.014222 | 0.016859 | 0.019798 | 0.023054 | 0.026639 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011 | 1160 | 1160 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 0.0079681 | 0.0097914 | 0.011871 | 0.014222 | 0.016859 | 0.019798 | 0.023054 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012 | 1232 | 1232 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 0.0063848 | 0.0079681 | 0.0097914 | 0.011871 | 0.014222 | 0.016859 | 0.019798 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013 | 1290 | 1290 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 0.0050252 | 0.0063848 | 0.0079681 | 0.0097914 | 0.011871 | 0.014222 | 0.016859 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014 | 1139 | 1139 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 0.0038729 | 0.0050252 | 0.0063848 | 0.0079681 | 0.0097914 | 0.011871 | 0.014222 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015 | 935 | 935 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 0.0029112 | 0.0038729 | 0.0050252 | 0.0063848 | 0.0079681 | 0.0097914 | 0.011871 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016 | 922 | 922 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 0.0021231 | 0.0029112 | 0.0038729 | 0.0050252 | 0.0063848 | 0.0079681 | 0.0097914 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017 | 669 | 669 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 0.0014916 | 0.0021231 | 0.0029112 | 0.0038729 | 0.0050252 | 0.0063848 | 0.0079681 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018 | 798 | 798 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 0.0009995 | 0.0014916 | 0.0021231 | 0.0029112 | 0.0038729 | 0.0050252 | 0.0063848 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019 | 762 | 762 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 0.00062954 | 0.0009995 | 0.0014916 | 0.0021231 | 0.0029112 | 0.0038729 | 0.0050252 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020 | 590 | 590 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 0.00036437 | 0.00062954 | 0.0009995 | 0.0014916 | 0.0021231 | 0.0029112 | 0.0038729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 788 | 788 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0.00018657 | 0.00036437 | 0.00062954 | 0.0009995 | 0.0014916 | 0.0021231 | 0.0029112 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 565 | 565 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 7.8714e-05 | 0.00018657 | 0.00036437 | 0.00062954 | 0.0009995 | 0.0014916 | 0.0021231 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 | 152 | 152 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 2.3323e-05 | 7.8714e-05 | 0.00018657 | 0.00036437 | 0.00062954 | 0.0009995 | 0.0014916 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grand Total | 26257 | 26257
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0

## OUTPUT<Forecast-HV-STEEL>
Exclude | NO
User Status List Desc | INSV
Crossarm Material | steel
Count of SAP ID | Voltage |  |  | Age | [6 empty] | Failure Probability | [6 empty] | Volumes
Years (Date Installed) | HV | Grand Total | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
1952 | 1 | 1 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 0.93713 | 0.94397 | 0.95023 | 0.95593 | 0.9611 | 0.96578 | 0.97 | 0.93713 | 0.0068446 | 0.0062569 | 0.0056994 | 0.0051731 | 0.0046784 | 0.0042158
1959 | 1 | 1 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.91279 | 0.92156 | 0.92967 | 0.87058 | 0.011653 | 0.01091 | 0.01018 | 0.0094676 | 0.0087751 | 0.0081056
1960 | 11 | 11 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.91279 | 0.92156 | 9.4399 | 0.13647 | 0.12819 | 0.12001 | 0.11198 | 0.10414 | 0.096526
1961 | 1 | 1 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.91279 | 0.845 | 0.013165 | 0.012406 | 0.011653 | 0.01091 | 0.01018 | 0.0094676
1962 | 1 | 1 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.83108 | 0.013925 | 0.013165 | 0.012406 | 0.011653 | 0.01091 | 0.01018
1963 | 1 | 1 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 0.8164 | 0.014682 | 0.013925 | 0.013165 | 0.012406 | 0.011653 | 0.01091
1964 | 3 | 3 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 2.4029 | 0.046293 | 0.044046 | 0.041776 | 0.039495 | 0.037219 | 0.03496
1965 | 7 | 7 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 5.4936 | 0.11317 | 0.10802 | 0.10277 | 0.097477 | 0.092156 | 0.086845
1966 | 4 | 4 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 3.0717 | 0.06754 | 0.064668 | 0.061724 | 0.058728 | 0.055701 | 0.052661
1967 | 3 | 3 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 2.251 | 0.052742 | 0.050655 | 0.048501 | 0.046293 | 0.044046 | 0.041776
1968 | 2 | 2 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 1.4642 | 0.036497 | 0.035161 | 0.03377 | 0.032334 | 0.030862 | 0.029364
1969 | 3 | 3 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 2.1396 | 0.056651 | 0.054745 | 0.052742 | 0.050655 | 0.048501 | 0.046293
1970 | 9 | 9 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 6.2435 | 0.17534 | 0.16995 | 0.16424 | 0.15823 | 0.15197 | 0.1455
1971 | 3 | 3 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 0.67368 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 2.021 | 0.060116 | 0.058446 | 0.056651 | 0.054745 | 0.052742 | 0.050655
1972 | 7 | 7 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 0.65313 | 0.67368 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 4.5719 | 0.14385 | 0.14027 | 0.13637 | 0.13219 | 0.12774 | 0.12306
1973 | 3 | 3 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 0.63212 | 0.65313 | 0.67368 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 1.8964 | 0.063032 | 0.061649 | 0.060116 | 0.058446 | 0.056651 | 0.054745
1974 | 3 | 3 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 0.32073 | 0.33631 | 0.35212 | 0.36813 | 0.38434 | 0.4007 | 0.41721 | 0.96219 | 0.046729 | 0.047427 | 0.048055 | 0.048613 | 0.049097 | 0.049505
1975 | 2 | 2 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 0.30541 | 0.32073 | 0.33631 | 0.35212 | 0.36813 | 0.38434 | 0.4007 | 0.61082 | 0.030644 | 0.031153 | 0.031618 | 0.032037 | 0.032408 | 0.032731
1976 | 3 | 3 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 0.29036 | 0.30541 | 0.32073 | 0.33631 | 0.35212 | 0.36813 | 0.38434 | 0 | 0.91623 | 0.045966 | 0.046729 | 0.047427 | 0.048055 | 0.048613
1977 | 6 | 6 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 0.27561 | 0.29036 | 0.30541 | 0.32073 | 0.33631 | 0.35212 | 0.36813 | 0 | 0 | 1.8325 | 0.091933 | 0.093459 | 0.094853 | 0.096111
1978 | 11 | 11 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 0.26117 | 0.27561 | 0.29036 | 0.30541 | 0.32073 | 0.33631 | 0.35212 | 0 | 0 | 0 | 3.3595 | 0.16854 | 0.17134 | 0.1739
1979 | 12 | 12 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 0.24707 | 0.26117 | 0.27561 | 0.29036 | 0.30541 | 0.32073 | 0.33631 | 0 | 0 | 0 | 0 | 3.6649 | 0.18387 | 0.18692
1980 | 190 | 190 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 0.23331 | 0.24707 | 0.26117 | 0.27561 | 0.29036 | 0.30541 | 0.32073 | 0 | 0 | 0 | 0 | 0 | 58.0276 | 2.9112
1981 | 218 | 218 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 0.21991 | 0.23331 | 0.24707 | 0.26117 | 0.27561 | 0.29036 | 0.30541 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5791
1982 | 152 | 152 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 0.20689 | 0.21991 | 0.23331 | 0.24707 | 0.26117 | 0.27561 | 0.29036 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1983 | 283 | 283 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 0.19426 | 0.20689 | 0.21991 | 0.23331 | 0.24707 | 0.26117 | 0.27561 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1984 | 303 | 303 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 0.18204 | 0.19426 | 0.20689 | 0.21991 | 0.23331 | 0.24707 | 0.26117 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1985 | 414 | 414 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 0.17022 | 0.18204 | 0.19426 | 0.20689 | 0.21991 | 0.23331 | 0.24707 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1986 | 518 | 518 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 0.15881 | 0.17022 | 0.18204 | 0.19426 | 0.20689 | 0.21991 | 0.23331 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1987 | 288 | 288 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 0.14784 | 0.15881 | 0.17022 | 0.18204 | 0.19426 | 0.20689 | 0.21991 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1988 | 487 | 487 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 0.13729 | 0.14784 | 0.15881 | 0.17022 | 0.18204 | 0.19426 | 0.20689 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1989 | 468 | 468 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 0.12718 | 0.13729 | 0.14784 | 0.15881 | 0.17022 | 0.18204 | 0.19426 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1990 | 639 | 639 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 0.1175 | 0.12718 | 0.13729 | 0.14784 | 0.15881 | 0.17022 | 0.18204 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1991 | 338 | 338 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 0.10827 | 0.1175 | 0.12718 | 0.13729 | 0.14784 | 0.15881 | 0.17022 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1992 | 318 | 318 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 0.099471 | 0.10827 | 0.1175 | 0.12718 | 0.13729 | 0.14784 | 0.15881 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1993 | 425 | 425 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 0.091112 | 0.099471 | 0.10827 | 0.1175 | 0.12718 | 0.13729 | 0.14784 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1994 | 400 | 400 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 0.083189 | 0.091112 | 0.099471 | 0.10827 | 0.1175 | 0.12718 | 0.13729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1995 | 347 | 347 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 0.075699 | 0.083189 | 0.091112 | 0.099471 | 0.10827 | 0.1175 | 0.12718 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1996 | 432 | 432 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 0.068636 | 0.075699 | 0.083189 | 0.091112 | 0.099471 | 0.10827 | 0.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1997 | 508 | 508 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 0.061995 | 0.068636 | 0.075699 | 0.083189 | 0.091112 | 0.099471 | 0.10827 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1998 | 636 | 636 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 0.055769 | 0.061995 | 0.068636 | 0.075699 | 0.083189 | 0.091112 | 0.099471 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1999 | 547 | 547 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 0.049951 | 0.055769 | 0.061995 | 0.068636 | 0.075699 | 0.083189 | 0.091112 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2000 | 659 | 659 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 0.044532 | 0.049951 | 0.055769 | 0.061995 | 0.068636 | 0.075699 | 0.083189 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 797 | 797 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 0.039502 | 0.044532 | 0.049951 | 0.055769 | 0.061995 | 0.068636 | 0.075699 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2002 | 665 | 665 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 0.034851 | 0.039502 | 0.044532 | 0.049951 | 0.055769 | 0.061995 | 0.068636 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 955 | 955 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 0.030567 | 0.034851 | 0.039502 | 0.044532 | 0.049951 | 0.055769 | 0.061995 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 708 | 708 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 0.026639 | 0.030567 | 0.034851 | 0.039502 | 0.044532 | 0.049951 | 0.055769 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 907 | 907 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 0.023054 | 0.026639 | 0.030567 | 0.034851 | 0.039502 | 0.044532 | 0.049951 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 852 | 852 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 0.019798 | 0.023054 | 0.026639 | 0.030567 | 0.034851 | 0.039502 | 0.044532 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 1001 | 1001 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 0.016859 | 0.019798 | 0.023054 | 0.026639 | 0.030567 | 0.034851 | 0.039502 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 943 | 943 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0.014222 | 0.016859 | 0.019798 | 0.023054 | 0.026639 | 0.030567 | 0.034851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 1090 | 1090 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 0.011871 | 0.014222 | 0.016859 | 0.019798 | 0.023054 | 0.026639 | 0.030567 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 1219 | 1219 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 0.0097914 | 0.011871 | 0.014222 | 0.016859 | 0.019798 | 0.023054 | 0.026639 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011 | 1303 | 1303 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 0.0079681 | 0.0097914 | 0.011871 | 0.014222 | 0.016859 | 0.019798 | 0.023054 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012 | 1473 | 1473 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 0.0063848 | 0.0079681 | 0.0097914 | 0.011871 | 0.014222 | 0.016859 | 0.019798 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013 | 1239 | 1239 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 0.0050252 | 0.0063848 | 0.0079681 | 0.0097914 | 0.011871 | 0.014222 | 0.016859 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014 | 1751 | 1751 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 0.0038729 | 0.0050252 | 0.0063848 | 0.0079681 | 0.0097914 | 0.011871 | 0.014222 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015 | 1588 | 1588 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 0.0029112 | 0.0038729 | 0.0050252 | 0.0063848 | 0.0079681 | 0.0097914 | 0.011871 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016 | 1863 | 1863 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 0.0021231 | 0.0029112 | 0.0038729 | 0.0050252 | 0.0063848 | 0.0079681 | 0.0097914 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017 | 1242 | 1242 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 0.0014916 | 0.0021231 | 0.0029112 | 0.0038729 | 0.0050252 | 0.0063848 | 0.0079681 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018 | 1051 | 1051 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 0.0009995 | 0.0014916 | 0.0021231 | 0.0029112 | 0.0038729 | 0.0050252 | 0.0063848 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019 | 501 | 501 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 0.00062954 | 0.0009995 | 0.0014916 | 0.0021231 | 0.0029112 | 0.0038729 | 0.0050252 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020 | 960 | 960 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 0.00036437 | 0.00062954 | 0.0009995 | 0.0014916 | 0.0021231 | 0.0029112 | 0.0038729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 1078 | 1078 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0.00018657 | 0.00036437 | 0.00062954 | 0.0009995 | 0.0014916 | 0.0021231 | 0.0029112 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 1022 | 1022 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 7.8714e-05 | 0.00018657 | 0.00036437 | 0.00062954 | 0.0009995 | 0.0014916 | 0.0021231 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 | 397 | 397 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 2.3323e-05 | 7.8714e-05 | 0.00018657 | 0.00036437 | 0.00062954 | 0.0009995 | 0.0014916 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 1 | 1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 0 | 2.9154e-06 | 2.3323e-05 | 7.8714e-05 | 0.00018657 | 0.00036437 | 0.00062954 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grand Total | 33273 | 33273
[17 empty] | 1.573 | 1.7801 | 2.7435 | 3.5778 | 4.055 | 58.6072 | 70.078

## OUTPUT<Forecast-ST-STEEL>
Exclude | NO
User Status List Desc | INSV
Crossarm Material | steel
Count of SAP ID | Voltage |  |  | Age | [6 empty] | Failure Probability | [6 empty] | Volumes
Years (Date Installed) | ST | Grand Total | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
1939 | 1 | 1 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 0.98915 | 0.99075 | 0.99215 | 0.99335 | 0.9944 | 0.9953 | 0.99607 | 0.98915 | 0.0016009 | 0.0013939 | 0.0012088 | 0.0010441 | 0.00089818 | 0.00076948
1952 | 1 | 1 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 0.93713 | 0.94397 | 0.95023 | 0.95593 | 0.9611 | 0.96578 | 0.97 | 0.93713 | 0.0068446 | 0.0062569 | 0.0056994 | 0.0051731 | 0.0046784 | 0.0042158
1954 | 1 | 1 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 0.92156 | 0.92967 | 0.93713 | 0.94397 | 0.95023 | 0.95593 | 0.9611 | 0.92156 | 0.0081056 | 0.0074614 | 0.0068446 | 0.0062569 | 0.0056994 | 0.0051731
1955 | 1 | 1 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 0.91279 | 0.92156 | 0.92967 | 0.93713 | 0.94397 | 0.95023 | 0.95593 | 0.91279 | 0.0087751 | 0.0081056 | 0.0074614 | 0.0068446 | 0.0062569 | 0.0056994
1957 | 1 | 1 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 0.89314 | 0.90332 | 0.91279 | 0.92156 | 0.92967 | 0.93713 | 0.94397 | 0.89314 | 0.01018 | 0.0094676 | 0.0087751 | 0.0081056 | 0.0074614 | 0.0068446
1959 | 1 | 1 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.91279 | 0.92156 | 0.92967 | 0.87058 | 0.011653 | 0.01091 | 0.01018 | 0.0094676 | 0.0087751 | 0.0081056
1961 | 6 | 6 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.91279 | 5.07 | 0.078991 | 0.074438 | 0.06992 | 0.06546 | 0.061082 | 0.056805
1962 | 1 | 1 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 0.89314 | 0.90332 | 0.83108 | 0.013925 | 0.013165 | 0.012406 | 0.011653 | 0.01091 | 0.01018
1964 | 4 | 4 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 0.88223 | 3.2039 | 0.061724 | 0.058728 | 0.055701 | 0.052661 | 0.049626 | 0.046613
1965 | 8 | 8 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 0.87058 | 6.2784 | 0.12934 | 0.12345 | 0.11746 | 0.1114 | 0.10532 | 0.099251
1966 | 8 | 8 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 0.85817 | 6.1433 | 0.13508 | 0.12934 | 0.12345 | 0.11746 | 0.1114 | 0.10532
1967 | 3 | 3 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 0.845 | 2.251 | 0.052742 | 0.050655 | 0.048501 | 0.046293 | 0.044046 | 0.041776
1968 | 2 | 2 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 0.83108 | 1.4642 | 0.036497 | 0.035161 | 0.03377 | 0.032334 | 0.030862 | 0.029364
1969 | 1 | 1 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 0.8164 | 0.7132 | 0.018884 | 0.018248 | 0.017581 | 0.016885 | 0.016167 | 0.015431
1970 | 9 | 9 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 0.80097 | 6.2435 | 0.17534 | 0.16995 | 0.16424 | 0.15823 | 0.15197 | 0.1455
1971 | 1 | 1 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 0.67368 | 0.69372 | 0.7132 | 0.73209 | 0.75033 | 0.76791 | 0.7848 | 0.67368 | 0.020039 | 0.019482 | 0.018884 | 0.018248 | 0.017581 | 0.016885
1973 | 16 | 16 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 0.33631 | 0.35212 | 0.36813 | 0.38434 | 0.4007 | 0.41721 | 0.43382 | 5.3809 | 0.25294 | 0.25629 | 0.25927 | 0.26185 | 0.26403 | 0.26579
1974 | 2 | 2 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 0.32073 | 0.33631 | 0.35212 | 0.36813 | 0.38434 | 0.4007 | 0.41721 | 0.64146 | 0.031153 | 0.031618 | 0.032037 | 0.032408 | 0.032731 | 0.033003
1975 | 6 | 6 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 0.30541 | 0.32073 | 0.33631 | 0.35212 | 0.36813 | 0.38434 | 0.4007 | 1.8325 | 0.091933 | 0.093459 | 0.094853 | 0.096111 | 0.097225 | 0.098193
1976 | 1 | 1 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 0.29036 | 0.30541 | 0.32073 | 0.33631 | 0.35212 | 0.36813 | 0.38434 | 0 | 0.30541 | 0.015322 | 0.015576 | 0.015809 | 0.016018 | 0.016204
1978 | 2 | 2 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 0.26117 | 0.27561 | 0.29036 | 0.30541 | 0.32073 | 0.33631 | 0.35212 | 0 | 0 | 0 | 0.61082 | 0.030644 | 0.031153 | 0.031618
1979 | 3 | 3 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 0.24707 | 0.26117 | 0.27561 | 0.29036 | 0.30541 | 0.32073 | 0.33631 | 0 | 0 | 0 | 0 | 0.91623 | 0.045966 | 0.046729
1980 | 38 | 38 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 0.23331 | 0.24707 | 0.26117 | 0.27561 | 0.29036 | 0.30541 | 0.32073 | 0 | 0 | 0 | 0 | 0 | 11.6055 | 0.58224
1981 | 104 | 104 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 0.21991 | 0.23331 | 0.24707 | 0.26117 | 0.27561 | 0.29036 | 0.30541 | 0 | 0 | 0 | 0 | 0 | 0 | 31.7625
1982 | 71 | 71 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 0.20689 | 0.21991 | 0.23331 | 0.24707 | 0.26117 | 0.27561 | 0.29036 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1983 | 145 | 145 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 0.19426 | 0.20689 | 0.21991 | 0.23331 | 0.24707 | 0.26117 | 0.27561 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1984 | 126 | 126 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 0.18204 | 0.19426 | 0.20689 | 0.21991 | 0.23331 | 0.24707 | 0.26117 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1985 | 324 | 324 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 0.17022 | 0.18204 | 0.19426 | 0.20689 | 0.21991 | 0.23331 | 0.24707 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1986 | 277 | 277 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 0.15881 | 0.17022 | 0.18204 | 0.19426 | 0.20689 | 0.21991 | 0.23331 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1987 | 87 | 87 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 0.14784 | 0.15881 | 0.17022 | 0.18204 | 0.19426 | 0.20689 | 0.21991 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1988 | 154 | 154 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 0.13729 | 0.14784 | 0.15881 | 0.17022 | 0.18204 | 0.19426 | 0.20689 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1989 | 109 | 109 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 0.12718 | 0.13729 | 0.14784 | 0.15881 | 0.17022 | 0.18204 | 0.19426 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1990 | 173 | 173 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 0.1175 | 0.12718 | 0.13729 | 0.14784 | 0.15881 | 0.17022 | 0.18204 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1991 | 44 | 44 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 0.10827 | 0.1175 | 0.12718 | 0.13729 | 0.14784 | 0.15881 | 0.17022 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1992 | 27 | 27 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 0.099471 | 0.10827 | 0.1175 | 0.12718 | 0.13729 | 0.14784 | 0.15881 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1993 | 94 | 94 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 0.091112 | 0.099471 | 0.10827 | 0.1175 | 0.12718 | 0.13729 | 0.14784 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1994 | 91 | 91 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 0.083189 | 0.091112 | 0.099471 | 0.10827 | 0.1175 | 0.12718 | 0.13729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1995 | 158 | 158 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 0.075699 | 0.083189 | 0.091112 | 0.099471 | 0.10827 | 0.1175 | 0.12718 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1996 | 97 | 97 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 0.068636 | 0.075699 | 0.083189 | 0.091112 | 0.099471 | 0.10827 | 0.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1997 | 102 | 102 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 0.061995 | 0.068636 | 0.075699 | 0.083189 | 0.091112 | 0.099471 | 0.10827 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1998 | 132 | 132 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 0.055769 | 0.061995 | 0.068636 | 0.075699 | 0.083189 | 0.091112 | 0.099471 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1999 | 175 | 175 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 0.049951 | 0.055769 | 0.061995 | 0.068636 | 0.075699 | 0.083189 | 0.091112 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2000 | 152 | 152 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 0.044532 | 0.049951 | 0.055769 | 0.061995 | 0.068636 | 0.075699 | 0.083189 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 303 | 303 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 0.039502 | 0.044532 | 0.049951 | 0.055769 | 0.061995 | 0.068636 | 0.075699 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2002 | 291 | 291 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 0.034851 | 0.039502 | 0.044532 | 0.049951 | 0.055769 | 0.061995 | 0.068636 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 154 | 154 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 0.030567 | 0.034851 | 0.039502 | 0.044532 | 0.049951 | 0.055769 | 0.061995 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 60 | 60 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 0.026639 | 0.030567 | 0.034851 | 0.039502 | 0.044532 | 0.049951 | 0.055769 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 346 | 346 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 0.023054 | 0.026639 | 0.030567 | 0.034851 | 0.039502 | 0.044532 | 0.049951 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 170 | 170 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 0.019798 | 0.023054 | 0.026639 | 0.030567 | 0.034851 | 0.039502 | 0.044532 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 105 | 105 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 0.016859 | 0.019798 | 0.023054 | 0.026639 | 0.030567 | 0.034851 | 0.039502 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 121 | 121 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0.014222 | 0.016859 | 0.019798 | 0.023054 | 0.026639 | 0.030567 | 0.034851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 233 | 233 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 0.011871 | 0.014222 | 0.016859 | 0.019798 | 0.023054 | 0.026639 | 0.030567 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 126 | 126 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 0.0097914 | 0.011871 | 0.014222 | 0.016859 | 0.019798 | 0.023054 | 0.026639 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011 | 221 | 221 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 0.0079681 | 0.0097914 | 0.011871 | 0.014222 | 0.016859 | 0.019798 | 0.023054 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012 | 204 | 204 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 0.0063848 | 0.0079681 | 0.0097914 | 0.011871 | 0.014222 | 0.016859 | 0.019798 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013 | 182 | 182 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 0.0050252 | 0.0063848 | 0.0079681 | 0.0097914 | 0.011871 | 0.014222 | 0.016859 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014 | 107 | 107 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 0.0038729 | 0.0050252 | 0.0063848 | 0.0079681 | 0.0097914 | 0.011871 | 0.014222 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2015 | 198 | 198 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 0.0029112 | 0.0038729 | 0.0050252 | 0.0063848 | 0.0079681 | 0.0097914 | 0.011871 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016 | 140 | 140 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 0.0021231 | 0.0029112 | 0.0038729 | 0.0050252 | 0.0063848 | 0.0079681 | 0.0097914 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2017 | 198 | 198 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 0.0014916 | 0.0021231 | 0.0029112 | 0.0038729 | 0.0050252 | 0.0063848 | 0.0079681 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018 | 345 | 345 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 0.0009995 | 0.0014916 | 0.0021231 | 0.0029112 | 0.0038729 | 0.0050252 | 0.0063848 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019 | 203 | 203 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 0.00062954 | 0.0009995 | 0.0014916 | 0.0021231 | 0.0029112 | 0.0038729 | 0.0050252 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020 | 214 | 214 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 0.00036437 | 0.00062954 | 0.0009995 | 0.0014916 | 0.0021231 | 0.0029112 | 0.0038729 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 128 | 128 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0.00018657 | 0.00036437 | 0.00062954 | 0.0009995 | 0.0014916 | 0.0021231 | 0.0029112 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 59 | 59 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 7.8714e-05 | 0.00018657 | 0.00036437 | 0.00062954 | 0.0009995 | 0.0014916 | 0.0021231 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 | 43 | 43 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 2.3323e-05 | 7.8714e-05 | 0.00018657 | 0.00036437 | 0.00062954 | 0.0009995 | 0.0014916 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 1 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 2.9154e-06 | 2.3323e-05 | 7.8714e-05 | 0.00018657 | 0.00036437 | 0.00062954 | 0.0009995 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 1 | 1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 0 | 2.9154e-06 | 2.3323e-05 | 7.8714e-05 | 0.00018657 | 0.00036437 | 0.00062954 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grand Total | 6912 | 6912
[17 empty] | 7.8548 | 4.6089 | 4.3241 | 1.0126 | 1.353 | 12.0926 | 32.8363

## OUTPUT<Replace-Volumes>
OUTPUT - PTS Forecast
WOOD | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
LV | 1657.9256 | 1836.3374 | 1681.8513 | 1642.2915 | 2485.6985 | 2424.559
HV | 471.3217 | 451.949 | 480.1142 | 409.7035 | 437.937 | 421.6963
ST | 27.2049 | 26.9311 | 26.9374 | 26.3333 | 27.8081 | 5.8644
Total | 2156.4523 | 2315.2175 | 2188.9029 | 2078.3283 | 2951.4437 | 2852.1197
STEEL | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
LV | 0 | 0 | 0 | 0 | 0 | 0
HV | 1.573 | 1.7801 | 2.7435 | 3.5778 | 4.055 | 58.6072
ST | 4.6089 | 4.3241 | 1.0126 | 1.353 | 12.0926 | 32.8363
Total | 6.1819 | 6.1042 | 3.7561 | 4.9309 | 16.1476 | 91.4435
TOTAL | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
LV | 1657.9256 | 1836.3374 | 1681.8513 | 1642.2915 | 2485.6985 | 2424.559
HV | 472.8947 | 453.7291 | 482.8577 | 413.2814 | 441.992 | 480.3035
ST | 31.8138 | 31.2552 | 27.9499 | 27.6863 | 39.9008 | 38.7006
Total | 2162.6341 | 2321.3217 | 2192.6589 | 2083.2592 | 2967.5913 | 2943.5632
| 1416 | 1916 | 2497 | 2497 | 2497 | 2497

## ANALYSIS<Volumes&REPEX>
Replacement Expenditure - Model Forecast Expenditure | [6 empty] | CPI | 0 | 0.03 | 0 | 0.03 | 0.03 | 0.03 | 0.03
| Source RIN | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | URate 2024
| CY18 | CY19 | CY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31
LV | 1532412.83 | 1197021.7396 | 10368924.6109 | 9779425.501 | 3329646.5 | 1735049.4495 | 2138104 | #REF! | 3751588.4299 | 5073105.3311 | 8008169.3467 | 8248414.4271 | 8495866.86 | 8750742.8658 |  | 3557.5774
HV | 1933230.2972 | 504561.1605 | 2691989.3013 | 3443316.3831 | 2031355.36 | 1395312.6699 | 1646898 | 1855126.4828 | 2048434.4482 | 2210061.3966 | 2487443.5725 | 2562066.8796 | 2638928.886 | 2718096.7526 |  | 4732.4655
ST | 362759.0528 | 53424.4499 | 41821.5178 | 29738.4059 | 103631.76 | 21534.4706 | 85956 | 66120 | 98205.3912 | 152076 | 223255.9276 | 229953.6054 | 236852.2135 | 243957.7799 |  | 6612
Total | 3828402.18 | 1755007.35 | 13102735.43 | 13252480.29 | 5464633.62 | 3151896.59 | 3870958 | 5396002.7838 | 6044788.221 | 7709725.0811 | 11308651.7031 | 11647911.2542 | 11997348.5918 | 12357269.0495 |  | 4023.8649
Replacement Expenditure - RIN Forecast Expenditure | FY24: CPI; FY25: 0; FY26: 0.03; FY27: 0; FY28: 0.03; FY29: 0.03; FY30: 0.03; FY31: 0.03
| CY18: Source RIN; FY25: 1; FY26: 2; FY27: 3; FY28: 4; FY29: 5; FY30: 6; FY31: 7 |  | URate 2024
| CY18 | CY19 | CY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31
LV | 1532412.83 | 1197021.7396 | 10368924.6109 | 9779425.501 | 3329646.5 | 1735049.4495 | 2138104 | 3340565.1514 | 3751588.4299 | 5073105.3311 | 8008169.3467 | 8248414.4271 | 8495866.86 | 8750742.8658 |  | 3557.5774
HV | 1933230.2972 | 504561.1605 | 2691989.3013 | 3443316.3831 | 2031355.36 | 1395312.6699 | 1646898 | 1855126.4828 | 2048434.4482 | 2210061.3966 | 2487443.5725 | 2562066.8796 | 2638928.886 | 2718096.7526 |  | 4732.4655
ST | 362759.0528 | 53424.4499 | 41821.5178 | 29738.4059 | 103631.76 | 21534.4706 | 85956 | 66120 | 98205.3912 | 152076 | 223255.9276 | 229953.6054 | 236852.2135 | 243957.7799 |  | 6612
Total | 3828402.18 | 1755007.35 | 13102735.43 | 13252480.29 | 5464633.62 | 3151896.59 | 3870958 | 5396002.7838 | 6044788.221 | 7709725.0811 | 11308651.7031 | 11647911.2542 | 11997348.5918 | 12357269.0495 |  | 4023.8649
Replacement Volumes | [23 empty] | XArms In Service - Calcs
| CY18: Source RIN |  |  | Source - Capex model 31 Oct 2024
| CY9 | CY10 | CY11 | CY12 | CY13 | CY14 | CY15 | CY16 | CY17 | CY18 | CY19 | CY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | Exclude | NO
LV | 248 | 241 | 162 | 193 | 145 | 429 | 663 | 470 | 365 | 479 | 378 | 2640 | 2694 | 1268 | 832 | 601 | 939 | 994 | 1426 | 2000 | 2000 | 2000 | 2000 | User Status List Desc | (All)
HV | 462 | 549 | 987 | 437 | 435 | 884 | 928 | 990 | 684 | 650 | 98 | 518 | 615 | 616 | 325 | 348 | 392 | 408 | 467 | 467 | 467 | 467 | 467 | Voltage | LV
ST | 28 | 38 | 137 | 0 | 8 | 38 | 45 | 42 | 2 | 157 | 4 | 11 | 12 | 14 | 10 | 13 | 10 | 14 | 23 | 30 | 30 | 30 | 30
Total | 738 | 828 | 1286 | 630 | 588 | 1351 | 1636 | 1502 | 1051 | 1286 | 480 | 3169 | 3321 | 1898 | 1167 | 962 | 1341 | 1416 | 1916 | 2497 | 2497 | 2497 | 2497 |  | Column Labels
[25 empty] | 1931 | 1934 | 1940 | 1949 | 1950 | 1951 | 1952 | 1953 | 1954 | 1955 | 1956 | 1957 | 1958 | 1959 | 1960 | 1961 | 1962 | 1963 | 1964 | 1965 | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
[24 empty] | Count of SAP ID | 1 | 2 | 3 | 2 | 84 | 42 | 36 | 133 | 102 | 148 | 109 | 263 | 295 | 464 | 593 | 835 | 734 | 737 | 1106 | 1482 | 1096 | 1471 | 1429 | 1141 | 781 | 1512 | 1611 | 1280 | 1193 | 1120 | 1243 | 1038 | 1510 | 952 | 1539 | 1110 | 1028 | 1508 | 1584 | 1912 | 2428 | 1532 | 1958 | 1250 | 1943 | 1210 | 1294 | 1156 | 833 | 630 | 922 | 1147 | 1250 | 990 | 1063 | 1713 | 1240 | 1609 | 1878 | 1240 | 1394 | 1453 | 1544 | 1734 | 1692 | 1747 | 1991 | 2035 | 2019 | 2187 | 2075 | 1505 | 1754 | 1596 | 3617 | 2247 | 1881 | 562 | 20 | 1
Failures | CY9 | CY10 | CY11 | CY12 | CY13 | CY14 | CY15 | CY16 | CY17 | CY18 | CY19 | CY20 | FY21 | FY22 | FY23 | FY24 | [8 empty] | Column Labels 1994: Exclude; Column Labels 1995: NO; Column Labels 2016: 80386; Column Labels 2017: 81891; Column Labels 2018: 83645; Column Labels 2019: 85241; Column Labels 2020: 88858; Column Labels 2021: 91105; Column Labels 2022: 92986; Column Labels 2023: 93548; Column Labels 2024: 93568
LV | 7 | 5 | 0 | 23 | 8 | 10 | 4 | 8 | 25 | 26 | 34 | 37 | 28 | 12 | 37 | 24 | [8 empty] | Column Labels 1994: User Status List Desc; Column Labels 1995: ASRT RMVD
HV | 2 | 6 | 46 | 18 | 5 | 9 | 6 | 1 | 6 | 9 | 2 | 4 | 1 | 6 | 5 | 3 | [8 empty] | Column Labels 1994: Voltage; Column Labels 1995: LV
ST | 0 | 0 | 13 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
Total | 9 | 11 | 59 | 41 | 14 | 19 | 10 | 9 | 31 | 35 | 36 | 42 | 29 | 18 | 42 | 27 | [8 empty] | Column Labels 1995: Column Labels
[74 empty] | 1900 | 1996 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
[73 empty] | Count of SAP ID | 1 | 1 | 3 | 2 | 9 | 1 | 4 | 2 | 1 | 1 | 3 | 59 | 5 | 35 | 15 | 24 | 24 | 35 | 104 | 74 | 114 | 138 | 751 | 1163 | 3328 | 1948 | 1643 | 1289 | 1557 | 1028
XArms In Service | CY9 | CY10 | CY11 | CY12 | CY13 | CY14 | CY15 | CY16 | CY17 | CY18 | CY19 | CY20 | FY21 | FY22 | FY23 | FY24 | [77 empty] | 517 | 655 | 1406 | 2569 | 5897 | 7845 | 9488 | 10777 | 12334
LV | CY17: 81236; CY18: 82239; CY19: 82672; CY20: 82961; FY21: 83260; FY22: 83498; FY23: 82771; FY24: 81234
HV | CY17: 37947; CY18: 38244; CY19: 38460; CY20: 38621; FY21: 38957; FY22: 39414; FY23: 39362; FY24: 39047 | [7 empty] | Exclude | NO
ST | CY17: 6250; CY18: 6443; CY19: 6587; CY20: 6779; FY21: 6972; FY22: 7083; FY23: 7133; FY24: 7166 | [7 empty] | User Status List Desc | (All)
Total | CY17: 125433; CY18: 126926; CY19: 127719; CY20: 128361; FY21: 129189; FY22: 129995; FY23: 129266; FY24: 127447 | [7 empty] | Voltage | HV
Column Labels
Failure Rates | CY9 | CY10 | CY11 | CY12 | CY13 | CY14 | CY15 | CY16 | CY17 | CY18 | CY19 | CY20 | FY21 | FY22 | FY23 | FY24 | [8 empty] | 1931 | 1934 | 1938 | 1942 | 1949 | 1950 | 1951 | 1952 | 1953 | 1954 | 1955 | 1956 | 1957 | 1958 | 1959 | 1960 | 1961 | 1962 | 1963 | 1964 | 1965 | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2025
LV | [8 empty] | 0.4493% | 0.5824% | 0.4572% | 3.182% | 3.236% | 1.519% | 1.005% | 0.7398% | [7 empty] | Count of SAP ID | 1 | 2 | 3 | 1 | 1 | 13 | 38 | 31 | 17 | 27 | 10 | 20 | 26 | 43 | 93 | 94 | 154 | 113 | 132 | 222 | 301 | 199 | 242 | 284 | 175 | 153 | 247 | 228 | 260 | 253 | 225 | 276 | 321 | 383 | 240 | 643 | 612 | 413 | 668 | 728 | 863 | 1074 | 677 | 984 | 665 | 982 | 531 | 470 | 543 | 476 | 375 | 485 | 547 | 690 | 587 | 726 | 864 | 696 | 975 | 720 | 923 | 865 | 1032 | 950 | 1117 | 1234 | 1313 | 1537 | 1277 | 1766 | 1601 | 1873 | 1259 | 1055 | 504 | 981 | 1083 | 1027 | 398 | 1
HV | [8 empty] | 1.803% | 1.7% | 0.2548% | 1.341% | 1.579% | 1.563% | 0.8257% | 0.8912% | [8 empty] | Column Labels 1993: Exclude; Column Labels 1994: NO; Column Labels 2016: 37310; Column Labels 2017: 38569; Column Labels 2018: 39624; Column Labels 2019: 40128; Column Labels 2020: 41109; Column Labels 2021: 42192; Column Labels 2022: 43219; Column Labels 2023: 43617; Column Labels 2025: 43618
ST | [8 empty] | 0.032% | 2.437% | 0.06073% | 0.1623% | 0.1721% | 0.1977% | 0.1402% | 0.1814% | [8 empty] | Column Labels 1993: User Status List Desc; Column Labels 1994: ASRT RMVD
Total | [8 empty] | 0.8379% | 1.013% | 0.3758% | 2.469% | 2.571% | 1.46% | 0.9028% | 0.7548% | [8 empty] | Column Labels 1993: Voltage; Column Labels 1994: HV
Column Labels
[74 empty] | 2001 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
[73 empty] | Count of SAP ID | 1 | 2 | 3 | 5 | 1 | 17 | 6 | 27 | 21 | 20 | 62 | 47 | 138 | 63 | 110 | 99 | 758 | 288 | 820 | 747 | 570 | 450 | 316 | 192
[88 empty] | 523 | 622 | 1380 | 1668 | 2488 | 3235 | 3805 | 4255 | 4571
[24 empty] | Exclude | NO
[24 empty] | User Status List Desc | (All)
[24 empty] | Voltage | ST
Column Labels
[25 empty] | 1938 | 1939 | 1944 | 1952 | 1953 | 1954 | 1955 | 1956 | 1957 | 1958 | 1959 | 1960 | 1961 | 1962 | 1963 | 1964 | 1965 | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
[24 empty] | Count of SAP ID | 2 | 1 | 1 | 14 | 6 | 17 | 2 | 1 | 2 | 2 | 4 | 11 | 12 | 7 | 14 | 84 | 81 | 37 | 15 | 15 | 21 | 25 | 14 | 1 | 19 | 31 | 14 | 7 | 2 | 2 | 3 | 41 | 114 | 88 | 174 | 135 | 329 | 290 | 93 | 167 | 121 | 179 | 44 | 27 | 105 | 92 | 167 | 97 | 107 | 137 | 178 | 155 | 307 | 292 | 162 | 62 | 346 | 170 | 107 | 123 | 233 | 127 | 221 | 207 | 187 | 110 | 198 | 142 | 198 | 345 | 203 | 215 | 128 | 59 | 43 | 1 | 1
[73 empty] | Exclude | NO | [17 empty] | 6301 | 6499 | 6844 | 7047 | 7262 | 7390 | 7449 | 7492 | 7493
[73 empty] | User Status List Desc | ASRT RMVD
[73 empty] | Voltage | ST
Column Labels
[74 empty] | 1900 | 2007 | 2009 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
[73 empty] | Count of SAP ID | 3 | 1 | 4 | 20 | 13 | 7 | 3 | 5 | 201 | 11 | 22 | 17 | 9 | 10 | 8 | 9
[80 empty] | 51 | 56 | 257 | 268 | 290 | 307 | 316 | 326 | 334