{"text_format":"1","workbook":"xlsx","n_sheets":16,"sheets":["EDCoP Actual V Performance","Total Network Demand","EDCoP_1-12-2024_mD_High V","EDCoP_1-12-2024_mD_High V by DS","EDCoP_1-12-2024_mD_High V by ZS","EDCoP_2-2-2025_MD_Low V","Low V contribution by DSS","Low V contribution by ZSS","Extreme Low V by DSS contributi","Extreme Low V by ZSS contri","Under-Voltage Augmentation","2024-25","2023-24","2022-23","2021-22","2020-21"],"not_rendered":{"charts":9,"images":2,"macros":0,"external_links":0,"defined_names":39,"comments":0,"pivot_tables":6},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"EDCoP Actual V Performance","index":0,"n_rows":231,"n_cols":13,"rows_kept":231,"cut":false,"hidden":false,"merged":[]}
["Distributor","Year","Month","Start Date","End Date","a) Below 216V for more than 1% of the time","b) Above 253V for more than 1% of the time","c) Below 216V for more than 1% of time, and above 253V for more than 1% of time","d) Below 207V for two consecutive time intervals","e) Above 260V for two consecutive time intervals","f) Below 207V for two consecutive time intervals, and above 260V for two consecutive time intervals","Compliance level (5%)","Compensation level (0%)"]
["Jemena",2021,"Nov","2021-11-28","2021-12-04",0.13,4.28,0,0.05,0.04,0,5,0]
["Jemena",2021,"Dec","2021-12-05","2021-12-11",0.03,3.45,0,0.02,0.01,0,5,0]
["Jemena",2021,"Dec","2021-12-12","2021-12-18",0.09,4.72,0,0.03,0.02,0,5,0]
["Jemena",2021,"Dec","2021-12-19","2021-12-25",0.03,3.95,0,0.01,0.01,0,5,0]
["Jemena",2021,"Dec","2021-12-26","2022-01-01",1.28,2.76,0.04,0.57999999999999996,0.03,0,5,0]
["Jemena",2022,"Jan","2022-01-02","2022-01-08",0.15,1.92,0,7.0000000000000007E-2,0.01,0,5,0]
["Jemena",2022,"Jan","2022-01-09","2022-01-15",1.3,2.52,0.04,0.56000000000000005,7.0000000000000007E-2,0,5,0]
["Jemena",2022,"Jan","2022-01-16","2022-01-22",0.97,2.4700000000000002,0.03,0.41,0.02,0,5,0]
["Jemena",2022,"Jan","2022-01-23","2022-01-29",3.54,1.58,0.01,1.57,0.06,0,5,0]
["Jemena",2022,"Jan","2022-01-30","2022-02-05",2.23,2.77,0.09,1.1000000000000001,0.04,0,5,0]
["Jemena",2022,"Feb","2022-02-06","2022-02-12",0.15,2.52,0.01,0.09,0.03,0,5,0]
["Jemena",2022,"Feb","2022-02-13","2022-02-19",0.43,2.42,0.02,0.21,0.02,0,5,0]
["Jemena",2022,"Feb","2022-02-20","2022-02-26",0.16,2.91,0.01,0.05,0.04,0,5,0]
["Jemena",2022,"Feb","2022-02-27","2022-03-05",0.44,1.67,0.01,0.18,0.03,0,5,0]
["Jemena",2022,"Mar","2022-03-06","2022-03-12",1.5199248E-2,2.8511026359999998,8.2905000000000001E-4,5.5269990000000003E-3,7.4614490000000002E-3,2.7635000000000002E-4,5,0]
["Jemena",2022,"Mar","2022-03-13","2022-03-19",4.3386945000000003E-2,2.0549383739999998,0,1.4093848000000001E-2,9.9485990000000007E-3,0,5,0]
["Jemena",2022,"Mar","2022-03-20","2022-03-26",4.6150444999999998E-2,2.6700934059999999,0,2.2937046999999999E-2,1.6028298E-2,0,5,0]
["Jemena",2022,"Mar","2022-03-27","2022-04-02",2.2660698E-2,3.0105565689999998,0,8.8431989999999995E-3,8.0141489999999999E-3,0,5,0]
["Jemena",2022,"Apr","2022-04-03","2022-04-09",3.2056596E-2,2.4409992809999999,5.5270000000000004E-4,2.3489746999999998E-2,1.5751948000000002E-2,0,5,0]
["Jemena",2022,"Apr","2022-04-10","2022-04-16",2.2384347999999998E-2,2.223788205,2.7635000000000002E-4,3.3162000000000001E-3,7.7377990000000001E-3,0,5,0]
["Jemena",2022,"Apr","2022-04-17","2022-04-23",3.5649146E-2,1.7346487589999999,2.7635000000000002E-4,5.2506489999999996E-3,2.2108000000000002E-3,0,5,0]
["Jemena",2022,"Apr","2022-04-24","2022-04-30",2.6805947E-2,1.5124633839999999,5.5270000000000004E-4,3.8689000000000002E-3,2.7634999999999999E-3,0,5,0]
["Jemena",2022,"May","2022-05-01","2022-05-07",0.19068147899999999,2.249212403,2.7634999999999999E-3,3.9518046000000001E-2,8.2904989999999998E-3,0,5,0]
["Jemena",2022,"May","2022-05-08","2022-05-14",0.11330348799999999,1.531255182,5.5270000000000004E-4,2.2384347999999998E-2,1.1053999E-2,2.7635000000000002E-4,5,0]
["Jemena",2022,"May","2022-05-15","2022-05-21",0.22467252500000001,1.540098381,8.2905000000000001E-4,6.2731442999999998E-2,1.8791797999999998E-2,0,5,0]
["Jemena",2022,"May","2022-05-22","2022-05-28",0.23130492499999999,1.7390703590000001,5.5270000000000004E-4,5.6651743999999997E-2,1.3264799000000001E-2,0,5,0]
["Jemena",2022,"May","2022-05-29","2022-06-04",1.131301643,2.0477737280000001,2.8720500000000001E-4,0.351252071,3.1305377000000002E-2,0,5,0]
["Jemena",2022,"Jun","2022-06-05","2022-06-11",0.97271522600000004,1.6027948750000001,1.4008E-3,0.28744407300000002,2.2412793E-2,5.6032E-4,5,0]
["Jemena",2022,"Jun","2022-06-12","2022-06-18",0.65226680599999998,1.506333825,2.7568299999999998E-4,0.169269577,1.7092368E-2,0,5,0]
["Jemena",2022,"Jun","2022-06-19","2022-06-25",0.418122885,1.4712854040000001,0,0.102808066,1.3781242000000001E-2,0,5,0]
["Jemena",2022,"Jun","2022-06-26","2022-07-02",0.83337696800000005,1.5793926599999999,2.75588E-4,0.25216267399999998,2.0117896E-2,0,5,0]
["Jemena",2022,"Jul","2022-07-03","2022-07-09",0.66964716099999999,2.0172053320000001,3.8564620000000002E-3,0.19778143200000001,1.8180465999999999E-2,0,5,0]
["Jemena",2022,"Jul","2022-07-10","2022-07-16",0.93599233400000004,2.0878769849999999,5.5074599999999996E-4,0.30401163199999998,2.2029828000000001E-2,2.7537299999999998E-4,5,0]
["Jemena",2022,"Jul","2022-07-17","2022-07-23",1.220750837,2.3236930259999999,5.5050769999999997E-3,0.40214587899999998,2.8075893000000001E-2,2.75254E-4,5,0]
["Jemena",2022,"Jul","2022-07-24","2022-07-30",0.61419109000000005,2.200186102,3.5788809999999999E-3,0.19986675500000001,1.4866122000000001E-2,0,5,0]
["Jemena",2022,"Jul","2022-07-31","2022-08-06",0.45349413500000002,2.342915359,3.8548380000000002E-3,0.108761496,1.3216587E-2,5.5069099999999996E-4,5,0]
["Jemena",2022,"Aug","2022-08-07","2022-08-13",0.61251950200000005,2.4638363089999999,2.2013279999999998E-3,0.173904908,2.0362284000000001E-2,1.1006639999999999E-3,5,0]
["Jemena",2022,"Aug","2022-08-14","2022-08-20",0.39746656400000002,2.4591179219999999,1.1010149999999999E-3,9.7990372000000006E-2,1.3762692999999999E-2,0,5,0]
["Jemena",2022,"Aug","2022-08-21","2022-08-27",0.45816935800000003,2.7234400650000001,8.8003720000000007E-3,0.12733037999999999,2.6676127000000001E-2,2.7501159999999999E-3,5,0]
["Jemena",2022,"Aug","2022-08-28","2022-09-03",0.30410932499999999,2.4790684249999999,3.8494850000000001E-3,6.2691615000000006E-2,1.1548454999999999E-2,0,5,0]
["Jemena",2022,"Sep","2022-09-04","2022-09-10",0.219804374,2.9670842949999998,2.4727989999999999E-3,3.3520166999999997E-2,1.6760084000000001E-2,2.7475500000000001E-4,5,0]
["Jemena",2022,"Sep","2022-09-11","2022-09-17",0.34717167700000001,2.6128513949999999,1.3733059999999999E-3,6.7291979000000002E-2,1.7578313000000002E-2,0,5,0]
["Jemena",2022,"Sep","2022-09-18","2022-09-24",0.153786583,2.6127241919999999,1.6477130000000001E-3,2.5539557000000001E-2,1.4280183E-2,0,5,0]
["Jemena",2022,"Sep","2022-09-25","2022-10-01",0.14658449900000001,3.0294129760000001,8.2350800000000003E-4,2.5803263999999999E-2,1.1803621E-2,2.74503E-4,5,0]
["Jemena",2022,"Oct","2022-10-02","2022-10-08",7.1071839999999997E-2,3.1471928,1.9208610000000001E-3,3.9240437000000003E-2,1.2348389E-2,5.4881699999999995E-4,5,0]
["Jemena",2022,"Oct","2022-10-09","2022-10-15",6.9144717999999994E-2,2.917797357,2.1950699999999999E-3,1.4267958000000001E-2,1.7011795999999999E-2,5.4876800000000004E-4,5,0]
["Jemena",2022,"Oct","2022-10-16","2022-10-22",4.2518872999999999E-2,3.8362995959999999,1.6458919999999999E-3,2.3316801000000002E-2,1.0149666E-2,0,5,0]
["Jemena",2022,"Oct","2022-10-23","2022-10-29",6.2274187000000002E-2,2.3677908030000001,3.5663629999999999E-3,9.7937818999999995E-2,1.0424754E-2,0,5,0]
["Jemena",2022,"Oct","2022-10-24","2022-10-30",6.6346631000000003E-2,2.8191834980000001,0,2.1110291999999999E-2,1.1788864E-2,0,5,0]
["Jemena",2022,"Oct","2022-10-30","2022-11-05",0.118439559,3.538107654,3.015822E-3,4.3866503000000001E-2,1.9739926000000001E-2,0,5,0]
["Jemena",2022,"Nov","2022-11-06","2022-11-12",3.2081954000000003E-2,2.427260338,8.2261400000000005E-4,6.3067089999999998E-3,5.7582989999999997E-3,2.7420500000000002E-4,5,0]
["Jemena",2022,"Nov","2022-11-13","2022-11-19",9.6491492999999998E-2,3.0690873600000002,1.3706180000000001E-3,2.1107514000000001E-2,1.617329E-2,0,5,0]
["Jemena",2022,"Nov","2022-11-20","2022-11-26",0.15459424499999999,2.3424865549999998,2.4669290000000001E-3,6.6881198000000003E-2,1.7268505999999999E-2,2.7410299999999999E-4,5,0]
["Jemena",2022,"Nov","2022-11-27","2022-12-03",1.9453121E-2,3.1990794020000002,0,7.6716529999999996E-3,9.0415909999999999E-3,0,5,0]
["Jemena",2022,"Dec","2022-12-04","2022-12-10",0.97628742300000004,2.6030677839999998,4.0005041999999998E-2,0.40443453099999999,7.1241860000000002E-3,0,5,0]
["Jemena",2022,"Dec","2022-12-11","2022-12-17",7.0692872000000004E-2,2.4928827619999998,1.6440199999999999E-3,1.1234139000000001E-2,6.8500849999999997E-3,0,5,0]
["Jemena",2022,"Dec","2022-12-18","2022-12-24",2.4659831E-2,2.247880624,0,3.5619756000000002E-2,4.3839700000000001E-3,0,5,0]
["Jemena",2022,"Dec","2022-12-25","2022-12-31",2.6519355180000002,2.1776122720000002,3.9458433000000001E-2,1.159639503,1.3152811E-2,0,5,0]
["Jemena",2023,"Jan","2023-01-01","2023-01-07",1.8238814480000001,2.0293969349999998,5.2337943999999997E-2,0.70587719500000001,3.8362890000000001E-3,2.74021E-4,5,0]
["Jemena",2023,"Jan","2023-01-08","2023-01-14",0.78697926900000004,1.8963026199999999,1.8333662000000001E-2,0.246820341,6.840919E-3,2.7363700000000002E-4,5,0]
["Jemena",2023,"Jan","2023-01-15","2023-01-21",2.9780980349999999,2.3330532759999998,7.2249391999999996E-2,1.56704552,7.6628140000000004E-3,2.7367199999999998E-4,5,0]
["Jemena",2023,"Jan","2023-01-22","2023-01-28",0.165492264,1.7859487489999999,1.914787E-3,3.8569272000000002E-2,6.9479396999999998E-2,2.7354099999999998E-4,5,0]
["Jemena",2023,"Jan","2023-01-29","2023-02-04",2.3795457999999998E-2,2.6864251019999998,0,1.2034484E-2,2.3521947000000001E-2,0,5,0]
["Jemena",2023,"Feb","2023-02-05","2023-02-11",7.1650477000000004E-2,2.4306467139999999,2.4612760000000001E-3,2.4065809000000001E-2,8.7512030000000008E-3,0,5,0]
["Jemena",2023,"Feb","2023-02-12","2023-02-18",2.8861796399999999,2.7631424249999998,9.1594370999999994E-2,1.2910705060000001,9.2961450000000004E-3,2.7341600000000001E-4,5,0]
["Jemena",2023,"Feb","2023-02-19","2023-02-25",0.85000778899999996,2.6404904349999998,3.0884526999999998E-2,0.28506692099999997,9.5660039999999995E-3,2.7331399999999998E-4,5,0]
["Jemena",2023,"Feb","2023-02-26","2023-03-04",3.3331603000000001E-2,2.0261243269999998,0,1.6119382000000002E-2,1.6392589999999999E-3,0,5,0]
["Jemena",2023,"Mar","2023-03-05","2023-03-11",9.6413842E-2,2.3477999619999999,4.0969049999999996E-3,2.7312703000000001E-2,3.8237779999999999E-3,0,5,0]
["Jemena",2023,"Mar","2023-03-12","2023-03-18",7.8102811999999994E-2,2.2783627900000001,5.1886479999999997E-3,2.102768E-2,2.457781E-3,0,5,0]
["Jemena",2023,"Mar","2023-03-19","2023-03-25",2.1023719E-2,2.267012147,2.7303499999999998E-4,6.5528469999999997E-3,1.092141E-3,0,5,0]
["Jemena",2023,"Mar","2023-03-26","2023-04-01",2.8391020999999999E-2,1.7474127319999999,0,2.3477189999999998E-2,2.7299059999999998E-3,0,5,0]
["Jemena",2023,"Apr","2023-04-02","2023-04-08",6.1135371000000001E-2,2.2205240169999998,2.72926E-4,3.2751092000000002E-2,3.275109E-3,0,5,0]
["Jemena",2023,"Apr","2023-04-09","2023-04-15",0.11322494700000001,2.0077647760000001,2.7283100000000002E-4,2.2099326999999998E-2,6.8207800000000002E-3,0,5,0]
["Jemena",2023,"Apr","2023-04-16","2023-04-22",6.9559049999999997E-2,2.0125751850000002,0,1.5548494E-2,3.8189280000000001E-3,0,5,0]
["Jemena",2023,"Apr","2023-04-23","2023-04-29",3.9301954E-2,1.676064564,6.2773949999999999E-3,2.7565954E-2,9.5525579999999992E-3,4.3668839999999997E-3,5,0]
["Jemena",2023,"Apr","2023-04-30","2023-05-06",0.237142717,1.924430885,1.910241E-3,6.1127697000000002E-2,9.0054200000000001E-3,2.72892E-4,5,0]
["Jemena",2023,"May","2023-05-07","2023-05-13",0.69218585099999996,2.3559945369999999,4.6345650000000002E-3,0.20010414100000001,1.9628744E-2,5.4524300000000005E-4,5,0]
["Jemena",2023,"May","2023-05-21","2023-05-27",0.67857629900000005,1.926633029,2.1819169999999998E-3,0.15818900899999999,1.5546160999999999E-2,0,5,0]
["Jemena",2023,"May","2023-05-28","2023-06-03",0.53379229800000005,1.8973220369999999,1.9093230000000001E-3,0.101194145,9.8193780000000001E-3,0,5,0]
["Jemena",2023,"Jun","2023-06-04","2023-06-10",0.337407499,1.6264841699999999,0,4.8551766000000003E-2,6.8190680000000002E-3,0,5,0]
["Jemena",2023,"Jun","2023-06-11","2023-06-17",0.55982975899999998,1.762699842,1.0912859999999999E-3,0.136956403,1.5278005000000001E-2,2.7282199999999998E-4,5,0]
["Jemena",2023,"Jun","2023-06-18","2023-06-24",1.485756385,1.8606745250000001,1.091465E-3,0.497162192,2.4830822999999998E-2,0,5,0]
["Jemena",2023,"Jun","2023-06-25","2023-07-01",1.0220478479999999,1.5609408600000001,5.43787E-4,0.28820716099999999,2.3110952000000001E-2,0,5,0]
["Jemena",2023,"Jul","2023-07-02","2023-07-08",0.71997187100000004,1.698155707,8.2408100000000005E-4,0.18267122999999999,1.9228551E-2,5.4938700000000003E-4,5,0]
["Jemena",2023,"Jul","2023-07-09","2023-07-15",0.468686671,1.8178949630000001,1.0880709999999999E-3,7.8885161999999995E-2,9.5206230000000006E-3,2.7201800000000001E-4,5,0]
["Jemena",2023,"Jul","2023-07-23","2023-07-29",0.70631575800000002,3.019799152,2.7207849999999999E-3,0.21739071300000001,2.6119534999999999E-2,2.7207799999999998E-4,5,0]
["Jemena",2023,"Jul","2023-07-30","2023-08-05",0.24159781,2.4148898249999999,1.9044870000000001E-3,4.5435624000000001E-2,1.4419688999999999E-2,0,5,0]
["Jemena",2023,"Aug","2023-08-06","2023-08-12",0.55595164900000005,2.1647554410000001,4.6261269999999998E-3,0.108577928,1.6327508000000001E-2,0,5,0]
["Jemena",2023,"Aug","2023-08-13","2023-08-19",1.080375002,2.410025445,1.0613256E-2,0.30669587599999998,1.6600219999999999E-2,0,5,0]
["Jemena",2023,"Aug","2023-08-20","2023-08-26",0.32012195100000002,2.4703288329999999,4.0831879999999997E-3,6.5603223000000002E-2,1.1705139E-2,0,5,0]
["Jemena",2023,"Aug","2023-08-27","2023-09-02",0.27035857200000002,2.1655912220000002,2.994909E-3,4.3290043E-2,1.2251899E-2,0,5,0]
["Jemena",2023,"Sep","2023-09-03","2023-09-09",0.49944143200000002,2.9617721590000001,9.5365250000000006E-3,0.13269393199999999,1.3351135E-2,5.4494400000000001E-4,5,0]
["Jemena",2023,"Sep","2023-09-10","2023-09-16",0.15397402900000001,2.5036449599999999,4.9053669999999999E-3,4.1968142E-2,4.9053669999999999E-3,5.4504100000000002E-4,5,0]
["Jemena",2023,"Sep","2023-09-17","2023-09-23",4.4462157000000002E-2,2.5156363100000001,5.4222099999999996E-4,9.759986E-3,2.982218E-3,0,5,0]
["Jemena",2023,"Sep","2023-09-24","2023-09-30",2.7077071000000001E-2,2.684732634,5.4701200000000004E-4,1.8051380999999998E-2,7.9316669999999999E-3,8.2051699999999999E-4,5,0]
["Jemena",2023,"Oct","2023-10-01","2023-10-07",0.167385531,2.3909874379999998,8.2051699999999999E-4,5.9077246E-2,1.0119713000000001E-2,5.4701200000000004E-4,5,0]
["Jemena",2023,"Oct","2023-10-08","2023-10-14",8.5445973999999994E-2,2.536253506,8.1377100000000003E-4,1.0036511E-2,1.0850281999999999E-2,0,5,0]
["Jemena",2023,"Oct","2023-10-15","2023-10-21",9.8466313E-2,2.3214179150000001,2.712571E-3,2.2243078999999999E-2,1.1121539E-2,8.1377100000000003E-4,5,0]
["Jemena",2023,"Oct","2023-10-22","2023-10-28",8.1919632000000006E-2,2.6244120500000001,2.1700560000000001E-3,1.0579025000000001E-2,9.4939970000000005E-3,0,5,0]
["Jemena",2023,"Oct","2023-10-29","2023-11-04",2.1723132999999999E-2,2.3941608219999999,0,2.7153920000000001E-3,8.6892529999999992E-3,0,5,0]
["Jemena",2023,"Nov","2023-11-05","2023-11-11",0.33047213800000003,1.5736121940000001,5.430931E-3,8.4179427000000001E-2,6.2455699999999998E-3,0,5,0]
["Jemena",2023,"Nov","2023-11-12","2023-11-18",1.3577327E-2,2.3890664500000001,1.0861860000000001E-3,1.1133407999999999E-2,2.9870119999999998E-3,0,5,0]
["Jemena",2023,"Nov","2023-11-19","2023-11-25",1.7378978E-2,2.4162211039999999,0,3.801652E-3,2.1723720000000001E-3,0,5,0]
["Jemena",2023,"Nov","2023-11-26","2023-12-02",1.3577327E-2,1.3653359979999999,0,4.3447449999999997E-3,1.900826E-3,2.7154700000000002E-4,5,0]
["Jemena",2023,"Dec","2023-12-03","2023-12-09",0.357315255,1.8879729030000001,5.3934380000000004E-3,0.107329412,5.1237660000000001E-3,2.6967199999999999E-4,5,0]
["Jemena",2023,"Dec","2023-12-10","2023-12-16",1.173612066,1.5438715709999999,3.0742595000000001E-2,0.43012666500000002,8.3598289999999992E-3,0,5,0]
["Jemena",2023,"Dec","2023-12-17","2023-12-23",1.6449985E-2,1.5541191029999999,1.8877029999999999E-3,1.2135234999999999E-2,4.31475E-3,1.618031E-3,5,0]
["Jemena",2023,"Dec","2023-12-24","2023-12-30",1.9146704000000001E-2,1.5721871199999999,2.6967199999999999E-4,1.8068016999999999E-2,3.236063E-3,2.6967199999999999E-4,5,0]
["Jemena",2023,"Dec","2023-12-31","2024-01-06",7.0114691000000007E-2,1.5152863510000001,1.618031E-3,1.860736E-2,1.618031E-3,0,5,0]
["Jemena",2024,"Jan","2024-01-07","2024-01-13",0.49322988699999998,1.6765501410000001,1.2674579E-2,0.17933180700000001,2.6967190000000002E-3,0,5,0]
["Jemena",2024,"Jan","2024-01-14","2024-01-20",0.56981670399999995,2.0559784909999999,1.2674579E-2,0.20522030799999999,4.0450779999999997E-3,0,5,0]
["Jemena",2024,"Jan","2024-01-21","2024-01-27",0.17744410399999999,1.8361959000000001,7.550813E-3,5.3125362000000002E-2,5.1237660000000001E-3,0,5,0]
["Jemena",2024,"Jan","2024-01-28","2024-02-03",5.6631096999999998E-2,1.958626939,2.157375E-3,2.8045877E-2,4.31475E-3,2.6967199999999999E-4,5,0]
["Jemena",2024,"Feb","2024-02-04","2024-02-10",2.6344246949999999,2.095080915,8.7643364000000001E-2,1.1450268459999999,6.4721249999999996E-3,5.3934399999999998E-4,5,0]
["Jemena",2024,"Feb","2024-02-11","2024-02-17",1.7509795829999999,2.1107218849999998,4.0990127000000001E-2,0.61943633200000003,1.2674579E-2,2.6967199999999999E-4,5,0]
["Jemena",2024,"Feb","2024-02-18","2024-02-24",3.024370249,2.2625471589999999,7.2541737999999995E-2,1.2612554309999999,9.1688440000000006E-3,0,5,0]
["Jemena",2024,"Feb","2024-02-25","2024-03-02",0.20575965199999999,1.5856707139999999,2.4270469999999999E-3,5.9867160000000003E-2,4.31475E-3,0,5,0]
["Jemena",2024,"Mar","2024-03-03","2024-03-09",0.102205646,2.5497477220000002,3.7754059999999998E-3,5.3395034000000001E-2,5.9327820000000002E-3,2.6967199999999999E-4,5,0]
["Jemena",2024,"Mar","2024-03-10","2024-03-16",2.9326888100000001,1.6021469740000001,5.4428807000000003E-2,1.2984773409999999,1.8322569E-2,0,5,0]
["Jemena",2024,"Mar","2024-03-17","2024-03-23",0.27483853200000002,2.1329625710000002,5.9278899999999999E-3,0.102121376,3.5028440000000002E-3,0,5,0]
["Jemena",2024,"Mar","2024-03-24","2024-03-30",1.4011376000000001E-2,1.8511183499999999,5.3889900000000002E-4,2.7214404000000001E-2,2.4250460000000001E-3,2.6945000000000002E-4,5,0]
["Jemena",2024,"Apr","2024-03-31","2024-04-06",2.0747615000000001E-2,1.22249257,1.3472479999999999E-3,7.8140369999999994E-3,8.0834899999999998E-4,0,5,0]
["Jemena",2024,"Apr","2024-04-07","2024-04-13",5.7931651000000001E-2,0.92286467999999999,1.8861469999999999E-3,1.1586330000000001E-2,2.6944949999999999E-3,2.6945000000000002E-4,5,0]
["Jemena",2024,"Apr","2024-04-14","2024-04-20",7.1134679000000006E-2,1.3682647720000001,1.8861469999999999E-3,2.2903211E-2,1.3472477E-2,0,5,0]
["Jemena",2024,"Apr","2024-04-21","2024-04-27",0.108588165,1.2246481659999999,3.7722939999999998E-3,4.4998073E-2,1.9669816999999999E-2,2.1555960000000001E-3,5,0]
["Jemena",2024,"Apr","2024-04-28","2024-05-04",0.25031862399999999,1.3095247720000001,7.0056880000000004E-3,3.6375688000000003E-2,1.8053118999999999E-2,2.6945000000000002E-4,5,0]
["Jemena",2024,"May","2024-05-05","2024-05-11",0.14038321100000001,1.2265343129999999,5.9278899999999999E-3,2.8561651E-2,1.4280826E-2,0,5,0]
["Jemena",2024,"May","2024-05-12","2024-05-18",0.45429192699999998,1.5496043129999999,9.9696330000000003E-3,0.12583293600000001,2.371156E-2,0,5,0]
["Jemena",2024,"May","2024-05-19","2024-05-25",0.67119880799999998,1.2286899090000001,9.1612840000000004E-3,0.189692477,1.9400367000000002E-2,0,5,0]
["Jemena",2024,"May","2024-05-26","2024-06-01",0.378037707,1.236773396,5.9278899999999999E-3,9.1073945000000003E-2,2.5867155999999999E-2,2.4250460000000001E-3,5,0]
["Jemena",2024,"Jun","2024-06-02","2024-06-08",0.84734666400000003,1.0798258810000001,9.8870469999999995E-3,0.26801914300000002,2.4584009E-2,2.4049570000000001E-3,5,0]
["Jemena",2024,"Jun","2024-06-09","2024-06-15",0.92029703900000004,0.99217854400000005,5.6115669999999996E-3,0.32146264200000002,2.6721749E-2,5.3443499999999999E-4,5,0]
["Jemena",2024,"Jun","2024-06-16","2024-06-22",1.522338046,1.3489138949999999,8.818177E-3,0.57291430099999996,3.8479318999999998E-2,2.13774E-3,5,0]
["Jemena",2024,"Jun","2024-06-23","2024-06-29",1.279704564,1.3529221570000001,1.2024787E-2,0.447054862,3.3402186E-2,4.5426970000000001E-3,5,0]
["Jemena",2024,"Jun","2024-06-30","2024-07-06",1.8256298980000001,1.3563959839999999,8.016525E-3,0.62448727599999998,4.0617058999999997E-2,2.6721750000000002E-3,5,0]
["Jemena",2024,"Jul","2024-07-07","2024-07-13",1.279704564,1.198470447,5.8787850000000001E-3,0.416324851,3.3402186E-2,4.5426970000000001E-3,5,0]
["Jemena",2024,"Jul","2024-07-14","2024-07-20",1.5196658709999999,1.168809306,6.9476549999999996E-3,0.49408514100000001,3.2867751000000001E-2,2.6721750000000002E-3,5,0]
["Jemena",2024,"Jul","2024-07-21","2024-07-27",0.85242379599999996,1.2273299360000001,3.2066099999999999E-3,0.19854259599999999,2.8325053999999999E-2,5.3443499999999999E-4,5,0]
["Jemena",2024,"Jul","2024-07-28","2024-08-03",1.831241466,1.54424988,9.6198299999999994E-3,0.61540188200000001,4.0349840999999997E-2,2.6721699999999999E-4,5,0]
["Jemena",2024,"Aug","2024-08-04","2024-08-10",1.044018737,1.692822805,5.3443500000000003E-3,0.25626157399999999,2.8057836999999999E-2,0,5,0]
["Jemena",2024,"Aug","2024-08-11","2024-08-17",0.124790568,1.9950457880000001,2.9393919999999999E-3,1.8972441999999999E-2,6.680437E-3,0,5,0]
["Jemena",2024,"Aug","2024-08-18","2024-08-24",0.410446066,1.6995032430000001,6.4132199999999999E-3,8.1234116999999995E-2,1.7369137E-2,1.603305E-3,5,0]
["Jemena",2024,"Aug","2024-08-25","2024-08-31",0.31478220400000001,2.0573074629999999,2.0842963999999999E-2,0.19747372599999999,9.6198299999999994E-3,0,5,0]
["Jemena",2024,"Aug","2024-09-01","2024-09-07",0.32039377200000002,1.6532746169999999,6.9476549999999996E-3,0.107955866,2.2179052000000001E-2,5.3443499999999999E-4,5,0]
["Jemena",2024,"Sep","2024-09-08","2024-09-14",0.16896429499999999,2.3104322690000001,5.6410970000000003E-3,3.2503465000000002E-2,1.7729162999999999E-2,0,5,0]
["Jemena",2024,"Sep","2024-09-15","2024-09-21",0.42281707899999998,2.420318859,1.1819537E-2,0.119807127,2.39077E-2,2.68626E-4,5,0]
["Jemena",2024,"Sep","2024-09-22","2024-09-28",0.21111439400000001,1.466519836,4.8346810000000004E-3,4.4855093999999998E-2,1.4772636E-2,2.6859340000000001E-3,5,0]
["Jemena",2024,"Sep","2024-09-29","2024-10-05",8.3714566000000004E-2,2.3483008889999999,4.2930549999999996E-3,1.7440534000000001E-2,1.4489059E-2,4.2930549999999996E-3,5,0]
["Jemena",2024,"Oct","2024-10-06","2024-10-12",0.122909136,2.7718962089999999,5.3672110000000002E-3,3.9717362999999999E-2,7.7824560000000001E-3,0,5,0]
["Jemena",2024,"Oct","2024-10-13","2024-10-19",5.4458632999999999E-2,2.1831741600000001,3.4874989999999998E-3,4.0508638E-2,8.5846120000000001E-3,0,5,0]
["Jemena",2024,"Oct","2024-10-20","2024-10-26",2.5749899E-2,2.5535316250000002,6.1692470000000001E-3,2.1190021E-2,6.7057030000000004E-3,2.4140530000000002E-3,5,0]
["Jemena",2024,"Oct","2024-10-27","2024-11-02",2.0918763E-2,2.6644603629999999,2.6818929999999999E-3,2.0114195000000001E-2,1.4482220000000001E-2,1.877325E-3,5,0]
["Jemena",2024,"Nov","2024-11-03","2024-11-09",1.8503967999999999E-2,2.2572158770000001,3.7544280000000002E-3,1.3676845999999999E-2,1.0458764000000001E-2,1.0726939999999999E-3,5,0]
["Jemena",2024,"Nov","2024-11-10","2024-11-16",2.2110102999999999E-2,2.4100012249999998,3.1966410000000001E-3,5.3277359999999996E-3,1.0655471E-2,0,5,0]
["Jemena",2024,"Nov","2024-11-17","2024-11-23",0.71383861400000004,2.6337448559999999,3.8888223E-2,0.243983646,1.3850599999999999E-2,0,5,0]
["Jemena",2024,"Nov","2024-11-24","2024-11-30",0.187547885,2.4298757129999999,3.7243549999999999E-3,4.8150591999999999E-2,0.120509492,0,5,0]
["Jemena",2024,"Dec","2024-12-01","2024-12-07",0.60110961799999996,3.7854738490000002,2.3948589999999999E-2,0.14927954700000001,8.1159112000000005E-2,0,5,0]
["Jemena",2024,"Dec","2024-12-08","2024-12-14",2.7666270294140299E-2,2.22447454038078,5.3204365950269904E-4,2.3143899188367401E-2,8.7787203817945303E-3,0,5,0]
["Jemena",2024,"Dec","2024-12-15","2024-12-21",3.76419585627277,4.1692598207399101,0.16596186068778401,1.7915370089630001,3.5905210244953301E-2,0,5,0]
["Jemena",2024,"Dec","2024-12-22","2024-12-28",0.789820096533567,1.75941069315356,1.7019692315874899E-2,0.328692807850333,1.8083423085617001E-2,5.3186538487108896E-4,5,0]
["Jemena",2024,"Dec","2024-12-29","2025-01-04",3.3772194581025303E-2,1.3798733675664601,1.5955367518594699E-3,7.1799153833675897E-3,4.2547646716252401E-3,0,5,0]
["Jemena",2025,"Jan","2025-01-05","2025-01-11",1.6981367813555901,1.44958357369004,3.3494870765623602E-2,0.61859177993338199,2.5519901535713201E-2,5.31664615327359E-4,5,0]
["Jemena",2025,"Jan","2025-01-12","2025-01-18",8.2397282484464096E-2,1.78961581602547,4.5185606523738403E-3,2.9503543083146799E-2,6.11334676497637E-3,2.6579768543375502E-4,5,0]
["Jemena",2025,"Jan","2025-01-19","2025-01-25",1.4886788141582601,1.6927311663398601,3.8525509200954398E-2,0.53271479964078305,2.5240850855797699E-2,7.9707950070940104E-4,5,0]
["Jemena",2025,"Jan","2025-01-26","2025-02-01",2.0769085698044698,1.98473728527677,8.2343222488730897E-2,0.99954047169385296,1.93905007796044E-2,1.0624931934029799E-3,5,0]
["Jemena",2025,"Feb","2025-02-02","2025-02-08",5.9511923097349797,1.5946146901056899,0.101704817037548,2.81586913803176,4.43464868022731E-2,0,5,0]
["Jemena",2025,"Feb","2025-02-09","2025-02-15",2.57007919167678,1.6249824121737,6.1059623394861998E-2,1.0406683639472101,2.9733381827063199E-2,2.6547662345592198E-4,5,0]
["Jemena",2025,"Feb","2025-02-16","2025-02-22",5.2550978430212003E-2,2.0603699270390701,3.7157257475907502E-3,3.5830212566053697E-2,1.35358580805092E-2,0,5,0]
["Jemena",2025,"Feb","2025-02-23","2025-03-01",0.336719098261479,1.4171920439831001,5.8375257381816604E-3,0.152041011271732,2.7064892058842299E-2,0,5,0]
["Jemena",2025,"Mar","2025-03-02","2025-03-08",0.236579045780167,1.37783424083853,6.3653554918430598E-3,6.9753687264780206E-2,2.91745460042807E-3,7.9566943648038302E-4,5,0]
["Jemena",2025,"Mar","2025-03-09","2025-03-15",2.5064903036586998,1.2569576850764099,2.8639542191614499E-2,0.91779125486275603,2.5457370836990598E-2,0,5,0]
["Jemena",2025,"Mar","2025-03-16","2025-03-22",0.13678730104870301,1.7323740549482001,3.1811000243884302E-3,0.108422492497906,1.5110225115845101E-2,5.3018333739807198E-4,5,0]
["Jemena",2025,"Mar","2025-03-23","2025-03-29",2.5977675104109501E-2,2.6937258613057198,2.6507831738887302E-4,6.6269579347218097E-3,8.4825061564439194E-3,0,5,0]
["Jemena",2025,"Mar","2025-03-30","2025-04-05",2.3044587303227001E-2,1.9042245761252801,1.8541621968113701E-3,2.2779706989396801E-2,1.7482100712792902E-2,2.3839228244717601E-3,5,0]
["Jemena",2025,"Apr","2025-04-06","2025-04-12",6.0373521444515903E-2,1.3078281684844899,5.2959229337294698E-4,2.3566857055096101E-2,6.3551075204753603E-3,0,5,0]
["Jemena",2025,"Apr","2025-04-13","2025-04-19",7.3862087040777694E-2,0.95094127831710895,2.6473866322859399E-4,1.6149058456944199E-2,1.7208013109858599E-2,0,5,0]
["Jemena",2025,"Apr","2025-04-20","2025-04-26",2.5940543216150899E-2,0.85471442903011496,2.6469942057296802E-4,4.4998901497404599E-3,1.6940762916669998E-2,2.6469942057296802E-4,5,0]
["Jemena",2025,"Apr","2025-04-27","2025-05-03",9.2881714739349003E-2,1.3672929346387901,1.0584810796507001E-3,2.5932786451442199E-2,2.1698862132839399E-2,0,5,0]
["Jemena",2025,"May","2025-05-04","2025-05-10",8.33335537924704E-2,1.1756644858848799,7.9365289326162195E-4,1.19047933989243E-2,8.4656308614572996E-3,0,5,0]
["Jemena",2025,"May","2025-05-11","2025-05-17",0.13250217531016401,1.0253711251048001,1.0579015992827399E-3,3.0150195579558201E-2,3.2794949577764999E-2,0,5,0]
["Jemena",2025,"May","2025-05-18","2025-05-24",1.1995580297431201,1.6180023578795999,1.4538495292170901E-2,0.43800521271140302,4.8902211437302098E-2,0,5,0]
["Jemena",2025,"May","2025-05-25","2025-05-31",0.43305255815428201,0.888563607732062,7.9265263847641597E-4,0.116519937856033,3.2498758177533102E-2,1.84952282311164E-3,5,0]
["Jemena",2025,"Jun","2025-06-01","2025-06-07",0.88951941646258204,1.12226863116515,5.2837506175383497E-3,0.25890378025937899,4.8610505681352903E-2,2.6418753087691798E-4,5,0]
["Jemena",2025,"Jun","2025-06-08","2025-06-14",1.3173817236404799,1.12423971802852,2.1137291995836E-3,0.39579579262202802,5.3900094589381699E-2,0,5,0]
["Jemena",2025,"Jun","2025-06-15","2025-06-21",1.4970154772595201,1.2410860493370699,1.8488193967566399E-3,0.49442713010406197,6.3388093603084894E-2,0,5,0]
["Jemena",2025,"Jun","2025-06-22","2025-06-28",1.6747485632183901,1.14203008789723,4.4899425287356302E-3,0.60138818458417898,5.7312795807978399E-2,0,5,0]
["Jemena",2025,"Jun","2025-06-29","2025-07-05",1.22674283542058,1.07970264619543,7.9195793119469495E-4,0.430297142615784,5.86048869084074E-2,0,5,0]
["Jemena",2025,"Jul","2025-07-06","2025-07-12",0.94057030149932197,1.27017862134069,1.84580659111165E-3,0.26474140249658501,3.3488205295882797E-2,0,5,0]
["Jemena",2025,"Jul","2025-07-13","2025-07-19",0.94052894208946103,1.2737208094664401,7.9080348269853801E-4,0.27757202242718698,4.4284995031118102E-2,0,5,0]
["Jemena",2025,"Jul","2025-07-20","2025-07-26",1.3272948228911601,1.1991785798077199,2.10890935116768E-3,0.37854922853459799,4.6132392056792898E-2,0,5,0]
["Jemena",2025,"Jul","2025-07-27","2025-08-02",1.2051909427435401,1.12345626931311,3.6912433162130001E-3,0.39654499625602502,4.5349560742045401E-2,2.6366023687235699E-4,5,0]
["Jemena",2025,"Aug","2025-08-03","2025-08-09",0.76178874008211195,0.99752398883026305,3.16423152682082E-3,0.205938735203922,4.7990844823449098E-2,0,5,0]
["Jemena",2025,"Aug","2025-08-10","2025-08-16",0.845187048728132,1.0300469929273299,7.64755831922491E-3,0.22731707831627099,2.7953144201304798E-2,0,5,0]
["Jemena",2025,"Aug","2025-08-17","2025-08-23",1.11451319825201,1.14695170354898,1.8460937973885701E-2,0.32702232982311802,2.2944308624686501E-2,0,5,0]
["Jemena",2025,"Aug","2025-08-24","2025-08-30",0.684256275440977,0.92250042401628196,4.7701831750339204E-3,0.17411168588873799,1.7490671641791002E-2,0,5,0]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Undervoltage compliance assessment"]
["Undervoltage threshold (%)",null,null,null,null,5]
["Actual (%)",null,null,null,null,{"$f":"F167","v":5.9511923097349797}]
["Improvement required from all customers above 253V to maintain 5% compliance (%)",null,null,null,null,{"$f":"IF(F221<F220,0,(F221-F220)/F221)","v":0.15983222524653021}]
[]
[]
["Overvoltage compliance assessment"]
["Over-voltage threshold (%)",null,null,null,null,5]
["Actual (%)",null,null,null,null,{"$f":"G158","v":3.7854738490000002}]
["Improvement required from all customers above 253V to maintain 5% compliance (%)",null,null,null,null,{"$f":"IF(F227<F226,0,(F227-F226)/F227)","v":0}]
[]
["Note 1: Week 15/12/2024-21/12/2024 over-voltage data under (b) is ignored due to this week performance has been contributed by AusNet's TT zone substation by 49% (which is outside JEN's control)"]
["Note 2: Week 1/12/2024-7/12/2024 over-voltage data under (b) is used for the over-voltage compliance analysis"]

{"sheet":"Total Network Demand","index":1,"n_rows":105130,"n_cols":4,"rows_kept":4500,"cut":true,"hidden":false,"merged":[],"bounds":{"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0}}
[null,"Network","Total"]
["Time Start (AEST)","Time End (AEST)","MW","MVAr"]
[45371,"2024-03-20T00:05:00",417.79155839999999,-0.4110432]
["2024-03-20T00:05:00","2024-03-20T00:10:00",415.22493839999998,-1.8088944]
["2024-03-20T00:10:00","2024-03-20T00:15:00",413.43058200000002,-1.7921376]
["2024-03-20T00:15:00","2024-03-20T00:20:00",410.19693599999999,-2.0750052000000001]
["2024-03-20T00:20:00","2024-03-20T00:25:00",407.82668159999997,-1.9000644]
["2024-03-20T00:25:00","2024-03-20T00:30:00",405.08116680000001,-3.6527783999999999]
["2024-03-20T00:30:00","2024-03-20T00:35:00",403.80376799999999,-3.6677711999999998]
["2024-03-20T00:35:00","2024-03-20T00:40:00",402.12390599999998,-3.7130627999999999]
["2024-03-20T00:40:00","2024-03-20T00:45:00",399.08046359999997,-4.6184244000000003]
["2024-03-20T00:45:00","2024-03-20T00:50:00",396.87861839999999,-4.9222007999999997]
["2024-03-20T00:50:00","2024-03-20T00:55:00",395.5947984,-5.2411212000000003]
["2024-03-20T00:55:00","2024-03-20T01:00:00",391.32608520000002,-6.9361427999999998]
["2024-03-20T01:00:00","2024-03-20T01:05:00",387.23117760000002,-8.4914711999999994]
["2024-03-20T01:05:00","2024-03-20T01:10:00",386.4400632,-8.8254011999999999]
["2024-03-20T01:10:00","2024-03-20T01:15:00",384.97391640000001,-9.6826416000000002]
["2024-03-20T01:15:00","2024-03-20T01:20:00",384.1871064,-8.5642656000000006]
["2024-03-20T01:20:00","2024-03-20T01:25:00",378.9829512,-10.3149756]
["2024-03-20T01:25:00","2024-03-20T01:30:00",378.7760796,-10.133022]
["2024-03-20T01:30:00","2024-03-20T01:35:00",377.86700039999999,-11.1163872]
["2024-03-20T01:35:00","2024-03-20T01:40:00",377.79878880000001,-9.9955739999999995]
["2024-03-20T01:40:00","2024-03-20T01:45:00",377.43741119999999,-9.9484163999999993]
["2024-03-20T01:45:00","2024-03-20T01:50:00",376.71801599999998,-10.434468000000001]
["2024-03-20T01:50:00","2024-03-20T01:55:00",375.87142319999998,-10.460690400000001]
["2024-03-20T01:55:00","2024-03-20T02:00:00",376.18259640000002,-9.1669224000000007]
["2024-03-20T02:00:00","2024-03-20T02:05:00",377.0149644,-9.4680108000000001]
["2024-03-20T02:05:00","2024-03-20T02:10:00",376.91296199999999,-10.144246799999999]
["2024-03-20T02:10:00","2024-03-20T02:15:00",376.88239320000002,-10.464646800000001]
["2024-03-20T02:15:00","2024-03-20T02:20:00",377.13408600000002,-11.3974308]
["2024-03-20T02:20:00","2024-03-20T02:25:00",376.66502279999997,-11.11449]
["2024-03-20T02:25:00","2024-03-20T02:30:00",375.14918039999998,-12.1782012]
["2024-03-20T02:30:00","2024-03-20T02:35:00",374.75212920000001,-11.7671388]
["2024-03-20T02:35:00","2024-03-20T02:40:00",375.11842680000001,-11.9766876]
["2024-03-20T02:40:00","2024-03-20T02:45:00",374.92857839999999,-12.839064]
["2024-03-20T02:45:00","2024-03-20T02:50:00",374.07264120000002,-13.4437584]
["2024-03-20T02:50:00","2024-03-20T02:55:00",374.23573320000003,-13.481873999999999]
["2024-03-20T02:55:00","2024-03-20T03:00:00",374.48309160000002,-12.808337999999999]
["2024-03-20T03:00:00","2024-03-20T03:05:00",374.58020399999998,-12.907997999999999]
["2024-03-20T03:05:00","2024-03-20T03:10:00",374.88810480000001,-13.433681999999999]
["2024-03-20T03:10:00","2024-03-20T03:15:00",376.23138239999997,-13.5688584]
["2024-03-20T03:15:00","2024-03-20T03:20:00",375.79177800000002,-13.4117076]
["2024-03-20T03:20:00","2024-03-20T03:25:00",376.45969919999999,-13.107298800000001]
["2024-03-20T03:25:00","2024-03-20T03:30:00",376.57199159999999,-13.194618]
["2024-03-20T03:30:00","2024-03-20T03:35:00",377.89681680000001,-12.7499916]
["2024-03-20T03:35:00","2024-03-20T03:40:00",380.63187479999999,-12.522822]
["2024-03-20T03:40:00","2024-03-20T03:45:00",381.7823712,-12.3478224]
["2024-03-20T03:45:00","2024-03-20T03:50:00",383.34514439999998,-11.413714799999999]
["2024-03-20T03:50:00","2024-03-20T03:55:00",385.22706479999999,-10.918957199999999]
["2024-03-20T03:55:00","2024-03-20T04:00:00",390.0043632,-9.4935012000000008]
["2024-03-20T04:00:00","2024-03-20T04:05:00",393.10616520000002,-8.8202687999999991]
["2024-03-20T04:05:00","2024-03-20T04:10:00",395.65490399999999,-8.6974572000000006]
["2024-03-20T04:10:00","2024-03-20T04:15:00",402.32694120000002,-6.8451696000000002]
["2024-03-20T04:15:00","2024-03-20T04:20:00",401.88661439999998,-6.7270152000000003]
["2024-03-20T04:20:00","2024-03-20T04:25:00",406.88760000000002,-5.6831015999999996]
["2024-03-20T04:25:00","2024-03-20T04:30:00",410.10003840000002,-4.1254103999999998]
["2024-03-20T04:30:00","2024-03-20T04:35:00",412.51647960000003,-2.8187448000000002]
["2024-03-20T04:35:00","2024-03-20T04:40:00",416.3045568,-1.8105708]
["2024-03-20T04:40:00","2024-03-20T04:45:00",420.10802999999999,-0.52464]
["2024-03-20T04:45:00","2024-03-20T04:50:00",420.94958759999997,-1.3592831999999999]
["2024-03-20T04:50:00","2024-03-20T04:55:00",423.91273439999998,2.8178399999999999E-2]
["2024-03-20T04:55:00","2024-03-20T05:00:00",432.50206079999998,3.1496832000000001]
["2024-03-20T05:00:00","2024-03-20T05:05:00",442.69093800000002,6.7009847999999996]
["2024-03-20T05:05:00","2024-03-20T05:10:00",447.44804640000001,8.1671771999999994]
["2024-03-20T05:10:00","2024-03-20T05:15:00",453.21168719999997,10.9413912]
["2024-03-20T05:15:00","2024-03-20T05:20:00",460.49421360000002,13.852748399999999]
["2024-03-20T05:20:00","2024-03-20T05:25:00",466.19259360000001,17.476407600000002]
["2024-03-20T05:25:00","2024-03-20T05:30:00",470.29792800000001,19.027557600000002]
["2024-03-20T05:30:00","2024-03-20T05:35:00",475.23330600000003,20.768158799999998]
["2024-03-20T05:35:00","2024-03-20T05:40:00",483.05822160000002,23.747443199999999]
["2024-03-20T05:40:00","2024-03-20T05:45:00",486.77464199999997,24.430585199999999]
["2024-03-20T05:45:00","2024-03-20T05:50:00",489.6486744,25.606737599999999]
["2024-03-20T05:50:00","2024-03-20T05:55:00",494.5833672,27.840118799999999]
["2024-03-20T05:55:00","2024-03-20T06:00:00",504.4476444,31.660896000000001]
["2024-03-20T06:00:00","2024-03-20T06:05:00",513.68340839999996,34.431104400000002]
["2024-03-20T06:05:00","2024-03-20T06:10:00",519.9804408,36.421027199999997]
["2024-03-20T06:10:00","2024-03-20T06:15:00",527.15924399999994,39.709060800000003]
["2024-03-20T06:15:00","2024-03-20T06:20:00",532.63858440000001,42.3647268]
["2024-03-20T06:20:00","2024-03-20T06:25:00",535.69323240000006,42.657262799999998]
["2024-03-20T06:25:00","2024-03-20T06:30:00",538.03424280000002,44.740468800000002]
["2024-03-20T06:30:00","2024-03-20T06:35:00",544.20852360000004,47.630017199999998]
["2024-03-20T06:35:00","2024-03-20T06:40:00",545.35823760000005,49.644542399999999]
["2024-03-20T06:40:00","2024-03-20T06:45:00",542.22455760000003,49.353339599999998]
["2024-03-20T06:45:00","2024-03-20T06:50:00",540.60821999999996,49.633239600000003]
["2024-03-20T06:50:00","2024-03-20T06:55:00",538.97040240000001,51.044995200000002]
["2024-03-20T06:55:00","2024-03-20T07:00:00",537.58164720000002,51.7048956]
["2024-03-20T07:00:00","2024-03-20T07:05:00",533.41180559999998,51.828483599999998]
["2024-03-20T07:05:00","2024-03-20T07:10:00",532.86403319999999,53.081608799999998]
["2024-03-20T07:10:00","2024-03-20T07:15:00",529.62275160000002,54.010841999999997]
["2024-03-20T07:15:00","2024-03-20T07:20:00",527.53212480000002,55.628061600000002]
["2024-03-20T07:20:00","2024-03-20T07:25:00",522.51667559999999,56.471908800000001]
["2024-03-20T07:25:00","2024-03-20T07:30:00",516.24847560000001,56.801804400000002]
["2024-03-20T07:30:00","2024-03-20T07:35:00",514.1935896,58.904714400000003]
["2024-03-20T07:35:00","2024-03-20T07:40:00",507.26044560000003,59.081617199999997]
["2024-03-20T07:40:00","2024-03-20T07:45:00",500.8182132,58.8610416]
["2024-03-20T07:45:00","2024-03-20T07:50:00",494.91960119999999,59.432374799999998]
["2024-03-20T07:50:00","2024-03-20T07:55:00",489.69970919999997,58.851874799999997]
["2024-03-20T07:55:00","2024-03-20T08:00:00",484.13440800000001,58.580843999999999]
["2024-03-20T08:00:00","2024-03-20T08:05:00",483.32614560000002,59.479453200000002]
["2024-03-20T08:05:00","2024-03-20T08:10:00",478.7072976,59.937233999999997]
["2024-03-20T08:10:00","2024-03-20T08:15:00",470.08091280000002,59.100622799999996]
["2024-03-20T08:15:00","2024-03-20T08:20:00",464.2821816,59.1740256]
["2024-03-20T08:20:00","2024-03-20T08:25:00",462.25017359999998,60.804002400000002]
["2024-03-20T08:25:00","2024-03-20T08:30:00",454.2152772,59.808537600000001]
["2024-03-20T08:30:00","2024-03-20T08:35:00",447.69684119999999,58.894433999999997]
["2024-03-20T08:35:00","2024-03-20T08:40:00",443.26292280000001,59.353091999999997]
["2024-03-20T08:40:00","2024-03-20T08:45:00",437.24020919999998,58.848975600000003]
["2024-03-20T08:45:00","2024-03-20T08:50:00",438.26215200000001,60.876370799999997]
["2024-03-20T08:50:00","2024-03-20T08:55:00",436.492662,60.532297200000002]
["2024-03-20T08:55:00","2024-03-20T09:00:00",434.06390040000002,59.713130399999997]
["2024-03-20T09:00:00","2024-03-20T09:05:00",434.6069028,58.556746799999999]
["2024-03-20T09:05:00","2024-03-20T09:10:00",429.7766484,58.5552384]
["2024-03-20T09:10:00","2024-03-20T09:15:00",433.07704439999998,59.0046648]
["2024-03-20T09:15:00","2024-03-20T09:20:00",428.21214959999998,60.167397600000001]
["2024-03-20T09:20:00","2024-03-20T09:25:00",411.47761800000001,59.926339200000001]
["2024-03-20T09:25:00","2024-03-20T09:30:00",395.18184719999999,62.4604176]
["2024-03-20T09:30:00","2024-03-20T09:35:00",385.6549584,63.8043756]
["2024-03-20T09:35:00","2024-03-20T09:40:00",394.10613719999998,65.367010800000003]
["2024-03-20T09:40:00","2024-03-20T09:45:00",393.86904240000001,63.7763268]
["2024-03-20T09:45:00","2024-03-20T09:50:00",384.2688048,67.932777599999994]
["2024-03-20T09:50:00","2024-03-20T09:55:00",377.93979839999997,66.750979200000003]
["2024-03-20T09:55:00","2024-03-20T10:00:00",376.0961532,70.068559199999996]
["2024-03-20T10:00:00","2024-03-20T10:05:00",369.35953560000002,71.536216800000005]
["2024-03-20T10:05:00","2024-03-20T10:10:00",368.90906999999999,68.437026000000003]
["2024-03-20T10:10:00","2024-03-20T10:15:00",364.38146999999998,66.373928399999997]
["2024-03-20T10:15:00","2024-03-20T10:20:00",370.00293240000002,66.778115999999997]
["2024-03-20T10:20:00","2024-03-20T10:25:00",383.0818716,68.117252399999998]
["2024-03-20T10:25:00","2024-03-20T10:30:00",381.76416,67.574158800000006]
["2024-03-20T10:30:00","2024-03-20T10:35:00",380.70382439999997,66.011052000000007]
["2024-03-20T10:35:00","2024-03-20T10:40:00",389.2752648,67.737441599999997]
["2024-03-20T10:40:00","2024-03-20T10:45:00",384.91713479999999,69.733109999999996]
["2024-03-20T10:45:00","2024-03-20T10:50:00",387.05275440000003,68.7145692]
["2024-03-20T10:50:00","2024-03-20T10:55:00",395.59687200000002,68.155280399999995]
["2024-03-20T10:55:00","2024-03-20T11:00:00",402.74282040000003,67.896994800000002]
["2024-03-20T11:00:00","2024-03-20T11:05:00",389.01573480000002,66.300582000000006]
["2024-03-20T11:05:00","2024-03-20T11:10:00",372.26215079999997,65.781332399999997]
["2024-03-20T11:10:00","2024-03-20T11:15:00",354.37689599999999,70.217376000000002]
["2024-03-20T11:15:00","2024-03-20T11:20:00",353.54059439999997,71.164870800000003]
["2024-03-20T11:20:00","2024-03-20T11:25:00",369.08310840000001,71.0153964]
["2024-03-20T11:25:00","2024-03-20T11:30:00",369.50168880000001,70.959398399999998]
["2024-03-20T11:30:00","2024-03-20T11:35:00",369.96704879999999,68.941328400000003]
["2024-03-20T11:35:00","2024-03-20T11:40:00",376.22623800000002,70.215051599999995]
["2024-03-20T11:40:00","2024-03-20T11:45:00",385.16595119999999,71.391195600000003]
["2024-03-20T11:45:00","2024-03-20T11:50:00",389.42386440000001,67.5573744]
["2024-03-20T11:50:00","2024-03-20T11:55:00",395.9533404,72.585128400000002]
["2024-03-20T11:55:00","2024-03-20T12:00:00",396.47292599999997,77.334162000000006]
["2024-03-20T12:00:00","2024-03-20T12:05:00",401.70323400000001,74.677792800000006]
["2024-03-20T12:05:00","2024-03-20T12:10:00",389.57320320000002,71.395732800000005]
["2024-03-20T12:10:00","2024-03-20T12:15:00",378.7027296,68.088149999999999]
["2024-03-20T12:15:00","2024-03-20T12:20:00",359.00355719999999,73.156975200000005]
["2024-03-20T12:20:00","2024-03-20T12:25:00",338.37590999999998,77.326534800000005]
["2024-03-20T12:25:00","2024-03-20T12:30:00",332.69091600000002,77.500069199999999]
["2024-03-20T12:30:00","2024-03-20T12:35:00",323.31456600000001,78.547048799999999]
["2024-03-20T12:35:00","2024-03-20T12:40:00",316.8146964,79.072178399999999]
["2024-03-20T12:40:00","2024-03-20T12:45:00",328.06247280000002,78.9516876]
["2024-03-20T12:45:00","2024-03-20T12:50:00",335.2235508,79.740560400000007]
["2024-03-20T12:50:00","2024-03-20T12:55:00",342.06,80.798138399999999]
["2024-03-20T12:55:00","2024-03-20T13:00:00",355.2759456,76.709368799999993]
["2024-03-20T13:00:00","2024-03-20T13:05:00",357.26352480000003,74.837914799999993]
["2024-03-20T13:05:00","2024-03-20T13:10:00",360.14099520000002,76.138487999999995]
["2024-03-20T13:10:00","2024-03-20T13:15:00",353.95142520000002,76.085036400000007]
["2024-03-20T13:15:00","2024-03-20T13:20:00",344.20694520000001,75.426841199999998]
["2024-03-20T13:20:00","2024-03-20T13:25:00",332.94788879999999,74.338684799999996]
["2024-03-20T13:25:00","2024-03-20T13:30:00",338.07785159999997,73.816363199999998]
["2024-03-20T13:30:00","2024-03-20T13:35:00",338.57933279999997,72.215200800000005]
["2024-03-20T13:35:00","2024-03-20T13:40:00",339.86096279999998,72.836216399999998]
["2024-03-20T13:40:00","2024-03-20T13:45:00",340.50399720000001,71.196557999999996]
["2024-03-20T13:45:00","2024-03-20T13:50:00",338.84972520000002,69.240026400000005]
["2024-03-20T13:50:00","2024-03-20T13:55:00",326.06041199999999,66.642420000000001]
["2024-03-20T13:55:00","2024-03-20T14:00:00",331.33174079999998,67.489315199999993]
["2024-03-20T14:00:00","2024-03-20T14:05:00",328.97944919999998,66.135084000000006]
["2024-03-20T14:05:00","2024-03-20T14:10:00",324.52343159999998,67.500473999999997]
["2024-03-20T14:10:00","2024-03-20T14:15:00",331.0118172,67.071911999999998]
["2024-03-20T14:15:00","2024-03-20T14:20:00",336.00826319999999,63.932444400000001]
["2024-03-20T14:20:00","2024-03-20T14:25:00",340.58327759999997,60.894052799999997]
["2024-03-20T14:25:00","2024-03-20T14:30:00",342.129186,64.066121999999993]
["2024-03-20T14:30:00","2024-03-20T14:35:00",340.17122519999998,62.822904000000001]
["2024-03-20T14:35:00","2024-03-20T14:40:00",340.35182759999998,62.5497072]
["2024-03-20T14:40:00","2024-03-20T14:45:00",338.72833320000001,59.027135999999999]
["2024-03-20T14:45:00","2024-03-20T14:50:00",341.77472999999998,54.739258800000002]
["2024-03-20T14:50:00","2024-03-20T14:55:00",345.9828144,54.976533600000003]
["2024-03-20T14:55:00","2024-03-20T15:00:00",344.96908439999999,56.482640400000001]
["2024-03-20T15:00:00","2024-03-20T15:05:00",351.77758080000001,57.418957200000001]
["2024-03-20T15:05:00","2024-03-20T15:10:00",354.3229728,56.446406400000001]
["2024-03-20T15:10:00","2024-03-20T15:15:00",355.40470679999999,53.544893999999999]
["2024-03-20T15:15:00","2024-03-20T15:20:00",360.68380079999997,53.383582799999999]
["2024-03-20T15:20:00","2024-03-20T15:25:00",364.13246520000001,51.838438799999999]
["2024-03-20T15:25:00","2024-03-20T15:30:00",364.8647436,49.799193600000002]
["2024-03-20T15:30:00","2024-03-20T15:35:00",366.58559159999999,50.8113648]
["2024-03-20T15:35:00","2024-03-20T15:40:00",373.14434999999997,49.466188799999998]
["2024-03-20T15:40:00","2024-03-20T15:45:00",376.40016359999998,46.969794]
["2024-03-20T15:45:00","2024-03-20T15:50:00",382.4271324,42.336036]
["2024-03-20T15:50:00","2024-03-20T15:55:00",386.85811319999999,42.2137356]
["2024-03-20T15:55:00","2024-03-20T16:00:00",393.57981960000001,43.449367199999998]
["2024-03-20T16:00:00","2024-03-20T16:05:00",402.86838599999999,42.604246799999999]
["2024-03-20T16:05:00","2024-03-20T16:10:00",407.95800600000001,41.392226399999998]
["2024-03-20T16:10:00","2024-03-20T16:15:00",413.71388760000002,40.907409600000001]
["2024-03-20T16:15:00","2024-03-20T16:20:00",417.5568672,40.324263600000002]
["2024-03-20T16:20:00","2024-03-20T16:25:00",421.08422519999999,38.941420800000003]
["2024-03-20T16:25:00","2024-03-20T16:30:00",431.19424559999999,37.958350799999998]
["2024-03-20T16:30:00","2024-03-20T16:35:00",441.8655996,37.978153200000001]
["2024-03-20T16:35:00","2024-03-20T16:40:00",443.97990240000001,36.085766399999997]
["2024-03-20T16:40:00","2024-03-20T16:45:00",452.91298560000001,34.711617599999997]
["2024-03-20T16:45:00","2024-03-20T16:50:00",461.41397999999998,36.716392800000001]
["2024-03-20T16:50:00","2024-03-20T16:55:00",467.4585156,35.422735199999998]
["2024-03-20T16:55:00","2024-03-20T17:00:00",474.4972884,35.2199916]
["2024-03-20T17:00:00","2024-03-20T17:05:00",480.46961640000001,35.954450399999999]
["2024-03-20T17:05:00","2024-03-20T17:10:00",483.99892799999998,34.940912400000002]
["2024-03-20T17:10:00","2024-03-20T17:15:00",487.74396480000001,33.854677199999998]
["2024-03-20T17:15:00","2024-03-20T17:20:00",493.2873768,33.0912936]
["2024-03-20T17:20:00","2024-03-20T17:25:00",499.02501960000001,33.976906800000002]
["2024-03-20T17:25:00","2024-03-20T17:30:00",506.81391120000001,33.470164799999999]
["2024-03-20T17:30:00","2024-03-20T17:35:00",512.26868999999999,33.944024400000004]
["2024-03-20T17:35:00","2024-03-20T17:40:00",518.54768999999999,33.791726400000002]
["2024-03-20T17:40:00","2024-03-20T17:45:00",523.03392480000002,32.9502636]
["2024-03-20T17:45:00","2024-03-20T17:50:00",527.9338884,33.023981999999997]
["2024-03-20T17:50:00","2024-03-20T17:55:00",531.53916000000004,32.149872000000002]
["2024-03-20T17:55:00","2024-03-20T18:00:00",535.41286200000002,31.840747199999999]
["2024-03-20T18:00:00","2024-03-20T18:05:00",538.20384120000006,31.021608000000001]
["2024-03-20T18:05:00","2024-03-20T18:10:00",542.00235480000003,30.6143532]
["2024-03-20T18:10:00","2024-03-20T18:15:00",543.53188920000002,32.949818399999998]
["2024-03-20T18:15:00","2024-03-20T18:20:00",545.2389144,32.280058799999999]
["2024-03-20T18:20:00","2024-03-20T18:25:00",549.94765800000005,32.463202799999998]
["2024-03-20T18:25:00","2024-03-20T18:30:00",550.75004760000002,31.7735652]
["2024-03-20T18:30:00","2024-03-20T18:35:00",551.82223080000006,31.295325600000002]
["2024-03-20T18:35:00","2024-03-20T18:40:00",552.50201159999995,31.090623600000001]
["2024-03-20T18:40:00","2024-03-20T18:45:00",551.32585800000004,29.489230800000001]
["2024-03-20T18:45:00","2024-03-20T18:50:00",549.49512719999996,29.2946016]
["2024-03-20T18:50:00","2024-03-20T18:55:00",550.67899079999995,29.538602399999998]
["2024-03-20T18:55:00","2024-03-20T19:00:00",552.45725879999998,29.832379199999998]
["2024-03-20T19:00:00","2024-03-20T19:05:00",553.67347440000003,30.2881812]
["2024-03-20T19:05:00","2024-03-20T19:10:00",551.0928672,29.158238399999998]
["2024-03-20T19:10:00","2024-03-20T19:15:00",549.11966399999994,28.3653972]
["2024-03-20T19:15:00","2024-03-20T19:20:00",548.08632720000003,27.690192]
["2024-03-20T19:20:00","2024-03-20T19:25:00",547.71782640000004,27.111338400000001]
["2024-03-20T19:25:00","2024-03-20T19:30:00",547.16184599999997,26.936185200000001]
["2024-03-20T19:30:00","2024-03-20T19:35:00",542.1082308,23.8485552]
["2024-03-20T19:35:00","2024-03-20T19:40:00",541.28407440000001,24.7478148]
["2024-03-20T19:40:00","2024-03-20T19:45:00",540.38076839999997,24.284928000000001]
["2024-03-20T19:45:00","2024-03-20T19:50:00",537.451728,22.384734000000002]
["2024-03-20T19:50:00","2024-03-20T19:55:00",532.96391400000005,21.421633199999999]
["2024-03-20T19:55:00","2024-03-20T20:00:00",532.30074839999997,21.285831600000002]
["2024-03-20T20:00:00","2024-03-20T20:05:00",528.92967120000003,20.833472400000002]
["2024-03-20T20:05:00","2024-03-20T20:10:00",524.70629039999994,19.530708000000001]
["2024-03-20T20:10:00","2024-03-20T20:15:00",521.86934399999996,18.205316400000001]
["2024-03-20T20:15:00","2024-03-20T20:20:00",519.11820120000004,17.318166000000002]
["2024-03-20T20:20:00","2024-03-20T20:25:00",517.96048800000005,16.851918000000001]
["2024-03-20T20:25:00","2024-03-20T20:30:00",514.46680919999994,15.0157224]
["2024-03-20T20:30:00","2024-03-20T20:35:00",510.7653588,14.9645148]
["2024-03-20T20:35:00","2024-03-20T20:40:00",508.57053480000002,15.0653928]
["2024-03-20T20:40:00","2024-03-20T20:45:00",504.13740000000001,13.000645199999999]
["2024-03-20T20:45:00","2024-03-20T20:50:00",501.77884440000003,12.523812]
["2024-03-20T20:50:00","2024-03-20T20:55:00",496.120206,11.0028972]
["2024-03-20T20:55:00","2024-03-20T21:00:00",493.03100519999998,10.052873999999999]
["2024-03-20T21:00:00","2024-03-20T21:05:00",488.82863400000002,9.4013975999999992]
["2024-03-20T21:05:00","2024-03-20T21:10:00",484.47352560000002,8.2727363999999994]
["2024-03-20T21:10:00","2024-03-20T21:15:00",481.09001280000001,6.9483360000000003]
["2024-03-20T21:15:00","2024-03-20T21:20:00",477.42558120000001,6.3428015999999996]
["2024-03-20T21:20:00","2024-03-20T21:25:00",473.84902440000002,5.8395815999999998]
["2024-03-20T21:25:00","2024-03-20T21:30:00",470.44828680000001,4.0625112000000003]
["2024-03-20T21:30:00","2024-03-20T21:35:00",465.89004240000003,2.9804148000000001]
["2024-03-20T21:35:00","2024-03-20T21:40:00",460.68983639999999,1.2395195999999999]
["2024-03-20T21:40:00","2024-03-20T21:45:00",457.05416400000001,0.89393160000000005]
["2024-03-20T21:45:00","2024-03-20T21:50:00",453.55031400000001,8.9643600000000004E-2]
["2024-03-20T21:50:00","2024-03-20T21:55:00",449.19799560000001,-1.2556620000000001]
["2024-03-20T21:55:00","2024-03-20T22:00:00",445.76810760000001,-2.2038251999999998]
["2024-03-20T22:00:00","2024-03-20T22:05:00",439.28880479999998,-4.1629104000000003]
["2024-03-20T22:05:00","2024-03-20T22:10:00",437.52745440000001,-3.7562052000000001]
["2024-03-20T22:10:00","2024-03-20T22:15:00",436.79952359999999,-4.1176716000000004]
["2024-03-20T22:15:00","2024-03-20T22:20:00",434.41494840000001,-4.6529651999999997]
["2024-03-20T22:20:00","2024-03-20T22:25:00",430.68184200000002,-5.4405900000000003]
["2024-03-20T22:25:00","2024-03-20T22:30:00",427.38962880000003,-6.4551588000000004]
["2024-03-20T22:30:00","2024-03-20T22:35:00",422.6668884,-6.7335383999999996]
["2024-03-20T22:35:00","2024-03-20T22:40:00",419.91418199999998,-6.5055335999999997]
["2024-03-20T22:40:00","2024-03-20T22:45:00",418.60477800000001,-6.9037452000000004]
["2024-03-20T22:45:00","2024-03-20T22:50:00",417.18001679999998,-7.2606468]
["2024-03-20T22:50:00","2024-03-20T22:55:00",414.26411159999998,-7.6769052000000002]
["2024-03-20T22:55:00","2024-03-20T23:00:00",411.79926360000002,-8.6659775999999997]
["2024-03-20T23:00:00","2024-03-20T23:05:00",417.02477879999998,-8.5295003999999999]
["2024-03-20T23:05:00","2024-03-20T23:10:00",428.21799479999999,-7.8629543999999996]
["2024-03-20T23:10:00","2024-03-20T23:15:00",431.65856760000003,-7.6295988000000001]
["2024-03-20T23:15:00","2024-03-20T23:20:00",430.4382276,-7.4893308000000003]
["2024-03-20T23:20:00","2024-03-20T23:25:00",427.1585316,-7.7564772]
["2024-03-20T23:25:00","2024-03-20T23:30:00",423.55046759999999,-8.2740516]
["2024-03-20T23:30:00","2024-03-20T23:35:00",420.84376079999998,-8.4518436000000001]
["2024-03-20T23:35:00","2024-03-20T23:40:00",415.2620928,-9.8910792000000001]
["2024-03-20T23:40:00","2024-03-20T23:45:00",411.85972320000002,-11.254791600000001]
["2024-03-20T23:45:00","2024-03-20T23:50:00",408.82935479999998,-12.3385392]
["2024-03-20T23:50:00","2024-03-20T23:55:00",405.96972599999998,-11.979805199999999]
["2024-03-20T23:55:00",45372,401.54806439999999,-12.99033]
[45372,"2024-03-21T00:05:00",399.53841840000001,-13.486048800000001]
["2024-03-21T00:05:00","2024-03-21T00:10:00",396.95678880000003,-14.100258]
["2024-03-21T00:10:00","2024-03-21T00:15:00",394.82910240000001,-14.70645]
["2024-03-21T00:15:00","2024-03-21T00:20:00",391.92759840000002,-15.4096872]
["2024-03-21T00:20:00","2024-03-21T00:25:00",388.84223279999998,-16.475590799999999]
["2024-03-21T00:25:00","2024-03-21T00:30:00",389.01909599999999,-15.623417999999999]
["2024-03-21T00:30:00","2024-03-21T00:35:00",386.1511332,-16.1455044]
["2024-03-21T00:35:00","2024-03-21T00:40:00",382.93197120000002,-17.327866799999999]
["2024-03-21T00:40:00","2024-03-21T00:45:00",380.43221160000002,-17.541580799999998]
["2024-03-21T00:45:00","2024-03-21T00:50:00",375.92688240000001,-19.534482000000001]
["2024-03-21T00:50:00","2024-03-21T00:55:00",375.12147959999999,-19.501573199999999]
["2024-03-21T00:55:00","2024-03-21T01:00:00",373.7903268,-19.716567600000001]
["2024-03-21T01:00:00","2024-03-21T01:05:00",371.661948,-20.914123199999999]
["2024-03-21T01:05:00","2024-03-21T01:10:00",371.9083152,-20.542608000000001]
["2024-03-21T01:10:00","2024-03-21T01:15:00",370.17550319999998,-21.338317199999999]
["2024-03-21T01:15:00","2024-03-21T01:20:00",370.62222960000003,-20.690215200000001]
["2024-03-21T01:20:00","2024-03-21T01:25:00",369.68334959999999,-20.550101999999999]
["2024-03-21T01:25:00","2024-03-21T01:30:00",367.69578719999998,-21.2572644]
["2024-03-21T01:30:00","2024-03-21T01:35:00",367.61051040000001,-20.782668000000001]
["2024-03-21T01:35:00","2024-03-21T01:40:00",367.39758,-20.713428]
["2024-03-21T01:40:00","2024-03-21T01:45:00",367.41729120000002,-20.375296800000001]
["2024-03-21T01:45:00","2024-03-21T01:50:00",365.84325239999998,-21.083756399999999]
["2024-03-21T01:50:00","2024-03-21T01:55:00",365.3226636,-20.998101599999998]
["2024-03-21T01:55:00","2024-03-21T02:00:00",365.03039760000001,-21.492969599999999]
["2024-03-21T02:00:00","2024-03-21T02:05:00",366.73149119999999,-20.294797200000001]
["2024-03-21T02:05:00","2024-03-21T02:10:00",367.14146879999998,-19.114960799999999]
["2024-03-21T02:10:00","2024-03-21T02:15:00",366.10112520000001,-19.970358000000001]
["2024-03-21T02:15:00","2024-03-21T02:20:00",367.23202079999999,-20.052531599999998]
["2024-03-21T02:20:00","2024-03-21T02:25:00",368.43208199999998,-19.384329600000001]
["2024-03-21T02:25:00","2024-03-21T02:30:00",369.25999680000001,-18.998169600000001]
["2024-03-21T02:30:00","2024-03-21T02:35:00",368.31146159999997,-19.352454000000002]
["2024-03-21T02:35:00","2024-03-21T02:40:00",367.77842399999997,-19.917655199999999]
["2024-03-21T02:40:00","2024-03-21T02:45:00",368.36733120000002,-19.73865]
["2024-03-21T02:45:00","2024-03-21T02:50:00",368.4229464,-19.43439]
["2024-03-21T02:50:00","2024-03-21T02:55:00",367.96469880000001,-19.485551999999998]
["2024-03-21T02:55:00","2024-03-21T03:00:00",368.20592399999998,-19.600720800000001]
["2024-03-21T03:00:00","2024-03-21T03:05:00",370.0959072,-19.2745572]
["2024-03-21T03:05:00","2024-03-21T03:10:00",371.55401039999998,-18.214988399999999]
["2024-03-21T03:10:00","2024-03-21T03:15:00",373.23772200000002,-17.696254799999998]
["2024-03-21T03:15:00","2024-03-21T03:20:00",372.83149559999998,-17.720189999999999]
["2024-03-21T03:20:00","2024-03-21T03:25:00",373.89326160000002,-17.221587599999999]
["2024-03-21T03:25:00","2024-03-21T03:30:00",374.75074560000002,-17.246941199999998]
["2024-03-21T03:30:00","2024-03-21T03:35:00",377.12850120000002,-16.610423999999998]
["2024-03-21T03:35:00","2024-03-21T03:40:00",377.92529760000002,-16.6234836]
["2024-03-21T03:40:00","2024-03-21T03:45:00",381.0197028,-16.0381596]
["2024-03-21T03:45:00","2024-03-21T03:50:00",381.22021799999999,-16.070245199999999]
["2024-03-21T03:50:00","2024-03-21T03:55:00",383.14039919999999,-15.680613599999999]
["2024-03-21T03:55:00","2024-03-21T04:00:00",387.33384239999998,-15.4711452]
["2024-03-21T04:00:00","2024-03-21T04:05:00",391.61687280000001,-14.3489352]
["2024-03-21T04:05:00","2024-03-21T04:10:00",398.74959480000001,-12.172717199999999]
["2024-03-21T04:10:00","2024-03-21T04:15:00",402.6569892,-11.1978756]
["2024-03-21T04:15:00","2024-03-21T04:20:00",403.78283640000001,-11.295734400000001]
["2024-03-21T04:20:00","2024-03-21T04:25:00",407.50645559999998,-10.255867200000001]
["2024-03-21T04:25:00","2024-03-21T04:30:00",409.0768104,-10.203033599999999]
["2024-03-21T04:30:00","2024-03-21T04:35:00",412.2696876,-9.2507712000000009]
["2024-03-21T04:35:00","2024-03-21T04:40:00",417.94968239999997,-7.5887675999999997]
["2024-03-21T04:40:00","2024-03-21T04:45:00",421.19622479999998,-5.8463136000000002]
["2024-03-21T04:45:00","2024-03-21T04:50:00",426.06972719999999,-4.1959008000000004]
["2024-03-21T04:50:00","2024-03-21T04:55:00",428.839494,-3.1986276]
["2024-03-21T04:55:00","2024-03-21T05:00:00",434.44015919999998,-1.1027100000000001]
["2024-03-21T05:00:00","2024-03-21T05:05:00",446.00223840000001,4.4592336000000001]
["2024-03-21T05:05:00","2024-03-21T05:10:00",454.78444560000003,9.4953108000000004]
["2024-03-21T05:10:00","2024-03-21T05:15:00",464.266752,12.518196]
["2024-03-21T05:15:00","2024-03-21T05:20:00",469.11850800000002,14.22828]
["2024-03-21T05:20:00","2024-03-21T05:25:00",475.27807319999999,18.594480000000001]
["2024-03-21T05:25:00","2024-03-21T05:30:00",478.92479159999999,20.546274]
["2024-03-21T05:30:00","2024-03-21T05:35:00",485.28352080000002,23.697996]
["2024-03-21T05:35:00","2024-03-21T05:40:00",493.34813159999999,25.705450800000001]
["2024-03-21T05:40:00","2024-03-21T05:45:00",497.9854704,26.941641600000001]
["2024-03-21T05:45:00","2024-03-21T05:50:00",503.18268,28.6773828]
["2024-03-21T05:50:00","2024-03-21T05:55:00",509.1339696,30.496861200000001]
["2024-03-21T05:55:00","2024-03-21T06:00:00",516.85125600000003,33.178912799999999]
["2024-03-21T06:00:00","2024-03-21T06:05:00",526.31217240000001,35.872590000000002]
["2024-03-21T06:05:00","2024-03-21T06:10:00",536.74758359999998,40.318795199999997]
["2024-03-21T06:10:00","2024-03-21T06:15:00",543.37295400000005,43.056160800000001]
["2024-03-21T06:15:00","2024-03-21T06:20:00",547.7150484,45.307582799999999]
["2024-03-21T06:20:00","2024-03-21T06:25:00",550.8668232,46.0296612]
["2024-03-21T06:25:00","2024-03-21T06:30:00",553.35247679999998,47.133744]
["2024-03-21T06:30:00","2024-03-21T06:35:00",557.44688880000001,49.278350400000001]
["2024-03-21T06:35:00","2024-03-21T06:40:00",559.22108160000005,49.856383200000003]
["2024-03-21T06:40:00","2024-03-21T06:45:00",561.88094760000001,50.377035599999999]
["2024-03-21T06:45:00","2024-03-21T06:50:00",560.27585280000005,51.0358704]
["2024-03-21T06:50:00","2024-03-21T06:55:00",561.06545159999996,54.782926799999998]
["2024-03-21T06:55:00","2024-03-21T07:00:00",557.93977919999998,54.379145999999999]
["2024-03-21T07:00:00","2024-03-21T07:05:00",557.14066200000002,55.945053600000001]
["2024-03-21T07:05:00","2024-03-21T07:10:00",553.71135600000002,57.145797600000002]
["2024-03-21T07:10:00","2024-03-21T07:15:00",552.66637920000005,57.598240799999999]
["2024-03-21T07:15:00","2024-03-21T07:20:00",549.49088759999995,59.366989199999999]
["2024-03-21T07:20:00","2024-03-21T07:25:00",544.23050639999997,60.858338400000001]
["2024-03-21T07:25:00","2024-03-21T07:30:00",534.13179239999999,59.642578800000003]
["2024-03-21T07:30:00","2024-03-21T07:35:00",532.14411359999997,60.942650399999998]
["2024-03-21T07:35:00","2024-03-21T07:40:00",527.17499880000003,60.726169200000001]
["2024-03-21T07:40:00","2024-03-21T07:45:00",519.82901159999994,59.977616400000002]
["2024-03-21T07:45:00","2024-03-21T07:50:00",512.76357959999996,59.923050000000003]
["2024-03-21T07:50:00","2024-03-21T07:55:00",510.5933268,61.746862800000002]
["2024-03-21T07:55:00","2024-03-21T08:00:00",502.40474280000001,62.317023599999999]
["2024-03-21T08:00:00","2024-03-21T08:05:00",499.28222640000001,62.309068799999999]
["2024-03-21T08:05:00","2024-03-21T08:10:00",495.23000999999999,60.492372000000003]
["2024-03-21T08:10:00","2024-03-21T08:15:00",489.3577836,59.212754400000001]
["2024-03-21T08:15:00","2024-03-21T08:20:00",485.91528840000001,59.464494000000002]
["2024-03-21T08:20:00","2024-03-21T08:25:00",481.39685880000002,60.809792399999999]
["2024-03-21T08:25:00","2024-03-21T08:30:00",479.32831920000001,61.891113599999997]
["2024-03-21T08:30:00","2024-03-21T08:35:00",469.0545156,60.933598799999999]
["2024-03-21T08:35:00","2024-03-21T08:40:00",462.92285040000002,59.840530800000003]
["2024-03-21T08:40:00","2024-03-21T08:45:00",457.18116839999999,61.733716800000003]
["2024-03-21T08:45:00","2024-03-21T08:50:00",450.62290080000002,63.586041600000001]
["2024-03-21T08:50:00","2024-03-21T08:55:00",443.1742428,61.7275992]
["2024-03-21T08:55:00","2024-03-21T09:00:00",434.72826959999998,60.853311599999998]
["2024-03-21T09:00:00","2024-03-21T09:05:00",429.93022680000001,61.847738399999997]
["2024-03-21T09:05:00","2024-03-21T09:10:00",422.10546959999999,60.072820800000002]
["2024-03-21T09:10:00","2024-03-21T09:15:00",415.3226664,60.047079600000004]
["2024-03-21T09:15:00","2024-03-21T09:20:00",406.74329879999999,61.159356000000002]
["2024-03-21T09:20:00","2024-03-21T09:25:00",402.5042292,64.146792000000005]
["2024-03-21T09:25:00","2024-03-21T09:30:00",398.30589600000002,66.392868000000007]
["2024-03-21T09:30:00","2024-03-21T09:35:00",393.30521520000002,66.171070799999995]
["2024-03-21T09:35:00","2024-03-21T09:40:00",387.4474644,66.005511600000006]
["2024-03-21T09:40:00","2024-03-21T09:45:00",381.92962080000001,67.656728400000006]
["2024-03-21T09:45:00","2024-03-21T09:50:00",375.4038468,69.104826000000003]
["2024-03-21T09:50:00","2024-03-21T09:55:00",371.68836959999999,69.8324772]
["2024-03-21T09:55:00","2024-03-21T10:00:00",366.06269759999998,64.357143600000001]
["2024-03-21T10:00:00","2024-03-21T10:05:00",363.3996492,66.317712]
["2024-03-21T10:05:00","2024-03-21T10:10:00",358.750698,64.179380399999999]
["2024-03-21T10:10:00","2024-03-21T10:15:00",353.36821079999999,64.640811600000006]
["2024-03-21T10:15:00","2024-03-21T10:20:00",351.00147479999998,65.316628800000004]
["2024-03-21T10:20:00","2024-03-21T10:25:00",345.50800079999999,66.3064404]
["2024-03-21T10:25:00","2024-03-21T10:30:00",341.62825320000002,66.546648000000005]
["2024-03-21T10:30:00","2024-03-21T10:35:00",335.1637968,65.938271999999998]
["2024-03-21T10:35:00","2024-03-21T10:40:00",335.01281519999998,67.352050800000001]
["2024-03-21T10:40:00","2024-03-21T10:45:00",333.82035480000002,69.090140399999996]
["2024-03-21T10:45:00","2024-03-21T10:50:00",328.39481760000001,69.15204]
["2024-03-21T10:50:00","2024-03-21T10:55:00",324.12846480000002,68.522199599999993]
["2024-03-21T10:55:00","2024-03-21T11:00:00",320.36470439999999,68.944396800000007]
["2024-03-21T11:00:00","2024-03-21T11:05:00",319.87724880000002,69.419948399999996]
["2024-03-21T11:05:00","2024-03-21T11:10:00",317.16764519999998,69.352400399999993]
["2024-03-21T11:10:00","2024-03-21T11:15:00",312.02929560000001,69.5150316]
["2024-03-21T11:15:00","2024-03-21T11:20:00",313.4105184,69.967910399999994]
["2024-03-21T11:20:00","2024-03-21T11:25:00",312.30795719999998,68.800665600000002]
["2024-03-21T11:25:00","2024-03-21T11:30:00",308.54110200000002,67.7778876]
["2024-03-21T11:30:00","2024-03-21T11:35:00",304.79156039999998,67.752946800000004]
["2024-03-21T11:35:00","2024-03-21T11:40:00",302.8032996,69.026726400000001]
["2024-03-21T11:40:00","2024-03-21T11:45:00",300.08000879999997,68.374859999999998]
["2024-03-21T11:45:00","2024-03-21T11:50:00",298.05125520000001,67.055875200000003]
["2024-03-21T11:50:00","2024-03-21T11:55:00",296.5686528,67.906413599999993]
["2024-03-21T11:55:00","2024-03-21T12:00:00",299.26142040000002,69.074907600000003]
["2024-03-21T12:00:00","2024-03-21T12:05:00",300.4264872,69.754031999999995]
["2024-03-21T12:05:00","2024-03-21T12:10:00",296.43599999999998,69.164882399999996]
["2024-03-21T12:10:00","2024-03-21T12:15:00",294.61164960000002,69.129145199999996]
["2024-03-21T12:15:00","2024-03-21T12:20:00",297.95279879999998,71.035537199999993]
["2024-03-21T12:20:00","2024-03-21T12:25:00",295.84066799999999,71.417670000000001]
["2024-03-21T12:25:00","2024-03-21T12:30:00",294.81523679999998,71.1589764]
["2024-03-21T12:30:00","2024-03-21T12:35:00",294.60598199999998,71.038117200000002]
["2024-03-21T12:35:00","2024-03-21T12:40:00",297.114846,72.240179999999995]
["2024-03-21T12:40:00","2024-03-21T12:45:00",296.69533319999999,73.108620000000002]
["2024-03-21T12:45:00","2024-03-21T12:50:00",297.61511039999999,75.639983999999998]
["2024-03-21T12:50:00","2024-03-21T12:55:00",295.32268319999997,74.711695199999994]
["2024-03-21T12:55:00","2024-03-21T13:00:00",298.76232479999999,75.3054384]
["2024-03-21T13:00:00","2024-03-21T13:05:00",297.94344719999998,73.427807999999999]
["2024-03-21T13:05:00","2024-03-21T13:10:00",296.9372856,72.627899999999997]
["2024-03-21T13:10:00","2024-03-21T13:15:00",298.99812839999998,72.955091999999993]
["2024-03-21T13:15:00","2024-03-21T13:20:00",302.61819000000003,73.527812400000002]
["2024-03-21T13:20:00","2024-03-21T13:25:00",303.35144400000001,73.328294400000004]
["2024-03-21T13:25:00","2024-03-21T13:30:00",303.44368680000002,73.537585199999995]
["2024-03-21T13:30:00","2024-03-21T13:35:00",304.38054599999998,73.135130399999994]
["2024-03-21T13:35:00","2024-03-21T13:40:00",307.12242120000002,72.778636800000001]
["2024-03-21T13:40:00","2024-03-21T13:45:00",307.40159999999997,72.290346]
["2024-03-21T13:45:00","2024-03-21T13:50:00",305.71152480000001,73.342904399999995]
["2024-03-21T13:50:00","2024-03-21T13:55:00",308.58759479999998,73.084642799999997]
["2024-03-21T13:55:00","2024-03-21T14:00:00",310.05929040000001,71.670514800000007]
["2024-03-21T14:00:00","2024-03-21T14:05:00",313.53590639999999,72.051621600000004]
["2024-03-21T14:05:00","2024-03-21T14:10:00",315.03755760000001,73.289298000000002]
["2024-03-21T14:10:00","2024-03-21T14:15:00",313.00643760000003,71.844699599999998]
["2024-03-21T14:15:00","2024-03-21T14:20:00",317.46462600000001,72.297968400000002]
["2024-03-21T14:20:00","2024-03-21T14:25:00",320.60798399999999,69.982606799999999]
["2024-03-21T14:25:00","2024-03-21T14:30:00",321.1744668,69.759867600000007]
["2024-03-21T14:30:00","2024-03-21T14:35:00",321.40515599999998,67.798990799999999]
["2024-03-21T14:35:00","2024-03-21T14:40:00",329.94602520000001,68.796024000000003]
["2024-03-21T14:40:00","2024-03-21T14:45:00",334.22210039999999,68.461404000000002]
["2024-03-21T14:45:00","2024-03-21T14:50:00",337.87476479999998,66.818121599999998]
["2024-03-21T14:50:00","2024-03-21T14:55:00",343.1020656,66.222881999999998]
["2024-03-21T14:55:00","2024-03-21T15:00:00",348.80229600000001,65.250584399999994]
["2024-03-21T15:00:00","2024-03-21T15:05:00",354.99311760000001,64.228400399999998]
["2024-03-21T15:05:00","2024-03-21T15:10:00",356.48817120000001,63.712029600000001]
["2024-03-21T15:10:00","2024-03-21T15:15:00",361.5567264,63.412195199999999]
["2024-03-21T15:15:00","2024-03-21T15:20:00",366.38901120000003,62.627028000000003]
["2024-03-21T15:20:00","2024-03-21T15:25:00",371.23664280000003,61.053831600000002]
["2024-03-21T15:25:00","2024-03-21T15:30:00",376.15801199999999,61.272866399999998]
["2024-03-21T15:30:00","2024-03-21T15:35:00",378.56633879999998,59.096743199999999]
["2024-03-21T15:35:00","2024-03-21T15:40:00",384.83064000000002,58.461568800000002]
["2024-03-21T15:40:00","2024-03-21T15:45:00",391.92551759999998,57.170227199999999]
["2024-03-21T15:45:00","2024-03-21T15:50:00",393.58091519999999,54.838470000000001]
["2024-03-21T15:50:00","2024-03-21T15:55:00",398.47237919999998,53.826517199999998]
["2024-03-21T15:55:00","2024-03-21T16:00:00",407.0919624,54.4673892]
["2024-03-21T16:00:00","2024-03-21T16:05:00",409.99435080000001,52.227855599999998]
["2024-03-21T16:05:00","2024-03-21T16:10:00",415.33754520000002,49.864335599999997]
["2024-03-21T16:10:00","2024-03-21T16:15:00",419.02339080000002,49.540220400000003]
["2024-03-21T16:15:00","2024-03-21T16:20:00",429.03281399999997,50.433354000000001]
["2024-03-21T16:20:00","2024-03-21T16:25:00",431.67107040000002,47.897511600000001]
["2024-03-21T16:25:00","2024-03-21T16:30:00",439.93479120000001,50.005070400000001]
["2024-03-21T16:30:00","2024-03-21T16:35:00",446.57476559999998,49.1079972]
["2024-03-21T16:35:00","2024-03-21T16:40:00",457.09699440000003,50.774424000000003]
["2024-03-21T16:40:00","2024-03-21T16:45:00",462.70787039999999,50.205641999999997]
["2024-03-21T16:45:00","2024-03-21T16:50:00",470.24213400000002,49.2519384]
["2024-03-21T16:50:00","2024-03-21T16:55:00",476.00344560000002,47.974522800000003]
["2024-03-21T16:55:00","2024-03-21T17:00:00",481.46886599999999,49.547497200000002]
["2024-03-21T17:00:00","2024-03-21T17:05:00",486.41548920000002,45.988391999999997]
["2024-03-21T17:05:00","2024-03-21T17:10:00",490.21556040000002,43.643332800000003]
["2024-03-21T17:10:00","2024-03-21T17:15:00",496.46901120000001,42.550741199999997]
["2024-03-21T17:15:00","2024-03-21T17:20:00",505.17919920000003,41.593869599999998]
["2024-03-21T17:20:00","2024-03-21T17:25:00",509.23277639999998,41.300445600000003]
["2024-03-21T17:25:00","2024-03-21T17:30:00",515.97171000000003,41.062485600000002]
["2024-03-21T17:30:00","2024-03-21T17:35:00",519.65270039999996,40.217306399999998]
["2024-03-21T17:35:00","2024-03-21T17:40:00",525.2844096,39.859907999999997]
["2024-03-21T17:40:00","2024-03-21T17:45:00",530.58999359999996,38.782409999999999]
["2024-03-21T17:45:00","2024-03-21T17:50:00",533.74652879999996,37.122355200000001]
["2024-03-21T17:50:00","2024-03-21T17:55:00",537.87220319999994,37.181690400000001]
["2024-03-21T17:55:00","2024-03-21T18:00:00",541.43130359999998,36.275479199999999]
["2024-03-21T18:00:00","2024-03-21T18:05:00",542.34228719999999,35.397891600000001]
["2024-03-21T18:05:00","2024-03-21T18:10:00",545.16722760000005,35.329265999999997]
["2024-03-21T18:10:00","2024-03-21T18:15:00",542.96205120000002,34.265026800000001]
["2024-03-21T18:15:00","2024-03-21T18:20:00",549.31950959999995,34.060316399999998]
["2024-03-21T18:20:00","2024-03-21T18:25:00",551.13781080000001,32.449609199999998]
["2024-03-21T18:25:00","2024-03-21T18:30:00",554.66371919999995,32.943194400000003]
["2024-03-21T18:30:00","2024-03-21T18:35:00",553.17340679999995,31.618970399999998]
["2024-03-21T18:35:00","2024-03-21T18:40:00",549.52983840000002,30.287653200000001]
["2024-03-21T18:40:00","2024-03-21T18:45:00",549.88345200000003,30.333691200000001]
["2024-03-21T18:45:00","2024-03-21T18:50:00",550.68719039999996,29.854092000000001]
["2024-03-21T18:50:00","2024-03-21T18:55:00",550.50455999999997,30.422453999999998]
["2024-03-21T18:55:00","2024-03-21T19:00:00",551.99595839999995,31.437880799999999]
["2024-03-21T19:00:00","2024-03-21T19:05:00",552.35088840000003,30.700610399999999]
["2024-03-21T19:05:00","2024-03-21T19:10:00",554.76702479999994,30.3757056]
["2024-03-21T19:10:00","2024-03-21T19:15:00",552.3131952,29.313703199999999]
["2024-03-21T19:15:00","2024-03-21T19:20:00",551.41604040000004,29.676573600000001]
["2024-03-21T19:20:00","2024-03-21T19:25:00",551.48494200000005,29.48283]
["2024-03-21T19:25:00","2024-03-21T19:30:00",547.5819444,27.375641999999999]
["2024-03-21T19:30:00","2024-03-21T19:35:00",547.37273040000002,27.192493200000001]
["2024-03-21T19:35:00","2024-03-21T19:40:00",544.12050480000005,26.654320800000001]
["2024-03-21T19:40:00","2024-03-21T19:45:00",541.32296880000001,26.242775999999999]
["2024-03-21T19:45:00","2024-03-21T19:50:00",541.11362640000004,25.9703412]
["2024-03-21T19:50:00","2024-03-21T19:55:00",538.65370080000002,25.27422]
["2024-03-21T19:55:00","2024-03-21T20:00:00",535.01231399999995,24.1088652]
["2024-03-21T20:00:00","2024-03-21T20:05:00",531.7603464,22.8203532]
["2024-03-21T20:05:00","2024-03-21T20:10:00",529.23537480000005,21.968103599999999]
["2024-03-21T20:10:00","2024-03-21T20:15:00",526.10665559999995,20.778576000000001]
["2024-03-21T20:15:00","2024-03-21T20:20:00",522.76814400000001,20.135239200000001]
["2024-03-21T20:20:00","2024-03-21T20:25:00",518.33721960000003,18.868411200000001]
["2024-03-21T20:25:00","2024-03-21T20:30:00",517.08948359999999,18.5569296]
["2024-03-21T20:30:00","2024-03-21T20:35:00",510.45874079999999,16.9268964]
["2024-03-21T20:35:00","2024-03-21T20:40:00",506.89456319999999,15.897102]
["2024-03-21T20:40:00","2024-03-21T20:45:00",506.4172332,15.489952799999999]
["2024-03-21T20:45:00","2024-03-21T20:50:00",503.74572840000002,15.2554476]
["2024-03-21T20:50:00","2024-03-21T20:55:00",498.90693479999999,14.1184116]
["2024-03-21T20:55:00","2024-03-21T21:00:00",495.55438199999998,12.234814800000001]
["2024-03-21T21:00:00","2024-03-21T21:05:00",489.44148960000001,11.087695200000001]
["2024-03-21T21:05:00","2024-03-21T21:10:00",486.48129239999997,10.463133600000001]
["2024-03-21T21:10:00","2024-03-21T21:15:00",482.54275799999999,9.2625335999999994]
["2024-03-21T21:15:00","2024-03-21T21:20:00",480.08278200000001,8.8039343999999993]
["2024-03-21T21:20:00","2024-03-21T21:25:00",475.66258920000001,8.3753004000000004]
["2024-03-21T21:25:00","2024-03-21T21:30:00",473.42818560000001,7.4292360000000004]
["2024-03-21T21:30:00","2024-03-21T21:35:00",469.52651520000001,6.8580059999999996]
["2024-03-21T21:35:00","2024-03-21T21:40:00",466.63949400000001,6.2628599999999999]
["2024-03-21T21:40:00","2024-03-21T21:45:00",463.69862280000001,4.4865551999999997]
["2024-03-21T21:45:00","2024-03-21T21:50:00",458.48469360000001,2.1414683999999999]
["2024-03-21T21:50:00","2024-03-21T21:55:00",454.01650560000002,1.9567871999999999]
["2024-03-21T21:55:00","2024-03-21T22:00:00",451.36975919999998,0.91844760000000003]
["2024-03-21T22:00:00","2024-03-21T22:05:00",447.43577040000002,0.47299439999999998]
["2024-03-21T22:05:00","2024-03-21T22:10:00",443.2703472,-1.4081748000000001]
["2024-03-21T22:10:00","2024-03-21T22:15:00",442.0513416,-0.98335680000000003]
["2024-03-21T22:15:00","2024-03-21T22:20:00",440.17183560000001,-1.2408935999999999]
["2024-03-21T22:20:00","2024-03-21T22:25:00",437.08905240000001,-1.053042]
["2024-03-21T22:25:00","2024-03-21T22:30:00",435.42539040000003,-1.5015996]
["2024-03-21T22:30:00","2024-03-21T22:35:00",431.70777120000002,-2.7180059999999999]
["2024-03-21T22:35:00","2024-03-21T22:40:00",428.94140759999999,-3.4181471999999999]
["2024-03-21T22:40:00","2024-03-21T22:45:00",426.33179039999999,-4.2041219999999999]
["2024-03-21T22:45:00","2024-03-21T22:50:00",423.37193159999998,-4.9509179999999997]
["2024-03-21T22:50:00","2024-03-21T22:55:00",419.56521359999999,-6.0025548000000004]
["2024-03-21T22:55:00","2024-03-21T23:00:00",416.86346639999999,-7.6265064000000002]
["2024-03-21T23:00:00","2024-03-21T23:05:00",422.69435399999998,-6.3259824]
["2024-03-21T23:05:00","2024-03-21T23:10:00",432.58759320000001,-5.6368248000000003]
["2024-03-21T23:10:00","2024-03-21T23:15:00",436.3948944,-5.200062]
["2024-03-21T23:15:00","2024-03-21T23:20:00",432.40376040000001,-6.2839739999999997]
["2024-03-21T23:20:00","2024-03-21T23:25:00",430.05638879999998,-7.0054487999999999]
["2024-03-21T23:25:00","2024-03-21T23:30:00",425.45385479999999,-7.4768952000000004]
["2024-03-21T23:30:00","2024-03-21T23:35:00",420.68095440000002,-7.8716916000000001]
["2024-03-21T23:35:00","2024-03-21T23:40:00",418.58069160000002,-8.3130875999999994]
["2024-03-21T23:40:00","2024-03-21T23:45:00",415.80348479999998,-9.1522824000000007]
["2024-03-21T23:45:00","2024-03-21T23:50:00",411.88116960000002,-9.4367903999999996]
["2024-03-21T23:50:00","2024-03-21T23:55:00",407.85693839999999,-10.1455644]
["2024-03-21T23:55:00",45373,403.5800112,-11.379616800000001]
[45373,"2024-03-22T00:05:00",400.27254479999999,-11.793434400000001]
["2024-03-22T00:05:00","2024-03-22T00:10:00",397.3069236,-13.2417984]
["2024-03-22T00:10:00","2024-03-22T00:15:00",395.47092240000001,-13.498473600000001]
["2024-03-22T00:15:00","2024-03-22T00:20:00",393.41275080000003,-13.859398799999999]
["2024-03-22T00:20:00","2024-03-22T00:25:00",390.29522159999999,-14.7102036]
["2024-03-22T00:25:00","2024-03-22T00:30:00",388.23989999999998,-14.9077392]
["2024-03-22T00:30:00","2024-03-22T00:35:00",385.85131439999998,-15.6210612]
["2024-03-22T00:35:00","2024-03-22T00:40:00",383.63972039999999,-16.105750799999999]
["2024-03-22T00:40:00","2024-03-22T00:45:00",381.79842000000002,-16.320215999999999]
["2024-03-22T00:45:00","2024-03-22T00:50:00",379.66243200000002,-16.52826]
["2024-03-22T00:50:00","2024-03-22T00:55:00",377.69135519999998,-17.705743200000001]
["2024-03-22T00:55:00","2024-03-22T01:00:00",374.92865039999998,-18.9614844]
["2024-03-22T01:00:00","2024-03-22T01:05:00",368.82300839999999,-19.127463599999999]
["2024-03-22T01:05:00","2024-03-22T01:10:00",372.89911799999999,-18.584170799999999]
["2024-03-22T01:10:00","2024-03-22T01:15:00",372.20874959999998,-19.559396400000001]
["2024-03-22T01:15:00","2024-03-22T01:20:00",371.8747176,-18.648243600000001]
["2024-03-22T01:20:00","2024-03-22T01:25:00",369.40284359999998,-19.861091999999999]
["2024-03-22T01:25:00","2024-03-22T01:30:00",368.65214639999999,-19.565728799999999]
["2024-03-22T01:30:00","2024-03-22T01:35:00",367.91069640000001,-19.510885200000001]
["2024-03-22T01:35:00","2024-03-22T01:40:00",367.3714008,-19.789360800000001]
["2024-03-22T01:40:00","2024-03-22T01:45:00",366.86205480000001,-20.024334]
["2024-03-22T01:45:00","2024-03-22T01:50:00",366.32349840000001,-19.6170528]
["2024-03-22T01:50:00","2024-03-22T01:55:00",365.57903040000002,-19.7704524]
["2024-03-22T01:55:00","2024-03-22T02:00:00",364.56573600000002,-20.5327524]
["2024-03-22T02:00:00","2024-03-22T02:05:00",365.28865919999998,-20.4267024]
["2024-03-22T02:05:00","2024-03-22T02:10:00",364.6298496,-20.716222800000001]
["2024-03-22T02:10:00","2024-03-22T02:15:00",364.84427160000001,-20.724831600000002]
["2024-03-22T02:15:00","2024-03-22T02:20:00",365.31458520000001,-20.121007200000001]
["2024-03-22T02:20:00","2024-03-22T02:25:00",365.56007160000001,-20.126372400000001]
["2024-03-22T02:25:00","2024-03-22T02:30:00",365.13794639999998,-19.984368]
["2024-03-22T02:30:00","2024-03-22T02:35:00",365.10404160000002,-19.604032799999999]
["2024-03-22T02:35:00","2024-03-22T02:40:00",364.76123760000002,-20.215046399999999]
["2024-03-22T02:40:00","2024-03-22T02:45:00",365.52930359999999,-19.920624]
["2024-03-22T02:45:00","2024-03-22T02:50:00",365.0697108,-20.682596400000001]
["2024-03-22T02:50:00","2024-03-22T02:55:00",366.33281640000001,-20.545532399999999]
["2024-03-22T02:55:00","2024-03-22T03:00:00",366.20574240000002,-20.229209999999998]
["2024-03-22T03:00:00","2024-03-22T03:05:00",367.16785679999998,-20.352982799999999]
["2024-03-22T03:05:00","2024-03-22T03:10:00",368.93829360000001,-19.5287112]
["2024-03-22T03:10:00","2024-03-22T03:15:00",368.29728,-19.824576]
["2024-03-22T03:15:00","2024-03-22T03:20:00",369.98309519999998,-19.574739600000001]
["2024-03-22T03:20:00","2024-03-22T03:25:00",371.56428599999998,-19.821127199999999]
["2024-03-22T03:25:00","2024-03-22T03:30:00",370.65268680000003,-20.286475200000002]
["2024-03-22T03:30:00","2024-03-22T03:35:00",374.67646200000001,-19.282918800000001]
["2024-03-22T03:35:00","2024-03-22T03:40:00",376.6237812,-18.543806400000001]
["2024-03-22T03:40:00","2024-03-22T03:45:00",377.06659919999998,-19.144506]
["2024-03-22T03:45:00","2024-03-22T03:50:00",377.56266360000001,-18.942018000000001]
["2024-03-22T03:50:00","2024-03-22T03:55:00",381.5670576,-18.711558]
["2024-03-22T03:55:00","2024-03-22T04:00:00",382.9461336,-18.488475600000001]
["2024-03-22T04:00:00","2024-03-22T04:05:00",387.96005280000003,-16.915938000000001]
["2024-03-22T04:05:00","2024-03-22T04:10:00",392.69801519999999,-15.427676399999999]
["2024-03-22T04:10:00","2024-03-22T04:15:00",396.933312,-14.351722799999999]
["2024-03-22T04:15:00","2024-03-22T04:20:00",399.07357560000003,-13.412835599999999]
["2024-03-22T04:20:00","2024-03-22T04:25:00",402.71478960000002,-12.8543196]
["2024-03-22T04:25:00","2024-03-22T04:30:00",405.3637152,-12.0321528]
["2024-03-22T04:30:00","2024-03-22T04:35:00",408.01275240000001,-10.7865948]
["2024-03-22T04:35:00","2024-03-22T04:40:00",414.51048120000002,-7.7374631999999997]
["2024-03-22T04:40:00","2024-03-22T04:45:00",416.49372720000002,-7.3713119999999996]
["2024-03-22T04:45:00","2024-03-22T04:50:00",417.62370120000003,-6.4482048000000001]
["2024-03-22T04:50:00","2024-03-22T04:55:00",425.34465719999997,-3.3666299999999998]
["2024-03-22T04:55:00","2024-03-22T05:00:00",431.4769632,-1.4899104000000001]
["2024-03-22T05:00:00","2024-03-22T05:05:00",441.88241879999998,2.2921140000000002]
["2024-03-22T05:05:00","2024-03-22T05:10:00",450.16431599999999,6.5947464]
["2024-03-22T05:10:00","2024-03-22T05:15:00",456.07699200000002,8.0284452000000002]
["2024-03-22T05:15:00","2024-03-22T05:20:00",462.04818119999999,9.3744876000000001]
["2024-03-22T05:20:00","2024-03-22T05:25:00",466.98013079999998,11.5266264]
["2024-03-22T05:25:00","2024-03-22T05:30:00",471.08850239999998,13.426910400000001]
["2024-03-22T05:30:00","2024-03-22T05:35:00",476.28445319999997,15.504785999999999]
["2024-03-22T05:35:00","2024-03-22T05:40:00",483.72344520000001,17.900222400000001]
["2024-03-22T05:40:00","2024-03-22T05:45:00",489.01960559999998,20.2950312]
["2024-03-22T05:45:00","2024-03-22T05:50:00",494.80517759999998,22.544969999999999]
["2024-03-22T05:50:00","2024-03-22T05:55:00",501.22253160000002,23.998054799999998]
["2024-03-22T05:55:00","2024-03-22T06:00:00",510.74107800000002,28.299717600000001]
["2024-03-22T06:00:00","2024-03-22T06:05:00",521.86751040000001,32.696409600000003]
["2024-03-22T06:05:00","2024-03-22T06:10:00",530.41173000000003,38.467002000000001]
["2024-03-22T06:10:00","2024-03-22T06:15:00",534.23504879999996,38.477812800000002]
["2024-03-22T06:15:00","2024-03-22T06:20:00",539.88294480000002,39.834774000000003]
["2024-03-22T06:20:00","2024-03-22T06:25:00",541.79269079999995,39.598176000000002]
["2024-03-22T06:25:00","2024-03-22T06:30:00",546.30485999999996,42.2266008]
["2024-03-22T06:30:00","2024-03-22T06:35:00",550.19276160000004,44.364868800000004]
["2024-03-22T06:35:00","2024-03-22T06:40:00",553.66040999999996,44.299171200000004]
["2024-03-22T06:40:00","2024-03-22T06:45:00",555.006306,45.397998000000001]
["2024-03-22T06:45:00","2024-03-22T06:50:00",555.70895159999998,45.6266544]
["2024-03-22T06:50:00","2024-03-22T06:55:00",556.10632559999999,47.940773999999998]
["2024-03-22T06:55:00","2024-03-22T07:00:00",557.15830200000005,50.239645199999998]
["2024-03-22T07:00:00","2024-03-22T07:05:00",555.221766,51.699550799999997]
["2024-03-22T07:05:00","2024-03-22T07:10:00",552.51927839999996,52.3650564]
["2024-03-22T07:10:00","2024-03-22T07:15:00",547.26112680000006,52.8058944]
["2024-03-22T07:15:00","2024-03-22T07:20:00",548.73523320000004,56.816991600000001]
["2024-03-22T07:20:00","2024-03-22T07:25:00",543.10960799999998,55.4588064]
["2024-03-22T07:25:00","2024-03-22T07:30:00",540.3179556,56.399001599999998]
["2024-03-22T07:30:00","2024-03-22T07:35:00",534.94335120000005,58.615555200000003]
["2024-03-22T07:35:00","2024-03-22T07:40:00",528.04079400000001,57.9036708]
["2024-03-22T07:40:00","2024-03-22T07:45:00",519.43197239999995,54.954042000000001]
["2024-03-22T07:45:00","2024-03-22T07:50:00",513.77746560000003,54.907580400000001]
["2024-03-22T07:50:00","2024-03-22T07:55:00",509.61633,56.760524400000001]
["2024-03-22T07:55:00","2024-03-22T08:00:00",502.07564400000001,56.453567999999997]
["2024-03-22T08:00:00","2024-03-22T08:05:00",496.19340360000001,56.056745999999997]
["2024-03-22T08:05:00","2024-03-22T08:10:00",493.64092199999999,55.467904799999999]
["2024-03-22T08:10:00","2024-03-22T08:15:00",486.91113480000001,54.143549999999998]
["2024-03-22T08:15:00","2024-03-22T08:20:00",484.23169919999998,56.404423199999997]
["2024-03-22T08:20:00","2024-03-22T08:25:00",477.41200800000001,54.8532096]
["2024-03-22T08:25:00","2024-03-22T08:30:00",470.63220000000001,51.840066]
["2024-03-22T08:30:00","2024-03-22T08:35:00",462.06974760000003,51.653415600000002]
["2024-03-22T08:35:00","2024-03-22T08:40:00",456.230346,52.817869199999997]
["2024-03-22T08:40:00","2024-03-22T08:45:00",453.95653440000001,52.918406400000002]
["2024-03-22T08:45:00","2024-03-22T08:50:00",447.40922519999998,52.934387999999998]
["2024-03-22T08:50:00","2024-03-22T08:55:00",441.57282240000001,56.920008000000003]
["2024-03-22T08:55:00","2024-03-22T09:00:00",436.22294879999998,57.783897600000003]
["2024-03-22T09:00:00","2024-03-22T09:05:00",428.6974596,57.434604]
["2024-03-22T09:05:00","2024-03-22T09:10:00",424.88294999999999,56.894414400000002]
["2024-03-22T09:10:00","2024-03-22T09:15:00",416.60699039999997,56.808879599999997]
["2024-03-22T09:15:00","2024-03-22T09:20:00",412.5105408,59.1027372]
["2024-03-22T09:20:00","2024-03-22T09:25:00",407.90311320000001,60.459454800000003]
["2024-03-22T09:25:00","2024-03-22T09:30:00",404.60727960000003,62.854348799999997]
["2024-03-22T09:30:00","2024-03-22T09:35:00",397.31396160000003,63.934475999999997]
["2024-03-22T09:35:00","2024-03-22T09:40:00",394.27522800000003,65.531711999999999]
["2024-03-22T09:40:00","2024-03-22T09:45:00",387.69131279999999,65.844926400000006]
["2024-03-22T09:45:00","2024-03-22T09:50:00",383.77728000000002,66.981499200000002]
["2024-03-22T09:50:00","2024-03-22T09:55:00",377.06773440000001,66.862910400000004]
["2024-03-22T09:55:00","2024-03-22T10:00:00",376.60978440000002,67.738910399999995]
["2024-03-22T10:00:00","2024-03-22T10:05:00",372.80081519999999,68.428538399999994]
["2024-03-22T10:05:00","2024-03-22T10:10:00",362.99636520000001,62.227279199999998]
["2024-03-22T10:10:00","2024-03-22T10:15:00",359.69289839999999,62.912813999999997]
["2024-03-22T10:15:00","2024-03-22T10:20:00",353.276094,59.463393600000003]
["2024-03-22T10:20:00","2024-03-22T10:25:00",349.53423720000001,58.7045496]
["2024-03-22T10:25:00","2024-03-22T10:30:00",343.744056,59.016376800000003]
["2024-03-22T10:30:00","2024-03-22T10:35:00",339.82648920000003,59.442806400000002]
["2024-03-22T10:35:00","2024-03-22T10:40:00",340.70054040000002,61.215973200000001]
["2024-03-22T10:40:00","2024-03-22T10:45:00",341.46276840000002,62.539679999999997]
["2024-03-22T10:45:00","2024-03-22T10:50:00",335.76371999999998,62.041917599999998]
["2024-03-22T10:50:00","2024-03-22T10:55:00",329.09496480000001,61.186988399999997]
["2024-03-22T10:55:00","2024-03-22T11:00:00",327.48186720000001,61.244293200000001]
["2024-03-22T11:00:00","2024-03-22T11:05:00",324.23173439999999,61.158907200000002]
["2024-03-22T11:05:00","2024-03-22T11:10:00",322.14580319999999,61.535485199999997]
["2024-03-22T11:10:00","2024-03-22T11:15:00",318.6015372,61.054648800000002]
["2024-03-22T11:15:00","2024-03-22T11:20:00",319.6698432,61.943613599999999]
["2024-03-22T11:20:00","2024-03-22T11:25:00",318.28267440000002,61.830142799999997]
["2024-03-22T11:25:00","2024-03-22T11:30:00",316.38656400000002,61.328331599999999]
["2024-03-22T11:30:00","2024-03-22T11:35:00",314.4712644,61.106250000000003]
["2024-03-22T11:35:00","2024-03-22T11:40:00",319.74161759999998,62.666749199999998]
["2024-03-22T11:40:00","2024-03-22T11:45:00",321.71994599999999,63.863037599999998]
["2024-03-22T11:45:00","2024-03-22T11:50:00",329.46351959999998,64.699061999999998]
["2024-03-22T11:50:00","2024-03-22T11:55:00",329.85985199999999,63.987680400000002]
["2024-03-22T11:55:00","2024-03-22T12:00:00",334.09615079999998,64.025680800000004]
["2024-03-22T12:00:00","2024-03-22T12:05:00",331.74101400000001,63.071624399999997]
["2024-03-22T12:05:00","2024-03-22T12:10:00",333.00768360000001,60.3891864]
["2024-03-22T12:10:00","2024-03-22T12:15:00",335.82051000000001,61.6913652]
["2024-03-22T12:15:00","2024-03-22T12:20:00",340.450872,60.951290399999998]
["2024-03-22T12:20:00","2024-03-22T12:25:00",336.87352440000001,59.831445600000002]
["2024-03-22T12:25:00","2024-03-22T12:30:00",330.14274239999997,60.003188399999999]
["2024-03-22T12:30:00","2024-03-22T12:35:00",322.32827639999999,60.953877599999998]
["2024-03-22T12:35:00","2024-03-22T12:40:00",318.14561639999999,61.180532399999997]
["2024-03-22T12:40:00","2024-03-22T12:45:00",314.67827999999997,61.334211600000003]
["2024-03-22T12:45:00","2024-03-22T12:50:00",314.19431639999999,62.345600400000002]
["2024-03-22T12:50:00","2024-03-22T12:55:00",312.52341719999998,62.101000800000001]
["2024-03-22T12:55:00","2024-03-22T13:00:00",311.39806199999998,60.439225200000003]
["2024-03-22T13:00:00","2024-03-22T13:05:00",304.94234399999999,60.260552400000002]
["2024-03-22T13:05:00","2024-03-22T13:10:00",308.7887652,60.465193200000002]
["2024-03-22T13:10:00","2024-03-22T13:15:00",308.97213360000001,62.390271599999998]
["2024-03-22T13:15:00","2024-03-22T13:20:00",311.39810879999999,62.311050000000002]
["2024-03-22T13:20:00","2024-03-22T13:25:00",306.87133799999998,61.4765844]
["2024-03-22T13:25:00","2024-03-22T13:30:00",301.60657200000003,61.2323412]
["2024-03-22T13:30:00","2024-03-22T13:35:00",300.5717712,62.277363600000001]
["2024-03-22T13:35:00","2024-03-22T13:40:00",302.01899040000001,63.757111199999997]
["2024-03-22T13:40:00","2024-03-22T13:45:00",307.21498079999998,65.5684428]
["2024-03-22T13:45:00","2024-03-22T13:50:00",306.44595479999998,64.573251600000006]
["2024-03-22T13:50:00","2024-03-22T13:55:00",304.59944999999999,63.485171999999999]
["2024-03-22T13:55:00","2024-03-22T14:00:00",306.74316599999997,63.5212608]
["2024-03-22T14:00:00","2024-03-22T14:05:00",313.02276119999999,62.374832400000003]
["2024-03-22T14:05:00","2024-03-22T14:10:00",310.98503040000003,61.084488]
["2024-03-22T14:10:00","2024-03-22T14:15:00",305.75942880000002,60.246842399999998]
["2024-03-22T14:15:00","2024-03-22T14:20:00",305.60061480000002,59.738281200000003]
["2024-03-22T14:20:00","2024-03-22T14:25:00",310.3649532,59.638347600000003]
["2024-03-22T14:25:00","2024-03-22T14:30:00",314.77450320000003,58.739620799999997]
["2024-03-22T14:30:00","2024-03-22T14:35:00",315.95419199999998,56.745314399999998]
["2024-03-22T14:35:00","2024-03-22T14:40:00",323.23022880000002,56.517489599999998]
["2024-03-22T14:40:00","2024-03-22T14:45:00",328.03160159999999,57.593839199999998]
["2024-03-22T14:45:00","2024-03-22T14:50:00",331.62589079999998,56.163108000000001]
["2024-03-22T14:50:00","2024-03-22T14:55:00",332.35610279999997,54.887907599999998]
["2024-03-22T14:55:00","2024-03-22T15:00:00",338.04737399999999,54.721754400000002]
["2024-03-22T15:00:00","2024-03-22T15:05:00",342.28084319999999,52.392326400000002]
["2024-03-22T15:05:00","2024-03-22T15:10:00",346.94901479999999,51.225213599999996]
["2024-03-22T15:10:00","2024-03-22T15:15:00",348.02777159999999,50.474607599999999]
["2024-03-22T15:15:00","2024-03-22T15:20:00",354.94308239999998,49.772306399999998]
["2024-03-22T15:20:00","2024-03-22T15:25:00",359.34931440000003,47.747055600000003]
["2024-03-22T15:25:00","2024-03-22T15:30:00",363.78068999999999,46.807525200000001]
["2024-03-22T15:30:00","2024-03-22T15:35:00",368.90273760000002,45.953509199999999]
["2024-03-22T15:35:00","2024-03-22T15:40:00",378.32312999999999,45.956163599999996]
["2024-03-22T15:40:00","2024-03-22T15:45:00",383.73367200000001,45.077998800000003]
["2024-03-22T15:45:00","2024-03-22T15:50:00",389.00483279999997,45.276910800000003]
["2024-03-22T15:50:00","2024-03-22T15:55:00",393.20814000000001,45.997963200000001]
["2024-03-22T15:55:00","2024-03-22T16:00:00",399.30319919999999,44.359554000000003]
["2024-03-22T16:00:00","2024-03-22T16:05:00",407.11033320000001,44.226972000000004]
["2024-03-22T16:05:00","2024-03-22T16:10:00",413.35121279999998,47.299132800000002]
["2024-03-22T16:10:00","2024-03-22T16:15:00",419.35319040000002,49.851909599999999]
["2024-03-22T16:15:00","2024-03-22T16:20:00",426.1467912,47.665030799999997]
["2024-03-22T16:20:00","2024-03-22T16:25:00",428.97149639999998,45.503557200000003]
["2024-03-22T16:25:00","2024-03-22T16:30:00",435.37242959999998,44.032229999999998]
["2024-03-22T16:30:00","2024-03-22T16:35:00",439.65569520000003,42.339221999999999]
["2024-03-22T16:35:00","2024-03-22T16:40:00",446.3350332,41.670682800000002]
["2024-03-22T16:40:00","2024-03-22T16:45:00",452.76905160000001,40.630290000000002]
["2024-03-22T16:45:00","2024-03-22T16:50:00",461.60296319999998,40.9303776]
["2024-03-22T16:50:00","2024-03-22T16:55:00",465.2125044,39.623296799999999]
["2024-03-22T16:55:00","2024-03-22T17:00:00",468.28193279999999,37.2742632]
["2024-03-22T17:00:00","2024-03-22T17:05:00",471.27222119999999,35.968563600000003]
["2024-03-22T17:05:00","2024-03-22T17:10:00",474.19560960000001,33.350913599999998]
["2024-03-22T17:10:00","2024-03-22T17:15:00",479.93249159999999,31.227015600000001]
["2024-03-22T17:15:00","2024-03-22T17:20:00",485.1677292,28.935783600000001]
["2024-03-22T17:20:00","2024-03-22T17:25:00",489.35376120000001,27.333390000000001]
["2024-03-22T17:25:00","2024-03-22T17:30:00",493.68020639999997,28.0330896]
["2024-03-22T17:30:00","2024-03-22T17:35:00",499.85061359999997,27.786823200000001]
["2024-03-22T17:35:00","2024-03-22T17:40:00",506.24729400000001,27.799183200000002]
["2024-03-22T17:40:00","2024-03-22T17:45:00",511.23617639999998,27.288965999999999]
["2024-03-22T17:45:00","2024-03-22T17:50:00",516.85498800000005,27.298725600000001]
["2024-03-22T17:50:00","2024-03-22T17:55:00",518.58092399999998,26.967019199999999]
["2024-03-22T17:55:00","2024-03-22T18:00:00",522.44141520000005,25.519041600000001]
["2024-03-22T18:00:00","2024-03-22T18:05:00",524.49342000000001,24.602018399999999]
["2024-03-22T18:05:00","2024-03-22T18:10:00",526.14514919999999,24.353045999999999]
["2024-03-22T18:10:00","2024-03-22T18:15:00",526.29336599999999,24.5289024]
["2024-03-22T18:15:00","2024-03-22T18:20:00",530.62703280000005,24.303338400000001]
["2024-03-22T18:20:00","2024-03-22T18:25:00",529.82597399999997,22.5331644]
["2024-03-22T18:25:00","2024-03-22T18:30:00",530.57750999999996,21.001495200000001]
["2024-03-22T18:30:00","2024-03-22T18:35:00",529.0522512,20.705895600000002]
["2024-03-22T18:35:00","2024-03-22T18:40:00",528.15283439999996,19.679581200000001]
["2024-03-22T18:40:00","2024-03-22T18:45:00",529.82817599999998,19.358892000000001]
["2024-03-22T18:45:00","2024-03-22T18:50:00",531.99931079999999,19.963731599999999]
["2024-03-22T18:50:00","2024-03-22T18:55:00",530.32639800000004,19.828957200000001]
["2024-03-22T18:55:00","2024-03-22T19:00:00",530.42768039999999,20.293056]
["2024-03-22T19:00:00","2024-03-22T19:05:00",531.82876920000001,19.117266000000001]
["2024-03-22T19:05:00","2024-03-22T19:10:00",529.18877399999997,17.7616488]
["2024-03-22T19:10:00","2024-03-22T19:15:00",527.56657080000002,17.875067999999999]
["2024-03-22T19:15:00","2024-03-22T19:20:00",528.13033440000004,18.137568000000002]
["2024-03-22T19:20:00","2024-03-22T19:25:00",525.73255919999997,16.997354399999999]
["2024-03-22T19:25:00","2024-03-22T19:30:00",525.60946799999999,17.1781176]
["2024-03-22T19:30:00","2024-03-22T19:35:00",522.34078920000002,15.900255599999999]
["2024-03-22T19:35:00","2024-03-22T19:40:00",519.31166399999995,14.7038256]
["2024-03-22T19:40:00","2024-03-22T19:45:00",517.57763039999998,14.649194400000001]
["2024-03-22T19:45:00","2024-03-22T19:50:00",516.61421759999996,14.022762]
["2024-03-22T19:50:00","2024-03-22T19:55:00",512.07570239999995,13.3963392]
["2024-03-22T19:55:00","2024-03-22T20:00:00",509.5204956,12.170683199999999]
["2024-03-22T20:00:00","2024-03-22T20:05:00",506.15323799999999,11.488004399999999]
["2024-03-22T20:05:00","2024-03-22T20:10:00",502.60669799999999,10.007676]
["2024-03-22T20:10:00","2024-03-22T20:15:00",499.19540160000003,8.8527191999999992]
["2024-03-22T20:15:00","2024-03-22T20:20:00",494.34467760000001,8.2208652000000004]
["2024-03-22T20:20:00","2024-03-22T20:25:00",491.23228920000003,6.6128723999999997]
["2024-03-22T20:25:00","2024-03-22T20:30:00",489.33396720000002,5.8853879999999998]
["2024-03-22T20:30:00","2024-03-22T20:35:00",485.81283719999999,4.4299416000000003]
["2024-03-22T20:35:00","2024-03-22T20:40:00",483.19044000000002,4.5319440000000002]
["2024-03-22T20:40:00","2024-03-22T20:45:00",480.78833759999998,3.8614223999999999]
["2024-03-22T20:45:00","2024-03-22T20:50:00",477.22878600000001,2.2385448000000001]
["2024-03-22T20:50:00","2024-03-22T20:55:00",474.8274816,2.2061928000000002]
["2024-03-22T20:55:00","2024-03-22T21:00:00",472.01487839999999,1.4209464000000001]
["2024-03-22T21:00:00","2024-03-22T21:05:00",469.82464800000002,1.9715807999999999]
["2024-03-22T21:05:00","2024-03-22T21:10:00",463.98350879999998,-0.93693479999999996]
["2024-03-22T21:10:00","2024-03-22T21:15:00",463.258644,-0.60851880000000003]
["2024-03-22T21:15:00","2024-03-22T21:20:00",460.3157832,-1.7676647999999999]
["2024-03-22T21:20:00","2024-03-22T21:25:00",457.43198760000001,-2.7348324000000002]
["2024-03-22T21:25:00","2024-03-22T21:30:00",454.17426119999999,-3.5709504000000001]
["2024-03-22T21:30:00","2024-03-22T21:35:00",452.68860480000001,-3.8277564000000002]
["2024-03-22T21:35:00","2024-03-22T21:40:00",450.32953199999997,-4.2645587999999996]
["2024-03-22T21:40:00","2024-03-22T21:45:00",445.40711399999998,-5.4967535999999999]
["2024-03-22T21:45:00","2024-03-22T21:50:00",441.14159160000003,-6.5374476000000001]
["2024-03-22T21:50:00","2024-03-22T21:55:00",436.93431720000001,-7.6423176000000002]
["2024-03-22T21:55:00","2024-03-22T22:00:00",430.576686,-11.230591199999999]
["2024-03-22T22:00:00","2024-03-22T22:05:00",430.6931136,-10.982454000000001]
["2024-03-22T22:05:00","2024-03-22T22:10:00",429.87393479999997,-11.256688799999999]
["2024-03-22T22:10:00","2024-03-22T22:15:00",426.98484239999999,-11.486166000000001]
["2024-03-22T22:15:00","2024-03-22T22:20:00",423.90998639999998,-12.051507600000001]
["2024-03-22T22:20:00","2024-03-22T22:25:00",421.59401159999999,-11.639893199999999]
["2024-03-22T22:25:00","2024-03-22T22:30:00",420.87569159999998,-11.1310164]
["2024-03-22T22:30:00","2024-03-22T22:35:00",418.6700616,-11.9374392]
["2024-03-22T22:35:00","2024-03-22T22:40:00",416.106966,-12.3665448]
["2024-03-22T22:40:00","2024-03-22T22:45:00",414.46045320000002,-13.083017999999999]
["2024-03-22T22:45:00","2024-03-22T22:50:00",410.09319720000002,-14.8899036]
["2024-03-22T22:50:00","2024-03-22T22:55:00",407.02870200000001,-14.721424799999999]
["2024-03-22T22:55:00","2024-03-22T23:00:00",405.8137428,-15.1023204]
["2024-03-22T23:00:00","2024-03-22T23:05:00",410.01109439999999,-15.1097172]
["2024-03-22T23:05:00","2024-03-22T23:10:00",420.69706919999999,-14.554872]
["2024-03-22T23:10:00","2024-03-22T23:15:00",425.63411400000001,-13.573376400000001]
["2024-03-22T23:15:00","2024-03-22T23:20:00",422.93763239999998,-14.208708]
["2024-03-22T23:20:00","2024-03-22T23:25:00",417.67036439999998,-15.547011599999999]
["2024-03-22T23:25:00","2024-03-22T23:30:00",414.09236399999998,-15.422404800000001]
["2024-03-22T23:30:00","2024-03-22T23:35:00",409.36115519999998,-16.407412799999999]
["2024-03-22T23:35:00","2024-03-22T23:40:00",405.24481919999999,-17.5101336]
["2024-03-22T23:40:00","2024-03-22T23:45:00",401.93624160000002,-17.6453256]
["2024-03-22T23:45:00","2024-03-22T23:50:00",398.85445440000001,-17.908415999999999]
["2024-03-22T23:50:00","2024-03-22T23:55:00",395.25327240000001,-18.3265548]
["2024-03-22T23:55:00",45374,395.0675316,-18.129590400000001]
[45374,"2024-03-23T00:05:00",391.41279359999999,-18.4350144]
["2024-03-23T00:05:00","2024-03-23T00:10:00",389.33307480000002,-19.2678552]
["2024-03-23T00:10:00","2024-03-23T00:15:00",388.00346760000002,-19.925903999999999]
["2024-03-23T00:15:00","2024-03-23T00:20:00",382.98036239999999,-20.965298399999998]
["2024-03-23T00:20:00","2024-03-23T00:25:00",379.67532360000001,-21.903468]
["2024-03-23T00:25:00","2024-03-23T00:30:00",378.14256,-21.706438800000001]
["2024-03-23T00:30:00","2024-03-23T00:35:00",375.5163336,-22.048100399999999]
["2024-03-23T00:35:00","2024-03-23T00:40:00",376.43477519999999,-21.5393112]
["2024-03-23T00:40:00","2024-03-23T00:45:00",374.56829520000002,-22.349221199999999]
["2024-03-23T00:45:00","2024-03-23T00:50:00",371.30338560000001,-23.143258800000002]
["2024-03-23T00:50:00","2024-03-23T00:55:00",369.88356959999999,-22.814558399999999]
["2024-03-23T00:55:00","2024-03-23T01:00:00",367.763148,-23.295228000000002]
["2024-03-23T01:00:00","2024-03-23T01:05:00",364.85000639999998,-23.968957199999998]
["2024-03-23T01:05:00","2024-03-23T01:10:00",364.86887639999998,-24.657987599999998]
["2024-03-23T01:10:00","2024-03-23T01:15:00",362.03434320000002,-25.8867996]
["2024-03-23T01:15:00","2024-03-23T01:20:00",358.92209759999997,-27.054444]
["2024-03-23T01:20:00","2024-03-23T01:25:00",356.52737760000002,-27.694004400000001]
["2024-03-23T01:25:00","2024-03-23T01:30:00",354.86774159999999,-27.725777999999998]
["2024-03-23T01:30:00","2024-03-23T01:35:00",354.18636359999999,-28.481615999999999]
["2024-03-23T01:35:00","2024-03-23T01:40:00",353.6294292,-28.441286399999999]
["2024-03-23T01:40:00","2024-03-23T01:45:00",351.83098200000001,-28.278350400000001]
["2024-03-23T01:45:00","2024-03-23T01:50:00",350.1164028,-29.0807328]
["2024-03-23T01:50:00","2024-03-23T01:55:00",349.64715480000001,-29.421127200000001]
["2024-03-23T01:55:00","2024-03-23T02:00:00",347.79474959999999,-30.634271999999999]
["2024-03-23T02:00:00","2024-03-23T02:05:00",348.79859399999998,-30.793369200000001]
["2024-03-23T02:05:00","2024-03-23T02:10:00",350.17648079999998,-29.729870399999999]
["2024-03-23T02:10:00","2024-03-23T02:15:00",349.46883960000002,-29.7656928]
["2024-03-23T02:15:00","2024-03-23T02:20:00",349.89432840000001,-29.378544000000002]
["2024-03-23T02:20:00","2024-03-23T02:25:00",349.863114,-28.634415600000001]
["2024-03-23T02:25:00","2024-03-23T02:30:00",349.32166439999997,-28.6732464]
["2024-03-23T02:30:00","2024-03-23T02:35:00",347.59679399999999,-29.4171516]
["2024-03-23T02:35:00","2024-03-23T02:40:00",347.69899679999997,-29.9366664]
["2024-03-23T02:40:00","2024-03-23T02:45:00",346.60296240000002,-30.6800988]
["2024-03-23T02:45:00","2024-03-23T02:50:00",343.482282,-31.693018800000001]
["2024-03-23T02:50:00","2024-03-23T02:55:00",341.68447800000001,-32.4856908]
["2024-03-23T02:55:00","2024-03-23T03:00:00",341.14141080000002,-32.318313600000003]
["2024-03-23T03:00:00","2024-03-23T03:05:00",341.03791560000002,-32.538426000000001]
["2024-03-23T03:05:00","2024-03-23T03:10:00",342.46753919999998,-31.496758799999999]
["2024-03-23T03:10:00","2024-03-23T03:15:00",344.25761999999997,-30.625693200000001]
["2024-03-23T03:15:00","2024-03-23T03:20:00",345.72161039999997,-30.197743200000001]
["2024-03-23T03:20:00","2024-03-23T03:25:00",344.98331760000002,-30.718700399999999]
["2024-03-23T03:25:00","2024-03-23T03:30:00",345.28616520000003,-30.439774799999999]
["2024-03-23T03:30:00","2024-03-23T03:35:00",347.17770480000001,-29.106004800000001]
["2024-03-23T03:35:00","2024-03-23T03:40:00",348.00918480000001,-29.6353404]
["2024-03-23T03:40:00","2024-03-23T03:45:00",348.3824424,-30.047686800000001]
["2024-03-23T03:45:00","2024-03-23T03:50:00",348.02223600000002,-31.019511600000001]
["2024-03-23T03:50:00","2024-03-23T03:55:00",348.18910080000001,-30.901191600000001]
["2024-03-23T03:55:00","2024-03-23T04:00:00",349.28212559999997,-30.614778000000001]
["2024-03-23T04:00:00","2024-03-23T04:05:00",351.92799480000002,-30.06165]
["2024-03-23T04:05:00","2024-03-23T04:10:00",354.85936079999999,-29.211825600000001]
["2024-03-23T04:10:00","2024-03-23T04:15:00",355.34723400000001,-29.927602799999999]
["2024-03-23T04:15:00","2024-03-23T04:20:00",355.79357279999999,-30.089058000000001]
["2024-03-23T04:20:00","2024-03-23T04:25:00",355.49217959999999,-30.039356399999999]
["2024-03-23T04:25:00","2024-03-23T04:30:00",356.50746720000001,-29.862255600000001]
["2024-03-23T04:30:00","2024-03-23T04:35:00",356.65360920000001,-29.668340400000002]
["2024-03-23T04:35:00","2024-03-23T04:40:00",360.54531120000001,-28.754324400000002]
["2024-03-23T04:40:00","2024-03-23T04:45:00",360.65517119999998,-28.716671999999999]
["2024-03-23T04:45:00","2024-03-23T04:50:00",358.2625668,-29.8298208]
["2024-03-23T04:50:00","2024-03-23T04:55:00",361.0950072,-28.464544799999999]
["2024-03-23T04:55:00","2024-03-23T05:00:00",364.21413360000003,-27.266472]
["2024-03-23T05:00:00","2024-03-23T05:05:00",368.15728439999998,-26.040422400000001]
["2024-03-23T05:05:00","2024-03-23T05:10:00",373.20336479999997,-24.5731836]
["2024-03-23T05:10:00","2024-03-23T05:15:00",374.8397832,-23.206066799999999]
["2024-03-23T05:15:00","2024-03-23T05:20:00",377.53922399999999,-22.770296399999999]
["2024-03-23T05:20:00","2024-03-23T05:25:00",380.5954716,-21.831765600000001]
["2024-03-23T05:25:00","2024-03-23T05:30:00",382.79936880000002,-20.005982400000001]
["2024-03-23T05:30:00","2024-03-23T05:35:00",384.82363199999998,-18.932462399999999]
["2024-03-23T05:35:00","2024-03-23T05:40:00",387.66723839999997,-18.142686000000001]
["2024-03-23T05:40:00","2024-03-23T05:45:00",387.31442759999999,-18.460447200000001]
["2024-03-23T05:45:00","2024-03-23T05:50:00",389.73213720000001,-17.827216799999999]
["2024-03-23T05:50:00","2024-03-23T05:55:00",393.0451716,-16.9132152]
["2024-03-23T05:55:00","2024-03-23T06:00:00",395.30985600000002,-16.898441999999999]
["2024-03-23T06:00:00","2024-03-23T06:05:00",404.47238879999998,-14.2688796]
["2024-03-23T06:05:00","2024-03-23T06:10:00",408.52603679999999,-11.9838804]
["2024-03-23T06:10:00","2024-03-23T06:15:00",408.28265759999999,-12.206656799999999]
["2024-03-23T06:15:00","2024-03-23T06:20:00",411.00992159999998,-11.501910000000001]
["2024-03-23T06:20:00","2024-03-23T06:25:00",409.29707519999999,-11.8440312]
["2024-03-23T06:25:00","2024-03-23T06:30:00",412.32773159999999,-10.946920799999999]
["2024-03-23T06:30:00","2024-03-23T06:35:00",415.59109560000002,-10.0294908]
["2024-03-23T06:35:00","2024-03-23T06:40:00",416.75931480000003,-10.173617999999999]
["2024-03-23T06:40:00","2024-03-23T06:45:00",420.343638,-9.3671699999999998]
["2024-03-23T06:45:00","2024-03-23T06:50:00",419.83061279999998,-9.6737927999999993]
["2024-03-23T06:50:00","2024-03-23T06:55:00",419.15521319999999,-9.4237403999999998]
["2024-03-23T06:55:00","2024-03-23T07:00:00",421.66125840000001,-7.3968936000000003]
["2024-03-23T07:00:00","2024-03-23T07:05:00",415.47395519999998,-8.3932655999999994]
["2024-03-23T07:05:00","2024-03-23T07:10:00",415.98335520000001,-8.4198059999999995]
["2024-03-23T07:10:00","2024-03-23T07:15:00",415.32363240000001,-7.7702783999999996]
["2024-03-23T07:15:00","2024-03-23T07:20:00",411.90148319999997,-6.5673047999999996]
["2024-03-23T07:20:00","2024-03-23T07:25:00",413.59862759999999,-4.9349844000000003]
["2024-03-23T07:25:00","2024-03-23T07:30:00",409.39526640000003,-4.9030019999999999]
["2024-03-23T07:30:00","2024-03-23T07:35:00",406.24119480000002,-4.0692120000000003]
["2024-03-23T07:35:00","2024-03-23T07:40:00",408.432006,-1.8156924000000001]
["2024-03-23T07:40:00","2024-03-23T07:45:00",408.54608639999998,-2.0330352]
["2024-03-23T07:45:00","2024-03-23T07:50:00",410.90492280000001,-0.97708680000000003]
["2024-03-23T07:50:00","2024-03-23T07:55:00",410.07935040000001,-0.48384719999999998]
["2024-03-23T07:55:00","2024-03-23T08:00:00",411.37400880000001,0.50303279999999995]
["2024-03-23T08:00:00","2024-03-23T08:05:00",413.82582480000002,4.1171999999999997E-3]
["2024-03-23T08:05:00","2024-03-23T08:10:00",413.14981080000001,-0.76073040000000003]
["2024-03-23T08:10:00","2024-03-23T08:15:00",412.1638284,4.8491999999999997E-3]
["2024-03-23T08:15:00","2024-03-23T08:20:00",413.33556240000001,0.73491839999999997]
["2024-03-23T08:20:00","2024-03-23T08:25:00",413.56814639999999,3.7438343999999999]
["2024-03-23T08:25:00","2024-03-23T08:30:00",411.24176399999999,4.8570216000000004]
["2024-03-23T08:30:00","2024-03-23T08:35:00",411.45590520000002,4.6012475999999998]
["2024-03-23T08:35:00","2024-03-23T08:40:00",408.52732680000003,5.9037876000000002]
["2024-03-23T08:40:00","2024-03-23T08:45:00",404.91065759999998,5.5594704000000004]
["2024-03-23T08:45:00","2024-03-23T08:50:00",402.9760824,6.6893472000000003]
["2024-03-23T08:50:00","2024-03-23T08:55:00",400.04078279999999,7.7815523999999998]
["2024-03-23T08:55:00","2024-03-23T09:00:00",397.68375959999997,6.2589324]
["2024-03-23T09:00:00","2024-03-23T09:05:00",396.5997648,6.3651527999999997]
["2024-03-23T09:05:00","2024-03-23T09:10:00",394.69287960000003,8.1490308000000002]
["2024-03-23T09:10:00","2024-03-23T09:15:00",394.58694120000001,9.0598475999999994]
["2024-03-23T09:15:00","2024-03-23T09:20:00",391.5070872,9.2987003999999995]
["2024-03-23T09:20:00","2024-03-23T09:25:00",392.99886600000002,7.6339692000000001]
["2024-03-23T09:25:00","2024-03-23T09:30:00",396.07322399999998,6.8159039999999997]
["2024-03-23T09:30:00","2024-03-23T09:35:00",397.55455799999999,7.2520404000000003]
["2024-03-23T09:35:00","2024-03-23T09:40:00",396.11676720000003,7.9850376000000001]
["2024-03-23T09:40:00","2024-03-23T09:45:00",390.41579639999998,7.1976443999999997]
["2024-03-23T09:45:00","2024-03-23T09:50:00",382.65401880000002,7.8093756000000001]
["2024-03-23T09:50:00","2024-03-23T09:55:00",374.91580320000003,9.8001468000000003]
["2024-03-23T09:55:00","2024-03-23T10:00:00",381.7883592,9.2124588000000003]
["2024-03-23T10:00:00","2024-03-23T10:05:00",388.9534716,8.2438307999999996]
["2024-03-23T10:05:00","2024-03-23T10:10:00",395.9311548,9.4337915999999993]
["2024-03-23T10:10:00","2024-03-23T10:15:00",397.58159640000002,9.4514940000000003]
["2024-03-23T10:15:00","2024-03-23T10:20:00",399.1870596,8.8578671999999994]
["2024-03-23T10:20:00","2024-03-23T10:25:00",398.36872080000001,8.8613759999999999]
["2024-03-23T10:25:00","2024-03-23T10:30:00",394.68128519999999,9.2199083999999996]
["2024-03-23T10:30:00","2024-03-23T10:35:00",386.38092599999999,9.4264715999999993]
["2024-03-23T10:35:00","2024-03-23T10:40:00",377.86092359999998,9.4861751999999999]
["2024-03-23T10:40:00","2024-03-23T10:45:00",370.71949560000002,9.7730183999999998]
["2024-03-23T10:45:00","2024-03-23T10:50:00",363.19174320000002,10.005077999999999]
["2024-03-23T10:50:00","2024-03-23T10:55:00",358.2176796,10.444205999999999]
["2024-03-23T10:55:00","2024-03-23T11:00:00",356.46497040000003,10.1722284]
["2024-03-23T11:00:00","2024-03-23T11:05:00",351.52632119999998,12.1662768]
["2024-03-23T11:05:00","2024-03-23T11:10:00",346.75459080000002,11.794957200000001]
["2024-03-23T11:10:00","2024-03-23T11:15:00",341.82538319999998,9.9808907999999992]
["2024-03-23T11:15:00","2024-03-23T11:20:00",340.41983399999998,10.479794399999999]
["2024-03-23T11:20:00","2024-03-23T11:25:00",340.30820399999999,9.2500128000000004]
["2024-03-23T11:25:00","2024-03-23T11:30:00",346.1901312,8.4249863999999999]
["2024-03-23T11:30:00","2024-03-23T11:35:00",351.67164480000002,7.0437348000000002]
["2024-03-23T11:35:00","2024-03-23T11:40:00",353.8135608,6.1590227999999998]
["2024-03-23T11:40:00","2024-03-23T11:45:00",355.10915399999999,6.9688764000000001]
["2024-03-23T11:45:00","2024-03-23T11:50:00",363.14661360000002,7.2438288000000002]
["2024-03-23T11:50:00","2024-03-23T11:55:00",362.71478760000002,6.9618827999999997]
["2024-03-23T11:55:00","2024-03-23T12:00:00",360.91615919999998,8.0943468000000003]
["2024-03-23T12:00:00","2024-03-23T12:05:00",357.35079719999999,8.4239219999999992]
["2024-03-23T12:05:00","2024-03-23T12:10:00",355.94503800000001,7.7047715999999999]
["2024-03-23T12:10:00","2024-03-23T12:15:00",346.46561759999997,7.2212940000000003]
["2024-03-23T12:15:00","2024-03-23T12:20:00",339.18992759999998,7.8066024000000001]
["2024-03-23T12:20:00","2024-03-23T12:25:00",317.56866359999998,7.1309712000000003]
["2024-03-23T12:25:00","2024-03-23T12:30:00",305.98887960000002,8.4534839999999996]
["2024-03-23T12:30:00","2024-03-23T12:35:00",300.62036160000002,9.2162495999999994]
["2024-03-23T12:35:00","2024-03-23T12:40:00",298.5407184,9.8984363999999996]
["2024-03-23T12:40:00","2024-03-23T12:45:00",302.8707852,9.7553280000000004]
["2024-03-23T12:45:00","2024-03-23T12:50:00",291.39205320000002,10.0813656]
["2024-03-23T12:50:00","2024-03-23T12:55:00",291.06543720000002,9.9926244000000004]
["2024-03-23T12:55:00","2024-03-23T13:00:00",288.1317876,8.8518323999999993]
["2024-03-23T13:00:00","2024-03-23T13:05:00",282.79497479999998,9.0811980000000005]
["2024-03-23T13:05:00","2024-03-23T13:10:00",278.28199919999997,10.4202732]
["2024-03-23T13:10:00","2024-03-23T13:15:00",271.38069359999997,12.201622800000001]
["2024-03-23T13:15:00","2024-03-23T13:20:00",270.2870016,9.2199924000000006]
["2024-03-23T13:20:00","2024-03-23T13:25:00",270.15223800000001,8.7768131999999994]
["2024-03-23T13:25:00","2024-03-23T13:30:00",267.91228799999999,8.3694839999999999]
["2024-03-23T13:30:00","2024-03-23T13:35:00",271.46747640000001,6.5902871999999997]
["2024-03-23T13:35:00","2024-03-23T13:40:00",275.87835360000003,7.1654207999999997]
["2024-03-23T13:40:00","2024-03-23T13:45:00",284.50747439999998,7.1330255999999999]
["2024-03-23T13:45:00","2024-03-23T13:50:00",296.17303559999999,5.3272931999999997]
["2024-03-23T13:50:00","2024-03-23T13:55:00",304.43142599999999,6.5361132]
["2024-03-23T13:55:00","2024-03-23T14:00:00",308.09374200000002,6.3872999999999998]
["2024-03-23T14:00:00","2024-03-23T14:05:00",307.54409759999999,4.7604420000000003]
["2024-03-23T14:05:00","2024-03-23T14:10:00",304.46448479999998,4.6060344000000004]
["2024-03-23T14:10:00","2024-03-23T14:15:00",300.70665600000001,5.2930992000000003]
["2024-03-23T14:15:00","2024-03-23T14:20:00",303.9139356,4.9079148000000004]
["2024-03-23T14:20:00","2024-03-23T14:25:00",311.89020240000002,4.6043928000000003]
["2024-03-23T14:25:00","2024-03-23T14:30:00",308.7051108,3.7952724]
["2024-03-23T14:30:00","2024-03-23T14:35:00",304.0683204,3.4227756]
["2024-03-23T14:35:00","2024-03-23T14:40:00",296.77162079999999,6.4077396000000002]
["2024-03-23T14:40:00","2024-03-23T14:45:00",289.49472839999999,6.1941743999999996]
["2024-03-23T14:45:00","2024-03-23T14:50:00",277.4142564,5.2074780000000001]
["2024-03-23T14:50:00","2024-03-23T14:55:00",273.20945519999998,5.7194484000000001]
["2024-03-23T14:55:00","2024-03-23T15:00:00",264.19965480000002,6.2613431999999998]
["2024-03-23T15:00:00","2024-03-23T15:05:00",265.87855680000001,5.0519147999999996]
["2024-03-23T15:05:00","2024-03-23T15:10:00",269.64876720000001,5.4298944000000002]
["2024-03-23T15:10:00","2024-03-23T15:15:00",277.64337,6.4378907999999999]
["2024-03-23T15:15:00","2024-03-23T15:20:00",287.63010839999998,5.7976812000000004]
["2024-03-23T15:20:00","2024-03-23T15:25:00",289.54765800000001,4.1155619999999997]
["2024-03-23T15:25:00","2024-03-23T15:30:00",301.21288679999998,2.4533604000000002]
["2024-03-23T15:30:00","2024-03-23T15:35:00",299.99120160000001,0.36935279999999998]
["2024-03-23T15:35:00","2024-03-23T15:40:00",312.3620616,0.28543679999999999]
["2024-03-23T15:40:00","2024-03-23T15:45:00",321.65016120000001,-0.14764079999999999]
["2024-03-23T15:45:00","2024-03-23T15:50:00",327.84047399999997,-0.46295760000000002]
["2024-03-23T15:50:00","2024-03-23T15:55:00",333.62407560000003,-1.4253228]
["2024-03-23T15:55:00","2024-03-23T16:00:00",335.87679359999998,-1.6492560000000001]
["2024-03-23T16:00:00","2024-03-23T16:05:00",340.67537040000002,-1.7930016]
["2024-03-23T16:05:00","2024-03-23T16:10:00",346.68642599999998,-2.7704304]
["2024-03-23T16:10:00","2024-03-23T16:15:00",351.2829936,-3.2298564000000001]
["2024-03-23T16:15:00","2024-03-23T16:20:00",356.94143880000001,-2.4247931999999999]
["2024-03-23T16:20:00","2024-03-23T16:25:00",361.45954560000001,-2.4714672000000002]
["2024-03-23T16:25:00","2024-03-23T16:30:00",366.84490920000002,-2.7120972000000001]
["2024-03-23T16:30:00","2024-03-23T16:35:00",370.57764839999999,-3.1950384000000001]
["2024-03-23T16:35:00","2024-03-23T16:40:00",378.1404804,-3.1046711999999999]
["2024-03-23T16:40:00","2024-03-23T16:45:00",385.20369599999998,-2.9229371999999998]
["2024-03-23T16:45:00","2024-03-23T16:50:00",388.7272428,-3.6541068000000001]
["2024-03-23T16:50:00","2024-03-23T16:55:00",391.14513360000001,-3.8313899999999999]
["2024-03-23T16:55:00","2024-03-23T17:00:00",394.73643120000003,-4.676088]
["2024-03-23T17:00:00","2024-03-23T17:05:00",397.61936159999999,-5.7630179999999998]
["2024-03-23T17:05:00","2024-03-23T17:10:00",400.710306,-6.8802935999999999]
["2024-03-23T17:10:00","2024-03-23T17:15:00",406.72192439999998,-7.3636379999999999]
["2024-03-23T17:15:00","2024-03-23T17:20:00",414.47716800000001,-7.7809920000000004]
["2024-03-23T17:20:00","2024-03-23T17:25:00",422.00140320000003,-8.0431968000000005]
["2024-03-23T17:25:00","2024-03-23T17:30:00",426.72696719999999,-9.7841111999999999]
["2024-03-23T17:30:00","2024-03-23T17:35:00",430.29489480000001,-10.362966]
["2024-03-23T17:35:00","2024-03-23T17:40:00",436.20296400000001,-10.601722799999999]
["2024-03-23T17:40:00","2024-03-23T17:45:00",441.7622088,-10.2179976]
["2024-03-23T17:45:00","2024-03-23T17:50:00",445.83713280000001,-9.9411719999999999]
["2024-03-23T17:50:00","2024-03-23T17:55:00",447.99757799999998,-11.4353496]
["2024-03-23T17:55:00","2024-03-23T18:00:00",453.32891519999998,-10.506190800000001]
["2024-03-23T18:00:00","2024-03-23T18:05:00",458.65805519999998,-10.2587508]
["2024-03-23T18:05:00","2024-03-23T18:10:00",462.41862959999997,-9.6144107999999999]
["2024-03-23T18:10:00","2024-03-23T18:15:00",463.61227200000002,-9.2813891999999996]
["2024-03-23T18:15:00","2024-03-23T18:20:00",468.41309999999999,-7.8282959999999999]
["2024-03-23T18:20:00","2024-03-23T18:25:00",472.1414628,-7.0037723999999999]
["2024-03-23T18:25:00","2024-03-23T18:30:00",471.54957719999999,-8.1931703999999996]
["2024-03-23T18:30:00","2024-03-23T18:35:00",470.04162600000001,-8.7654180000000004]
["2024-03-23T18:35:00","2024-03-23T18:40:00",469.5325368,-9.6540540000000004]
["2024-03-23T18:40:00","2024-03-23T18:45:00",469.6876944,-9.4568940000000001]
["2024-03-23T18:45:00","2024-03-23T18:50:00",471.0159084,-9.4819464]
["2024-03-23T18:50:00","2024-03-23T18:55:00",471.32134680000001,-8.9114375999999993]
["2024-03-23T18:55:00","2024-03-23T19:00:00",472.90535640000002,-7.5905316000000003]
["2024-03-23T19:00:00","2024-03-23T19:05:00",470.69898480000001,-8.4157943999999993]
["2024-03-23T19:05:00","2024-03-23T19:10:00",471.75059399999998,-8.3050680000000003]
["2024-03-23T19:10:00","2024-03-23T19:15:00",470.36883,-10.320028799999999]
["2024-03-23T19:15:00","2024-03-23T19:20:00",471.08253120000001,-9.3211776000000004]
["2024-03-23T19:20:00","2024-03-23T19:25:00",468.51859080000003,-9.6040559999999999]
["2024-03-23T19:25:00","2024-03-23T19:30:00",469.19387879999999,-10.257254400000001]
["2024-03-23T19:30:00","2024-03-23T19:35:00",467.43122879999999,-11.1132156]
["2024-03-23T19:35:00","2024-03-23T19:40:00",465.27599880000002,-11.7219312]
["2024-03-23T19:40:00","2024-03-23T19:45:00",462.49024079999998,-12.3953448]
["2024-03-23T19:45:00","2024-03-23T19:50:00",460.84522800000002,-13.345786800000001]
["2024-03-23T19:50:00","2024-03-23T19:55:00",458.75774519999999,-14.223633599999999]
["2024-03-23T19:55:00","2024-03-23T20:00:00",457.11308279999997,-14.383692]
["2024-03-23T20:00:00","2024-03-23T20:05:00",454.36778880000003,-15.135528000000001]
["2024-03-23T20:05:00","2024-03-23T20:10:00",454.15448520000001,-14.905446]
["2024-03-23T20:10:00","2024-03-23T20:15:00",452.44272840000002,-15.740764799999999]
["2024-03-23T20:15:00","2024-03-23T20:20:00",451.29552000000001,-15.392281199999999]
["2024-03-23T20:20:00","2024-03-23T20:25:00",448.69336920000001,-16.096725599999999]
["2024-03-23T20:25:00","2024-03-23T20:30:00",445.30411320000002,-17.631202800000001]
["2024-03-23T20:30:00","2024-03-23T20:35:00",443.17763159999998,-18.510752400000001]
["2024-03-23T20:35:00","2024-03-23T20:40:00",443.39591280000002,-18.520734000000001]
["2024-03-23T20:40:00","2024-03-23T20:45:00",443.31835319999999,-18.781777200000001]
["2024-03-23T20:45:00","2024-03-23T20:50:00",443.25969959999998,-17.9986392]
["2024-03-23T20:50:00","2024-03-23T20:55:00",439.75086599999997,-19.065877199999999]
["2024-03-23T20:55:00","2024-03-23T21:00:00",435.94183079999999,-19.845846000000002]
["2024-03-23T21:00:00","2024-03-23T21:05:00",435.3979008,-19.8297192]
["2024-03-23T21:05:00","2024-03-23T21:10:00",433.17657839999998,-19.757800799999998]
["2024-03-23T21:10:00","2024-03-23T21:15:00",429.0456408,-20.9267064]
["2024-03-23T21:15:00","2024-03-23T21:20:00",427.28295000000003,-21.701997599999999]
["2024-03-23T21:20:00","2024-03-23T21:25:00",423.79133519999999,-21.843100799999998]
["2024-03-23T21:25:00","2024-03-23T21:30:00",420.91220399999997,-22.560055200000001]
["2024-03-23T21:30:00","2024-03-23T21:35:00",417.61563599999999,-22.768961999999998]
["2024-03-23T21:35:00","2024-03-23T21:40:00",416.9916336,-24.136002000000001]
["2024-03-23T21:40:00","2024-03-23T21:45:00",415.91622719999998,-24.285346799999999]
["2024-03-23T21:45:00","2024-03-23T21:50:00",414.10447199999999,-24.016579199999999]
["2024-03-23T21:50:00","2024-03-23T21:55:00",410.17314479999999,-24.3700212]
["2024-03-23T21:55:00","2024-03-23T22:00:00",406.5095508,-25.6076172]
["2024-03-23T22:00:00","2024-03-23T22:05:00",404.32743959999999,-25.923495599999999]
["2024-03-23T22:05:00","2024-03-23T22:10:00",405.82888079999998,-24.9322464]
["2024-03-23T22:10:00","2024-03-23T22:15:00",404.17623959999997,-24.474053999999999]
["2024-03-23T22:15:00","2024-03-23T22:20:00",401.86867439999997,-25.063559999999999]
["2024-03-23T22:20:00","2024-03-23T22:25:00",399.06432000000001,-25.690174800000001]
["2024-03-23T22:25:00","2024-03-23T22:30:00",396.91455359999998,-25.9272636]
["2024-03-23T22:30:00","2024-03-23T22:35:00",393.81042719999999,-26.1568848]
["2024-03-23T22:35:00","2024-03-23T22:40:00",391.60854719999998,-27.798912000000001]
["2024-03-23T22:40:00","2024-03-23T22:45:00",389.92156440000002,-27.931480799999999]
["2024-03-23T22:45:00","2024-03-23T22:50:00",388.82260680000002,-27.508047600000001]
["2024-03-23T22:50:00","2024-03-23T22:55:00",385.4041368,-28.111709999999999]
["2024-03-23T22:55:00","2024-03-23T23:00:00",384.85825199999999,-27.889141200000001]
["2024-03-23T23:00:00","2024-03-23T23:05:00",389.72645999999997,-28.190193600000001]
["2024-03-23T23:05:00","2024-03-23T23:10:00",399.6456804,-27.655676400000001]
["2024-03-23T23:10:00","2024-03-23T23:15:00",402.90939359999999,-27.501430800000001]
["2024-03-23T23:15:00","2024-03-23T23:20:00",399.6391716,-28.2289332]
["2024-03-23T23:20:00","2024-03-23T23:25:00",397.79984760000002,-27.9756252]
["2024-03-23T23:25:00","2024-03-23T23:30:00",393.75892440000001,-28.378622400000001]
["2024-03-23T23:30:00","2024-03-23T23:35:00",390.29197679999999,-29.209493999999999]
["2024-03-23T23:35:00","2024-03-23T23:40:00",388.22913240000003,-30.033816000000002]
["2024-03-23T23:40:00","2024-03-23T23:45:00",385.84048680000001,-30.112836000000001]
["2024-03-23T23:45:00","2024-03-23T23:50:00",382.62453479999999,-30.474288000000001]
["2024-03-23T23:50:00","2024-03-23T23:55:00",379.43711519999999,-30.9207024]
["2024-03-23T23:55:00",45375,375.58338479999998,-31.914923999999999]
[45375,"2024-03-24T00:05:00",374.44418159999998,-31.6738404]
["2024-03-24T00:05:00","2024-03-24T00:10:00",371.57328840000002,-32.2780044]
["2024-03-24T00:10:00","2024-03-24T00:15:00",370.50196080000001,-32.3252436]
["2024-03-24T00:15:00","2024-03-24T00:20:00",365.56168559999998,-33.239215199999997]
["2024-03-24T00:20:00","2024-03-24T00:25:00",363.69237479999998,-33.458936399999999]
["2024-03-24T00:25:00","2024-03-24T00:30:00",362.46931080000002,-33.955897200000003]
["2024-03-24T00:30:00","2024-03-24T00:35:00",360.54907200000002,-33.622062]
["2024-03-24T00:35:00","2024-03-24T00:40:00",359.53529520000001,-33.523257600000001]
["2024-03-24T00:40:00","2024-03-24T00:45:00",358.9070208,-33.9003984]
["2024-03-24T00:45:00","2024-03-24T00:50:00",357.5941272,-33.666491999999998]
["2024-03-24T00:50:00","2024-03-24T00:55:00",355.07358840000001,-33.703919999999997]
["2024-03-24T00:55:00","2024-03-24T01:00:00",352.07153520000003,-34.699078800000002]
["2024-03-24T01:00:00","2024-03-24T01:05:00",349.87713000000002,-35.956903199999999]
["2024-03-24T01:05:00","2024-03-24T01:10:00",348.47336280000002,-36.004443600000002]
["2024-03-24T01:10:00","2024-03-24T01:15:00",347.02665000000002,-36.532787999999996]
["2024-03-24T01:15:00","2024-03-24T01:20:00",344.4601356,-36.614899200000004]
["2024-03-24T01:20:00","2024-03-24T01:25:00",343.18479839999998,-37.339399200000003]
["2024-03-24T01:25:00","2024-03-24T01:30:00",341.75244359999999,-37.574133600000003]
["2024-03-24T01:30:00","2024-03-24T01:35:00",340.79802239999998,-37.560709199999998]
["2024-03-24T01:35:00","2024-03-24T01:40:00",339.11488680000002,-38.446898400000002]
["2024-03-24T01:40:00","2024-03-24T01:45:00",338.87096639999999,-37.940185200000002]
["2024-03-24T01:45:00","2024-03-24T01:50:00",337.37367,-38.413128]
["2024-03-24T01:50:00","2024-03-24T01:55:00",336.36734039999999,-38.4960168]
["2024-03-24T01:55:00","2024-03-24T02:00:00",336.25819319999999,-38.958014400000003]
["2024-03-24T02:00:00","2024-03-24T02:05:00",336.17674319999998,-39.094105200000001]
["2024-03-24T02:05:00","2024-03-24T02:10:00",335.9936424,-39.333086399999999]
["2024-03-24T02:10:00","2024-03-24T02:15:00",335.83216679999998,-39.630820800000002]
["2024-03-24T02:15:00","2024-03-24T02:20:00",334.45963319999998,-39.341228399999999]
["2024-03-24T02:20:00","2024-03-24T02:25:00",333.7977204,-39.613792799999999]
["2024-03-24T02:25:00","2024-03-24T02:30:00",334.850346,-39.190691999999999]
["2024-03-24T02:30:00","2024-03-24T02:35:00",334.9299312,-38.545022400000001]
["2024-03-24T02:35:00","2024-03-24T02:40:00",334.66288800000001,-38.881838399999999]
["2024-03-24T02:40:00","2024-03-24T02:45:00",333.80795879999999,-39.515701200000002]
["2024-03-24T02:45:00","2024-03-24T02:50:00",332.02819199999999,-39.967283999999999]
["2024-03-24T02:50:00","2024-03-24T02:55:00",330.5626944,-40.434699600000002]
["2024-03-24T02:55:00","2024-03-24T03:00:00",330.79962840000002,-40.158028799999997]
["2024-03-24T03:00:00","2024-03-24T03:05:00",330.32474999999999,-40.884837599999997]
["2024-03-24T03:05:00","2024-03-24T03:10:00",330.5283192,-40.7425164]
["2024-03-24T03:10:00","2024-03-24T03:15:00",330.57233400000001,-40.714111199999998]
["2024-03-24T03:15:00","2024-03-24T03:20:00",330.58207800000002,-40.5879768]
["2024-03-24T03:20:00","2024-03-24T03:25:00",330.68128439999998,-40.743386399999999]
["2024-03-24T03:25:00","2024-03-24T03:30:00",329.78397719999998,-41.613582000000001]
["2024-03-24T03:30:00","2024-03-24T03:35:00",328.1429832,-42.158272799999999]
["2024-03-24T03:35:00","2024-03-24T03:40:00",329.53142639999999,-41.805866399999999]
["2024-03-24T03:40:00","2024-03-24T03:45:00",328.49747760000002,-42.420908400000002]
["2024-03-24T03:45:00","2024-03-24T03:50:00",328.4085948,-42.035674800000002]
["2024-03-24T03:50:00","2024-03-24T03:55:00",327.72768839999998,-42.351172800000001]
["2024-03-24T03:55:00","2024-03-24T04:00:00",329.71606439999999,-42.015900000000002]
["2024-03-24T04:00:00","2024-03-24T04:05:00",331.5911304,-41.735610000000001]
["2024-03-24T04:05:00","2024-03-24T04:10:00",335.1544212,-40.868566800000004]
["2024-03-24T04:10:00","2024-03-24T04:15:00",335.07692400000002,-41.674061999999999]
["2024-03-24T04:15:00","2024-03-24T04:20:00",336.08397480000002,-40.712751599999997]
["2024-03-24T04:20:00","2024-03-24T04:25:00",336.9097812,-40.925637600000002]
["2024-03-24T04:25:00","2024-03-24T04:30:00",338.26305719999999,-40.1318652]
["2024-03-24T04:30:00","2024-03-24T04:35:00",337.24165440000002,-39.984178800000002]
["2024-03-24T04:35:00","2024-03-24T04:40:00",337.31874599999998,-40.2705816]
["2024-03-24T04:40:00","2024-03-24T04:45:00",337.49587919999999,-40.542932399999998]
["2024-03-24T04:45:00","2024-03-24T04:50:00",336.2531712,-40.741837199999999]
["2024-03-24T04:50:00","2024-03-24T04:55:00",338.79984239999999,-40.068478800000001]
["2024-03-24T04:55:00","2024-03-24T05:00:00",340.89032520000001,-39.391144799999999]
["2024-03-24T05:00:00","2024-03-24T05:05:00",344.95394879999998,-38.510116799999999]
["2024-03-24T05:05:00","2024-03-24T05:10:00",347.64906719999999,-37.575066]
["2024-03-24T05:10:00","2024-03-24T05:15:00",349.7158068,-36.794767200000003]
["2024-03-24T05:15:00","2024-03-24T05:20:00",350.47727880000002,-36.459490799999998]
["2024-03-24T05:20:00","2024-03-24T05:25:00",350.6818356,-36.502058400000003]
["2024-03-24T05:25:00","2024-03-24T05:30:00",350.36648159999999,-36.495950399999998]
["2024-03-24T05:30:00","2024-03-24T05:35:00",349.63153319999998,-37.292258400000001]
["2024-03-24T05:35:00","2024-03-24T05:40:00",352.88260320000001,-35.740376400000002]
["2024-03-24T05:40:00","2024-03-24T05:45:00",354.91787879999998,-35.679029999999997]
["2024-03-24T05:45:00","2024-03-24T05:50:00",358.4170704,-34.307650799999998]
["2024-03-24T05:50:00","2024-03-24T05:55:00",359.09324400000003,-34.280109600000003]
["2024-03-24T05:55:00","2024-03-24T06:00:00",362.33952240000002,-33.440488799999997]
["2024-03-24T06:00:00","2024-03-24T06:05:00",367.61731559999998,-31.9044192]
["2024-03-24T06:05:00","2024-03-24T06:10:00",368.63609400000001,-31.692299999999999]
["2024-03-24T06:10:00","2024-03-24T06:15:00",369.89826959999999,-32.160213599999999]
["2024-03-24T06:15:00","2024-03-24T06:20:00",371.52253560000003,-32.098023599999998]
["2024-03-24T06:20:00","2024-03-24T06:25:00",369.63653399999998,-32.237965199999998]
["2024-03-24T06:25:00","2024-03-24T06:30:00",372.33187199999998,-31.3556484]
["2024-03-24T06:30:00","2024-03-24T06:35:00",372.20384280000002,-30.950443199999999]
["2024-03-24T06:35:00","2024-03-24T06:40:00",373.75741679999999,-30.9103776]
["2024-03-24T06:40:00","2024-03-24T06:45:00",374.57816279999997,-30.9399312]
["2024-03-24T06:45:00","2024-03-24T06:50:00",374.62474320000001,-30.175628400000001]
["2024-03-24T06:50:00","2024-03-24T06:55:00",372.41695559999999,-30.371822399999999]
["2024-03-24T06:55:00","2024-03-24T07:00:00",372.93294959999997,-30.109818000000001]
["2024-03-24T07:00:00","2024-03-24T07:05:00",370.92146880000001,-29.878408799999999]
["2024-03-24T07:05:00","2024-03-24T07:10:00",371.68019399999997,-29.5905852]
["2024-03-24T07:10:00","2024-03-24T07:15:00",370.2380124,-30.254498399999999]
["2024-03-24T07:15:00","2024-03-24T07:20:00",369.39954719999997,-26.889595199999999]
["2024-03-24T07:20:00","2024-03-24T07:25:00",368.61406799999997,-26.3244984]
["2024-03-24T07:25:00","2024-03-24T07:30:00",367.68824640000003,-24.281150400000001]
["2024-03-24T07:30:00","2024-03-24T07:35:00",366.21055080000002,-22.477226399999999]
["2024-03-24T07:35:00","2024-03-24T07:40:00",365.98484999999999,-21.129367200000001]
["2024-03-24T07:40:00","2024-03-24T07:45:00",363.98248560000002,-21.458695200000001]
["2024-03-24T07:45:00","2024-03-24T07:50:00",363.641796,-21.0293736]
["2024-03-24T07:50:00","2024-03-24T07:55:00",360.54094679999997,-21.040379999999999]
["2024-03-24T07:55:00","2024-03-24T08:00:00",354.58546439999998,-22.946578800000001]
["2024-03-24T08:00:00","2024-03-24T08:05:00",356.32249560000002,-21.7330392]
["2024-03-24T08:05:00","2024-03-24T08:10:00",360.19515239999998,-21.487058399999999]
["2024-03-24T08:10:00","2024-03-24T08:15:00",367.13983439999998,-21.026831999999999]
["2024-03-24T08:15:00","2024-03-24T08:20:00",374.74814040000001,-20.197679999999998]
["2024-03-24T08:20:00","2024-03-24T08:25:00",380.81205720000003,-17.148662399999999]
["2024-03-24T08:25:00","2024-03-24T08:30:00",380.67076200000002,-17.3390916]
["2024-03-24T08:30:00","2024-03-24T08:35:00",380.65839,-17.6766288]
["2024-03-24T08:35:00","2024-03-24T08:40:00",381.7892592,-19.372100400000001]
["2024-03-24T08:40:00","2024-03-24T08:45:00",379.75409519999999,-20.432734799999999]
["2024-03-24T08:45:00","2024-03-24T08:50:00",376.61823479999998,-20.869212000000001]
["2024-03-24T08:50:00","2024-03-24T08:55:00",371.64369479999999,-20.260060800000002]
["2024-03-24T08:55:00","2024-03-24T09:00:00",370.32035999999999,-19.0511388]
["2024-03-24T09:00:00","2024-03-24T09:05:00",369.46701719999999,-17.820784799999998]
["2024-03-24T09:05:00","2024-03-24T09:10:00",366.66873120000002,-17.459018400000001]
["2024-03-24T09:10:00","2024-03-24T09:15:00",361.43535000000003,-18.382215599999999]
["2024-03-24T09:15:00","2024-03-24T09:20:00",361.881846,-17.283130799999999]
["2024-03-24T09:20:00","2024-03-24T09:25:00",361.80057959999999,-16.582753199999999]
["2024-03-24T09:25:00","2024-03-24T09:30:00",354.72042479999999,-15.875499599999999]
["2024-03-24T09:30:00","2024-03-24T09:35:00",345.3540552,-14.7703656]
["2024-03-24T09:35:00","2024-03-24T09:40:00",336.9544224,-14.719516799999999]
["2024-03-24T09:40:00","2024-03-24T09:45:00",324.40478280000002,-15.8701332]
["2024-03-24T09:45:00","2024-03-24T09:50:00",316.07103599999999,-15.2103252]
["2024-03-24T09:50:00","2024-03-24T09:55:00",316.26032759999998,-14.70843]
["2024-03-24T09:55:00","2024-03-24T10:00:00",317.88923039999997,-15.1455936]
["2024-03-24T10:00:00","2024-03-24T10:05:00",320.19265680000001,-15.1640304]
["2024-03-24T10:05:00","2024-03-24T10:10:00",321.30963120000001,-14.7954648]
["2024-03-24T10:10:00","2024-03-24T10:15:00",318.26643840000003,-14.1936684]
["2024-03-24T10:15:00","2024-03-24T10:20:00",318.82990919999997,-14.049336]
["2024-03-24T10:20:00","2024-03-24T10:25:00",316.63521960000003,-14.1991116]
["2024-03-24T10:25:00","2024-03-24T10:30:00",315.49861199999998,-13.362424799999999]
["2024-03-24T10:30:00","2024-03-24T10:35:00",312.83906519999999,-12.3734436]
["2024-03-24T10:35:00","2024-03-24T10:40:00",310.87971240000002,-11.710082399999999]
["2024-03-24T10:40:00","2024-03-24T10:45:00",308.42364359999999,-10.4465664]
["2024-03-24T10:45:00","2024-03-24T10:50:00",297.38058599999999,-9.3438564]
["2024-03-24T10:50:00","2024-03-24T10:55:00",289.39517760000001,-9.1531500000000001]
["2024-03-24T10:55:00","2024-03-24T11:00:00",282.73137120000001,-9.0804036000000004]
["2024-03-24T11:00:00","2024-03-24T11:05:00",271.43701920000001,-9.6387023999999997]
["2024-03-24T11:05:00","2024-03-24T11:10:00",254.05188480000001,-7.9705823999999996]
["2024-03-24T11:10:00","2024-03-24T11:15:00",242.78574359999999,-8.0166708]
["2024-03-24T11:15:00","2024-03-24T11:20:00",230.45214240000001,-6.6219827999999996]
["2024-03-24T11:20:00","2024-03-24T11:25:00",228.9941724,-5.8154256000000002]
["2024-03-24T11:25:00","2024-03-24T11:30:00",231.4801224,-5.5262028000000001]
["2024-03-24T11:30:00","2024-03-24T11:35:00",229.130718,-4.4985492000000002]
["2024-03-24T11:35:00","2024-03-24T11:40:00",228.2076012,-3.7054716000000001]
["2024-03-24T11:40:00","2024-03-24T11:45:00",224.6397432,-2.4437519999999999]
["2024-03-24T11:45:00","2024-03-24T11:50:00",218.25085559999999,-1.5116436]
["2024-03-24T11:50:00","2024-03-24T11:55:00",218.56218240000001,-1.9713480000000001]
["2024-03-24T11:55:00","2024-03-24T12:00:00",205.15974,-4.0250496]
["2024-03-24T12:00:00","2024-03-24T12:05:00",197.3448492,-4.8432360000000001]
["2024-03-24T12:05:00","2024-03-24T12:10:00",191.91859919999999,-3.2569067999999999]
["2024-03-24T12:10:00","2024-03-24T12:15:00",189.3441072,-2.4707051999999998]
["2024-03-24T12:15:00","2024-03-24T12:20:00",193.61527319999999,-2.0281104000000001]
["2024-03-24T12:20:00","2024-03-24T12:25:00",192.589416,-1.874514]
["2024-03-24T12:25:00","2024-03-24T12:30:00",193.87547760000001,-1.2473196]
["2024-03-24T12:30:00","2024-03-24T12:35:00",190.52077679999999,-1.8888708000000001]
["2024-03-24T12:35:00","2024-03-24T12:40:00",190.996332,-3.6902496]
["2024-03-24T12:40:00","2024-03-24T12:45:00",189.60966959999999,-4.1874419999999999]
["2024-03-24T12:45:00","2024-03-24T12:50:00",186.7010568,-1.1400792]
["2024-03-24T12:50:00","2024-03-24T12:55:00",184.29252,-0.33915719999999999]
["2024-03-24T12:55:00","2024-03-24T13:00:00",184.11564240000001,0.19431480000000001]
["2024-03-24T13:00:00","2024-03-24T13:05:00",183.27811560000001,2.3818823999999998]
["2024-03-24T13:05:00","2024-03-24T13:10:00",183.40566240000001,4.3132235999999997]
["2024-03-24T13:10:00","2024-03-24T13:15:00",183.80777520000001,5.3150592000000003]
["2024-03-24T13:15:00","2024-03-24T13:20:00",186.14172600000001,4.9433040000000004]
["2024-03-24T13:20:00","2024-03-24T13:25:00",191.00575319999999,4.6910400000000001]
["2024-03-24T13:25:00","2024-03-24T13:30:00",189.43687439999999,4.0905288000000004]
["2024-03-24T13:30:00","2024-03-24T13:35:00",189.2126988,3.4104719999999999]
["2024-03-24T13:35:00","2024-03-24T13:40:00",191.04945000000001,3.5134584000000002]
["2024-03-24T13:40:00","2024-03-24T13:45:00",193.07592840000001,3.8898252000000002]
["2024-03-24T13:45:00","2024-03-24T13:50:00",194.26425359999999,3.4273356000000001]
["2024-03-24T13:50:00","2024-03-24T13:55:00",196.4283624,3.8098139999999998]
["2024-03-24T13:55:00","2024-03-24T14:00:00",201.65367599999999,3.8031564000000002]
["2024-03-24T14:00:00","2024-03-24T14:05:00",204.93482639999999,3.3322512]
["2024-03-24T14:05:00","2024-03-24T14:10:00",206.1235332,3.0405335999999998]
["2024-03-24T14:10:00","2024-03-24T14:15:00",207.1338624,2.3023812000000001]
["2024-03-24T14:15:00","2024-03-24T14:20:00",212.17506839999999,2.4748679999999998]
["2024-03-24T14:20:00","2024-03-24T14:25:00",215.40293159999999,3.7031436000000002]
["2024-03-24T14:25:00","2024-03-24T14:30:00",219.29000160000001,3.2768736000000001]
["2024-03-24T14:30:00","2024-03-24T14:35:00",223.3360596,3.2211599999999998]
["2024-03-24T14:35:00","2024-03-24T14:40:00",228.96410040000001,3.4259976000000001]
["2024-03-24T14:40:00","2024-03-24T14:45:00",233.80963679999999,3.2028072000000001]
["2024-03-24T14:45:00","2024-03-24T14:50:00",236.24396759999999,1.8433728]
["2024-03-24T14:50:00","2024-03-24T14:55:00",241.39377239999999,1.6741248]
["2024-03-24T14:55:00","2024-03-24T15:00:00",246.22862040000001,5.23968E-2]
["2024-03-24T15:00:00","2024-03-24T15:05:00",252.19390920000001,-0.89237759999999999]
["2024-03-24T15:05:00","2024-03-24T15:10:00",255.57534720000001,-0.63072240000000002]
["2024-03-24T15:10:00","2024-03-24T15:15:00",261.9639588,-1.1583576]
["2024-03-24T15:15:00","2024-03-24T15:20:00",269.35432200000002,-1.3941372000000001]
["2024-03-24T15:20:00","2024-03-24T15:25:00",274.43756280000002,-1.8298224000000001]
["2024-03-24T15:25:00","2024-03-24T15:30:00",281.38414560000001,-2.1285660000000002]
["2024-03-24T15:30:00","2024-03-24T15:35:00",288.04916159999999,-1.4606664]
["2024-03-24T15:35:00","2024-03-24T15:40:00",295.10371679999997,-1.3857444000000001]
["2024-03-24T15:40:00","2024-03-24T15:45:00",302.06413079999999,-2.2274124]
["2024-03-24T15:45:00","2024-03-24T15:50:00",309.98436479999998,-1.6437396]
["2024-03-24T15:50:00","2024-03-24T15:55:00",314.00391480000002,-3.7532711999999999]
["2024-03-24T15:55:00","2024-03-24T16:00:00",322.38117119999998,-4.4742731999999998]
["2024-03-24T16:00:00","2024-03-24T16:05:00",329.38589400000001,-3.6789480000000001]
["2024-03-24T16:05:00","2024-03-24T16:10:00",335.11338599999999,-2.9012783999999998]
["2024-03-24T16:10:00","2024-03-24T16:15:00",341.64673320000003,-3.9925272000000001]
["2024-03-24T16:15:00","2024-03-24T16:20:00",349.61576639999998,-4.9494803999999997]
["2024-03-24T16:20:00","2024-03-24T16:25:00",355.70989680000002,-4.0167827999999997]
["2024-03-24T16:25:00","2024-03-24T16:30:00",362.13601560000001,-4.6278180000000004]
["2024-03-24T16:30:00","2024-03-24T16:35:00",369.46552439999999,-4.1780448000000003]
["2024-03-24T16:35:00","2024-03-24T16:40:00",377.01200039999998,-4.9928831999999996]
["2024-03-24T16:40:00","2024-03-24T16:45:00",386.5922592,-4.2875220000000001]
["2024-03-24T16:45:00","2024-03-24T16:50:00",393.00762600000002,-4.1365163999999996]
["2024-03-24T16:50:00","2024-03-24T16:55:00",399.2547816,-5.0666159999999998]
["2024-03-24T16:55:00","2024-03-24T17:00:00",406.687434,-4.8249684000000004]
["2024-03-24T17:00:00","2024-03-24T17:05:00",413.37661439999999,-5.0258267999999999]
["2024-03-24T17:05:00","2024-03-24T17:10:00",419.81898719999998,-4.6287419999999999]
["2024-03-24T17:10:00","2024-03-24T17:15:00",425.36992320000002,-5.1120815999999998]
["2024-03-24T17:15:00","2024-03-24T17:20:00",433.63756319999999,-4.8881148000000003]
["2024-03-24T17:20:00","2024-03-24T17:25:00",440.86760040000001,-4.8382056000000002]
["2024-03-24T17:25:00","2024-03-24T17:30:00",444.99684000000002,-5.1819936000000002]
["2024-03-24T17:30:00","2024-03-24T17:35:00",449.42055479999999,-6.0934163999999997]
["2024-03-24T17:35:00","2024-03-24T17:40:00",454.57440359999998,-6.2407728000000002]
["2024-03-24T17:40:00","2024-03-24T17:45:00",460.535304,-6.8997827999999997]
["2024-03-24T17:45:00","2024-03-24T17:50:00",464.07780480000002,-6.1873487999999996]
["2024-03-24T17:50:00","2024-03-24T17:55:00",467.3223648,-6.0573275999999998]
["2024-03-24T17:55:00","2024-03-24T18:00:00",470.99894760000001,-6.3080363999999998]
["2024-03-24T18:00:00","2024-03-24T18:05:00",474.00160440000002,-5.8868495999999997]
["2024-03-24T18:05:00","2024-03-24T18:10:00",477.17492879999998,-5.0715396000000004]
["2024-03-24T18:10:00","2024-03-24T18:15:00",477.30412799999999,-5.8599924000000003]
["2024-03-24T18:15:00","2024-03-24T18:20:00",480.42031680000002,-5.2245612000000001]
["2024-03-24T18:20:00","2024-03-24T18:25:00",479.85563999999999,-6.3366119999999997]
["2024-03-24T18:25:00","2024-03-24T18:30:00",479.03273639999998,-7.6321475999999997]
["2024-03-24T18:30:00","2024-03-24T18:35:00",477.19800600000002,-8.1434028000000005]
["2024-03-24T18:35:00","2024-03-24T18:40:00",478.4746404,-7.530786]
["2024-03-24T18:40:00","2024-03-24T18:45:00",481.21749840000001,-6.0758939999999999]
["2024-03-24T18:45:00","2024-03-24T18:50:00",484.89884280000001,-4.4937756000000002]
["2024-03-24T18:50:00","2024-03-24T18:55:00",484.4360772,-3.8876232000000002]
["2024-03-24T18:55:00","2024-03-24T19:00:00",484.89203279999998,-4.2195144000000004]
["2024-03-24T19:00:00","2024-03-24T19:05:00",484.26508439999998,-4.8118356000000002]
["2024-03-24T19:05:00","2024-03-24T19:10:00",483.50724000000002,-4.8776532000000001]
["2024-03-24T19:10:00","2024-03-24T19:15:00",481.17761639999998,-5.7762216000000004]
["2024-03-24T19:15:00","2024-03-24T19:20:00",480.17601719999999,-5.9097059999999999]
["2024-03-24T19:20:00","2024-03-24T19:25:00",477.9554364,-6.7250112]
["2024-03-24T19:25:00","2024-03-24T19:30:00",475.51350480000002,-8.0948688000000004]
["2024-03-24T19:30:00","2024-03-24T19:35:00",474.72921120000001,-7.8680892]
["2024-03-24T19:35:00","2024-03-24T19:40:00",472.37949839999999,-8.5128348000000003]
["2024-03-24T19:40:00","2024-03-24T19:45:00",471.32326440000003,-8.7761171999999998]
["2024-03-24T19:45:00","2024-03-24T19:50:00",470.22101040000001,-9.6248027999999994]
["2024-03-24T19:50:00","2024-03-24T19:55:00",466.59584039999999,-10.6633692]
["2024-03-24T19:55:00","2024-03-24T20:00:00",463.863204,-11.6079288]
["2024-03-24T20:00:00","2024-03-24T20:05:00",462.72437159999998,-11.3750868]
["2024-03-24T20:05:00","2024-03-24T20:10:00",462.8255388,-10.7458188]
["2024-03-24T20:10:00","2024-03-24T20:15:00",459.272694,-12.666451199999999]
["2024-03-24T20:15:00","2024-03-24T20:20:00",458.86038000000002,-12.242324399999999]
["2024-03-24T20:20:00","2024-03-24T20:25:00",453.95254560000001,-13.661365200000001]
["2024-03-24T20:25:00","2024-03-24T20:30:00",451.26038160000002,-13.514340000000001]
["2024-03-24T20:30:00","2024-03-24T20:35:00",445.912194,-15.3800484]
["2024-03-24T20:35:00","2024-03-24T20:40:00",445.4613804,-14.775384000000001]
["2024-03-24T20:40:00","2024-03-24T20:45:00",442.99323959999998,-16.345381199999999]
["2024-03-24T20:45:00","2024-03-24T20:50:00",440.79360600000001,-16.993840800000001]
["2024-03-24T20:50:00","2024-03-24T20:55:00",438.44688839999998,-17.462309999999999]
["2024-03-24T20:55:00","2024-03-24T21:00:00",435.3852612,-17.545466399999999]
["2024-03-24T21:00:00","2024-03-24T21:05:00",432.42905400000001,-17.610588]
["2024-03-24T21:05:00","2024-03-24T21:10:00",431.07508080000002,-17.861932800000002]
["2024-03-24T21:10:00","2024-03-24T21:15:00",427.74887159999997,-18.969480000000001]
["2024-03-24T21:15:00","2024-03-24T21:20:00",425.36531760000003,-18.7991052]
["2024-03-24T21:20:00","2024-03-24T21:25:00",420.68110560000002,-19.873404000000001]
["2024-03-24T21:25:00","2024-03-24T21:30:00",418.83925440000002,-20.160798]
["2024-03-24T21:30:00","2024-03-24T21:35:00",415.30499520000001,-20.303486400000001]
["2024-03-24T21:35:00","2024-03-24T21:40:00",413.42499359999999,-20.902264800000001]
["2024-03-24T21:40:00","2024-03-24T21:45:00",411.4111092,-20.6508048]
["2024-03-24T21:45:00","2024-03-24T21:50:00",407.9825232,-21.309285599999999]
["2024-03-24T21:50:00","2024-03-24T21:55:00",404.30660160000002,-22.066770000000002]
["2024-03-24T21:55:00","2024-03-24T22:00:00",400.45378440000002,-22.6900452]
["2024-03-24T22:00:00","2024-03-24T22:05:00",397.8870048,-23.109648]
["2024-03-24T22:05:00","2024-03-24T22:10:00",397.25700719999998,-22.848918000000001]
["2024-03-24T22:10:00","2024-03-24T22:15:00",395.44731239999999,-23.5664868]
["2024-03-24T22:15:00","2024-03-24T22:20:00",394.859376,-22.167711600000001]
["2024-03-24T22:20:00","2024-03-24T22:25:00",391.22844479999998,-23.377605599999999]
["2024-03-24T22:25:00","2024-03-24T22:30:00",389.13462240000001,-23.548363200000001]
["2024-03-24T22:30:00","2024-03-24T22:35:00",387.30302399999999,-23.798734799999998]
["2024-03-24T22:35:00","2024-03-24T22:40:00",386.82418919999998,-22.8664296]
["2024-03-24T22:40:00","2024-03-24T22:45:00",384.60063359999998,-23.414231999999998]
["2024-03-24T22:45:00","2024-03-24T22:50:00",379.14482520000001,-25.170187200000001]
["2024-03-24T22:50:00","2024-03-24T22:55:00",377.1890616,-25.721945999999999]
["2024-03-24T22:55:00","2024-03-24T23:00:00",374.31767760000002,-26.6434368]
["2024-03-24T23:00:00","2024-03-24T23:05:00",380.42215440000001,-26.679412800000001]
["2024-03-24T23:05:00","2024-03-24T23:10:00",391.06049280000002,-25.518445199999999]
["2024-03-24T23:10:00","2024-03-24T23:15:00",397.290864,-23.884617599999999]
["2024-03-24T23:15:00","2024-03-24T23:20:00",395.13386279999997,-24.450532800000001]
["2024-03-24T23:20:00","2024-03-24T23:25:00",393.21617279999998,-25.2366636]
["2024-03-24T23:25:00","2024-03-24T23:30:00",390.07797119999998,-24.706697999999999]
["2024-03-24T23:30:00","2024-03-24T23:35:00",387.71357519999998,-24.499906800000002]
["2024-03-24T23:35:00","2024-03-24T23:40:00",385.78416479999999,-25.569188400000002]
["2024-03-24T23:40:00","2024-03-24T23:45:00",383.23964280000001,-26.741696399999999]
["2024-03-24T23:45:00","2024-03-24T23:50:00",379.66046999999998,-26.703808800000001]
["2024-03-24T23:50:00","2024-03-24T23:55:00",377.0000268,-27.168327600000001]
["2024-03-24T23:55:00",45376,374.05480920000002,-27.254256000000002]
[45376,"2024-03-25T00:05:00",370.78562640000001,-27.9467316]
["2024-03-25T00:05:00","2024-03-25T00:10:00",368.80816199999998,-27.980932800000001]
["2024-03-25T00:10:00","2024-03-25T00:15:00",367.40218679999998,-28.062608399999998]
["2024-03-25T00:15:00","2024-03-25T00:20:00",364.94223720000002,-28.484580000000001]
["2024-03-25T00:20:00","2024-03-25T00:25:00",361.7267592,-29.097702000000002]
["2024-03-25T00:25:00","2024-03-25T00:30:00",360.03240479999999,-28.5547872]
["2024-03-25T00:30:00","2024-03-25T00:35:00",358.90990799999997,-29.5156536]
["2024-03-25T00:35:00","2024-03-25T00:40:00",357.53476080000002,-29.626362]
["2024-03-25T00:40:00","2024-03-25T00:45:00",354.68785800000001,-30.0862704]
["2024-03-25T00:45:00","2024-03-25T00:50:00",353.88550559999999,-29.493795599999999]
["2024-03-25T00:50:00","2024-03-25T00:55:00",353.32699439999999,-29.285012399999999]
["2024-03-25T00:55:00","2024-03-25T01:00:00",352.7535456,-29.7446412]
["2024-03-25T01:00:00","2024-03-25T01:05:00",351.82926959999998,-30.201072]
["2024-03-25T01:05:00","2024-03-25T01:10:00",350.93600520000001,-30.508209600000001]
["2024-03-25T01:10:00","2024-03-25T01:15:00",349.47910200000001,-31.266758400000001]
["2024-03-25T01:15:00","2024-03-25T01:20:00",348.34876200000002,-31.112711999999998]
["2024-03-25T01:20:00","2024-03-25T01:25:00",347.73159720000001,-31.348537199999999]
["2024-03-25T01:25:00","2024-03-25T01:30:00",345.6613524,-31.407559200000001]
["2024-03-25T01:30:00","2024-03-25T01:35:00",344.669916,-32.031182399999999]
["2024-03-25T01:35:00","2024-03-25T01:40:00",343.99383239999997,-32.114474399999999]
["2024-03-25T01:40:00","2024-03-25T01:45:00",343.76066880000002,-32.1166944]
["2024-03-25T01:45:00","2024-03-25T01:50:00",341.74546559999999,-32.990324399999999]
["2024-03-25T01:50:00","2024-03-25T01:55:00",341.1301464,-33.324843600000001]
["2024-03-25T01:55:00","2024-03-25T02:00:00",340.70619720000002,-33.0988392]
["2024-03-25T02:00:00","2024-03-25T02:05:00",341.09465280000001,-33.448083599999997]
["2024-03-25T02:05:00","2024-03-25T02:10:00",342.39704760000001,-32.647109999999998]
["2024-03-25T02:10:00","2024-03-25T02:15:00",342.949884,-32.722296]
["2024-03-25T02:15:00","2024-03-25T02:20:00",343.65663480000001,-31.661231999999998]
["2024-03-25T02:20:00","2024-03-25T02:25:00",344.81028240000001,-31.2714888]
["2024-03-25T02:25:00","2024-03-25T02:30:00",345.09350039999998,-32.141534399999998]
["2024-03-25T02:30:00","2024-03-25T02:35:00",344.95294080000002,-31.060682400000001]
["2024-03-25T02:35:00","2024-03-25T02:40:00",344.74072919999998,-31.023871199999999]
["2024-03-25T02:40:00","2024-03-25T02:45:00",344.62360919999998,-31.0537548]
["2024-03-25T02:45:00","2024-03-25T02:50:00",345.28386360000002,-31.3561692]
["2024-03-25T02:50:00","2024-03-25T02:55:00",344.49066599999998,-31.6331676]
["2024-03-25T02:55:00","2024-03-25T03:00:00",346.06097999999997,-31.003941600000001]
["2024-03-25T03:00:00","2024-03-25T03:05:00",346.67369880000001,-30.655168799999998]
["2024-03-25T03:05:00","2024-03-25T03:10:00",347.60555160000001,-30.377936399999999]
["2024-03-25T03:10:00","2024-03-25T03:15:00",347.44519079999998,-30.790094400000001]
["2024-03-25T03:15:00","2024-03-25T03:20:00",349.63737359999999,-30.397081199999999]
["2024-03-25T03:20:00","2024-03-25T03:25:00",350.25691319999999,-30.335864399999998]
["2024-03-25T03:25:00","2024-03-25T03:30:00",351.62394119999999,-30.0245724]
["2024-03-25T03:30:00","2024-03-25T03:35:00",353.01090360000001,-30.181676400000001]
["2024-03-25T03:35:00","2024-03-25T03:40:00",358.62828359999997,-28.148241599999999]
["2024-03-25T03:40:00","2024-03-25T03:45:00",358.69471440000001,-27.7692324]
["2024-03-25T03:45:00","2024-03-25T03:50:00",361.02711959999999,-27.2574012]
["2024-03-25T03:50:00","2024-03-25T03:55:00",361.14708239999999,-27.154788]
["2024-03-25T03:55:00","2024-03-25T04:00:00",363.5743008,-26.8916112]
["2024-03-25T04:00:00","2024-03-25T04:05:00",370.93412760000001,-25.2888804]
["2024-03-25T04:05:00","2024-03-25T04:10:00",375.12530400000003,-24.582614400000001]
["2024-03-25T04:10:00","2024-03-25T04:15:00",378.08450399999998,-23.797004399999999]
["2024-03-25T04:15:00","2024-03-25T04:20:00",383.1474432,-21.731068799999999]
["2024-03-25T04:20:00","2024-03-25T04:25:00",385.91281199999997,-21.003460799999999]
["2024-03-25T04:25:00","2024-03-25T04:30:00",385.62031560000003,-21.575401200000002]
["2024-03-25T04:30:00","2024-03-25T04:35:00",388.82046000000003,-20.2733004]
["2024-03-25T04:35:00","2024-03-25T04:40:00",396.24855480000002,-18.539192400000001]
["2024-03-25T04:40:00","2024-03-25T04:45:00",402.33517920000003,-15.9113436]
["2024-03-25T04:45:00","2024-03-25T04:50:00",407.25014279999999,-13.5975012]
["2024-03-25T04:50:00","2024-03-25T04:55:00",409.69296960000003,-11.9102052]
["2024-03-25T04:55:00","2024-03-25T05:00:00",416.76147600000002,-9.9056820000000005]
["2024-03-25T05:00:00","2024-03-25T05:05:00",427.86065159999998,-5.4340320000000002]
["2024-03-25T05:05:00","2024-03-25T05:10:00",433.55175960000003,-3.0686976000000001]
["2024-03-25T05:10:00","2024-03-25T05:15:00",438.83580119999999,-0.84289199999999997]
["2024-03-25T05:15:00","2024-03-25T05:20:00",445.07553480000001,0.96710399999999996]
["2024-03-25T05:20:00","2024-03-25T05:25:00",450.070176,3.0536088000000001]
["2024-03-25T05:25:00","2024-03-25T05:30:00",455.46627000000001,6.23874]
["2024-03-25T05:30:00","2024-03-25T05:35:00",461.75548199999997,9.0429732000000005]
["2024-03-25T05:35:00","2024-03-25T05:40:00",469.09416479999999,11.4181116]
["2024-03-25T05:40:00","2024-03-25T05:45:00",474.67463759999998,13.281223199999999]
["2024-03-25T05:45:00","2024-03-25T05:50:00",480.03802919999998,14.9942244]
["2024-03-25T05:50:00","2024-03-25T05:55:00",487.81110840000002,18.863009999999999]
["2024-03-25T05:55:00","2024-03-25T06:00:00",498.38324039999998,22.9066188]
["2024-03-25T06:00:00","2024-03-25T06:05:00",508.76933880000001,26.8988616]
["2024-03-25T06:05:00","2024-03-25T06:10:00",519.8419308,32.904421200000002]
["2024-03-25T06:10:00","2024-03-25T06:15:00",528.29859720000002,35.020643999999997]
["2024-03-25T06:15:00","2024-03-25T06:20:00",531.58429679999995,35.895511200000001]
["2024-03-25T06:20:00","2024-03-25T06:25:00",533.76772319999998,36.379208400000003]
["2024-03-25T06:25:00","2024-03-25T06:30:00",535.3448052,37.476261600000001]
["2024-03-25T06:30:00","2024-03-25T06:35:00",538.6824828,38.953754400000001]
["2024-03-25T06:35:00","2024-03-25T06:40:00",545.90699040000004,41.859780000000001]
["2024-03-25T06:40:00","2024-03-25T06:45:00",549.04084560000001,44.315221200000003]
["2024-03-25T06:45:00","2024-03-25T06:50:00",547.70778959999996,44.174967600000002]
["2024-03-25T06:50:00","2024-03-25T06:55:00",545.30766000000006,44.243001599999999]
["2024-03-25T06:55:00","2024-03-25T07:00:00",544.96948320000001,43.9352448]
["2024-03-25T07:00:00","2024-03-25T07:05:00",542.19882719999998,44.333953200000003]
["2024-03-25T07:05:00","2024-03-25T07:10:00",543.24705840000001,46.954056000000001]
["2024-03-25T07:10:00","2024-03-25T07:15:00",540.69592439999997,47.940775199999997]
["2024-03-25T07:15:00","2024-03-25T07:20:00",534.93210239999996,47.576553599999997]
["2024-03-25T07:20:00","2024-03-25T07:25:00",533.04365399999995,48.793825200000001]
["2024-03-25T07:25:00","2024-03-25T07:30:00",527.66591759999994,48.772218000000002]
["2024-03-25T07:30:00","2024-03-25T07:35:00",522.84281039999996,49.1867904]
["2024-03-25T07:35:00","2024-03-25T07:40:00",517.34669159999999,48.832780800000002]
["2024-03-25T07:40:00","2024-03-25T07:45:00",511.93979519999999,48.282276000000003]
["2024-03-25T07:45:00","2024-03-25T07:50:00",509.22002639999999,49.975610400000001]
["2024-03-25T07:50:00","2024-03-25T07:55:00",500.90890919999998,49.909366800000001]
["2024-03-25T07:55:00","2024-03-25T08:00:00",497.58036120000003,50.7795372]
["2024-03-25T08:00:00","2024-03-25T08:05:00",496.10964480000001,52.351166399999997]
["2024-03-25T08:05:00","2024-03-25T08:10:00",492.22935239999998,51.366022800000003]
["2024-03-25T08:10:00","2024-03-25T08:15:00",483.45364560000002,49.753749599999999]
["2024-03-25T08:15:00","2024-03-25T08:20:00",481.16867400000001,51.592574399999997]
["2024-03-25T08:20:00","2024-03-25T08:25:00",475.62427079999998,52.648879200000003]
["2024-03-25T08:25:00","2024-03-25T08:30:00",474.5067588,54.454555200000001]
["2024-03-25T08:30:00","2024-03-25T08:35:00",463.45554479999998,52.342236]
["2024-03-25T08:35:00","2024-03-25T08:40:00",462.81032399999998,53.948469600000003]
["2024-03-25T08:40:00","2024-03-25T08:45:00",459.34562879999999,55.706900400000002]
["2024-03-25T08:45:00","2024-03-25T08:50:00",456.19537079999998,56.360802]
["2024-03-25T08:50:00","2024-03-25T08:55:00",447.60761400000001,55.394068799999999]
["2024-03-25T08:55:00","2024-03-25T09:00:00",442.75661639999998,54.135322799999997]
["2024-03-25T09:00:00","2024-03-25T09:05:00",437.2902588,54.036467999999999]
["2024-03-25T09:05:00","2024-03-25T09:10:00",432.66136920000002,55.758203999999999]
["2024-03-25T09:10:00","2024-03-25T09:15:00",427.8251904,56.152017600000001]
["2024-03-25T09:15:00","2024-03-25T09:20:00",425.7834732,57.476489999999998]
["2024-03-25T09:20:00","2024-03-25T09:25:00",421.38869879999999,58.094998799999999]
["2024-03-25T09:25:00","2024-03-25T09:30:00",418.28308199999998,59.933497199999998]
["2024-03-25T09:30:00","2024-03-25T09:35:00",411.16895640000001,62.536920000000002]
["2024-03-25T09:35:00","2024-03-25T09:40:00",406.19261760000001,63.256994400000004]
["2024-03-25T09:40:00","2024-03-25T09:45:00",400.71733560000001,63.854780400000003]
["2024-03-25T09:45:00","2024-03-25T09:50:00",395.5438848,64.362016800000006]
["2024-03-25T09:50:00","2024-03-25T09:55:00",387.1651584,59.442350400000002]
["2024-03-25T09:55:00","2024-03-25T10:00:00",386.46447599999999,59.3165172]
["2024-03-25T10:00:00","2024-03-25T10:05:00",384.01378560000001,59.678226000000002]
["2024-03-25T10:05:00","2024-03-25T10:10:00",382.40490720000003,60.958729200000001]
["2024-03-25T10:10:00","2024-03-25T10:15:00",381.88397759999998,60.472403999999997]
["2024-03-25T10:15:00","2024-03-25T10:20:00",377.40702959999999,62.373867599999997]
["2024-03-25T10:20:00","2024-03-25T10:25:00",373.91824439999999,63.711938400000001]
["2024-03-25T10:25:00","2024-03-25T10:30:00",368.14195439999997,64.213281600000002]
["2024-03-25T10:30:00","2024-03-25T10:35:00",364.60140000000001,63.644512800000001]
["2024-03-25T10:35:00","2024-03-25T10:40:00",361.4706888,65.091196800000006]
["2024-03-25T10:40:00","2024-03-25T10:45:00",357.3752088,66.148180800000006]
["2024-03-25T10:45:00","2024-03-25T10:50:00",354.55424399999998,65.3918496]
["2024-03-25T10:50:00","2024-03-25T10:55:00",348.39411719999998,65.215657199999995]
["2024-03-25T10:55:00","2024-03-25T11:00:00",349.85629080000001,65.786533199999994]
["2024-03-25T11:00:00","2024-03-25T11:05:00",347.05315439999998,65.329809600000004]
["2024-03-25T11:05:00","2024-03-25T11:10:00",345.24201840000001,65.971776000000006]
["2024-03-25T11:10:00","2024-03-25T11:15:00",345.01426199999997,68.341867199999996]
["2024-03-25T11:15:00","2024-03-25T11:20:00",340.25276880000001,67.384275599999995]
["2024-03-25T11:20:00","2024-03-25T11:25:00",341.15826479999998,68.323959599999995]
["2024-03-25T11:25:00","2024-03-25T11:30:00",337.44320640000001,67.339644000000007]
["2024-03-25T11:30:00","2024-03-25T11:35:00",335.77562039999998,67.999515599999995]
["2024-03-25T11:35:00","2024-03-25T11:40:00",334.24782599999998,70.008259199999998]
["2024-03-25T11:40:00","2024-03-25T11:45:00",329.11322159999997,70.146339600000005]
["2024-03-25T11:45:00","2024-03-25T11:50:00",328.71192719999999,70.841833199999996]
["2024-03-25T11:50:00","2024-03-25T11:55:00",326.85610079999998,71.097550799999993]
["2024-03-25T11:55:00","2024-03-25T12:00:00",323.85202679999998,71.063703599999997]
["2024-03-25T12:00:00","2024-03-25T12:05:00",321.3445428,70.875125999999995]
["2024-03-25T12:05:00","2024-03-25T12:10:00",319.13756160000003,70.931668799999997]
["2024-03-25T12:10:00","2024-03-25T12:15:00",318.91157279999999,72.049732800000001]
["2024-03-25T12:15:00","2024-03-25T12:20:00",323.79360359999998,72.049154400000006]
["2024-03-25T12:20:00","2024-03-25T12:25:00",323.83534680000002,72.512208000000001]
["2024-03-25T12:25:00","2024-03-25T12:30:00",321.24353280000003,74.369275200000004]
["2024-03-25T12:30:00","2024-03-25T12:35:00",322.71174359999998,75.32226]
["2024-03-25T12:35:00","2024-03-25T12:40:00",323.21029199999998,75.175864799999999]
["2024-03-25T12:40:00","2024-03-25T12:45:00",325.02480960000003,75.984014400000007]
["2024-03-25T12:45:00","2024-03-25T12:50:00",324.5287932,79.533620400000004]
["2024-03-25T12:50:00","2024-03-25T12:55:00",321.70024560000002,80.864546399999995]
["2024-03-25T12:55:00","2024-03-25T13:00:00",323.79689880000001,80.481179999999995]
["2024-03-25T13:00:00","2024-03-25T13:05:00",328.19976600000001,80.164426800000001]
["2024-03-25T13:05:00","2024-03-25T13:10:00",328.76326920000002,80.686497599999996]
["2024-03-25T13:10:00","2024-03-25T13:15:00",328.77712079999998,81.688233600000004]
["2024-03-25T13:15:00","2024-03-25T13:20:00",329.98827840000001,81.626064]
["2024-03-25T13:20:00","2024-03-25T13:25:00",330.40099079999999,80.643360000000001]
["2024-03-25T13:25:00","2024-03-25T13:30:00",330.68196599999999,80.185383599999994]
["2024-03-25T13:30:00","2024-03-25T13:35:00",332.68812839999998,79.683529199999995]
["2024-03-25T13:35:00","2024-03-25T13:40:00",334.26960600000001,79.608894000000006]
["2024-03-25T13:40:00","2024-03-25T13:45:00",336.95328239999998,79.749474000000006]
["2024-03-25T13:45:00","2024-03-25T13:50:00",335.9896056,78.716686800000005]
["2024-03-25T13:50:00","2024-03-25T13:55:00",336.6709548,78.206421599999999]
["2024-03-25T13:55:00","2024-03-25T14:00:00",339.84998760000002,77.1916224]
["2024-03-25T14:00:00","2024-03-25T14:05:00",343.79556239999999,77.604394799999994]
["2024-03-25T14:05:00","2024-03-25T14:10:00",344.53668479999999,78.054481199999998]
["2024-03-25T14:10:00","2024-03-25T14:15:00",344.40071039999998,77.454355199999995]
["2024-03-25T14:15:00","2024-03-25T14:20:00",346.80686400000002,76.181877600000007]
["2024-03-25T14:20:00","2024-03-25T14:25:00",353.40390000000002,75.652132800000004]
["2024-03-25T14:25:00","2024-03-25T14:30:00",355.94829959999998,74.868390000000005]
["2024-03-25T14:30:00","2024-03-25T14:35:00",355.8576936,74.355691199999995]
["2024-03-25T14:35:00","2024-03-25T14:40:00",361.12307759999999,72.822040799999996]
["2024-03-25T14:40:00","2024-03-25T14:45:00",365.0802516,73.308746400000004]
["2024-03-25T14:45:00","2024-03-25T14:50:00",370.91686559999999,72.724657199999996]
["2024-03-25T14:50:00","2024-03-25T14:55:00",375.23777280000002,72.351731999999998]
["2024-03-25T14:55:00","2024-03-25T15:00:00",381.6023376,71.543666400000006]
["2024-03-25T15:00:00","2024-03-25T15:05:00",386.30258880000002,71.004260400000007]
["2024-03-25T15:05:00","2024-03-25T15:10:00",390.45675360000001,70.096030799999994]
["2024-03-25T15:10:00","2024-03-25T15:15:00",392.63439959999999,67.822390799999994]
["2024-03-25T15:15:00","2024-03-25T15:20:00",399.02321760000001,66.508291200000002]
["2024-03-25T15:20:00","2024-03-25T15:25:00",405.27724799999999,65.480455199999994]
["2024-03-25T15:25:00","2024-03-25T15:30:00",411.08077800000001,65.645163600000004]
["2024-03-25T15:30:00","2024-03-25T15:35:00",410.86762679999998,62.344974000000001]
["2024-03-25T15:35:00","2024-03-25T15:40:00",418.29357479999999,60.823069199999999]
["2024-03-25T15:40:00","2024-03-25T15:45:00",422.25004680000001,59.128341599999999]
["2024-03-25T15:45:00","2024-03-25T15:50:00",427.8319932,59.569370399999997]
["2024-03-25T15:50:00","2024-03-25T15:55:00",435.33969239999999,60.019999200000001]
["2024-03-25T15:55:00","2024-03-25T16:00:00",444.86902559999999,60.110043599999997]
["2024-03-25T16:00:00","2024-03-25T16:05:00",452.35575119999999,59.464360800000001]
["2024-03-25T16:05:00","2024-03-25T16:10:00",457.95945360000002,62.479725600000002]
["2024-03-25T16:10:00","2024-03-25T16:15:00",461.2412448,60.986522399999998]
["2024-03-25T16:15:00","2024-03-25T16:20:00",473.07958200000002,61.412483999999999]
["2024-03-25T16:20:00","2024-03-25T16:25:00",479.09824800000001,59.72316]
["2024-03-25T16:25:00","2024-03-25T16:30:00",485.4231456,58.614787200000002]
["2024-03-25T16:30:00","2024-03-25T16:35:00",491.32558080000001,58.499856000000001]
["2024-03-25T16:35:00","2024-03-25T16:40:00",499.24053959999998,58.603482]
["2024-03-25T16:40:00","2024-03-25T16:45:00",501.66381719999998,57.040992000000003]
["2024-03-25T16:45:00","2024-03-25T16:50:00",508.09015199999999,56.769208800000001]
["2024-03-25T16:50:00","2024-03-25T16:55:00",514.15632960000005,56.7342972]
["2024-03-25T16:55:00","2024-03-25T17:00:00",518.43452400000001,54.420656399999999]
["2024-03-25T17:00:00","2024-03-25T17:05:00",518.34065880000003,50.051913599999999]
["2024-03-25T17:05:00","2024-03-25T17:10:00",525.73563720000004,49.436917200000003]
["2024-03-25T17:10:00","2024-03-25T17:15:00",529.05459959999996,48.502972800000002]
["2024-03-25T17:15:00","2024-03-25T17:20:00",537.2190276,48.874955999999997]
["2024-03-25T17:20:00","2024-03-25T17:25:00",541.16627400000004,47.590944]
["2024-03-25T17:25:00","2024-03-25T17:30:00",544.35815160000004,46.010891999999998]
["2024-03-25T17:30:00","2024-03-25T17:35:00",547.80052320000004,46.452995999999999]
["2024-03-25T17:35:00","2024-03-25T17:40:00",554.34349199999997,46.593401999999998]
["2024-03-25T17:40:00","2024-03-25T17:45:00",556.5616248,45.925887600000003]
["2024-03-25T17:45:00","2024-03-25T17:50:00",558.18000840000002,44.295012]
["2024-03-25T17:50:00","2024-03-25T17:55:00",559.07333879999999,43.273248000000002]
["2024-03-25T17:55:00","2024-03-25T18:00:00",561.36564480000004,41.668025999999998]
["2024-03-25T18:00:00","2024-03-25T18:05:00",561.69191639999997,40.863030000000002]
["2024-03-25T18:05:00","2024-03-25T18:10:00",562.05183959999999,40.497657599999997]
["2024-03-25T18:10:00","2024-03-25T18:15:00",561.00279599999999,38.566600800000003]
["2024-03-25T18:15:00","2024-03-25T18:20:00",565.25974199999996,38.593618800000002]
["2024-03-25T18:20:00","2024-03-25T18:25:00",565.53877199999999,37.0404312]
["2024-03-25T18:25:00","2024-03-25T18:30:00",562.64530560000003,36.460897199999998]
["2024-03-25T18:30:00","2024-03-25T18:35:00",560.79339479999999,35.426530800000002]
["2024-03-25T18:35:00","2024-03-25T18:40:00",558.63690480000002,34.258090799999998]
["2024-03-25T18:40:00","2024-03-25T18:45:00",559.71654360000002,34.744138800000002]
["2024-03-25T18:45:00","2024-03-25T18:50:00",559.90619040000001,34.803086399999998]
["2024-03-25T18:50:00","2024-03-25T18:55:00",558.43597439999996,34.638646799999997]
["2024-03-25T18:55:00","2024-03-25T19:00:00",559.65754919999995,33.818011200000001]
["2024-03-25T19:00:00","2024-03-25T19:05:00",556.0307196,31.991469599999999]
["2024-03-25T19:05:00","2024-03-25T19:10:00",553.80583799999999,31.700552399999999]
["2024-03-25T19:10:00","2024-03-25T19:15:00",550.39270079999994,30.069613199999999]
["2024-03-25T19:15:00","2024-03-25T19:20:00",550.35819839999999,30.4752996]
["2024-03-25T19:20:00","2024-03-25T19:25:00",550.73284560000002,29.819208]
["2024-03-25T19:25:00","2024-03-25T19:30:00",548.04688320000002,29.826239999999999]
["2024-03-25T19:30:00","2024-03-25T19:35:00",544.98971280000001,28.058830799999999]
["2024-03-25T19:35:00","2024-03-25T19:40:00",544.07961120000004,28.072912800000001]
["2024-03-25T19:40:00","2024-03-25T19:45:00",540.67482359999997,26.774847600000001]
["2024-03-25T19:45:00","2024-03-25T19:50:00",536.63198880000004,25.6383084]
["2024-03-25T19:50:00","2024-03-25T19:55:00",532.38782639999999,24.369257999999999]
["2024-03-25T19:55:00","2024-03-25T20:00:00",529.76216639999996,23.8813824]
["2024-03-25T20:00:00","2024-03-25T20:05:00",525.92220239999995,22.013292]
["2024-03-25T20:05:00","2024-03-25T20:10:00",522.98232959999996,20.956177199999999]
["2024-03-25T20:10:00","2024-03-25T20:15:00",521.1911556,19.63626]
["2024-03-25T20:15:00","2024-03-25T20:20:00",518.34282719999999,19.508676000000001]
["2024-03-25T20:20:00","2024-03-25T20:25:00",516.63578399999994,19.515909600000001]
["2024-03-25T20:25:00","2024-03-25T20:30:00",512.80836239999996,18.116192399999999]
["2024-03-25T20:30:00","2024-03-25T20:35:00",509.85239519999999,17.247739200000002]
["2024-03-25T20:35:00","2024-03-25T20:40:00",506.53827960000001,16.4879508]
["2024-03-25T20:40:00","2024-03-25T20:45:00",506.63763719999997,17.785938000000002]
["2024-03-25T20:45:00","2024-03-25T20:50:00",502.66278840000001,16.679167199999998]
["2024-03-25T20:50:00","2024-03-25T20:55:00",496.32139319999999,15.2206428]
["2024-03-25T20:55:00","2024-03-25T21:00:00",492.22815839999998,13.368895200000001]
["2024-03-25T21:00:00","2024-03-25T21:05:00",487.05804000000001,12.3381492]
["2024-03-25T21:05:00","2024-03-25T21:10:00",483.23081639999998,11.8238784]
["2024-03-25T21:10:00","2024-03-25T21:15:00",479.47039319999999,10.312802400000001]
["2024-03-25T21:15:00","2024-03-25T21:20:00",474.97000559999998,8.4121895999999996]
["2024-03-25T21:20:00","2024-03-25T21:25:00",472.34487239999999,8.3843219999999992]
["2024-03-25T21:25:00","2024-03-25T21:30:00",468.47033879999998,7.2598560000000001]
["2024-03-25T21:30:00","2024-03-25T21:35:00",464.31027,5.9245691999999996]
["2024-03-25T21:35:00","2024-03-25T21:40:00",460.20154200000002,4.0416324000000001]
["2024-03-25T21:40:00","2024-03-25T21:45:00",455.84142600000001,1.4135244]
["2024-03-25T21:45:00","2024-03-25T21:50:00",452.79664200000002,0.52766279999999999]
["2024-03-25T21:50:00","2024-03-25T21:55:00",448.84595880000001,2.02332E-2]
["2024-03-25T21:55:00","2024-03-25T22:00:00",444.2316204,-1.4849448000000001]
["2024-03-25T22:00:00","2024-03-25T22:05:00",440.0451228,-2.2668816000000001]
["2024-03-25T22:05:00","2024-03-25T22:10:00",436.9174908,-2.3754719999999998]
["2024-03-25T22:10:00","2024-03-25T22:15:00",435.27163560000002,-2.8924379999999998]
["2024-03-25T22:15:00","2024-03-25T22:20:00",433.50818759999999,-2.8172448000000001]
["2024-03-25T22:20:00","2024-03-25T22:25:00",429.41316719999998,-4.0057271999999999]
["2024-03-25T22:25:00","2024-03-25T22:30:00",426.88624199999998,-4.2595320000000001]
["2024-03-25T22:30:00","2024-03-25T22:35:00",422.8567716,-3.9680772000000002]
["2024-03-25T22:35:00","2024-03-25T22:40:00",419.5004988,-5.3646864000000001]
["2024-03-25T22:40:00","2024-03-25T22:45:00",419.06810639999998,-5.3931372]
["2024-03-25T22:45:00","2024-03-25T22:50:00",417.98799600000001,-5.8158779999999997]
["2024-03-25T22:50:00","2024-03-25T22:55:00",414.67781159999998,-5.7888599999999997]
["2024-03-25T22:55:00","2024-03-25T23:00:00",413.14362720000003,-6.3639276000000002]
["2024-03-25T23:00:00","2024-03-25T23:05:00",416.98996199999999,-6.9634992000000002]
["2024-03-25T23:05:00","2024-03-25T23:10:00",426.9382584,-5.7133127999999997]
["2024-03-25T23:10:00","2024-03-25T23:15:00",433.09593840000002,-4.5154367999999998]
["2024-03-25T23:15:00","2024-03-25T23:20:00",431.89956599999999,-4.4973168000000001]
["2024-03-25T23:20:00","2024-03-25T23:25:00",425.93888520000002,-6.5744303999999998]
["2024-03-25T23:25:00","2024-03-25T23:30:00",421.10029800000001,-7.0990799999999998]
["2024-03-25T23:30:00","2024-03-25T23:35:00",418.61064720000002,-7.4898372000000002]
["2024-03-25T23:35:00","2024-03-25T23:40:00",414.66710879999999,-8.3444135999999993]
["2024-03-25T23:40:00","2024-03-25T23:45:00",412.5843648,-8.9965379999999993]
["2024-03-25T23:45:00","2024-03-25T23:50:00",410.65243679999998,-8.5011455999999992]
["2024-03-25T23:50:00","2024-03-25T23:55:00",405.884568,-9.3313451999999995]
["2024-03-25T23:55:00",45377,401.937522,-10.4688564]
[45377,"2024-03-26T00:05:00",399.67149719999998,-10.5742092]
["2024-03-26T00:05:00","2024-03-26T00:10:00",399.06309599999997,-10.318143600000001]
["2024-03-26T00:10:00","2024-03-26T00:15:00",397.11365760000001,-10.5497616]
["2024-03-26T00:15:00","2024-03-26T00:20:00",393.60160439999999,-11.565583200000001]
["2024-03-26T00:20:00","2024-03-26T00:25:00",391.07974560000002,-11.9877252]
["2024-03-26T00:25:00","2024-03-26T00:30:00",388.8539652,-12.6432792]
["2024-03-26T00:30:00","2024-03-26T00:35:00",386.84113439999999,-13.0682112]
["2024-03-26T00:35:00","2024-03-26T00:40:00",384.48644280000002,-14.0766408]
["2024-03-26T00:40:00","2024-03-26T00:45:00",382.00280759999998,-14.381569199999999]
["2024-03-26T00:45:00","2024-03-26T00:50:00",380.205828,-14.8762296]
["2024-03-26T00:50:00","2024-03-26T00:55:00",378.05754839999997,-15.371823600000001]
["2024-03-26T00:55:00","2024-03-26T01:00:00",375.90764639999998,-15.9540828]
["2024-03-26T01:00:00","2024-03-26T01:05:00",369.19773839999999,-16.7426472]
["2024-03-26T01:05:00","2024-03-26T01:10:00",373.16896680000002,-17.504774399999999]
["2024-03-26T01:10:00","2024-03-26T01:15:00",371.68997999999999,-18.934560000000001]
["2024-03-26T01:15:00","2024-03-26T01:20:00",369.62481000000002,-19.425009599999999]
["2024-03-26T01:20:00","2024-03-26T01:25:00",368.99651519999998,-19.1157936]
["2024-03-26T01:25:00","2024-03-26T01:30:00",367.71263160000001,-19.710822]
["2024-03-26T01:30:00","2024-03-26T01:35:00",367.4686476,-19.515426000000001]
["2024-03-26T01:35:00","2024-03-26T01:40:00",369.2922696,-18.155089199999999]
["2024-03-26T01:40:00","2024-03-26T01:45:00",368.5026312,-18.129631199999999]
["2024-03-26T01:45:00","2024-03-26T01:50:00",367.68371400000001,-17.778852000000001]
["2024-03-26T01:50:00","2024-03-26T01:55:00",366.95947919999998,-17.472466799999999]
["2024-03-26T01:55:00","2024-03-26T02:00:00",365.78229479999999,-18.388701600000001]
["2024-03-26T02:00:00","2024-03-26T02:05:00",367.08035640000003,-17.973637199999999]
["2024-03-26T02:05:00","2024-03-26T02:10:00",365.92831080000002,-18.531769199999999]
["2024-03-26T02:10:00","2024-03-26T02:15:00",365.12629079999999,-18.358476]
["2024-03-26T02:15:00","2024-03-26T02:20:00",363.2371392,-19.4292576]
["2024-03-26T02:20:00","2024-03-26T02:25:00",361.95013799999998,-19.197246]
["2024-03-26T02:25:00","2024-03-26T02:30:00",360.79079519999999,-20.001546000000001]
["2024-03-26T02:30:00","2024-03-26T02:35:00",361.91795880000001,-19.561074000000001]
["2024-03-26T02:35:00","2024-03-26T02:40:00",362.262744,-19.396684799999999]
["2024-03-26T02:40:00","2024-03-26T02:45:00",362.59278360000002,-19.863826799999998]
["2024-03-26T02:45:00","2024-03-26T02:50:00",361.84189800000001,-20.561420399999999]
["2024-03-26T02:50:00","2024-03-26T02:55:00",363.79969679999999,-19.694901600000001]
["2024-03-26T02:55:00","2024-03-26T03:00:00",364.53676439999998,-18.572724000000001]
["2024-03-26T03:00:00","2024-03-26T03:05:00",364.66534680000001,-17.830147199999999]
["2024-03-26T03:05:00","2024-03-26T03:10:00",365.22072359999999,-17.7160884]
["2024-03-26T03:10:00","2024-03-26T03:15:00",367.54025280000002,-17.604865199999999]
["2024-03-26T03:15:00","2024-03-26T03:20:00",367.68470639999998,-17.0519736]
["2024-03-26T03:20:00","2024-03-26T03:25:00",368.29477919999999,-17.5466172]
["2024-03-26T03:25:00","2024-03-26T03:30:00",369.72891479999998,-16.965418799999998]
["2024-03-26T03:30:00","2024-03-26T03:35:00",371.87930999999998,-16.678237200000002]
["2024-03-26T03:35:00","2024-03-26T03:40:00",374.24797439999998,-16.7225076]
["2024-03-26T03:40:00","2024-03-26T03:45:00",373.97552760000002,-16.725324000000001]
["2024-03-26T03:45:00","2024-03-26T03:50:00",375.82304160000001,-16.162406399999998]
["2024-03-26T03:50:00","2024-03-26T03:55:00",376.8065196,-16.516031999999999]
["2024-03-26T03:55:00","2024-03-26T04:00:00",379.398144,-16.348903199999999]
["2024-03-26T04:00:00","2024-03-26T04:05:00",383.7198204,-14.8453476]
["2024-03-26T04:05:00","2024-03-26T04:10:00",389.0894088,-13.634415600000001]
["2024-03-26T04:10:00","2024-03-26T04:15:00",393.50625359999998,-12.537249600000001]
["2024-03-26T04:15:00","2024-03-26T04:20:00",396.54453119999999,-11.8472904]
["2024-03-26T04:20:00","2024-03-26T04:25:00",399.05609399999997,-11.746491600000001]
["2024-03-26T04:25:00","2024-03-26T04:30:00",401.17282560000001,-10.5237756]
["2024-03-26T04:30:00","2024-03-26T04:35:00",405.19085280000002,-8.7175799999999999]
["2024-03-26T04:35:00","2024-03-26T04:40:00",411.18459960000001,-6.2649803999999998]
["2024-03-26T04:40:00","2024-03-26T04:45:00",413.51292239999998,-5.0183207999999997]
["2024-03-26T04:45:00","2024-03-26T04:50:00",416.30220120000001,-3.5230367999999999]
["2024-03-26T04:50:00","2024-03-26T04:55:00",421.19266800000003,-1.864344]
["2024-03-26T04:55:00","2024-03-26T05:00:00",428.40551879999998,0.27093840000000002]
["2024-03-26T05:00:00","2024-03-26T05:05:00",439.06193280000002,4.8922992000000001]
["2024-03-26T05:05:00","2024-03-26T05:10:00",447.10871279999998,9.7743263999999996]
["2024-03-26T05:10:00","2024-03-26T05:15:00",453.13901040000002,12.903168000000001]
["2024-03-26T05:15:00","2024-03-26T05:20:00",459.59494799999999,13.3467384]
["2024-03-26T05:20:00","2024-03-26T05:25:00",462.98551200000003,15.003280800000001]
["2024-03-26T05:25:00","2024-03-26T05:30:00",468.1413756,17.044213200000002]
["2024-03-26T05:30:00","2024-03-26T05:35:00",472.56470400000001,18.112787999999998]
["2024-03-26T05:35:00","2024-03-26T05:40:00",479.10388440000003,19.562732400000002]
["2024-03-26T05:40:00","2024-03-26T05:45:00",482.64903959999998,20.776767599999999]
["2024-03-26T05:45:00","2024-03-26T05:50:00",485.23310759999998,21.643149600000001]
["2024-03-26T05:50:00","2024-03-26T05:55:00",494.45885399999997,24.521988]
["2024-03-26T05:55:00","2024-03-26T06:00:00",504.33172560000003,28.557302400000001]
["2024-03-26T06:00:00","2024-03-26T06:05:00",513.52001280000002,32.751927600000002]
["2024-03-26T06:05:00","2024-03-26T06:10:00",519.85089479999999,34.876023600000003]
["2024-03-26T06:10:00","2024-03-26T06:15:00",527.57300280000004,38.885498400000003]
["2024-03-26T06:15:00","2024-03-26T06:20:00",532.33929599999999,39.428391599999998]
["2024-03-26T06:20:00","2024-03-26T06:25:00",535.02098639999997,41.081719200000002]
["2024-03-26T06:25:00","2024-03-26T06:30:00",538.8640848,43.862524800000003]
["2024-03-26T06:30:00","2024-03-26T06:35:00",542.98553159999994,45.602705999999998]
["2024-03-26T06:35:00","2024-03-26T06:40:00",546.70585319999998,46.962608400000001]
["2024-03-26T06:40:00","2024-03-26T06:45:00",545.7342744,47.080629600000002]
["2024-03-26T06:45:00","2024-03-26T06:50:00",546.90294119999999,48.1836816]
["2024-03-26T06:50:00","2024-03-26T06:55:00",545.82727799999998,47.824843199999997]
["2024-03-26T06:55:00","2024-03-26T07:00:00",547.51786919999995,49.665545999999999]
["2024-03-26T07:00:00","2024-03-26T07:05:00",542.00602079999999,49.622056800000003]
["2024-03-26T07:05:00","2024-03-26T07:10:00",542.59291919999998,51.159762000000001]
["2024-03-26T07:10:00","2024-03-26T07:15:00",539.45831039999996,51.7423188]
["2024-03-26T07:15:00","2024-03-26T07:20:00",535.91314320000004,51.860056800000002]
["2024-03-26T07:20:00","2024-03-26T07:25:00",531.41974560000006,52.394072399999999]
["2024-03-26T07:25:00","2024-03-26T07:30:00",529.77068640000005,54.431088000000003]
["2024-03-26T07:30:00","2024-03-26T07:35:00",526.38828599999999,55.134528000000003]
["2024-03-26T07:35:00","2024-03-26T07:40:00",522.72527760000003,55.527380399999998]
["2024-03-26T07:40:00","2024-03-26T07:45:00",518.77960199999995,55.022853599999998]
["2024-03-26T07:45:00","2024-03-26T07:50:00",516.12454439999999,54.763944000000002]
["2024-03-26T07:50:00","2024-03-26T07:55:00",516.42789119999998,56.676504000000001]
["2024-03-26T07:55:00","2024-03-26T08:00:00",510.56733480000003,56.548828800000003]
["2024-03-26T08:00:00","2024-03-26T08:05:00",510.33281879999998,57.424389599999998]
["2024-03-26T08:05:00","2024-03-26T08:10:00",513.90781560000005,57.789805200000004]
["2024-03-26T08:10:00","2024-03-26T08:15:00",512.40971279999997,57.414112799999998]
["2024-03-26T08:15:00","2024-03-26T08:20:00",512.91763319999995,57.8912184]
["2024-03-26T08:20:00","2024-03-26T08:25:00",513.88757999999996,59.027815199999999]
["2024-03-26T08:25:00","2024-03-26T08:30:00",511.6510068,58.5528336]
["2024-03-26T08:30:00","2024-03-26T08:35:00",504.93575759999999,57.906174]
["2024-03-26T08:35:00","2024-03-26T08:40:00",499.2883104,58.809846]
["2024-03-26T08:40:00","2024-03-26T08:45:00",496.0947372,59.49729]
["2024-03-26T08:45:00","2024-03-26T08:50:00",492.15179640000002,61.624392]
["2024-03-26T08:50:00","2024-03-26T08:55:00",481.68438959999997,62.604163200000002]
["2024-03-26T08:55:00","2024-03-26T09:00:00",480.09623640000001,62.512897199999998]
["2024-03-26T09:00:00","2024-03-26T09:05:00",472.29158280000001,61.720839599999998]
["2024-03-26T09:05:00","2024-03-26T09:10:00",470.27109239999999,59.889823200000002]
["2024-03-26T09:10:00","2024-03-26T09:15:00",467.39799599999998,55.8891384]
["2024-03-26T09:15:00","2024-03-26T09:20:00",471.27641039999997,56.491362000000002]
["2024-03-26T09:20:00","2024-03-26T09:25:00",470.53125240000003,56.575544399999998]
["2024-03-26T09:25:00","2024-03-26T09:30:00",476.5229736,56.6190432]
["2024-03-26T09:30:00","2024-03-26T09:35:00",481.83012359999998,59.884664399999998]
["2024-03-26T09:35:00","2024-03-26T09:40:00",479.38600079999998,61.362225600000002]
["2024-03-26T09:40:00","2024-03-26T09:45:00",471.84758399999998,63.139334400000003]
["2024-03-26T09:45:00","2024-03-26T09:50:00",468.37555200000003,63.763824]
["2024-03-26T09:50:00","2024-03-26T09:55:00",473.10157320000002,65.115899999999996]
["2024-03-26T09:55:00","2024-03-26T10:00:00",475.45435800000001,65.961749999999995]
["2024-03-26T10:00:00","2024-03-26T10:05:00",488.49828000000002,66.120280800000003]
["2024-03-26T10:05:00","2024-03-26T10:10:00",490.57118159999999,64.187386799999999]
["2024-03-26T10:10:00","2024-03-26T10:15:00",489.20779199999998,64.4516268]
["2024-03-26T10:15:00","2024-03-26T10:20:00",490.78130399999998,63.939487200000002]
["2024-03-26T10:20:00","2024-03-26T10:25:00",484.8475704,64.339206000000004]
["2024-03-26T10:25:00","2024-03-26T10:30:00",473.0988552,65.932970400000002]
["2024-03-26T10:30:00","2024-03-26T10:35:00",475.96577639999998,65.591548799999998]
["2024-03-26T10:35:00","2024-03-26T10:40:00",477.79266360000003,66.954480000000004]
["2024-03-26T10:40:00","2024-03-26T10:45:00",471.6906252,67.577252400000006]
["2024-03-26T10:45:00","2024-03-26T10:50:00",461.50448399999999,66.3310812]
["2024-03-26T10:50:00","2024-03-26T10:55:00",447.34283040000003,65.015069999999994]
["2024-03-26T10:55:00","2024-03-26T11:00:00",436.75779840000001,64.961943599999998]
["2024-03-26T11:00:00","2024-03-26T11:05:00",440.64664199999999,65.090822399999993]
["2024-03-26T11:05:00","2024-03-26T11:10:00",433.57999919999997,61.283782799999997]
["2024-03-26T11:10:00","2024-03-26T11:15:00",427.16905439999999,61.316977199999997]
["2024-03-26T11:15:00","2024-03-26T11:20:00",419.92412999999999,62.780806800000001]
["2024-03-26T11:20:00","2024-03-26T11:25:00",416.64521280000002,64.179871199999994]
["2024-03-26T11:25:00","2024-03-26T11:30:00",416.303472,63.6148764]
["2024-03-26T11:30:00","2024-03-26T11:35:00",413.05418040000001,62.368420800000003]
["2024-03-26T11:35:00","2024-03-26T11:40:00",412.007676,62.662537200000003]
["2024-03-26T11:40:00","2024-03-26T11:45:00",417.055182,64.330935600000004]
["2024-03-26T11:45:00","2024-03-26T11:50:00",407.8149588,64.537810800000003]
["2024-03-26T11:50:00","2024-03-26T11:55:00",400.60701360000002,64.833704400000002]
["2024-03-26T11:55:00","2024-03-26T12:00:00",392.72681879999999,66.044863199999995]
["2024-03-26T12:00:00","2024-03-26T12:05:00",380.98607520000002,69.152824800000005]
["2024-03-26T12:05:00","2024-03-26T12:10:00",366.89129279999997,70.179944399999997]
["2024-03-26T12:10:00","2024-03-26T12:15:00",354.65806079999999,72.119773199999997]
["2024-03-26T12:15:00","2024-03-26T12:20:00",343.15260719999998,73.626163199999993]
["2024-03-26T12:20:00","2024-03-26T12:25:00",330.11477639999998,73.156090800000001]
["2024-03-26T12:25:00","2024-03-26T12:30:00",328.36807920000001,72.955181999999994]
["2024-03-26T12:30:00","2024-03-26T12:35:00",328.79631719999998,73.714386000000005]
["2024-03-26T12:35:00","2024-03-26T12:40:00",336.1971168,73.651437599999994]
["2024-03-26T12:40:00","2024-03-26T12:45:00",344.71596479999999,75.000037199999994]
["2024-03-26T12:45:00","2024-03-26T12:50:00",347.42583359999998,75.114123599999999]
["2024-03-26T12:50:00","2024-03-26T12:55:00",337.6818336,74.447734800000006]
["2024-03-26T12:55:00","2024-03-26T13:00:00",340.34893080000001,74.584364399999998]
["2024-03-26T13:00:00","2024-03-26T13:05:00",338.1953388,75.427958399999994]
["2024-03-26T13:05:00","2024-03-26T13:10:00",338.87660640000001,75.374871600000006]
["2024-03-26T13:10:00","2024-03-26T13:15:00",337.03594079999999,74.747223599999998]
["2024-03-26T13:15:00","2024-03-26T13:20:00",337.41335759999998,75.200386800000004]
["2024-03-26T13:20:00","2024-03-26T13:25:00",332.72614800000002,74.367100800000003]
["2024-03-26T13:25:00","2024-03-26T13:30:00",331.36799639999998,73.407381599999994]
["2024-03-26T13:30:00","2024-03-26T13:35:00",331.09821119999998,74.428299600000003]
["2024-03-26T13:35:00","2024-03-26T13:40:00",334.6935264,74.503765200000004]
["2024-03-26T13:40:00","2024-03-26T13:45:00",333.22071240000002,73.299662400000003]
["2024-03-26T13:45:00","2024-03-26T13:50:00",331.26417240000001,72.104827200000003]
["2024-03-26T13:50:00","2024-03-26T13:55:00",332.285166,71.199310800000006]
["2024-03-26T13:55:00","2024-03-26T14:00:00",334.76673720000002,71.217874800000004]
["2024-03-26T14:00:00","2024-03-26T14:05:00",337.7855232,71.699320799999995]
["2024-03-26T14:05:00","2024-03-26T14:10:00",335.60568599999999,70.5028212]
["2024-03-26T14:10:00","2024-03-26T14:15:00",338.76860520000002,70.574098800000002]
["2024-03-26T14:15:00","2024-03-26T14:20:00",341.34896880000002,71.569160400000001]
["2024-03-26T14:20:00","2024-03-26T14:25:00",345.7895484,72.639721199999997]
["2024-03-26T14:25:00","2024-03-26T14:30:00",347.85354719999998,71.556386399999994]
["2024-03-26T14:30:00","2024-03-26T14:35:00",351.72650040000002,72.151647600000004]
["2024-03-26T14:35:00","2024-03-26T14:40:00",358.04547359999998,72.088914000000003]
["2024-03-26T14:40:00","2024-03-26T14:45:00",363.00820679999998,71.276904000000002]
["2024-03-26T14:45:00","2024-03-26T14:50:00",368.90552400000001,70.166000400000001]
["2024-03-26T14:50:00","2024-03-26T14:55:00",367.46109840000003,68.4083124]
["2024-03-26T14:55:00","2024-03-26T15:00:00",372.61775879999999,68.438355599999994]
["2024-03-26T15:00:00","2024-03-26T15:05:00",377.85590880000001,67.882815600000001]
["2024-03-26T15:05:00","2024-03-26T15:10:00",382.29258240000001,65.977558799999997]
["2024-03-26T15:10:00","2024-03-26T15:15:00",384.93434639999998,65.175686400000004]
["2024-03-26T15:15:00","2024-03-26T15:20:00",390.63829079999999,64.037037600000005]
["2024-03-26T15:20:00","2024-03-26T15:25:00",398.0324124,63.025789199999998]
["2024-03-26T15:25:00","2024-03-26T15:30:00",402.50795160000001,61.470278399999998]
["2024-03-26T15:30:00","2024-03-26T15:35:00",404.88366600000001,60.117668399999999]
["2024-03-26T15:35:00","2024-03-26T15:40:00",413.4577104,59.995958399999999]
["2024-03-26T15:40:00","2024-03-26T15:45:00",418.3387788,58.098805200000001]
["2024-03-26T15:45:00","2024-03-26T15:50:00",422.84517360000001,58.1232732]
["2024-03-26T15:50:00","2024-03-26T15:55:00",424.9238532,55.442101200000003]
["2024-03-26T15:55:00","2024-03-26T16:00:00",434.2316328,55.1972448]
["2024-03-26T16:00:00","2024-03-26T16:05:00",436.622772,53.133176400000004]
["2024-03-26T16:05:00","2024-03-26T16:10:00",440.98644000000002,51.302584799999998]
["2024-03-26T16:10:00","2024-03-26T16:15:00",448.77383880000002,50.242808400000001]
["2024-03-26T16:15:00","2024-03-26T16:20:00",456.00023759999999,49.464207600000002]
["2024-03-26T16:20:00","2024-03-26T16:25:00",462.75671399999999,49.702921199999999]
["2024-03-26T16:25:00","2024-03-26T16:30:00",470.3593596,48.7644588]
["2024-03-26T16:30:00","2024-03-26T16:35:00",474.65479319999997,47.233389600000002]
["2024-03-26T16:35:00","2024-03-26T16:40:00",481.6378752,47.8802412]
["2024-03-26T16:40:00","2024-03-26T16:45:00",486.43888440000001,47.180833200000002]
["2024-03-26T16:45:00","2024-03-26T16:50:00",492.76313399999998,47.640120000000003]
["2024-03-26T16:50:00","2024-03-26T16:55:00",497.40792599999997,46.031971200000001]
["2024-03-26T16:55:00","2024-03-26T17:00:00",502.44374160000001,45.4357872]
["2024-03-26T17:00:00","2024-03-26T17:05:00",505.365228,42.139084799999999]
["2024-03-26T17:05:00","2024-03-26T17:10:00",511.46147639999998,40.400742000000001]
["2024-03-26T17:10:00","2024-03-26T17:15:00",517.30145640000001,40.792324800000003]
["2024-03-26T17:15:00","2024-03-26T17:20:00",521.10126360000004,38.834831999999999]
["2024-03-26T17:20:00","2024-03-26T17:25:00",524.49525960000005,36.408707999999997]
["2024-03-26T17:25:00","2024-03-26T17:30:00",530.83370400000001,36.588022799999997]
["2024-03-26T17:30:00","2024-03-26T17:35:00",535.80942719999996,38.652375599999999]
["2024-03-26T17:35:00","2024-03-26T17:40:00",540.76776359999997,40.500959999999999]
["2024-03-26T17:40:00","2024-03-26T17:45:00",543.78046200000006,41.533311599999998]
["2024-03-26T17:45:00","2024-03-26T17:50:00",546.09016320000001,39.302377200000002]
["2024-03-26T17:50:00","2024-03-26T17:55:00",547.47692759999995,37.634877600000003]
["2024-03-26T17:55:00","2024-03-26T18:00:00",552.04224120000003,37.987604400000002]
["2024-03-26T18:00:00","2024-03-26T18:05:00",552.34723919999999,36.917670000000001]
["2024-03-26T18:05:00","2024-03-26T18:10:00",551.73441720000005,34.577431199999999]
["2024-03-26T18:10:00","2024-03-26T18:15:00",555.36127080000006,34.985348399999999]
["2024-03-26T18:15:00","2024-03-26T18:20:00",559.23999600000002,35.875869600000001]
["2024-03-26T18:20:00","2024-03-26T18:25:00",560.06711040000005,35.674323600000001]
["2024-03-26T18:25:00","2024-03-26T18:30:00",559.32404399999996,35.404113600000002]
["2024-03-26T18:30:00","2024-03-26T18:35:00",554.68061279999995,33.594307200000003]
["2024-03-26T18:35:00","2024-03-26T18:40:00",554.76072959999999,33.835625999999998]
["2024-03-26T18:40:00","2024-03-26T18:45:00",556.85342160000005,33.7160832]
["2024-03-26T18:45:00","2024-03-26T18:50:00",558.23365079999996,33.856924800000002]
["2024-03-26T18:50:00","2024-03-26T18:55:00",557.65375440000003,33.798244799999999]
["2024-03-26T18:55:00","2024-03-26T19:00:00",559.02220439999996,33.340094399999998]
["2024-03-26T19:00:00","2024-03-26T19:05:00",556.52547719999995,31.663957199999999]
["2024-03-26T19:05:00","2024-03-26T19:10:00",555.29553480000004,30.364982399999999]
["2024-03-26T19:10:00","2024-03-26T19:15:00",552.14008320000005,29.691188400000001]
["2024-03-26T19:15:00","2024-03-26T19:20:00",550.31022359999997,29.403268799999999]
["2024-03-26T19:20:00","2024-03-26T19:25:00",550.23586920000002,29.6745552]
["2024-03-26T19:25:00","2024-03-26T19:30:00",546.07442160000005,28.143841200000001]
["2024-03-26T19:30:00","2024-03-26T19:35:00",544.00381440000001,27.26247]
["2024-03-26T19:35:00","2024-03-26T19:40:00",545.03787239999997,28.0730808]
["2024-03-26T19:40:00","2024-03-26T19:45:00",542.61650039999995,26.9448732]
["2024-03-26T19:45:00","2024-03-26T19:50:00",538.68503399999997,26.267454000000001]
["2024-03-26T19:50:00","2024-03-26T19:55:00",535.51964520000001,24.8254704]
["2024-03-26T19:55:00","2024-03-26T20:00:00",532.61243160000004,23.892685199999999]
["2024-03-26T20:00:00","2024-03-26T20:05:00",530.83369200000004,23.998529999999999]
["2024-03-26T20:05:00","2024-03-26T20:10:00",525.52250400000003,22.269662400000001]
["2024-03-26T20:10:00","2024-03-26T20:15:00",522.59773800000005,20.460511199999999]
["2024-03-26T20:15:00","2024-03-26T20:20:00",519.35871959999997,18.430003200000002]
["2024-03-26T20:20:00","2024-03-26T20:25:00",517.88345279999999,18.252814799999999]
["2024-03-26T20:25:00","2024-03-26T20:30:00",513.74055599999997,16.819146]
["2024-03-26T20:30:00","2024-03-26T20:35:00",510.85315559999998,17.519986800000002]
["2024-03-26T20:35:00","2024-03-26T20:40:00",507.60161520000003,16.841161199999998]
["2024-03-26T20:40:00","2024-03-26T20:45:00",505.86832679999998,16.054070400000001]
["2024-03-26T20:45:00","2024-03-26T20:50:00",503.44538999999997,16.298570399999999]
["2024-03-26T20:50:00","2024-03-26T20:55:00",495.95926320000001,13.6762104]
["2024-03-26T20:55:00","2024-03-26T21:00:00",492.81123839999998,12.2958684]
["2024-03-26T21:00:00","2024-03-26T21:05:00",489.18677159999999,11.790830400000001]
["2024-03-26T21:05:00","2024-03-26T21:10:00",486.226404,10.631877599999999]
["2024-03-26T21:10:00","2024-03-26T21:15:00",482.6423916,10.029809999999999]
["2024-03-26T21:15:00","2024-03-26T21:20:00",477.60836519999998,8.7868823999999996]
["2024-03-26T21:20:00","2024-03-26T21:25:00",472.80147959999999,7.4893619999999999]
["2024-03-26T21:25:00","2024-03-26T21:30:00",470.1003,6.7625472000000002]
["2024-03-26T21:30:00","2024-03-26T21:35:00",466.348116,6.2694276000000002]
["2024-03-26T21:35:00","2024-03-26T21:40:00",464.65148520000002,6.4075848000000004]
["2024-03-26T21:40:00","2024-03-26T21:45:00",458.76755159999999,4.2876456000000003]
["2024-03-26T21:45:00","2024-03-26T21:50:00",456.78497040000002,4.1667936000000001]
["2024-03-26T21:50:00","2024-03-26T21:55:00",452.26487279999998,3.7065671999999998]
["2024-03-26T21:55:00","2024-03-26T22:00:00",447.91887960000003,2.8630140000000002]
["2024-03-26T22:00:00","2024-03-26T22:05:00",444.20208600000001,1.9855992]
["2024-03-26T22:05:00","2024-03-26T22:10:00",441.47010719999997,1.4556708]
["2024-03-26T22:10:00","2024-03-26T22:15:00",438.75305400000002,-0.21687239999999999]
["2024-03-26T22:15:00","2024-03-26T22:20:00",436.10495880000002,-1.4769192]
["2024-03-26T22:20:00","2024-03-26T22:25:00",431.569278,-1.567866]
["2024-03-26T22:25:00","2024-03-26T22:30:00",428.32729920000003,-2.7570131999999998]
["2024-03-26T22:45:00","2024-03-26T22:50:00",419.43226559999999,-5.221266]
["2024-03-27T03:05:00","2024-03-27T03:10:00",369.47423880000002,-16.7643564]
["2024-03-27T07:20:00","2024-03-27T07:25:00",546.24203999999997,49.556701199999999]
["2024-03-27T11:55:00","2024-03-27T12:00:00",382.35257760000002,72.230530799999997]
["2024-03-27T16:00:00","2024-03-27T16:05:00",478.5832752,43.687107599999997]
["2024-03-27T20:15:00","2024-03-27T20:20:00",515.80893839999999,13.807546800000001]
["2024-03-28T04:20:00","2024-03-28T04:25:00",398.82590399999998,-14.2812672]
["2024-03-28T04:55:00","2024-03-28T05:00:00",421.01326440000003,-9.7774859999999997]
["2024-03-28T09:15:00","2024-03-28T09:20:00",510.30221999999998,61.237015200000002]
["2024-03-28T16:25:00","2024-03-28T16:30:00",430.44346080000003,32.605669200000001]
["2024-03-28T17:50:00","2024-03-28T17:55:00",517.78268879999996,23.410707599999999]
["2024-03-28T22:10:00","2024-03-28T22:15:00",420.546786,-16.164957600000001]
["2024-03-29T04:30:00","2024-03-29T04:35:00",336.93612000000002,-36.5665476]
["2024-03-29T06:45:00","2024-03-29T06:50:00",361.47799559999999,-32.086474799999998]
["2024-03-29T11:05:00","2024-03-29T11:10:00",198.07232999999999,0.35029559999999998]
["2024-03-29T16:35:00","2024-03-29T16:40:00",403.70414160000001,7.4626020000000004]
["2024-03-29T19:45:00","2024-03-29T19:50:00",442.04654879999998,-13.1560656]
[45381,"2024-03-30T00:05:00",354.58597800000001,-36.613346399999998]
["2024-03-30T04:15:00","2024-03-30T04:20:00",328.49770799999999,-40.588280400000002]
["2024-03-30T11:20:00","2024-03-30T11:25:00",204.07050480000001,4.9586411999999997]
["2024-03-30T12:55:00","2024-03-30T13:00:00",201.7472124,12.3046872]
["2024-03-30T17:15:00","2024-03-30T17:20:00",435.74669280000001,3.3937560000000002]
["2024-03-30T23:25:00","2024-03-30T23:30:00",377.7765852,-31.973288400000001]
["2024-03-31T01:50:00","2024-03-31T01:55:00",323.10476519999997,-40.7256012]
["2024-03-31T06:10:00","2024-03-31T06:15:00",350.77708439999998,-35.406103199999997]
["2024-03-31T11:30:00","2024-03-31T11:35:00",182.0841672,-7.0231260000000004]
["2024-03-31T14:45:00","2024-03-31T14:50:00",238.34691960000001,0.98097599999999996]
["2024-03-31T19:05:00","2024-03-31T19:10:00",442.41776520000002,-16.1461416]
["2024-03-31T23:35:00","2024-03-31T23:40:00",366.63866519999999,-34.414966800000002]
["2024-04-01T03:45:00","2024-04-01T03:50:00",321.70865759999998,-43.362824400000001]
["2024-04-01T08:00:00","2024-04-01T08:05:00",330.81898560000002,-21.531272399999999]
["2024-04-01T11:40:00","2024-04-01T11:45:00",438.15962999999999,1.5949788]
["2024-04-01T16:40:00","2024-04-01T16:45:00",504.90494639999997,2.800878]
["2024-04-01T20:55:00","2024-04-01T21:00:00",432.5898444,-18.615402]
["2024-04-02T04:05:00","2024-04-02T04:10:00",357.41997479999998,-29.453289600000002]
["2024-04-02T05:35:00","2024-04-02T05:40:00",442.09196639999999,2.5797599999999998]
["2024-04-02T09:50:00","2024-04-02T09:55:00",416.61432719999999,46.781278800000003]
["2024-04-02T14:10:00","2024-04-02T14:15:00",388.94024039999999,40.638545999999998]
["2024-04-02T18:30:00","2024-04-02T18:35:00",555.96032160000004,22.405536000000001]
["2024-04-02T22:45:00","2024-04-02T22:50:00",414.05218439999999,-15.129858]
["2024-04-03T03:05:00","2024-04-03T03:10:00",363.08045279999999,-27.540590399999999]
["2024-04-03T06:35:00","2024-04-03T06:40:00",537.77501280000001,36.512114400000002]
["2024-04-03T11:45:00","2024-04-03T11:50:00",484.72513800000002,56.457247199999998]
["2024-04-03T16:00:00","2024-04-03T16:05:00",548.54893079999999,32.227663200000002]
["2024-04-03T18:40:00","2024-04-03T18:45:00",579.90160319999995,26.131944000000001]
["2024-04-04T00:40:00","2024-04-04T00:45:00",387.42768360000002,-21.740230799999999]
["2024-04-04T04:55:00","2024-04-04T05:00:00",438.39858359999999,-3.4986899999999999]
["2024-04-04T11:05:00","2024-04-04T11:10:00",348.58297800000003,49.590584399999997]
["2024-04-04T13:35:00","2024-04-04T13:40:00",408.89313959999998,50.981994]
["2024-04-04T17:50:00","2024-04-04T17:55:00",565.34043480000003,28.267856399999999]
["2024-04-04T22:50:00","2024-04-04T22:55:00",429.86667360000001,-10.625059200000001]
["2024-04-05T02:30:00","2024-04-05T02:35:00",369.20202360000002,-25.374862799999999]
["2024-04-05T06:45:00","2024-04-05T06:50:00",548.20784400000002,41.754661200000001]
["2024-04-05T10:55:00","2024-04-05T11:00:00",345.37435199999999,55.788278400000003]
["2024-04-05T15:25:00","2024-04-05T15:30:00",389.38776480000001,33.525314399999999]
["2024-04-05T19:45:00","2024-04-05T19:50:00",515.83865519999995,9.7471751999999992]
[45388,"2024-04-06T00:05:00",386.24863319999997,-26.454465599999999]
["2024-04-06T06:00:00","2024-04-06T06:05:00",392.02216320000002,-20.861752800000001]
["2024-04-06T08:40:00","2024-04-06T08:45:00",430.70773079999998,-1.7503236]
["2024-04-06T12:55:00","2024-04-06T13:00:00",393.42230519999998,-1.5081587999999999]
["2024-04-06T18:05:00","2024-04-06T18:10:00",482.95300680000003,-8.1222168000000003]
["2024-04-06T21:35:00","2024-04-06T21:40:00",414.78814560000001,-26.3831028]
["2024-04-07T01:50:00","2024-04-07T01:55:00",336.76804920000001,-39.0210948]
["2024-04-07T05:50:00","2024-04-07T05:55:00",339.72513359999999,-38.927351999999999]
["2024-04-07T10:30:00","2024-04-07T10:35:00",372.32979599999999,-9.0903480000000005]
["2024-04-07T14:45:00","2024-04-07T14:50:00",283.42746959999999,-5.5216152000000003]
["2024-04-07T17:55:00","2024-04-07T18:00:00",495.69147600000002,-6.0411168000000002]
["2024-04-07T23:25:00","2024-04-07T23:30:00",410.064054,-25.2087276]
["2024-04-08T03:40:00","2024-04-08T03:45:00",340.77778439999997,-35.992839600000003]
["2024-04-08T06:00:00","2024-04-08T06:05:00",423.63235320000001,-9.2521439999999995]
["2024-04-08T12:20:00","2024-04-08T12:25:00",330.9605664,61.7621064]
["2024-04-08T16:40:00","2024-04-08T16:45:00",568.63942320000001,40.225988399999999]
["2024-04-08T20:55:00","2024-04-08T21:00:00",539.0202984,15.7177416]
["2024-04-09T01:05:00","2024-04-09T01:10:00",399.61809840000001,-19.024058400000001]
["2024-04-09T05:35:00","2024-04-09T05:40:00",432.92056200000002,-6.9167015999999997]
["2024-04-09T09:50:00","2024-04-09T09:55:00",534.63217199999997,62.4212664]
["2024-04-09T12:50:00","2024-04-09T12:55:00",452.60925839999999,56.414304000000001]
["2024-04-09T18:30:00","2024-04-09T18:35:00",659.27339640000002,50.796117600000002]
["2024-04-09T22:45:00","2024-04-09T22:50:00",489.13552079999999,0.42241800000000002]
["2024-04-10T00:55:00","2024-04-10T01:00:00",416.72715479999999,-17.380141200000001]
["2024-04-10T07:25:00","2024-04-10T07:30:00",556.769634,48.918826799999998]
["2024-04-10T11:40:00","2024-04-10T11:45:00",485.32820040000001,63.293269199999997]
["2024-04-10T17:20:00","2024-04-10T17:25:00",599.11038959999996,41.464376399999999]
["2024-04-10T20:20:00","2024-04-10T20:25:00",578.37597840000001,25.9151916]
["2024-04-11T00:40:00","2024-04-11T00:45:00",417.6512472,-14.692674]
["2024-04-11T05:25:00","2024-04-11T05:30:00",417.05499600000002,-12.877274399999999]
["2024-04-11T09:15:00","2024-04-11T09:20:00",521.89713959999995,48.319093199999998]
["2024-04-11T13:35:00","2024-04-11T13:40:00",485.35228080000002,51.569667600000002]
["2024-04-11T17:30:00","2024-04-11T17:35:00",578.10365639999998,26.8580556]
["2024-04-11T22:10:00","2024-04-11T22:15:00",514.53908039999999,6.8512560000000002]
["2024-04-12T02:30:00","2024-04-12T02:35:00",375.33181200000001,-27.239551200000001]
["2024-04-12T06:45:00","2024-04-12T06:50:00",501.81389999999999,18.383517600000001]
["2024-04-12T07:55:00","2024-04-12T08:00:00",551.85347160000003,44.344965600000002]
["2024-04-12T15:25:00","2024-04-12T15:30:00",529.0501524,36.107581199999998]
["2024-04-12T19:40:00","2024-04-12T19:45:00",576.95350199999996,22.089929999999999]
["2024-04-13T00:20:00","2024-04-13T00:25:00",423.47051279999999,-22.0610292]
["2024-04-13T04:20:00","2024-04-13T04:25:00",350.55201,-41.738720399999998]
["2024-04-13T08:40:00","2024-04-13T08:45:00",366.3394692,-11.004443999999999]
["2024-04-13T12:25:00","2024-04-13T12:30:00",411.48029279999997,-2.9019732]
["2024-04-13T17:15:00","2024-04-13T17:20:00",470.02141920000003,-13.0989012]
["2024-04-13T21:35:00","2024-04-13T21:40:00",475.82042519999999,-15.956239200000001]
["2024-04-14T00:30:00","2024-04-14T00:35:00",401.25370199999998,-32.994895200000002]
["2024-04-14T06:10:00","2024-04-14T06:15:00",369.91929240000002,-37.8247608]
["2024-04-14T10:30:00","2024-04-14T10:35:00",355.20701279999997,-19.893543600000001]
["2024-04-14T12:35:00","2024-04-14T12:40:00",363.97320839999998,-14.684054400000001]
["2024-04-14T19:10:00","2024-04-14T19:15:00",534.02939279999998,-3.1112928000000002]
["2024-04-14T23:25:00","2024-04-14T23:30:00",426.70942200000002,-25.680261600000001]
["2024-04-15T00:40:00","2024-04-15T00:45:00",385.97217599999999,-30.961102799999999]
["2024-04-15T08:05:00","2024-04-15T08:10:00",557.8397592,58.715736]
["2024-04-15T12:20:00","2024-04-15T12:25:00",391.51087200000001,62.017546799999998]
["2024-04-15T16:40:00","2024-04-15T16:45:00",520.20473400000003,40.024143600000002]
["2024-04-15T19:25:00","2024-04-15T19:30:00",596.20319519999998,31.791837600000001]
["2024-04-16T01:15:00","2024-04-16T01:20:00",392.48871960000002,-20.014109999999999]
["2024-04-16T05:35:00","2024-04-16T05:40:00",426.23468639999999,-10.1903784]
["2024-04-16T07:30:00","2024-04-16T07:35:00",568.85323319999998,48.823751999999999]
["2024-04-16T14:10:00","2024-04-16T14:15:00",442.83929039999998,72.0304596]
["2024-04-16T18:30:00","2024-04-16T18:35:00",624.10078439999995,52.880549999999999]
["2024-04-16T19:35:00","2024-04-16T19:40:00",600.02828280000006,45.585055199999999]
["2024-04-17T03:10:00","2024-04-17T03:15:00",374.76735839999998,-24.6392484]
["2024-04-17T07:25:00","2024-04-17T07:30:00",582.65485799999999,54.604972799999999]
["2024-04-17T07:40:00","2024-04-17T07:45:00",593.74164599999995,60.200924399999998]
["2024-04-17T16:05:00","2024-04-17T16:10:00",505.02385079999999,37.265752800000001]
["2024-04-17T20:20:00","2024-04-17T20:25:00",599.78544720000002,26.239034400000001]
["2024-04-18T00:05:00","2024-04-18T00:10:00",444.37219800000003,-15.963647999999999]
["2024-04-18T00:45:00","2024-04-18T00:50:00",418.62795720000003,-21.539262000000001]
["2024-04-18T05:00:00","2024-04-18T05:05:00",408.32298359999999,-22.476861599999999]
["2024-04-18T11:50:00","2024-04-18T11:55:00",474.31358160000002,52.167896399999997]
["2024-04-18T13:40:00","2024-04-18T13:45:00",486.8165664,50.000152800000002]
["2024-04-18T17:55:00","2024-04-18T18:00:00",660.39715799999999,46.763710799999998]
["2024-04-18T22:15:00","2024-04-18T22:20:00",520.68474000000003,3.4209192000000002]
["2024-04-19T02:35:00","2024-04-19T02:40:00",381.37652279999998,-29.539943999999998]
["2024-04-19T06:55:00","2024-04-19T07:00:00",548.68081199999995,27.006872399999999]
["2024-04-19T11:10:00","2024-04-19T11:15:00",444.52250880000003,48.473502000000003]
["2024-04-19T19:00:00","2024-04-19T19:05:00",622.80103440000005,32.758936800000001]
["2024-04-19T19:50:00","2024-04-19T19:55:00",597.86025719999998,23.060604000000001]
["2024-04-20T00:05:00","2024-04-20T00:10:00",448.29439680000002,-20.879418000000001]
["2024-04-20T07:05:00","2024-04-20T07:10:00",447.67752480000001,-15.351705600000001]
["2024-04-20T08:45:00","2024-04-20T08:50:00",420.56543040000003,-0.1334736]
["2024-04-20T13:00:00","2024-04-20T13:05:00",334.07943360000002,-5.8270667999999999]
["2024-04-20T18:50:00","2024-04-20T18:55:00",564.874056,1.0149948]
["2024-04-20T21:40:00","2024-04-20T21:45:00",514.42884719999995,-13.587047999999999]
["2024-04-21T01:55:00","2024-04-21T02:00:00",370.58998680000002,-45.294157200000001]
["2024-04-21T06:55:00","2024-04-21T07:00:00",390.39067920000002,-39.386176800000001]
["2024-04-21T10:35:00","2024-04-21T10:40:00",351.01610399999998,-17.453133600000001]
["2024-04-21T14:55:00","2024-04-21T15:00:00",287.64611280000003,-18.9561396]
["2024-04-21T19:10:00","2024-04-21T19:15:00",570.36214080000002,-8.6820000000000005E-3]
["2024-04-22T02:00:00","2024-04-22T02:05:00",372.11408999999998,-43.362437999999997]
["2024-04-22T03:50:00","2024-04-22T03:55:00",371.50300320000002,-43.035669599999999]
["2024-04-22T08:05:00","2024-04-22T08:10:00",628.35198119999995,70.027369199999995]
["2024-04-22T14:05:00","2024-04-22T14:10:00",380.232168,58.110159600000003]
["2024-04-22T16:45:00","2024-04-22T16:50:00",551.08989840000004,36.818814000000003]
["2024-04-22T21:00:00","2024-04-22T21:05:00",549.27388199999996,8.1017772000000008]
["2024-04-23T01:50:00","2024-04-23T01:55:00",386.89529759999999,-29.4612768]
["2024-04-23T05:40:00","2024-04-23T05:45:00",441.25674479999998,-12.811738800000001]
["2024-04-23T09:55:00","2024-04-23T10:00:00",420.89158079999999,43.203633600000003]
["2024-04-23T13:55:00","2024-04-23T14:00:00",405.12923640000002,70.805350799999999]
["2024-04-23T18:35:00","2024-04-23T18:40:00",596.00161200000002,38.278861200000001]
["2024-04-23T22:50:00","2024-04-23T22:55:00",456.75548040000001,-4.3461648000000004]
["2024-04-24T06:20:00","2024-04-24T06:25:00",507.052392,18.679131600000002]
["2024-04-24T07:30:00","2024-04-24T07:35:00",606.34095000000002,56.809620000000002]
["2024-04-24T11:50:00","2024-04-24T11:55:00",517.56356879999998,63.299649600000002]
["2024-04-24T18:25:00","2024-04-24T18:30:00",669.06680640000002,52.346474399999998]
["2024-04-24T20:25:00","2024-04-24T20:30:00",616.39016279999998,32.3514768]
["2024-04-25T00:45:00","2024-04-25T00:50:00",426.05290439999999,-22.711416]
["2024-04-25T05:00:00","2024-04-25T05:05:00",380.01325919999999,-30.900113999999999]
["2024-04-25T08:50:00","2024-04-25T08:55:00",440.92969799999997,-7.1997299999999997]
["2024-04-25T13:40:00","2024-04-25T13:45:00",451.17543000000001,-2.9753004000000001]
["2024-04-25T17:55:00","2024-04-25T18:00:00",575.7796032,13.7054148]
["2024-04-25T20:55:00","2024-04-25T21:00:00",532.21194360000004,-4.7765219999999999]
["2024-04-26T02:35:00","2024-04-26T02:40:00",348.76699919999999,-43.569203999999999]
["2024-04-26T06:50:00","2024-04-26T06:55:00",498.6327144,5.8820291999999998]
["2024-04-26T13:20:00","2024-04-26T13:25:00",511.26605280000001,25.9286256]
["2024-04-26T15:30:00","2024-04-26T15:35:00",539.33150039999998,23.248425600000001]
["2024-04-26T19:50:00","2024-04-26T19:55:00",604.35696959999996,26.8728108]
["2024-04-27T01:25:00","2024-04-27T01:30:00",383.97682079999998,-35.350718399999998]
["2024-04-27T04:25:00","2024-04-27T04:30:00",359.08551119999998,-38.038507199999998]
["2024-04-27T08:45:00","2024-04-27T08:50:00",411.05934120000001,-6.6086651999999999]
["2024-04-27T13:30:00","2024-04-27T13:35:00",249.11239320000001,-5.2532052]
["2024-04-27T17:20:00","2024-04-27T17:25:00",501.47600160000002,-9.8003028000000008]
["2024-04-27T21:40:00","2024-04-27T21:45:00",499.20500399999997,-12.1615944]
["2024-04-28T01:35:00","2024-04-28T01:40:00",383.70555960000002,-39.4086444]
["2024-04-28T06:20:00","2024-04-28T06:25:00",392.07528960000002,-34.290618000000002]
["2024-04-28T10:35:00","2024-04-28T10:40:00",309.9809952,-10.749726000000001]
["2024-04-28T14:50:00","2024-04-28T14:55:00",298.65885960000003,-13.035636]
["2024-04-28T20:20:00","2024-04-28T20:25:00",515.87280599999997,-9.2709911999999992]
["2024-04-28T23:30:00","2024-04-28T23:35:00",428.64686760000001,-27.163389599999999]
["2024-04-29T03:50:00","2024-04-29T03:55:00",357.25263480000001,-35.829760800000003]
["2024-04-29T08:25:00","2024-04-29T08:30:00",617.26321919999998,69.606098399999993]
["2024-04-29T12:25:00","2024-04-29T12:30:00",601.221408,66.349189199999998]
["2024-04-29T16:45:00","2024-04-29T16:50:00",634.32210599999996,45.859426800000001]
["2024-04-29T20:30:00","2024-04-29T20:35:00",637.09098840000001,45.8212452]
["2024-04-30T01:20:00","2024-04-30T01:25:00",411.59557080000002,-21.069964800000001]
["2024-04-30T05:40:00","2024-04-30T05:45:00",458.26910279999998,-1.4510460000000001]
["2024-04-30T08:35:00","2024-04-30T08:40:00",603.57044519999999,79.311980399999996]
["2024-04-30T14:20:00","2024-04-30T14:25:00",547.46880120000003,61.255196400000003]
["2024-04-30T18:35:00","2024-04-30T18:40:00",718.8538092,77.533425600000001]
["2024-04-30T20:40:00","2024-04-30T20:45:00",648.38665679999997,40.547836799999999]
["2024-05-01T03:15:00","2024-05-01T03:20:00",398.20640159999999,-23.214505200000001]
["2024-05-01T07:30:00","2024-05-01T07:35:00",653.10595079999996,75.398065200000005]
["2024-05-01T12:45:00","2024-05-01T12:50:00",402.71569199999999,56.858833199999999]
["2024-05-01T16:10:00","2024-05-01T16:15:00",528.91526880000004,39.876004799999997]
["2024-05-01T20:25:00","2024-05-01T20:30:00",633.02489639999999,37.313038800000001]
["2024-05-02T00:45:00","2024-05-02T00:50:00",435.50514479999998,-15.9320868]
["2024-05-02T03:30:00","2024-05-02T03:35:00",396.25705679999999,-23.765983200000001]
["2024-05-02T09:20:00","2024-05-02T09:25:00",662.45100720000005,90.577012800000006]
["2024-05-02T13:40:00","2024-05-02T13:45:00",406.05541799999997,55.773645600000002]
["2024-05-02T15:35:00","2024-05-02T15:40:00",478.49369519999999,42.089894399999999]
["2024-05-02T22:20:00","2024-05-02T22:25:00",547.21956239999997,8.7822600000000008]
["2024-05-03T02:35:00","2024-05-03T02:40:00",400.27998000000002,-26.4915804]
["2024-05-03T08:00:00","2024-05-03T08:05:00",692.39011200000004,88.910569199999998]
["2024-05-03T11:15:00","2024-05-03T11:20:00",410.6541024,52.167104399999999]
["2024-05-03T15:30:00","2024-05-03T15:35:00",460.23742679999998,28.817076]
["2024-05-03T20:05:00","2024-05-03T20:10:00",618.61833360000003,39.493625999999999]
["2024-05-04T00:10:00","2024-05-04T00:15:00",468.63608879999998,-17.516779199999998]
["2024-05-04T04:25:00","2024-05-04T04:30:00",387.08361239999999,-33.804387599999998]
["2024-05-04T07:50:00","2024-05-04T07:55:00",527.25432960000001,13.807329599999999]
["2024-05-04T13:05:00","2024-05-04T13:10:00",357.68012879999998,3.4895255999999999]
["2024-05-04T17:20:00","2024-05-04T17:25:00",578.77290719999996,8.0736612000000001]
["2024-05-04T21:40:00","2024-05-04T21:45:00",552.27494039999999,-4.7837999999999999E-2]
["2024-05-05T02:55:00","2024-05-05T03:00:00",365.74586399999998,-42.832853999999998]
["2024-05-05T06:20:00","2024-05-05T06:25:00",390.23389680000002,-35.901702]
["2024-05-05T10:35:00","2024-05-05T10:40:00",448.20666119999999,-9.5502731999999995]
["2024-05-05T15:00:00","2024-05-05T15:05:00",355.52282400000001,-16.394724]
["2024-05-05T19:15:00","2024-05-05T19:20:00",582.79831799999999,7.4085863999999999]
["2024-05-05T23:30:00","2024-05-05T23:35:00",446.53880880000003,-24.961283999999999]
["2024-05-06T03:05:00","2024-05-06T03:10:00",367.76383440000001,-36.297926400000001]
["2024-05-06T08:10:00","2024-05-06T08:15:00",652.24079519999998,72.649785600000001]
["2024-05-06T12:25:00","2024-05-06T12:30:00",426.11454959999998,56.696094000000002]
["2024-05-06T14:50:00","2024-05-06T14:55:00",450.16383000000002,47.394779999999997]
["2024-05-06T21:05:00","2024-05-06T21:10:00",595.36866840000005,25.848619200000002]
["2024-05-07T01:20:00","2024-05-07T01:25:00",414.39199919999999,-19.250523600000001]
["2024-05-07T02:55:00","2024-05-07T03:00:00",392.84135520000001,-23.931788399999999]
["2024-05-07T10:00:00","2024-05-07T10:05:00",492.23951640000001,63.392839199999997]
["2024-05-07T14:15:00","2024-05-07T14:20:00",421.61498879999999,53.815759200000002]
["2024-05-07T19:20:00","2024-05-07T19:25:00",686.57665199999997,53.968987200000001]
["2024-05-07T22:55:00","2024-05-07T23:00:00",508.03009800000001,1.2128483999999999]
["2024-05-08T03:15:00","2024-05-08T03:20:00",389.90504399999998,-26.576337599999999]
["2024-05-08T07:30:00","2024-05-08T07:35:00",637.48550639999996,66.756523200000004]
["2024-05-08T10:05:00","2024-05-08T10:10:00",497.96939520000001,67.220194800000002]
["2024-05-08T16:10:00","2024-05-08T16:15:00",539.69839200000001,38.116388399999998]
["2024-05-08T20:25:00","2024-05-08T20:30:00",616.76795760000005,43.744362000000002]
["2024-05-08T21:50:00","2024-05-08T21:55:00",558.26091240000005,16.492667999999998]
["2024-05-09T05:05:00","2024-05-09T05:10:00",427.05433199999999,-14.7850608]
["2024-05-09T09:20:00","2024-05-09T09:25:00",619.4022516,69.797449200000003]
["2024-05-09T09:55:00","2024-05-09T10:00:00",603.76285800000005,70.056964800000003]
["2024-05-09T18:00:00","2024-05-09T18:05:00",688.19624520000002,64.406281199999995]
["2024-05-09T22:15:00","2024-05-09T22:20:00",530.07689400000004,2.1572184000000001]
["2024-05-10T02:20:00","2024-05-10T02:25:00",389.80813560000001,-26.545588800000001]
["2024-05-10T06:55:00","2024-05-10T07:00:00",555.63849479999999,32.919962400000003]
["2024-05-10T11:15:00","2024-05-10T11:20:00",565.38751679999996,57.124963200000003]
["2024-05-10T14:25:00","2024-05-10T14:30:00",551.71632120000004,46.318712400000003]
["2024-05-10T19:50:00","2024-05-10T19:55:00",610.96572360000005,26.962936800000001]
["2024-05-11T00:10:00","2024-05-11T00:15:00",439.30556999999999,-21.424311599999999]
["2024-05-11T02:30:00","2024-05-11T02:35:00",370.3825248,-34.0157004]
["2024-05-11T08:50:00","2024-05-11T08:55:00",469.25263080000002,0.12759480000000001]
["2024-05-11T13:05:00","2024-05-11T13:10:00",356.38098120000001,-3.5282580000000001]
["2024-05-11T17:20:00","2024-05-11T17:25:00",534.10269240000002,-1.1350595999999999]
["2024-05-11T21:15:00","2024-05-11T21:20:00",504.89156279999997,-12.746764799999999]
["2024-05-11T21:45:00","2024-05-11T21:50:00",494.87589600000001,-14.7008004]
["2024-05-12T02:00:00","2024-05-12T02:05:00",373.1905812,-40.890376799999999]
["2024-05-12T09:20:00","2024-05-12T09:25:00",398.5803636,-9.6115283999999992]
["2024-05-12T10:40:00","2024-05-12T10:45:00",312.62121480000002,-15.451854000000001]
["2024-05-12T15:00:00","2024-05-12T15:05:00",322.84853520000001,-17.620275599999999]
["2024-05-12T21:25:00","2024-05-12T21:30:00",506.59461119999997,-12.3537876]
["2024-05-12T23:35:00","2024-05-12T23:40:00",437.41766519999999,-26.646363600000001]
["2024-05-13T03:55:00","2024-05-13T04:00:00",365.3845632,-38.674982399999998]
["2024-05-13T09:30:00","2024-05-13T09:35:00",532.69954440000004,64.8513552]
["2024-05-13T12:30:00","2024-05-13T12:35:00",432.43182359999997,48.109293600000001]
["2024-05-13T16:50:00","2024-05-13T16:55:00",614.3712888,40.644830399999996]
["2024-05-13T21:35:00","2024-05-13T21:40:00",557.49346679999996,15.024433200000001]
["2024-05-14T01:30:00","2024-05-14T01:35:00",392.41541519999998,-27.4693644]
["2024-05-14T05:45:00","2024-05-14T05:50:00",450.4561812,-4.9921547999999998]
["2024-05-14T10:00:00","2024-05-14T10:05:00",569.31287280000004,66.442575599999998]
["2024-05-14T16:20:00","2024-05-14T16:25:00",558.26368319999995,32.098228800000001]
["2024-05-14T18:40:00","2024-05-14T18:45:00",686.51283839999996,51.436843199999998]
["2024-05-14T23:00:00","2024-05-14T23:05:00",510.61013279999997,-0.41284080000000001]
["2024-05-15T04:25:00","2024-05-15T04:30:00",414.27846240000002,-21.187104000000001]
["2024-05-15T07:35:00","2024-05-15T07:40:00",715.63968239999997,95.142003599999995]
["2024-05-15T11:55:00","2024-05-15T12:00:00",426.27296039999999,61.992148800000002]
["2024-05-15T16:30:00","2024-05-15T16:35:00",583.15235040000005,39.747028800000002]
["2024-05-15T20:30:00","2024-05-15T20:35:00",656.48045879999995,43.845241199999997]
["2024-05-16T00:50:00","2024-05-16T00:55:00",439.32373439999998,-19.039052399999999]
["2024-05-16T04:35:00","2024-05-16T04:40:00",422.81202719999999,-18.903664800000001]
["2024-05-16T09:30:00","2024-05-16T09:35:00",592.5928116,82.636255199999994]
["2024-05-16T13:45:00","2024-05-16T13:50:00",433.63758360000003,63.336863999999998]
["2024-05-16T21:00:00","2024-05-16T21:05:00",635.23696199999995,41.855387999999998]
["2024-05-16T22:25:00","2024-05-16T22:30:00",547.77924240000004,11.943816]
["2024-05-17T02:40:00","2024-05-17T02:45:00",401.71855199999999,-26.1343104]
["2024-05-17T08:45:00","2024-05-17T08:50:00",678.31102320000002,91.800190799999996]
["2024-05-17T11:20:00","2024-05-17T11:25:00",616.31614079999997,72.554383200000004]
["2024-05-17T15:35:00","2024-05-17T15:40:00",647.01036599999998,59.889811199999997]
["2024-05-17T19:55:00","2024-05-17T20:00:00",699.58966439999995,53.983738799999998]
["2024-05-17T23:30:00","2024-05-17T23:35:00",529.36432319999994,-3.8730408000000001]
["2024-05-18T04:30:00","2024-05-18T04:35:00",401.83165079999998,-31.924771199999999]
["2024-05-18T08:50:00","2024-05-18T08:55:00",531.41828039999996,30.422857199999999]
["2024-05-18T15:55:00","2024-05-18T16:00:00",477.38547599999998,-0.48313319999999998]
["2024-05-18T17:30:00","2024-05-18T17:35:00",645.63130320000005,29.866356]
["2024-05-18T21:45:00","2024-05-18T21:50:00",608.55414719999999,16.857987600000001]
["2024-05-19T04:00:00","2024-05-19T04:05:00",392.0215728,-39.240492000000003]
["2024-05-19T06:25:00","2024-05-19T06:30:00",428.32568880000002,-27.938803199999999]
["2024-05-19T10:40:00","2024-05-19T10:45:00",492.02922840000002,5.7549935999999997]
["2024-05-19T16:05:00","2024-05-19T16:10:00",578.15286719999995,9.9030527999999993]
["2024-05-19T19:20:00","2024-05-19T19:25:00",652.09236480000004,26.117916000000001]
["2024-05-19T23:35:00","2024-05-19T23:40:00",470.09123520000003,-23.287639200000001]
["2024-05-20T03:50:00","2024-05-20T03:55:00",385.51326119999999,-36.148842000000002]
["2024-05-20T08:15:00","2024-05-20T08:20:00",703.02278279999996,89.364285600000002]
["2024-05-20T12:30:00","2024-05-20T12:35:00",600.05063759999996,77.544247200000001]
["2024-05-20T15:55:00","2024-05-20T16:00:00",657.29106839999997,68.125052400000001]
["2024-05-20T21:10:00","2024-05-20T21:15:00",656.70935399999996,39.594694799999999]
["2024-05-21T01:30:00","2024-05-21T01:35:00",426.03425399999998,-21.141411600000001]
["2024-05-21T05:45:00","2024-05-21T05:50:00",481.9498572,-1.2738948000000001]
["2024-05-21T11:00:00","2024-05-21T11:05:00",670.90760639999996,100.5015756]
["2024-05-21T14:25:00","2024-05-21T14:30:00",616.80737639999995,75.405624000000003]
["2024-05-21T18:40:00","2024-05-21T18:45:00",778.73895240000002,91.694632799999994]
["2024-05-21T23:05:00","2024-05-21T23:10:00",555.44563679999999,9.1231644000000003]
["2024-05-22T03:20:00","2024-05-22T03:25:00",420.8058216,-23.591980800000002]
["2024-05-22T07:35:00","2024-05-22T07:40:00",755.24285159999999,105.7073748]
["2024-05-22T10:50:00","2024-05-22T10:55:00",543.50024280000002,79.394447999999997]
["2024-05-22T16:15:00","2024-05-22T16:20:00",644.27361480000002,57.421048800000001]
["2024-05-22T20:30:00","2024-05-22T20:35:00",686.50538519999998,62.082399600000002]
["2024-05-22T22:55:00","2024-05-22T23:00:00",520.39404239999999,2.0417915999999998]
["2024-05-23T05:10:00","2024-05-23T05:15:00",439.58709119999997,-12.000904800000001]
["2024-05-23T09:25:00","2024-05-23T09:30:00",674.22878040000001,90.738194399999998]
["2024-05-23T15:20:00","2024-05-23T15:25:00",537.13562760000002,49.256045999999998]
["2024-05-23T18:05:00","2024-05-23T18:10:00",732.44563200000005,77.433856800000001]
["2024-05-23T22:25:00","2024-05-23T22:30:00",572.39659800000004,15.129057599999999]
["2024-05-24T03:25:00","2024-05-24T03:30:00",417.30113160000002,-23.439301199999999]
["2024-05-24T07:00:00","2024-05-24T07:05:00",661.99505399999998,67.612861199999998]
["2024-05-24T11:20:00","2024-05-24T11:25:00",658.64679720000004,86.146668000000005]
["2024-05-24T15:35:00","2024-05-24T15:40:00",642.82578479999995,57.385477199999997]
["2024-05-24T17:50:00","2024-05-24T17:55:00",743.45579399999997,79.082018399999995]
["2024-05-25T00:15:00","2024-05-25T00:20:00",469.84433999999999,-20.960808]
["2024-05-25T04:30:00","2024-05-25T04:35:00",382.98456599999997,-35.185874400000003]
["2024-05-25T10:15:00","2024-05-25T10:20:00",460.2125484,11.561512799999999]
["2024-05-25T13:10:00","2024-05-25T13:15:00",358.88142720000002,-1.4885124000000001]
["2024-05-25T17:25:00","2024-05-25T17:30:00",585.24070319999998,16.1236164]
["2024-05-25T22:20:00","2024-05-25T22:25:00",533.42928359999996,-7.2252108000000002]
["2024-05-26T02:05:00","2024-05-26T02:10:00",406.3932216,-37.551261599999997]
["2024-05-26T06:25:00","2024-05-26T06:30:00",427.43971920000001,-29.917600799999999]
["2024-05-26T10:25:00","2024-05-26T10:30:00",405.15067920000001,1.1578728]
["2024-05-26T15:00:00","2024-05-26T15:05:00",377.7063948,-17.306293199999999]
["2024-05-26T19:20:00","2024-05-26T19:25:00",650.40184799999997,33.619198799999999]
["2024-05-26T22:30:00","2024-05-26T22:35:00",517.28024640000001,-1.6991316000000001]
["2024-05-27T04:00:00","2024-05-27T04:05:00",404.28891119999997,-33.243302399999997]
["2024-05-27T08:15:00","2024-05-27T08:20:00",749.96430720000001,122.14829279999999]
["2024-05-27T12:30:00","2024-05-27T12:35:00",453.47863560000002,61.1601456]
["2024-05-27T17:15:00","2024-05-27T17:20:00",679.76491080000005,55.387818000000003]
["2024-05-27T21:10:00","2024-05-27T21:15:00",644.65686840000001,33.729825599999998]
["2024-05-28T01:25:00","2024-05-28T01:30:00",433.00957319999998,-19.709409600000001]
["2024-05-28T05:20:00","2024-05-28T05:25:00",471.42428760000001,-6.3725735999999999]
["2024-05-28T10:05:00","2024-05-28T10:10:00",554.61734879999995,72.280839599999993]
["2024-05-28T14:25:00","2024-05-28T14:30:00",456.35254200000003,52.007143200000002]
["2024-05-28T17:25:00","2024-05-28T17:30:00",678.82563600000003,66.776231999999993]
["2024-05-28T23:00:00","2024-05-28T23:05:00",526.46930280000004,2.4620844000000002]
["2024-05-29T03:20:00","2024-05-29T03:25:00",411.36090000000002,-23.874315599999999]
["2024-05-29T05:30:00","2024-05-29T05:35:00",483.20533799999998,0.96843120000000005]
["2024-05-29T11:55:00","2024-05-29T12:00:00",452.94173760000001,63.510246000000002]
["2024-05-29T16:15:00","2024-05-29T16:20:00",589.60685520000004,45.139375200000003]
["2024-05-29T17:35:00","2024-05-29T17:40:00",700.65916679999998,62.343024]
["2024-05-30T00:55:00","2024-05-30T01:00:00",436.6620168,-16.716993599999999]
["2024-05-30T05:10:00","2024-05-30T05:15:00",429.45984120000003,-13.90095]
["2024-05-30T10:00:00","2024-05-30T10:05:00",568.31355959999996,62.9818164]
["2024-05-30T13:50:00","2024-05-30T13:55:00",559.10829120000005,60.973709999999997]
["2024-05-30T18:05:00","2024-05-30T18:10:00",694.84794839999995,55.511038800000001]
["2024-05-30T22:25:00","2024-05-30T22:30:00",518.58844439999996,3.0241235999999998]
["2024-05-31T00:25:00","2024-05-31T00:30:00",440.31255720000001,-15.0981516]
["2024-05-31T07:00:00","2024-05-31T07:05:00",580.993788,40.929849599999997]
["2024-05-31T11:20:00","2024-05-31T11:25:00",434.55921840000002,53.533106400000001]
["2024-05-31T12:30:00","2024-05-31T12:35:00",416.76407519999998,52.318623600000002]
["2024-05-31T19:55:00","2024-05-31T20:00:00",629.12973239999997,30.3348312]
["2024-06-01T00:15:00","2024-06-01T00:20:00",459.11416919999999,-20.960228399999998]
["2024-06-01T04:55:00","2024-06-01T05:00:00",395.68127279999999,-33.217906800000002]
["2024-06-01T08:55:00","2024-06-01T09:00:00",538.06016639999996,26.346603600000002]
["2024-06-01T13:10:00","2024-06-01T13:15:00",479.76320520000002,6.6957659999999999]
["2024-06-01T17:00:00","2024-06-01T17:05:00",621.74479799999995,20.089161600000001]
["2024-06-01T21:50:00","2024-06-01T21:55:00",573.14548200000002,12.5638548]
["2024-06-02T02:05:00","2024-06-02T02:10:00",400.39934879999998,-30.0079584]
["2024-06-02T04:45:00","2024-06-02T04:50:00",383.21138999999999,-34.343745599999998]
["2024-06-02T10:45:00","2024-06-02T10:50:00",486.40880520000002,19.064605199999999]
["2024-06-02T15:00:00","2024-06-02T15:05:00",500.61815760000002,15.3310344]
["2024-06-02T16:50:00","2024-06-02T16:55:00",595.10975759999997,32.7747156]
["2024-06-02T23:40:00","2024-06-02T23:45:00",480.22677119999997,-13.693564800000001]
["2024-06-03T03:55:00","2024-06-03T04:00:00",404.11172520000002,-24.629589599999999]
["2024-06-03T08:15:00","2024-06-03T08:20:00",766.30575239999996,119.33224319999999]
["2024-06-03T11:55:00","2024-06-03T12:00:00",694.87842720000003,109.96769159999999]
["2024-06-03T16:55:00","2024-06-03T17:00:00",756.03364079999994,95.835345599999997]
["2024-06-03T21:10:00","2024-06-03T21:15:00",672.85577039999998,55.135348800000003]
[45447,"2024-06-04T00:05:00",492.83578440000002,0.39397559999999998]
["2024-06-04T05:50:00","2024-06-04T05:55:00",503.95668119999999,13.667115600000001]
["2024-06-04T10:05:00","2024-06-04T10:10:00",684.32679840000003,115.6824288]
["2024-06-04T12:05:00","2024-06-04T12:10:00",646.18341840000005,89.456918400000006]
["2024-06-04T14:30:00","2024-06-04T14:35:00",678.21494759999996,93.592846800000004]
["2024-06-04T18:45:00","2024-06-04T18:50:00",803.12447039999995,117.1799568]
["2024-06-04T23:50:00","2024-06-04T23:55:00",514.45003919999999,5.0772060000000003]
["2024-06-05T03:25:00","2024-06-05T03:30:00",421.64395080000003,-14.2045572]
["2024-06-05T07:40:00","2024-06-05T07:45:00",736.1710392,121.2797652]
["2024-06-05T11:55:00","2024-06-05T12:00:00",620.11607760000004,93.179750400000003]
["2024-06-05T16:20:00","2024-06-05T16:25:00",665.37654959999998,77.987150400000004]
["2024-06-05T20:40:00","2024-06-05T20:45:00",707.83582560000002,76.927762799999996]
["2024-06-06T04:20:00","2024-06-06T04:25:00",421.93020000000001,-14.9323128]
["2024-06-06T05:15:00","2024-06-06T05:20:00",457.96628520000002,-3.9112019999999998]
["2024-06-06T09:35:00","2024-06-06T09:40:00",697.54536240000004,110.6597364]
["2024-06-06T13:50:00","2024-06-06T13:55:00",499.54229400000003,65.731281600000003]
["2024-06-06T19:05:00","2024-06-06T19:10:00",718.96605599999998,70.481620800000002]
["2024-06-06T22:30:00","2024-06-06T22:35:00",558.10255800000004,18.984062399999999]
["2024-06-07T02:45:00","2024-06-07T02:50:00",408.16594079999999,-17.340077999999998]
["2024-06-07T06:50:00","2024-06-07T06:55:00",602.59572839999998,52.388370000000002]
["2024-06-07T11:25:00","2024-06-07T11:30:00",611.65188000000001,85.948493999999997]
["2024-06-07T15:40:00","2024-06-07T15:45:00",593.45401919999995,51.739198799999997]
["2024-06-07T23:15:00","2024-06-07T23:20:00",527.16345960000001,0.23572080000000001]
["2024-06-08T00:20:00","2024-06-08T00:25:00",465.99135360000002,-11.3577564]
["2024-06-08T04:35:00","2024-06-08T04:40:00",391.54673400000001,-26.972276399999998]
["2024-06-08T11:20:00","2024-06-08T11:25:00",518.83103519999997,20.881399200000001]
["2024-06-08T13:15:00","2024-06-08T13:20:00",558.43825079999999,21.713232000000001]
["2024-06-08T17:35:00","2024-06-08T17:40:00",646.44068159999995,51.730688399999998]
["2024-06-08T23:25:00","2024-06-08T23:30:00",488.87831879999999,-12.508421999999999]
["2024-06-09T02:10:00","2024-06-09T02:15:00",386.20355760000001,-32.5046952]
["2024-06-09T06:30:00","2024-06-09T06:35:00",398.56455599999998,-30.6515472]
["2024-06-09T10:45:00","2024-06-09T10:50:00",530.30513759999997,13.263176400000001]
["2024-06-09T18:10:00","2024-06-09T18:15:00",641.29141319999997,32.4919692]
["2024-06-09T19:25:00","2024-06-09T19:30:00",622.77375359999996,39.493084799999998]
["2024-06-09T23:40:00","2024-06-09T23:45:00",493.52566560000002,-12.9999552]
["2024-06-10T06:15:00","2024-06-10T06:20:00",442.33317840000001,-16.9923024]
["2024-06-10T08:20:00","2024-06-10T08:25:00",539.58821639999996,19.984494000000002]
["2024-06-10T12:35:00","2024-06-10T12:40:00",366.39245039999997,9.4480500000000003]
["2024-06-10T18:20:00","2024-06-10T18:25:00",710.01487680000002,54.657619199999999]
["2024-06-10T21:15:00","2024-06-10T21:20:00",611.28622680000001,18.865107600000002]
["2024-06-11T01:35:00","2024-06-11T01:40:00",396.94608240000002,-30.2092812]
["2024-06-11T06:25:00","2024-06-11T06:30:00",554.62371359999997,30.3352872]
["2024-06-11T10:10:00","2024-06-11T10:15:00",736.96888799999999,107.3494092]
["2024-06-11T14:30:00","2024-06-11T14:35:00",571.61570759999995,71.955888000000002]
["2024-06-11T18:30:00","2024-06-11T18:35:00",779.27621999999997,96.855049199999996]
["2024-06-11T23:10:00","2024-06-11T23:15:00",543.18980880000004,11.2300164]
["2024-06-12T03:25:00","2024-06-12T03:30:00",410.2387344,-15.9675732]
["2024-06-12T06:35:00","2024-06-12T06:40:00",600.23564639999995,50.4712344]
["2024-06-12T12:05:00","2024-06-12T12:10:00",645.00150240000005,98.862623999999997]
["2024-06-12T16:20:00","2024-06-12T16:25:00",755.73893399999997,96.6072408]
["2024-06-12T20:35:00","2024-06-12T20:40:00",747.81713639999998,99.166453200000007]
["2024-06-13T01:20:00","2024-06-13T01:25:00",456.77123160000002,-8.7963503999999997]
["2024-06-13T05:15:00","2024-06-13T05:20:00",474.96197640000003,-1.0207307999999999]
["2024-06-13T09:35:00","2024-06-13T09:40:00",773.699028,140.2582152]
["2024-06-13T13:25:00","2024-06-13T13:30:00",764.05680240000004,126.01602]
["2024-06-13T18:10:00","2024-06-13T18:15:00",833.5961436,134.34935039999999]
["2024-06-13T22:30:00","2024-06-13T22:35:00",607.87790759999996,37.990688400000003]
["2024-06-14T01:30:00","2024-06-14T01:35:00",456.27516839999998,-8.3356595999999996]
["2024-06-14T07:05:00","2024-06-14T07:10:00",679.36051799999996,91.951636800000003]
["2024-06-14T11:25:00","2024-06-14T11:30:00",700.99243679999995,107.6571156]
["2024-06-14T17:55:00","2024-06-14T18:00:00",794.24364960000003,109.24872120000001]
["2024-06-14T20:05:00","2024-06-14T20:10:00",734.84353920000001,79.468094399999998]
["2024-06-15T00:20:00","2024-06-15T00:25:00",515.42861040000003,-1.2983064]
["2024-06-15T06:00:00","2024-06-15T06:05:00",471.4106496,-8.5148759999999992]
["2024-06-15T09:00:00","2024-06-15T09:05:00",636.42299519999995,54.691737600000003]
["2024-06-15T13:15:00","2024-06-15T13:20:00",512.48349840000003,25.4546028]
["2024-06-15T17:45:00","2024-06-15T17:50:00",726.15809400000001,79.530584399999995]
["2024-06-15T21:55:00","2024-06-15T22:00:00",613.9979376,30.546351600000001]
["2024-06-16T02:10:00","2024-06-16T02:15:00",422.1258072,-27.3869316]
["2024-06-16T06:30:00","2024-06-16T06:35:00",455.00663639999999,-18.001235999999999]
["2024-06-16T12:50:00","2024-06-16T12:55:00",476.26315199999999,11.263339200000001]
["2024-06-16T15:05:00","2024-06-16T15:10:00",550.41065040000001,17.4790752]
["2024-06-16T19:25:00","2024-06-16T19:30:00",707.07437519999996,51.743625600000001]
["2024-06-17T00:55:00","2024-06-17T01:00:00",441.22859879999999,-21.234242399999999]
["2024-06-17T04:05:00","2024-06-17T04:10:00",414.16300080000002,-22.520704800000001]
["2024-06-17T08:20:00","2024-06-17T08:25:00",786.22235639999997,122.6315328]
["2024-06-17T13:00:00","2024-06-17T13:05:00",569.96939880000002,82.967640000000003]
["2024-06-17T17:00:00","2024-06-17T17:05:00",759.60466799999995,95.471328]
["2024-06-17T21:15:00","2024-06-17T21:20:00",707.74919999999997,73.104729599999999]
["2024-06-18T01:05:00","2024-06-18T01:10:00",471.20624759999998,-7.0453739999999998]
["2024-06-18T05:55:00","2024-06-18T06:00:00",546.53760239999997,17.191426799999999]
["2024-06-18T10:10:00","2024-06-18T10:15:00",697.23555120000003,116.46326879999999]
["2024-06-18T12:50:00","2024-06-18T12:55:00",589.29095400000006,81.523486800000001]
["2024-06-18T18:50:00","2024-06-18T18:55:00",829.83765359999995,107.6237448]
["2024-06-18T23:05:00","2024-06-18T23:10:00",607.73123999999996,23.659312799999999]
["2024-06-19T03:25:00","2024-06-19T03:30:00",468.51082919999999,-8.5045128000000005]
["2024-06-19T07:55:00","2024-06-19T08:00:00",882.44057280000004,159.1133748]
["2024-06-19T12:05:00","2024-06-19T12:10:00",597.16412400000002,103.2202824]
["2024-06-19T16:20:00","2024-06-19T16:25:00",733.44040319999999,94.416397200000006]
["2024-06-19T20:00:00","2024-06-19T20:05:00",849.24630360000003,115.1041644]
["2024-06-20T01:00:00","2024-06-20T01:05:00",504.40107599999999,0.37935720000000001]
["2024-06-20T05:15:00","2024-06-20T05:20:00",509.275014,7.0567164]
["2024-06-20T08:05:00","2024-06-20T08:10:00",833.54859839999995,144.81838920000001]
["2024-06-20T13:55:00","2024-06-20T14:00:00",646.94797319999998,101.8259352]
["2024-06-20T18:10:00","2024-06-20T18:15:00",836.99028480000004,111.188868]
["2024-06-20T19:50:00","2024-06-20T19:55:00",799.64573159999998,95.429466000000005]
["2024-06-21T02:50:00","2024-06-21T02:55:00",455.60483640000001,-9.1205795999999992]
["2024-06-21T07:05:00","2024-06-21T07:10:00",744.7514496,100.32318840000001]
["2024-06-21T12:15:00","2024-06-21T12:20:00",724.18954559999997,111.922476]
["2024-06-21T15:45:00","2024-06-21T15:50:00",727.56058559999997,90.856331999999995]
["2024-06-21T20:05:00","2024-06-21T20:10:00",764.90115600000001,80.989108799999997]
["2024-06-22T00:20:00","2024-06-22T00:25:00",527.05631159999996,-0.66808559999999995]
["2024-06-22T04:40:00","2024-06-22T04:45:00",438.97475400000002,-18.171122400000002]
["2024-06-22T09:00:00","2024-06-22T09:05:00",619.13703480000004,55.045317599999997]
["2024-06-22T13:15:00","2024-06-22T13:20:00",536.37422760000004,23.394798000000002]
["2024-06-22T15:05:00","2024-06-22T15:10:00",591.38660879999998,27.092241600000001]
["2024-06-22T21:55:00","2024-06-22T22:00:00",622.38065040000004,24.657143999999999]
["2024-06-23T02:10:00","2024-06-23T02:15:00",447.30416159999999,-23.715007199999999]
["2024-06-23T07:10:00","2024-06-23T07:15:00",525.79502160000004,2.1646116000000002]
["2024-06-23T10:50:00","2024-06-23T10:55:00",486.74789520000002,25.8748188]
["2024-06-23T15:05:00","2024-06-23T15:10:00",439.69491479999999,1.2119004]
["2024-06-23T19:15:00","2024-06-23T19:20:00",747.33250439999995,66.104545200000004]
["2024-06-23T23:45:00","2024-06-23T23:50:00",525.01335359999996,-7.4524163999999997]
["2024-06-24T04:00:00","2024-06-24T04:05:00",437.5307148,-22.357335599999999]
["2024-06-24T07:20:00","2024-06-24T07:25:00",772.90824480000003,110.8576956]
["2024-06-24T12:40:00","2024-06-24T12:45:00",686.14077840000004,102.3133728]
["2024-06-24T17:00:00","2024-06-24T17:05:00",811.3202364,110.2824744]
["2024-06-24T19:25:00","2024-06-24T19:30:00",844.41590759999997,113.8327632]
["2024-06-25T01:35:00","2024-06-25T01:40:00",462.33029759999999,-7.8625512000000004]
["2024-06-25T05:55:00","2024-06-25T06:00:00",547.19806319999998,24.109426800000001]
["2024-06-25T07:30:00","2024-06-25T07:35:00",761.47560480000004,110.622936]
["2024-06-25T14:35:00","2024-06-25T14:40:00",565.70732880000003,75.647679600000004]
["2024-06-25T18:50:00","2024-06-25T18:55:00",796.88773319999996,119.70216000000001]
["2024-06-25T23:05:00","2024-06-25T23:10:00",572.75664119999999,17.1528864]
["2024-06-26T02:15:00","2024-06-26T02:20:00",435.86835480000002,-15.110849999999999]
["2024-06-26T07:45:00","2024-06-26T07:50:00",763.38561000000004,111.927846]
["2024-06-26T12:00:00","2024-06-26T12:05:00",599.33807639999998,76.329764400000002]
["2024-06-26T14:20:00","2024-06-26T14:25:00",601.6936584,78.492085200000005]
["2024-06-26T20:40:00","2024-06-26T20:45:00",737.99100239999996,89.029657200000003]
["2024-06-27T01:00:00","2024-06-27T01:05:00",469.32092399999999,-6.9945936]
["2024-06-27T02:25:00","2024-06-27T02:30:00",434.03234400000002,-14.7436788]
["2024-06-27T09:35:00","2024-06-27T09:40:00",662.09439840000005,113.4933444]
["2024-06-27T13:55:00","2024-06-27T14:00:00",544.45049640000002,77.436384000000004]
["2024-06-27T14:30:00","2024-06-27T14:35:00",542.99741640000002,75.327868800000005]
["2024-06-27T22:35:00","2024-06-27T22:40:00",597.29948999999999,32.343359999999997]
["2024-06-28T02:50:00","2024-06-28T02:55:00",435.03183480000001,-15.192334799999999]
["2024-06-28T06:55:00","2024-06-28T07:00:00",660.46211640000001,70.365524399999998]
["2024-06-28T07:15:00","2024-06-28T07:20:00",705.10219319999999,90.379010399999999]
["2024-06-28T11:30:00","2024-06-28T11:35:00",552.24205440000003,81.761564399999997]
["2024-06-28T19:00:00","2024-06-28T19:05:00",723.71303039999998,81.6469776]
["2024-06-28T20:10:00","2024-06-28T20:15:00",679.10282040000004,61.786456800000003]
["2024-06-29T00:25:00","2024-06-29T00:30:00",475.78562520000003,-10.467053999999999]
["2024-06-29T04:45:00","2024-06-29T04:50:00",401.0048352,-25.335880800000002]
["2024-06-29T09:25:00","2024-06-29T09:30:00",620.31454680000002,40.621730399999997]
["2024-06-29T13:20:00","2024-06-29T13:25:00",649.44118200000003,46.987089599999997]
["2024-06-29T17:40:00","2024-06-29T17:45:00",714.75942120000002,65.132177999999996]
["2024-06-30T01:50:00","2024-06-30T01:55:00",431.89139399999999,-26.263838400000001]
["2024-06-30T02:15:00","2024-06-30T02:20:00",422.25287279999998,-28.783892399999999]
["2024-06-30T06:35:00","2024-06-30T06:40:00",455.32573200000002,-19.1635116]
["2024-06-30T13:55:00","2024-06-30T14:00:00",475.34938319999998,14.706933599999999]
["2024-06-30T15:15:00","2024-06-30T15:20:00",554.5398768,16.949936399999999]
["2024-06-30T19:30:00","2024-06-30T19:35:00",720.99773879999998,70.173250800000005]
["2024-07-01T02:00:00","2024-07-01T02:05:00",424.6761444,-25.398691199999998]
["2024-07-01T04:10:00","2024-07-01T04:15:00",423.70934879999999,-23.983628400000001]
["2024-07-01T08:25:00","2024-07-01T08:30:00",767.32840080000005,130.89384240000001]
["2024-07-01T13:45:00","2024-07-01T13:50:00",639.59764199999995,93.963255599999997]
["2024-07-01T17:05:00","2024-07-01T17:10:00",778.52731319999998,113.33552280000001]
["2024-07-01T21:20:00","2024-07-01T21:25:00",713.89549199999999,83.482843200000005]
["2024-07-02T01:40:00","2024-07-02T01:45:00",465.08554320000002,-7.4035751999999997]
["2024-07-02T08:50:00","2024-07-02T08:55:00",784.54851480000002,156.95974799999999]
["2024-07-02T10:15:00","2024-07-02T10:20:00",674.80650360000004,131.015244]
["2024-07-02T14:35:00","2024-07-02T14:40:00",587.48694599999999,85.747591200000002]
["2024-07-02T20:55:00","2024-07-02T21:00:00",792.62531760000002,109.39866600000001]
["2024-07-02T23:15:00","2024-07-02T23:20:00",638.97236880000003,36.432845999999998]
["2024-07-03T03:30:00","2024-07-03T03:35:00",484.09148399999998,-5.2268087999999997]
["2024-07-03T09:00:00","2024-07-03T09:05:00",850.61132999999995,168.18008760000001]
["2024-07-03T12:10:00","2024-07-03T12:15:00",601.27156439999999,101.44163039999999]
["2024-07-03T16:25:00","2024-07-03T16:30:00",720.972624,87.780153600000006]
["2024-07-03T21:05:00","2024-07-03T21:10:00",789.69744360000004,105.143568]
["2024-07-04T01:05:00","2024-07-04T01:10:00",519.80475000000001,1.3203456]
["2024-07-04T05:20:00","2024-07-04T05:25:00",548.56165559999999,16.3593276]
["2024-07-04T08:50:00","2024-07-04T08:55:00",878.86570440000003,165.28682520000001]
["2024-07-04T14:00:00","2024-07-04T14:05:00",806.91373199999998,144.75743879999999]
["2024-07-04T18:15:00","2024-07-04T18:20:00",871.64985119999994,142.7268492]
["2024-07-05T01:15:00","2024-07-05T01:20:00",490.94619119999999,-6.1106819999999997]
["2024-07-05T02:55:00","2024-07-05T03:00:00",449.8321416,-14.937116400000001]
["2024-07-05T07:15:00","2024-07-05T07:20:00",708.03514199999995,103.6019148]
["2024-07-05T11:30:00","2024-07-05T11:35:00",759.19148159999997,122.624718]
["2024-07-05T16:00:00","2024-07-05T16:05:00",729.77898240000002,97.901767199999995]
["2024-07-05T20:10:00","2024-07-05T20:15:00",733.64864639999996,72.870807600000006]
["2024-07-06T00:25:00","2024-07-06T00:30:00",519.83467680000001,-4.2243947999999998]
["2024-07-06T04:05:00","2024-07-06T04:10:00",430.91032919999998,-22.8474912]
["2024-07-06T09:05:00","2024-07-06T09:10:00",648.72758999999996,65.266250400000004]
["2024-07-06T13:20:00","2024-07-06T13:25:00",472.96115759999998,28.987357200000002]
["2024-07-06T20:10:00","2024-07-06T20:15:00",727.74881159999995,79.144615200000004]
["2024-07-06T22:00:00","2024-07-06T22:05:00",649.86955680000005,54.887656800000002]
["2024-07-07T02:15:00","2024-07-07T02:20:00",447.1303944,-25.2576228]
["2024-07-07T08:15:00","2024-07-07T08:20:00",570.3697932,11.704718400000001]
["2024-07-07T10:55:00","2024-07-07T11:00:00",462.72471719999999,21.9632784]
["2024-07-07T15:15:00","2024-07-07T15:20:00",464.06204880000001,9.6184800000000001E-2]
["2024-07-07T20:20:00","2024-07-07T20:25:00",703.05484200000001,63.358778399999998]
["2024-07-07T23:50:00","2024-07-07T23:55:00",526.73211839999999,-6.6788195999999997]
["2024-07-08T04:10:00","2024-07-08T04:15:00",434.68533480000002,-20.954037599999999]
["2024-07-08T08:25:00","2024-07-08T08:30:00",775.12260240000001,128.95950120000001]
["2024-07-08T12:45:00","2024-07-08T12:50:00",654.81830160000004,96.744759599999995]
["2024-07-08T17:05:00","2024-07-08T17:10:00",759.04474919999996,104.4250296]
["2024-07-08T21:20:00","2024-07-08T21:25:00",661.35616319999997,52.8186204]
["2024-07-09T03:10:00","2024-07-09T03:15:00",415.05438359999999,-19.577096399999999]
["2024-07-09T06:00:00","2024-07-09T06:05:00",508.20697560000002,7.5493800000000002]
["2024-07-09T10:15:00","2024-07-09T10:20:00",705.98482439999998,112.8933672]
["2024-07-09T15:15:00","2024-07-09T15:20:00",727.23929639999994,95.049477600000003]
["2024-07-09T18:55:00","2024-07-09T19:00:00",779.48936879999997,97.484428800000003]
["2024-07-09T23:10:00","2024-07-09T23:15:00",570.96564839999996,27.3600624]
["2024-07-10T03:20:00","2024-07-10T03:25:00",422.98098119999997,-7.5326988000000004]
["2024-07-10T07:50:00","2024-07-10T07:55:00",718.99268159999997,114.75550079999999]
["2024-07-10T12:10:00","2024-07-10T12:15:00",585.73619759999997,92.909054400000002]
["2024-07-10T15:25:00","2024-07-10T15:30:00",550.65934440000001,60.809816400000003]
["2024-07-10T20:45:00","2024-07-10T20:50:00",723.99913079999999,76.915255200000004]
["2024-07-11T01:05:00","2024-07-11T01:10:00",477.33380399999999,-8.6440032000000002]
["2024-07-11T03:30:00","2024-07-11T03:35:00",432.59248919999999,-18.061029600000001]
["2024-07-11T09:45:00","2024-07-11T09:50:00",781.93869840000002,140.20651319999999]
["2024-07-11T14:00:00","2024-07-11T14:05:00",726.23005680000006,109.1149752]
["2024-07-11T19:55:00","2024-07-11T20:00:00",780.02640120000001,100.493292]
["2024-07-11T22:40:00","2024-07-11T22:45:00",601.48462800000004,45.739564799999997]
["2024-07-12T02:55:00","2024-07-12T03:00:00",425.37419879999999,-19.226899199999998]
["2024-07-12T07:10:00","2024-07-12T07:15:00",642.43518359999996,65.790337199999996]
["2024-07-12T10:20:00","2024-07-12T10:25:00",706.98758520000001,102.2841336]
["2024-07-12T15:50:00","2024-07-12T15:55:00",549.92658359999996,41.767131599999999]
["2024-07-12T20:10:00","2024-07-12T20:15:00",705.34657679999998,59.3352]
["2024-07-12T22:25:00","2024-07-12T22:30:00",611.39387399999998,26.186854799999999]
["2024-07-13T04:45:00","2024-07-13T04:50:00",417.58764960000002,-25.039029599999999]
["2024-07-13T09:05:00","2024-07-13T09:10:00",552.61349640000003,34.827433200000002]
["2024-07-13T14:50:00","2024-07-13T14:55:00",543.02146679999998,15.393012000000001]
["2024-07-13T17:40:00","2024-07-13T17:45:00",698.17784759999995,66.943605599999998]
["2024-07-13T22:00:00","2024-07-13T22:05:00",590.2672824,11.7996096]
["2024-07-14T02:55:00","2024-07-14T03:00:00",410.36957280000001,-31.7338536]
["2024-07-14T06:40:00","2024-07-14T06:45:00",455.72686199999998,-18.593874]
["2024-07-14T10:55:00","2024-07-14T11:00:00",510.55278720000001,25.359999599999998]
["2024-07-14T15:00:00","2024-07-14T15:05:00",509.55031439999999,14.2034688]
["2024-07-14T19:35:00","2024-07-14T19:40:00",741.01643639999998,76.575339600000007]
["2024-07-14T23:50:00","2024-07-14T23:55:00",517.22434320000002,-9.7648428000000003]
["2024-07-15T04:10:00","2024-07-15T04:15:00",433.47422039999998,-23.0242848]
["2024-07-15T05:25:00","2024-07-15T05:30:00",492.6565152,-4.7986896000000003]
["2024-07-15T12:45:00","2024-07-15T12:50:00",803.53829759999996,127.31353799999999]
["2024-07-15T17:05:00","2024-07-15T17:10:00",883.85251440000002,143.18030880000001]
["2024-07-15T21:50:00","2024-07-15T21:55:00",707.31188520000001,58.663420799999997]
["2024-07-16T01:40:00","2024-07-16T01:45:00",472.04464200000001,-6.1125384]
["2024-07-16T06:00:00","2024-07-16T06:05:00",547.74337200000002,20.863795199999998]
["2024-07-16T09:55:00","2024-07-16T10:00:00",718.69066080000005,105.55737240000001]
["2024-07-16T14:40:00","2024-07-16T14:45:00",673.1611236,88.254801599999993]
["2024-07-16T18:55:00","2024-07-16T19:00:00",797.15938679999999,109.9628112]
["2024-07-16T22:00:00","2024-07-16T22:05:00",625.94905559999995,29.946701999999998]
["2024-07-17T03:35:00","2024-07-17T03:40:00",435.1404192,-16.1019252]
["2024-07-17T07:50:00","2024-07-17T07:55:00",764.43018600000005,110.8894308]
["2024-07-17T09:45:00","2024-07-17T09:50:00",734.07467280000003,111.85253160000001]
["2024-07-17T16:30:00","2024-07-17T16:35:00",731.81105760000003,87.392191199999999]
["2024-07-17T20:45:00","2024-07-17T20:50:00",754.00959,104.2858284]
["2024-07-17T21:50:00","2024-07-17T21:55:00",678.93548880000003,53.0343576]
["2024-07-18T05:25:00","2024-07-18T05:30:00",507.67950839999997,6.934596]
["2024-07-18T09:40:00","2024-07-18T09:45:00",747.57198840000001,147.36489599999999]
["2024-07-18T14:00:00","2024-07-18T14:05:00",671.82083639999996,97.449426000000003]
["2024-07-18T16:55:00","2024-07-18T17:00:00",797.05928759999995,107.1271356]
["2024-07-18T22:40:00","2024-07-18T22:45:00",615.87248520000003,42.435476399999999]
["2024-07-19T02:55:00","2024-07-19T03:00:00",448.53100920000003,-15.690258]
["2024-07-19T05:00:00","2024-07-19T05:05:00",489.24530520000002,-2.9808012000000002]
["2024-07-19T11:35:00","2024-07-19T11:40:00",837.80209920000004,147.32967239999999]
["2024-07-19T15:50:00","2024-07-19T15:55:00",814.00828079999997,109.7287176]
["2024-07-19T17:05:00","2024-07-19T17:10:00",850.50762480000003,117.4038432]
["2024-07-20T00:30:00","2024-07-20T00:35:00",518.58279479999999,-6.5309087999999997]
["2024-07-20T04:45:00","2024-07-20T04:50:00",425.27405160000001,-24.863698800000002]
["2024-07-20T09:10:00","2024-07-20T09:15:00",658.03102560000002,52.553698799999999]
["2024-07-20T13:25:00","2024-07-20T13:30:00",636.35223480000002,41.832835199999998]
["2024-07-20T17:40:00","2024-07-20T17:45:00",742.54112880000002,63.062901599999996]
["2024-07-20T21:15:00","2024-07-20T21:20:00",662.74933559999999,32.193082799999999]
["2024-07-21T02:20:00","2024-07-21T02:25:00",437.19809880000003,-28.755909599999999]
["2024-07-21T06:40:00","2024-07-21T06:45:00",470.71403520000001,-15.3100044]
["2024-07-21T09:20:00","2024-07-21T09:25:00",560.67035039999996,26.8211136]
["2024-07-21T15:15:00","2024-07-21T15:20:00",539.7066456,9.10731]
["2024-07-21T19:35:00","2024-07-21T19:40:00",691.02976079999996,41.4904656]
["2024-07-21T23:50:00","2024-07-21T23:55:00",484.29932159999998,-16.813468799999999]
["2024-07-22T00:05:00","2024-07-22T00:10:00",468.41231879999998,-20.526027599999999]
["2024-07-22T04:15:00","2024-07-22T04:20:00",401.598612,-31.027755599999999]
["2024-07-22T08:30:00","2024-07-22T08:35:00",721.73000760000002,103.7670576]
["2024-07-22T16:10:00","2024-07-22T16:15:00",657.91166639999994,64.318105200000005]
["2024-07-22T17:10:00","2024-07-22T17:15:00",709.17824640000003,68.826253199999996]
["2024-07-22T21:25:00","2024-07-22T21:30:00",633.68263079999997,38.171977200000001]
["2024-07-23T04:15:00","2024-07-23T04:20:00",416.81695439999999,-17.105296800000001]
["2024-07-23T06:05:00","2024-07-23T06:10:00",534.07121759999995,22.339886400000001]
["2024-07-23T10:25:00","2024-07-23T10:30:00",539.65167840000004,81.997886399999999]
["2024-07-23T16:20:00","2024-07-23T16:25:00",596.20540440000002,54.942326399999999]
["2024-07-23T19:00:00","2024-07-23T19:05:00",735.30154800000003,74.099453999999994]
["2024-07-23T23:20:00","2024-07-23T23:25:00",541.82148719999998,8.0555219999999998]
["2024-07-24T04:25:00","2024-07-24T04:30:00",430.55205239999998,-17.4757116]
["2024-07-24T07:55:00","2024-07-24T08:00:00",751.2871116,106.82203079999999]
["2024-07-24T12:15:00","2024-07-24T12:20:00",662.99073120000003,105.40194839999999]
["2024-07-24T16:30:00","2024-07-24T16:35:00",684.43621919999998,77.183473199999995]
["2024-07-24T23:10:00","2024-07-24T23:15:00",564.86361959999999,14.055059999999999]
["2024-07-25T01:10:00","2024-07-25T01:15:00",462.44417279999999,-8.1204467999999999]
["2024-07-25T05:25:00","2024-07-25T05:30:00",478.33064280000002,1.5133920000000001]
["2024-07-25T11:15:00","2024-07-25T11:20:00",765.4236396,119.451018]
["2024-07-25T14:05:00","2024-07-25T14:10:00",761.82628079999995,117.2408592]
["2024-07-25T18:20:00","2024-07-25T18:25:00",822.22841640000001,105.0383028]
["2024-07-25T23:20:00","2024-07-25T23:25:00",573.98893199999998,15.3292284]
["2024-07-26T03:00:00","2024-07-26T03:05:00",443.547552,-16.044606000000002]
["2024-07-26T07:20:00","2024-07-26T07:25:00",739.24113720000003,100.2777924]
["2024-07-26T11:25:00","2024-07-26T11:30:00",522.35874479999995,90.070023599999999]
["2024-07-26T15:55:00","2024-07-26T16:00:00",580.19300639999994,47.782105199999997]
["2024-07-26T20:15:00","2024-07-26T20:20:00",709.70176919999994,58.521839999999997]
["2024-07-27T03:50:00","2024-07-27T03:55:00",415.06132559999998,-25.711831199999999]
["2024-07-27T04:55:00","2024-07-27T05:00:00",424.21638239999999,-23.200514399999999]
["2024-07-27T09:10:00","2024-07-27T09:15:00",608.99300040000003,40.017279600000002]
["2024-07-27T15:55:00","2024-07-27T16:00:00",649.27081680000003,44.594775599999998]
["2024-07-27T17:50:00","2024-07-27T17:55:00",747.84700320000002,65.773099200000004]
["2024-07-27T22:05:00","2024-07-27T22:10:00",646.94416079999996,27.280958399999999]
["2024-07-28T02:20:00","2024-07-28T02:25:00",454.02900360000001,-25.713932400000001]
["2024-07-28T06:20:00","2024-07-28T06:25:00",477.37895759999998,-16.274384399999999]
["2024-07-28T11:00:00","2024-07-28T11:05:00",553.56528479999997,37.727611199999998]
["2024-07-28T15:20:00","2024-07-28T15:25:00",602.09700840000005,27.632350800000001]
["2024-07-28T18:25:00","2024-07-28T18:30:00",791.69337359999997,93.564004800000006]
["2024-07-28T23:55:00",45502,518.96661719999997,-9.3889464]
["2024-07-29T04:15:00","2024-07-29T04:20:00",440.34568560000002,-24.4274016]
["2024-07-29T10:50:00","2024-07-29T10:55:00",778.58152080000002,128.56456320000001]
["2024-07-29T12:50:00","2024-07-29T12:55:00",729.64375919999998,112.5678564]
["2024-07-29T17:10:00","2024-07-29T17:15:00",804.57470639999997,120.2672784]
["2024-07-29T22:55:00","2024-07-29T23:00:00",570.91591919999996,15.280048799999999]
["2024-07-30T01:50:00","2024-07-30T01:55:00",450.02431319999999,-14.6944368]
["2024-07-30T06:05:00","2024-07-30T06:10:00",570.8279976,30.272805600000002]
["2024-07-30T11:00:00","2024-07-30T11:05:00",558.90851280000004,89.061492000000001]
["2024-07-30T14:45:00","2024-07-30T14:50:00",484.57873080000002,66.371784000000005]
["2024-07-30T19:00:00","2024-07-30T19:05:00",812.62697760000003,110.4330708]
["2024-07-30T22:45:00","2024-07-30T22:50:00",609.11187959999995,27.6903288]
["2024-07-31T03:40:00","2024-07-31T03:45:00",468.22268279999997,-10.326378]
["2024-07-31T07:55:00","2024-07-31T08:00:00",846.906882,148.2026232]
["2024-07-31T12:15:00","2024-07-31T12:20:00",740.39705279999998,134.34849360000001]
["2024-07-31T17:50:00","2024-07-31T17:55:00",855.66899999999998,116.27451240000001]
["2024-07-31T20:50:00","2024-07-31T20:55:00",824.03295960000003,99.737324400000006]
["2024-08-01T01:10:00","2024-08-01T01:15:00",514.03677600000003,-5.9655947999999999]
["2024-08-01T05:55:00","2024-08-01T06:00:00",616.1007108,36.174692399999998]
["2024-08-01T09:50:00","2024-08-01T09:55:00",744.05847960000006,136.02239639999999]
["2024-08-01T14:05:00","2024-08-01T14:10:00",504.01049640000002,78.076589999999996]
["2024-08-01T18:00:00","2024-08-01T18:05:00",819.04205039999999,102.9209604]
["2024-08-01T22:45:00","2024-08-01T22:50:00",634.41430679999996,31.190142000000002]
["2024-08-02T03:00:00","2024-08-02T03:05:00",468.13200840000002,-13.9432008]
["2024-08-02T05:45:00","2024-08-02T05:50:00",561.82073879999996,16.9482444]
["2024-08-02T11:40:00","2024-08-02T11:45:00",527.27679000000001,90.907335599999996]
["2024-08-02T15:55:00","2024-08-02T16:00:00",651.10887000000002,62.223711600000001]
["2024-08-02T22:10:00","2024-08-02T22:15:00",636.78459120000002,28.013003999999999]
["2024-08-03T00:35:00","2024-08-03T00:40:00",490.02192839999998,-15.552400799999999]
["2024-08-03T04:50:00","2024-08-03T04:55:00",424.23629879999999,-25.9505628]
["2024-08-03T10:15:00","2024-08-03T10:20:00",630.16420919999996,48.437196]
["2024-08-03T13:30:00","2024-08-03T13:35:00",497.81919720000002,13.3219788]
["2024-08-03T17:50:00","2024-08-03T17:55:00",667.24852920000001,53.217591599999999]
["2024-08-03T22:05:00","2024-08-03T22:10:00",611.18538479999995,14.884836]
["2024-08-04T01:00:00","2024-08-04T01:05:00",479.2041456,-22.466386799999999]
["2024-08-04T06:45:00","2024-08-04T06:50:00",500.43476279999999,-9.9157715999999994]
["2024-08-04T11:00:00","2024-08-04T11:05:00",418.67490600000002,12.959885999999999]
["2024-08-04T13:05:00","2024-08-04T13:10:00",347.33409239999997,2.8719071999999999]
["2024-08-04T19:40:00","2024-08-04T19:45:00",711.5805924,53.334261599999998]
["2024-08-04T23:55:00",45509,499.09097159999999,-14.3309616]
["2024-08-05T05:10:00","2024-08-05T05:15:00",474.81231600000001,-10.538800800000001]
["2024-08-05T08:35:00","2024-08-05T08:40:00",794.8059528,125.47981799999999]
["2024-08-05T12:50:00","2024-08-05T12:55:00",530.55248159999996,86.594493600000007]
["2024-08-05T17:15:00","2024-08-05T17:20:00",727.42319280000004,74.371246799999994]
["2024-08-05T21:30:00","2024-08-05T21:35:00",695.18528400000002,63.637762799999997]
["2024-08-06T01:50:00","2024-08-06T01:55:00",457.82430240000002,-12.9472956]
["2024-08-06T05:20:00","2024-08-06T05:25:00",504.14196479999998,2.3619083999999999]
["2024-08-06T10:25:00","2024-08-06T10:30:00",573.68984880000005,93.207828000000006]
["2024-08-06T14:45:00","2024-08-06T14:50:00",468.9256896,60.852861599999997]
["2024-08-06T19:00:00","2024-08-06T19:05:00",763.34579280000003,91.212509999999995]
["2024-08-07T00:25:00","2024-08-07T00:30:00",494.41336200000001,-5.4926687999999997]
["2024-08-07T03:40:00","2024-08-07T03:45:00",430.4384508,-18.2784792]
["2024-08-07T07:55:00","2024-08-07T08:00:00",755.72625960000005,131.4714468]
["2024-08-07T12:10:00","2024-08-07T12:15:00",471.88814760000002,74.063607599999997]
["2024-08-07T16:35:00","2024-08-07T16:40:00",617.31298679999998,55.889697599999998]
["2024-08-07T20:50:00","2024-08-07T20:55:00",702.85806600000001,75.141301200000001]
["2024-08-08T00:15:00","2024-08-08T00:20:00",504.49390080000001,-1.9069356]
["2024-08-08T05:30:00","2024-08-08T05:35:00",496.26616200000001,4.3843199999999998]
["2024-08-08T09:50:00","2024-08-08T09:55:00",687.17294040000002,104.0285868]
["2024-08-08T12:20:00","2024-08-08T12:25:00",626.33336640000005,91.825417200000004]
["2024-08-08T18:25:00","2024-08-08T18:30:00",822.4474884,104.6385708]
["2024-08-08T22:45:00","2024-08-08T22:50:00",573.25857840000003,17.005990799999999]
["2024-08-09T00:25:00","2024-08-09T00:30:00",487.77508440000003,-6.7215347999999997]
["2024-08-09T07:20:00","2024-08-09T07:25:00",689.85743760000003,92.857040400000002]
["2024-08-09T11:40:00","2024-08-09T11:45:00",449.5359828,69.763419600000006]
["2024-08-09T16:50:00","2024-08-09T16:55:00",585.31134239999994,49.8129828]
["2024-08-09T20:20:00","2024-08-09T20:25:00",659.96753760000001,52.026690000000002]
["2024-08-10T00:35:00","2024-08-10T00:40:00",470.4529488,-15.286554000000001]
["2024-08-10T04:50:00","2024-08-10T04:55:00",407.86287240000001,-24.544250399999999]
["2024-08-10T07:15:00","2024-08-10T07:20:00",520.58487720000005,13.592748]
["2024-08-10T13:30:00","2024-08-10T13:35:00",312.05390999999997,1.529328]
["2024-08-10T17:45:00","2024-08-10T17:50:00",583.41867839999998,21.469422000000002]
["2024-08-10T19:20:00","2024-08-10T19:25:00",599.12532959999999,27.375081600000001]
["2024-08-11T02:25:00","2024-08-11T02:30:00",400.07341919999999,-37.303612800000003]
["2024-08-11T06:45:00","2024-08-11T06:50:00",454.97086439999998,-13.933327200000001]
["2024-08-11T07:25:00","2024-08-11T07:30:00",484.39282680000002,-7.6234668000000001]
["2024-08-11T15:20:00","2024-08-11T15:25:00",327.77705159999999,-8.4682931999999997]
["2024-08-11T19:40:00","2024-08-11T19:45:00",606.92968440000004,21.221972399999999]
["2024-08-11T23:50:00","2024-08-11T23:55:00",464.61730560000001,-21.3439476]
["2024-08-12T04:20:00","2024-08-12T04:25:00",406.40134440000003,-29.364536399999999]
["2024-08-12T08:35:00","2024-08-12T08:40:00",649.90903920000005,89.812615199999996]
["2024-08-12T11:55:00","2024-08-12T12:00:00",397.70686319999999,64.350937200000004]
["2024-08-12T17:15:00","2024-08-12T17:20:00",596.45035559999997,53.466487200000003]
["2024-08-12T21:30:00","2024-08-12T21:35:00",591.08357880000005,25.548576000000001]
[45517,"2024-08-13T00:05:00",471.36112200000002,-7.7319144]
["2024-08-13T06:10:00","2024-08-13T06:15:00",531.36332879999998,16.811377199999999]
["2024-08-13T10:25:00","2024-08-13T10:30:00",445.63138679999997,61.149020399999998]
["2024-08-13T14:45:00","2024-08-13T14:50:00",409.99849799999998,54.703685999999998]
["2024-08-13T18:45:00","2024-08-13T18:50:00",648.78483359999996,55.865490000000001]
["2024-08-13T23:20:00","2024-08-13T23:25:00",498.2200848,1.1165160000000001]
["2024-08-14T03:40:00","2024-08-14T03:45:00",397.12791959999998,-21.517083599999999]
["2024-08-14T06:50:00","2024-08-14T06:55:00",584.41961279999998,53.325525599999999]
["2024-08-14T12:15:00","2024-08-14T12:20:00",458.3737284,66.3883692]
["2024-08-14T16:35:00","2024-08-14T16:40:00",528.13495920000003,46.855795200000003]
["2024-08-14T18:55:00","2024-08-14T19:00:00",635.21551320000003,55.974031199999999]
["2024-08-14T21:00:00","2024-08-14T21:05:00",577.30363439999996,41.033415599999998]
["2024-08-15T01:15:00","2024-08-15T01:20:00",414.48148200000003,5.1675779999999998]
["2024-08-15T07:00:00","2024-08-15T07:05:00",593.8347096,48.858910799999997]
["2024-08-15T09:55:00","2024-08-15T10:00:00",484.43242559999999,74.522557199999994]
["2024-08-15T14:10:00","2024-08-15T14:15:00",591.54375000000005,67.621947599999999]
["2024-08-15T18:45:00","2024-08-15T18:50:00",628.50024240000005,53.975740799999997]
["2024-08-15T22:50:00","2024-08-15T22:55:00",482.52119279999999,-4.0453476000000004]
["2024-08-16T03:05:00","2024-08-16T03:10:00",385.2724068,-23.979046799999999]
["2024-08-16T11:10:00","2024-08-16T11:15:00",567.94533839999997,69.619292400000006]
["2024-08-16T11:45:00","2024-08-16T11:50:00",550.36794840000005,64.967852399999998]
["2024-08-16T16:00:00","2024-08-16T16:05:00",532.92966720000004,41.224976400000003]
["2024-08-16T20:20:00","2024-08-16T20:25:00",627.93330839999999,49.771971600000001]
["2024-08-17T01:55:00","2024-08-17T02:00:00",408.54059280000001,-26.460159600000001]
["2024-08-17T05:00:00","2024-08-17T05:05:00",393.9508884,-29.505783600000001]
["2024-08-17T09:15:00","2024-08-17T09:20:00",559.64162160000001,24.587032799999999]
["2024-08-17T14:00:00","2024-08-17T14:05:00",442.26776999999998,9.6363731999999995]
["2024-08-17T17:55:00","2024-08-17T18:00:00",592.00129200000003,24.1095276]
["2024-08-17T22:10:00","2024-08-17T22:15:00",519.55976999999996,-8.4936779999999992]
["2024-08-18T06:05:00","2024-08-18T06:10:00",391.11236400000001,-33.962490000000003]
["2024-08-18T06:50:00","2024-08-18T06:55:00",406.73314440000001,-30.50817]
["2024-08-18T11:05:00","2024-08-18T11:10:00",353.28502079999998,-10.894808400000001]
["2024-08-18T18:10:00","2024-08-18T18:15:00",612.0344844,26.148582000000001]
["2024-08-18T19:45:00","2024-08-18T19:50:00",613.10790959999997,32.540900399999998]
[45523,"2024-08-19T00:05:00",458.94807839999999,-22.4711496]
["2024-08-19T06:15:00","2024-08-19T06:20:00",545.98684800000001,17.921967599999999]
["2024-08-19T08:40:00","2024-08-19T08:45:00",690.71286959999998,97.868695200000005]
["2024-08-19T13:00:00","2024-08-19T13:05:00",394.63958280000003,60.817548000000002]
["2024-08-19T17:15:00","2024-08-19T17:20:00",609.57504119999999,42.5868684]
["2024-08-19T21:00:00","2024-08-19T21:05:00",636.44137799999999,39.001346400000003]
["2024-08-20T01:55:00","2024-08-20T02:00:00",411.3397248,-20.324581200000001]
["2024-08-20T06:10:00","2024-08-20T06:15:00",531.8051352,24.171320399999999]
["2024-08-20T13:25:00","2024-08-20T13:30:00",669.41404920000002,88.489435200000003]
["2024-08-20T14:50:00","2024-08-20T14:55:00",500.96119440000001,69.821983200000005]
["2024-08-20T19:05:00","2024-08-20T19:10:00",710.52862560000005,74.617928399999997]
["2024-08-21T01:10:00","2024-08-21T01:15:00",428.59576079999999,-13.5805416]
["2024-08-21T03:45:00","2024-08-21T03:50:00",401.10896279999997,-19.787353199999998]
["2024-08-21T08:00:00","2024-08-21T08:05:00",621.78831360000004,77.766207600000001]
["2024-08-21T13:15:00","2024-08-21T13:20:00",529.22461920000001,64.010224800000003]
["2024-08-21T16:40:00","2024-08-21T16:45:00",572.62935960000004,43.156692]
["2024-08-21T21:00:00","2024-08-21T21:05:00",618.00016559999995,38.912192400000002]
["2024-08-22T01:20:00","2024-08-22T01:25:00",422.26597679999998,-16.498354800000001]
["2024-08-22T05:35:00","2024-08-22T05:40:00",465.91231800000003,-1.4767199999999999E-2]
["2024-08-22T09:55:00","2024-08-22T10:00:00",477.86621400000001,73.508347200000003]
["2024-08-22T13:25:00","2024-08-22T13:30:00",407.14764839999998,63.549979200000003]
["2024-08-22T18:30:00","2024-08-22T18:35:00",666.85648319999996,63.9669588]
["2024-08-22T22:50:00","2024-08-22T22:55:00",515.30627400000003,6.1648680000000002]
["2024-08-23T03:05:00","2024-08-23T03:10:00",399.38473199999999,-22.9092336]
["2024-08-23T08:10:00","2024-08-23T08:15:00",630.02160240000001,73.026056400000002]
["2024-08-23T11:45:00","2024-08-23T11:50:00",457.18378680000001,66.969502800000001]
["2024-08-23T16:00:00","2024-08-23T16:05:00",592.86381240000003,44.2586832]
["2024-08-23T20:15:00","2024-08-23T20:20:00",621.53069879999998,29.485821600000001]
["2024-08-24T00:40:00","2024-08-24T00:45:00",440.38988160000002,-19.452970799999999]
["2024-08-24T04:55:00","2024-08-24T05:00:00",379.81249680000002,-30.186423600000001]
["2024-08-24T08:20:00","2024-08-24T08:25:00",417.02394479999998,-3.2446320000000002]
["2024-08-24T13:35:00","2024-08-24T13:40:00",248.98876440000001,7.9956060000000004]
["2024-08-24T17:55:00","2024-08-24T18:00:00",505.78496280000002,-5.5461011999999998]
["2024-08-24T20:25:00","2024-08-24T20:30:00",495.90564000000001,-11.9182164]
["2024-08-25T02:30:00","2024-08-25T02:35:00",344.76344399999999,-48.758012399999998]
["2024-08-25T06:50:00","2024-08-25T06:55:00",385.5653532,-34.573465200000001]
["2024-08-25T12:50:00","2024-08-25T12:55:00",220.96070280000001,-0.39141599999999999]
["2024-08-25T15:30:00","2024-08-25T15:35:00",468.699342,-7.1671788000000003]
["2024-08-25T19:45:00","2024-08-25T19:50:00",538.84136160000003,-2.2594764000000001]
["2024-08-26T00:55:00","2024-08-26T01:00:00",394.04962440000003,-32.371468800000002]
["2024-08-26T04:25:00","2024-08-26T04:30:00",377.08596119999999,-32.363809199999999]
["2024-08-26T08:40:00","2024-08-26T08:45:00",577.70792759999995,68.083089599999994]
["2024-08-26T12:55:00","2024-08-26T13:00:00",496.3667916,63.538612800000003]
["2024-08-26T15:20:00","2024-08-26T15:25:00",537.88331159999996,53.830570799999997]
["2024-08-26T21:35:00","2024-08-26T21:40:00",560.50222199999996,18.5660484]
["2024-08-27T01:55:00","2024-08-27T02:00:00",398.72939880000001,-21.662510399999999]
["2024-08-27T07:45:00","2024-08-27T07:50:00",629.83138559999998,73.063321200000004]
["2024-08-27T10:30:00","2024-08-27T10:35:00",545.41807440000002,75.937364400000007]
["2024-08-27T14:50:00","2024-08-27T14:55:00",491.81414640000003,64.991977199999994]
["2024-08-27T19:50:00","2024-08-27T19:55:00",639.70031400000005,43.988475600000001]
["2024-08-27T23:30:00","2024-08-27T23:35:00",479.99247120000001,-1.4066604]
["2024-08-28T03:45:00","2024-08-28T03:50:00",383.50307400000003,-21.846965999999998]
["2024-08-28T07:55:00","2024-08-28T08:00:00",593.51257199999998,72.292762800000006]
["2024-08-28T12:25:00","2024-08-28T12:30:00",348.34612559999999,59.715988799999998]
["2024-08-28T16:40:00","2024-08-28T16:45:00",586.29610439999999,46.342992000000002]
["2024-08-28T20:00:00","2024-08-28T20:05:00",687.93857160000005,66.254991599999997]
["2024-08-29T01:20:00","2024-08-29T01:25:00",433.66536960000002,-12.285828]
["2024-08-29T05:35:00","2024-08-29T05:40:00",469.11080040000002,0.70209960000000005]
["2024-08-29T09:55:00","2024-08-29T10:00:00",606.32850959999996,86.392022400000002]
["2024-08-29T14:45:00","2024-08-29T14:50:00",540.99852720000001,63.9360432]
["2024-08-29T18:30:00","2024-08-29T18:35:00",696.31096679999996,62.895219599999997]
["2024-08-29T22:50:00","2024-08-29T22:55:00",515.99853480000002,7.9083348000000004]
["2024-08-30T02:50:00","2024-08-30T02:55:00",397.77444120000001,-21.131821200000001]
["2024-08-30T07:25:00","2024-08-30T07:30:00",576.21290399999998,54.467356799999997]
["2024-08-30T11:45:00","2024-08-30T11:50:00",372.63008400000001,57.586213200000003]
["2024-08-30T14:55:00","2024-08-30T15:00:00",509.39269680000001,44.531539199999997]
["2024-08-30T20:25:00","2024-08-30T20:30:00",596.31124199999999,25.629316800000002]
["2024-08-31T00:40:00","2024-08-31T00:45:00",430.64298839999998,-21.073545599999999]
["2024-08-31T03:00:00","2024-08-31T03:05:00",379.85636520000003,-31.900320000000001]
["2024-08-31T09:20:00","2024-08-31T09:25:00",434.72077080000003,13.190383199999999]
["2024-08-31T13:35:00","2024-08-31T13:40:00",400.61494440000001,-0.58840440000000005]
["2024-08-31T19:05:00","2024-08-31T19:10:00",564.22698720000005,9.3785112000000002]
["2024-08-31T22:15:00","2024-08-31T22:20:00",488.47902959999999,-13.8848796]
["2024-09-01T02:30:00","2024-09-01T02:35:00",370.06012079999999,-37.064341200000001]
["2024-09-01T07:10:00","2024-09-01T07:15:00",401.78233560000001,-27.957053999999999]
["2024-09-01T11:10:00","2024-09-01T11:15:00",279.4938156,-3.3614411999999998]
["2024-09-01T15:25:00","2024-09-01T15:30:00",314.28027839999999,-13.524186]
["2024-09-01T19:45:00","2024-09-01T19:50:00",536.52064559999997,-0.36287639999999999]
["2024-09-01T21:55:00","2024-09-01T22:00:00",481.5182532,-13.317278399999999]
["2024-09-02T04:25:00","2024-09-02T04:30:00",376.95191399999999,-31.755966000000001]
["2024-09-02T08:40:00","2024-09-02T08:45:00",558.83683919999999,73.042631999999998]
["2024-09-02T10:00:00","2024-09-02T10:05:00",515.57629680000002,67.151867999999993]
["2024-09-02T17:20:00","2024-09-02T17:25:00",716.01776759999996,73.342562400000006]
["2024-09-02T21:35:00","2024-09-02T21:40:00",657.11588640000002,44.496135600000002]
["2024-09-03T02:05:00","2024-09-03T02:10:00",433.8345468,-17.747792400000002]
["2024-09-03T06:15:00","2024-09-03T06:20:00",585.54737639999996,38.559523200000001]
["2024-09-03T10:30:00","2024-09-03T10:35:00",614.93998439999996,91.746177599999996]
["2024-09-03T14:10:00","2024-09-03T14:15:00",413.42184600000002,70.681208400000003]
["2024-09-03T19:10:00","2024-09-03T19:15:00",696.93475799999999,59.034211200000001]
["2024-09-03T23:25:00","2024-09-03T23:30:00",521.97225119999996,4.8664788000000003]
["2024-09-04T02:15:00","2024-09-04T02:20:00",423.61252439999998,-15.9885036]
["2024-09-04T08:05:00","2024-09-04T08:10:00",621.39245640000001,85.117732799999999]
["2024-09-04T12:25:00","2024-09-04T12:30:00",469.16740920000001,70.361879999999999]
["2024-09-04T14:20:00","2024-09-04T14:25:00",508.20807960000002,69.556340399999996]
["2024-09-04T21:00:00","2024-09-04T21:05:00",613.81818959999998,35.578394400000001]
["2024-09-05T01:20:00","2024-09-05T01:25:00",416.10959400000002,-16.2050664]
["2024-09-05T05:35:00","2024-09-05T05:40:00",449.51952119999999,-1.8331968000000001]
["2024-09-05T09:25:00","2024-09-05T09:30:00",576.84653639999999,73.135428000000005]
["2024-09-05T14:15:00","2024-09-05T14:20:00",633.43968600000005,72.441671999999997]
["2024-09-05T18:30:00","2024-09-05T18:35:00",684.77016479999998,56.014221599999999]
["2024-09-05T21:10:00","2024-09-05T21:15:00",591.47794799999997,24.3694296]
["2024-09-06T03:10:00","2024-09-06T03:15:00",386.05596960000003,-21.076560000000001]
["2024-09-06T07:25:00","2024-09-06T07:30:00",565.99598279999998,51.875112000000001]
["2024-09-06T09:15:00","2024-09-06T09:20:00",531.07291199999997,66.829548000000003]
["2024-09-06T16:05:00","2024-09-06T16:10:00",573.67206959999999,38.625779999999999]
["2024-09-06T20:25:00","2024-09-06T20:30:00",569.92542479999997,18.5138088]
["2024-09-06T21:20:00","2024-09-06T21:25:00",540.98021040000003,8.7312024000000008]
["2024-09-07T05:00:00","2024-09-07T05:05:00",387.35702520000001,-27.1305984]
["2024-09-07T09:20:00","2024-09-07T09:25:00",340.46712120000001,5.3371295999999999]
["2024-09-07T09:25:00","2024-09-07T09:30:00",331.84643999999997,4.7486003999999999]
["2024-09-07T17:55:00","2024-09-07T18:00:00",521.68919759999994,-2.6518608000000001]
["2024-09-07T18:00:00","2024-09-07T18:05:00",521.95609560000003,-3.6244871999999999]
["2024-09-08T01:50:00","2024-09-08T01:55:00",378.06674040000001,-35.215403999999999]
["2024-09-08T02:40:00","2024-09-08T02:45:00",363.65742599999999,-39.665303999999999]
["2024-09-08T06:55:00","2024-09-08T07:00:00",391.98075239999997,-28.392479999999999]
["2024-09-08T11:10:00","2024-09-08T11:15:00",241.51898159999999,-7.5528275999999996]
["2024-09-08T16:15:00","2024-09-08T16:20:00",492.34838159999998,-5.9486879999999998]
["2024-09-08T19:50:00","2024-09-08T19:55:00",571.23826919999999,5.5921019999999997]
["2024-09-09T00:05:00","2024-09-09T00:10:00",424.81881959999998,-26.207727599999998]
["2024-09-09T04:20:00","2024-09-09T04:25:00",376.18173839999997,-33.051698399999999]
["2024-09-09T08:45:00","2024-09-09T08:50:00",531.45552480000003,70.0052412]
["2024-09-09T13:05:00","2024-09-09T13:10:00",475.08682199999998,70.219666799999999]
["2024-09-09T20:45:00","2024-09-09T20:50:00",623.38364639999998,37.039801199999999]
["2024-09-09T21:40:00","2024-09-09T21:45:00",583.93325040000002,23.635395599999999]
["2024-09-10T02:00:00","2024-09-10T02:05:00",411.28069199999999,-19.596128400000001]
["2024-09-10T08:50:00","2024-09-10T08:55:00",528.02570879999996,83.078667600000003]
["2024-09-10T10:40:00","2024-09-10T10:45:00",388.16059200000001,80.445277200000007]
["2024-09-10T14:55:00","2024-09-10T15:00:00",385.66343879999999,58.441705200000001]
["2024-09-10T20:55:00","2024-09-10T21:00:00",597.30625680000003,28.211738400000002]
["2024-09-10T23:35:00","2024-09-10T23:40:00",477.98299559999998,-5.1535260000000003]
["2024-09-11T03:50:00","2024-09-11T03:55:00",392.43165119999998,-22.5052044]
["2024-09-11T08:05:00","2024-09-11T08:10:00",618.57559200000003,72.029867999999993]
["2024-09-11T15:40:00","2024-09-11T15:45:00",585.62861999999996,56.667847199999997]
["2024-09-11T16:45:00","2024-09-11T16:50:00",631.26496680000002,56.416282799999998]
["2024-09-11T21:05:00","2024-09-11T21:10:00",626.75862119999999,37.209147600000001]
["2024-09-12T03:45:00","2024-09-12T03:50:00",420.78503640000002,-17.110540799999999]
["2024-09-12T05:40:00","2024-09-12T05:45:00",488.17766640000002,5.7381083999999998]
["2024-09-12T10:00:00","2024-09-12T10:05:00",450.48032280000001,72.455530800000005]
["2024-09-12T15:50:00","2024-09-12T15:55:00",451.83459720000002,48.206113199999997]
["2024-09-12T18:40:00","2024-09-12T18:45:00",707.96771520000004,64.698061199999998]
["2024-09-12T22:55:00","2024-09-12T23:00:00",518.79642360000003,5.4529415999999999]
["2024-09-13T03:55:00","2024-09-13T04:00:00",407.03358839999999,-21.1950492]
["2024-09-13T07:35:00","2024-09-13T07:40:00",643.67703719999997,70.5120024]
["2024-09-13T11:50:00","2024-09-13T11:55:00",550.60072079999998,74.824946400000002]
["2024-09-13T16:00:00","2024-09-13T16:05:00",519.45288960000005,39.183996]
["2024-09-13T20:30:00","2024-09-13T20:35:00",624.55881480000005,33.203067599999997]
["2024-09-14T00:45:00","2024-09-14T00:50:00",450.05860680000001,-17.520069599999999]
["2024-09-14T08:05:00","2024-09-14T08:10:00",524.1497124,15.196440000000001]
["2024-09-14T09:25:00","2024-09-14T09:30:00",506.94650159999998,26.853746399999999]
["2024-09-14T13:40:00","2024-09-14T13:45:00",541.55859359999999,34.683967199999998]
["2024-09-14T18:00:00","2024-09-14T18:05:00",690.73663439999996,46.506492000000001]
["2024-09-14T22:50:00","2024-09-14T22:55:00",565.93171319999999,3.5472792000000002]
["2024-09-15T02:35:00","2024-09-15T02:40:00",422.54733720000002,-30.617591999999998]
["2024-09-15T06:55:00","2024-09-15T07:00:00",458.45869440000001,-14.1854388]
["2024-09-15T10:55:00","2024-09-15T11:00:00",353.69236080000002,-0.8246772]
["2024-09-15T15:35:00","2024-09-15T15:40:00",363.31205039999998,-9.6896856000000007]
["2024-09-15T19:50:00","2024-09-15T19:55:00",670.09572479999997,29.654496000000002]
["2024-09-15T23:00:00","2024-09-15T23:05:00",507.54207719999999,-16.927370400000001]
["2024-09-16T04:30:00","2024-09-16T04:35:00",411.80119560000003,-32.493383999999999]
["2024-09-16T08:45:00","2024-09-16T08:50:00",611.37804359999996,86.807204400000003]
["2024-09-16T15:05:00","2024-09-16T15:10:00",564.94403399999999,57.371193599999998]
["2024-09-16T17:25:00","2024-09-16T17:30:00",696.25450679999994,56.948341200000002]
["2024-09-16T21:40:00","2024-09-16T21:45:00",618.3379152,24.307863600000001]
["2024-09-17T03:10:00","2024-09-17T03:15:00",406.22144520000001,-29.1682956]
["2024-09-17T06:20:00","2024-09-17T06:25:00",553.40256720000002,23.510479199999999]
["2024-09-17T10:35:00","2024-09-17T10:40:00",472.12807679999997,75.705569999999994]
["2024-09-17T15:15:00","2024-09-17T15:20:00",392.76497879999999,44.5481616]
["2024-09-17T19:15:00","2024-09-17T19:20:00",687.3365976,48.636409200000003]
["2024-09-17T23:35:00","2024-09-17T23:40:00",508.1844084,-5.3119296]
["2024-09-18T03:50:00","2024-09-18T03:55:00",417.97903439999999,-27.701696399999999]
["2024-09-18T10:20:00","2024-09-18T10:25:00",384.32515799999999,69.772329600000006]
["2024-09-18T12:30:00","2024-09-18T12:35:00",304.96792920000001,61.752100800000001]
["2024-09-18T16:45:00","2024-09-18T16:50:00",492.87680160000002,30.721350000000001]
["2024-09-18T22:05:00","2024-09-18T22:10:00",530.68836120000003,4.1470115999999999]
["2024-09-19T01:25:00","2024-09-19T01:30:00",409.10471159999997,-25.377181199999999]
["2024-09-19T05:40:00","2024-09-19T05:45:00",471.50622720000001,-9.1086276000000002]
["2024-09-19T10:10:00","2024-09-19T10:15:00",534.95905319999997,67.377765600000004]
["2024-09-19T14:20:00","2024-09-19T14:25:00",426.25820399999998,61.072855199999999]
["2024-09-19T18:35:00","2024-09-19T18:40:00",695.63495639999996,55.747958400000002]
["2024-09-19T22:15:00","2024-09-19T22:20:00",560.16357960000005,9.6622464000000008]
["2024-09-20T03:15:00","2024-09-20T03:20:00",397.99735199999998,-31.795241999999998]
["2024-09-20T07:35:00","2024-09-20T07:40:00",608.7876516,61.0883988]
["2024-09-20T10:20:00","2024-09-20T10:25:00",552.29229120000002,70.359333599999999]
["2024-09-20T16:10:00","2024-09-20T16:15:00",565.66634999999997,35.075575200000003]
["2024-09-20T20:30:00","2024-09-20T20:35:00",650.1179472,38.771908799999999]
["2024-09-20T22:25:00","2024-09-20T22:30:00",553.86186720000001,6.4640544000000002]
["2024-09-21T05:05:00","2024-09-21T05:10:00",411.473634,-25.373258400000001]
["2024-09-21T09:25:00","2024-09-21T09:30:00",458.35396800000001,15.6935676]
["2024-09-21T13:40:00","2024-09-21T13:45:00",379.76909760000001,0.53080559999999999]
["2024-09-21T17:10:00","2024-09-21T17:15:00",514.42172040000003,-8.1185171999999994]
["2024-09-21T22:20:00","2024-09-21T22:25:00",493.8366312,-19.4174136]
["2024-09-22T02:35:00","2024-09-22T02:40:00",378.72137400000003,-39.922328399999998]
["2024-09-22T05:15:00","2024-09-22T05:20:00",376.4410608,-40.070452799999998]
["2024-09-22T11:15:00","2024-09-22T11:20:00",296.14543320000001,-8.1187392000000003]
["2024-09-22T15:35:00","2024-09-22T15:40:00",366.52729440000002,-14.860401599999999]
["2024-09-22T17:20:00","2024-09-22T17:25:00",477.36836160000001,-4.3741116]
["2024-09-23T00:10:00","2024-09-23T00:15:00",418.6305552,-28.765803600000002]
["2024-09-23T04:30:00","2024-09-23T04:35:00",382.08138839999998,-31.373732400000002]
["2024-09-23T09:45:00","2024-09-23T09:50:00",438.73822799999999,65.027210400000001]
["2024-09-23T13:05:00","2024-09-23T13:10:00",551.18085959999996,65.804584800000001]
["2024-09-23T17:25:00","2024-09-23T17:30:00",623.174532,46.7655192]
["2024-09-23T21:50:00","2024-09-23T21:55:00",547.39609680000001,11.998082399999999]
["2024-09-24T02:05:00","2024-09-24T02:10:00",408.43617,-18.682848]
["2024-09-24T06:20:00","2024-09-24T06:25:00",512.22934559999999,16.792119599999999]
["2024-09-24T10:35:00","2024-09-24T10:40:00",479.76810719999997,69.352454399999999]
["2024-09-24T12:15:00","2024-09-24T12:20:00",346.95407879999999,78.874734000000004]
["2024-09-24T19:15:00","2024-09-24T19:20:00",599.63408760000004,36.711666000000001]
["2024-09-24T23:30:00","2024-09-24T23:35:00",469.34912880000002,-2.6144135999999998]
["2024-09-25T04:40:00","2024-09-25T04:45:00",395.011032,-17.028956399999998]
["2024-09-25T08:10:00","2024-09-25T08:15:00",590.06991840000001,66.4885752]
["2024-09-25T12:30:00","2024-09-25T12:35:00",635.54010600000004,85.067683200000005]
["2024-09-25T16:45:00","2024-09-25T16:50:00",664.77804000000003,62.941102800000003]
["2024-09-25T21:05:00","2024-09-25T21:10:00",660.17045640000003,47.88288]
["2024-09-26T01:25:00","2024-09-26T01:30:00",457.55181720000002,-7.7413980000000002]
["2024-09-26T04:50:00","2024-09-26T04:55:00",440.2933524,-14.9483424]
["2024-09-26T10:05:00","2024-09-26T10:10:00",545.29889519999995,75.435165600000005]
["2024-09-26T14:20:00","2024-09-26T14:25:00",521.46118439999998,66.330734399999997]
["2024-09-26T16:55:00","2024-09-26T17:00:00",566.7844308,35.514307199999998]
["2024-09-26T23:00:00","2024-09-26T23:05:00",534.23232959999996,-4.9796496000000001]
["2024-09-27T03:15:00","2024-09-27T03:20:00",394.04434320000001,-36.662428800000001]
["2024-09-27T05:00:00","2024-09-27T05:05:00",406.02323639999997,-28.709465999999999]
["2024-09-27T11:55:00","2024-09-27T12:00:00",198.18103679999999,4.7139708000000002]
["2024-09-27T16:10:00","2024-09-27T16:15:00",335.45928839999999,-8.8812479999999994]
["2024-09-27T20:30:00","2024-09-27T20:35:00",545.16891720000001,-1.6332275999999999]
["2024-09-27T23:45:00","2024-09-27T23:50:00",457.1182068,-26.1539748]
["2024-09-28T05:05:00","2024-09-28T05:10:00",385.14731399999999,-39.397881599999998]
["2024-09-28T09:25:00","2024-09-28T09:30:00",279.88691160000002,-4.4556215999999997]
["2024-09-28T11:50:00","2024-09-28T11:55:00",177.03324839999999,0.69714359999999997]
["2024-09-28T18:05:00","2024-09-28T18:10:00",472.9422624,-12.3267036]
["2024-09-28T22:20:00","2024-09-28T22:25:00",441.8068404,-25.585918800000002]
["2024-09-28T23:55:00",45564,410.42190840000001,-32.752518000000002]
["2024-09-29T07:00:00","2024-09-29T07:05:00",361.42075560000001,-31.8761808]
["2024-09-29T11:15:00","2024-09-29T11:20:00",485.17365719999998,-1.5721164000000001]
["2024-09-29T12:00:00","2024-09-29T12:05:00",508.27560240000003,2.4429107999999999]
["2024-09-29T19:55:00","2024-09-29T20:00:00",562.1200632,2.4263219999999999]
["2024-09-30T00:10:00","2024-09-30T00:15:00",430.27144440000001,-27.142416000000001]
["2024-09-30T04:05:00","2024-09-30T04:10:00",388.78956959999999,-34.721847599999997]
["2024-09-30T08:50:00","2024-09-30T08:55:00",446.88105239999999,56.621230799999999]
["2024-09-30T13:05:00","2024-09-30T13:10:00",394.40113079999998,44.7753972]
["2024-09-30T16:10:00","2024-09-30T16:15:00",432.00959640000002,36.548014799999997]
["2024-09-30T21:45:00","2024-09-30T21:50:00",542.49875520000001,9.7055051999999993]
["2024-10-01T02:00:00","2024-10-01T02:05:00",397.5415572,-24.977494799999999]
["2024-10-01T06:20:00","2024-10-01T06:25:00",508.28132520000003,19.6678584]
["2024-10-01T06:55:00","2024-10-01T07:00:00",530.72147759999996,42.079546800000003]
["2024-10-01T10:45:00","2024-10-01T10:50:00",544.33459679999999,78.360686400000006]
["2024-10-01T15:00:00","2024-10-01T15:05:00",413.15168519999997,66.479240399999995]
["2024-10-01T23:20:00","2024-10-01T23:25:00",509.4438576,1.6215732]
["2024-10-01T23:40:00","2024-10-01T23:45:00",488.07749280000002,-4.8462804000000004]
["2024-10-02T03:55:00","2024-10-02T04:00:00",405.81289079999999,-20.441336400000001]
["2024-10-02T11:05:00","2024-10-02T11:10:00",304.31619000000001,65.498782800000001]
["2024-10-02T12:35:00","2024-10-02T12:40:00",298.22071080000001,71.325333599999993]
["2024-10-02T16:50:00","2024-10-02T16:55:00",478.52206080000002,36.527884800000002]
["2024-10-02T23:10:00","2024-10-02T23:15:00",520.04822760000002,6.4183859999999999]
["2024-10-03T01:30:00","2024-10-03T01:35:00",413.46021839999997,-19.670143199999998]
["2024-10-03T05:45:00","2024-10-03T05:50:00",468.4444464,-2.4170820000000002]
["2024-10-03T11:15:00","2024-10-03T11:20:00",315.13324319999998,86.407579200000001]
["2024-10-03T14:25:00","2024-10-03T14:30:00",392.57684519999998,86.962161600000002]
["2024-10-03T18:45:00","2024-10-03T18:50:00",589.37773079999999,40.169936399999997]
["2024-10-03T23:00:00","2024-10-03T23:05:00",457.81402320000001,-3.1511832000000002]
["2024-10-04T06:20:00","2024-10-04T06:25:00",465.81823200000002,11.765824800000001]
["2024-10-04T07:40:00","2024-10-04T07:45:00",491.137134,51.696258]
["2024-10-04T11:55:00","2024-10-04T12:00:00",369.99461639999998,78.498739200000003]
["2024-10-04T18:25:00","2024-10-04T18:30:00",575.91395520000003,27.116826]
["2024-10-04T20:35:00","2024-10-04T20:40:00",543.52004639999996,18.219743999999999]
["2024-10-05T00:50:00","2024-10-05T00:55:00",398.84999040000002,-20.8109088]
["2024-10-05T06:10:00","2024-10-05T06:15:00",381.60402720000002,-19.446817200000002]
["2024-10-05T09:30:00","2024-10-05T09:35:00",314.8550568,9.6723660000000002]
["2024-10-05T13:45:00","2024-10-05T13:50:00",416.04680999999999,5.5430916000000003]
["2024-10-05T18:15:00","2024-10-05T18:20:00",541.41882239999995,3.5806811999999999]
["2024-10-05T22:25:00","2024-10-05T22:30:00",453.63565560000001,-23.182112400000001]
["2024-10-06T02:45:00","2024-10-06T02:50:00",357.31568759999999,-41.538428400000001]
["2024-10-06T06:20:00","2024-10-06T06:25:00",369.30572160000003,-32.9047488]
["2024-10-06T11:20:00","2024-10-06T11:25:00",273.1965624,-1.7013396000000001]
["2024-10-06T15:40:00","2024-10-06T15:45:00",388.32742200000001,-10.09188]
["2024-10-06T22:45:00","2024-10-06T22:50:00",407.72210999999999,-27.354195600000001]
["2024-10-07T00:15:00","2024-10-07T00:20:00",386.03435159999998,-31.5473292]
["2024-10-07T04:35:00","2024-10-07T04:40:00",405.63346799999999,-19.930280400000001]
["2024-10-07T08:50:00","2024-10-07T08:55:00",590.55534239999997,74.995204799999996]
["2024-10-07T13:10:00","2024-10-07T13:15:00",504.403302,65.932687200000004]
["2024-10-07T17:30:00","2024-10-07T17:35:00",653.76230880000003,48.306688800000003]
["2024-10-07T21:45:00","2024-10-07T21:50:00",530.30807400000003,7.9393224]
["2024-10-08T01:15:00","2024-10-08T01:20:00",409.9076124,-22.930633199999999]
["2024-10-08T06:25:00","2024-10-08T06:30:00",637.71852239999998,75.948897599999995]
["2024-10-08T10:45:00","2024-10-08T10:50:00",505.63511879999999,88.881614400000004]
["2024-10-08T17:40:00","2024-10-08T17:45:00",597.09420720000003,46.061253600000001]
["2024-10-08T19:20:00","2024-10-08T19:25:00",675.0311256,64.631113200000001]
["2024-10-08T23:40:00","2024-10-08T23:45:00",485.47399799999999,-3.3992399999999998]
["2024-10-09T05:45:00","2024-10-09T05:50:00",627.95785439999997,55.889465999999999]
["2024-10-09T08:15:00","2024-10-09T08:20:00",556.31349599999999,88.354968]
["2024-10-09T12:35:00","2024-10-09T12:40:00",308.92527239999998,86.424880799999997]
["2024-10-09T17:50:00","2024-10-09T17:55:00",557.59920120000004,36.1124352]
["2024-10-09T21:15:00","2024-10-09T21:20:00",522.94581240000002,9.9891287999999996]
["2024-10-10T01:30:00","2024-10-10T01:35:00",407.78169120000001,-16.519392]
["2024-10-10T05:55:00","2024-10-10T06:00:00",578.16545280000003,48.061071599999998]
["2024-10-10T10:10:00","2024-10-10T10:15:00",346.6770684,74.11542]
["2024-10-10T14:25:00","2024-10-10T14:30:00",301.10259480000002,67.311296400000003]
["2024-10-10T18:40:00","2024-10-10T18:45:00",587.86934040000006,25.722045600000001]
["2024-10-11T00:40:00","2024-10-11T00:45:00",411.76105200000001,-19.07856]
["2024-10-11T03:20:00","2024-10-11T03:25:00",400.10485799999998,-22.814251200000001]
["2024-10-11T07:40:00","2024-10-11T07:45:00",530.29608599999995,67.673535599999994]
["2024-10-11T12:45:00","2024-10-11T12:50:00",364.38685320000002,53.853657599999998]
["2024-10-11T16:15:00","2024-10-11T16:20:00",540.16175639999994,34.067388000000001]
["2024-10-11T20:35:00","2024-10-11T20:40:00",567.39345839999999,17.161624799999998]
["2024-10-12T00:50:00","2024-10-12T00:55:00",409.83144600000003,-23.8494168]
["2024-10-12T05:15:00","2024-10-12T05:20:00",425.20003439999999,-20.458833599999998]
["2024-10-12T09:30:00","2024-10-12T09:35:00",268.90740959999999,12.360576]
["2024-10-12T12:55:00","2024-10-12T13:00:00",159.5297616,12.407374799999999]
["2024-10-12T18:10:00","2024-10-12T18:15:00",473.91558240000001,-15.3170664]
["2024-10-12T22:25:00","2024-10-12T22:30:00",434.99391120000001,-28.444572000000001]
["2024-10-13T01:00:00","2024-10-13T01:05:00",383.1183924,-40.405876800000001]
["2024-10-13T07:05:00","2024-10-13T07:10:00",368.6655816,-22.922651999999999]
["2024-10-13T11:20:00","2024-10-13T11:25:00",170.3413836,2.0554872]
["2024-10-13T17:05:00","2024-10-13T17:10:00",409.31235959999998,-9.4533419999999992]
["2024-10-13T20:00:00","2024-10-13T20:05:00",481.63891919999998,-14.9807796]
["2024-10-14T00:15:00","2024-10-14T00:20:00",376.15150319999998,-33.6789816]
["2024-10-14T04:35:00","2024-10-14T04:40:00",402.12436680000002,-10.859523599999999]
["2024-10-14T07:50:00","2024-10-14T07:55:00",491.54422319999998,71.397090000000006]
["2024-10-14T13:15:00","2024-10-14T13:20:00",309.75387599999999,94.131357600000001]
["2024-10-14T17:30:00","2024-10-14T17:35:00",528.02318160000004,34.570809599999997]
["2024-10-14T19:55:00","2024-10-14T20:00:00",552.25340879999999,21.2668404]
["2024-10-15T02:10:00","2024-10-15T02:15:00",386.1309,-18.823797599999999]
["2024-10-15T06:25:00","2024-10-15T06:30:00",534.64608480000004,40.199005200000002]
["2024-10-15T12:20:00","2024-10-15T12:25:00",378.4832328,85.576100400000001]
["2024-10-15T15:05:00","2024-10-15T15:10:00",494.82049080000002,78.751165200000003]
["2024-10-15T19:20:00","2024-10-15T19:25:00",561.31711440000004,30.680545200000001]
["2024-10-16T00:05:00","2024-10-16T00:10:00",415.82241720000002,-9.5865995999999996]
["2024-10-16T04:00:00","2024-10-16T04:05:00",404.37086640000001,-10.83966]
["2024-10-16T08:15:00","2024-10-16T08:20:00",497.28991439999999,67.408550399999996]
["2024-10-16T12:10:00","2024-10-16T12:15:00",353.47483679999999,97.115097599999999]
["2024-10-16T16:55:00","2024-10-16T17:00:00",526.8836652,73.904787600000006]
["2024-10-16T21:10:00","2024-10-16T21:15:00",513.37908479999999,21.1230072]
["2024-10-17T01:30:00","2024-10-17T01:35:00",389.89720920000002,-13.178051999999999]
["2024-10-17T07:15:00","2024-10-17T07:20:00",483.85329480000001,60.534291600000003]
["2024-10-17T10:10:00","2024-10-17T10:15:00",358.11723719999998,98.545876800000002]
["2024-10-17T14:25:00","2024-10-17T14:30:00",592.54612440000005,87.023250000000004]
["2024-10-17T19:20:00","2024-10-17T19:25:00",575.33421840000005,46.538403600000002]
["2024-10-17T23:05:00","2024-10-17T23:10:00",454.38613199999998,-0.84223440000000005]
["2024-10-18T03:20:00","2024-10-18T03:25:00",385.74837839999998,-13.463520000000001]
["2024-10-18T07:05:00","2024-10-18T07:10:00",560.23023720000003,62.685674400000003]
["2024-10-18T12:00:00","2024-10-18T12:05:00",458.06190240000001,81.173185200000006]
["2024-10-18T16:15:00","2024-10-18T16:20:00",568.4459736,56.068007999999999]
["2024-10-18T19:10:00","2024-10-18T19:15:00",563.63466600000004,25.367172]
["2024-10-19T00:55:00","2024-10-19T01:00:00",383.10244560000001,-25.1313432]
["2024-10-19T05:10:00","2024-10-19T05:15:00",394.73307720000003,-23.391835199999999]
["2024-10-19T07:15:00","2024-10-19T07:20:00",460.25278200000002,-3.3207624]
["2024-10-19T13:50:00","2024-10-19T13:55:00",230.8283232,8.4137292000000006]
["2024-10-19T18:10:00","2024-10-19T18:15:00",482.78623199999998,-12.279435599999999]
["2024-10-19T19:20:00","2024-10-19T19:25:00",498.07277040000002,-10.3890096]
["2024-10-20T02:45:00","2024-10-20T02:50:00",346.69974000000002,-42.644508000000002]
["2024-10-20T07:05:00","2024-10-20T07:10:00",349.37079840000001,-28.618386000000001]
["2024-10-20T11:20:00","2024-10-20T11:25:00",252.9507012,-8.1931247999999997]
["2024-10-20T14:25:00","2024-10-20T14:30:00",269.0670192,-8.0674644000000004]
["2024-10-20T20:00:00","2024-10-20T20:05:00",488.83394040000002,-17.112477599999998]
["2024-10-21T00:15:00","2024-10-21T00:20:00",382.11236760000003,-34.172403600000003]
["2024-10-21T02:10:00","2024-10-21T02:15:00",358.03782960000001,-37.732952400000002]
["2024-10-21T08:55:00","2024-10-21T09:00:00",383.85319199999998,62.157767999999997]
["2024-10-21T13:10:00","2024-10-21T13:15:00",310.03250159999999,87.057444000000004]
["2024-10-21T14:15:00","2024-10-21T14:20:00",326.02112640000001,75.612465599999993]
["2024-10-21T21:50:00","2024-10-21T21:55:00",472.76421360000001,6.0721572000000004]
["2024-10-22T02:10:00","2024-10-22T02:15:00",376.709136,-19.873484399999999]
["2024-10-22T06:40:00","2024-10-22T06:45:00",504.84413039999998,58.694844000000003]
["2024-10-22T10:45:00","2024-10-22T10:50:00",324.6370392,98.110869600000001]
["2024-10-22T15:05:00","2024-10-22T15:10:00",567.13749359999997,111.3776232]
["2024-10-22T18:45:00","2024-10-22T18:50:00",569.09643719999997,43.2176616]
["2024-10-22T23:40:00","2024-10-22T23:45:00",432.64964639999999,-6.6596555999999998]
["2024-10-23T04:00:00","2024-10-23T04:05:00",403.22472119999998,-14.954984400000001]
["2024-10-23T06:50:00","2024-10-23T06:55:00",565.40544120000004,55.514814000000001]
["2024-10-23T12:40:00","2024-10-23T12:45:00",283.1894964,84.412865999999994]
["2024-10-23T16:55:00","2024-10-23T17:00:00",470.3983968,48.515584799999999]
["2024-10-23T21:10:00","2024-10-23T21:15:00",505.97371920000001,7.5245255999999996]
["2024-10-24T01:35:00","2024-10-24T01:40:00",387.86624879999999,-20.904237599999998]
["2024-10-24T05:50:00","2024-10-24T05:55:00",518.44356960000005,26.517023999999999]
["2024-10-24T10:10:00","2024-10-24T10:15:00",418.19390759999999,70.0731696]
["2024-10-24T13:40:00","2024-10-24T13:45:00",376.9299168,68.092201200000005]
["2024-10-24T18:45:00","2024-10-24T18:50:00",573.84819240000002,26.477608799999999]
["2024-10-24T23:05:00","2024-10-24T23:10:00",459.69134159999999,-9.0677375999999992]
["2024-10-25T01:45:00","2024-10-25T01:50:00",390.36150600000002,-22.707500400000001]
["2024-10-25T07:40:00","2024-10-25T07:45:00",517.77922679999995,66.556259999999995]
["2024-10-25T07:45:00","2024-10-25T07:50:00",513.99280199999998,66.992179199999995]
["2024-10-25T13:50:00","2024-10-25T13:55:00",282.59246280000002,55.126101599999998]
["2024-10-25T16:25:00","2024-10-25T16:30:00",409.71524879999998,30.935056800000002]
["2024-10-25T20:40:00","2024-10-25T20:45:00",555.46864679999999,32.748609600000002]
["2024-10-26T01:55:00","2024-10-26T02:00:00",388.96903079999998,-30.229374]
["2024-10-26T05:20:00","2024-10-26T05:25:00",437.83713840000001,-16.5782712]
["2024-10-26T09:35:00","2024-10-26T09:40:00",247.76013119999999,15.646962]
["2024-10-26T14:00:00","2024-10-26T14:05:00",184.12557960000001,20.792696400000001]
["2024-10-26T18:15:00","2024-10-26T18:20:00",465.28222440000002,-5.4931320000000001]
["2024-10-26T22:30:00","2024-10-26T22:35:00",405.60571679999998,-29.894763600000001]
["2024-10-27T02:50:00","2024-10-27T02:55:00",340.49745359999997,-42.826265999999997]
["2024-10-27T08:45:00","2024-10-27T08:50:00",282.85755360000002,-18.145194]
["2024-10-27T11:25:00","2024-10-27T11:30:00",307.47097200000002,0.71462639999999999]
["2024-10-27T15:45:00","2024-10-27T15:50:00",423.94720080000002,7.4926512000000001]
["2024-10-27T20:50:00","2024-10-27T20:55:00",462.49138319999997,-16.471962000000001]
["2024-10-28T00:25:00","2024-10-28T00:30:00",369.86330279999999,-32.323484399999998]
["2024-10-28T04:40:00","2024-10-28T04:45:00",412.1899416,-18.142434000000002]
["2024-10-28T08:55:00","2024-10-28T09:00:00",463.36200960000002,64.829228400000005]
["2024-10-28T13:20:00","2024-10-28T13:25:00",281.62120320000002,69.142747200000002]
["2024-10-28T17:35:00","2024-10-28T17:40:00",524.90355959999999,29.752477200000001]
["2024-10-29T01:20:00","2024-10-29T01:25:00",383.87503559999999,-22.614013199999999]
["2024-10-29T02:15:00","2024-10-29T02:20:00",378.64240919999997,-24.521205599999998]
["2024-10-29T06:30:00","2024-10-29T06:35:00",559.37453400000004,51.615983999999997]
["2024-10-29T13:05:00","2024-10-29T13:10:00",270.36726119999997,77.247717600000001]
["2024-10-29T15:10:00","2024-10-29T15:15:00",326.47149480000002,57.624764399999997]
["2024-10-29T19:25:00","2024-10-29T19:30:00",565.22492880000004,36.939763200000002]
["2024-10-29T23:45:00","2024-10-29T23:50:00",424.02785160000002,-13.150718400000001]
["2024-10-30T03:50:00","2024-10-30T03:55:00",396.00195239999999,-19.966684799999999]
["2024-10-30T08:20:00","2024-10-30T08:25:00",532.65342599999997,71.132512800000001]
["2024-10-30T12:40:00","2024-10-30T12:45:00",278.55166680000002,83.211951600000006]
["2024-10-30T20:15:00","2024-10-30T20:20:00",538.97134080000001,34.4195256]
["2024-10-30T21:20:00","2024-10-30T21:25:00",495.50066040000002,18.147009600000001]
["2024-10-31T01:35:00","2024-10-31T01:40:00",378.29763839999998,-20.510140799999999]
["2024-10-31T08:20:00","2024-10-31T08:25:00",442.37156640000001,67.438335600000002]
["2024-10-31T10:15:00","2024-10-31T10:20:00",367.05498239999997,73.858434000000003]
["2024-10-31T14:30:00","2024-10-31T14:35:00",378.95501280000002,60.039922799999999]
["2024-10-31T20:05:00","2024-10-31T20:10:00",567.78624360000003,23.642056799999999]
["2024-10-31T23:10:00","2024-10-31T23:15:00",460.20787680000001,-7.4195111999999996]
["2024-11-01T03:25:00","2024-11-01T03:30:00",388.65886920000003,-22.7470116]
["2024-11-01T08:10:00","2024-11-01T08:15:00",542.82880799999998,52.234456799999997]
["2024-11-01T12:05:00","2024-11-01T12:10:00",340.46555160000003,60.811154399999999]
["2024-11-01T16:20:00","2024-11-01T16:25:00",385.2501408,26.225091599999999]
["2024-11-01T20:15:00","2024-11-01T20:20:00",542.28790200000003,9.1578780000000002]
["2024-11-02T01:00:00","2024-11-02T01:05:00",398.541876,-27.336120000000001]
["2024-11-02T05:20:00","2024-11-02T05:25:00",410.3424564,-22.910584799999999]
["2024-11-02T09:35:00","2024-11-02T09:40:00",226.36000079999999,11.9114532]
["2024-11-02T15:20:00","2024-11-02T15:25:00",308.60738520000001,6.2056079999999998]
["2024-11-02T18:15:00","2024-11-02T18:20:00",453.47058240000001,0.18728400000000001]
["2024-11-02T22:30:00","2024-11-02T22:35:00",401.9308608,-25.816250400000001]
["2024-11-03T03:05:00","2024-11-03T03:10:00",348.24246959999999,-32.024367599999998]
["2024-11-03T07:10:00","2024-11-03T07:15:00",316.01467200000002,-18.665440799999999]
["2024-11-03T11:25:00","2024-11-03T11:30:00",168.45751200000001,18.109542000000001]
["2024-11-03T15:10:00","2024-11-03T15:15:00",231.0004668,13.6672476]
["2024-11-03T20:05:00","2024-11-03T20:10:00",455.3859324,-19.768192800000001]
["2024-11-04T00:20:00","2024-11-04T00:25:00",358.39993079999999,-36.818511600000001]
["2024-11-04T03:15:00","2024-11-04T03:20:00",339.94663200000002,-38.6243196]
["2024-11-04T09:00:00","2024-11-04T09:05:00",306.01922639999998,25.515769200000001]
["2024-11-04T13:20:00","2024-11-04T13:25:00",288.88737959999997,26.530121999999999]
["2024-11-04T19:40:00","2024-11-04T19:45:00",497.66599680000002,-0.14826]
["2024-11-04T21:55:00","2024-11-04T22:00:00",427.64289120000001,-22.3209336]
["2024-11-05T02:15:00","2024-11-05T02:20:00",347.4796212,-37.748354399999997]
["2024-11-05T07:45:00","2024-11-05T07:50:00",287.30067000000003,-12.8846772]
["2024-11-05T10:50:00","2024-11-05T10:55:00",175.29345839999999,18.0868392]
["2024-11-05T15:10:00","2024-11-05T15:15:00",310.14404639999998,24.552240000000001]
["2024-11-05T19:25:00","2024-11-05T19:30:00",502.08289079999997,2.8844028000000002]
["2024-11-05T22:10:00","2024-11-05T22:15:00",412.77120239999999,-19.463846400000001]
["2024-11-06T04:05:00","2024-11-06T04:10:00",382.62329039999997,-21.603910800000001]
["2024-11-06T08:20:00","2024-11-06T08:25:00",468.08471880000002,84.904960799999998]
["2024-11-06T14:35:00","2024-11-06T14:40:00",591.89779559999999,129.8744892]
["2024-11-06T17:00:00","2024-11-06T17:05:00",583.85297879999996,80.4184044]
["2024-11-06T21:20:00","2024-11-06T21:25:00",482.93794079999998,5.088438]
["2024-11-07T02:40:00","2024-11-07T02:45:00",379.74324239999999,-15.601593599999999]
["2024-11-07T05:55:00","2024-11-07T06:00:00",490.71967919999997,25.335183600000001]
["2024-11-07T10:15:00","2024-11-07T10:20:00",320.20398119999999,81.332712000000001]
["2024-11-07T14:45:00","2024-11-07T14:50:00",451.32571560000002,66.480977999999993]
["2024-11-07T18:50:00","2024-11-07T18:55:00",539.59548840000002,20.927998800000001]
["2024-11-07T23:10:00","2024-11-07T23:15:00",437.77850280000001,-12.324027600000001]
["2024-11-08T02:50:00","2024-11-08T02:55:00",365.30280240000002,-29.817512399999998]
["2024-11-08T07:50:00","2024-11-08T07:55:00",433.0668288,59.256017999999997]
["2024-11-08T12:05:00","2024-11-08T12:10:00",316.74593879999998,64.368478800000005]
["2024-11-08T16:20:00","2024-11-08T16:25:00",406.82273279999998,31.823073600000001]
["2024-11-08T21:35:00","2024-11-08T21:40:00",466.57949400000001,-11.184096]
["2024-11-09T01:00:00","2024-11-09T01:05:00",384.23970359999998,-26.5764864]
["2024-11-09T05:20:00","2024-11-09T05:25:00",402.15499920000002,-19.198412399999999]
["2024-11-09T09:40:00","2024-11-09T09:45:00",213.7838352,18.7549332]
["2024-11-09T13:55:00","2024-11-09T14:00:00",340.02540720000002,5.0152092000000001]
["2024-11-09T18:15:00","2024-11-09T18:20:00",440.95775040000001,-10.573227599999999]
["2024-11-09T21:45:00","2024-11-09T21:50:00",427.05383519999998,-24.609272399999998]
["2024-11-10T02:50:00","2024-11-10T02:55:00",342.48064440000002,-44.126624399999997]
["2024-11-10T07:10:00","2024-11-10T07:15:00",322.79265720000001,-24.7662564]
["2024-11-10T09:50:00","2024-11-10T09:55:00",273.2873376,-7.4195352000000003]
["2024-11-10T15:50:00","2024-11-10T15:55:00",283.79923079999998,-2.2836335999999999]
["2024-11-10T20:05:00","2024-11-10T20:10:00",473.675184,-16.098678]
["2024-11-10T21:55:00","2024-11-10T22:00:00",414.64893239999998,-26.128635599999999]
["2024-11-11T04:45:00","2024-11-11T04:50:00",415.8691164,-17.683550400000001]
["2024-11-11T09:00:00","2024-11-11T09:05:00",350.15481,61.711162799999997]
["2024-11-11T14:20:00","2024-11-11T14:25:00",370.26217200000002,80.757291600000002]
["2024-11-11T17:40:00","2024-11-11T17:45:00",546.0460392,48.156724799999999]
["2024-11-11T21:55:00","2024-11-11T22:00:00",456.43778040000001,-0.97874879999999997]
["2024-11-12T02:15:00","2024-11-12T02:20:00",370.50479519999999,-22.913014799999999]
["2024-11-12T04:45:00","2024-11-12T04:50:00",424.02975120000002,-7.6686468000000003]
["2024-11-12T10:50:00","2024-11-12T10:55:00",364.80054000000001,89.227990800000001]
["2024-11-12T15:10:00","2024-11-12T15:15:00",544.76020800000003,84.514299600000001]
["2024-11-12T16:50:00","2024-11-12T16:55:00",591.17251080000005,58.285764]
["2024-11-12T23:50:00","2024-11-12T23:55:00",421.73269199999999,-7.0913795999999998]
["2024-11-13T04:05:00","2024-11-13T04:10:00",397.58877480000001,-13.0518132]
["2024-11-13T09:15:00","2024-11-13T09:20:00",579.1347816,77.990585999999993]
["2024-11-13T12:45:00","2024-11-13T12:50:00",567.88266480000004,77.823459600000007]
["2024-11-13T17:00:00","2024-11-13T17:05:00",461.36155559999997,31.648162800000001]
["2024-11-13T21:20:00","2024-11-13T21:25:00",498.11406360000001,5.4721919999999997]
["2024-11-14T01:40:00","2024-11-14T01:45:00",383.54083800000001,-20.946908400000002]
["2024-11-14T05:55:00","2024-11-14T06:00:00",500.0749452,24.587759999999999]
["2024-11-14T09:05:00","2024-11-14T09:10:00",460.02728280000002,62.852901600000003]
["2024-11-14T14:35:00","2024-11-14T14:40:00",271.48490880000003,61.548096000000001]
["2024-11-14T18:50:00","2024-11-14T18:55:00",535.63784280000004,15.612814800000001]
["2024-11-14T21:10:00","2024-11-14T21:15:00",499.02295079999999,1.7337072]
["2024-11-15T03:30:00","2024-11-15T03:35:00",383.82180360000001,-24.124492799999999]
["2024-11-15T07:45:00","2024-11-15T07:50:00",438.11492520000002,61.628653200000002]
["2024-11-15T12:05:00","2024-11-15T12:10:00",265.26369119999998,76.545076800000004]
["2024-11-15T16:15:00","2024-11-15T16:20:00",375.24329879999999,33.599936399999997]
["2024-11-15T20:45:00","2024-11-15T20:50:00",507.20335920000002,5.3407739999999997]
["2024-11-16T01:00:00","2024-11-16T01:05:00",382.08486959999999,-26.189775600000001]
["2024-11-16T04:20:00","2024-11-16T04:25:00",378.9044844,-27.3330552]
["2024-11-16T09:40:00","2024-11-16T09:45:00",228.80404559999999,32.478803999999997]
["2024-11-16T13:55:00","2024-11-16T14:00:00",323.03436240000002,64.365520799999999]
["2024-11-16T16:05:00","2024-11-16T16:10:00",500.3663196,70.799461199999996]
["2024-11-16T22:35:00","2024-11-16T22:40:00",479.15482919999999,8.4580920000000006]
["2024-11-17T02:50:00","2024-11-17T02:55:00",395.53511520000001,-17.384409600000001]
["2024-11-17T04:10:00","2024-11-17T04:15:00",384.58774920000002,-19.000999199999999]
["2024-11-17T11:30:00","2024-11-17T11:35:00",469.62641639999998,2.2368383999999999]
["2024-11-17T15:45:00","2024-11-17T15:50:00",327.10383480000002,7.6838123999999999]
["2024-11-17T16:15:00","2024-11-17T16:20:00",350.36006520000001,6.4846440000000003]
["2024-11-18T00:25:00","2024-11-18T00:30:00",377.61235679999999,-30.566492400000001]
["2024-11-18T00:30:00","2024-11-18T00:35:00",375.90536400000002,-30.630982800000002]
["2024-11-18T08:40:00","2024-11-18T08:45:00",425.52724920000003,53.815267200000001]
["2024-11-18T09:05:00","2024-11-18T09:10:00",417.48037920000002,53.376775199999997]
["2024-11-18T13:25:00","2024-11-18T13:30:00",417.09384599999998,74.560489200000006]
["2024-11-18T17:40:00","2024-11-18T17:45:00",519.87760679999997,30.093898800000002]
["2024-11-18T23:05:00","2024-11-18T23:10:00",437.74911359999999,-10.512822]
["2024-11-19T02:20:00","2024-11-19T02:25:00",385.4773692,-19.615150799999999]
["2024-11-19T06:35:00","2024-11-19T06:40:00",545.6703996,50.594617200000002]
["2024-11-19T11:10:00","2024-11-19T11:15:00",299.62324319999999,71.533363199999997]
["2024-11-19T15:15:00","2024-11-19T15:20:00",317.690808,59.682856800000003]
["2024-11-19T19:30:00","2024-11-19T19:35:00",550.46101080000005,18.981325200000001]
["2024-11-20T03:35:00","2024-11-20T03:40:00",387.57228479999998,-21.688026000000001]
["2024-11-20T04:10:00","2024-11-20T04:15:00",406.01822399999998,-16.191672000000001]
["2024-11-20T08:30:00","2024-11-20T08:35:00",420.92423400000001,68.372659200000001]
["2024-11-20T15:40:00","2024-11-20T15:45:00",331.80722639999999,56.019382800000002]
["2024-11-20T17:05:00","2024-11-20T17:10:00",484.61619359999997,38.214256800000001]
["2024-11-20T21:25:00","2024-11-20T21:30:00",492.6167724,5.8327704000000002]
["2024-11-21T03:45:00","2024-11-21T03:50:00",395.14026360000003,-19.4705136]
["2024-11-21T06:00:00","2024-11-21T06:05:00",514.2892908,30.621159599999999]
["2024-11-21T10:20:00","2024-11-21T10:25:00",328.31637000000001,98.225927999999996]
["2024-11-21T14:35:00","2024-11-21T14:40:00",436.11122519999998,124.9772796]
["2024-11-21T22:30:00","2024-11-21T22:35:00",463.94059920000001,5.6963460000000001]
["2024-11-21T23:15:00","2024-11-21T23:20:00",461.56774200000001,2.6198472000000002]
["2024-11-22T03:30:00","2024-11-22T03:35:00",393.88945919999998,-15.349874399999999]
["2024-11-22T10:35:00","2024-11-22T10:40:00",495.9018312,140.4826008]
["2024-11-22T12:10:00","2024-11-22T12:15:00",589.71129719999999,152.15838959999999]
["2024-11-22T16:30:00","2024-11-22T16:35:00",869.13172199999997,189.22119480000001]
["2024-11-22T22:40:00","2024-11-22T22:45:00",557.78606760000002,65.340548400000003]
["2024-11-23T01:05:00","2024-11-23T01:10:00",463.46603520000002,11.9886336]
["2024-11-23T05:25:00","2024-11-23T05:30:00",447.8109528,13.240660800000001]
["2024-11-23T10:45:00","2024-11-23T10:50:00",568.51567439999997,121.3554444]
["2024-11-23T14:00:00","2024-11-23T14:05:00",746.90425679999998,147.9591288]
["2024-11-23T18:20:00","2024-11-23T18:25:00",606.66311280000002,71.081036400000002]
["2024-11-23T22:50:00","2024-11-23T22:55:00",466.22927879999997,4.892436]
["2024-11-24T03:00:00","2024-11-24T03:05:00",390.4857432,-14.2377816]
["2024-11-24T07:15:00","2024-11-24T07:20:00",431.3733684,-3.7700640000000001]
["2024-11-24T10:55:00","2024-11-24T11:00:00",449.32050479999998,19.392934799999999]
["2024-11-24T15:55:00","2024-11-24T16:00:00",475.38953759999998,19.7248044]
["2024-11-24T20:10:00","2024-11-24T20:15:00",505.39595400000002,27.3539016]
["2024-11-25T00:30:00","2024-11-25T00:35:00",385.77520440000001,-21.191046]
["2024-11-25T05:40:00","2024-11-25T05:45:00",477.11031839999998,18.3276672]
["2024-11-25T09:05:00","2024-11-25T09:10:00",565.8655248,81.673900799999998]
["2024-11-25T13:25:00","2024-11-25T13:30:00",571.97334839999996,81.534626399999993]
["2024-11-25T17:45:00","2024-11-25T17:50:00",590.77228079999998,74.258201999999997]
["2024-11-25T22:00:00","2024-11-25T22:05:00",464.12338920000002,28.005573600000002]
["2024-11-26T02:20:00","2024-11-26T02:25:00",384.48975480000001,-7.2482531999999997]
["2024-11-26T05:50:00","2024-11-26T05:55:00",505.88552040000002,41.809022400000003]
["2024-11-26T11:00:00","2024-11-26T11:05:00",426.0336312,117.09298920000001]
["2024-11-26T15:15:00","2024-11-26T15:20:00",576.78915840000002,131.12968319999999]
["2024-11-26T22:15:00","2024-11-26T22:20:00",527.72092320000002,62.965932000000002]
["2024-11-26T23:55:00",45623,456.09898079999999,19.307239200000001]
["2024-11-27T04:10:00","2024-11-27T04:15:00",447.96394079999999,20.089717199999999]
["2024-11-27T10:20:00","2024-11-27T10:25:00",438.88771800000001,134.97327000000001]
["2024-11-27T12:50:00","2024-11-27T12:55:00",545.3620128,173.42484239999999]
["2024-11-27T17:05:00","2024-11-27T17:10:00",688.44683280000004,117.56117759999999]
["2024-11-27T22:05:00","2024-11-27T22:10:00",488.12616839999998,43.044325200000003]
["2024-11-28T01:45:00","2024-11-28T01:50:00",398.57613120000002,1.9630896]
["2024-11-28T06:00:00","2024-11-28T06:05:00",513.26860199999999,54.555976800000003]
["2024-11-28T10:20:00","2024-11-28T10:25:00",372.24389280000003,116.927736]
["2024-11-28T12:50:00","2024-11-28T12:55:00",409.97135639999999,126.21846720000001]
["2024-11-28T19:00:00","2024-11-28T19:05:00",621.85917600000005,79.179957599999994]
["2024-11-28T23:15:00","2024-11-28T23:20:00",481.02803039999998,22.4716956]
["2024-11-29T05:15:00","2024-11-29T05:20:00",465.71010840000002,28.381489200000001]
["2024-11-29T07:55:00","2024-11-29T08:00:00",507.01676639999999,96.978555600000007]
["2024-11-29T12:10:00","2024-11-29T12:15:00",452.7076596,143.16292920000001]
["2024-11-29T17:20:00","2024-11-29T17:25:00",767.48560799999996,176.4304272]
["2024-11-29T20:50:00","2024-11-29T20:55:00",638.54774399999997,96.373567199999997]
["2024-11-30T01:05:00","2024-11-30T01:10:00",433.34484120000002,10.387608]
["2024-11-30T05:05:00","2024-11-30T05:10:00",423.53401919999999,20.216138399999998]
["2024-11-30T09:45:00","2024-11-30T09:50:00",528.90886079999996,58.948501200000003]
["2024-11-30T14:00:00","2024-11-30T14:05:00",443.09252400000003,46.1304096]
["2024-11-30T17:10:00","2024-11-30T17:15:00",462.42886440000001,39.7722336]
["2024-11-30T22:40:00","2024-11-30T22:45:00",436.75816680000003,9.3268799999999999E-2]
["2024-12-01T02:55:00","2024-12-01T03:00:00",363.56251680000003,-19.097196]
["2024-12-01T05:15:00","2024-12-01T05:20:00",371.01057359999999,-13.1589036]
["2024-12-01T11:35:00","2024-12-01T11:40:00",349.22592839999999,32.1970356]
["2024-12-01T15:55:00","2024-12-01T16:00:00",473.33324040000002,25.625523600000001]
["2024-12-01T20:10:00","2024-12-01T20:15:00",504.98809199999999,27.361624800000001]
["2024-12-02T00:20:00","2024-12-02T00:25:00",387.93304080000001,-14.2393284]
["2024-12-02T04:50:00","2024-12-02T04:55:00",413.57836079999998,-1.9941708]
["2024-12-02T09:05:00","2024-12-02T09:10:00",396.53638560000002,104.1976488]
["2024-12-02T12:05:00","2024-12-02T12:10:00",420.19247639999998,146.83262160000001]
["2024-12-02T17:45:00","2024-12-02T17:50:00",783.94843319999995,151.19186160000001]
["2024-12-02T22:00:00","2024-12-02T22:05:00",564.63792720000004,49.055403599999998]
["2024-12-03T00:10:00","2024-12-03T00:15:00",477.10130040000001,19.4969556]
["2024-12-03T06:40:00","2024-12-03T06:45:00",565.46222160000002,92.026443599999993]
["2024-12-03T10:55:00","2024-12-03T11:00:00",580.27584360000003,162.46096560000001]
["2024-12-03T16:35:00","2024-12-03T16:40:00",681.62380800000005,121.8575352]
["2024-12-03T19:35:00","2024-12-03T19:40:00",591.14090880000003,50.317092000000002]
["2024-12-03T23:55:00",45630,423.77958599999999,-10.1257644]
["2024-12-04T04:40:00","2024-12-04T04:45:00",426.29435160000003,-9.4816991999999995]
["2024-12-04T08:30:00","2024-12-04T08:35:00",402.87725760000001,77.630239200000005]
["2024-12-04T12:50:00","2024-12-04T12:55:00",337.43343119999997,116.9069724]
["2024-12-04T17:05:00","2024-12-04T17:10:00",537.98181720000002,77.305536000000004]
["2024-12-04T19:05:00","2024-12-04T19:10:00",590.4902664,60.186076800000002]
["2024-12-05T01:45:00","2024-12-05T01:50:00",388.51598039999999,-19.398100800000002]
["2024-12-05T06:00:00","2024-12-05T06:05:00",486.33051239999998,38.484292799999999]
["2024-12-05T11:30:00","2024-12-05T11:35:00",452.11821600000002,137.35148280000001]
["2024-12-05T14:40:00","2024-12-05T14:45:00",616.13907600000005,165.4789236]
["2024-12-05T18:55:00","2024-12-05T19:00:00",815.68255079999994,151.63142880000001]
["2024-12-05T23:35:00","2024-12-05T23:40:00",501.29668559999999,24.387181200000001]
["2024-12-06T03:35:00","2024-12-06T03:40:00",407.62729200000001,-4.2460883999999997]
["2024-12-06T07:55:00","2024-12-06T08:00:00",616.16286839999998,123.862494]
["2024-12-06T11:40:00","2024-12-06T11:45:00",630.31743359999996,159.3143436]
["2024-12-06T16:30:00","2024-12-06T16:35:00",655.94127479999997,100.4937972]
["2024-12-06T20:50:00","2024-12-06T20:55:00",547.94605439999998,44.932113600000001]
["2024-12-06T23:45:00","2024-12-06T23:50:00",463.40073000000001,8.3447303999999995]
["2024-12-07T05:25:00","2024-12-07T05:30:00",433.46191920000001,7.7480279999999997]
["2024-12-07T09:45:00","2024-12-07T09:50:00",407.01982320000002,72.271103999999994]
["2024-12-07T11:50:00","2024-12-07T11:55:00",515.6661312,88.658620799999994]
["2024-12-07T18:25:00","2024-12-07T18:30:00",592.02681240000004,64.962920400000002]
["2024-12-07T22:40:00","2024-12-07T22:45:00",426.695334,-13.724524799999999]
["2024-12-08T02:55:00","2024-12-08T03:00:00",359.37464160000002,-28.78323]
["2024-12-08T06:35:00","2024-12-08T06:40:00",330.17334840000001,-18.499681200000001]
["2024-12-08T11:35:00","2024-12-08T11:40:00",170.77287240000001,26.740305599999999]
["2024-12-08T15:55:00","2024-12-08T16:00:00",277.8762696,14.4588936]
["2024-12-08T18:40:00","2024-12-08T18:45:00",462.60235920000002,-5.457408]
["2024-12-09T00:30:00","2024-12-09T00:35:00",375.41580119999998,-27.168551999999998]
["2024-12-09T04:50:00","2024-12-09T04:55:00",399.85345560000002,-16.256497199999998]
["2024-12-09T06:45:00","2024-12-09T06:50:00",498.40330560000001,47.452521599999997]
["2024-12-09T13:25:00","2024-12-09T13:30:00",294.48456479999999,95.9342556]
["2024-12-09T17:45:00","2024-12-09T17:50:00",518.87744520000001,56.285422799999999]
["2024-12-09T18:50:00","2024-12-09T18:55:00",539.93075639999995,39.509517600000002]
["2024-12-10T02:25:00","2024-12-10T02:30:00",379.5729948,-17.087578799999999]
["2024-12-10T06:40:00","2024-12-10T06:45:00",515.46430559999999,47.056418399999998]
["2024-12-10T11:15:00","2024-12-10T11:20:00",286.38024239999999,87.327674400000006]
["2024-12-10T15:20:00","2024-12-10T15:25:00",344.59835399999997,74.370022800000001]
["2024-12-10T19:35:00","2024-12-10T19:40:00",538.13692319999996,23.092884000000002]
["2024-12-10T23:20:00","2024-12-10T23:25:00",440.72179679999999,-7.1318712]
["2024-12-11T04:15:00","2024-12-11T04:20:00",408.90863880000001,-8.4713484000000001]
["2024-12-11T08:30:00","2024-12-11T08:35:00",468.09387720000001,73.528268400000002]
["2024-12-11T12:50:00","2024-12-11T12:55:00",304.54970159999999,104.83481639999999]
["2024-12-11T13:45:00","2024-12-11T13:50:00",323.88443519999998,110.7117648]
["2024-12-11T21:25:00","2024-12-11T21:30:00",507.17453640000002,19.644611999999999]
["2024-12-11T21:30:00","2024-12-11T21:35:00",503.45918879999999,19.295424000000001]
["2024-12-12T01:50:00","2024-12-12T01:55:00",394.8717876,-10.455192]
["2024-12-12T06:10:00","2024-12-12T06:15:00",510.29373120000002,47.429298000000003]
["2024-12-12T10:25:00","2024-12-12T10:30:00",347.84037599999999,103.2817716]
["2024-12-12T18:15:00","2024-12-12T18:20:00",649.52063759999999,101.93957159999999]
["2024-12-12T19:05:00","2024-12-12T19:10:00",646.30908239999997,86.387685599999998]
["2024-12-12T23:20:00","2024-12-12T23:25:00",478.65711599999997,12.350613600000001]
["2024-12-13T06:20:00","2024-12-13T06:25:00",529.63601040000003,59.230877999999997]
["2024-12-13T08:00:00","2024-12-13T08:05:00",540.95261760000005,75.178083599999994]
["2024-12-13T12:15:00","2024-12-13T12:20:00",334.91458080000001,100.87286400000001]
["2024-12-13T18:05:00","2024-12-13T18:10:00",544.51598760000002,54.789278400000001]
["2024-12-13T20:55:00","2024-12-13T21:00:00",515.10092399999996,28.804657200000001]
["2024-12-14T01:10:00","2024-12-14T01:15:00",392.04754800000001,-17.394926399999999]
["2024-12-14T05:30:00","2024-12-14T05:35:00",370.96715399999999,-10.5537384]
["2024-12-14T13:10:00","2024-12-14T13:15:00",259.33689120000003,48.702787200000003]
["2024-12-14T14:10:00","2024-12-14T14:15:00",404.11338000000001,44.12811]
["2024-12-14T18:25:00","2024-12-14T18:30:00",480.73213800000002,31.044803999999999]
["2024-12-15T01:15:00","2024-12-15T01:20:00",361.72334039999998,-31.638448799999999]
["2024-12-15T03:05:00","2024-12-15T03:10:00",344.921334,-36.193070400000003]
["2024-12-15T07:20:00","2024-12-15T07:25:00",299.4590316,-12.920778]
["2024-12-15T13:20:00","2024-12-15T13:25:00",321.27207479999998,66.027796800000004]
["2024-12-15T16:00:00","2024-12-15T16:05:00",560.14784880000002,92.065918800000006]
["2024-12-15T20:15:00","2024-12-15T20:20:00",685.36311120000005,106.4505144]
["2024-12-16T01:05:00","2024-12-16T01:10:00",426.4778508,-0.82166879999999998]
["2024-12-16T04:55:00","2024-12-16T05:00:00",469.61089920000001,18.749713199999999]
["2024-12-16T09:10:00","2024-12-16T09:15:00",746.84368080000002,159.6227208]
["2024-12-16T13:10:00","2024-12-16T13:15:00",884.10514079999996,222.02349839999999]
["2024-12-16T17:50:00","2024-12-16T17:55:00",1090.748014,269.76697919999998]
["2024-12-16T22:05:00","2024-12-16T22:10:00",580.39325399999996,73.0939956]
["2024-12-17T05:35:00","2024-12-17T05:40:00",505.21830599999998,35.860728000000002]
["2024-12-17T06:45:00","2024-12-17T06:50:00",533.4949752,68.091796799999997]
["2024-12-17T11:05:00","2024-12-17T11:10:00",393.5540148,113.875428]
["2024-12-17T15:20:00","2024-12-17T15:25:00",431.17038359999998,103.5362724]
["2024-12-17T20:20:00","2024-12-17T20:25:00",541.06103159999998,26.918895599999999]
[45644,"2024-12-18T00:05:00",413.0553324,-9.9030924000000002]
["2024-12-18T04:15:00","2024-12-18T04:20:00",406.4529708,-12.0757428]
["2024-12-18T08:05:00","2024-12-18T08:10:00",456.1493016,67.391259599999998]
["2024-12-18T12:55:00","2024-12-18T13:00:00",286.55975039999998,95.857282799999993]
["2024-12-18T17:10:00","2024-12-18T17:15:00",470.1315444,59.161635599999997]
["2024-12-19T00:30:00","2024-12-19T00:35:00",400.85874360000003,-14.505044399999999]
["2024-12-19T01:50:00","2024-12-19T01:55:00",374.21985960000001,-22.660527600000002]
["2024-12-19T06:05:00","2024-12-19T06:10:00",469.000248,26.281126799999999]
["2024-12-19T12:35:00","2024-12-19T12:40:00",348.14678400000003,105.79624920000001]
["2024-12-19T14:45:00","2024-12-19T14:50:00",467.62953720000002,122.74351559999999]
["2024-12-19T19:05:00","2024-12-19T19:10:00",690.12673080000002,101.760228]
["2024-12-20T00:40:00","2024-12-20T00:45:00",415.2954732,-4.8614268000000003]
["2024-12-20T03:40:00","2024-12-20T03:45:00",381.64534680000003,-17.556859200000002]
["2024-12-20T08:00:00","2024-12-20T08:05:00",456.04913879999998,76.195591199999996]
["2024-12-20T12:45:00","2024-12-20T12:50:00",531.83639640000001,145.59086640000001]
["2024-12-20T16:40:00","2024-12-20T16:45:00",672.01680599999997,125.15549040000001]
["2024-12-20T20:55:00","2024-12-20T21:00:00",529.17169679999995,21.957111600000001]
["2024-12-21T01:10:00","2024-12-21T01:15:00",382.00914239999997,-20.698446000000001]
["2024-12-21T07:30:00","2024-12-21T07:35:00",393.33600360000003,-8.1439859999999999]
["2024-12-21T09:50:00","2024-12-21T09:55:00",306.93918480000002,9.9379380000000008]
["2024-12-21T14:05:00","2024-12-21T14:10:00",182.3860344,25.915339199999998]
["2024-12-21T19:35:00","2024-12-21T19:40:00",454.02207240000001,-12.935438400000001]
["2024-12-21T22:45:00","2024-12-21T22:50:00",396.70071719999999,-30.146587199999999]
["2024-12-22T03:05:00","2024-12-22T03:10:00",334.93176,-41.650424399999999]
["2024-12-22T07:40:00","2024-12-22T07:45:00",334.2145428,-24.246351600000001]
["2024-12-22T11:40:00","2024-12-22T11:45:00",146.07554279999999,13.918197599999999]
["2024-12-22T16:00:00","2024-12-22T16:05:00",329.0028504,4.7537256000000001]
["2024-12-22T19:45:00","2024-12-22T19:50:00",470.80122119999999,-13.54017]
["2024-12-23T00:35:00","2024-12-23T00:40:00",354.89333160000001,-40.104261600000001]
["2024-12-23T04:55:00","2024-12-23T05:00:00",370.04103479999998,-35.332389599999999]
["2024-12-23T07:50:00","2024-12-23T07:55:00",334.60822560000003,4.5583152]
["2024-12-23T13:35:00","2024-12-23T13:40:00",314.08134239999998,18.040184400000001]
["2024-12-23T17:50:00","2024-12-23T17:55:00",458.74242600000002,-3.004032]
["2024-12-24T00:15:00","2024-12-24T00:20:00",373.72100760000001,-37.994006400000004]
["2024-12-24T02:30:00","2024-12-24T02:35:00",341.88036360000001,-41.388001199999998]
["2024-12-24T06:45:00","2024-12-24T06:50:00",391.00305959999997,-11.872064399999999]
["2024-12-24T11:05:00","2024-12-24T11:10:00",346.83359760000002,5.1488123999999997]
["2024-12-24T14:40:00","2024-12-24T14:45:00",218.52167159999999,18.444829200000001]
["2024-12-24T19:40:00","2024-12-24T19:45:00",443.52457559999999,-17.502838799999999]
[45651,"2024-12-25T00:05:00",347.27481,-51.710526000000002]
["2024-12-25T02:45:00","2024-12-25T02:50:00",300.37877400000002,-59.422786799999997]
["2024-12-25T08:35:00","2024-12-25T08:40:00",215.0556708,-22.8532668]
["2024-12-25T12:55:00","2024-12-25T13:00:00",202.11694679999999,14.977089599999999]
["2024-12-25T14:50:00","2024-12-25T14:55:00",304.94878679999999,28.985246400000001]
["2024-12-25T21:35:00","2024-12-25T21:40:00",526.91986799999995,15.903518399999999]
["2024-12-26T01:50:00","2024-12-26T01:55:00",364.83427319999998,-33.4051008]
["2024-12-26T07:15:00","2024-12-26T07:20:00",351.1971168,-1.3734287999999999]
["2024-12-26T10:30:00","2024-12-26T10:35:00",509.52389399999998,51.193870799999999]
["2024-12-26T14:45:00","2024-12-26T14:50:00",614.42102880000004,87.140722800000006]
["2024-12-26T19:20:00","2024-12-26T19:25:00",666.60112560000005,73.830772800000005]
["2024-12-26T23:25:00","2024-12-26T23:30:00",437.16723000000002,-11.9980788]
["2024-12-27T03:40:00","2024-12-27T03:45:00",347.83222560000002,-35.9104332]
["2024-12-27T08:00:00","2024-12-27T08:05:00",357.45538199999999,-3.7498320000000001]
["2024-12-27T09:45:00","2024-12-27T09:50:00",277.57591919999999,8.0496780000000001]
["2024-12-27T16:35:00","2024-12-27T16:40:00",386.24319960000003,8.1729863999999992]
["2024-12-27T20:55:00","2024-12-27T21:00:00",431.63357880000001,-23.422385999999999]
["2024-12-28T02:10:00","2024-12-28T02:15:00",326.96787719999998,-46.238874000000003]
["2024-12-28T05:35:00","2024-12-28T05:40:00",329.20325159999999,-41.023072800000001]
["2024-12-28T09:50:00","2024-12-28T09:55:00",235.8156132,-5.8107300000000004]
["2024-12-28T14:15:00","2024-12-28T14:20:00",388.1596212,-0.83620320000000004]
["2024-12-28T18:30:00","2024-12-28T18:35:00",416.31451079999999,-16.7479452]
["2024-12-28T22:45:00","2024-12-28T22:50:00",374.10961200000003,-36.360264000000001]
["2024-12-29T02:20:00","2024-12-29T02:25:00",321.90323519999998,-47.9187972]
["2024-12-29T07:25:00","2024-12-29T07:30:00",250.15045559999999,-29.140129200000001]
["2024-12-29T11:40:00","2024-12-29T11:45:00",158.52399600000001,-0.32712000000000002]
["2024-12-29T14:05:00","2024-12-29T14:10:00",166.17628680000001,9.0270983999999999]
["2024-12-29T20:20:00","2024-12-29T20:25:00",451.59417480000002,-14.519603999999999]
["2024-12-30T00:35:00","2024-12-30T00:40:00",346.50259080000001,-39.376871999999999]
["2024-12-30T02:10:00","2024-12-30T02:15:00",330.75655319999998,-41.5610268]
["2024-12-30T09:15:00","2024-12-30T09:20:00",251.81979720000001,21.7817112]
["2024-12-30T13:35:00","2024-12-30T13:40:00",395.1280428,61.789927200000001]
["2024-12-30T17:50:00","2024-12-30T17:55:00",481.52529720000001,28.850519999999999]
["2024-12-30T21:15:00","2024-12-30T21:20:00",447.42866520000001,-12.721272000000001]
["2024-12-31T02:30:00","2024-12-31T02:35:00",342.05124360000002,-35.454747599999997]
["2024-12-31T06:45:00","2024-12-31T06:50:00",358.32191640000002,-8.5984368]
["2024-12-31T09:20:00","2024-12-31T09:25:00",276.14005800000001,19.242586800000002]
["2024-12-31T15:25:00","2024-12-31T15:30:00",306.98855639999999,41.710523999999999]
["2024-12-31T19:40:00","2024-12-31T19:45:00",440.32934039999998,-9.4744451999999999]
["2024-12-31T21:05:00","2024-12-31T21:10:00",414.7703712,-23.892081600000001]
["2025-01-01T04:20:00","2025-01-01T04:25:00",326.23120799999998,-44.9857224]
["2025-01-01T08:35:00","2025-01-01T08:40:00",286.29741239999998,-25.803130800000002]
["2025-01-01T13:30:00","2025-01-01T13:35:00",101.0974164,6.0162443999999997]
["2025-01-01T17:15:00","2025-01-01T17:20:00",362.45327279999998,-19.097705999999999]
["2025-01-01T21:30:00","2025-01-01T21:35:00",392.79977400000001,-36.453829200000001]
["2025-01-02T01:35:00","2025-01-02T01:40:00",322.41800280000001,-47.821108799999998]
["2025-01-02T06:10:00","2025-01-02T06:15:00",355.45286520000002,-24.142980000000001]
["2025-01-02T10:30:00","2025-01-02T10:35:00",162.36461639999999,20.0528136]
["2025-01-02T13:40:00","2025-01-02T13:45:00",154.6894944,31.898379599999998]
["2025-01-02T19:05:00","2025-01-02T19:10:00",441.24551760000003,-13.861306799999999]
["2025-01-02T23:25:00","2025-01-02T23:30:00",389.07217439999999,-33.541592399999999]
["2025-01-03T03:40:00","2025-01-03T03:45:00",333.95543759999998,-42.103267199999998]
["2025-01-03T04:05:00","2025-01-03T04:10:00",343.40840639999999,-40.997455199999997]
["2025-01-03T12:20:00","2025-01-03T12:25:00",217.8608868,48.4443324]
["2025-01-03T16:35:00","2025-01-03T16:40:00",482.9306196,73.317853200000002]
["2025-01-03T20:30:00","2025-01-03T20:35:00",535.24519680000003,19.172066399999999]
["2025-01-04T01:15:00","2025-01-04T01:20:00",363.54755160000002,-28.393101600000001]
["2025-01-04T05:30:00","2025-01-04T05:35:00",347.3767848,-26.772801600000001]
["2025-01-04T08:35:00","2025-01-04T08:40:00",313.86514199999999,21.779313599999998]
["2025-01-04T14:10:00","2025-01-04T14:15:00",507.7204188,93.632943600000004]
["2025-01-04T14:15:00","2025-01-04T14:20:00",507.59857679999999,94.280534399999993]
["2025-01-04T20:40:00","2025-01-04T20:45:00",616.80959040000005,62.549911199999997]
["2025-01-04T22:50:00","2025-01-04T22:55:00",457.28858880000001,21.205513199999999]
["2025-01-05T03:10:00","2025-01-05T03:15:00",373.281678,-22.834815599999999]
["2025-01-05T08:45:00","2025-01-05T08:50:00",414.82920239999999,14.8503396]
["2025-01-05T11:45:00","2025-01-05T11:50:00",515.76721199999997,81.253006799999994]
["2025-01-05T16:05:00","2025-01-05T16:10:00",836.71040879999998,151.4414592]
["2025-01-05T20:50:00","2025-01-05T20:55:00",664.88460959999998,82.189357200000003]
["2025-01-06T00:45:00","2025-01-06T00:50:00",457.80705,3.0467460000000002]
["2025-01-06T05:00:00","2025-01-06T05:05:00",457.3804116,10.411197599999999]
["2025-01-06T09:15:00","2025-01-06T09:20:00",556.22669519999999,48.406661999999997]
["2025-01-06T15:35:00","2025-01-06T15:40:00",483.7284252,23.7879024]
["2025-01-06T17:55:00","2025-01-06T18:00:00",467.7348336,8.3357411999999993]
["2025-01-06T22:15:00","2025-01-06T22:20:00",420.45478439999999,-19.734685200000001]
["2025-01-07T03:40:00","2025-01-07T03:45:00",360.94952760000001,-29.191268399999998]
["2025-01-07T06:50:00","2025-01-07T06:55:00",416.81526120000001,12.314569199999999]
["2025-01-07T11:10:00","2025-01-07T11:15:00",239.47205159999999,57.989259599999997]
["2025-01-07T15:45:00","2025-01-07T15:50:00",361.90628279999999,68.438968799999998]
["2025-01-07T19:45:00","2025-01-07T19:50:00",519.65057400000001,22.203356400000001]
["2025-01-08T00:05:00","2025-01-08T00:10:00",393.49845599999998,-19.695848399999999]
["2025-01-08T03:50:00","2025-01-08T03:55:00",367.74335280000003,-24.249157199999999]
["2025-01-08T08:45:00","2025-01-08T08:50:00",338.1043224,45.3460392]
["2025-01-08T13:00:00","2025-01-08T13:05:00",390.79421280000003,97.429938000000007]
["2025-01-08T20:15:00","2025-01-08T20:20:00",618.03666959999998,63.775179600000001]
["2025-01-08T21:40:00","2025-01-08T21:45:00",534.60106800000005,29.653791600000002]
["2025-01-09T01:55:00","2025-01-09T02:00:00",395.71385759999998,-11.223849599999999]
["2025-01-09T06:15:00","2025-01-09T06:20:00",447.73902479999998,24.608337599999999]
["2025-01-09T10:40:00","2025-01-09T10:45:00",356.2413636,93.389349600000003]
["2025-01-09T14:50:00","2025-01-09T14:55:00",540.8414808,112.66698839999999]
["2025-01-09T19:10:00","2025-01-09T19:15:00",678.014904,109.1029272]
["2025-01-09T22:45:00","2025-01-09T22:50:00",500.48222879999997,20.3388144]
["2025-01-10T03:45:00","2025-01-10T03:50:00",402.62901119999998,-7.5953232000000002]
["2025-01-10T08:05:00","2025-01-10T08:10:00",486.60621600000002,63.912737999999997]
["2025-01-10T15:10:00","2025-01-10T15:15:00",567.21629159999998,131.62410840000001]
["2025-01-10T16:45:00","2025-01-10T16:50:00",685.81099919999997,139.1024568]
["2025-01-10T21:00:00","2025-01-10T21:05:00",640.12467360000005,78.441238799999994]
["2025-01-11T03:15:00","2025-01-11T03:20:00",410.31540960000001,-7.0424148000000004]
["2025-01-11T05:40:00","2025-01-11T05:45:00",403.19980800000002,-5.9385348000000002]
["2025-01-11T09:55:00","2025-01-11T10:00:00",389.97598799999997,77.784537599999993]
["2025-01-11T15:20:00","2025-01-11T15:25:00",625.67814120000003,141.4717728]
["2025-01-11T18:35:00","2025-01-11T18:40:00",725.31664439999997,118.5236628]
["2025-01-11T22:50:00","2025-01-11T22:55:00",521.14118040000005,25.479067199999999]
["2025-01-12T03:05:00","2025-01-12T03:10:00",408.43734360000002,-9.5669292000000006]
["2025-01-12T07:30:00","2025-01-12T07:35:00",389.65156200000001,7.3958339999999998]
["2025-01-12T11:45:00","2025-01-12T11:50:00",538.76437199999998,42.884330400000003]
["2025-01-12T16:05:00","2025-01-12T16:10:00",512.40970679999998,27.2474688]
["2025-01-12T22:10:00","2025-01-12T22:15:00",454.53672,-5.7536867999999997]
["2025-01-13T00:45:00","2025-01-13T00:50:00",394.77655440000001,-18.638535600000001]
["2025-01-13T05:00:00","2025-01-13T05:05:00",432.45151320000002,-3.7939812000000002]
["2025-01-13T10:15:00","2025-01-13T10:20:00",367.39650840000002,95.130213600000005]
["2025-01-13T13:40:00","2025-01-13T13:45:00",471.36024600000002,129.75584280000001]
["2025-01-13T17:55:00","2025-01-13T18:00:00",655.38998160000006,105.1643424]
["2025-01-13T22:20:00","2025-01-13T22:25:00",503.77781520000002,31.936512]
["2025-01-14T02:35:00","2025-01-14T02:40:00",401.7716964,-9.8582028000000008]
["2025-01-14T06:50:00","2025-01-14T06:55:00",517.83728040000005,50.199663600000001]
["2025-01-14T10:05:00","2025-01-14T10:10:00",384.35512080000001,102.97400759999999]
["2025-01-14T15:30:00","2025-01-14T15:35:00",498.60331200000002,122.1601848]
["2025-01-14T19:45:00","2025-01-14T19:50:00",672.5039448,109.2739284]
["2025-01-15T02:30:00","2025-01-15T02:35:00",421.71879840000003,-1.6279079999999999]
["2025-01-15T04:25:00","2025-01-15T04:30:00",443.206344,4.8024335999999996]
["2025-01-15T08:45:00","2025-01-15T08:50:00",611.81217360000005,86.3172876]
["2025-01-15T14:35:00","2025-01-15T14:40:00",573.8218584,80.497558799999993]
["2025-01-15T17:20:00","2025-01-15T17:25:00",567.5930472,44.300477999999998]
["2025-01-15T21:40:00","2025-01-15T21:45:00",471.94047239999998,-1.6235459999999999]
["2025-01-16T01:55:00","2025-01-16T02:00:00",374.13505199999997,-24.940030799999999]
["2025-01-16T05:20:00","2025-01-16T05:25:00",446.18033279999997,-1.1015448000000001]
["2025-01-16T10:35:00","2025-01-16T10:40:00",361.64611079999997,68.956136400000005]
["2025-01-16T14:50:00","2025-01-16T14:55:00",299.3495628,73.992599999999996]
["2025-01-16T17:05:00","2025-01-16T17:10:00",455.93475000000001,48.919135199999999]
["2025-01-16T23:30:00","2025-01-16T23:35:00",438.61560359999999,-10.816266000000001]
["2025-01-17T03:45:00","2025-01-17T03:50:00",390.84580319999998,-18.077214000000001]
["2025-01-17T09:30:00","2025-01-17T09:35:00",386.72139600000003,66.077296799999999]
["2025-01-17T12:25:00","2025-01-17T12:30:00",287.74678440000002,84.498368400000004]
["2025-01-17T16:40:00","2025-01-17T16:45:00",393.41827080000002,55.708474799999998]
["2025-01-17T21:35:00","2025-01-17T21:40:00",471.68690880000003,-2.6620691999999999]
["2025-01-18T01:20:00","2025-01-18T01:25:00",377.30534399999999,-24.543958799999999]
["2025-01-18T05:40:00","2025-01-18T05:45:00",379.4784492,-17.579541599999999]
["2025-01-18T09:40:00","2025-01-18T09:45:00",254.77802399999999,27.172854000000001]
["2025-01-18T14:15:00","2025-01-18T14:20:00",301.80107040000001,52.939357200000003]
["2025-01-18T18:35:00","2025-01-18T18:40:00",621.11173559999997,69.293475599999994]
["2025-01-18T22:50:00","2025-01-18T22:55:00",447.07411200000001,-9.4200672000000001]
["2025-01-19T04:25:00","2025-01-19T04:30:00",358.58284800000001,-34.174218000000003]
["2025-01-19T07:30:00","2025-01-19T07:35:00",322.36769279999999,-13.907876399999999]
["2025-01-19T11:45:00","2025-01-19T11:50:00",381.08509320000002,65.691700800000007]
["2025-01-19T16:30:00","2025-01-19T16:35:00",699.47874000000002,119.75734319999999]
["2025-01-19T20:25:00","2025-01-19T20:30:00",676.93993320000004,82.778055600000002]
["2025-01-20T00:40:00","2025-01-20T00:45:00",435.98460119999999,-3.9874787999999999]
["2025-01-20T04:35:00","2025-01-20T04:40:00",430.30016640000002,-5.0608332000000003]
["2025-01-20T09:20:00","2025-01-20T09:25:00",486.22950959999997,121.5652596]
["2025-01-20T13:40:00","2025-01-20T13:45:00",719.63651400000003,185.0072964]
["2025-01-20T16:40:00","2025-01-20T16:45:00",859.37097359999996,197.75979599999999]
["2025-01-20T22:15:00","2025-01-20T22:20:00",611.84684879999998,89.9114328]
["2025-01-21T02:35:00","2025-01-21T02:40:00",447.32909519999998,9.4450307999999996]
["2025-01-21T04:45:00","2025-01-21T04:50:00",481.08691199999998,21.333703199999999]
["2025-01-21T11:10:00","2025-01-21T11:15:00",583.77408839999998,165.08214599999999]
["2025-01-21T15:30:00","2025-01-21T15:35:00",750.27559919999999,190.7762256]
["2025-01-21T16:50:00","2025-01-21T16:55:00",792.757386,177.75744599999999]
["2025-01-22T00:10:00","2025-01-22T00:15:00",458.26665120000001,7.1827068000000001]
["2025-01-22T04:25:00","2025-01-22T04:30:00",442.31901360000001,3.0045348000000001]
["2025-01-22T08:40:00","2025-01-22T08:45:00",546.8117436,76.329453599999994]
["2025-01-22T11:35:00","2025-01-22T11:40:00",415.81626599999998,88.489401599999994]
["2025-01-22T17:20:00","2025-01-22T17:25:00",451.84260840000002,47.940218399999999]
["2025-01-22T21:40:00","2025-01-22T21:45:00",476.08117440000001,-0.2100408]
["2025-01-22T23:40:00","2025-01-22T23:45:00",429.43879199999998,-11.856800399999999]
["2025-01-23T06:15:00","2025-01-23T06:20:00",496.07882999999998,32.231093999999999]
["2025-01-23T10:35:00","2025-01-23T10:40:00",307.8578784,82.047939600000007]
["2025-01-23T11:45:00","2025-01-23T11:50:00",462.92211839999999,76.113669599999994]
["2025-01-23T19:10:00","2025-01-23T19:15:00",532.62341519999995,16.768215600000001]
["2025-01-23T23:30:00","2025-01-23T23:35:00",433.89630119999998,-12.363799200000001]
["2025-01-24T04:10:00","2025-01-24T04:15:00",398.18206320000002,-18.382191599999999]
["2025-01-24T08:10:00","2025-01-24T08:15:00",476.11476959999999,48.880132799999998]
["2025-01-24T12:25:00","2025-01-24T12:30:00",263.65041480000002,75.477703199999993]
["2025-01-24T16:15:00","2025-01-24T16:20:00",352.96289039999999,49.968775200000003]
["2025-01-24T21:05:00","2025-01-24T21:10:00",485.4614388,0.69805919999999999]
["2025-01-25T01:20:00","2025-01-25T01:25:00",380.88543720000001,-23.359172399999999]
["2025-01-25T04:00:00","2025-01-25T04:05:00",366.64746839999998,-27.392057999999999]
["2025-01-25T10:00:00","2025-01-25T10:05:00",276.24607320000001,23.7794268]
["2025-01-25T14:15:00","2025-01-25T14:20:00",241.0664328,41.205264]
["2025-01-25T18:35:00","2025-01-25T18:40:00",479.44492320000001,15.155098799999999]
["2025-01-25T23:05:00","2025-01-25T23:10:00",430.61541840000001,-18.838456799999999]
["2025-01-26T03:10:00","2025-01-26T03:15:00",350.50265880000001,-36.731886000000003]
["2025-01-26T07:30:00","2025-01-26T07:35:00",351.16732200000001,-19.753278000000002]
["2025-01-26T11:10:00","2025-01-26T11:15:00",217.738944,10.1964948]
["2025-01-26T16:10:00","2025-01-26T16:15:00",320.624526,20.993810400000001]
["2025-01-26T20:25:00","2025-01-26T20:30:00",489.18506639999998,-2.8821492000000002]
["2025-01-26T23:15:00","2025-01-26T23:20:00",424.11766319999998,-23.467994399999998]
["2025-01-27T05:05:00","2025-01-27T05:10:00",368.62286640000002,-32.945631599999999]
["2025-01-27T09:20:00","2025-01-27T09:25:00",434.17375079999999,42.826635600000003]
["2025-01-27T11:20:00","2025-01-27T11:25:00",364.85146559999998,63.885447599999999]
["2025-01-27T18:00:00","2025-01-27T18:05:00",870.06408720000002,160.9394748]
["2025-01-27T22:15:00","2025-01-27T22:20:00",511.82485320000001,16.101800399999998]
["2025-01-27T23:05:00","2025-01-27T23:10:00",489.44511360000001,6.8257295999999998]
["2025-01-28T06:55:00","2025-01-28T07:00:00",525.36434880000002,49.157736]
["2025-01-28T11:10:00","2025-01-28T11:15:00",387.9176592,92.985922799999997]
["2025-01-28T15:30:00","2025-01-28T15:35:00",364.40201519999999,79.119003599999999]
["2025-01-28T15:35:00","2025-01-28T15:40:00",369.48815760000002,78.883694399999996]
["2025-01-28T19:55:00","2025-01-28T20:00:00",556.73690759999999,25.8250092]
["2025-01-29T00:10:00","2025-01-29T00:15:00",414.52505760000003,-15.514758]
["2025-01-29T06:15:00","2025-01-29T06:20:00",485.15298960000001,34.222130399999998]
["2025-01-29T08:50:00","2025-01-29T08:55:00",389.65469159999998,63.2539248]
["2025-01-29T13:05:00","2025-01-29T13:10:00",304.40401320000001,85.321634399999994]
["2025-01-29T18:20:00","2025-01-29T18:25:00",517.91189759999997,33.583269600000001]
["2025-01-29T21:45:00","2025-01-29T21:50:00",476.57863200000003,-1.1297016]
["2025-01-30T02:00:00","2025-01-30T02:05:00",385.23191279999998,-20.850937200000001]
["2025-01-30T06:05:00","2025-01-30T06:10:00",511.75983000000002,29.4724428]
["2025-01-30T10:40:00","2025-01-30T10:45:00",367.94943239999998,76.424637599999997]
["2025-01-30T14:55:00","2025-01-30T15:00:00",315.49670400000002,77.2631844]
["2025-01-30T22:30:00","2025-01-30T22:35:00",443.1672552,-8.8757160000000006]
["2025-01-30T23:35:00","2025-01-30T23:40:00",428.57560799999999,-15.122118]
["2025-01-31T03:55:00","2025-01-31T04:00:00",394.37194319999998,-20.707529999999998]
["2025-01-31T10:35:00","2025-01-31T10:40:00",338.02644720000001,85.764240000000001]
["2025-01-31T12:30:00","2025-01-31T12:35:00",285.53980200000001,87.040317599999995]
["2025-01-31T16:50:00","2025-01-31T16:55:00",444.77081759999999,55.834418399999997]
["2025-01-31T21:05:00","2025-01-31T21:10:00",504.18037559999999,8.2330188]
["2025-02-01T01:20:00","2025-02-01T01:25:00",388.96598879999999,-20.749103999999999]
["2025-02-01T05:45:00","2025-02-01T05:50:00",404.17360559999997,-16.713037199999999]
["2025-02-01T10:00:00","2025-02-01T10:05:00",275.58249239999998,33.528958799999998]
["2025-02-01T17:25:00","2025-02-01T17:30:00",729.69308760000001,120.3335544]
["2025-02-01T18:40:00","2025-02-01T18:45:00",773.79629880000005,121.05747599999999]
["2025-02-01T22:55:00","2025-02-01T23:00:00",528.62873999999999,23.9024088]
["2025-02-02T05:30:00","2025-02-02T05:35:00",422.57276400000001,-7.4132724000000003]
["2025-02-02T07:35:00","2025-02-02T07:40:00",455.82054840000001,20.703280800000002]
["2025-02-02T11:50:00","2025-02-02T11:55:00",651.70858439999995,116.74326600000001]
["2025-02-02T17:35:00","2025-02-02T17:40:00",1020.7865,219.74869319999999]
["2025-02-02T20:30:00","2025-02-02T20:35:00",821.6198832,126.7578456]
["2025-02-03T00:50:00","2025-02-03T00:55:00",482.8622292,10.4605368]
["2025-02-03T05:40:00","2025-02-03T05:45:00",572.71536000000003,53.313255599999998]
["2025-02-03T09:25:00","2025-02-03T09:30:00",691.88511240000003,169.8401724]
["2025-02-03T13:45:00","2025-02-03T13:50:00",844.67771640000001,209.433414]
["2025-02-03T17:45:00","2025-02-03T17:50:00",1059.4404360000001,238.6043856]
["2025-02-03T22:25:00","2025-02-03T22:30:00",663.57961079999995,84.519762]
["2025-02-04T02:40:00","2025-02-04T02:45:00",525.14216160000001,38.369863199999998]
["2025-02-04T06:55:00","2025-02-04T07:00:00",704.06021520000002,130.82675280000001]
["2025-02-04T12:30:00","2025-02-04T12:35:00",827.83867199999997,224.6110716]
["2025-02-04T15:35:00","2025-02-04T15:40:00",808.41156120000005,189.4303104]
["2025-02-04T19:50:00","2025-02-04T19:55:00",634.85982960000001,67.417141200000003]
["2025-02-05T00:35:00","2025-02-05T00:40:00",450.88730399999997,5.6029248000000003]
["2025-02-05T04:30:00","2025-02-05T04:35:00",448.5128856,5.6014163999999997]
["2025-02-05T08:50:00","2025-02-05T08:55:00",495.16168320000003,83.414789999999996]
["2025-02-05T12:40:00","2025-02-05T12:45:00",342.04757999999998,114.62228279999999]
["2025-02-05T17:25:00","2025-02-05T17:30:00",575.95052639999994,83.294054399999993]
["2025-02-05T21:45:00","2025-02-05T21:50:00",530.93177760000003,26.973596400000002]
["2025-02-06T00:45:00","2025-02-06T00:50:00",437.56149599999998,2.1630672]
["2025-02-06T06:20:00","2025-02-06T06:25:00",542.60982000000001,48.0331908]
["2025-02-06T10:40:00","2025-02-06T10:45:00",498.36244199999999,144.2584512]
["2025-02-06T17:10:00","2025-02-06T17:15:00",927.31184519999999,222.42401039999999]
["2025-02-06T19:20:00","2025-02-06T19:25:00",857.13481679999995,185.355018]
["2025-02-06T23:35:00","2025-02-06T23:40:00",525.20198760000005,31.9191468]
["2025-02-07T05:15:00","2025-02-07T05:20:00",512.65998360000003,32.875135200000003]
["2025-02-07T08:15:00","2025-02-07T08:20:00",623.38707120000004,101.0035464]
["2025-02-07T12:30:00","2025-02-07T12:35:00",548.71429799999999,105.51817320000001]
["2025-02-07T16:50:00","2025-02-07T16:55:00",554.00036399999999,73.195600799999994]
["2025-02-07T19:40:00","2025-02-07T19:45:00",568.46342760000005,33.550606799999997]
["2025-02-08T01:25:00","2025-02-08T01:30:00",394.29323640000001,-17.4630732]
["2025-02-08T05:45:00","2025-02-08T05:50:00",413.45055359999998,-11.905277999999999]
["2025-02-08T12:05:00","2025-02-08T12:10:00",407.82443519999998,14.0148312]
["2025-02-08T14:20:00","2025-02-08T14:25:00",422.14255680000002,17.337185999999999]
["2025-02-08T18:40:00","2025-02-08T18:45:00",490.56693480000001,2.3079983999999998]
["2025-02-09T00:10:00","2025-02-09T00:15:00",400.48329000000001,-23.940534]
["2025-02-09T03:20:00","2025-02-09T03:25:00",353.71651439999999,-34.290772799999999]
["2025-02-09T07:35:00","2025-02-09T07:40:00",344.76949919999998,-11.776120799999999]
["2025-02-09T12:15:00","2025-02-09T12:20:00",352.94187720000002,35.319160799999999]
["2025-02-09T16:15:00","2025-02-09T16:20:00",485.08993679999998,47.187250800000001]
["2025-02-09T20:30:00","2025-02-09T20:35:00",517.30446480000001,4.2784176]
[45698,"2025-02-10T00:05:00",425.15565120000002,-13.7308512]
["2025-02-10T05:10:00","2025-02-10T05:15:00",470.74047000000002,10.834472399999999]
["2025-02-10T09:25:00","2025-02-10T09:30:00",514.33816920000004,91.825250400000002]
["2025-02-10T12:05:00","2025-02-10T12:10:00",387.28091760000001,110.9299188]
["2025-02-10T18:05:00","2025-02-10T18:10:00",629.81698319999998,83.710491599999997]
["2025-02-10T22:20:00","2025-02-10T22:25:00",499.76478479999997,18.9783036]
["2025-02-11T02:40:00","2025-02-11T02:45:00",420.28226640000003,-4.7779236000000003]
["2025-02-11T07:10:00","2025-02-11T07:15:00",555.11256960000003,68.666509199999993]
["2025-02-11T11:20:00","2025-02-11T11:25:00",428.04637200000002,120.9462444]
["2025-02-11T15:35:00","2025-02-11T15:40:00",687.33088799999996,152.09370720000001]
["2025-02-11T19:15:00","2025-02-11T19:20:00",824.18741880000005,158.7376428]
["2025-02-12T00:15:00","2025-02-12T00:20:00",488.04625320000002,15.1176312]
["2025-02-12T04:30:00","2025-02-12T04:35:00",466.77741359999999,13.5501804]
["2025-02-12T07:20:00","2025-02-12T07:25:00",585.90180239999995,97.835830799999997]
["2025-02-12T13:10:00","2025-02-12T13:15:00",689.26282800000001,191.03677440000001]
["2025-02-12T17:25:00","2025-02-12T17:30:00",998.24411520000001,234.83569199999999]
["2025-02-12T19:05:00","2025-02-12T19:10:00",989.32991159999995,214.07176680000001]
["2025-02-13T02:05:00","2025-02-13T02:10:00",526.582086,32.524071599999999]
["2025-02-13T06:20:00","2025-02-13T06:25:00",655.99626120000005,100.1356236]
["2025-02-13T11:30:00","2025-02-13T11:35:00",681.63221399999998,167.93638440000001]
["2025-02-13T15:00:00","2025-02-13T15:05:00",946.24250280000001,229.33509599999999]
["2025-02-13T19:20:00","2025-02-13T19:25:00",680.77607160000002,77.262084000000002]
["2025-02-13T23:35:00","2025-02-13T23:40:00",486.93801719999999,5.591736]
["2025-02-14T02:15:00","2025-02-14T02:20:00",431.34244560000002,-6.3976056000000003]
["2025-02-14T08:15:00","2025-02-14T08:20:00",497.58307559999997,77.691131999999996]
["2025-02-14T12:30:00","2025-02-14T12:35:00",461.36912280000001,92.884591200000003]
["2025-02-14T14:20:00","2025-02-14T14:25:00",481.94789880000002,77.767497599999999]
["2025-02-14T21:10:00","2025-02-14T21:15:00",502.2563988,8.0447999999999995E-3]
["2025-02-15T01:25:00","2025-02-15T01:30:00",374.44168560000003,-28.718563199999998]
["2025-02-15T06:25:00","2025-02-15T06:30:00",399.684864,-16.346354399999999]
["2025-02-15T10:05:00","2025-02-15T10:10:00",287.20235880000001,12.8625708]
["2025-02-15T14:20:00","2025-02-15T14:25:00",229.89744479999999,5.5255824000000002]
["2025-02-15T18:30:00","2025-02-15T18:35:00",453.70545479999998,-17.902801199999999]
["2025-02-15T23:00:00","2025-02-15T23:05:00",411.5153004,-33.822667199999998]
["2025-02-16T03:15:00","2025-02-16T03:20:00",351.0227112,-45.083026799999999]
["2025-02-16T06:35:00","2025-02-16T06:40:00",389.58475679999998,-29.47269]
["2025-02-16T11:55:00","2025-02-16T12:00:00",237.91069200000001,-6.2337575999999997]
["2025-02-16T16:15:00","2025-02-16T16:20:00",306.83198640000001,-11.509057200000001]
["2025-02-16T18:40:00","2025-02-16T18:45:00",464.47533240000001,-23.095951199999998]
["2025-02-17T00:50:00","2025-02-17T00:55:00",365.2036956,-39.549670800000001]
["2025-02-17T05:10:00","2025-02-17T05:15:00",447.7788084,-9.3907691999999994]
["2025-02-17T09:25:00","2025-02-17T09:30:00",356.91536159999998,56.138229600000003]
["2025-02-17T13:25:00","2025-02-17T13:30:00",292.93111440000001,71.929361999999998]
["2025-02-17T18:05:00","2025-02-17T18:10:00",532.26424440000005,32.655630000000002]
["2025-02-17T22:20:00","2025-02-17T22:25:00",435.34177560000001,-12.498842399999999]
["2025-02-18T01:30:00","2025-02-18T01:35:00",375.95952240000003,-27.886203600000002]
["2025-02-18T07:00:00","2025-02-18T07:05:00",521.04237479999995,53.476421999999999]
["2025-02-18T11:15:00","2025-02-18T11:20:00",290.03503319999999,79.066790400000002]
["2025-02-18T13:35:00","2025-02-18T13:40:00",413.74376999999998,73.024376399999994]
["2025-02-18T19:55:00","2025-02-18T20:00:00",539.3723688,11.807926800000001]
["2025-02-19T00:15:00","2025-02-19T00:20:00",401.58996359999998,-20.8982472]
["2025-02-19T01:40:00","2025-02-19T01:45:00",377.50274519999999,-27.000901200000001]
["2025-02-19T08:50:00","2025-02-19T08:55:00",542.04908880000005,58.863955199999999]
["2025-02-19T13:10:00","2025-02-19T13:15:00",406.12329840000001,69.549064799999996]
["2025-02-19T13:45:00","2025-02-19T13:50:00",427.50102600000002,66.360511200000005]
["2025-02-19T21:50:00","2025-02-19T21:55:00",470.9949828,-3.7982244000000001]
["2025-02-20T02:05:00","2025-02-20T02:10:00",378.8139516,-25.182154799999999]
["2025-02-20T06:10:00","2025-02-20T06:15:00",541.48106759999996,33.604619999999997]
["2025-02-20T10:45:00","2025-02-20T10:50:00",434.62352399999997,57.685981200000001]
["2025-02-20T15:00:00","2025-02-20T15:05:00",292.51547040000003,62.532257999999999]
["2025-02-20T19:15:00","2025-02-20T19:20:00",547.03360320000002,17.507843999999999]
["2025-02-20T20:35:00","2025-02-20T20:40:00",520.76308800000004,6.8465423999999997]
["2025-02-21T03:55:00","2025-02-21T04:00:00",384.74076359999998,-28.4864484]
["2025-02-21T04:00:00","2025-02-21T04:05:00",391.44590399999998,-25.759069199999999]
["2025-02-21T08:40:00","2025-02-21T08:45:00",413.9080548,56.084841599999997]
["2025-02-21T12:35:00","2025-02-21T12:40:00",330.32598840000003,94.1947428]
["2025-02-21T16:55:00","2025-02-21T17:00:00",612.79627800000003,106.1828916]
["2025-02-22T01:05:00","2025-02-22T01:10:00",424.58619479999999,-8.9726915999999992]
["2025-02-22T01:30:00","2025-02-22T01:35:00",403.10621159999999,-15.442962]
["2025-02-22T05:50:00","2025-02-22T05:55:00",433.55658240000002,-4.2782651999999999]
["2025-02-22T13:10:00","2025-02-22T13:15:00",542.28518880000001,118.8247896]
["2025-02-22T14:30:00","2025-02-22T14:35:00",631.80494880000003,125.76743519999999]
["2025-02-22T18:45:00","2025-02-22T18:50:00",881.36035319999996,162.46930320000001]
["2025-02-23T01:15:00","2025-02-23T01:20:00",544.72420199999999,32.616052799999999]
["2025-02-23T03:25:00","2025-02-23T03:30:00",503.38075800000001,18.957172799999999]
["2025-02-23T07:40:00","2025-02-23T07:45:00",517.92905519999999,35.930574]
["2025-02-23T12:00:00","2025-02-23T12:05:00",690.84230760000003,113.0252796]
["2025-02-23T20:00:00","2025-02-23T20:05:00",571.09598879999999,23.840353199999999]
["2025-02-23T20:35:00","2025-02-23T20:40:00",546.49185480000006,15.6409488]
["2025-02-24T00:55:00","2025-02-24T01:00:00",398.01999840000002,-22.282655999999999]
["2025-02-24T08:05:00","2025-02-24T08:10:00",500.97513359999999,64.800998399999997]
["2025-02-24T09:30:00","2025-02-24T09:35:00",488.71240560000001,75.045764399999996]
["2025-02-24T13:50:00","2025-02-24T13:55:00",325.92197520000002,90.859875599999995]
["2025-02-24T20:10:00","2025-02-24T20:15:00",546.16053839999995,18.656853600000002]
["2025-02-24T22:30:00","2025-02-24T22:35:00",434.00129399999997,-15.0431916]
["2025-02-25T02:45:00","2025-02-25T02:50:00",391.42009919999998,-18.763360800000001]
["2025-02-25T08:15:00","2025-02-25T08:20:00",479.56842719999997,73.318202400000004]
["2025-02-25T11:25:00","2025-02-25T11:30:00",338.84426159999998,98.936009999999996]
["2025-02-25T15:40:00","2025-02-25T15:45:00",484.43465279999998,98.784147599999997]
["2025-02-25T20:00:00","2025-02-25T20:05:00",595.01376359999995,41.608036800000001]
["2025-02-26T00:20:00","2025-02-26T00:25:00",420.8587488,-9.0995916000000001]
["2025-02-26T04:35:00","2025-02-26T04:40:00",434.1309804,-4.0758587999999998]
["2025-02-26T08:05:00","2025-02-26T08:10:00",524.36108999999999,85.361125200000004]
["2025-02-26T13:15:00","2025-02-26T13:20:00",619.98252960000002,169.5272028]
["2025-02-26T17:30:00","2025-02-26T17:35:00",688.74519959999998,105.5598024]
["2025-02-26T21:50:00","2025-02-26T21:55:00",530.04597360000002,25.9777524]
["2025-02-27T03:10:00","2025-02-27T03:15:00",409.84039680000001,-9.4520592000000008]
["2025-02-27T06:30:00","2025-02-27T06:35:00",572.80832880000003,54.422043600000002]
["2025-02-27T10:45:00","2025-02-27T10:50:00",378.81276960000002,102.051804]
["2025-02-27T15:15:00","2025-02-27T15:20:00",520.3639584,119.94404280000001]
["2025-02-27T19:25:00","2025-02-27T19:30:00",641.0504052,84.337976400000002]
["2025-02-27T23:40:00","2025-02-27T23:45:00",464.55714840000002,2.4210959999999999]
["2025-02-28T03:20:00","2025-02-28T03:25:00",420.15435600000001,-5.4678516000000004]
["2025-02-28T08:20:00","2025-02-28T08:25:00",501.94063799999998,80.633688000000006]
["2025-02-28T12:35:00","2025-02-28T12:40:00",433.81382880000001,115.3727256]
["2025-02-28T19:25:00","2025-02-28T19:30:00",627.50389440000004,83.513222400000004]
["2025-02-28T21:15:00","2025-02-28T21:20:00",540.77117520000002,23.729836800000001]
["2025-03-01T01:30:00","2025-03-01T01:35:00",406.62555359999999,-15.955873199999999]
["2025-03-01T07:30:00","2025-03-01T07:35:00",422.50786799999997,10.0091976]
["2025-03-01T10:10:00","2025-03-01T10:15:00",293.14117320000003,36.617575199999997]
["2025-03-01T14:30:00","2025-03-01T14:35:00",334.79631239999998,60.2511048]
["2025-03-01T19:35:00","2025-03-01T19:40:00",530.69418240000005,14.7800136]
["2025-03-01T23:05:00","2025-03-01T23:10:00",443.13877439999999,-15.7155948]
["2025-03-02T03:25:00","2025-03-02T03:30:00",364.52490840000002,-32.538356399999998]
["2025-03-02T07:40:00","2025-03-02T07:45:00",391.7075208,-14.5886856]
["2025-03-02T10:20:00","2025-03-02T10:25:00",428.454678,3.5435856000000001]
["2025-03-02T16:20:00","2025-03-02T16:25:00",394.65758520000003,-5.5079064000000004]
["2025-03-02T20:35:00","2025-03-02T20:40:00",471.58876079999999,-17.718214799999998]
["2025-03-03T02:25:00","2025-03-03T02:30:00",356.62189439999997,-40.641423600000003]
["2025-03-03T05:15:00","2025-03-03T05:20:00",454.84455839999998,-7.2492023999999997]
["2025-03-03T09:30:00","2025-03-03T09:35:00",401.87972400000001,64.128806400000002]
["2025-03-03T14:30:00","2025-03-03T14:35:00",294.0535572,68.905786800000001]
["2025-03-03T18:10:00","2025-03-03T18:15:00",551.28350039999998,29.227863599999999]
["2025-03-03T22:25:00","2025-03-03T22:30:00",430.51502040000003,-19.805227200000001]
["2025-03-04T02:35:00","2025-03-04T02:40:00",380.51009879999998,-25.6560804]
["2025-03-04T07:05:00","2025-03-04T07:10:00",539.4976656,45.734157600000003]
["2025-03-04T11:25:00","2025-03-04T11:30:00",339.8959428,92.011092000000005]
["2025-03-04T14:40:00","2025-03-04T14:45:00",471.79171200000002,124.12121879999999]
["2025-03-04T20:00:00","2025-03-04T20:05:00",696.66249359999995,108.3253284]
["2025-03-05T00:20:00","2025-03-05T00:25:00",455.73259200000001,4.0730208000000001]
["2025-03-05T02:45:00","2025-03-05T02:50:00",421.11685440000002,-6.5508600000000001]
["2025-03-05T09:00:00","2025-03-05T09:05:00",506.81051760000003,104.75345040000001]
["2025-03-05T13:15:00","2025-03-05T13:20:00",635.54688599999997,170.79811799999999]
["2025-03-05T17:30:00","2025-03-05T17:35:00",724.83746880000001,115.48815]
["2025-03-05T21:30:00","2025-03-05T21:35:00",552.32057880000002,36.799394399999997]
["2025-03-06T02:10:00","2025-03-06T02:15:00",428.30231400000002,-10.724299200000001]
["2025-03-06T06:25:00","2025-03-06T06:30:00",570.82491359999995,43.184169599999997]
["2025-03-06T09:35:00","2025-03-06T09:40:00",574.16555519999997,68.804787599999997]
["2025-03-06T15:05:00","2025-03-06T15:10:00",436.99334879999998,63.827593200000003]
["2025-03-06T19:25:00","2025-03-06T19:30:00",620.13209879999999,42.8123796]
["2025-03-06T21:40:00","2025-03-06T21:45:00",521.06599200000005,11.753170799999999]
["2025-03-07T04:00:00","2025-03-07T04:05:00",424.98117719999999,-14.853562800000001]
["2025-03-07T08:20:00","2025-03-07T08:25:00",494.1948984,60.035826]
["2025-03-07T14:05:00","2025-03-07T14:10:00",495.47717640000002,116.4540444]
["2025-03-07T17:00:00","2025-03-07T17:05:00",686.53382520000002,112.9505892]
["2025-03-07T21:15:00","2025-03-07T21:20:00",566.87211479999996,26.727493200000001]
["2025-03-08T02:10:00","2025-03-08T02:15:00",398.7607908,-24.4060296]
["2025-03-08T05:55:00","2025-03-08T06:00:00",434.55512640000001,-15.6230388]
["2025-03-08T10:10:00","2025-03-08T10:15:00",332.3019888,43.775541599999997]
["2025-03-08T14:25:00","2025-03-08T14:30:00",478.16028240000003,80.481001199999994]
["2025-03-08T16:35:00","2025-03-08T16:40:00",628.42945440000005,87.184118400000003]
["2025-03-08T23:05:00","2025-03-08T23:10:00",477.723996,-7.4516460000000002]
["2025-03-09T03:25:00","2025-03-09T03:30:00",382.1368152,-31.713721199999998]
["2025-03-09T09:00:00","2025-03-09T09:05:00",373.70233560000003,17.802204]
["2025-03-09T12:00:00","2025-03-09T12:05:00",448.60422240000003,71.756907600000005]
["2025-03-09T16:20:00","2025-03-09T16:25:00",780.72031319999996,127.2856056]
["2025-03-09T21:05:00","2025-03-09T21:10:00",649.11360720000005,58.719523199999998]
["2025-03-10T00:55:00","2025-03-10T01:00:00",475.47732960000002,2.3979924000000001]
["2025-03-10T05:15:00","2025-03-10T05:20:00",455.6833656,-3.2110403999999999]
["2025-03-10T09:10:00","2025-03-10T09:15:00",480.37211280000002,58.444626]
["2025-03-10T13:55:00","2025-03-10T14:00:00",660.15804479999997,136.7144304]
["2025-03-10T18:10:00","2025-03-10T18:15:00",884.13256079999996,168.22246559999999]
["2025-03-10T21:15:00","2025-03-10T21:20:00",638.11782960000005,50.763045599999998]
["2025-03-11T02:50:00","2025-03-11T02:55:00",437.76658200000003,-7.4217371999999999]
["2025-03-11T07:05:00","2025-03-11T07:10:00",617.64020640000001,83.670419999999993]
["2025-03-11T09:00:00","2025-03-11T09:05:00",603.25521479999998,116.8412124]
["2025-03-11T15:45:00","2025-03-11T15:50:00",931.75889159999997,193.5058812]
["2025-03-11T20:00:00","2025-03-11T20:05:00",801.64193880000005,116.33153280000001]
["2025-03-12T00:20:00","2025-03-12T00:25:00",497.61590760000001,7.4928312000000004]
["2025-03-12T04:05:00","2025-03-12T04:10:00",476.64864840000001,0.49707600000000002]
["2025-03-12T08:55:00","2025-03-12T09:00:00",679.47137520000001,126.98736479999999]
["2025-03-12T13:15:00","2025-03-12T13:20:00",810.56737199999998,196.97597279999999]
["2025-03-12T16:10:00","2025-03-12T16:15:00",939.30748919999996,206.95301520000001]
["2025-03-12T21:55:00","2025-03-12T22:00:00",544.13197200000002,17.644377599999999]
["2025-03-13T02:10:00","2025-03-13T02:15:00",438.19911839999997,-12.968091599999999]
["2025-03-13T04:15:00","2025-03-13T04:20:00",460.22251319999998,-5.4148464000000001]
["2025-03-13T10:50:00","2025-03-13T10:55:00",560.62577880000003,81.606613199999998]
["2025-03-13T15:05:00","2025-03-13T15:10:00",467.6144208,83.597476799999995]
["2025-03-13T16:00:00","2025-03-13T16:05:00",531.87496199999998,80.2737348]
["2025-03-13T23:45:00","2025-03-13T23:50:00",439.79422679999999,-24.744381600000001]
["2025-03-14T04:00:00","2025-03-14T04:05:00",418.14900720000003,-23.2945764]
["2025-03-14T08:25:00","2025-03-14T08:30:00",496.15458360000002,58.714856400000002]
["2025-03-14T12:40:00","2025-03-14T12:45:00",425.23777319999999,95.419714799999994]
["2025-03-14T16:55:00","2025-03-14T17:00:00",641.78315520000001,80.713736400000002]
["2025-03-14T20:30:00","2025-03-14T20:35:00",585.37793520000002,25.7196684]
["2025-03-15T01:35:00","2025-03-15T01:40:00",419.96096399999999,-22.7358072]
["2025-03-15T05:55:00","2025-03-15T06:00:00",451.36047359999998,-11.3533524]
["2025-03-15T10:10:00","2025-03-15T10:15:00",437.95395600000001,55.704160799999997]
["2025-03-15T11:15:00","2025-03-15T11:20:00",542.39939760000004,74.108924400000006]
["2025-03-15T18:50:00","2025-03-15T18:55:00",782.30222879999997,117.126648]
["2025-03-15T23:05:00","2025-03-15T23:10:00",563.05974600000002,14.4174528]
["2025-03-15T23:20:00","2025-03-15T23:25:00",553.55046719999996,11.361044400000001]
["2025-03-16T07:45:00","2025-03-16T07:50:00",491.86264560000001,-8.497992]
["2025-03-16T12:00:00","2025-03-16T12:05:00",506.35658519999998,-0.29332799999999998]
["2025-03-16T15:25:00","2025-03-16T15:30:00",484.80276839999999,-18.891468]
["2025-03-16T20:40:00","2025-03-16T20:45:00",485.85827879999999,-35.585798400000002]
["2025-03-17T00:55:00","2025-03-17T01:00:00",385.56774239999999,-52.9596588]
["2025-03-17T03:30:00","2025-03-17T03:35:00",383.4111504,-52.098705600000002]
["2025-03-17T05:20:00","2025-03-17T05:25:00",481.33803,-16.62039]
["2025-03-17T09:40:00","2025-03-17T09:45:00",522.90634680000005,43.266162000000001]
["2025-03-17T15:35:00","2025-03-17T15:40:00",385.94296320000001,27.087733199999999]
["2025-03-17T18:15:00","2025-03-17T18:20:00",573.71691239999996,15.412433999999999]
["2025-03-17T22:35:00","2025-03-17T22:40:00",441.88284119999997,-32.003403599999999]
["2025-03-18T03:40:00","2025-03-18T03:45:00",394.21014480000002,-42.879188399999997]
["2025-03-18T07:00:00","2025-03-18T07:05:00",571.61373479999997,35.492414400000001]
["2025-03-18T07:05:00","2025-03-18T07:10:00",569.7411816,36.066383999999999]
["2025-03-18T07:10:00","2025-03-18T07:15:00",564.69262920000006,35.170816799999997]
["2025-03-18T07:15:00","2025-03-18T07:20:00",558.34632120000003,36.077976]
["2025-03-18T07:20:00","2025-03-18T07:25:00",552.92030639999996,38.826290399999998]
["2025-03-18T07:25:00","2025-03-18T07:30:00",542.87205359999996,38.7755844]
["2025-03-18T07:30:00","2025-03-18T07:35:00",536.84074559999999,39.440755199999998]
["2025-03-18T07:35:00","2025-03-18T07:40:00",527.9430744,39.399540000000002]
["2025-03-18T07:40:00","2025-03-18T07:45:00",522.43528920000006,39.756080400000002]
["2025-03-18T07:45:00","2025-03-18T07:50:00",517.17976680000004,40.578364800000003]
["2025-03-18T07:50:00","2025-03-18T07:55:00",511.43346839999998,40.908568799999998]
["2025-03-18T07:55:00","2025-03-18T08:00:00",505.15713240000002,41.108946000000003]
["2025-03-18T08:00:00","2025-03-18T08:05:00",502.28387400000003,41.732236800000003]
["2025-03-18T08:05:00","2025-03-18T08:10:00",498.10476720000003,43.101649199999997]
["2025-03-18T08:10:00","2025-03-18T08:15:00",488.6250048,43.150132800000002]
["2025-03-18T08:15:00","2025-03-18T08:20:00",484.49540400000001,43.822298400000001]
["2025-03-18T08:20:00","2025-03-18T08:25:00",478.1686224,43.211482799999999]
["2025-03-18T08:25:00","2025-03-18T08:30:00",472.53830040000003,43.807779600000003]
["2025-03-18T08:30:00","2025-03-18T08:35:00",462.7872792,38.520673199999997]
["2025-03-18T08:35:00","2025-03-18T08:40:00",458.83034400000003,38.5420728]
["2025-03-18T08:40:00","2025-03-18T08:45:00",452.64894479999998,40.628365199999998]
["2025-03-18T08:45:00","2025-03-18T08:50:00",448.39176959999998,42.051753599999998]
["2025-03-18T08:50:00","2025-03-18T08:55:00",438.53084519999999,41.4204984]
["2025-03-18T08:55:00","2025-03-18T09:00:00",434.314188,42.825221999999997]
["2025-03-18T09:00:00","2025-03-18T09:05:00",426.59542920000001,40.401494399999997]
["2025-03-18T09:05:00","2025-03-18T09:10:00",418.30873200000002,37.915672800000003]
["2025-03-18T09:10:00","2025-03-18T09:15:00",410.72610120000002,39.881065200000002]
["2025-03-18T09:15:00","2025-03-18T09:20:00",405.27119040000002,41.481569999999998]
["2025-03-18T09:20:00","2025-03-18T09:25:00",400.22558279999998,39.3229884]
["2025-03-18T09:25:00","2025-03-18T09:30:00",394.7723388,40.0300656]
["2025-03-18T09:30:00","2025-03-18T09:35:00",385.96176600000001,42.304486799999999]
["2025-03-18T09:35:00","2025-03-18T09:40:00",386.10929160000001,43.954849199999998]
["2025-03-18T09:40:00","2025-03-18T09:45:00",378.33686760000001,45.088355999999997]
["2025-03-18T09:45:00","2025-03-18T09:50:00",374.83674120000001,47.269923599999998]
["2025-03-18T09:50:00","2025-03-18T09:55:00",371.94912599999998,48.050727600000002]
["2025-03-18T09:55:00","2025-03-18T10:00:00",366.6333156,46.901090400000001]
["2025-03-18T10:00:00","2025-03-18T10:05:00",363.16896359999998,48.167999999999999]
["2025-03-18T10:05:00","2025-03-18T10:10:00",359.98323360000001,48.084301199999999]
["2025-03-18T10:10:00","2025-03-18T10:15:00",349.91891759999999,47.885050800000002]
["2025-03-18T10:15:00","2025-03-18T10:20:00",347.11080959999998,48.834418800000002]
["2025-03-18T10:20:00","2025-03-18T10:25:00",346.20785760000001,51.051152399999999]
["2025-03-18T10:25:00","2025-03-18T10:30:00",341.8485996,52.182430799999999]
["2025-03-18T10:30:00","2025-03-18T10:35:00",339.25660679999999,52.539524399999998]
["2025-03-18T10:35:00","2025-03-18T10:40:00",338.86642920000003,52.594814399999997]
["2025-03-18T10:40:00","2025-03-18T10:45:00",334.10237999999998,53.245569600000003]
["2025-03-18T10:45:00","2025-03-18T10:50:00",327.43497120000001,52.428911999999997]
["2025-03-18T10:50:00","2025-03-18T10:55:00",320.0141064,49.725704399999998]
["2025-03-18T10:55:00","2025-03-18T11:00:00",322.60083120000002,52.723730400000001]
["2025-03-18T11:00:00","2025-03-18T11:05:00",317.14462079999998,53.944468800000003]
["2025-03-18T11:05:00","2025-03-18T11:10:00",319.46590320000001,56.119146000000001]
["2025-03-18T11:10:00","2025-03-18T11:15:00",315.24790200000001,55.4054328]
["2025-03-18T11:15:00","2025-03-18T11:20:00",315.98014080000002,56.716768799999997]
["2025-03-18T11:20:00","2025-03-18T11:25:00",314.08566000000002,57.215227200000001]
["2025-03-18T11:25:00","2025-03-18T11:30:00",305.5952628,54.944256000000003]
["2025-03-18T11:30:00","2025-03-18T11:35:00",304.58571480000001,54.919287599999997]
["2025-03-18T11:35:00","2025-03-18T11:40:00",307.34064599999999,56.948587199999999]
["2025-03-18T11:40:00","2025-03-18T11:45:00",307.5721704,57.142313999999999]
["2025-03-18T11:45:00","2025-03-18T11:50:00",302.72180759999998,58.377481199999998]
["2025-03-18T11:50:00","2025-03-18T11:55:00",303.36133319999999,60.638067599999999]
["2025-03-18T11:55:00","2025-03-18T12:00:00",304.17750599999999,60.986198399999999]
["2025-03-18T12:00:00","2025-03-18T12:05:00",305.8520244,62.606566800000003]
["2025-03-18T12:05:00","2025-03-18T12:10:00",306.75817799999999,62.918010000000002]
["2025-03-18T12:10:00","2025-03-18T12:15:00",302.84172000000001,62.7358908]
["2025-03-18T12:15:00","2025-03-18T12:20:00",305.61237240000003,62.886433199999999]
["2025-03-18T12:20:00","2025-03-18T12:25:00",306.13786199999998,63.779274000000001]
["2025-03-18T12:25:00","2025-03-18T12:30:00",306.76364039999999,63.796460400000001]
["2025-03-18T12:30:00","2025-03-18T12:35:00",306.40751280000001,64.933957199999995]
["2025-03-18T12:35:00","2025-03-18T12:40:00",309.61284119999999,65.079068399999997]
["2025-03-18T12:40:00","2025-03-18T12:45:00",311.38123680000001,66.722567999999995]
["2025-03-18T12:45:00","2025-03-18T12:50:00",303.65566680000001,65.345153999999994]
["2025-03-18T12:50:00","2025-03-18T12:55:00",300.34183560000002,64.5757452]
["2025-03-18T12:55:00","2025-03-18T13:00:00",303.61685640000002,63.8472048]
["2025-03-18T13:00:00","2025-03-18T13:05:00",304.73581680000001,63.324683999999998]
["2025-03-18T13:05:00","2025-03-18T13:10:00",307.30668480000003,64.0858968]
["2025-03-18T13:10:00","2025-03-18T13:15:00",297.41939760000002,64.628227199999998]
["2025-03-18T13:15:00","2025-03-18T13:20:00",301.20060119999999,65.174277599999996]
["2025-03-18T13:20:00","2025-03-18T13:25:00",309.49924800000002,66.136820400000005]
["2025-03-18T13:25:00","2025-03-18T13:30:00",316.77665159999998,67.725823199999994]
["2025-03-18T13:30:00","2025-03-18T13:35:00",318.00594960000001,67.470937199999995]
["2025-03-18T13:35:00","2025-03-18T13:40:00",323.21418119999998,68.655805200000003]
["2025-03-18T13:40:00","2025-03-18T13:45:00",323.4875892,71.227156800000003]
["2025-03-18T13:45:00","2025-03-18T13:50:00",323.806848,71.233198799999997]
["2025-03-18T13:50:00","2025-03-18T13:55:00",327.03827999999999,70.963303199999999]
["2025-03-18T13:55:00","2025-03-18T14:00:00",328.1960436,70.814228400000005]
["2025-03-18T14:00:00","2025-03-18T14:05:00",328.42119120000001,70.467830399999997]
["2025-03-18T14:05:00","2025-03-18T14:10:00",329.09626079999998,66.705777600000005]
["2025-03-18T14:10:00","2025-03-18T14:15:00",330.09245759999999,65.559933599999994]
["2025-03-18T14:15:00","2025-03-18T14:20:00",335.59535519999997,67.265492399999999]
["2025-03-18T14:20:00","2025-03-18T14:25:00",342.0988572,68.895644399999995]
["2025-03-18T14:25:00","2025-03-18T14:30:00",344.58746760000002,67.204515599999993]
["2025-03-18T14:30:00","2025-03-18T14:35:00",345.86089679999998,66.328177199999999]
["2025-03-18T14:35:00","2025-03-18T14:40:00",351.98203799999999,65.732265600000005]
["2025-03-18T14:40:00","2025-03-18T14:45:00",355.3567764,65.034912000000006]
["2025-03-18T14:45:00","2025-03-18T14:50:00",362.7323136,64.9690236]
["2025-03-18T14:50:00","2025-03-18T14:55:00",365.60022720000001,63.162821999999998]
["2025-03-18T14:55:00","2025-03-18T15:00:00",371.94940680000002,62.617432800000003]
["2025-03-18T15:00:00","2025-03-18T15:05:00",378.13656839999999,60.909428400000003]
["2025-03-18T15:05:00","2025-03-18T15:10:00",382.89819,59.203482000000001]
["2025-03-18T15:10:00","2025-03-18T15:15:00",386.08003200000002,56.222034000000001]
["2025-03-18T15:15:00","2025-03-18T15:20:00",392.77041000000003,55.076622]
["2025-03-18T15:20:00","2025-03-18T15:25:00",395.95346039999998,53.416338000000003]
["2025-03-18T15:25:00","2025-03-18T15:30:00",402.94140479999999,52.1063592]
["2025-03-18T15:30:00","2025-03-18T15:35:00",404.81941080000001,50.349456000000004]
["2025-03-18T15:35:00","2025-03-18T15:40:00",415.33840199999997,53.142426]
["2025-03-18T15:40:00","2025-03-18T15:45:00",423.88265639999997,55.617957599999997]
["2025-03-18T15:45:00","2025-03-18T15:50:00",429.29586599999999,54.478558800000002]
["2025-03-18T15:50:00","2025-03-18T15:55:00",433.35165480000001,51.0954312]
["2025-03-18T15:55:00","2025-03-18T16:00:00",440.37549239999998,46.802487599999999]
["2025-03-18T16:00:00","2025-03-18T16:05:00",446.9711064,46.443016800000002]
["2025-03-18T16:05:00","2025-03-18T16:10:00",452.96193,50.588549999999998]
["2025-03-18T16:10:00","2025-03-18T16:15:00",459.86148960000003,48.115422000000002]
["2025-03-18T16:15:00","2025-03-18T16:20:00",473.33574479999999,48.963616799999997]
["2025-03-18T16:20:00","2025-03-18T16:25:00",474.31586520000002,48.3722292]
["2025-03-18T16:25:00","2025-03-18T16:30:00",481.38317640000002,46.969548000000003]
["2025-03-18T16:30:00","2025-03-18T16:35:00",487.28317079999999,45.905558399999997]
["2025-03-18T16:35:00","2025-03-18T16:40:00",492.76142399999998,43.746181200000002]
["2025-03-18T16:40:00","2025-03-18T16:45:00",502.17668759999998,42.182172000000001]
["2025-03-18T16:45:00","2025-03-18T16:50:00",509.8527732,40.662269999999999]
["2025-03-18T16:50:00","2025-03-18T16:55:00",515.43073560000005,40.722501600000001]
["2025-03-18T16:55:00","2025-03-18T17:00:00",523.1186232,40.429102800000003]
["2025-03-18T17:00:00","2025-03-18T17:05:00",527.16872760000001,38.755580399999999]
["2025-03-18T17:05:00","2025-03-18T17:10:00",533.07898320000004,37.640468400000003]
["2025-03-18T17:10:00","2025-03-18T17:15:00",539.03693039999996,36.4553352]
["2025-03-18T17:15:00","2025-03-18T17:20:00",548.78178600000001,36.309331200000003]
["2025-03-18T17:20:00","2025-03-18T17:25:00",554.56598399999996,34.499326799999999]
["2025-03-18T17:25:00","2025-03-18T17:30:00",562.5197316,34.728852000000003]
["2025-03-18T17:30:00","2025-03-18T17:35:00",570.97524720000001,36.7775508]
["2025-03-18T17:35:00","2025-03-18T17:40:00",577.95260640000004,36.921698399999997]
["2025-03-18T17:40:00","2025-03-18T17:45:00",584.1033936,35.5440732]
["2025-03-18T17:45:00","2025-03-18T17:50:00",584.81704079999997,33.017274]
["2025-03-18T17:50:00","2025-03-18T17:55:00",586.66047719999995,31.959371999999998]
["2025-03-18T17:55:00","2025-03-18T18:00:00",593.40246239999999,32.249842800000003]
["2025-03-18T18:00:00","2025-03-18T18:05:00",592.00179479999997,29.043801599999998]
["2025-03-18T18:05:00","2025-03-18T18:10:00",590.92625759999999,26.784187200000002]
["2025-03-18T18:10:00","2025-03-18T18:15:00",593.10336119999999,28.210891199999999]
["2025-03-18T18:15:00","2025-03-18T18:20:00",597.29539439999996,27.707251200000002]
["2025-03-18T18:20:00","2025-03-18T18:25:00",597.33600839999997,25.683546]
["2025-03-18T18:25:00","2025-03-18T18:30:00",597.43204800000001,25.5904764]
["2025-03-18T18:30:00","2025-03-18T18:35:00",595.04566079999995,24.168619199999998]
["2025-03-18T18:35:00","2025-03-18T18:40:00",589.23592440000004,20.438439599999999]
["2025-03-18T18:40:00","2025-03-18T18:45:00",587.15767559999995,18.9871704]
["2025-03-18T18:45:00","2025-03-18T18:50:00",581.91797039999994,16.567432799999999]
["2025-03-18T18:50:00","2025-03-18T18:55:00",582.29384640000001,17.020981200000001]
["2025-03-18T18:55:00","2025-03-18T19:00:00",587.7242076,18.923829600000001]
["2025-03-18T19:00:00","2025-03-18T19:05:00",587.64849479999998,18.7186092]
["2025-03-18T19:05:00","2025-03-18T19:10:00",592.33404480000002,19.194361199999999]
["2025-03-18T19:10:00","2025-03-18T19:15:00",591.57324960000005,18.193399200000002]
["2025-03-18T19:15:00","2025-03-18T19:20:00",586.24285080000004,15.7159452]
["2025-03-18T19:20:00","2025-03-18T19:25:00",586.16908679999995,15.4299336]
["2025-03-18T19:25:00","2025-03-18T19:30:00",587.68196760000001,15.8218224]
["2025-03-18T19:30:00","2025-03-18T19:35:00",582.78746160000003,13.7757684]
["2025-03-18T19:35:00","2025-03-18T19:40:00",581.30447040000001,13.3836732]
["2025-03-18T19:40:00","2025-03-18T19:45:00",580.85125319999997,12.737948400000001]
["2025-03-18T19:45:00","2025-03-18T19:50:00",574.47204959999999,10.5566964]
["2025-03-18T19:50:00","2025-03-18T19:55:00",571.550208,10.2329688]
["2025-03-18T19:55:00","2025-03-18T20:00:00",566.59831320000001,8.4659700000000004]
["2025-03-18T20:00:00","2025-03-18T20:05:00",562.74299040000005,5.9948892000000003]
["2025-03-18T20:05:00","2025-03-18T20:10:00",559.12637280000001,3.9495756000000002]
["2025-03-18T20:10:00","2025-03-18T20:15:00",557.07813599999997,3.4045356]
["2025-03-18T20:15:00","2025-03-18T20:20:00",552.54461160000005,2.1342876]
["2025-03-18T20:20:00","2025-03-18T20:25:00",547.34118120000005,0.80116080000000001]
["2025-03-18T20:25:00","2025-03-18T20:30:00",548.07115199999998,1.3453128000000001]
["2025-03-18T20:30:00","2025-03-18T20:35:00",543.2085816,-0.49981439999999999]
["2025-03-18T20:35:00","2025-03-18T20:40:00",538.75324079999996,-1.4264508]
["2025-03-18T20:40:00","2025-03-18T20:45:00",535.48103279999998,-3.1555848000000002]
["2025-03-18T20:45:00","2025-03-18T20:50:00",532.59317759999999,-4.1392692000000002]
["2025-03-18T20:50:00","2025-03-18T20:55:00",527.54294640000001,-5.1302795999999997]
["2025-03-18T20:55:00","2025-03-18T21:00:00",524.75272199999995,-6.1978092]
["2025-03-18T21:00:00","2025-03-18T21:05:00",518.25232559999995,-7.4677008000000002]
["2025-03-18T21:05:00","2025-03-18T21:10:00",514.76024640000003,-8.5329192000000003]
["2025-03-18T21:10:00","2025-03-18T21:15:00",511.68007799999998,-9.6370824000000006]
["2025-03-18T21:15:00","2025-03-18T21:20:00",508.3788672,-9.6525011999999997]
["2025-03-18T21:20:00","2025-03-18T21:25:00",503.1626076,-10.513543200000001]
["2025-03-18T21:25:00","2025-03-18T21:30:00",498.77290799999997,-12.276195599999999]
["2025-03-18T21:30:00","2025-03-18T21:35:00",496.61773920000002,-12.3601008]
["2025-03-18T21:35:00","2025-03-18T21:40:00",492.320832,-13.0218624]
["2025-03-18T21:40:00","2025-03-18T21:45:00",488.6429976,-14.281362]
["2025-03-18T21:45:00","2025-03-18T21:50:00",483.36896280000002,-16.7811576]
["2025-03-18T21:50:00","2025-03-18T21:55:00",476.6472612,-19.1345028]
["2025-03-18T21:55:00","2025-03-18T22:00:00",470.325648,-20.3862384]
["2025-03-18T22:00:00","2025-03-18T22:05:00",471.87338399999999,-19.241601599999999]
["2025-03-18T22:05:00","2025-03-18T22:10:00",470.08136760000002,-19.253973599999998]
["2025-03-18T22:10:00","2025-03-18T22:15:00",468.30620279999999,-19.8710244]
["2025-03-18T22:15:00","2025-03-18T22:20:00",465.58029479999999,-20.223295199999999]
["2025-03-18T22:20:00","2025-03-18T22:25:00",460.23071279999999,-21.990212400000001]
["2025-03-18T22:25:00","2025-03-18T22:30:00",457.51987680000002,-23.1553404]
["2025-03-18T22:30:00","2025-03-18T22:35:00",452.70632280000001,-24.229772400000002]
["2025-03-18T22:35:00","2025-03-18T22:40:00",450.7047096,-24.671805599999999]
["2025-03-18T22:40:00","2025-03-18T22:45:00",449.18372640000001,-24.7334028]
["2025-03-18T22:45:00","2025-03-18T22:50:00",445.11960720000002,-25.363973999999999]
["2025-03-18T22:50:00","2025-03-18T22:55:00",441.57981119999999,-25.786301999999999]
["2025-03-18T22:55:00","2025-03-18T23:00:00",438.989034,-26.672348400000001]
["2025-03-18T23:00:00","2025-03-18T23:05:00",446.95511640000001,-26.006606399999999]
["2025-03-18T23:05:00","2025-03-18T23:10:00",458.38310639999997,-24.759445199999998]
["2025-03-18T23:10:00","2025-03-18T23:15:00",463.12326719999999,-23.662785599999999]
["2025-03-18T23:15:00","2025-03-18T23:20:00",457.85945520000001,-24.126196799999999]
["2025-03-18T23:20:00","2025-03-18T23:25:00",455.57085360000002,-24.864259199999999]
["2025-03-18T23:25:00","2025-03-18T23:30:00",452.44071000000002,-25.817646]
["2025-03-18T23:30:00","2025-03-18T23:35:00",444.8271408,-27.1528548]
["2025-03-18T23:35:00","2025-03-18T23:40:00",438.1875,-28.082798400000001]
["2025-03-18T23:40:00","2025-03-18T23:45:00",434.29678200000001,-29.527609200000001]
["2025-03-18T23:45:00","2025-03-18T23:50:00",429.29127119999998,-31.155718799999999]
["2025-03-18T23:50:00","2025-03-18T23:55:00",425.6857536,-31.813222799999998]
["2025-03-18T23:55:00",45735,424.14521880000001,-32.382657600000002]
[45735,"2025-03-19T00:05:00",427.11404279999999,-31.098849600000001]
["2025-03-19T00:05:00","2025-03-19T00:10:00",427.33831559999999,-31.153221599999998]
["2025-03-19T00:10:00","2025-03-19T00:15:00",426.7114176,-31.454541599999999]
["2025-03-19T00:15:00","2025-03-19T00:20:00",422.66062920000002,-31.610544000000001]
["2025-03-19T00:20:00","2025-03-19T00:25:00",420.00587760000002,-32.698468800000001]
["2025-03-19T00:25:00","2025-03-19T00:30:00",417.11125079999999,-32.9632164]
["2025-03-19T00:30:00","2025-03-19T00:35:00",415.99741080000001,-33.167488800000001]
["2025-03-19T00:35:00","2025-03-19T00:40:00",414.35993400000001,-33.263227200000003]
["2025-03-19T00:40:00","2025-03-19T00:45:00",412.68027599999999,-33.296240400000002]
["2025-03-19T00:45:00","2025-03-19T00:50:00",407.3785092,-34.6502616]
["2025-03-19T00:50:00","2025-03-19T00:55:00",406.57786320000002,-35.315588400000003]
["2025-03-19T00:55:00","2025-03-19T01:00:00",404.99576039999999,-35.276833199999999]
["2025-03-19T01:00:00","2025-03-19T01:05:00",400.97426639999998,-36.541999199999999]
["2025-03-19T01:05:00","2025-03-19T01:10:00",400.10398800000002,-37.762272000000003]
["2025-03-19T01:10:00","2025-03-19T01:15:00",399.94702080000002,-37.272146399999997]
["2025-03-19T01:15:00","2025-03-19T01:20:00",399.26790840000001,-37.697279999999999]
["2025-03-19T01:20:00","2025-03-19T01:25:00",398.44653,-36.819577199999998]
["2025-03-19T01:25:00","2025-03-19T01:30:00",396.81363479999999,-36.8776692]
["2025-03-19T01:30:00","2025-03-19T01:35:00",396.08645999999999,-37.512020399999997]
["2025-03-19T01:35:00","2025-03-19T01:40:00",394.63895760000003,-38.414590799999999]
["2025-03-19T01:40:00","2025-03-19T01:45:00",395.10467640000002,-38.830522799999997]
["2025-03-19T01:45:00","2025-03-19T01:50:00",394.17533639999999,-38.661361200000002]
["2025-03-19T01:50:00","2025-03-19T01:55:00",394.23010799999997,-38.874811200000003]
["2025-03-19T01:55:00","2025-03-19T02:00:00",394.95566760000003,-37.864787999999997]
["2025-03-19T02:00:00","2025-03-19T02:05:00",396.40733160000002,-36.906434400000002]
["2025-03-19T02:05:00","2025-03-19T02:10:00",396.28904640000002,-37.334311200000002]
["2025-03-19T02:10:00","2025-03-19T02:15:00",395.7787596,-37.032380400000001]
["2025-03-19T02:15:00","2025-03-19T02:20:00",394.50465480000003,-37.703118000000003]
["2025-03-19T02:20:00","2025-03-19T02:25:00",394.07154120000001,-37.481281199999998]
["2025-03-19T02:25:00","2025-03-19T02:30:00",392.55189840000003,-38.5831272]
["2025-03-19T02:30:00","2025-03-19T02:35:00",393.10489200000001,-38.312483999999998]
["2025-03-19T02:35:00","2025-03-19T02:40:00",394.0888764,-38.150050800000002]
["2025-03-19T02:40:00","2025-03-19T02:45:00",393.5591976,-38.465532000000003]
["2025-03-19T02:45:00","2025-03-19T02:50:00",394.24709760000002,-38.250413999999999]
["2025-03-19T02:50:00","2025-03-19T02:55:00",394.31165520000002,-38.454210000000003]
["2025-03-19T02:55:00","2025-03-19T03:00:00",393.67880639999998,-38.601170400000001]
["2025-03-19T03:00:00","2025-03-19T03:05:00",393.58148999999997,-38.223073200000002]
["2025-03-19T03:05:00","2025-03-19T03:10:00",396.67512240000002,-38.5816248]
["2025-03-19T03:10:00","2025-03-19T03:15:00",397.87972680000001,-38.363418000000003]
["2025-03-19T03:15:00","2025-03-19T03:20:00",398.7152064,-37.644936000000001]
["2025-03-19T03:20:00","2025-03-19T03:25:00",396.24448560000002,-38.827433999999997]
["2025-03-19T03:25:00","2025-03-19T03:30:00",397.96737239999999,-37.860472799999997]
["2025-03-19T03:30:00","2025-03-19T03:35:00",398.65969200000001,-37.525359600000002]
["2025-03-19T03:35:00","2025-03-19T03:40:00",400.68056639999998,-37.093887600000002]
["2025-03-19T03:40:00","2025-03-19T03:45:00",401.91940679999999,-36.819962400000001]
["2025-03-19T03:45:00","2025-03-19T03:50:00",405.86862000000002,-36.284377200000002]
["2025-03-19T03:50:00","2025-03-19T03:55:00",406.41676560000002,-36.056535599999997]
["2025-03-19T03:55:00","2025-03-19T04:00:00",410.5304112,-34.673983200000002]
["2025-03-19T04:00:00","2025-03-19T04:05:00",417.61402199999998,-32.731142400000003]
["2025-03-19T04:05:00","2025-03-19T04:10:00",420.68764800000002,-31.692085200000001]
["2025-03-19T04:10:00","2025-03-19T04:15:00",425.81343959999998,-30.632671200000001]
["2025-03-19T04:15:00","2025-03-19T04:20:00",427.34403359999999,-30.994620000000001]
["2025-03-19T04:20:00","2025-03-19T04:25:00",429.08311079999999,-31.531615200000001]
["2025-03-19T04:25:00","2025-03-19T04:30:00",429.64051560000001,-31.311710399999999]
["2025-03-19T04:30:00","2025-03-19T04:35:00",432.21610440000001,-29.885477999999999]
["2025-03-19T04:35:00","2025-03-19T04:40:00",433.598478,-29.969464800000001]
["2025-03-19T04:40:00","2025-03-19T04:45:00",439.05618720000001,-27.267808800000001]
["2025-03-19T04:45:00","2025-03-19T04:50:00",439.97610479999997,-26.895866399999999]
["2025-03-19T04:50:00","2025-03-19T04:55:00",445.26388200000002,-25.320366]
["2025-03-19T04:55:00","2025-03-19T05:00:00",449.62342080000002,-23.640100799999999]
["2025-03-19T05:00:00","2025-03-19T05:05:00",461.5947516,-19.190349600000001]
["2025-03-19T05:05:00","2025-03-19T05:10:00",467.94911999999999,-16.371267599999999]
["2025-03-19T05:10:00","2025-03-19T05:15:00",472.95468840000001,-14.351941200000001]
["2025-03-19T05:15:00","2025-03-19T05:20:00",479.47108200000002,-12.394910400000001]
["2025-03-19T05:20:00","2025-03-19T05:25:00",486.36180359999997,-8.8132103999999991]
["2025-03-19T05:25:00","2025-03-19T05:30:00",491.26660559999999,-7.7613671999999996]
["2025-03-19T05:30:00","2025-03-19T05:35:00",499.2072336,-4.4254655999999999]
["2025-03-19T05:35:00","2025-03-19T05:40:00",506.17395599999998,-2.2450931999999999]
["2025-03-19T05:40:00","2025-03-19T05:45:00",509.36836679999999,-0.35705160000000002]
["2025-03-19T05:45:00","2025-03-19T05:50:00",519.11442360000001,2.3905332000000001]
["2025-03-19T05:50:00","2025-03-19T05:55:00",532.18266840000001,10.22226]
["2025-03-19T05:55:00","2025-03-19T06:00:00",541.85271239999997,12.937256400000001]
["2025-03-19T06:00:00","2025-03-19T06:05:00",548.05962,16.799250000000001]
["2025-03-19T06:05:00","2025-03-19T06:10:00",554.78255999999999,18.958818000000001]
["2025-03-19T06:10:00","2025-03-19T06:15:00",558.28368479999995,19.470565199999999]
["2025-03-19T06:15:00","2025-03-19T06:20:00",563.08146720000002,21.2479704]
["2025-03-19T06:20:00","2025-03-19T06:25:00",566.43841440000006,22.875668399999999]
["2025-03-19T06:25:00","2025-03-19T06:30:00",568.19018879999999,25.391366399999999]
["2025-03-19T06:30:00","2025-03-19T06:35:00",574.75523399999997,27.958582799999999]
["2025-03-19T06:35:00","2025-03-19T06:40:00",578.02535999999998,30.576052799999999]
["2025-03-19T06:40:00","2025-03-19T06:45:00",578.36052240000004,31.049977200000001]
["2025-03-19T06:45:00","2025-03-19T06:50:00",579.19008719999999,32.839154399999998]
["2025-03-19T06:50:00","2025-03-19T06:55:00",575.8088616,32.901780000000002]
["2025-03-19T06:55:00","2025-03-19T07:00:00",573.57534599999997,33.710863199999999]
["2025-03-19T07:00:00","2025-03-19T07:05:00",567.20140200000003,34.8397656]
["2025-03-19T07:05:00","2025-03-19T07:10:00",561.0079356,36.060414000000002]
["2025-03-19T07:10:00","2025-03-19T07:15:00",553.01126160000001,34.491522000000003]
["2025-03-19T07:15:00","2025-03-19T07:20:00",547.58077200000002,37.1683716]
["2025-03-19T07:20:00","2025-03-19T07:25:00",542.113068,39.284347199999999]
["2025-03-19T07:25:00","2025-03-19T07:30:00",535.823982,40.838377199999996]
["2025-03-19T07:30:00","2025-03-19T07:35:00",530.2748484,42.188812800000001]
["2025-03-19T07:35:00","2025-03-19T07:40:00",525.75825840000005,42.7099908]
["2025-03-19T07:40:00","2025-03-19T07:45:00",515.15041919999999,42.8190144]
["2025-03-19T07:45:00","2025-03-19T07:50:00",510.28083839999999,44.548401599999998]
["2025-03-19T07:50:00","2025-03-19T07:55:00",505.71643440000003,40.175030399999997]
["2025-03-19T07:55:00","2025-03-19T08:00:00",499.98931440000001,39.744302400000002]
["2025-03-19T08:00:00","2025-03-19T08:05:00",498.95238840000002,40.486059599999997]
["2025-03-19T08:05:00","2025-03-19T08:10:00",494.34130920000001,40.977148800000002]
["2025-03-19T08:10:00","2025-03-19T08:15:00",486.6764976,42.579967199999999]
["2025-03-19T08:15:00","2025-03-19T08:20:00",481.72971840000002,45.263322000000002]
["2025-03-19T08:20:00","2025-03-19T08:25:00",479.67154679999999,46.218493199999998]
["2025-03-19T08:25:00","2025-03-19T08:30:00",474.93194879999999,46.502486400000002]
["2025-03-19T08:30:00","2025-03-19T08:35:00",466.79186879999997,46.230950399999998]
["2025-03-19T08:35:00","2025-03-19T08:40:00",461.7983868,46.723059599999999]
["2025-03-19T08:40:00","2025-03-19T08:45:00",457.10024399999998,46.147432799999997]
["2025-03-19T08:45:00","2025-03-19T08:50:00",450.37703520000002,46.037746800000001]
["2025-03-19T08:50:00","2025-03-19T08:55:00",445.11024839999999,46.562144400000001]
["2025-03-19T08:55:00","2025-03-19T09:00:00",440.44775399999997,47.958838800000002]
["2025-03-19T09:00:00","2025-03-19T09:05:00",436.61481240000001,48.1751364]
["2025-03-19T09:05:00","2025-03-19T09:10:00",429.91345319999999,46.623656400000002]
["2025-03-19T09:10:00","2025-03-19T09:15:00",429.5245008,48.828108]
["2025-03-19T09:15:00","2025-03-19T09:20:00",426.39608759999999,50.101900800000003]
["2025-03-19T09:20:00","2025-03-19T09:25:00",422.20206359999997,50.311801199999998]
["2025-03-19T09:25:00","2025-03-19T09:30:00",413.88371640000003,48.074300399999998]
["2025-03-19T09:30:00","2025-03-19T09:35:00",407.94040439999998,48.112442399999999]
["2025-03-19T09:35:00","2025-03-19T09:40:00",412.8669792,50.270184]
["2025-03-19T09:40:00","2025-03-19T09:45:00",404.67220079999998,50.414204400000003]
["2025-03-19T09:45:00","2025-03-19T09:50:00",402.52680600000002,51.833950799999997]
["2025-03-19T09:50:00","2025-03-19T09:55:00",400.84902959999999,55.145965199999999]
["2025-03-19T09:55:00","2025-03-19T10:00:00",404.48012879999999,58.099486800000001]
["2025-03-19T10:00:00","2025-03-19T10:05:00",405.37320119999998,59.298837599999999]
["2025-03-19T10:05:00","2025-03-19T10:10:00",410.12356080000001,62.3045124]
["2025-03-19T10:10:00","2025-03-19T10:15:00",412.93689360000002,66.193610399999997]
["2025-03-19T10:15:00","2025-03-19T10:20:00",411.69886680000002,69.431886000000006]
["2025-03-19T10:20:00","2025-03-19T10:25:00",402.99089400000003,69.507195600000003]
["2025-03-19T10:25:00","2025-03-19T10:30:00",397.25438400000002,67.326457199999993]
["2025-03-19T10:30:00","2025-03-19T10:35:00",395.77620719999999,70.953548400000003]
["2025-03-19T10:35:00","2025-03-19T10:40:00",395.00860080000001,71.147623199999998]
["2025-03-19T10:40:00","2025-03-19T10:45:00",393.60051479999998,71.374372800000003]
["2025-03-19T10:45:00","2025-03-19T10:50:00",400.36381080000001,72.483853199999999]
["2025-03-19T10:50:00","2025-03-19T10:55:00",409.47969000000001,72.828464400000001]
["2025-03-19T10:55:00","2025-03-19T11:00:00",421.21389119999998,73.068117599999994]
["2025-03-19T11:00:00","2025-03-19T11:05:00",429.15865919999999,72.084274800000003]
["2025-03-19T11:05:00","2025-03-19T11:10:00",428.5339596,72.610438799999997]
["2025-03-19T11:10:00","2025-03-19T11:15:00",423.79352999999998,74.220005999999998]
["2025-03-19T11:15:00","2025-03-19T11:20:00",424.27846440000002,79.224804000000006]
["2025-03-19T11:20:00","2025-03-19T11:25:00",427.23206640000001,80.980399199999994]
["2025-03-19T11:25:00","2025-03-19T11:30:00",426.36783600000001,80.519267999999997]
["2025-03-19T11:30:00","2025-03-19T11:35:00",410.51972760000001,77.775064799999996]
["2025-03-19T11:35:00","2025-03-19T11:40:00",415.48134119999997,80.256336000000005]
["2025-03-19T11:40:00","2025-03-19T11:45:00",417.60609240000002,81.984861600000002]
["2025-03-19T11:45:00","2025-03-19T11:50:00",427.67559599999998,84.134620799999993]
["2025-03-19T11:50:00","2025-03-19T11:55:00",431.5537056,84.817303199999998]
["2025-03-19T11:55:00","2025-03-19T12:00:00",429.9947196,83.9200692]
["2025-03-19T12:00:00","2025-03-19T12:05:00",428.42812800000002,86.448340799999997]
["2025-03-19T12:05:00","2025-03-19T12:10:00",427.34022599999997,91.907309999999995]
["2025-03-19T12:10:00","2025-03-19T12:15:00",418.10802719999998,95.346075600000006]
["2025-03-19T12:15:00","2025-03-19T12:20:00",409.91730239999998,97.558861199999996]
["2025-03-19T12:20:00","2025-03-19T12:25:00",408.14759759999998,98.734914000000003]
["2025-03-19T12:25:00","2025-03-19T12:30:00",404.57814839999998,102.1653264]
["2025-03-19T12:30:00","2025-03-19T12:35:00",411.06825120000002,102.5179596]
["2025-03-19T12:35:00","2025-03-19T12:40:00",415.23465959999999,102.6263292]
["2025-03-19T12:40:00","2025-03-19T12:45:00",418.05004559999998,102.66435]
["2025-03-19T12:45:00","2025-03-19T12:50:00",418.27317840000001,105.03386759999999]
["2025-03-19T12:50:00","2025-03-19T12:55:00",420.38770920000002,104.7702036]
["2025-03-19T12:55:00","2025-03-19T13:00:00",424.74989640000001,105.8578512]
["2025-03-19T13:00:00","2025-03-19T13:05:00",433.18909200000002,105.1185672]
["2025-03-19T13:05:00","2025-03-19T13:10:00",439.48183799999998,105.39294599999999]
["2025-03-19T13:10:00","2025-03-19T13:15:00",443.20808520000003,105.157704]
["2025-03-19T13:15:00","2025-03-19T13:20:00",454.84341000000001,110.4125604]
["2025-03-19T13:20:00","2025-03-19T13:25:00",471.02936640000001,113.5247232]
["2025-03-19T13:25:00","2025-03-19T13:30:00",480.54973200000001,112.1124696]
["2025-03-19T13:30:00","2025-03-19T13:35:00",484.22252040000001,111.5108268]
["2025-03-19T13:35:00","2025-03-19T13:40:00",495.43183440000001,110.06892240000001]
["2025-03-19T13:40:00","2025-03-19T13:45:00",498.12837960000002,111.1238676]
["2025-03-19T13:45:00","2025-03-19T13:50:00",504.15204840000001,110.1250404]
["2025-03-19T13:50:00","2025-03-19T13:55:00",495.09294840000001,105.27471]
["2025-03-19T13:55:00","2025-03-19T14:00:00",495.75632400000001,101.6092956]
["2025-03-19T14:00:00","2025-03-19T14:05:00",514.13918639999997,97.501260000000002]
["2025-03-19T14:05:00","2025-03-19T14:10:00",531.78525960000002,97.946037599999997]
["2025-03-19T14:10:00","2025-03-19T14:15:00",541.64144520000002,97.027435199999999]
["2025-03-19T14:15:00","2025-03-19T14:20:00",546.00419399999998,96.343655999999996]
["2025-03-19T14:20:00","2025-03-19T14:25:00",556.96977000000004,95.121220800000003]
["2025-03-19T14:25:00","2025-03-19T14:30:00",565.73873519999995,96.673100399999996]
["2025-03-19T14:30:00","2025-03-19T14:35:00",565.59738719999996,97.344439199999997]
["2025-03-19T14:35:00","2025-03-19T14:40:00",574.12679400000002,104.13193200000001]
["2025-03-19T14:40:00","2025-03-19T14:45:00",576.88558560000001,99.580250399999997]
["2025-03-19T14:45:00","2025-03-19T14:50:00",567.5008656,99.262678800000003]
["2025-03-19T14:50:00","2025-03-19T14:55:00",540.24755879999998,97.295071199999995]
["2025-03-19T14:55:00","2025-03-19T15:00:00",532.22996880000005,97.073587200000006]
["2025-03-19T15:00:00","2025-03-19T15:05:00",537.00065759999995,95.302710000000005]
["2025-03-19T15:05:00","2025-03-19T15:10:00",546.69203400000004,94.952491199999997]
["2025-03-19T15:10:00","2025-03-19T15:15:00",553.2473076,95.558040000000005]
["2025-03-19T15:15:00","2025-03-19T15:20:00",555.96048240000005,96.582056399999999]
["2025-03-19T15:20:00","2025-03-19T15:25:00",561.34892760000002,94.515752399999997]
["2025-03-19T15:25:00","2025-03-19T15:30:00",563.34261360000005,93.802384799999999]
["2025-03-19T15:30:00","2025-03-19T15:35:00",570.10784039999999,94.462590000000006]
["2025-03-19T15:35:00","2025-03-19T15:40:00",582.08953080000003,95.168177999999997]
["2025-03-19T15:40:00","2025-03-19T15:45:00",591.21808680000004,93.839137199999996]
["2025-03-19T15:45:00","2025-03-19T15:50:00",601.25344319999999,93.442322399999995]
["2025-03-19T15:50:00","2025-03-19T15:55:00",608.10693839999999,91.686823200000006]
["2025-03-19T15:55:00","2025-03-19T16:00:00",614.87863800000002,90.355196399999997]
["2025-03-19T16:00:00","2025-03-19T16:05:00",623.62003800000002,90.206758800000003]
["2025-03-19T16:05:00","2025-03-19T16:10:00",633.27130320000003,91.239982800000007]
["2025-03-19T16:10:00","2025-03-19T16:15:00",642.4005684,95.156384399999993]
["2025-03-19T16:15:00","2025-03-19T16:20:00",656.01356639999995,101.2642896]
["2025-03-19T16:20:00","2025-03-19T16:25:00",659.16650879999997,100.65216119999999]
["2025-03-19T16:25:00","2025-03-19T16:30:00",663.95854320000001,104.1477288]
["2025-03-19T16:30:00","2025-03-19T16:35:00",667.13419080000006,103.95823679999999]
["2025-03-19T16:35:00","2025-03-19T16:40:00",676.24393080000004,104.03598599999999]
["2025-03-19T16:40:00","2025-03-19T16:45:00",682.17141119999997,103.5179388]
["2025-03-19T16:45:00","2025-03-19T16:50:00",690.49819679999996,103.97270039999999]
["2025-03-19T16:50:00","2025-03-19T16:55:00",699.63673559999995,103.5432516]
["2025-03-19T16:55:00","2025-03-19T17:00:00",704.96493720000001,103.1216592]
["2025-03-19T17:00:00","2025-03-19T17:05:00",707.93274719999999,108.78132479999999]
["2025-03-19T17:05:00","2025-03-19T17:10:00",716.08829519999995,106.8880332]
["2025-03-19T17:10:00","2025-03-19T17:15:00",723.76026960000002,102.7316172]
["2025-03-19T17:15:00","2025-03-19T17:20:00",730.23653999999999,101.7179256]
["2025-03-19T17:20:00","2025-03-19T17:25:00",732.55319159999999,99.727603200000004]
["2025-03-19T17:25:00","2025-03-19T17:30:00",733.86603239999999,97.884683999999993]
["2025-03-19T17:30:00","2025-03-19T17:35:00",736.14981120000004,96.532364400000006]
["2025-03-19T17:35:00","2025-03-19T17:40:00",738.84397920000004,95.861632799999995]
["2025-03-19T17:40:00","2025-03-19T17:45:00",742.10219040000004,100.9855812]
["2025-03-19T17:45:00","2025-03-19T17:50:00",746.1604572,103.7798844]
["2025-03-19T17:50:00","2025-03-19T17:55:00",748.66193039999996,102.96664079999999]
["2025-03-19T17:55:00","2025-03-19T18:00:00",750.49697160000005,101.09972999999999]
["2025-03-19T18:00:00","2025-03-19T18:05:00",753.74416680000002,104.557626]
["2025-03-19T18:05:00","2025-03-19T18:10:00",754.66856640000003,109.8466524]
["2025-03-19T18:10:00","2025-03-19T18:15:00",750.78839040000003,108.3989064]
["2025-03-19T18:15:00","2025-03-19T18:20:00",748.32034680000004,105.21235799999999]
["2025-03-19T18:20:00","2025-03-19T18:25:00",748.92156120000004,104.95312920000001]
["2025-03-19T18:25:00","2025-03-19T18:30:00",745.38681120000001,103.7014332]
["2025-03-19T18:30:00","2025-03-19T18:35:00",741.66961079999999,104.6313912]
["2025-03-19T18:35:00","2025-03-19T18:40:00",736.90669200000002,103.5760956]
["2025-03-19T18:40:00","2025-03-19T18:45:00",732.46052280000004,102.29248680000001]
["2025-03-19T18:45:00","2025-03-19T18:50:00",726.77409720000003,99.038313599999995]
["2025-03-19T18:50:00","2025-03-19T18:55:00",724.62491880000005,99.117183600000004]
["2025-03-19T18:55:00","2025-03-19T19:00:00",723.10583880000001,99.134275200000005]
["2025-03-19T19:00:00","2025-03-19T19:05:00",720.23280480000005,96.451951199999996]
["2025-03-19T19:05:00","2025-03-19T19:10:00",713.12268119999999,92.020329599999997]
["2025-03-19T19:10:00","2025-03-19T19:15:00",701.82594959999994,90.011346000000003]
["2025-03-19T19:15:00","2025-03-19T19:20:00",702.21388560000003,84.294680400000004]
["2025-03-19T19:20:00","2025-03-19T19:25:00",699.92451600000004,79.424792400000001]
["2025-03-19T19:25:00","2025-03-19T19:30:00",694.00371240000004,73.327454399999993]
["2025-03-19T19:30:00","2025-03-19T19:35:00",689.6905908,72.177825600000006]
["2025-03-19T19:35:00","2025-03-19T19:40:00",687.55689840000002,72.492388800000001]
["2025-03-19T19:40:00","2025-03-19T19:45:00",684.42619679999996,71.797641600000006]
["2025-03-19T19:45:00","2025-03-19T19:50:00",678.97121400000003,69.1128456]
["2025-03-19T19:50:00","2025-03-19T19:55:00",671.14783680000005,67.054232400000004]
["2025-03-19T19:55:00","2025-03-19T20:00:00",665.06019839999999,64.539929999999998]
["2025-03-19T20:00:00","2025-03-19T20:05:00",661.33864559999995,64.258814400000006]
["2025-03-19T20:05:00","2025-03-19T20:10:00",654.74968679999995,63.384133200000001]
["2025-03-19T20:10:00","2025-03-19T20:15:00",650.6665236,62.697842399999999]
["2025-03-19T20:15:00","2025-03-19T20:20:00",639.10384439999996,57.359276399999999]
["2025-03-19T20:20:00","2025-03-19T20:25:00",629.86466759999996,49.828158000000002]
["2025-03-19T20:25:00","2025-03-19T20:30:00",627.3312684,48.830626799999997]
["2025-03-19T20:30:00","2025-03-19T20:35:00",621.22692359999996,48.102604800000002]
["2025-03-19T20:35:00","2025-03-19T20:40:00",617.32878119999998,47.6121804]
["2025-03-19T20:40:00","2025-03-19T20:45:00",610.96343520000005,46.4974968]
["2025-03-19T20:45:00","2025-03-19T20:50:00",603.99519720000001,44.121049200000002]
["2025-03-19T20:50:00","2025-03-19T20:55:00",597.5362824,43.482164400000002]
["2025-03-19T20:55:00","2025-03-19T21:00:00",592.94218320000004,42.277888799999999]
["2025-03-19T21:00:00","2025-03-19T21:05:00",584.27111160000004,40.786369200000003]
["2025-03-19T21:05:00","2025-03-19T21:10:00",577.80395639999995,39.958000800000001]
["2025-03-19T21:10:00","2025-03-19T21:15:00",570.76523520000001,37.826003999999998]
["2025-03-19T21:15:00","2025-03-19T21:20:00",566.54090159999998,37.9995288]
["2025-03-19T21:20:00","2025-03-19T21:25:00",559.40885639999999,34.637114400000002]
["2025-03-19T21:25:00","2025-03-19T21:30:00",553.33369919999996,31.606177200000001]
["2025-03-19T21:30:00","2025-03-19T21:35:00",547.58140319999995,26.497359599999999]
["2025-03-19T21:35:00","2025-03-19T21:40:00",548.08900080000001,19.675846799999999]
["2025-03-19T21:40:00","2025-03-19T21:45:00",544.17386039999997,10.9144296]
["2025-03-19T21:45:00","2025-03-19T21:50:00",539.88881760000004,9.9955739999999995]
["2025-03-19T21:50:00","2025-03-19T21:55:00",532.49395560000005,6.6924935999999997]
["2025-03-19T21:55:00","2025-03-19T22:00:00",528.48579480000001,4.2300312]
["2025-03-19T22:00:00","2025-03-19T22:05:00",522.32938320000005,2.4690132]
["2025-03-19T22:05:00","2025-03-19T22:10:00",517.30308839999998,1.1851908]
["2025-03-19T22:10:00","2025-03-19T22:15:00",513.83788319999996,0.30553079999999999]
["2025-03-19T22:15:00","2025-03-19T22:20:00",511.10776920000001,-0.4222128]
["2025-03-19T22:20:00","2025-03-19T22:25:00",507.3110532,-0.8441592]
["2025-03-19T22:25:00","2025-03-19T22:30:00",501.99668639999999,-2.8298952000000002]
["2025-03-19T22:30:00","2025-03-19T22:35:00",494.94922200000002,-4.5755423999999998]
["2025-03-19T22:35:00","2025-03-19T22:40:00",494.78521319999999,-4.4884176]
["2025-03-19T22:40:00","2025-03-19T22:45:00",491.35656840000001,-6.7516308]
["2025-03-19T22:45:00","2025-03-19T22:50:00",487.31972880000001,-7.5199128000000002]
["2025-03-19T22:50:00","2025-03-19T22:55:00",481.54955760000001,-8.8742339999999995]
["2025-03-19T22:55:00","2025-03-19T23:00:00",476.98246080000001,-10.402962]
["2025-03-19T23:00:00","2025-03-19T23:05:00",482.83723320000001,-9.5980103999999997]
["2025-03-19T23:05:00","2025-03-19T23:10:00",492.55311840000002,-9.9172872000000005]
["2025-03-19T23:10:00","2025-03-19T23:15:00",496.55162519999999,-8.7810252000000002]
["2025-03-19T23:15:00","2025-03-19T23:20:00",493.35563400000001,-8.8609679999999997]
["2025-03-19T23:20:00","2025-03-19T23:25:00",487.354716,-10.704758399999999]
["2025-03-19T23:25:00","2025-03-19T23:30:00",484.52438640000003,-10.1388804]
["2025-03-19T23:30:00","2025-03-19T23:35:00",478.552164,-11.594041199999999]
["2025-03-19T23:35:00","2025-03-19T23:40:00",475.99187760000001,-12.4697028]
["2025-03-19T23:40:00","2025-03-19T23:45:00",472.5743736,-12.886542]
["2025-03-19T23:45:00","2025-03-19T23:50:00",467.42399640000002,-13.438648799999999]
["2025-03-19T23:50:00","2025-03-19T23:55:00",463.2036708,-14.6062764]
["2025-03-19T23:55:00",45736,459.19291079999999,-16.667888399999999]
[]
["Minimum Demand Time for week 1/12/2024 to 7/12/2024"]
["Start date/time","End date/time","Minimum Demand"]
[{"$f":"A73848","v":"2024-12-01T09:45:00"},{"$f":"B73848","v":"2024-12-01T09:50:00"},{"$f":"MIN(C73731:C75746)","v":231.2294856}]
[]
["Maximum Demand Time for week 2/2/2025 to 8/2/2025"]
["Start date/time","End date/time","Maximum Demand"]
[{"$f":"A92380","v":"2025-02-03T18:05:00"},{"$f":"B92380","v":"2025-02-03T18:10:00"},{"$f":"MAX(C91875:C93890)","v":1075.351232}]

{"sheet":"EDCoP_1-12-2024_mD_High V","index":2,"n_rows":16409,"n_cols":15,"rows_kept":4500,"cut":true,"hidden":false,"merged":[],"bounds":{"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0}}
[null,null,"Substation","HV.Feeder","Start.Time","End.Time","Min.One.Percentage","Max.One.Percentage","One.Percentage.Interection","Min.Consecutive.Violation","Max.Consecutive.Violation","Consecutive.Violation.Intersection","ZS","Circuit","Max.One.Percentage (%)"]
[1,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (01)",{"$f":"IF(H2=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[2,null,"ROSEBERRY-HIGH","PTN-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","ROSEBERRY-HIGH (01)",{"$f":"IF(H3=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[3,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[4,null,"MT ALEXANDER 902-WILLOW","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER 902-WILLOW (02)",7.0293828201883877E-5]
[5,null,"FREDERICK-JUSTIN 3","TH0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","FREDERICK-JUSTIN 3 (01)",7.0293828201883877E-5]
[6,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (03)",7.0293828201883877E-5]
[7,null,"BREX 8-RADFORD","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BREX 8-RADFORD (01)",7.0293828201883877E-5]
[8,null,"BREX 8-RADFORD","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BREX 8-RADFORD (01)",7.0293828201883877E-5]
[9,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (02)",7.0293828201883877E-5]
[10,null,"BELLEVUE-SWANSTON","EP0-027","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BELLEVUE-SWANSTON (02)",7.0293828201883877E-5]
[11,null,"COPE-UCM 1","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","COPE-UCM 1 (02)",7.0293828201883877E-5]
[12,null,"RAGLAN-DALEY","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-DALEY (02)",7.0293828201883877E-5]
[13,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[14,null,"RESERVE-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RESERVE-DUNDAS (01)",7.0293828201883877E-5]
[15,null,"COPE-UCM 2","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","COPE-UCM 2 (02)",7.0293828201883877E-5]
[16,null,"CHIFLEY 51-53-RAGLAN","EP0-035","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","CHIFLEY 51-53-RAGLAN (02)",7.0293828201883877E-5]
[17,null,"CHIFLEY 72-REX","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","CHIFLEY 72-REX (00)",7.0293828201883877E-5]
[18,null,"RESERVE-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RESERVE-DUNDAS (01)",7.0293828201883877E-5]
[19,null,"MOORE-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE-PUCKLE (01)",7.0293828201883877E-5]
[20,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (01)",7.0293828201883877E-5]
[21,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (03)",7.0293828201883877E-5]
[22,null,"RALEIGH-NAPIER No. 2","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-NAPIER No. 2 (03)",7.0293828201883877E-5]
[23,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (01)",7.0293828201883877E-5]
[24,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (02)",7.0293828201883877E-5]
[25,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (02)",7.0293828201883877E-5]
[26,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[27,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (01)",7.0293828201883877E-5]
[28,null,"HUME 1445-CAMP","BMS-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","HUME 1445-CAMP (03)",7.0293828201883877E-5]
[29,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (03)",7.0293828201883877E-5]
[30,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (02)",7.0293828201883877E-5]
[31,null,"MOORE-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE-PUCKLE (01)",7.0293828201883877E-5]
[32,null,"HOMER-EDDY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HOMER-EDDY (03)",7.0293828201883877E-5]
[33,null,"McPHERSON-ALEXANDRA 2","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (04)",7.0293828201883877E-5]
[34,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (02)",7.0293828201883877E-5]
[35,null,"MT ALEXANDER-RUSSELL","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-RUSSELL (01)",7.0293828201883877E-5]
[36,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (01)",7.0293828201883877E-5]
[37,null,"NICHOLSON-BREWSTER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NICHOLSON-BREWSTER (01)",7.0293828201883877E-5]
[38,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (01)",7.0293828201883877E-5]
[39,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (01)",7.0293828201883877E-5]
[40,null,"JESICA 49-VANESSA","BD0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","JESICA 49-VANESSA (01)",7.0293828201883877E-5]
[41,null,"FREIGHT-CUSTOM","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (01)",7.0293828201883877E-5]
[42,null,"KEILOR-GOLF P5","SA0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","SA0","KEILOR-GOLF P5 (00)",7.0293828201883877E-5]
[43,null,"RESERVOIR RD-P52","SBY-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","RESERVOIR RD-P52 (00)",7.0293828201883877E-5]
[44,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[45,null,"MOORE-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE-PUCKLE (02)",7.0293828201883877E-5]
[46,null,"MT ALEXANDER-HOMER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","MT ALEXANDER-HOMER (03)",7.0293828201883877E-5]
[47,null,"RALEIGH-NAPIER No. 2","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-NAPIER No. 2 (01)",7.0293828201883877E-5]
[48,null,"COPE-UCM 1","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","COPE-UCM 2 (02)",7.0293828201883877E-5]
[49,null,"BELL 99-NATIONAL BANK","EP0-042","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BELL 99-NATIONAL BANK (01)",7.0293828201883877E-5]
[50,null,"ALBERT 62-OVANDO","PTN-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","PTN","ALBERT 62-OVANDO (03)",0]
[51,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[52,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[53,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[54,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[55,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[56,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[57,null,"BELL-QUINN","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BELL-QUINN (01)",7.0293828201883877E-5]
[58,null,"MT ALEXANDER-HOMER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","MT ALEXANDER-HOMER (03)",7.0293828201883877E-5]
[59,null,"ALBERT 28-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT 28-RAGLAN (01)",7.0293828201883877E-5]
[60,null,"ROSEBERRY-HIGH","PTN-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","ROSEBERRY-HIGH (03)",7.0293828201883877E-5]
[61,null,"HUME-CAMPBELL","BD0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","HUME-CAMPBELL (02)",7.0293828201883877E-5]
[62,null,"MEROLA 54 -FREEMAN","BD0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","MEROLA 54 -FREEMAN (01)",7.0293828201883877E-5]
[63,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[64,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (01)",7.0293828201883877E-5]
[65,null,"BICENTENNIAL-SHABA","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","BICENTENNIAL-SHABA (04)",7.0293828201883877E-5]
[66,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",{"$f":"IF(H67=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[67,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (01)",7.0293828201883877E-5]
[68,null,"THE BOULEVARD-GILBERT","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","THE BOULEVARD-GILBERT (01)",7.0293828201883877E-5]
[69,null,"LAWSON-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LAWSON-SALISBURY (02)",7.0293828201883877E-5]
[70,null,"WEBB-CORONATION","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","WEBB-CORONATION (03)",7.0293828201883877E-5]
[71,null,"SALISBURY-JACK","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","SALISBURY-JACK (01)",0]
[72,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[73,null,"HILLSYDE-LOEMAN","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HILLSYDE-LOEMAN (02)",7.0293828201883877E-5]
[74,null,"ELINDA-TUNALEY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELINDA-TUNALEY (02)",7.0293828201883877E-5]
[75,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (02)",0]
[76,null,"EAST-HARDING","FT0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","EAST-HARDING (02)",7.0293828201883877E-5]
[77,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (01)",7.0293828201883877E-5]
[78,null,"DONALD-LAWSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",7.0293828201883877E-5]
[79,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",7.0293828201883877E-5]
[80,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (02)",7.0293828201883877E-5]
[81,null,"KILMORE-CHARLTON","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","KILMORE-CHARLTON (02)",7.0293828201883877E-5]
[82,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (01)",7.0293828201883877E-5]
[83,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",7.0293828201883877E-5]
[84,null,"COLLINS-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","COLLINS-WATERDALE (02)",7.0293828201883877E-5]
[85,null,"BREX 8-RADFORD","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BREX 8-RADFORD (01)",7.0293828201883877E-5]
[86,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (04)",7.0293828201883877E-5]
[87,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (04)",7.0293828201883877E-5]
[88,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[89,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (01)",7.0293828201883877E-5]
[90,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (03)",7.0293828201883877E-5]
[91,null,"GAP-PRESTON","SBY-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","GAP-PRESTON (02)",7.0293828201883877E-5]
[92,null,"BLAKE-SESTON","NH0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","BLAKE-SESTON (02)",7.0293828201883877E-5]
[93,null,"MARGTMARY-MURRAY","CN0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","MARGTMARY-MURRAY (03)",0]
[94,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",7.0293828201883877E-5]
[95,null,"JOHNSON-BENAUD","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","JOHNSON-BENAUD (02)",7.0293828201883877E-5]
[96,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (02)",7.0293828201883877E-5]
[97,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[98,null,"RENFEW-ARKLEY","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","RENFEW-ARKLEY (02)",7.0293828201883877E-5]
[99,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (01)",7.0293828201883877E-5]
[100,null,"JOHN-WINIFRED","PV0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","JOHN-WINIFRED (01)",7.0293828201883877E-5]
[101,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (02)",7.0293828201883877E-5]
[102,null,"RIGGALL-APOLLO","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","RIGGALL-APOLLO (02)",7.0293828201883877E-5]
[103,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (02)",7.0293828201883877E-5]
[104,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[105,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (01)",7.0293828201883877E-5]
[106,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (04)",7.0293828201883877E-5]
[107,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (03)",7.0293828201883877E-5]
[108,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (02)",7.0293828201883877E-5]
[109,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[110,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[111,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (03)",7.0293828201883877E-5]
[112,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[113,null,"LIVINGSTONE-ELIZABETH","CN0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","LIVINGSTONE-ELIZABETH (01)",7.0293828201883877E-5]
[114,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (03)",7.0293828201883877E-5]
[115,null,"CRAWFORD-ROBINSON","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (02)",7.0293828201883877E-5]
[116,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[117,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (01)",7.0293828201883877E-5]
[118,null,"HENLEY-CLARKE","BD0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","HENLEY-CLARKE (02)",7.0293828201883877E-5]
[119,null,"SUSSEX-BANYULE","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","SUSSEX-BANYULE (02)",7.0293828201883877E-5]
[120,null,"WILKINSON-LIBERTY","EP0-036","2024-12-01","2024-12-07","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",0]
[121,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-CAMERON (03)",7.0293828201883877E-5]
[122,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (01)",7.0293828201883877E-5]
[123,null,"PUNJEL-CALDER","SHM-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","PUNJEL-CALDER (00)",7.0293828201883877E-5]
[124,null,"BRADFORD-KIRBY","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","BRADFORD-KIRBY (02)",7.0293828201883877E-5]
[125,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[126,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (01)",7.0293828201883877E-5]
[127,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (02)",7.0293828201883877E-5]
[128,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[129,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (02)",7.0293828201883877E-5]
[130,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (03)",{"$f":"IF(H131=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[131,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (04)",7.0293828201883877E-5]
[132,null,"HUNT-BAXTER","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",0]
[133,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",7.0293828201883877E-5]
[134,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[135,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[136,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[137,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[138,null,"KERNAN-MARKS","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-MARKS (02)",7.0293828201883877E-5]
[139,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[140,null,"HIGH 883-MELB WATER","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","HIGH 883-MELB WATER (00)",0]
[141,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (02)",7.0293828201883877E-5]
[142,null,"WILLOWTREE-PERSICA","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (04)",7.0293828201883877E-5]
[143,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (03)",7.0293828201883877E-5]
[144,null,"BELL-ORIEL","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BELL-ORIEL (01)",7.0293828201883877E-5]
[145,null,"WODONGA-CUTHBERT","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WODONGA-CUTHBERT (01)",7.0293828201883877E-5]
[146,null,"FENTON-MYRNONG","FT0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","FENTON-MYRNONG (03)",7.0293828201883877E-5]
[147,null,"BAILEY-HOPETOUN","HB0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","BAILEY-HOPETOUN (02)",7.0293828201883877E-5]
[148,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[149,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[150,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[151,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[152,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[153,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[154,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (01)",7.0293828201883877E-5]
[155,null,"CHATHAM-CANTERBURY","FT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","CHATHAM-CANTERBURY (02)",7.0293828201883877E-5]
[156,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (02)",7.0293828201883877E-5]
[157,null,"OWEN-GORDON","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","Y","N","FE0","OWEN-GORDON (01)",7.0293828201883877E-5]
[158,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (03)",7.0293828201883877E-5]
[159,null,"PARINGA-JASMINE","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","PARINGA-JASMINE (03)",7.0293828201883877E-5]
[160,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (04)",7.0293828201883877E-5]
[161,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[162,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[163,null,"ELATA-BEVERAGE","AW0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","ELATA-BEVERAGE (01)",7.0293828201883877E-5]
[164,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (02)",7.0293828201883877E-5]
[165,null,"HAMPDEN-CROTHERS","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",7.0293828201883877E-5]
[166,null,"PECK-PASCOE VALE","PV0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","PECK-PASCOE VALE (01)",7.0293828201883877E-5]
[167,null,"WOODLAND-WALLACE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-WALLACE (01)",7.0293828201883877E-5]
[168,null,"CHALLIS-JUBILLEE","NT0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NT0","CHALLIS-JUBILLEE (04)",7.0293828201883877E-5]
[169,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (03)",7.0293828201883877E-5]
[170,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",0]
[171,null,"CRESSWELL-CAMERON","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","CRESSWELL-CAMERON (02)",7.0293828201883877E-5]
[172,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (01)",7.0293828201883877E-5]
[173,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[174,null,"GREENSBOROUGH-YALLAMBIE","NH0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","GREENSBOROUGH-YALLAMBIE (01)",7.0293828201883877E-5]
[175,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (02)",7.0293828201883877E-5]
[176,null,"HUNT-BAXTER","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",0]
[177,null,"SEPARATION-FULHAM","FF0-093","2024-12-01","2024-12-07","Y","N","N","N","N","N","FF0","SEPARATION-FULHAM (01)",0]
[178,null,"LOVAT-LONGFORD","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","LOVAT-LONGFORD (02)",7.0293828201883877E-5]
[179,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (02)",7.0293828201883877E-5]
[180,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[181,null,"RAILWAY-RYE","BD0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","RAILWAY-RYE (02)",7.0293828201883877E-5]
[182,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[183,null,"WILKINSON-LIBERTY","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","WILKINSON-LIBERTY (02)",0]
[184,null,"ALMA-ELPHINSTONE","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","ALMA-ELPHINSTONE (02)",7.0293828201883877E-5]
[185,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[186,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (02)",7.0293828201883877E-5]
[187,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[188,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[189,null,"BRADSHAW-MARY","ES0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","BRADSHAW-MARY (02)",0]
[190,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (04)",7.0293828201883877E-5]
[191,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (02)",7.0293828201883877E-5]
[192,null,"CRAWFORD-ROBINSON","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (01)",7.0293828201883877E-5]
[193,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[194,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (03)",{"$f":"IF(H195=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[195,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","BEAUMONT-WARATAH (04)",7.0293828201883877E-5]
[196,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (02)",7.0293828201883877E-5]
[197,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[198,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[199,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (02)",7.0293828201883877E-5]
[200,null,"RESERVE-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RESERVE-DUNDAS (01)",7.0293828201883877E-5]
[201,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[202,null,"ROKEWOOD-ELLAM","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","ROKEWOOD-ELLAM (02)",7.0293828201883877E-5]
[203,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","HEIDELBERG-LATHAM (02)",7.0293828201883877E-5]
[204,null,"DAVIDSON-PERKINS","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAVIDSON-PERKINS (01)",7.0293828201883877E-5]
[205,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[206,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[207,null,"NEWCASTLE-DUNDAS","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NEWCASTLE-DUNDAS (02)",7.0293828201883877E-5]
[208,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[209,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (01)",7.0293828201883877E-5]
[210,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (01)",7.0293828201883877E-5]
[211,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","THISTLE-MT ALEXANDER (01)",7.0293828201883877E-5]
[212,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (04)",7.0293828201883877E-5]
[213,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (02)",7.0293828201883877E-5]
[214,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (01)",7.0293828201883877E-5]
[215,null,"RAGLAN-RESERVE","EP0-028","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","RAGLAN-RESERVE (01)",7.0293828201883877E-5]
[216,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (02)",7.0293828201883877E-5]
[217,null,"THOMAS-WILSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-WILSON (02)",7.0293828201883877E-5]
[218,null,"BROADHURST-MCFADZEAN","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","OCONNOR-MACFADZEAN (02)",7.0293828201883877E-5]
[219,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[220,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (02)",7.0293828201883877E-5]
[221,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (02)",7.0293828201883877E-5]
[222,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[223,null,"BLAKE-SESTON","NH0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","BLAKE-SESTON (02)",7.0293828201883877E-5]
[224,null,"MADDEN-STUDLEY","FW0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","MADDEN-STUDLEY (02)",7.0293828201883877E-5]
[225,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (02)",7.0293828201883877E-5]
[226,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (02)",7.0293828201883877E-5]
[227,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[228,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[229,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (02)",7.0293828201883877E-5]
[230,null,"CHARTERIS-WARNCLIFFE","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","CHARTERIS-WARNCLIFFE (02)",7.0293828201883877E-5]
[231,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[232,null,"BRASSEY CRT-P5E2","COO-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","COO","BRASSEY CRT-P5E2 (00)",0]
[233,null,"WOOD-GREENBELT","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","WOOD-GREENBELT (02)",0]
[234,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[235,null,"KELVIN-ALBERT","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KELVIN-ALBERT (01)",7.0293828201883877E-5]
[236,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[237,null,"BURKE-FLINDERS","SBY-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (02)",7.0293828201883877E-5]
[238,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (02)",7.0293828201883877E-5]
[239,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[240,null,"WALHALLA-MORELAND","CS0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (02)",0]
[241,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","BEAUMONT-WARATAH (04)",0]
[242,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[243,null,"KELVERNE-NEWLANDS","CN0-001","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","KELVERNE-NEWLANDS (02)",7.0293828201883877E-5]
[244,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[245,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[246,null,"RENFEW-ARKLEY","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","RENFEW-ARKLEY (01)",7.0293828201883877E-5]
[247,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[248,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[249,null,"FINN-HAUGHTON","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","FINN-HAUGHTON (03)",7.0293828201883877E-5]
[250,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (00)",7.0293828201883877E-5]
[251,null,"ST HELLIER-UP HEIDELBERG","NH0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","ST HELLIER-UP HEIDELBERG (01)",7.0293828201883877E-5]
[252,null,"ERINBANK-DOBIES","BD0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","ERINBANK-DOBIES (02)",7.0293828201883877E-5]
[253,null,"BIMBADEEN-YALLAMBIE","NH0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",0]
[254,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[255,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[256,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (01)",7.0293828201883877E-5]
[257,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[258,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (01)",{"$f":"IF(H259=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[259,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (02)",7.0293828201883877E-5]
[260,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[261,null,"VANBERG-TENNYSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","VANBERG-TENNYSON (04)",7.0293828201883877E-5]
[262,null,"JELLICOE-OSNEY","EP0-034","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","JELLICOE-OSNEY (02)",0]
[263,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[264,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (03)",7.0293828201883877E-5]
[265,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[266,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[267,null,"MT ALEXANDER 902-WILLOW","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER 902-WILLOW (02)",7.0293828201883877E-5]
[268,null,"SOUTH-BELL","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",7.0293828201883877E-5]
[269,null,"BRADSHAW-MARY","ES0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","BRADSHAW-MARY (02)",0]
[270,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (02)",7.0293828201883877E-5]
[271,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[272,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[273,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[274,null,"DARLINGTON-RENNIE","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",0]
[275,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (02)",7.0293828201883877E-5]
[276,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[277,null,"HENDERSON-WILSON","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HENDERSON-WILSON (02)",7.0293828201883877E-5]
[278,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[279,null,"JULIET-BENT","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JULIET-BENT (04)",7.0293828201883877E-5]
[280,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (03)",7.0293828201883877E-5]
[281,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[282,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (02)",7.0293828201883877E-5]
[283,null,"WOODLAND-WALLACE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-WALLACE (01)",7.0293828201883877E-5]
[284,null,"PEARL-WHEATSHEAF","PV0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","PEARL-WHEATSHEAF (02)",0]
[285,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",7.0293828201883877E-5]
[286,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[287,null,"GRAVES-MARKET","ES0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","GRAVES-MARKET (02)",0]
[288,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[289,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[290,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[291,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[292,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","THISTLE-MT ALEXANDER (01)",7.0293828201883877E-5]
[293,null,"SOUTH-BELL","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",7.0293828201883877E-5]
[294,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (04)",7.0293828201883877E-5]
[295,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[296,null,"DELAWARE-MENDIP","CN0-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","DELAWARE-MENDIP (01)",0]
[297,null,"JUSTIN-VIEW","PV0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","JUSTIN-VIEW (03)",0]
[298,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (02)",7.0293828201883877E-5]
[299,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (01)",7.0293828201883877E-5]
[300,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[301,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (01)",7.0293828201883877E-5]
[302,null,"SALTAU-MILLEARA","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SALTAU-MILLEARA (02)",7.0293828201883877E-5]
[303,null,"WILLOWTREE-PERSICA","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (01)",7.0293828201883877E-5]
[304,null,"BROWNING-MOORE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BROWNING-MOORE (01)",7.0293828201883877E-5]
[305,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[306,null,"NICHOLSON-BREWSTER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NICHOLSON-BREWSTER (01)",7.0293828201883877E-5]
[307,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",7.0293828201883877E-5]
[308,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (02)",7.0293828201883877E-5]
[309,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (02)",7.0293828201883877E-5]
[310,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[311,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[312,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","SOUTH-DERBY (02)",0]
[313,null,"VISION-MASCOMA","PV0-022","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","VISION-MASCOMA (02)",0]
[314,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[315,null,"CRESSWELL-CAMERON","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","CRESSWELL-CAMERON (02)",7.0293828201883877E-5]
[316,null,"HOME-WILKINSON","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","HOME-WILKINSON (01)",0]
[317,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[318,null,"BRADMAN-CHAPPEL","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","BRADMAN-CHAPPEL (02)",7.0293828201883877E-5]
[319,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (02)",7.0293828201883877E-5]
[320,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[321,null,"GELLIBRAND-VICTORIA","NT0-015","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","GELLIBRAND-VICTORIA (03)",0]
[322,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",{"$f":"IF(H323=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[323,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (03)",7.0293828201883877E-5]
[324,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[325,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",7.0293828201883877E-5]
[326,null,"COUANGALT RD-P19","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","COUANGALT RD-P19 (00)",7.0293828201883877E-5]
[327,null,"PASLEY-NEILL","SBY-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","PASLEY-NEILL (02)",7.0293828201883877E-5]
[328,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[329,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[330,null,"FREIGHT-CUSTOM","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (01)",7.0293828201883877E-5]
[331,null,"BROWNING-MOORE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BROWNING-MOORE (02)",7.0293828201883877E-5]
[332,null,"ANSTEY-PHILLIP","TT0-008","2024-12-01","2024-12-07","Y","N","N","Y","N","N","TT0","ANSTEY-PHILLIP (02)",0]
[333,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[334,null,"CAMBRIAN-HIGH","PTN-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","PTN","CAMBRIAN-HIGH (02)",0]
[335,null,"NICHOLSON-BREWSTER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NICHOLSON-BREWSTER (01)",7.0293828201883877E-5]
[336,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[337,null,"VANBERG-TENNYSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","VANBERG-TENNYSON (04)",7.0293828201883877E-5]
[338,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (02)",7.0293828201883877E-5]
[339,null,"WHITTON-BOYNE","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","WHITTON-BOYNE (03)",7.0293828201883877E-5]
[340,null,"RENFEW-ARKLEY","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","RENFEW-ARKLEY (04)",7.0293828201883877E-5]
[341,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (03)",7.0293828201883877E-5]
[342,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[343,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (01)",7.0293828201883877E-5]
[344,null,"WHITTON-BOYNE","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","WHITTON-BOYNE (03)",7.0293828201883877E-5]
[345,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[346,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[347,null,"FANNY-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FANNY-SALISBURY (01)",7.0293828201883877E-5]
[348,null,"LISTON-JOHNSON","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LISTON-JOHNSON (02)",7.0293828201883877E-5]
[349,null,"DELAWARE-MENDIP","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","DELAWARE-MENDIP (01)",0]
[350,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[351,null,"BREX 8-RADFORD","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BREX 8-RADFORD (02)",7.0293828201883877E-5]
[352,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (03)",7.0293828201883877E-5]
[353,null,"KELVIN-ALBERT","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KELVIN-ALBERT (02)",7.0293828201883877E-5]
[354,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (01)",7.0293828201883877E-5]
[355,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[356,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[357,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (02)",7.0293828201883877E-5]
[358,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (03)",7.0293828201883877E-5]
[359,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (03)",7.0293828201883877E-5]
[360,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[361,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[362,null,"CARROL-ORRONG","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CARROL-ORRONG (01)",7.0293828201883877E-5]
[363,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (02)",7.0293828201883877E-5]
[364,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (03)",7.0293828201883877E-5]
[365,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",7.0293828201883877E-5]
[366,null,"CHIFLEY 62-RENNICK","EP0-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","CHIFLEY 62-RENNICK (01)",7.0293828201883877E-5]
[367,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[368,null,"KIORA-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KIORA-PASCOE VALE (01)",7.0293828201883877E-5]
[369,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (02)",7.0293828201883877E-5]
[370,null,"SIMMINGTON-KENTMERE","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","SIMMINGTON-KENTMERE (01)",7.0293828201883877E-5]
[371,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (02)",7.0293828201883877E-5]
[372,null,"SOUTH-BELL","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",7.0293828201883877E-5]
[373,null,"CARROL-ORRONG","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CARROL-ORRONG (01)",7.0293828201883877E-5]
[374,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[375,null,"KELVIN-ALBERT","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KELVIN-ALBERT (01)",7.0293828201883877E-5]
[376,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[377,null,"WHITELAW-BROADWAY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BROADWAY (01)",7.0293828201883877E-5]
[378,null,"DARLINGTON-RENNIE","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",0]
[379,null,"SEXTON-HALSEY","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SEXTON-HALSEY (03)",7.0293828201883877E-5]
[380,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (02)",7.0293828201883877E-5]
[381,null,"BANYULE-MCCRAE","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","BANYULE-MCCRAE (01)",7.0293828201883877E-5]
[382,null,"HOMER-EDDY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HOMER-EDDY (01)",7.0293828201883877E-5]
[383,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (03)",7.0293828201883877E-5]
[384,null,"SALISBURY-JACK","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","SALISBURY-JACK (01)",0]
[385,null,"FENTON-MYRNONG","FT0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","FENTON-MYRNONG (01)",7.0293828201883877E-5]
[386,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",{"$f":"IF(H387=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[387,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[388,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (02)",7.0293828201883877E-5]
[389,null,"BRAY-BARTROP","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRAY-BARTROP (02)",7.0293828201883877E-5]
[390,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",7.0293828201883877E-5]
[391,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (02)",7.0293828201883877E-5]
[392,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (03)",7.0293828201883877E-5]
[393,null,"DELAWARE-MENDIP","CN0-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","DELAWARE-MENDIP (01)",0]
[394,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[395,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[396,null,"CRAWFORD-ROBINSON","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (01)",7.0293828201883877E-5]
[397,null,"KIORA-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KIORA-PASCOE VALE (03)",7.0293828201883877E-5]
[398,null,"CAPULET-BENT","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAPULET-BENT (02)",7.0293828201883877E-5]
[399,null,"RAGLAN 45-BEECHER","EP0-028","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN 45-BEECHER (02)",7.0293828201883877E-5]
[400,null,"LEVER-QUEEN","CS0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEVER-QUEEN (03)",0]
[401,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (02)",7.0293828201883877E-5]
[402,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (04)",7.0293828201883877E-5]
[403,null,"BELL-QUINN","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BELL-QUINN (01)",7.0293828201883877E-5]
[404,null,"WILFRED-CEDRIC","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","WILFRED-CEDRIC (02)",7.0293828201883877E-5]
[405,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (02)",7.0293828201883877E-5]
[406,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (01)",7.0293828201883877E-5]
[407,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUTLER-PASCOE VALE (01)",7.0293828201883877E-5]
[408,null,"YEA-KIEWA","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","YEA-KIEWA (01)",7.0293828201883877E-5]
[409,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",7.0293828201883877E-5]
[410,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (02)",7.0293828201883877E-5]
[411,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (03)",7.0293828201883877E-5]
[412,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[413,null,"SUFFOLK-DONGOLA","FW0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","SUFFOLK-DONGOLA (02)",0]
[414,null,"GAP-COWPER","SBY-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","GAP-COWPER (02)",7.0293828201883877E-5]
[415,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (02)",7.0293828201883877E-5]
[416,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (00)",7.0293828201883877E-5]
[417,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (02)",7.0293828201883877E-5]
[418,null,"GLEN-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLEN-GLASS (04)",7.0293828201883877E-5]
[419,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (02)",7.0293828201883877E-5]
[420,null,"GLASS-NAPIER NO.2","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER NO.2 (02)",7.0293828201883877E-5]
[421,null,"FANNY-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FANNY-SALISBURY (01)",7.0293828201883877E-5]
[422,null,"CRANWELL-CARNARVON","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRANWELL-CARNARVON (03)",7.0293828201883877E-5]
[423,null,"JULIET-BENT","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JULIET-BENT (04)",7.0293828201883877E-5]
[424,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[425,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",0]
[426,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[427,null,"SUFFOLK-THOMSON","FW0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","SUFFOLK-THOMSON (04)",0]
[428,null,"COLLINS-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","COLLINS-WATERDALE (02)",7.0293828201883877E-5]
[429,null,"SALTAU-MILLEARA","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SALTAU-MILLEARA (02)",7.0293828201883877E-5]
[430,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KERFERD-RALEIGH (02)",7.0293828201883877E-5]
[431,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[432,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (02)",7.0293828201883877E-5]
[433,null,"O'DOWD-HOWARD","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","O'DOWD-HOWARD (02)",0]
[434,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (01)",7.0293828201883877E-5]
[435,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (03)",7.0293828201883877E-5]
[436,null,"RAGLAN-DALEY","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-DALEY (02)",7.0293828201883877E-5]
[437,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[438,null,"FERGUSON-THE PARADE","ES0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","FERGUSON-THE PARADE (01)",7.0293828201883877E-5]
[439,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (01)",7.0293828201883877E-5]
[440,null,"MT ALEXANDER-HOMER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","MT ALEXANDER-HOMER (03)",7.0293828201883877E-5]
[441,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (00)",7.0293828201883877E-5]
[442,null,"CAPULET-BENT","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAPULET-BENT (01)",7.0293828201883877E-5]
[443,null,"WESTMERE-WARNE","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WESTMERE-WARNE (01)",7.0293828201883877E-5]
[444,null,"WINCHESTER-WHARTON","BMS-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","WINCHESTER-WHARTON (03)",7.0293828201883877E-5]
[445,null,"PERIGRINE-DEEP CREEK","COO-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","COO","PERIGRINE-DEEP CREEK (00)",0]
[446,null,"EISENHOWER-CHALEYER","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","EISENHOWER-CHALEYER (01)",0]
[447,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (02)",7.0293828201883877E-5]
[448,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[449,null,"KILMORE-CHARLTON","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","KILMORE-CHARLTON (02)",7.0293828201883877E-5]
[450,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (02)",{"$f":"IF(H451=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[451,null,"DIAMOND-ROSEHILL","ES0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","DIAMOND-ROSEHILL (01)",0]
[452,null,"MANOEL-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MANOEL-DAREBIN (02)",7.0293828201883877E-5]
[453,null,"FORREST-HUDSONS","YVE-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","YVE","FORREST-HUDSONS (04)",7.0293828201883877E-5]
[454,null,"HENDERSON-WILSON","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HENDERSON-WILSON (01)",7.0293828201883877E-5]
[455,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","N","Y","N","FW0","BEAUMONT-WARATAH (04)",0]
[456,null,"WEST-KINGSLEY","AW0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","WEST-KINGSLEY (01)",0]
[457,null,"SUNSHINE-MARKET No 2","TH0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","SUNSHINE-MARKET No 2 (02)",7.0293828201883877E-5]
[458,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[459,null,"GRANGE-CRAMER","CS0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GRANGE-CRAMER (01)",0]
[460,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",7.0293828201883877E-5]
[461,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (01)",7.0293828201883877E-5]
[462,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (01)",7.0293828201883877E-5]
[463,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[464,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (02)",7.0293828201883877E-5]
[465,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[466,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (01)",7.0293828201883877E-5]
[467,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (01)",7.0293828201883877E-5]
[468,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUTLER-PASCOE VALE (01)",7.0293828201883877E-5]
[469,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[470,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (02)",7.0293828201883877E-5]
[471,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[472,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (01)",7.0293828201883877E-5]
[473,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[474,null,"WHITTON-BOYNE","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","WHITTON-BOYNE (03)",7.0293828201883877E-5]
[475,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[476,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (02)",7.0293828201883877E-5]
[477,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[478,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[479,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[480,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[481,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","TT0","ROYAL-MCMAHON (01)",0]
[482,null,"MAYFIELD-MUNRO","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",0]
[483,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (01)",7.0293828201883877E-5]
[484,null,"BEVERLEY-GREVILLE","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","BEVERLEY-GREVILLE (01)",7.0293828201883877E-5]
[485,null,"WHITE-CHEDDAR","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITE-CHEDDAR (02)",7.0293828201883877E-5]
[486,null,"GREENVALE-WALLACE","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","GREENVALE-WALLACE (02)",7.0293828201883877E-5]
[487,null,"HARCOURT-SHERBOURNE","AW0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","HARCOURT-SHERBOURNE (02)",7.0293828201883877E-5]
[488,null,"SIMMINGTON-KENTMERE","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","SIMMINGTON-KENTMERE (02)",7.0293828201883877E-5]
[489,null,"MCCUBBIN-BLACKMAN","SHM-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","MCCUBBIN-BLACKMAN (03)",7.0293828201883877E-5]
[490,null,"SEXTON-HALSEY","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SEXTON-HALSEY (03)",7.0293828201883877E-5]
[491,null,"PORTER-DOUGHARTY","NH0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NH0","PORTER-DOUGHARTY (01)",0]
[492,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[493,null,"TONGUE-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","TONGUE-MACKAY (02)",7.0293828201883877E-5]
[494,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (02)",7.0293828201883877E-5]
[495,null,"LATROBE-MENZIES","SBY-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","LATROBE-MENZIES (01)",7.0293828201883877E-5]
[496,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[497,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (03)",7.0293828201883877E-5]
[498,null,"KALANG-PLUMPTON","PV0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","KALANG-PLUMPTON (02)",0]
[499,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[500,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (04)",7.0293828201883877E-5]
[501,null,"HAMPDEN-CROTHERS","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",7.0293828201883877E-5]
[502,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[503,null,"RENFEW-ARKLEY","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","RENFEW-ARKLEY (01)",7.0293828201883877E-5]
[504,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[505,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (03)",7.0293828201883877E-5]
[506,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[507,null,"SOUTH-BELL","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",7.0293828201883877E-5]
[508,null,"GREIG-THOMSON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","GREIG-THOMSON (01)",7.0293828201883877E-5]
[509,null,"ALBERT-HARROW","EPN-035","2024-12-01","2024-12-07","Y","N","N","Y","N","N","EPN","ALBERT-HARROW (02)",0]
[510,null,"BREWSTER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-NAPIER (03)",7.0293828201883877E-5]
[511,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[512,null,"HILLSYDE-LOEMAN","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HILLSYDE-LOEMAN (02)",7.0293828201883877E-5]
[513,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",7.0293828201883877E-5]
[514,null,"GORDON-WOOD","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","GORDON-WOOD (02)",{"$f":"IF(H515=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[515,null,"CARWARP-ERSKINE","NH0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","CARWARP-ERSKINE (02)",0]
[516,null,"RENFEW-ARKLEY","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","RENFEW-ARKLEY (03)",7.0293828201883877E-5]
[517,null,"FREIGHT-CUSTOM","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (02)",7.0293828201883877E-5]
[518,null,"PASCOE VALE-KELLAWAY","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-KELLAWAY (03)",7.0293828201883877E-5]
[519,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[520,null,"MT ALEXANDER 902-WILLOW","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER 902-WILLOW (02)",7.0293828201883877E-5]
[521,null,"THE CROSSWAY-UPLAND","NS0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","NS0","THE CROSSWAY-UPLAND (04)",0]
[522,null,"WEBB-CORONATION","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","WEBB-CORONATION (03)",7.0293828201883877E-5]
[523,null,"LOCH-WENDORA","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LOCH-WENDORA (03)",7.0293828201883877E-5]
[524,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (04)",7.0293828201883877E-5]
[525,null,"DALGETY-HIGH","PTN-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","PTN","NA",0]
[526,null,"LAUREL-TYLER","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","LAUREL-TYLER (01)",0]
[527,null,"WODONGA-CUTHBERT","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WODONGA-CUTHBERT (01)",7.0293828201883877E-5]
[528,null,"LAWSON-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LAWSON-SALISBURY (02)",7.0293828201883877E-5]
[529,null,"ROSS-ELIZABETH","NT0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NT0","ROSS-ELIZABETH (01)",7.0293828201883877E-5]
[530,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (03)",7.0293828201883877E-5]
[531,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (01)",7.0293828201883877E-5]
[532,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[533,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (03)",7.0293828201883877E-5]
[534,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (02)",7.0293828201883877E-5]
[535,null,"BRAY-BARTROP","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRAY-BARTROP (01)",7.0293828201883877E-5]
[536,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",7.0293828201883877E-5]
[537,null,"BURTON-OAKLAND","YVE-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","YVE","BURTON-OAKLAND (01)",7.0293828201883877E-5]
[538,null,"YALLAMBIE-WENDOVER","NH0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","YALLAMBIE-WENDOVER (01)",0]
[539,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[540,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[541,null,"AMIS-VISTA","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","AMIS-VISTA (02)",7.0293828201883877E-5]
[542,null,"CARROL-ORRONG","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CARROL-ORRONG (01)",7.0293828201883877E-5]
[543,null,"NICHOLSON-BREWSTER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NICHOLSON-BREWSTER (01)",7.0293828201883877E-5]
[544,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[545,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (02)",7.0293828201883877E-5]
[546,null,"ALEXANDRA-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",0]
[547,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[548,null,"SALTAU-MILLEARA","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SALTAU-MILLEARA (02)",7.0293828201883877E-5]
[549,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[550,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[551,null,"MACPHERSON-SHEPHERD","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","MACPHERSON-SHEPHERD (02)",7.0293828201883877E-5]
[552,null,"SALMON-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","SALMON-SCHOFIELD (02)",7.0293828201883877E-5]
[553,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[554,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (02)",7.0293828201883877E-5]
[555,null,"MCIVOR-KIEWA","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","MCIVOR-KIEWA (02)",7.0293828201883877E-5]
[556,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (03)",7.0293828201883877E-5]
[557,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[558,null,"GLEN-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLEN-GLASS (03)",7.0293828201883877E-5]
[559,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (02)",7.0293828201883877E-5]
[560,null,"CHARTERIS-WARNCLIFFE","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","CHARTERIS-WARNCLIFFE (02)",7.0293828201883877E-5]
[561,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (00)",7.0293828201883877E-5]
[562,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (02)",7.0293828201883877E-5]
[563,null,"LOCH-WENDORA","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LOCH-WENDORA (02)",7.0293828201883877E-5]
[564,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",7.0293828201883877E-5]
[565,null,"SAMARA-ELMHURST","AW0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SAMARA-ELMHURST (02)",7.0293828201883877E-5]
[566,null,"WATERSONS RD-P3W1","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","WATERSONS RD-P3W1 (00)",7.0293828201883877E-5]
[567,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[568,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[569,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (01)",7.0293828201883877E-5]
[570,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (01)",7.0293828201883877E-5]
[571,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (01)",7.0293828201883877E-5]
[572,null,"BREX-RADFORD","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BREX-RADFORD (00)",7.0293828201883877E-5]
[573,null,"LATROBE-MENZIES","SBY-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","LATROBE-MENZIES (01)",7.0293828201883877E-5]
[574,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[575,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (02)",7.0293828201883877E-5]
[576,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[577,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",0]
[578,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HODDLE-FLETCHER (02)",{"$f":"IF(H579=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[579,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (02)",7.0293828201883877E-5]
[580,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[581,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (01)",7.0293828201883877E-5]
[582,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (01)",7.0293828201883877E-5]
[583,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (01)",7.0293828201883877E-5]
[584,null,"ROSS-ELIZABETH","NT0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NT0","ROSS-ELIZABETH (01)",7.0293828201883877E-5]
[585,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (02)",7.0293828201883877E-5]
[586,null,"GLASS-NAPIER NO.2","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER NO.2 (02)",7.0293828201883877E-5]
[587,null,"GLASS-NAPIER NO.2","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER NO.2 (02)",7.0293828201883877E-5]
[588,null,"MAGDALA-WOODLAND","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MAGDALA-WOODLAND (03)",7.0293828201883877E-5]
[589,null,"LOCKSLEY-KINSALE","CN0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","LOCKSLEY-KINSALE (02)",7.0293828201883877E-5]
[590,null,"BROWNING-MOORE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BROWNING-MOORE (02)",7.0293828201883877E-5]
[591,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (03)",7.0293828201883877E-5]
[592,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (02)",7.0293828201883877E-5]
[593,null,"MARGTMARY-MURRAY","CN0-008","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","MARGTMARY-MURRAY (03)",0]
[594,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[595,null,"LANCEFIELD RD-P50","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","LANCEFIELD RD-P50 (00)",7.0293828201883877E-5]
[596,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[597,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (02)",7.0293828201883877E-5]
[598,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (04)",7.0293828201883877E-5]
[599,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[600,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[601,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (01)",7.0293828201883877E-5]
[602,null,"LAWSON-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LAWSON-SALISBURY (01)",7.0293828201883877E-5]
[603,null,"HEIDELBERG-KINGSLEY","HB0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","HEIDELBERG-KINGSLEY (03)",7.0293828201883877E-5]
[604,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[605,null,"LEVER-GORDON","CS0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEVER-GORDON (02)",0]
[606,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (01)",7.0293828201883877E-5]
[607,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[608,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[609,null,"MUNRO-ERSKINE","NH0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","MUNRO-ERSKINE (02)",0]
[610,null,"ALMA-ELPHINSTONE","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","ALMA-ELPHINSTONE (02)",7.0293828201883877E-5]
[611,null,"ASCOT VALE 331-YOUNG","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ASCOT VALE 331-YOUNG (01)",7.0293828201883877E-5]
[612,null,"HAWKHURST-FRANCIS","FW0-013","2024-12-01","2024-12-07","Y","Y","Y","Y","N","N","FW0","HAWKHURST-FRANCIS (01)",7.0293828201883877E-5]
[613,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[614,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (04)",7.0293828201883877E-5]
[615,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",7.0293828201883877E-5]
[616,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[617,null,"WILLOWTREE-PERSICA","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (01)",7.0293828201883877E-5]
[618,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (02)",7.0293828201883877E-5]
[619,null,"ETZEL-CLYDESDALE","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","ETZEL-CLYDESDALE (03)",7.0293828201883877E-5]
[620,null,"FINNINGLEY-MARHAM","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FINNINGLEY-MARHAM (02)",7.0293828201883877E-5]
[621,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (02)",7.0293828201883877E-5]
[622,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[623,null,"STEWART-PASCOE VALE","PV0-022","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","STEWART-PASCOE VALE (01)",0]
[624,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[625,null,"THORPE-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","THORPE-WOODS (01)",0]
[626,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (02)",7.0293828201883877E-5]
[627,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[628,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[629,null,"NEWMAN-HOTHAM","AW0-007","2024-12-01","2024-12-07","Y","N","N","Y","N","N","AW0","NEWMAN-HOTHAM (03)",0]
[630,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[631,null,"HIGGINS-MCKELL","SBY-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","HIGGINS-MCKELL (01)",7.0293828201883877E-5]
[632,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (02)",7.0293828201883877E-5]
[633,null,"NEILL-MOUNSEY","SBY-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","NEILL-MOUNSEY (02)",7.0293828201883877E-5]
[634,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[635,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (01)",7.0293828201883877E-5]
[636,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[637,null,"KEADY-SYDNEY","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",0]
[638,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",0]
[639,null,"ALMA-CHANDLER","NT0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NT0","ALMA-CHANDLER (02)",7.0293828201883877E-5]
[640,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (03)",7.0293828201883877E-5]
[641,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[642,null,"SUFFOLK-DONGOLA","FW0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","SUFFOLK-DONGOLA (02)",{"$f":"IF(H643=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":0}]
[643,null,"KILMORE-CHARLTON","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WINTER-KERANG (02)",7.0293828201883877E-5]
[644,null,"MT PLEASANT-BELL","CS0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","MT PLEASANT-BELL (01)",7.0293828201883877E-5]
[645,null,"MERCHISTON-CARNARVON","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MERCHISTON-CARNARVON (02)",7.0293828201883877E-5]
[646,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[647,null,"MANOEL-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MANOEL-DAREBIN (01)",7.0293828201883877E-5]
[648,null,"RENFEW-ARKLEY","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","RENFEW-ARKLEY (03)",7.0293828201883877E-5]
[649,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[650,null,"MAGDALA-WOODLAND","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MAGDALA-WOODLAND (01)",7.0293828201883877E-5]
[651,null,"MEROLA 54 -FREEMAN","BD0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","MEROLA 54 -FREEMAN (02)",7.0293828201883877E-5]
[652,null,"KATUNGA-HAMILTON","BD0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","KATUNGA-HAMILTON (02)",7.0293828201883877E-5]
[653,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[654,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (01)",7.0293828201883877E-5]
[655,null,"DIAMOND-ROSEHILL","ES0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","DIAMOND-ROSEHILL (01)",0]
[656,null,"MELTON-MEWS","SHM-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","MELTON-MEWS (04)",7.0293828201883877E-5]
[657,null,"JOHNSON-BENAUD","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","JOHNSON-BENAUD (01)",7.0293828201883877E-5]
[658,null,"HAMPDEN-CROTHERS","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",7.0293828201883877E-5]
[659,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[660,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[661,null,"GLASS-NAPIER NO.2","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER NO.2 (02)",7.0293828201883877E-5]
[662,null,"HILLSIDE-HURTLE","ES0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","HILLSIDE-HURTLE (02)",7.0293828201883877E-5]
[663,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (02)",7.0293828201883877E-5]
[664,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (01)",7.0293828201883877E-5]
[665,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",0]
[666,null,"WALHALLA-MORELAND","CS0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (02)",0]
[667,null,"WALHALLA-MORELAND","CS0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (02)",0]
[668,null,"WADHAM-MORELAND","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WADHAM-MORELAND (01)",7.0293828201883877E-5]
[669,null,"WADHAM-MORELAND","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WADHAM-MORELAND (02)",7.0293828201883877E-5]
[670,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (05)",7.0293828201883877E-5]
[671,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","NA",7.0293828201883877E-5]
[672,null,"BELLEVUE-SWANSTON","EP0-027","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BELLEVUE-SWANSTON (02)",7.0293828201883877E-5]
[673,null,"FLETCHER-NICHOLSON","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-NICHOLSON (01)",7.0293828201883877E-5]
[674,null,"GLENGYLE-NICHOLSON","CS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","GLENGYLE-NICHOLSON (02)",7.0293828201883877E-5]
[675,null,"GLENGYLE-NICHOLSON","CS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","GLENGYLE-NICHOLSON (02)",7.0293828201883877E-5]
[676,null,"GLENGYLE-NICHOLSON","CS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","GLENGYLE-NICHOLSON (02)",7.0293828201883877E-5]
[677,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (04)",7.0293828201883877E-5]
[678,null,"MT ALEXANDER-RUSSELL","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-RUSSELL (01)",7.0293828201883877E-5]
[679,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (01)",7.0293828201883877E-5]
[680,null,"VANBERG-TENNYSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","VANBERG-TENNYSON (03)",7.0293828201883877E-5]
[681,null,"WHITE-CHEDDAR","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITE-CHEDDAR (02)",7.0293828201883877E-5]
[682,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (02)",7.0293828201883877E-5]
[683,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[684,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[685,null,"STATION-HALL","CS0-005","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","STATION-HALL (01)",7.0293828201883877E-5]
[686,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[687,null,"GLEN-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLEN-GLASS (02)",7.0293828201883877E-5]
[688,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (04)",7.0293828201883877E-5]
[689,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[690,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[691,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (02)",7.0293828201883877E-5]
[692,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (02)",7.0293828201883877E-5]
[693,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[694,null,"REYNARD-ROYAL","CS0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","REYNARD-ROYAL (02)",0]
[695,null,"GRAHAM-WOODLANDS","CS0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",0]
[696,null,"GRAHAM-WOODLANDS","CS0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",0]
[697,null,"MALMSBURY-WOODBURN","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","MALMSBURY-WOODBURN (02)",7.0293828201883877E-5]
[698,null,"SOUDAN-HIGH","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","SOUDAN-HIGH (01)",0]
[699,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[700,null,"WALHALLA-MORELAND","CS0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (02)",0]
[701,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[702,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",0]
[703,null,"WALTHAM-LEE","FT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","WALTHAM-LEE (01)",7.0293828201883877E-5]
[704,null,"FINN-HAUGHTON","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","FINN-HAUGHTON (03)",7.0293828201883877E-5]
[705,null,"WADHAM-MORELAND","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WADHAM-MORELAND (03)",7.0293828201883877E-5]
[706,null,"WADHAM-MORELAND","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WADHAM-MORELAND (03)",{"$f":"IF(H707=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[707,null,"WADHAM-MORELAND","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WADHAM-MORELAND (03)",7.0293828201883877E-5]
[708,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[709,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[710,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[711,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[712,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[713,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[714,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[715,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[716,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[717,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[718,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[719,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[720,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[721,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[722,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[723,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[724,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[725,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[726,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[727,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[728,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[729,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[730,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[731,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[732,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[733,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[734,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[735,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[736,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[737,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[738,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[739,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[740,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[741,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[742,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[743,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[744,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[745,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[746,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[747,null,"BRENTWOOD-WENTWORTH","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BRENTWOOD-WENTWORTH (02)",7.0293828201883877E-5]
[748,null,"BRENTWOOD-WENTWORTH","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BRENTWOOD-WENTWORTH (02)",7.0293828201883877E-5]
[749,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0",null,7.0293828201883877E-5]
[750,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[751,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[752,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[753,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[754,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[755,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[756,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[757,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[758,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[759,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[760,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[761,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[762,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[763,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[764,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[765,null,"BRENTWOOD-WENTWORTH","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BRENTWOOD-WENTWORTH (02)",7.0293828201883877E-5]
[766,null,"BRENTWOOD-WENTWORTH","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BRENTWOOD-WENTWORTH (02)",7.0293828201883877E-5]
[767,null,"BRENTWOOD-WENTWORTH","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BRENTWOOD-WENTWORTH (02)",7.0293828201883877E-5]
[768,null,"FOSTERS-MIDWAY","TMA-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TMA","FOSTERS-MIDWAY (01)",7.0293828201883877E-5]
[769,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[770,null,"BELL-ORIEL","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","BELL-ORIEL (01)",{"$f":"IF(H771=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[771,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (02)",7.0293828201883877E-5]
[772,null,"HARDING-NICHOLSON","CS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","HARDING-NICHOLSON (02)",7.0293828201883877E-5]
[773,null,"HARDING-NICHOLSON","CS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","HARDING-NICHOLSON (02)",7.0293828201883877E-5]
[774,null,"HARDING-NICHOLSON","CS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","HARDING-NICHOLSON (02)",7.0293828201883877E-5]
[775,null,"HARDING-NICHOLSON","CS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","HARDING-NICHOLSON (02)",7.0293828201883877E-5]
[776,null,"DARLINGTON-RENNIE","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",0]
[777,null,"DARLINGTON-RENNIE","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",0]
[778,null,"DARLINGTON-RENNIE","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",0]
[779,null,"DARLINGTON-RENNIE","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",0]
[780,null,"DARLINGTON-RENNIE","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",0]
[781,null,"DARLINGTON-RENNIE","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",0]
[782,null,"DARLINGTON-RENNIE","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",0]
[783,null,"DARLINGTON-RENNIE","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",0]
[784,null,"NEWCASTLE-DUNDAS","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NEWCASTLE-DUNDAS (02)",7.0293828201883877E-5]
[785,null,"BLIBURG-SUNSET","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","BLIBURG-SUNSET (02)",7.0293828201883877E-5]
[786,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (03)",7.0293828201883877E-5]
[787,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (02)",7.0293828201883877E-5]
[788,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[789,null,"HUTCHINSON-NICHOLSON","CS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",7.0293828201883877E-5]
[790,null,"HUTCHINSON-NICHOLSON","CS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",7.0293828201883877E-5]
[791,null,"HILLVIEW DR-P3","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","Y","N","SBY","HILLVIEW DR-P3 (00)",7.0293828201883877E-5]
[792,null,"SYDNEY-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","SYDNEY-MURRAY (04)",0]
[793,null,"SYDNEY-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","SYDNEY-MURRAY (04)",0]
[794,null,"HILLSIDE-HURTLE","ES0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","HILLSIDE-HURTLE (02)",7.0293828201883877E-5]
[795,null,"KEADY-SYDNEY","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",0]
[796,null,"KEADY-SYDNEY","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",0]
[797,null,"KEADY-SYDNEY","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",0]
[798,null,"MALACCA-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","MALACCA-WATERDALE (03)",7.0293828201883877E-5]
[799,null,"GOLEEN-SYDNEY","CN0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","GOLEEN-SYDNEY (03)",7.0293828201883877E-5]
[800,null,"GOLEEN-SYDNEY","CN0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","GOLEEN-SYDNEY (03)",7.0293828201883877E-5]
[801,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (02)",7.0293828201883877E-5]
[802,null,"DUNCANS LA STH-P1","SHM-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","DUNCANS LA STH-P1 (00)",7.0293828201883877E-5]
[803,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",0]
[804,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[805,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[806,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[807,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[808,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[809,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[810,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[811,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[812,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[813,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[814,null,"CARR-NEWLANDS","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","CARR-NEWLANDS (01)",0]
[815,null,"MORRIS-MCMAHONS","CN0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","MORRIS-MCMAHONS (02)",0]
[816,null,"MORRIS-MCMAHONS","CN0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","MORRIS-MCMAHONS (02)",0]
[817,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[818,null,"CARR-NEWLANDS","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","SHORE-MCMAHONS (03)",0]
[819,null,"MORRIS-MCMAHONS","CN0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","MORRIS-MCMAHONS (02)",0]
[820,null,"HOME-WILKINSON","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","HOME-WILKINSON (01)",0]
[821,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[822,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[823,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[824,null,"GOFF-ELIZABETH","CS0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","GOFF-ELIZABETH (02)",7.0293828201883877E-5]
[825,null,"GOFF-ELIZABETH","CS0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","GOFF-ELIZABETH (02)",7.0293828201883877E-5]
[826,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (02)",7.0293828201883877E-5]
[827,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",0]
[828,null,"BROWNING-MOORE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BROWNING-MOORE (02)",7.0293828201883877E-5]
[829,null,"HILLSYDE-LOEMAN","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HILLSYDE-LOEMAN (01)",7.0293828201883877E-5]
[830,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[831,null,"HUNT-BAXTER","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",0]
[832,null,"HUNT-BAXTER","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",0]
[833,null,"STIRLING-GLENCAIRN","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","STIRLING-GLENCAIRN (01)",7.0293828201883877E-5]
[834,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",{"$f":"IF(H835=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[835,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",0]
[836,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (04)",7.0293828201883877E-5]
[837,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","THISTLE-MT ALEXANDER (01)",7.0293828201883877E-5]
[838,null,"MAYFIELD-MUNRO","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",0]
[839,null,"MAYFIELD-MUNRO","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",0]
[840,null,"MAYFIELD-MUNRO","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",0]
[841,null,"MAYFIELD-MUNRO","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",0]
[842,null,"MAYFIELD-MUNRO","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",0]
[843,null,"MAYFIELD-MUNRO","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",0]
[844,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[845,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (02)",7.0293828201883877E-5]
[846,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[847,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (03)",7.0293828201883877E-5]
[848,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (03)",7.0293828201883877E-5]
[849,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (02)",7.0293828201883877E-5]
[850,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[851,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",0]
[852,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",0]
[853,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",0]
[854,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",0]
[855,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",0]
[856,null,"JUKES-BONWICK","CN0-010","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","JUKES-BONWICK (01)",0]
[857,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",0]
[858,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",0]
[859,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",0]
[860,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",0]
[861,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",0]
[862,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",0]
[863,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",0]
[864,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",0]
[865,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",0]
[866,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",0]
[867,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",0]
[868,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",0]
[869,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",0]
[870,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",0]
[871,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",0]
[872,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",0]
[873,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",0]
[874,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",0]
[875,null,"REYNARD-SPRINGHALL","CS0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",0]
[876,null,"REYNARD-SPRINGHALL","CS0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",0]
[877,null,"VANBERG-TENNYSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","VANBERG-TENNYSON (01)",7.0293828201883877E-5]
[878,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[879,null,"CAMBRIAN-HIGH","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","CAMBRIAN-HIGH (01)",7.0293828201883877E-5]
[880,null,"MITCHELL-HACKETT","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",0]
[881,null,"MITCHELL-HACKETT","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",0]
[882,null,"MITCHELL-HACKETT","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",0]
[883,null,"MITCHELL-HACKETT","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",0]
[884,null,"MITCHELL-HACKETT","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",0]
[885,null,"MITCHELL-HACKETT","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",0]
[886,null,"MITCHELL-HACKETT","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",0]
[887,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[888,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",0]
[889,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",0]
[890,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",0]
[891,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",0]
[892,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",0]
[893,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",0]
[894,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",0]
[895,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",0]
[896,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",0]
[897,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (02)",7.0293828201883877E-5]
[898,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (01)",{"$f":"IF(H899=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":0}]
[899,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (01)",0]
[900,null,"WARATAH-DERBY","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WARATAH-DERBY (01)",0]
[901,null,"DAVERN-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DAVERN-O'HEA (01)",0]
[902,null,"DAVERN-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DAVERN-O'HEA (01)",0]
[903,null,"BOLINGBROKE-BURGUNDY","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BOLINGBROKE-BURGUNDY (02)",0]
[904,null,"WARATAH-DERBY","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WARATAH-DERBY (01)",0]
[905,null,"WARATAH-DERBY","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WARATAH-DERBY (01)",0]
[906,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[907,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[908,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[909,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[910,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[911,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[912,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[913,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[914,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[915,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[916,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[917,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[918,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[919,null,"GREENWOOD-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",0]
[920,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KERFERD-RALEIGH (01)",7.0293828201883877E-5]
[921,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[922,null,"GISBORNE MELTON RD-P31E2","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","GISBORNE MELTON RD-P31E2 (00)",7.0293828201883877E-5]
[923,null,"WARATAH-DERBY","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WARATAH-DERBY (01)",0]
[924,null,"WARATAH-DERBY","CS0-002","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","WARATAH-DERBY (01)",0]
[925,null,"WARATAH-DERBY","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WARATAH-DERBY (01)",0]
[926,null,"WARATAH-DERBY","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WARATAH-DERBY (01)",0]
[927,null,"WARATAH-DERBY","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WARATAH-DERBY (01)",0]
[928,null,"WARATAH-DERBY","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WARATAH-DERBY (01)",0]
[929,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (04)",7.0293828201883877E-5]
[930,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",7.0293828201883877E-5]
[931,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (02)",7.0293828201883877E-5]
[932,null,"HENDERSON-WILSON","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HENDERSON-WILSON (02)",7.0293828201883877E-5]
[933,null,"McEWEN-CURTIN","SBY-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","McEWEN-CURTIN (03)",7.0293828201883877E-5]
[934,null,"SOUDAN-HIGH","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","SOUDAN-HIGH (01)",0]
[935,null,"SOUTHERN-MEDWAY","ST0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","SOUTHERN-MEDWAY (02)",7.0293828201883877E-5]
[936,null,"SOUDAN-HIGH","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","SOUDAN-HIGH (01)",0]
[937,null,"SOUDAN-HIGH","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","SOUDAN-HIGH (01)",0]
[938,null,"SOUDAN-HIGH","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","SOUDAN-HIGH (01)",0]
[939,null,"SOUDAN-HIGH","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","SOUDAN-HIGH (01)",0]
[940,null,"WILLOWTREE-PERSICA","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (04)",7.0293828201883877E-5]
[941,null,"COPE-GAFFNEY","CS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","COPE-GAFFNEY (02)",7.0293828201883877E-5]
[942,null,"COPE-GAFFNEY","CS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","COPE-GAFFNEY (02)",7.0293828201883877E-5]
[943,null,"LEWIS-WILLIAMS","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",0]
[944,null,"LEWIS-WILLIAMS","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",0]
[945,null,"LEWIS-WILLIAMS","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",0]
[946,null,"LEWIS-WILLIAMS","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",0]
[947,null,"LEWIS-WILLIAMS","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",0]
[948,null,"LEWIS-WILLIAMS","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",0]
[949,null,"LEWIS-WILLIAMS","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",0]
[950,null,"LEWIS-WILLIAMS","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",0]
[951,null,"LEWIS-WILLIAMS","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",0]
[952,null,"LEWIS-WILLIAMS","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",0]
[953,null,"LEWIS-WILLIAMS","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",0]
[954,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[955,null,"QUINN-NOGA","AW0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","QUINN-NOGA (02)",7.0293828201883877E-5]
[956,null,"CRAMER-MARKET NO2","PTN-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","CRAMER-MARKET NO2 (01)",7.0293828201883877E-5]
[957,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (01)",7.0293828201883877E-5]
[958,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[959,null,"HOME-WILKINSON","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","HOME-WILKINSON (01)",0]
[960,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[961,null,"REYNARD-SPRINGHALL","CS0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",0]
[962,null,"BICENTENNIAL-SHABA","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","BICENTENNIAL-SHABA (02)",{"$f":"IF(H963=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[963,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[964,null,"WILLOWTREE-PERSICA","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (04)",7.0293828201883877E-5]
[965,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","BEAUMONT-WARATAH (04)",7.0293828201883877E-5]
[966,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[967,null,"NOVIAN-MARAMA","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","NOVIAN-MARAMA (03)",0]
[968,null,"NOVIAN-MARAMA","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","NOVIAN-MARAMA (03)",0]
[969,null,"CRANWELL-CARNARVON","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRANWELL-CARNARVON (03)",7.0293828201883877E-5]
[970,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (01)",7.0293828201883877E-5]
[971,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[972,null,"NOVIAN-MARAMA","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","NOVIAN-MARAMA (03)",0]
[973,null,"NOVIAN-MARAMA","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","NOVIAN-MARAMA (03)",0]
[974,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[975,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",7.0293828201883877E-5]
[976,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (02)",7.0293828201883877E-5]
[977,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUTLER-PASCOE VALE (01)",7.0293828201883877E-5]
[978,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","BEAUMONT-WARATAH (04)",0]
[979,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[980,null,"DEAKIN-BUCKLEY","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","DEAKIN-BUCKLEY (01)",7.0293828201883877E-5]
[981,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (01)",7.0293828201883877E-5]
[982,null,"DELAWARE-MENDIP","CN0-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","DELAWARE-MENDIP (01)",0]
[983,null,"CRAWFORD-ROBINSON","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (01)",7.0293828201883877E-5]
[984,null,"BEDWELL-HUGHES","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEDWELL-HUGHES (02)",7.0293828201883877E-5]
[985,null,"SEPARATION-SHIERS","FF0-093","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","SEPARATION-SHIERS (02)",7.0293828201883877E-5]
[986,null,"KILMORE-CHARLTON","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","KILMORE-CHARLTON (02)",7.0293828201883877E-5]
[987,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[988,null,"KALANG-PLUMPTON","PV0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","KALANG-PLUMPTON (02)",0]
[989,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[990,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[991,null,"GOULBURN-PALMERSTON","SHM-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","SHM","GOULBURN-PALMERSTON (04)",0]
[992,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (03)",7.0293828201883877E-5]
[993,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[994,null,"PETERSON-JACKSON","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","PETERSON-JACKSON (01)",7.0293828201883877E-5]
[995,null,"PETERSON-JACKSON","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","PETERSON-JACKSON (01)",7.0293828201883877E-5]
[996,null,"PETERSON-JACKSON","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","PETERSON-JACKSON (01)",7.0293828201883877E-5]
[997,null,"PETERSON-JACKSON","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","PETERSON-JACKSON (01)",7.0293828201883877E-5]
[998,null,"PETERSON-JACKSON","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","PETERSON-JACKSON (01)",7.0293828201883877E-5]
[999,null,"PETERSON-JACKSON","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","PETERSON-JACKSON (01)",7.0293828201883877E-5]
[1000,null,"PETERSON-JACKSON","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","PETERSON-JACKSON (01)",7.0293828201883877E-5]
[1001,null,"PETERSON-JACKSON","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","PETERSON-JACKSON (01)",7.0293828201883877E-5]
[1002,null,"PETERSON-JACKSON","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","PETERSON-JACKSON (01)",7.0293828201883877E-5]
[1003,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1004,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[1005,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[1006,null,"WHITTON-BOYNE","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","WHITTON-BOYNE (03)",7.0293828201883877E-5]
[1007,null,"WHITTON-BOYNE","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","WHITTON-BOYNE (03)",7.0293828201883877E-5]
[1008,null,"WHITTON-BOYNE","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","WHITTON-BOYNE (03)",7.0293828201883877E-5]
[1009,null,"WHITTON-BOYNE","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","WHITTON-BOYNE (03)",7.0293828201883877E-5]
[1010,null,"WHITTON-BOYNE","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","WHITTON-BOYNE (03)",7.0293828201883877E-5]
[1011,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1012,null,"MALCOLM-ELIZABETH","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","McGOWAN-MURRAY (02)",7.0293828201883877E-5]
[1013,null,"MALCOLM-ELIZABETH","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","McGOWAN-MURRAY (02)",7.0293828201883877E-5]
[1014,null,"MALCOLM-ELIZABETH","CN0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","McGOWAN-MURRAY (02)",7.0293828201883877E-5]
[1015,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (03)",7.0293828201883877E-5]
[1016,null,"MOUNT-BELL","CS0-003","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","MOUNT-BELL (01)",0]
[1017,null,"MALCOLM-ELIZABETH","CN0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","MALCOLM-ELIZABETH (02)",0]
[1018,null,"MALCOLM-ELIZABETH","CN0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","MALCOLM-ELIZABETH (02)",0]
[1019,null,"MALCOLM-ELIZABETH","CN0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","MALCOLM-ELIZABETH (02)",0]
[1020,null,"MALCOLM-ELIZABETH","CN0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","MALCOLM-ELIZABETH (02)",0]
[1021,null,"MALCOLM-ELIZABETH","CN0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","MALCOLM-ELIZABETH (02)",0]
[1022,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",7.0293828201883877E-5]
[1023,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (01)",7.0293828201883877E-5]
[1024,null,"BLIBURG-SUNSET","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","BLIBURG-SUNSET (02)",7.0293828201883877E-5]
[1025,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[1026,null,"LIVINGSTONE-ELIZABETH","CN0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","LIVINGSTONE-ELIZABETH (01)",{"$f":"IF(H1027=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1027,null,"ARTHUR-ELIZABETH","CN0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ARTHUR-ELIZABETH (01)",0]
[1028,null,"FAWKNER-BATMAN","ES0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","FAWKNER-BATMAN (02)",7.0293828201883877E-5]
[1029,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[1030,null,"EAST-HARDING","FT0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","EAST-HARDING (01)",7.0293828201883877E-5]
[1031,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[1032,null,"RYAN-MOORE","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","RYAN-MOORE (02)",7.0293828201883877E-5]
[1033,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (02)",7.0293828201883877E-5]
[1034,null,"DAVERN-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DAVERN-O'HEA (01)",0]
[1035,null,"DAVERN-O'HEA","CS0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","DAVERN-O'HEA (01)",7.0293828201883877E-5]
[1036,null,"DAVERN-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","CS0","DAVERN-O'HEA (01)",7.0293828201883877E-5]
[1037,null,"DAVERN-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","CS0","DAVERN-O'HEA (01)",7.0293828201883877E-5]
[1038,null,"DAVERN-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DAVERN-O'HEA (01)",0]
[1039,null,"DAVERN-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DAVERN-O'HEA (01)",0]
[1040,null,"DAVERN-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DAVERN-O'HEA (01)",0]
[1041,null,"DAVERN-O'HEA","CS0-002","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","CS0","DAVERN-O'HEA (01)",7.0293828201883877E-5]
[1042,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (01)",7.0293828201883877E-5]
[1043,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (01)",7.0293828201883877E-5]
[1044,null,"BENSON RD-P1","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","BENSON RD-P1 (00)",7.0293828201883877E-5]
[1045,null,"PARKER-AVOCA","PV0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","PARKER-AVOCA (01)",7.0293828201883877E-5]
[1046,null,"FOKKER-VICKERS","AW0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FOKKER-VICKERS (01)",7.0293828201883877E-5]
[1047,null,"GEELONG-MALDEN","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","GEELONG-MALDEN (02)",7.0293828201883877E-5]
[1048,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[1049,null,"LANGTON-GREENVALE","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","LANGTON-GREENVALE (02)",7.0293828201883877E-5]
[1050,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (03)",7.0293828201883877E-5]
[1051,null,"WINGATE-VASEY","FT0-026","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","WINGATE-VASEY (02)",7.0293828201883877E-5]
[1052,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (03)",7.0293828201883877E-5]
[1053,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[1054,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[1055,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (03)",7.0293828201883877E-5]
[1056,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[1057,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[1058,null,"OWEN-GORDON","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","Y","N","FE0","OWEN-GORDON (01)",7.0293828201883877E-5]
[1059,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (03)",7.0293828201883877E-5]
[1060,null,"DONALD-LAWSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",7.0293828201883877E-5]
[1061,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1062,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[1063,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[1064,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[1065,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[1066,null,"DIXON-DERBY","CN0-005","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","DIXON-DERBY (01)",7.0293828201883877E-5]
[1067,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[1068,null,"SALMON-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALMON-SCHOFIELD (02)",7.0293828201883877E-5]
[1069,null,"BIMBADEEN-YALLAMBIE","NH0-002","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",0]
[1070,null,"CUMBERLAND-KENT","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","CUMBERLAND-KENT (04)",0]
[1071,null,"CUMBERLAND-KENT","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","CUMBERLAND-KENT (04)",0]
[1072,null,"GLASS-NAPIER NO.2","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER NO.2 (02)",7.0293828201883877E-5]
[1073,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[1074,null,"QUINN-ST. JAMES","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","QUINN-ST. JAMES (01)",7.0293828201883877E-5]
[1075,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[1076,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[1077,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[1078,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[1079,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[1080,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[1081,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[1082,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[1083,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[1084,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NA",0]
[1085,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[1086,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",0]
[1087,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",0]
[1088,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",0]
[1089,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",0]
[1090,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",{"$f":"IF(H1091=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":0}]
[1091,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",0]
[1092,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",0]
[1093,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","ESSEX-LANDELLS (02)",0]
[1094,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",0]
[1095,null,"PASCOE VALE-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-MT ALEXANDER (04)",7.0293828201883877E-5]
[1096,null,"DIXON-DERBY","CN0-005","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","DIXON-DERBY (02)",7.0293828201883877E-5]
[1097,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",7.0293828201883877E-5]
[1098,null,"ANDERSON-BEVERLEY","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","ANDERSON-BEVERLEY (02)",7.0293828201883877E-5]
[1099,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","ALMA-PALMERSTON (02)",0]
[1100,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1101,null,"LANDELLS-MARTIN","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","LANDELLS-MARTIN (03)",0]
[1102,null,"LANDELLS-MARTIN","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","LANDELLS-MARTIN (03)",0]
[1103,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[1104,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (01)",7.0293828201883877E-5]
[1105,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (02)",7.0293828201883877E-5]
[1106,null,"ESSEX-DOWNS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-DOWNS (02)",0]
[1107,null,"ESSEX-DOWNS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-DOWNS (02)",0]
[1108,null,"BROADHURST-MCFADZEAN","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","OCONNOR-MACFADZEAN (02)",7.0293828201883877E-5]
[1109,null,"CUMBERLAND-KENT","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CUMBERLAND-KENT (04)",0]
[1110,null,"CUMBERLAND-KENT","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CUMBERLAND-KENT (04)",0]
[1111,null,"CUMBERLAND-KENT","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CUMBERLAND-KENT (04)",0]
[1112,null,"CUMBERLAND-KENT","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CUMBERLAND-KENT (04)",0]
[1113,null,"ALEXANDRA-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",0]
[1114,null,"ALEXANDRA-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",0]
[1115,null,"ALEXANDRA-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",0]
[1116,null,"ALEXANDRA-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",0]
[1117,null,"ALEXANDRA-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",0]
[1118,null,"ALEXANDRA-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",0]
[1119,null,"ALEXANDRA-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",0]
[1120,null,"ALEXANDRA-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",0]
[1121,null,"ALEXANDRA-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",0]
[1122,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1123,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1124,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1125,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1126,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1127,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1128,null,"CAMDON-NORTON","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","CAMDON-NORTON (02)",0]
[1129,null,"CAMDON-NORTON","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","CAMDON-NORTON (02)",0]
[1130,null,"CAMDON-NORTON","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","CAMDON-NORTON (03)",0]
[1131,null,"CAMDON-NORTON","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","CAMDON-NORTON (03)",0]
[1132,null,"CAMDON-NORTON","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","CAMDON-NORTON (03)",0]
[1133,null,"CAMDON-NORTON","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","CAMDON-NORTON (03)",0]
[1134,null,"CAMDON-NORTON","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","CAMDON-NORTON (03)",0]
[1135,null,"CAMDON-NORTON","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","CAMDON-NORTON (03)",0]
[1136,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (02)",0]
[1137,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1138,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1139,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1140,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1141,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1142,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1143,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1144,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1145,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1146,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1147,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1148,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1149,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1150,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",0]
[1151,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[1152,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[1153,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[1154,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",{"$f":"IF(H1155=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":0}]
[1155,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","CORNWALL-HIGH SCHOOL (03)",0]
[1156,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","CORNWALL-HIGH SCHOOL (03)",0]
[1157,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",7.0293828201883877E-5]
[1158,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",7.0293828201883877E-5]
[1159,null,"JOFFRE-KENT","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","JOFFRE-KENT (02)",0]
[1160,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[1161,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[1162,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[1163,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[1164,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[1165,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[1166,null,"NORTHUMBERLAND-FAWKNER","PV0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","NORTHUMBERLAND-FAWKNER (03)",7.0293828201883877E-5]
[1167,null,"NORTHUMBERLAND-FAWKNER","PV0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","NORTHUMBERLAND-FAWKNER (03)",7.0293828201883877E-5]
[1168,null,"YARCOMBE-WOKING","ST0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","YARCOMBE-WOKING (01)",7.0293828201883877E-5]
[1169,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (01)",7.0293828201883877E-5]
[1170,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[1171,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (01)",7.0293828201883877E-5]
[1172,null,"MERRICKS-ROSEBUD","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","MERRICKS-ROSEBUD (03)",7.0293828201883877E-5]
[1173,null,"WEBB-CORONATION","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","WEBB-CORONATION (03)",7.0293828201883877E-5]
[1174,null,"NEWTON-CREVELLI","NH0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","NEWTON-CREVELLI (02)",7.0293828201883877E-5]
[1175,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (03)",7.0293828201883877E-5]
[1176,null,"SPELLMAN-CECIL","SHM-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","SPELLMAN-CECIL (04)",7.0293828201883877E-5]
[1177,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[1178,null,"DALGETY-HIGH","PTN-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","PTN","DALGETY-HIGH (02)",0]
[1179,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (04)",7.0293828201883877E-5]
[1180,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (01)",7.0293828201883877E-5]
[1181,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (02)",7.0293828201883877E-5]
[1182,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[1183,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (01)",7.0293828201883877E-5]
[1184,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (05)",7.0293828201883877E-5]
[1185,null,"STEWART-OSBORNE","NT0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","STEWART-OSBORNE (01)",0]
[1186,null,"DONALD-LAWSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",7.0293828201883877E-5]
[1187,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (01)",7.0293828201883877E-5]
[1188,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[1189,null,"HOBBS-BROADHURST","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HOBBS-BROADHURST (01)",7.0293828201883877E-5]
[1190,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[1191,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[1192,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (01)",7.0293828201883877E-5]
[1193,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (03)",7.0293828201883877E-5]
[1194,null,"COLE-OSBORNE","NT0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","COLE-OSBORNE (04)",0]
[1195,null,"DOROTHY-ALEC","CN0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","DOROTHY-ALEC (01)",7.0293828201883877E-5]
[1196,null,"GLEN-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLEN-GLASS (03)",7.0293828201883877E-5]
[1197,null,"BEATRICE-FEHON","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","BEATRICE-FEHON (03)",7.0293828201883877E-5]
[1198,null,"NICHOLSON-BREWSTER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NICHOLSON-BREWSTER (01)",7.0293828201883877E-5]
[1199,null,"KILMORE-CHARLTON","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","KILMORE-CHARLTON (02)",7.0293828201883877E-5]
[1200,null,"FORREST-HUDSONS","YVE-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","YVE","FORREST-HUDSONS (04)",7.0293828201883877E-5]
[1201,null,"CENTREWAY-WINGARA","AW0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","CENTREWAY-WINGARA (03)",7.0293828201883877E-5]
[1202,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (01)",7.0293828201883877E-5]
[1203,null,"LANGDON-PETERLEE","ST0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","LANGDON-PETERLEE (02)",7.0293828201883877E-5]
[1204,null,"BUCKLEY-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-MT ALEXANDER (01)",7.0293828201883877E-5]
[1205,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[1206,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[1207,null,"MIMOSA-LAUREL","BD0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","MIMOSA-LAUREL (01)",7.0293828201883877E-5]
[1208,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (04)",7.0293828201883877E-5]
[1209,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (03)",7.0293828201883877E-5]
[1210,null,null,null,"2024-12-01","2024-12-07","Y","N","N","Y","N","N",null,"THE GLADE-SHERLOWE (01)",0]
[1211,null,"FREIGHT-CUSTOM","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (02)",7.0293828201883877E-5]
[1212,null,"COLLINS-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","OUTHWAITE-MCEWAN (03)",7.0293828201883877E-5]
[1213,null,"NORWOOD-PROSPECT","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","NORWOOD-PROSPECT (02)",7.0293828201883877E-5]
[1214,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",0]
[1215,null,"ROSS-ELIZABETH","NT0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NT0","ROSS-ELIZABETH (01)",7.0293828201883877E-5]
[1216,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[1217,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (02)",7.0293828201883877E-5]
[1218,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (01)",{"$f":"IF(H1219=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1219,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[1220,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[1221,null,"MONT ALBERT-RAINSFORD","BD0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","MONT ALBERT-RAINSFORD (01)",7.0293828201883877E-5]
[1222,null,"CHIFLEY 51-53-RAGLAN","EP0-035","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","CHIFLEY 51-53-RAGLAN (02)",7.0293828201883877E-5]
[1223,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[1224,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (02)",7.0293828201883877E-5]
[1225,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[1226,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1227,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[1228,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[1229,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[1230,null,"NICHOLSON-BREWSTER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NICHOLSON-BREWSTER (01)",7.0293828201883877E-5]
[1231,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[1232,null,"LAWSON-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LAWSON-SALISBURY (02)",7.0293828201883877E-5]
[1233,null,"MELON-CREMORNE","BY0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","MELON-CREMORNE (01)",7.0293828201883877E-5]
[1234,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (02)",7.0293828201883877E-5]
[1235,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (02)",7.0293828201883877E-5]
[1236,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[1237,null,"KELVIN-ALBERT","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KELVIN-ALBERT (01)",7.0293828201883877E-5]
[1238,null,"WILDWOOD RD N-P6","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","WILDWOOD RD N-P6 (00)",7.0293828201883877E-5]
[1239,null,"ESSEX-SWAN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","ESSEX-SWAN (01)",7.0293828201883877E-5]
[1240,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","ALMA-PALMERSTON (02)",0]
[1241,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",0]
[1242,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",0]
[1243,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",0]
[1244,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",0]
[1245,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",0]
[1246,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","ALMA-PALMERSTON (02)",0]
[1247,null,"SUFFOLK-DONGOLA","FW0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","SUFFOLK-DONGOLA (01)",0]
[1248,null,"ARGYLE-BROAD","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","ARGYLE-BROAD (01)",7.0293828201883877E-5]
[1249,null,"ARGYLE-BROAD","FW0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","ARGYLE-BROAD (01)",0]
[1250,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1251,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1252,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1253,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1254,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1255,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1256,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1257,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1258,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1259,null,"SUFFOLK-DONGOLA","FW0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","SUFFOLK-DONGOLA (02)",0]
[1260,null,"SUFFOLK-DONGOLA","FW0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","SUFFOLK-DONGOLA (02)",0]
[1261,null,"SUFFOLK-DONGOLA","FW0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","SUFFOLK-DONGOLA (02)",0]
[1262,null,"SUFFOLK-DONGOLA","FW0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","SUFFOLK-DONGOLA (02)",0]
[1263,null,"ALMA-ELPHINSTONE","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","ALMA-ELPHINSTONE (02)",7.0293828201883877E-5]
[1264,null,"ALMA-ELPHINSTONE","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","ALMA-ELPHINSTONE (02)",7.0293828201883877E-5]
[1265,null,"ALMA-ELPHINSTONE","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","ALMA-ELPHINSTONE (02)",7.0293828201883877E-5]
[1266,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1267,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1268,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1269,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1270,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1271,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1272,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1273,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1274,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1275,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1276,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1277,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1278,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1279,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1280,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1281,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1282,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",{"$f":"IF(H1283=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1283,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1284,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1285,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[1286,null,"GOVAN-STANLAKE","FW0-017","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","GOVAN-STANLAKE (02)",0]
[1287,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",0]
[1288,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",0]
[1289,null,"RICHELIEU-ESSEX","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","RICHELIEU-ESSEX (01)",7.0293828201883877E-5]
[1290,null,"NEWELL-MOORE","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","NEWELL-MOORE (02)",7.0293828201883877E-5]
[1291,null,"NEWELL-MOORE","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","NEWELL-MOORE (02)",7.0293828201883877E-5]
[1292,null,"NEWELL-MOORE","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","NEWELL-MOORE (02)",7.0293828201883877E-5]
[1293,null,"NEWELL-MOORE","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","NEWELL-MOORE (02)",7.0293828201883877E-5]
[1294,null,"NEWELL-MOORE","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","NEWELL-MOORE (02)",7.0293828201883877E-5]
[1295,null,"OWEN-GORDON","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","Y","N","FE0","OWEN-GORDON (01)",7.0293828201883877E-5]
[1296,null,"OWEN-GORDON","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","Y","N","FE0","OWEN-GORDON (01)",7.0293828201883877E-5]
[1297,null,"OWEN-GORDON","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","OWEN-GORDON (01)",7.0293828201883877E-5]
[1298,null,"OWEN-GORDON","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","OWEN-GORDON (01)",7.0293828201883877E-5]
[1299,null,"OWEN-GORDON","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","Y","N","FE0","OWEN-GORDON (01)",7.0293828201883877E-5]
[1300,null,"OWEN-GORDON","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","Y","N","FE0","OWEN-GORDON (01)",7.0293828201883877E-5]
[1301,null,"OWEN-GORDON","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","OWEN-GORDON (01)",7.0293828201883877E-5]
[1302,null,"OWEN-GORDON","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","OWEN-GORDON (01)",7.0293828201883877E-5]
[1303,null,"MACPHERSON-SHEPHERD","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","MACPHERSON-SHEPHERD (02)",7.0293828201883877E-5]
[1304,null,"MACPHERSON-SHEPHERD","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","MACPHERSON-SHEPHERD (02)",7.0293828201883877E-5]
[1305,null,"NEWELL-MOORE","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","NEWELL-MOORE (01)",7.0293828201883877E-5]
[1306,null,"PAISLEY 79-FRENCH","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","PAISLEY 79-FRENCH (01)",7.0293828201883877E-5]
[1307,null,"ANN-ERROL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","ANN-ERROL (04)",7.0293828201883877E-5]
[1308,null,"RYAN-MOORE","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","RYAN-MOORE (02)",7.0293828201883877E-5]
[1309,null,"RYAN-MOORE","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","RYAN-MOORE (02)",7.0293828201883877E-5]
[1310,null,"RYAN-MOORE","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","RYAN-MOORE (02)",7.0293828201883877E-5]
[1311,null,"RIPPON-HOADLEY","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","RIPPON-HOADLEY (02)",7.0293828201883877E-5]
[1312,null,"RIPPON-HOADLEY","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","RIPPON-HOADLEY (02)",7.0293828201883877E-5]
[1313,null,"RIPPON-HOADLEY","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","RIPPON-HOADLEY (02)",7.0293828201883877E-5]
[1314,null,"HAMILTON-O'FARRELL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (01)",7.0293828201883877E-5]
[1315,null,"ALEXANDER-JOHN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","ALEXANDER-JOHN (02)",7.0293828201883877E-5]
[1316,null,"ALEXANDER-JOHN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","ALEXANDER-JOHN (02)",7.0293828201883877E-5]
[1317,null,"ALEXANDER-JOHN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","DICKSON-WILLIAMSTOWN (03)",7.0293828201883877E-5]
[1318,null,"ALEXANDER-JOHN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","DICKSON-WILLIAMSTOWN (03)",7.0293828201883877E-5]
[1319,null,"ALEXANDER-JOHN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","DICKSON-WILLIAMSTOWN (03)",7.0293828201883877E-5]
[1320,null,"ALEXANDER-JOHN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","DICKSON-WILLIAMSTOWN (03)",7.0293828201883877E-5]
[1321,null,"ALEXANDER-JOHN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","DICKSON-WILLIAMSTOWN (03)",7.0293828201883877E-5]
[1322,null,"HAMILTON-O'FARRELL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (01)",7.0293828201883877E-5]
[1323,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (02)",7.0293828201883877E-5]
[1324,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (02)",7.0293828201883877E-5]
[1325,null,"ALEXANDER-JOHN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","ALEXANDER-JOHN (02)",7.0293828201883877E-5]
[1326,null,"STATION-GAMON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STATION-GAMON (02)",7.0293828201883877E-5]
[1327,null,"STATION-GAMON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STATION-GAMON (02)",7.0293828201883877E-5]
[1328,null,"STATION-GAMON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STATION-GAMON (02)",7.0293828201883877E-5]
[1329,null,"STATION-GAMON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STATION-GAMON (02)",7.0293828201883877E-5]
[1330,null,"BROWNING-GAMON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","BROWNING-GAMON (02)",7.0293828201883877E-5]
[1331,null,"BROWNING-GAMON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","BROWNING-GAMON (02)",7.0293828201883877E-5]
[1332,null,"STATION-GAMON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STATION-GAMON (02)",7.0293828201883877E-5]
[1333,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1334,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1335,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1336,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1337,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1338,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1339,null,"HAMILTON-O'FARRELL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",7.0293828201883877E-5]
[1340,null,"O'FARRELL-WILLIAMSTOWN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","O'FARRELL-WILLIAMSTOWN (02)",7.0293828201883877E-5]
[1341,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (02)",7.0293828201883877E-5]
[1342,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1343,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1344,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1345,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1346,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",{"$f":"IF(H1347=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1347,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1348,null,"WALTER-ARRAN 2","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","WALTER-ARRAN 2 (04)",7.0293828201883877E-5]
[1349,null,"ALEXANDER-JOHN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","ALEXANDER-JOHN (01)",7.0293828201883877E-5]
[1350,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (02)",7.0293828201883877E-5]
[1351,null,"NICHOLSON-LYONS","FE0-022","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FE0","NICHOLSON-LYONS (01)",0]
[1352,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (02)",7.0293828201883877E-5]
[1353,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (02)",7.0293828201883877E-5]
[1354,null,"STATION-GAMON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STATION-GAMON (02)",7.0293828201883877E-5]
[1355,null,"STATION-GAMON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STATION-GAMON (02)",7.0293828201883877E-5]
[1356,null,"GREIG-THOMSON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","GREIG-THOMSON (01)",7.0293828201883877E-5]
[1357,null,"GREIG-THOMSON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","GREIG-THOMSON (01)",7.0293828201883877E-5]
[1358,null,"GREIG-THOMSON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","GREIG-THOMSON (01)",7.0293828201883877E-5]
[1359,null,"GREIG-THOMSON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","GREIG-THOMSON (01)",7.0293828201883877E-5]
[1360,null,"O'FARRELL-WILLIAMSTOWN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","O'FARRELL-WILLIAMSTOWN (03)",7.0293828201883877E-5]
[1361,null,"ANDERSON-FEHON","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","ANDERSON-FEHON (02)",7.0293828201883877E-5]
[1362,null,"ANDERSON-FEHON","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","ANDERSON-FEHON (02)",7.0293828201883877E-5]
[1363,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (01)",7.0293828201883877E-5]
[1364,null,"BLACKWOOD-POWELL","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","BLACKWOOD-POWELL (03)",7.0293828201883877E-5]
[1365,null,"HAMILTON-O'FARRELL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",7.0293828201883877E-5]
[1366,null,"HAMILTON-O'FARRELL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",7.0293828201883877E-5]
[1367,null,"HAMILTON-O'FARRELL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",7.0293828201883877E-5]
[1368,null,"HAMILTON-O'FARRELL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",7.0293828201883877E-5]
[1369,null,"HAMILTON-O'FARRELL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",7.0293828201883877E-5]
[1370,null,"HAMILTON-O'FARRELL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",7.0293828201883877E-5]
[1371,null,"HYDE 258-KENT","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HYDE 258-KENT (02)",7.0293828201883877E-5]
[1372,null,"HYDE 258-KENT","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HYDE 258-KENT (02)",7.0293828201883877E-5]
[1373,null,"YORK-HYDE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","YORK-HYDE (02)",7.0293828201883877E-5]
[1374,null,"LENNOX-HYDE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","LENNOX-HYDE (03)",7.0293828201883877E-5]
[1375,null,"LENNOX-HYDE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","LENNOX-HYDE (03)",7.0293828201883877E-5]
[1376,null,"LENNOX-HYDE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","LENNOX-HYDE (03)",7.0293828201883877E-5]
[1377,null,"LENNOX-HYDE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","LENNOX-HYDE (03)",7.0293828201883877E-5]
[1378,null,"LENNOX-HYDE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","LENNOX-HYDE (03)",7.0293828201883877E-5]
[1379,null,"LENNOX-HYDE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","LENNOX-HYDE (03)",7.0293828201883877E-5]
[1380,null,"HAMILTON-O'FARRELL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",7.0293828201883877E-5]
[1381,null,"HAMILTON-O'FARRELL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",7.0293828201883877E-5]
[1382,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (02)",7.0293828201883877E-5]
[1383,null,"TONGUE-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","TONGUE-MACKAY (02)",7.0293828201883877E-5]
[1384,null,"TONGUE-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","TONGUE-MACKAY (02)",7.0293828201883877E-5]
[1385,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (01)",7.0293828201883877E-5]
[1386,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (01)",7.0293828201883877E-5]
[1387,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (01)",7.0293828201883877E-5]
[1388,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (01)",7.0293828201883877E-5]
[1389,null,"LENNOX-HYDE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","LENNOX-HYDE (03)",7.0293828201883877E-5]
[1390,null,"LENNOX-HYDE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","LENNOX-HYDE (03)",7.0293828201883877E-5]
[1391,null,"TONGUE-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","TONGUE-MACKAY (02)",7.0293828201883877E-5]
[1392,null,"TONGUE-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","TONGUE-MACKAY (02)",7.0293828201883877E-5]
[1393,null,"TONGUE-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","TONGUE-MACKAY (02)",7.0293828201883877E-5]
[1394,null,"TONGUE-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","TONGUE-MACKAY (02)",7.0293828201883877E-5]
[1395,null,"TONGUE-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","TONGUE-MACKAY (02)",7.0293828201883877E-5]
[1396,null,"TONGUE-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","TONGUE-MACKAY (02)",7.0293828201883877E-5]
[1397,null,"TONGUE-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","TONGUE-MACKAY (02)",7.0293828201883877E-5]
[1398,null,"EDGAR-SOMERVILLE","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","EDGAR-SOMERVILLE (02)",7.0293828201883877E-5]
[1399,null,"NEYLON-ROBERTS","FW0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","NEYLON-ROBERTS (02)",7.0293828201883877E-5]
[1400,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[1401,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[1402,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[1403,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[1404,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[1405,null,"GEELONG-QUEENSVILLE","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","GEELONG-QUEENSVILLE (01)",7.0293828201883877E-5]
[1406,null,"GEELONG-QUEENSVILLE","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","GEELONG-QUEENSVILLE (01)",7.0293828201883877E-5]
[1407,null,"WEBB-CORONATION","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","WEBB-CORONATION (04)",7.0293828201883877E-5]
[1408,null,"WEBB-CORONATION","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","WEBB-CORONATION (04)",7.0293828201883877E-5]
[1409,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (01)",7.0293828201883877E-5]
[1410,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",{"$f":"IF(H1411=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1411,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[1412,null,"WEBB-CORONATION","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","WEBB-CORONATION (03)",7.0293828201883877E-5]
[1413,null,"WEBB-CORONATION","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","WEBB-CORONATION (03)",7.0293828201883877E-5]
[1414,null,"WEBB-CORONATION","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","WEBB-CORONATION (03)",7.0293828201883877E-5]
[1415,null,"WEBB-CORONATION","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","WEBB-CORONATION (03)",7.0293828201883877E-5]
[1416,null,"WEBB-CORONATION","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","WEBB-CORONATION (03)",7.0293828201883877E-5]
[1417,null,"WEBB-CORONATION","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","WEBB-CORONATION (03)",7.0293828201883877E-5]
[1418,null,"HAWKHURST-FRANCIS","FW0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","HAWKHURST-FRANCIS (01)",7.0293828201883877E-5]
[1419,null,"HAWKHURST-FRANCIS","FW0-013","2024-12-01","2024-12-07","Y","Y","Y","Y","N","N","FW0","HAWKHURST-FRANCIS (01)",7.0293828201883877E-5]
[1420,null,"HAWKHURST-FRANCIS","FW0-013","2024-12-01","2024-12-07","Y","Y","Y","Y","N","N","FW0","HAWKHURST-FRANCIS (01)",7.0293828201883877E-5]
[1421,null,"HAWKHURST-FRANCIS","FW0-013","2024-12-01","2024-12-07","Y","Y","Y","Y","N","N","FW0","HAWKHURST-FRANCIS (01)",7.0293828201883877E-5]
[1422,null,"HAWKHURST-FRANCIS","FW0-013","2024-12-01","2024-12-07","Y","Y","Y","Y","N","N","FW0","HAWKHURST-FRANCIS (01)",7.0293828201883877E-5]
[1423,null,"HAWKHURST-FRANCIS","FW0-013","2024-12-01","2024-12-07","Y","Y","Y","Y","N","N","FW0","HAWKHURST-FRANCIS (01)",7.0293828201883877E-5]
[1424,null,"HAWKHURST-FRANCIS","FW0-013","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","FW0","HAWKHURST-FRANCIS (01)",7.0293828201883877E-5]
[1425,null,"HAWKHURST-FRANCIS","FW0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","HAWKHURST-FRANCIS (01)",0]
[1426,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","BEAUMONT-WARATAH (04)",0]
[1427,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","N","Y","N","FW0","BEAUMONT-WARATAH (04)",0]
[1428,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","BEAUMONT-WARATAH (04)",7.0293828201883877E-5]
[1429,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","BEAUMONT-WARATAH (04)",0]
[1430,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","BEAUMONT-WARATAH (04)",0]
[1431,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","N","Y","N","FW0","BEAUMONT-WARATAH (04)",0]
[1432,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","BEAUMONT-WARATAH (04)",7.0293828201883877E-5]
[1433,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","BEAUMONT-WARATAH (04)",7.0293828201883877E-5]
[1434,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","BEAUMONT-WARATAH (04)",7.0293828201883877E-5]
[1435,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","N","Y","N","FW0","BEAUMONT-WARATAH (04)",0]
[1436,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","BEAUMONT-WARATAH (04)",7.0293828201883877E-5]
[1437,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","N","Y","N","FW0","BEAUMONT-WARATAH (04)",0]
[1438,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","BEAUMONT-WARATAH (04)",0]
[1439,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[1440,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[1441,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[1442,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[1443,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[1444,null,"BEAUMONT-ROBERTS","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","BEAUMONT-ROBERTS (01)",7.0293828201883877E-5]
[1445,null,"WATT-THE AVENUE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","WATT-THE AVENUE (04)",7.0293828201883877E-5]
[1446,null,"NEYLON-ROBERTS","FW0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","NEYLON-ROBERTS (02)",0]
[1447,null,"CALA-HAMPTON","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","CALA-HAMPTON (01)",7.0293828201883877E-5]
[1448,null,"CALA-HAMPTON","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","CALA-HAMPTON (01)",7.0293828201883877E-5]
[1449,null,"CALA-HAMPTON","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","CALA-HAMPTON (01)",7.0293828201883877E-5]
[1450,null,"CALA-HAMPTON","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","CALA-HAMPTON (01)",7.0293828201883877E-5]
[1451,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (01)",7.0293828201883877E-5]
[1452,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (01)",7.0293828201883877E-5]
[1453,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (01)",7.0293828201883877E-5]
[1454,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","NA",7.0293828201883877E-5]
[1455,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[1456,null,"MARYSTON-SOMERVILLE","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","MARYSTON-SOMERVILLE (01)",7.0293828201883877E-5]
[1457,null,"MARYSTON-SOMERVILLE","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","MARYSTON-SOMERVILLE (01)",7.0293828201883877E-5]
[1458,null,"AUSTIN-SEVERN","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","AUSTIN-SEVERN (02)",7.0293828201883877E-5]
[1459,null,"AUSTIN-SEVERN","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","AUSTIN-SEVERN (02)",7.0293828201883877E-5]
[1460,null,"ALOHA-GREENE","FW0-005","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","ALOHA-GREENE (04)",7.0293828201883877E-5]
[1461,null,"WATT-THE AVENUE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","WATT-THE AVENUE (04)",7.0293828201883877E-5]
[1462,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1463,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1464,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","BEAUMONT-WARATAH (04)",7.0293828201883877E-5]
[1465,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","BEAUMONT-WARATAH (04)",0]
[1466,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","BEAUMONT-WARATAH (04)",0]
[1467,null,"BEAUMONT-WARATAH","FW0-016","2024-12-01","2024-12-07","Y","N","N","N","Y","N","FW0","BEAUMONT-WARATAH (04)",0]
[1468,null,"ALMOND-CONIFER","FW0-006","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","ALMOND-CONIFER (01)",0]
[1469,null,"CONIFER-PRIMULA","FW0-006","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","ALMOND-CONIFER (01)",0]
[1470,null,"HAWKHURST-FRANCIS","FW0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","HAWKHURST-FRANCIS (01)",0]
[1471,null,"ROSAMOND-RIVER","BY0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","ROSAMOND-RIVER (02)",7.0293828201883877E-5]
[1472,null,"OMAR-MITCHELL","BY0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","OMAR-MITCHELL (01)",7.0293828201883877E-5]
[1473,null,"BOSQUET-BALLARAT","BY0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","BOSQUET-BALLARAT (02)",7.0293828201883877E-5]
[1474,null,"MADDEN-STUDLEY","FW0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","MADDEN-STUDLEY (02)",{"$f":"IF(H1475=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1475,null,"MADDEN-STUDLEY","FW0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","MADDEN-STUDLEY (02)",7.0293828201883877E-5]
[1476,null,"MADDEN-STUDLEY","FW0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","MADDEN-STUDLEY (01)",7.0293828201883877E-5]
[1477,null,"SOUTH-BEACHLEY","TH0-022","2024-12-01","2024-12-07","Y","N","N","Y","N","N","TH0","SOUTH-BEACHLEY (02)",0]
[1478,null,"HAMPDEN-CROTHERS","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",7.0293828201883877E-5]
[1479,null,"HAMPDEN-CROTHERS","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",7.0293828201883877E-5]
[1480,null,"HAMPDEN-CROTHERS","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",7.0293828201883877E-5]
[1481,null,"HAMPDEN-CROTHERS","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",7.0293828201883877E-5]
[1482,null,"HAMPDEN-CROTHERS","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",7.0293828201883877E-5]
[1483,null,"MELON-CREMORNE","BY0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","MELON-CREMORNE (01)",7.0293828201883877E-5]
[1484,null,"VINE-SHEPHERD","BY0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","VINE-SHEPHERD (03)",7.0293828201883877E-5]
[1485,null,"RALEIGH-CHIFLEY","YVE-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","YVE","RALEIGH-CHIFLEY (01)",7.0293828201883877E-5]
[1486,null,"PAISLEY 79-FRENCH","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","PAISLEY 79-FRENCH (01)",7.0293828201883877E-5]
[1487,null,"PAISLEY 79-FRENCH","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","PAISLEY 79-FRENCH (01)",7.0293828201883877E-5]
[1488,null,"PAISLEY 79-FRENCH","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","PAISLEY 79-FRENCH (01)",7.0293828201883877E-5]
[1489,null,"PAISLEY 79-FRENCH","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","PAISLEY 79-FRENCH (01)",7.0293828201883877E-5]
[1490,null,"OWEN-GORDON","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","Y","N","FE0","OWEN-GORDON (01)",7.0293828201883877E-5]
[1491,null,"KELLAWAY-GORDON","BY0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","KELLAWAY-GORDON (01)",7.0293828201883877E-5]
[1492,null,"KELLAWAY-GORDON","BY0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","KELLAWAY-GORDON (01)",7.0293828201883877E-5]
[1493,null,"SUFFOLK-DONGOLA","FW0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","SUFFOLK-DONGOLA (02)",0]
[1494,null,"MADDEN-STUDLEY","FW0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","MADDEN-STUDLEY (02)",7.0293828201883877E-5]
[1495,null,"PAISLEY 79-FRENCH","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","PAISLEY 79-FRENCH (01)",7.0293828201883877E-5]
[1496,null,"PAISLEY 79-FRENCH","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","PAISLEY 79-FRENCH (01)",7.0293828201883877E-5]
[1497,null,"GEELONG-OLD GEELONG","TH0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","TH0","GEELONG-OLD GEELONG (01)",0]
[1498,null,"VICTORIA-SOMERVILLE 3","TH0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","VICTORIA-SOMERVILLE 3 (00)",7.0293828201883877E-5]
[1499,null,"JAMES-INDUSTRIAL GARDENS","TH0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","JAMES-INDUSTRIAL GARDENS (02)",7.0293828201883877E-5]
[1500,null,"JAMES-INDUSTRIAL GARDENS","TH0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","JAMES-INDUSTRIAL GARDENS (02)",7.0293828201883877E-5]
[1501,null,"OMAR-MITCHELL","BY0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","OMAR-MITCHELL (02)",7.0293828201883877E-5]
[1502,null,"OMAR-MITCHELL","BY0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","OMAR-MITCHELL (02)",7.0293828201883877E-5]
[1503,null,"MELON-CREMORNE","BY0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","MELON-CREMORNE (01)",7.0293828201883877E-5]
[1504,null,"ESSEX-SWAN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","ESSEX-SWAN (01)",7.0293828201883877E-5]
[1505,null,"HYDE-BRISTOW","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HYDE-BRISTOW (02)",7.0293828201883877E-5]
[1506,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[1507,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (02)",7.0293828201883877E-5]
[1508,null,"WINGATE-VASEY","FT0-026","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","WINGATE-VASEY (02)",7.0293828201883877E-5]
[1509,null,"BRASSEY-PYALONG","NH0-020","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NH0","BRASSEY-PYALONG (01)",0]
[1510,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[1511,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (01)",7.0293828201883877E-5]
[1512,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (03)",7.0293828201883877E-5]
[1513,null,"THE BOULEVARD-NEVILLE","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","THE BOULEVARD-NEVILLE (02)",7.0293828201883877E-5]
[1514,null,"EAGLEMONT-THE RIGHI","HB0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","EAGLEMONT-THE RIGHI (02)",7.0293828201883877E-5]
[1515,null,"THE EYRIE-LAWRENCE","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","THE EYRIE-LAWRENCE (02)",7.0293828201883877E-5]
[1516,null,"MALTRAVERS-LOWER HEIDELBERG","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","MALTRAVERS-LOWER HEIDELBERG (02)",7.0293828201883877E-5]
[1517,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",0]
[1518,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",0]
[1519,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[1520,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[1521,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[1522,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[1523,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LANTANA-IVANHOE (01)",7.0293828201883877E-5]
[1524,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LANTANA-IVANHOE (01)",7.0293828201883877E-5]
[1525,null,"LANTANA-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LANTANA-IVANHOE (01)",7.0293828201883877E-5]
[1526,null,"BANKSIA-OSNEY","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BANKSIA-OSNEY (01)",7.0293828201883877E-5]
[1527,null,"BANKSIA-OSNEY","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BANKSIA-OSNEY (01)",7.0293828201883877E-5]
[1528,null,"BANKSIA-OSNEY","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BANKSIA-OSNEY (01)",7.0293828201883877E-5]
[1529,null,"BANKSIA-OSNEY","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BANKSIA-OSNEY (01)",7.0293828201883877E-5]
[1530,null,"BANKSIA-OSNEY","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BANKSIA-OSNEY (01)",7.0293828201883877E-5]
[1531,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1532,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",0]
[1533,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1534,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1535,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1536,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1537,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",0]
[1538,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",{"$f":"IF(H1539=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1539,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",0]
[1540,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1541,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1542,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1543,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1544,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1545,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1546,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1547,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1548,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1549,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1550,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1551,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1552,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1553,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1554,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1555,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",0]
[1556,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1557,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1558,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",0]
[1559,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",0]
[1560,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",0]
[1561,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1562,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1563,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",0]
[1564,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","Y","N","N","EP0","MELCOMBE-BANKSIA (02)",0]
[1565,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1566,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1567,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1568,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1569,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1570,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1571,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (02)",7.0293828201883877E-5]
[1572,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (02)",7.0293828201883877E-5]
[1573,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (02)",7.0293828201883877E-5]
[1574,null,"LANTANA-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","LANTANA-IVANHOE (01)",0]
[1575,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (02)",7.0293828201883877E-5]
[1576,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (02)",7.0293828201883877E-5]
[1577,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[1578,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1579,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[1580,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[1581,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[1582,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1583,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[1584,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1585,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1586,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1587,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1588,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1589,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1590,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1591,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1592,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1593,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1594,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[1595,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1596,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[1597,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[1598,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (02)",7.0293828201883877E-5]
[1599,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (02)",7.0293828201883877E-5]
[1600,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (02)",7.0293828201883877E-5]
[1601,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (02)",7.0293828201883877E-5]
[1602,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (01)",{"$f":"IF(H1603=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1603,null,"CLIFTON-WATERDALE","HB0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","CLIFTON-WATERDALE (01)",7.0293828201883877E-5]
[1604,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (02)",7.0293828201883877E-5]
[1605,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (02)",7.0293828201883877E-5]
[1606,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",7.0293828201883877E-5]
[1607,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",7.0293828201883877E-5]
[1608,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (02)",7.0293828201883877E-5]
[1609,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (01)",7.0293828201883877E-5]
[1610,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (02)",7.0293828201883877E-5]
[1611,null,"JELLICOE-WATERDALE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","JELLICOE-WATERDALE (02)",0]
[1612,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1613,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1614,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1615,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1616,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1617,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (02)",7.0293828201883877E-5]
[1618,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1619,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1620,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (02)",7.0293828201883877E-5]
[1621,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (02)",7.0293828201883877E-5]
[1622,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1623,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1624,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1625,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1626,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1627,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1628,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1629,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1630,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1631,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1632,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1633,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1634,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1635,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1636,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",0]
[1637,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",0]
[1638,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",0]
[1639,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",0]
[1640,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1641,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1642,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1643,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1644,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1645,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1646,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1647,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1648,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1649,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1650,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1651,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",7.0293828201883877E-5]
[1652,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",0]
[1653,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",7.0293828201883877E-5]
[1654,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",7.0293828201883877E-5]
[1655,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",7.0293828201883877E-5]
[1656,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",7.0293828201883877E-5]
[1657,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",7.0293828201883877E-5]
[1658,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1659,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1660,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1661,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1662,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1663,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1664,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1665,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1666,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",{"$f":"IF(H1667=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1667,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1668,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1669,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1670,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1671,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1672,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1673,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1674,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1675,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1676,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1677,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[1678,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (01)",7.0293828201883877E-5]
[1679,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (01)",7.0293828201883877E-5]
[1680,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (01)",7.0293828201883877E-5]
[1681,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (01)",7.0293828201883877E-5]
[1682,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (01)",7.0293828201883877E-5]
[1683,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1684,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1685,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1686,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1687,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1688,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1689,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1690,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1691,null,"HAWKER-COOK","EP0-034","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","HAWKER-COOK (02)",0]
[1692,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (02)",7.0293828201883877E-5]
[1693,null,"HAWKER-COOK","EP0-034","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","HAWKER-COOK (02)",0]
[1694,null,"HAWKER-COOK","EP0-034","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","HAWKER-COOK (02)",0]
[1695,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[1696,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[1697,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[1698,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[1699,null,"HAWKER-COOK","EP0-034","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","HAWKER-COOK (02)",0]
[1700,null,"HAWKER-COOK","EP0-034","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","HAWKER-COOK (02)",0]
[1701,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1702,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1703,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1704,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1705,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (01)",7.0293828201883877E-5]
[1706,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (01)",7.0293828201883877E-5]
[1707,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (01)",7.0293828201883877E-5]
[1708,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (01)",7.0293828201883877E-5]
[1709,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1710,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1711,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1712,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1713,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1714,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1715,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NA",7.0293828201883877E-5]
[1716,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1717,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1718,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[1719,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[1720,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[1721,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[1722,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[1723,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[1724,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NA",7.0293828201883877E-5]
[1725,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[1726,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[1727,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1728,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1729,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1730,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",{"$f":"IF(H1731=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1731,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1732,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1733,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1734,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1735,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1736,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1737,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NA",7.0293828201883877E-5]
[1738,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1739,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1740,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1741,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1742,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1743,null,"BANKSIA-OSNEY","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BANKSIA-OSNEY (01)",7.0293828201883877E-5]
[1744,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1745,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1746,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1747,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1748,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1749,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[1750,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1751,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1752,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1753,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1754,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[1755,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1756,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1757,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[1758,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1759,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1760,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1761,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1762,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1763,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[1764,null,"HAWKER-COOK","EP0-034","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","HAWKER-COOK (02)",0]
[1765,null,"HAWKER-COOK","EP0-034","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","HAWKER-COOK (02)",0]
[1766,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (02)",7.0293828201883877E-5]
[1767,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (02)",7.0293828201883877E-5]
[1768,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NA",7.0293828201883877E-5]
[1769,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (04)",7.0293828201883877E-5]
[1770,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (04)",7.0293828201883877E-5]
[1771,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (04)",7.0293828201883877E-5]
[1772,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[1773,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[1774,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1775,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1776,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1777,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1778,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[1779,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[1780,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[1781,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[1782,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[1783,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[1784,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (04)",7.0293828201883877E-5]
[1785,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (04)",7.0293828201883877E-5]
[1786,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (04)",7.0293828201883877E-5]
[1787,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (02)",7.0293828201883877E-5]
[1788,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (02)",7.0293828201883877E-5]
[1789,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1790,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1791,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1792,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1793,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1794,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",{"$f":"IF(H1795=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1795,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1796,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1797,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1798,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1799,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NA",7.0293828201883877E-5]
[1800,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1801,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1802,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1803,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (04)",7.0293828201883877E-5]
[1804,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (02)",7.0293828201883877E-5]
[1805,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1806,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1807,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1808,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1809,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1810,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1811,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1812,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1813,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1814,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1815,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1816,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1817,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (00)",7.0293828201883877E-5]
[1818,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1819,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1820,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1821,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1822,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[1823,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1824,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1825,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1826,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1827,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1828,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1829,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1830,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1831,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[1832,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","Y","Y","Y","Y","N","N","EP0","NA",7.0293828201883877E-5]
[1833,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1834,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (02)",7.0293828201883877E-5]
[1835,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","EP0","NA",7.0293828201883877E-5]
[1836,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1837,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1838,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1839,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1840,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1841,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (03)",7.0293828201883877E-5]
[1842,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (03)",7.0293828201883877E-5]
[1843,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (03)",7.0293828201883877E-5]
[1844,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (03)",7.0293828201883877E-5]
[1845,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1846,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (03)",7.0293828201883877E-5]
[1847,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (03)",7.0293828201883877E-5]
[1848,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (03)",7.0293828201883877E-5]
[1849,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1850,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1851,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1852,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1853,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1854,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1855,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1856,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (02)",7.0293828201883877E-5]
[1857,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1858,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",{"$f":"IF(H1859=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1859,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1860,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1861,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1862,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1863,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1864,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1865,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1866,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1867,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1868,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1869,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1870,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1871,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1872,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1873,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1874,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1875,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1876,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1877,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1878,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1879,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1880,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1881,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1882,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[1883,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1884,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1885,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1886,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1887,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1888,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1889,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1890,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1891,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1892,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1893,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1894,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1895,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1896,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1897,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1898,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1899,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[1900,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (02)",7.0293828201883877E-5]
[1901,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (02)",7.0293828201883877E-5]
[1902,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1903,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1904,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1905,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1906,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1907,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1908,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1909,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1910,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1911,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1912,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (02)",7.0293828201883877E-5]
[1913,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (02)",7.0293828201883877E-5]
[1914,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1915,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1916,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1917,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1918,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1919,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1920,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1921,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1922,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",{"$f":"IF(H1923=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[1923,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1924,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1925,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1926,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1927,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1928,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[1929,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NA",7.0293828201883877E-5]
[1930,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (02)",7.0293828201883877E-5]
[1931,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (02)",7.0293828201883877E-5]
[1932,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (02)",7.0293828201883877E-5]
[1933,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1934,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (02)",7.0293828201883877E-5]
[1935,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1936,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1937,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1938,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1939,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1940,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1941,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[1942,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (01)",7.0293828201883877E-5]
[1943,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (01)",7.0293828201883877E-5]
[1944,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (01)",7.0293828201883877E-5]
[1945,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (01)",7.0293828201883877E-5]
[1946,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (01)",7.0293828201883877E-5]
[1947,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (01)",7.0293828201883877E-5]
[1948,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (01)",7.0293828201883877E-5]
[1949,null,"BUCHANAN-SALISBURY","HB0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","BUCHANAN-SALISBURY (02)",7.0293828201883877E-5]
[1950,null,"BUCHANAN-SALISBURY","HB0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","BUCHANAN-SALISBURY (01)",7.0293828201883877E-5]
[1951,null,"BUCHANAN-SALISBURY","HB0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","BUCHANAN-SALISBURY (01)",7.0293828201883877E-5]
[1952,null,"PINE-MARSHALL","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","PINE-MARSHALL (02)",7.0293828201883877E-5]
[1953,null,"MARSHALL-TOORA","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","MARSHALL-TOORA (02)",7.0293828201883877E-5]
[1954,null,"MARSHALL-TOORA","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","MARSHALL-TOORA (02)",7.0293828201883877E-5]
[1955,null,"MARSHALL-TOORA","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","MARSHALL-TOORA (02)",7.0293828201883877E-5]
[1956,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","YOUNG-LOWER HEIDELBERG (02)",7.0293828201883877E-5]
[1957,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (01)",7.0293828201883877E-5]
[1958,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (01)",7.0293828201883877E-5]
[1959,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1960,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1961,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1962,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1963,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1964,null,"RUSSELL-PINE","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RUSSELL-PINE (02)",7.0293828201883877E-5]
[1965,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1966,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1967,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1968,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1969,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1970,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1971,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1972,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1973,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[1974,null,"CHARTERIS-BURKE","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","CHARTERIS-BURKE (01)",7.0293828201883877E-5]
[1975,null,"WILFRED-LOWER HEIDELBERG","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","WILFRED-LOWER HEIDELBERG (02)",7.0293828201883877E-5]
[1976,null,"CHARTERIS-WARNCLIFFE","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","CHARTERIS-WARNCLIFFE (02)",7.0293828201883877E-5]
[1977,null,"CHARTERIS-WARNCLIFFE","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","CHARTERIS-WARNCLIFFE (02)",7.0293828201883877E-5]
[1978,null,"CHARTERIS-WARNCLIFFE","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","CHARTERIS-WARNCLIFFE (02)",7.0293828201883877E-5]
[1979,null,"WILFRED-CEDRIC","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","WILFRED-CEDRIC (02)",7.0293828201883877E-5]
[1980,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[1981,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[1982,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[1983,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[1984,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[1985,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[1986,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",{"$f":"IF(H1987=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":0}]
[1987,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[1988,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[1989,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[1990,null,"COLLINS-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","DOUGHARTY-MARKS (01)",7.0293828201883877E-5]
[1991,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1992,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1993,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1994,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1995,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1996,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1997,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1998,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[1999,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[2003,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[2008,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[2016,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[2021,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[2029,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[2037,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[2042,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[2050,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",{"$f":"IF(H2051=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[2055,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (03)",7.0293828201883877E-5]
[2063,null,"WILKINSON-LIBERTY","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","WILKINSON-LIBERTY (02)",0]
[2071,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (03)",7.0293828201883877E-5]
[2076,null,"WILKINSON-LIBERTY","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","WILKINSON-LIBERTY (02)",0]
[2084,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (03)",7.0293828201883877E-5]
[2092,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (02)",7.0293828201883877E-5]
[2097,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[2105,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[2117,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[2118,null,"ALAMEIN-SOUTHERN","EPN-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALAMEIN-SOUTHERN (03)",7.0293828201883877E-5]
[2126,null,"BELL-ORIEL","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BELL-ORIEL (01)",7.0293828201883877E-5]
[2138,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",7.0293828201883877E-5]
[2139,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","NA",7.0293828201883877E-5]
[2146,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","NA",7.0293828201883877E-5]
[2158,null,"COLLINS-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","OUTHWAITE-MCEWAN (04)",7.0293828201883877E-5]
[2159,null,"COLLINS-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","OUTHWAITE-MCEWAN (04)",7.0293828201883877E-5]
[2171,null,"SEPARATION-FULHAM","FF0-093","2024-12-01","2024-12-07","Y","N","N","N","N","N","FF0","SEPARATION-FULHAM (01)",0]
[2179,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[2180,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[2192,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[2200,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[2205,null,"SEPARATION-FULHAM","FF0-093","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","SEPARATION-FULHAM (01)",7.0293828201883877E-5]
[2213,null,"MALTRAVERS-LOWER HEIDELBERG","HB0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","MALTRAVERS-LOWER HEIDELBERG (02)",7.0293828201883877E-5]
[2221,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (01)",7.0293828201883877E-5]
[2226,null,"DAVIDSON-PERKINS","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAVIDSON-PERKINS (01)",7.0293828201883877E-5]
[2234,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (02)",7.0293828201883877E-5]
[2242,null,"DAVIDSON-PERKINS","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAVIDSON-PERKINS (01)",{"$f":"IF(H2243=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[2247,null,"WATERDALE-GRIFFITHS","EPN-033","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","WATERDALE-GRIFFITHS (01)",0]
[2255,null,"ALPHINGTON-PARK","FF0-088","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","ALPHINGTON-PARK (02)",7.0293828201883877E-5]
[2260,null,"ALPHINGTON-PARK","FF0-088","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","ALPHINGTON-PARK (02)",7.0293828201883877E-5]
[2268,null,"ALPHINGTON-PARK","FF0-088","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","ALPHINGTON-PARK (02)",7.0293828201883877E-5]
[2276,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[2281,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (01)",7.0293828201883877E-5]
[2289,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (02)",7.0293828201883877E-5]
[2294,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (02)",7.0293828201883877E-5]
[2301,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (02)",7.0293828201883877E-5]
[2309,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (03)",7.0293828201883877E-5]
[2314,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",0]
[2322,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[2330,null,"GRENHILDA-DOUGLAS","NH0-020","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","GRENHILDA-DOUGLAS (02)",0]
[2335,null,"GRENHILDA-DOUGLAS","NH0-020","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NH0","GRENHILDA-DOUGLAS (02)",0]
[2343,null,"DORSET-BERKELEY","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","DORSET-BERKELEY (01)",7.0293828201883877E-5]
[2348,null,"BEVERLEY-GREVILLE","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","BEVERLEY-GREVILLE (02)",7.0293828201883877E-5]
[2356,null,"QUINN-ST. JAMES","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","QUINN-ST. JAMES (01)",7.0293828201883877E-5]
[2364,null,"ANDERSON-BEVERLEY","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","ANDERSON-BEVERLEY (03)",7.0293828201883877E-5]
[2369,null,"ANDERSON-BEVERLEY","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","ANDERSON-BEVERLEY (03)",7.0293828201883877E-5]
[2377,null,"HAUGHTON-GREVILLE","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","HAUGHTON-GREVILLE (02)",7.0293828201883877E-5]
[2382,null,"BEETHAM-PROSPECT","NH0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","BEETHAM-PROSPECT (02)",0]
[2390,null,"INVERMAY-BELLEVUE","NH0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","INVERMAY-BELLEVUE (01)",0]
[2398,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (02)",7.0293828201883877E-5]
[2403,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",7.0293828201883877E-5]
[2411,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (02)",7.0293828201883877E-5]
[2419,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[2424,null,"CANTALA-MCCRAE","NH0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","CANTALA-MCCRAE (02)",7.0293828201883877E-5]
[2432,null,"SUSSEX-BANYULE","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","SUSSEX-BANYULE (02)",7.0293828201883877E-5]
[2444,null,"CASTLETON 21-HAVILAH","NH0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","CASTLETON 21-HAVILAH (02)",0]
[2445,null,"CASTLETON 21-HAVILAH","NH0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","CASTLETON 21-HAVILAH (02)",0]
[2456,null,"MYDDLETON-GRACE","NH0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","MYDDLETON-GRACE (01)",0]
[2464,null,null,null,"2024-12-01","2024-12-07","N","Y","N","N","N","N",null,"THE GLADE-SHERLOWE (01)",7.0293828201883877E-5]
[2465,null,null,null,"2024-12-01","2024-12-07","Y","N","N","N","N","N",null,"THE GLADE-SHERLOWE (01)",0]
[2473,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","YALLAMBIE-LOWER PLENTY (01)",0]
[2485,null,"BIMBADEEN-YALLAMBIE","NH0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",0]
[2486,null,"BIMBADEEN-YALLAMBIE","NH0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",0]
[2498,null,"BIMBADEEN-YALLAMBIE","NH0-002","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",{"$f":"IF(H2499=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[2506,null,"FRENSHAM-HARBORNE","WT0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","WT0","FRENSHAM-HARBORNE (02)",7.0293828201883877E-5]
[2507,null,"YALLAMBIE-JANICE","NH0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","YALLAMBIE-JANICE (01)",0]
[2519,null,"MUNRO-ERSKINE","NH0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","MUNRO-ERSKINE (02)",0]
[2527,null,"CASTLETON 21-HAVILAH","NH0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","CASTLETON 21-HAVILAH (03)",0]
[2532,null,"BRASSEY-PYALONG","NH0-020","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NH0","BRASSEY-PYALONG (01)",0]
[2540,null,"BRASSEY-PYALONG","NH0-020","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","BRASSEY-PYALONG (01)",0]
[2548,null,"YALLAMBIE-WENDOVER","NH0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","YALLAMBIE-WENDOVER (01)",0]
[2553,null,"PORTER-DOUGHARTY","NH0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","PORTER-DOUGHARTY (02)",0]
[2561,null,"PORTER-DOUGHARTY","NH0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NH0","PORTER-DOUGHARTY (01)",0]
[2569,null,"CARWARP-ERSKINE","NH0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","CARWARP-ERSKINE (02)",0]
[2574,null,"BRAIDHILL-WINDSOR","NH0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","BRAIDHILL-WINDSOR (02)",0]
[2582,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[2587,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[2595,null,"ROBERN-ROSEBUD","NH0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","ROBERN-ROSEBUD (01)",0]
[2603,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (02)",7.0293828201883877E-5]
[2609,null,"YALLAMBIE-WENDOVER","NH0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","YALLAMBIE-WENDOVER (01)",0]
[2615,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[2623,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (02)",7.0293828201883877E-5]
[2628,null,null,null,"2024-12-01","2024-12-07","Y","N","N","N","N","N",null,"THE GLADE-SHERLOWE (02)",0]
[2636,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[2641,null,null,null,"2024-12-01","2024-12-07","Y","N","N","N","N","N",null,"THE GLADE-SHERLOWE (02)",0]
[2649,null,null,null,"2024-12-01","2024-12-07","Y","N","N","N","N","N",null,"THE GLADE-SHERLOWE (02)",0]
[2657,null,null,null,"2024-12-01","2024-12-07","Y","N","N","N","N","N",null,"THE GLADE-SHERLOWE (02)",0]
[2662,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (02)",7.0293828201883877E-5]
[2670,null,null,null,"2024-12-01","2024-12-07","Y","N","N","N","N","N",null,"THE GLADE-SHERLOWE (03)",0]
[2675,null,null,null,"2024-12-01","2024-12-07","Y","N","N","N","N","N",null,"THE GLADE-SHERLOWE (03)",0]
[2683,null,null,null,"2024-12-01","2024-12-07","Y","N","N","N","N","N",null,"THE GLADE-SHERLOWE (04)",0]
[2691,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[2696,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[2704,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (02)",7.0293828201883877E-5]
[2712,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[2717,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[2725,null,"BRASSEY-PYALONG","NH0-020","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NH0","BRASSEY-PYALONG (01)",0]
[2730,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (01)",7.0293828201883877E-5]
[2738,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[2746,null,"CARWARP-ERSKINE","NH0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","CARWARP-ERSKINE (02)",0]
[2751,null,null,null,"2024-12-01","2024-12-07","Y","N","N","N","N","N",null,"THE GLADE-SHERLOWE (01)",0]
[2758,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[2770,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[2771,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[2779,null,"ALBERT 6-FOLEY","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT 6-FOLEY (01)",7.0293828201883877E-5]
[2791,null,"POWELL-EXCELSIOR","PTN-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","POWELL-EXCELSIOR (01)",7.0293828201883877E-5]
[2792,null,"POWELL-EXCELSIOR","PTN-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","POWELL-EXCELSIOR (01)",7.0293828201883877E-5]
[2800,null,"POWELL-EXCELSIOR","PTN-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","POWELL-EXCELSIOR (02)",7.0293828201883877E-5]
[2812,null,"POWELL-EXCELSIOR","PTN-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","POWELL-EXCELSIOR (02)",7.0293828201883877E-5]
[2813,null,"CRAWLEY-HIGH","CN0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","CRAWLEY-HIGH (02)",7.0293828201883877E-5]
[2825,null,"MARGTMARY-MURRAY","CN0-008","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","MARGTMARY-MURRAY (03)",0]
[2833,null,"BONVIEW-CARRINGTON","CN0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","BONVIEW-CARRINGTON (02)",7.0293828201883877E-5]
[2834,null,"KNOX-GILBERT","CN0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","KNOX-GILBERT (02)",7.0293828201883877E-5]
[2846,null,"SYMONS-GILBERT","CN0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","SYMONS-GILBERT (04)",0]
[2854,null,"MOUNT-BELL","CS0-003","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","MOUNT-BELL (02)",0]
[2855,null,"MOUNT-BELL","CS0-003","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","MOUNT-BELL (01)",0]
[2867,null,"BUNDOORA PARK-CHILDRENS FARM","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BUNDOORA PARK-CHILDRENS FARM (01)",7.0293828201883877E-5]
[2875,null,"BONVIEW-CARRINGTON","CN0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","BONVIEW-CARRINGTON (01)",7.0293828201883877E-5]
[2880,null,"CAROLE JOY-SPRING","CN0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","CAROLE JOY-SPRING (02)",0]
[2888,null,"HIGH 883-MELB WATER","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","HIGH 883-MELB WATER (00)",0]
[2896,null,"GLASGOW-HIGH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GLASGOW-HIGH (02)",7.0293828201883877E-5]
[2901,null,"ASQUITH-STURDEE","TT0-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","TT0","ASQUITH-STURDEE (01)",0]
[2909,null,"ANSTEY-PHILLIP","TT0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","TT0","ANSTEY-PHILLIP (02)",0]
[2911,null,"ANSTEY-PHILLIP","TT0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","TT0","ANSTEY-PHILLIP (02)",0]
[2921,null,"ANSTEY-LOCKTON","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANSTEY-LOCKTON (04)",7.0293828201883877E-5]
[2929,null,"HENDERSON-WILSON","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HENDERSON-WILSON (01)",7.0293828201883877E-5]
[2934,null,"ROSENTHAL-HUGHES","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-HUGHES (02)",7.0293828201883877E-5]
[2942,null,"LUDEMAN-BRAITHWAITE","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LUDEMAN-BRAITHWAITE (01)",7.0293828201883877E-5]
[2950,null,"LUDEMAN-BRAITHWAITE","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LUDEMAN-BRAITHWAITE (02)",7.0293828201883877E-5]
[2955,null,"LUDEMAN-BRAITHWAITE","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LUDEMAN-BRAITHWAITE (02)",7.0293828201883877E-5]
[2963,null,"LUDEMAN-BRAITHWAITE","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LUDEMAN-BRAITHWAITE (02)",7.0293828201883877E-5]
[2968,null,"LUDEMAN-BRAITHWAITE","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LUDEMAN-BRAITHWAITE (01)",7.0293828201883877E-5]
[2976,null,"ROSENTHAL-HUGHES","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-HUGHES (02)",7.0293828201883877E-5]
[2984,null,"ASQUITH-STURDEE","TT0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","TT0","ASQUITH-STURDEE (01)",0]
[2989,null,"LUDEMAN-BRAITHWAITE","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LUDEMAN-BRAITHWAITE (02)",7.0293828201883877E-5]
[2997,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",7.0293828201883877E-5]
[3002,null,"ROSENTHAL-HUGHES","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-HUGHES (01)",7.0293828201883877E-5]
[3010,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (02)",{"$f":"IF(H3011=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[3018,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (02)",7.0293828201883877E-5]
[3023,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (02)",7.0293828201883877E-5]
[3031,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",7.0293828201883877E-5]
[3039,null,"HOBBS-BROADHURST","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HOBBS-BROADHURST (01)",7.0293828201883877E-5]
[3044,null,"HOBBS-BROADHURST","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HOBBS-BROADHURST (02)",7.0293828201883877E-5]
[3052,null,"GLASGOW-HIGH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GLASGOW-HIGH (02)",7.0293828201883877E-5]
[3057,null,"GLASGOW-HIGH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GLASGOW-HIGH (02)",7.0293828201883877E-5]
[3066,null,"HOBBS-BROADHURST","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HOBBS-BROADHURST (01)",7.0293828201883877E-5]
[3072,null,"HOBBS-BROADHURST","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HOBBS-BROADHURST (01)",7.0293828201883877E-5]
[3077,null,"MONZA-FLORENCE","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MONZA-FLORENCE (01)",7.0293828201883877E-5]
[3085,null,"BREX 8-RADFORD","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BREX 8-RADFORD (01)",7.0293828201883877E-5]
[3093,null,"LAWLEY-GLASGOW","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LAWLEY-GLASGOW (02)",7.0293828201883877E-5]
[3098,null,"LAWLEY-GLASGOW","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LAWLEY-GLASGOW (02)",7.0293828201883877E-5]
[3106,null,"BRAY-BARTROP","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRAY-BARTROP (01)",7.0293828201883877E-5]
[3118,null,"BRAY-BARTROP","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRAY-BARTROP (01)",7.0293828201883877E-5]
[3119,null,"BRAY-BARTROP","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRAY-BARTROP (02)",7.0293828201883877E-5]
[3127,null,"BROADHURST-MCFADZEAN","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","OCONNOR-MACFADZEAN (01)",7.0293828201883877E-5]
[3139,null,"HENDERSON-WILSON","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HENDERSON-WILSON (02)",7.0293828201883877E-5]
[3140,null,"HENDERSON-WILSON","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HENDERSON-WILSON (02)",7.0293828201883877E-5]
[3152,null,"LUDEMAN-BRAITHWAITE","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LUDEMAN-BRAITHWAITE (02)",7.0293828201883877E-5]
[3160,null,"O'CONNOR-WHITBY","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","OCONNOR-MACFADZEAN (04)",0]
[3161,null,"O'CONNOR-WHITBY","CN0-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",0]
[3173,null,"O'CONNOR-WHITBY","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","OCONNOR-MACFADZEAN (04)",0]
[3181,null,"LAWLEY-PALLANT","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LAWLEY-PALLANT (01)",7.0293828201883877E-5]
[3182,null,"LAWLEY-PALLANT","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LAWLEY-PALLANT (01)",7.0293828201883877E-5]
[3194,null,"GREGORY-PLENTY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","GREGORY-PLENTY (04)",7.0293828201883877E-5]
[3202,null,"CAMBRIAN-HIGH","PTN-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","PTN","CAMBRIAN-HIGH (02)",{"$f":"IF(H3203=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":0}]
[3207,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (03)",7.0293828201883877E-5]
[3215,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",7.0293828201883877E-5]
[3221,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (01)",7.0293828201883877E-5]
[3227,null,"TENNYSON-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","TENNYSON-TYLER (02)",7.0293828201883877E-5]
[3235,null,"ALEXANDRA-NORTHERNHAY","CN0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","ALEXANDRA-NORTHERNHAY (02)",7.0293828201883877E-5]
[3243,null,"HOME-WILKINSON","CN0-011","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","CN0","HOME-WILKINSON (01)",7.0293828201883877E-5]
[3248,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (02)",7.0293828201883877E-5]
[3256,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (02)",7.0293828201883877E-5]
[3261,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (02)",7.0293828201883877E-5]
[3269,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (02)",7.0293828201883877E-5]
[3277,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (02)",7.0293828201883877E-5]
[3282,null,"DELAWARE-MENDIP","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","DELAWARE-MENDIP (01)",0]
[3290,null,"HIGH 883-MELB WATER","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","HIGH 883-MELB WATER (00)",0]
[3295,null,"O'DOWD-HOWARD","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","O'DOWD-HOWARD (02)",0]
[3303,null,"O'DOWD-HOWARD","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","O'DOWD-HOWARD (02)",0]
[3311,null,"O'DOWD-HOWARD","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","O'DOWD-HOWARD (01)",0]
[3316,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (02)",7.0293828201883877E-5]
[3324,null,"FORDHAM-STRATHMERTON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FORDHAM-STRATHMERTON (02)",7.0293828201883877E-5]
[3332,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (02)",7.0293828201883877E-5]
[3337,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (02)",7.0293828201883877E-5]
[3345,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (02)",7.0293828201883877E-5]
[3350,null,"FORDHAM-STRATHMERTON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FORDHAM-STRATHMERTON (02)",7.0293828201883877E-5]
[3358,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","TT0","ROYAL-MCMAHON (01)",0]
[3366,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (01)",7.0293828201883877E-5]
[3374,null,"CARROL-ORRONG","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CARROL-ORRONG (02)",7.0293828201883877E-5]
[3378,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (02)",7.0293828201883877E-5]
[3383,null,"WHITE-CHEDDAR","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITE-CHEDDAR (03)",7.0293828201883877E-5]
[3391,null,"RATHCOWN-CHEDDAR","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","RATHCOWN-CHEDDAR (01)",7.0293828201883877E-5]
[3399,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (01)",7.0293828201883877E-5]
[3404,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (01)",7.0293828201883877E-5]
[3412,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[3420,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[3425,null,"CHEDDAR-JINGHI","TT0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","TT0","CHEDDAR-JINGHI (04)",0]
[3433,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (03)",7.0293828201883877E-5]
[3445,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[3446,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[3454,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[3466,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (01)",7.0293828201883877E-5]
[3467,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (01)",7.0293828201883877E-5]
[3475,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (01)",7.0293828201883877E-5]
[3487,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[3488,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[3500,null,"LISTON-JOHNSON","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LISTON-JOHNSON (02)",7.0293828201883877E-5]
[3508,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (01)",7.0293828201883877E-5]
[3509,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (01)",7.0293828201883877E-5]
[3521,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (01)",7.0293828201883877E-5]
[3523,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (01)",7.0293828201883877E-5]
[3533,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (02)",7.0293828201883877E-5]
[3541,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (02)",7.0293828201883877E-5]
[3549,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[3554,null,"ROMSEY-KEON","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROMSEY-KEON (02)",7.0293828201883877E-5]
[3562,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[3570,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","NA",7.0293828201883877E-5]
[3575,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[3583,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (02)",7.0293828201883877E-5]
[3588,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (02)",7.0293828201883877E-5]
[3596,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (02)",7.0293828201883877E-5]
[3604,null,"MARSHALL-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MARSHALL-INVERMAY (01)",7.0293828201883877E-5]
[3609,null,"MARSHALL-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MARSHALL-INVERMAY (01)",7.0293828201883877E-5]
[3617,null,"ROBINS-SHAPIRO","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROBINS-SHAPIRO (02)",7.0293828201883877E-5]
[3625,null,"MARSHALL-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MARSHALL-INVERMAY (01)",7.0293828201883877E-5]
[3630,null,"MARSHALL-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MARSHALL-INVERMAY (01)",7.0293828201883877E-5]
[3638,null,"MARSHALL-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MARSHALL-INVERMAY (02)",7.0293828201883877E-5]
[3643,null,"MARSHALL-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MARSHALL-INVERMAY (02)",7.0293828201883877E-5]
[3651,null,"MANOEL-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MANOEL-DAREBIN (01)",7.0293828201883877E-5]
[3659,null,"MANOEL-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MANOEL-DAREBIN (02)",7.0293828201883877E-5]
[3664,null,"MANOEL-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MANOEL-DAREBIN (02)",7.0293828201883877E-5]
[3672,null,"MARSHALL-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MARSHALL-INVERMAY (02)",7.0293828201883877E-5]
[3676,null,"DOLE-LOCHER","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","DOLE-LOCHER (03)",7.0293828201883877E-5]
[3684,null,"INVERNESS-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERNESS-INVERMAY (02)",7.0293828201883877E-5]
[3692,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",7.0293828201883877E-5]
[3697,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[3705,null,"MANOEL-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MANOEL-DAREBIN (01)",7.0293828201883877E-5]
[3713,null,"MANOEL-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MANOEL-DAREBIN (01)",7.0293828201883877E-5]
[3718,null,"MANOEL-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MANOEL-DAREBIN (01)",7.0293828201883877E-5]
[3726,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",7.0293828201883877E-5]
[3731,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",7.0293828201883877E-5]
[3739,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (01)",7.0293828201883877E-5]
[3747,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (01)",7.0293828201883877E-5]
[3752,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (01)",7.0293828201883877E-5]
[3760,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (02)",7.0293828201883877E-5]
[3772,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (02)",7.0293828201883877E-5]
[3773,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (02)",7.0293828201883877E-5]
[3781,null,"AYR-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","AYR-DAREBIN (01)",7.0293828201883877E-5]
[3793,null,"MARSHALL-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MARSHALL-INVERMAY (02)",7.0293828201883877E-5]
[3794,null,"MARSHALL-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MARSHALL-INVERMAY (02)",7.0293828201883877E-5]
[3802,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (01)",7.0293828201883877E-5]
[3814,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[3815,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[3827,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[3831,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[3835,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[3847,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (02)",7.0293828201883877E-5]
[3855,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (02)",7.0293828201883877E-5]
[3856,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (02)",7.0293828201883877E-5]
[3868,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[3876,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (02)",7.0293828201883877E-5]
[3881,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (02)",7.0293828201883877E-5]
[3889,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[3897,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (02)",7.0293828201883877E-5]
[3902,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[3910,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[3915,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[3923,null,"McMAHON-CHEDDAR","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","McMAHON-CHEDDAR (02)",7.0293828201883877E-5]
[3931,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (02)",7.0293828201883877E-5]
[3936,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[3944,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[3952,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","NA",7.0293828201883877E-5]
[3957,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[3965,null,"KILMORE-CHARLTON","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","KILMORE-CHARLTON (02)",7.0293828201883877E-5]
[3970,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (01)",{"$f":"IF(H3971=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[3978,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (01)",7.0293828201883877E-5]
[3986,null,"KILMORE-CHARLTON","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","KILMORE-CHARLTON (02)",7.0293828201883877E-5]
[3990,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",7.0293828201883877E-5]
[3998,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (02)",7.0293828201883877E-5]
[4003,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",7.0293828201883877E-5]
[4011,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (02)",7.0293828201883877E-5]
[4019,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (02)",7.0293828201883877E-5]
[4024,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (01)",7.0293828201883877E-5]
[4032,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (02)",7.0293828201883877E-5]
[4040,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (02)",7.0293828201883877E-5]
[4045,null,"THE FAIRWAY-DUNNE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","THE FAIRWAY-DUNNE (01)",7.0293828201883877E-5]
[4053,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (01)",7.0293828201883877E-5]
[4058,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (01)",7.0293828201883877E-5]
[4066,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (02)",7.0293828201883877E-5]
[4074,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (02)",7.0293828201883877E-5]
[4079,null,"DRIVER-THE FAIRWAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","DRIVER-THE FAIRWAY (02)",7.0293828201883877E-5]
[4087,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (01)",7.0293828201883877E-5]
[4095,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (01)",7.0293828201883877E-5]
[4100,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (01)",7.0293828201883877E-5]
[4108,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (02)",7.0293828201883877E-5]
[4120,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (02)",7.0293828201883877E-5]
[4121,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (02)",7.0293828201883877E-5]
[4129,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (02)",7.0293828201883877E-5]
[4139,null,"EISENHOWER-CHALEYER","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","EISENHOWER-CHALEYER (01)",0]
[4141,null,"EISENHOWER-CHALEYER","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","EISENHOWER-CHALEYER (01)",0]
[4153,null,"BLAKE-SESTON","NH0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","BLAKE-SESTON (02)",7.0293828201883877E-5]
[4161,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",7.0293828201883877E-5]
[4162,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",{"$f":"IF(H4163=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[4174,null,"NEWTON-CREVELLI","NH0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","NEWTON-CREVELLI (01)",7.0293828201883877E-5]
[4182,null,"WOOD-GREENBELT","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","WOOD-GREENBELT (02)",0]
[4183,null,"WOOD-GREENBELT","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","WOOD-GREENBELT (02)",0]
[4195,null,"WOOD-GREENBELT","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","WOOD-GREENBELT (02)",0]
[4203,null,"WOOD-GREENBELT","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","WOOD-GREENBELT (02)",0]
[4208,null,"WOOD-GREENBELT","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","WOOD-GREENBELT (02)",0]
[4216,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[4224,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[4229,null,"GORDON-WOOD","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","GORDON-WOOD (02)",7.0293828201883877E-5]
[4237,null,"GORDON-WOOD","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","GORDON-WOOD (01)",7.0293828201883877E-5]
[4245,null,"GORDON-WOOD","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","GORDON-WOOD (01)",7.0293828201883877E-5]
[4250,null,"GORDON-WOOD","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","NA",7.0293828201883877E-5]
[4258,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[4263,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[4271,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[4279,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (01)",7.0293828201883877E-5]
[4284,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (01)",7.0293828201883877E-5]
[4288,null,"BEAUCHAMP-HIGH","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","BEAUCHAMP-HIGH (01)",7.0293828201883877E-5]
[4296,null,"ALBERT-HARROW","EPN-035","2024-12-01","2024-12-07","Y","N","N","Y","N","N","EPN","ALBERT-HARROW (02)",0]
[4304,null,"SOUTH-BELL","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",7.0293828201883877E-5]
[4312,null,"SOUTH-BELL","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",7.0293828201883877E-5]
[4317,null,"BELGROVE-OVANDO","PTN-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","PTN","BELGROVE-OVANDO (02)",0]
[4325,null,"REX-CHIFLEY","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","REX-CHIFLEY (01)",7.0293828201883877E-5]
[4333,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[4338,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[4346,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[4351,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[4359,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (02)",7.0293828201883877E-5]
[4367,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (02)",7.0293828201883877E-5]
[4372,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (02)",7.0293828201883877E-5]
[4380,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4385,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4393,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4401,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4406,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4414,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (02)",7.0293828201883877E-5]
[4422,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[4427,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[4435,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[4441,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[4447,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[4455,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[4467,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4468,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4476,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4488,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4489,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4501,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4509,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4510,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[4522,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (01)",7.0293828201883877E-5]
[4530,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[4535,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[4543,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (01)",7.0293828201883877E-5]
[4551,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[4556,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[4564,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[4572,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[4577,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[4585,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[4590,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[4596,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[4605,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (02)",7.0293828201883877E-5]
[4610,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","Y","Y","Y","Y","N","N","EP0","TIERNAN-RAGLAN (02)",{"$f":"IF(H4611=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[4618,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[4623,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[4631,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[4639,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[4644,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[4652,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[4660,null,"BEECHER-RAGLAN","EP0-028","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BEECHER-RAGLAN (02)",7.0293828201883877E-5]
[4665,null,"FINK-CHIFLEY","EP0-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FINK-CHIFLEY (02)",7.0293828201883877E-5]
[4673,null,"COPE-UCM 1","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","COPE-UCM 1 (02)",7.0293828201883877E-5]
[4678,null,"CHIFLEY 51-53-RAGLAN","EP0-035","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","CHIFLEY 51-53-RAGLAN (02)",7.0293828201883877E-5]
[4686,null,"CHIFLEY 51-53-RAGLAN","EP0-035","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","CHIFLEY 51-53-RAGLAN (02)",7.0293828201883877E-5]
[4694,null,"RESERVE-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RESERVE-DUNDAS (01)",7.0293828201883877E-5]
[4699,null,"NEWCASTLE-DUNDAS","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NEWCASTLE-DUNDAS (02)",7.0293828201883877E-5]
[4707,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (02)",7.0293828201883877E-5]
[4715,null,"SALISBURY-JACK","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","SALISBURY-JACK (01)",0]
[4720,null,"FERGUSON-TOWNHALL","NT0-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NT0","FERGUSON-TOWNHALL (01)",0]
[4728,null,"COLE-OSBORNE","NT0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","COLE-OSBORNE (01)",0]
[4733,null,"STEWART-OSBORNE","NT0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","STEWART-OSBORNE (01)",0]
[4741,null,"ALMA-CHANDLER","NT0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NT0","ALMA-CHANDLER (02)",7.0293828201883877E-5]
[4751,null,"QUEEN-RUSSELL","NT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NT0","QUEEN-RUSSELL (04)",7.0293828201883877E-5]
[4753,null,"PEEL-DOUGLAS","NT0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","NT0","PEEL-DOUGLAS (03)",7.0293828201883877E-5]
[4761,null,"NEWCASTLE-ELIZABETH","NT0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NT0","NEWCASTLE-ELIZABETH (02)",7.0293828201883877E-5]
[4773,null,"BLENHEIM-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (02)",0]
[4774,null,"BLENHEIM-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (02)",0]
[4782,null,"BLENHEIM-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (03)",0]
[4794,null,"THORPE-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NT0","THORPE-WOODS (01)",0]
[4795,null,"THORPE-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NT0","THORPE-WOODS (01)",0]
[4803,null,"CHALLIS-JUBILLEE","NT0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","CHALLIS-JUBILLEE (01)",0]
[4815,null,"BRADLEY-MASON","NT0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","BRADLEY-MASON (01)",0]
[4816,null,"WILLIAM-JUNCTION","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","WILLIAM-JUNCTION (01)",0]
[4828,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[4836,null,"GREENVALE-WALLACE","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","GREENVALE-WALLACE (02)",7.0293828201883877E-5]
[4837,null,"CARROL-ORRONG","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CARROL-ORRONG (02)",7.0293828201883877E-5]
[4849,null,"LANGDON-PETERLEE","ST0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","LANGDON-PETERLEE (02)",7.0293828201883877E-5]
[4857,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (02)",7.0293828201883877E-5]
[4858,null,"GORDON-WOOD","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","GORDON-WOOD (01)",7.0293828201883877E-5]
[4870,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (01)",7.0293828201883877E-5]
[4878,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (02)",7.0293828201883877E-5]
[4883,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[4891,null,"JOSEPHINE-MURPHY","PV0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","JOSEPHINE-MURPHY (01)",7.0293828201883877E-5]
[4899,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (01)",7.0293828201883877E-5]
[4904,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (02)",7.0293828201883877E-5]
[4911,null,"FLORENCE-LINCOLN","ES0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","FLORENCE-LINCOLN (02)",0]
[4916,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[4924,null,"HOBBS-BROADHURST","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HOBBS-BROADHURST (01)",7.0293828201883877E-5]
[4932,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",7.0293828201883877E-5]
[4937,null,"CUMBERLAND-KENT","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CUMBERLAND-KENT (04)",0]
[4945,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (01)",7.0293828201883877E-5]
[4953,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (01)",7.0293828201883877E-5]
[4958,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (03)",7.0293828201883877E-5]
[4966,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (02)",7.0293828201883877E-5]
[4971,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",7.0293828201883877E-5]
[4979,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[4987,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[4992,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[5000,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",7.0293828201883877E-5]
[5005,null,"WESTMINSTER-MILITARY","BY0-014","2024-12-01","2024-12-07","Y","N","N","Y","N","N","BY0","WESTMINSTER-MILITARY (02)",0]
[5013,null,"CRAWFORD-ROBINSON","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (02)",7.0293828201883877E-5]
[5021,null,"GELLIBRAND-VICTORIA","NT0-015","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","GELLIBRAND-VICTORIA (03)",0]
[5026,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[5034,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[5042,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",7.0293828201883877E-5]
[5047,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",7.0293828201883877E-5]
[5053,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",7.0293828201883877E-5]
[5059,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (02)",7.0293828201883877E-5]
[5067,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",7.0293828201883877E-5]
[5075,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",7.0293828201883877E-5]
[5080,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",7.0293828201883877E-5]
[5088,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",7.0293828201883877E-5]
[5096,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (02)",7.0293828201883877E-5]
[5101,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (02)",7.0293828201883877E-5]
[5109,null,"DELHI-MOOLTAN","FT0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","DELHI-MOOLTAN (02)",7.0293828201883877E-5]
[5121,null,"DELHI-MOOLTAN","FT0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","DELHI-MOOLTAN (01)",7.0293828201883877E-5]
[5122,null,"FENTON-MYRNONG","FT0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","FENTON-MYRNONG (01)",{"$f":"IF(H5123=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[5130,null,"FENTON-MYRNONG","FT0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","FENTON-MYRNONG (01)",7.0293828201883877E-5]
[5142,null,"FENTON-MYRNONG","FT0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","FENTON-MYRNONG (03)",7.0293828201883877E-5]
[5143,null,"FENTON-MYRNONG","FT0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","FENTON-MYRNONG (02)",7.0293828201883877E-5]
[5155,null,"BANK-MT ALEXANDER","FT0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","BANK-MT ALEXANDER (03)",7.0293828201883877E-5]
[5163,null,"EAST-HARDING","FT0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","EAST-HARDING (01)",7.0293828201883877E-5]
[5164,null,"EAST-HARDING","FT0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","EAST-HARDING (01)",7.0293828201883877E-5]
[5176,null,"MIDDLE-ASCOT VALE","FT0-026","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","MIDDLE-ASCOT VALE (03)",7.0293828201883877E-5]
[5184,null,"ROXBURGH-ROTHWELL","FT0-026","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","ROXBURGH-ROTHWELL (02)",7.0293828201883877E-5]
[5185,null,"ROXBURGH-ROTHWELL","FT0-026","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","ROXBURGH-ROTHWELL (02)",7.0293828201883877E-5]
[5197,null,"RETREAT-HAVEN","ES0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","RETREAT-HAVEN (01)",7.0293828201883877E-5]
[5205,null,"CHARLES-EPSOM","ES0-022","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","CHARLES-EPSOM (01)",0]
[5206,null,"CHARLES-EPSOM","ES0-022","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","CHARLES-EPSOM (01)",0]
[5217,null,"ST LEONARDS-EPSOM","ES0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","ST LEONARDS-EPSOM (03)",7.0293828201883877E-5]
[5225,null,"DARLING-EGLINTON","ES0-023","2024-12-01","2024-12-07","Y","N","N","Y","N","N","ES0","DARLING-EGLINTON (01)",0]
[5230,null,"GRANDVIEW-HOLMES","ES0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","GRANDVIEW-HOLMES (03)",7.0293828201883877E-5]
[5238,null,"BROWNING-MOORE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BROWNING-MOORE (01)",7.0293828201883877E-5]
[5246,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (05)",7.0293828201883877E-5]
[5251,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (05)",7.0293828201883877E-5]
[5259,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",7.0293828201883877E-5]
[5264,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",7.0293828201883877E-5]
[5272,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",7.0293828201883877E-5]
[5280,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",7.0293828201883877E-5]
[5285,null,"BROWNING-MOORE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BROWNING-MOORE (01)",7.0293828201883877E-5]
[5293,null,"BROWNING-MOORE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BROWNING-MOORE (02)",7.0293828201883877E-5]
[5298,null,"BROWNING-MOORE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BROWNING-MOORE (02)",7.0293828201883877E-5]
[5306,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",7.0293828201883877E-5]
[5314,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",{"$f":"IF(H5315=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[5319,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[5327,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[5335,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (02)",7.0293828201883877E-5]
[5340,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (02)",7.0293828201883877E-5]
[5348,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (02)",7.0293828201883877E-5]
[5353,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (02)",7.0293828201883877E-5]
[5361,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[5368,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (01)",7.0293828201883877E-5]
[5373,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[5381,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (01)",7.0293828201883877E-5]
[5386,null,"ARDMILLAN-MANTELL","ES0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","ARDMILLAN-MANTELL (01)",7.0293828201883877E-5]
[5394,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[5402,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (03)",7.0293828201883877E-5]
[5407,null,"HOMER-EDDY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HOMER-EDDY (03)",7.0293828201883877E-5]
[5415,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[5423,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[5428,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[5436,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[5448,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[5449,null,"EDDY-TAYLOR","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","EDDY-TAYLOR (01)",7.0293828201883877E-5]
[5457,null,"EDDY-TAYLOR","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","EDDY-TAYLOR (01)",7.0293828201883877E-5]
[5469,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (02)",7.0293828201883877E-5]
[5470,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (02)",7.0293828201883877E-5]
[5478,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (02)",7.0293828201883877E-5]
[5490,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (02)",7.0293828201883877E-5]
[5491,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (02)",7.0293828201883877E-5]
[5503,null,"McPHERSON-ALEXANDRA 2","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (04)",7.0293828201883877E-5]
[5511,null,"McPHERSON-ALEXANDRA 2","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (01)",7.0293828201883877E-5]
[5516,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (01)",7.0293828201883877E-5]
[5523,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (01)",7.0293828201883877E-5]
[5531,null,"MCPHERSON-BENT","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MCPHERSON-BENT (02)",7.0293828201883877E-5]
[5536,null,"LAWSON-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LAWSON-SALISBURY (02)",7.0293828201883877E-5]
[5544,null,"LAWSON-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LAWSON-SALISBURY (04)",7.0293828201883877E-5]
[5552,null,"LAWSON-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LAWSON-SALISBURY (01)",7.0293828201883877E-5]
[5557,null,"MCPHERSON-BENT","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MCPHERSON-BENT (01)",7.0293828201883877E-5]
[5565,null,"CAPULET-BENT","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAPULET-BENT (01)",7.0293828201883877E-5]
[5573,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (02)",7.0293828201883877E-5]
[5578,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (02)",7.0293828201883877E-5]
[5586,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (02)",7.0293828201883877E-5]
[5591,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (02)",7.0293828201883877E-5]
[5599,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (02)",7.0293828201883877E-5]
[5607,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[5612,null,"MCPHERSON-BENT","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MCPHERSON-BENT (02)",7.0293828201883877E-5]
[5620,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (02)",7.0293828201883877E-5]
[5625,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (02)",7.0293828201883877E-5]
[5633,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (02)",7.0293828201883877E-5]
[5641,null,"MCPHERSON-BENT","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MCPHERSON-BENT (03)",7.0293828201883877E-5]
[5646,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (01)",7.0293828201883877E-5]
[5654,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (01)",7.0293828201883877E-5]
[5662,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (01)",7.0293828201883877E-5]
[5669,null,"PASCOE VALE-KELLAWAY","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-KELLAWAY (03)",7.0293828201883877E-5]
[5674,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (02)",7.0293828201883877E-5]
[5679,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (03)",7.0293828201883877E-5]
[5687,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (04)",7.0293828201883877E-5]
[5695,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (01)",7.0293828201883877E-5]
[5700,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (04)",7.0293828201883877E-5]
[5708,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (04)",7.0293828201883877E-5]
[5716,null,"CRAWFORD-ROBINSON","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (01)",7.0293828201883877E-5]
[5721,null,"CRAWFORD-ROBINSON","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (01)",7.0293828201883877E-5]
[5729,null,"CRAWFORD-ROBINSON","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (01)",7.0293828201883877E-5]
[5734,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (03)",7.0293828201883877E-5]
[5742,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[5750,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[5755,null,"CRAWFORD-ROBINSON","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (02)",7.0293828201883877E-5]
[5763,null,"CRAWFORD-ROBINSON","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (02)",7.0293828201883877E-5]
[5775,null,"RALEIGH-NAPIER No. 2","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-NAPIER No. 2 (03)",7.0293828201883877E-5]
[5776,null,"RALEIGH-NAPIER No. 2","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-NAPIER No. 2 (03)",7.0293828201883877E-5]
[5784,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (02)",7.0293828201883877E-5]
[5796,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (02)",7.0293828201883877E-5]
[5797,null,"WOODLAND-NAPIER","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-NAPIER (02)",7.0293828201883877E-5]
[5805,null,"SALMON-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALMON-SCHOFIELD (02)",7.0293828201883877E-5]
[5817,null,"SALMON-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALMON-SCHOFIELD (01)",7.0293828201883877E-5]
[5818,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (04)",7.0293828201883877E-5]
[5829,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (01)",7.0293828201883877E-5]
[5837,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (01)",7.0293828201883877E-5]
[5838,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (02)",7.0293828201883877E-5]
[5850,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (02)",7.0293828201883877E-5]
[5858,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[5859,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","GLASS-NAPIER (01)",7.0293828201883877E-5]
[5871,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (02)",7.0293828201883877E-5]
[5879,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (02)",7.0293828201883877E-5]
[5884,null,"GLEN-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLEN-GLASS (01)",7.0293828201883877E-5]
[5892,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[5900,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[5905,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[5913,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[5918,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (01)",7.0293828201883877E-5]
[5926,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (01)",7.0293828201883877E-5]
[5934,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (03)",7.0293828201883877E-5]
[5939,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (02)",7.0293828201883877E-5]
[5947,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (03)",7.0293828201883877E-5]
[5955,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (03)",7.0293828201883877E-5]
[5960,null,"GLASS-NAPIER NO.2","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER NO.2 (02)",7.0293828201883877E-5]
[5968,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (01)",7.0293828201883877E-5]
[5971,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (01)",7.0293828201883877E-5]
[5980,null,"GLEN-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLEN-GLASS (02)",7.0293828201883877E-5]
[5988,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[5993,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[6001,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[6006,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[6014,null,"GLEN-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLEN-GLASS (03)",7.0293828201883877E-5]
[6022,null,"GLEN-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLEN-GLASS (04)",7.0293828201883877E-5]
[6027,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (03)",7.0293828201883877E-5]
[6035,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (03)",7.0293828201883877E-5]
[6043,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (03)",7.0293828201883877E-5]
[6048,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (02)",7.0293828201883877E-5]
[6056,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (02)",7.0293828201883877E-5]
[6061,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (01)",7.0293828201883877E-5]
[6069,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (01)",7.0293828201883877E-5]
[6077,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (01)",7.0293828201883877E-5]
[6082,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (01)",{"$f":"IF(H6083=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[6090,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (02)",7.0293828201883877E-5]
[6098,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUTLER-PASCOE VALE (00)",7.0293828201883877E-5]
[6103,null,"BREWSTER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-NAPIER (03)",7.0293828201883877E-5]
[6111,null,"NICHOLSON-BREWSTER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NICHOLSON-BREWSTER (02)",7.0293828201883877E-5]
[6123,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (02)",7.0293828201883877E-5]
[6126,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","N","N","Y","N","N","NS0","NAPIER-BUTLER (02)",0]
[6131,null,"SHAFTESBURY-RALEIGH","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SHAFTESBURY-RALEIGH (01)",7.0293828201883877E-5]
[6143,null,"BREWSTER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-NAPIER (03)",7.0293828201883877E-5]
[6144,null,"BREWSTER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-NAPIER (03)",7.0293828201883877E-5]
[6156,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[6164,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[6165,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (04)",7.0293828201883877E-5]
[6177,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[6185,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (00)",7.0293828201883877E-5]
[6186,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (00)",7.0293828201883877E-5]
[6198,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (02)",7.0293828201883877E-5]
[6206,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (03)",7.0293828201883877E-5]
[6211,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (02)",7.0293828201883877E-5]
[6219,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[6227,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[6232,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[6240,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[6248,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","NA",7.0293828201883877E-5]
[6253,null,"NICHOLSON-FLETCHER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NICHOLSON-FLETCHER (02)",7.0293828201883877E-5]
[6261,null,"NICHOLSON-BREWSTER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NICHOLSON-BREWSTER (01)",7.0293828201883877E-5]
[6266,null,"NICHOLSON-BREWSTER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NICHOLSON-BREWSTER (01)",7.0293828201883877E-5]
[6274,null,"NICHOLSON-BREWSTER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NICHOLSON-BREWSTER (01)",{"$f":"IF(H6275=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[6281,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[6286,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[6294,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HODDLE-FLETCHER (02)",7.0293828201883877E-5]
[6299,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HODDLE-FLETCHER (02)",7.0293828201883877E-5]
[6307,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (02)",7.0293828201883877E-5]
[6315,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (03)",7.0293828201883877E-5]
[6320,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (03)",7.0293828201883877E-5]
[6328,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[6336,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUTLER-PASCOE VALE (01)",7.0293828201883877E-5]
[6341,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUTLER-PASCOE VALE (01)",7.0293828201883877E-5]
[6349,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUTLER-PASCOE VALE (01)",7.0293828201883877E-5]
[6354,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (02)",7.0293828201883877E-5]
[6362,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (02)",7.0293828201883877E-5]
[6370,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[6375,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[6383,null,"VANBERG-TENNYSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","VANBERG-TENNYSON (01)",7.0293828201883877E-5]
[6388,null,"DONALD-LAWSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",7.0293828201883877E-5]
[6396,null,"DONALD-LAWSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",7.0293828201883877E-5]
[6404,null,"DONALD-LAWSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",7.0293828201883877E-5]
[6409,null,"DONALD-LAWSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",7.0293828201883877E-5]
[6417,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (04)",7.0293828201883877E-5]
[6425,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (04)",7.0293828201883877E-5]
[6434,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (04)",7.0293828201883877E-5]
[6437,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (04)",7.0293828201883877E-5]
[6449,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (01)",7.0293828201883877E-5]
[6450,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (01)",7.0293828201883877E-5]
[6458,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (01)",7.0293828201883877E-5]
[6470,null,"VANBERG-TENNYSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","VANBERG-TENNYSON (01)",7.0293828201883877E-5]
[6471,null,"VANBERG-TENNYSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NA",7.0293828201883877E-5]
[6479,null,"VANBERG-TENNYSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","VANBERG-TENNYSON (02)",7.0293828201883877E-5]
[6491,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (01)",7.0293828201883877E-5]
[6492,null,"BUCKLEY-MCPHERSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-MCPHERSON (01)",7.0293828201883877E-5]
[6504,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (02)",7.0293828201883877E-5]
[6512,null,"BUCKLEY-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-HODDLE (03)",7.0293828201883877E-5]
[6513,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (03)",7.0293828201883877E-5]
[6525,null,"BUCKLEY-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-HODDLE (03)",7.0293828201883877E-5]
[6533,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (03)",7.0293828201883877E-5]
[6538,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (03)",7.0293828201883877E-5]
[6546,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (03)",7.0293828201883877E-5]
[6554,null,"BUCKLEY-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-HODDLE (03)",7.0293828201883877E-5]
[6559,null,"BUCKLEY-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-HODDLE (03)",7.0293828201883877E-5]
[6567,null,"MT ALEXANDER 902-WILLOW","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER 902-WILLOW (01)",7.0293828201883877E-5]
[6575,null,"MT ALEXANDER-RUSSELL","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-RUSSELL (01)",7.0293828201883877E-5]
[6580,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (01)",7.0293828201883877E-5]
[6583,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (01)",7.0293828201883877E-5]
[6592,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (02)",7.0293828201883877E-5]
[6600,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (03)",7.0293828201883877E-5]
[6608,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","THISTLE-MT ALEXANDER (01)",7.0293828201883877E-5]
[6613,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (01)",7.0293828201883877E-5]
[6621,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (01)",7.0293828201883877E-5]
[6626,null,"MT ALEXANDER-RUSSELL","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-RUSSELL (01)",7.0293828201883877E-5]
[6634,null,"FIELD-GRANDISON","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FIELD-GRANDISON (03)",7.0293828201883877E-5]
[6642,null,"BUCKLEY-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-MT ALEXANDER (03)",7.0293828201883877E-5]
[6647,null,"FORRESTER-HEDDERWICK","ES0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","FORRESTER-HEDDERWICK (02)",7.0293828201883877E-5]
[6655,null,"MCCARRON-FORRESTER","ES0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","MCCARRON-FORRESTER (01)",7.0293828201883877E-5]
[6663,null,"DAISY-BUCKLEY","ES0-024","2024-12-01","2024-12-07","Y","N","N","Y","N","N","ES0","DAISY-BUCKLEY (01)",0]
[6668,null,"VIDA-ALMA","ES0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","VIDA-ALMA (02)",7.0293828201883877E-5]
[6676,null,"MATTHEWS-KEILOR","ES0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","MATTHEWS-KEILOR (01)",7.0293828201883877E-5]
[6681,null,"CRESSWELL-CAMERON","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","CRESSWELL-CAMERON (02)",7.0293828201883877E-5]
[6689,null,"HILLSIDE-ROBERTS","AW0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","HILLSIDE-ROBERTS (01)",0]
[6697,null,"WEST-KINGSLEY","AW0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","WEST-KINGSLEY (02)",0]
[6702,null,"WEST-KINGSLEY","AW0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","WEST-KINGSLEY (01)",0]
[6710,null,"KINGSLEY-AJ DAVIS RESERVE","AW0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","KINGSLEY-AJ DAVIS RESERVE (01)",7.0293828201883877E-5]
[6718,null,"SEXTON-PARER","AW0-006","2024-12-01","2024-12-07","Y","N","N","Y","N","N","AW0","SEXTON-PARER (01)",0]
[6723,null,"COPE-MOORE","AW0-001","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","COPE-MOORE (02)",7.0293828201883877E-5]
[6731,null,"GORDON-SHARPS","AW0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","GORDON-SHARPS (02)",7.0293828201883877E-5]
[6736,null,"THERESA-CHRISTOPHER","AW0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","THERESA-CHRISTOPHER (02)",7.0293828201883877E-5]
[6743,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (01)",7.0293828201883877E-5]
[6751,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (01)",7.0293828201883877E-5]
[6756,null,"KEILOR-MC CULLOCH","ES0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KEILOR-MC CULLOCH (03)",7.0293828201883877E-5]
[6764,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KERFERD-RALEIGH (02)",7.0293828201883877E-5]
[6776,null,"FIRST-BULLA","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FIRST-BULLA (02)",7.0293828201883877E-5]
[6777,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (02)",7.0293828201883877E-5]
[6785,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (02)",7.0293828201883877E-5]
[6797,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (01)",7.0293828201883877E-5]
[6798,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (01)",7.0293828201883877E-5]
[6806,null,"CRANWELL-CARNARVON","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRANWELL-CARNARVON (01)",7.0293828201883877E-5]
[6818,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (01)",7.0293828201883877E-5]
[6819,null,"CRANWELL-CARNARVON","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRANWELL-CARNARVON (02)",7.0293828201883877E-5]
[6831,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (04)",7.0293828201883877E-5]
[6839,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (01)",7.0293828201883877E-5]
[6840,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (01)",7.0293828201883877E-5]
[6852,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (03)",7.0293828201883877E-5]
[6860,null,"JAMES-WILLIAMSON","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JAMES-WILLIAMSON (02)",7.0293828201883877E-5]
[6861,null,"JAMES-WILLIAMSON","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JAMES-WILLIAMSON (01)",7.0293828201883877E-5]
[6873,null,"MERCHISTON-CARNARVON","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MERCHISTON-CARNARVON (01)",7.0293828201883877E-5]
[6881,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[6886,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[6891,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[6901,null,"WOODLAND-NAPIER","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-NAPIER (02)",7.0293828201883877E-5]
[6906,null,"MAGDALA-WOODLAND","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MAGDALA-WOODLAND (01)",7.0293828201883877E-5]
[6914,null,"GLENVIEW-UPLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLENVIEW-UPLAND (03)",{"$f":"IF(H6915=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[6919,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (03)",7.0293828201883877E-5]
[6927,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (03)",7.0293828201883877E-5]
[6935,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (01)",7.0293828201883877E-5]
[6940,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (04)",7.0293828201883877E-5]
[6948,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (03)",7.0293828201883877E-5]
[6956,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (03)",7.0293828201883877E-5]
[6961,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (03)",7.0293828201883877E-5]
[6969,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (02)",7.0293828201883877E-5]
[6974,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (01)",7.0293828201883877E-5]
[6982,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (02)",7.0293828201883877E-5]
[6990,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (02)",7.0293828201883877E-5]
[6995,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (01)",7.0293828201883877E-5]
[7003,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (03)",7.0293828201883877E-5]
[7008,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (03)",7.0293828201883877E-5]
[7016,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (03)",7.0293828201883877E-5]
[7024,null,"HILLSYDE-LOEMAN","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HILLSYDE-LOEMAN (01)",7.0293828201883877E-5]
[7029,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[7037,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[7046,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[7049,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[7057,null,"HILLSYDE-LOEMAN","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HILLSYDE-LOEMAN (03)",7.0293828201883877E-5]
[7062,null,"THE CROSSWAY-UPLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THE CROSSWAY-UPLAND (02)",7.0293828201883877E-5]
[7070,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[7078,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (03)",7.0293828201883877E-5]
[7083,null,"GLENVIEW-UPLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLENVIEW-UPLAND (02)",7.0293828201883877E-5]
[7091,null,"THE CROSSWAY-UPLAND","NS0-017","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NS0","THE CROSSWAY-UPLAND (04)",0]
[7099,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (02)",7.0293828201883877E-5]
[7104,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","PROGRESS-PASCOE VALE (02)",7.0293828201883877E-5]
[7112,null,"HILLSYDE-LOEMAN","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HILLSYDE-LOEMAN (02)",7.0293828201883877E-5]
[7124,null,"JOHN-WINIFRED","PV0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","JOHN-WINIFRED (01)",7.0293828201883877E-5]
[7125,null,"JOHN-WINIFRED","PV0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","JOHN-WINIFRED (01)",7.0293828201883877E-5]
[7133,null,"MARGARET-WINIFRED","PV0-022","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","MARGARET-WINIFRED (01)",0]
[7145,null,"CLAYTON-MASCOMA","AW0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","CLAYTON-MASCOMA (01)",7.0293828201883877E-5]
[7146,null,"LOCKHEED-BOEING","AW0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","LOCKHEED-BOEING (02)",0]
[7158,null,"LOCH-WENDORA","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LOCH-WENDORA (01)",7.0293828201883877E-5]
[7166,null,"PECK-PASCOE VALE","PV0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","PECK-PASCOE VALE (01)",7.0293828201883877E-5]
[7167,null,"PECK-PASCOE VALE","PV0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","PECK-PASCOE VALE (01)",7.0293828201883877E-5]
[7179,null,"KINGSTON-COLLINSON","TMA-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TMA","KINGSTON-COLLINSON (02)",7.0293828201883877E-5]
[7187,null,"ELIZA-EREBUS","TMA-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TMA","ELIZA-EREBUS (01)",7.0293828201883877E-5]
[7188,null,"KINGSTON-COLLINSON","TMA-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TMA","KINGSTON-COLLINSON (02)",7.0293828201883877E-5]
[7199,null,"CENTREWAY-WINGARA","AW0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","CENTREWAY-WINGARA (03)",7.0293828201883877E-5]
[7207,null,"QUINN-NOGA","AW0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","QUINN-NOGA (01)",7.0293828201883877E-5]
[7212,null,"QUINN-NOGA","AW0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","QUINN-NOGA (01)",7.0293828201883877E-5]
[7220,null,"ROSEHILL-TALBOT","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","ROSEHILL-TALBOT (01)",7.0293828201883877E-5]
[7228,null,"MCPHERSON-QUINN","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","MCPHERSON-QUINN (03)",7.0293828201883877E-5]
[7233,null,"FAWKNER-ROBERTS","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FAWKNER-ROBERTS (02)",7.0293828201883877E-5]
[7241,null,"FAWKNER-ROBERTS","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FAWKNER-ROBERTS (02)",7.0293828201883877E-5]
[7246,null,"FAWKNER-ROBERTS","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FAWKNER-ROBERTS (02)",7.0293828201883877E-5]
[7254,null,"SALTAU-MILLEARA","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SALTAU-MILLEARA (01)",7.0293828201883877E-5]
[7262,null,"PARKSIDE-STERLING","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","PARKSIDE-STERLING (01)",7.0293828201883877E-5]
[7267,null,"BUCKLEY-THE CROSSWAY","BY0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","BY0","BUCKLEY-THE CROSSWAY (02)",0]
[7275,null,"DAVIS-MILITARY","BY0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","DAVIS-MILITARY (02)",7.0293828201883877E-5]
[7283,null,"DAVIS-MILITARY","BY0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","BY0","DAVIS-MILITARY (03)",0]
[7288,null,"WOOD-BROWN","BY0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","WOOD-BROWN (02)",7.0293828201883877E-5]
[7296,null,"CHRISTINA-BARBARA","BY0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","BY0","CHRISTINA-BARBARA (01)",0]
[7301,null,"CHRISTINA-BARBARA","BY0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","BY0","CHRISTINA-BARBARA (01)",0]
[7309,null,"CLYDEBANK-AFTON","ES0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","CLYDEBANK-AFTON (01)",0]
[7317,null,"NEWMAN-HOTHAM","AW0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","NEWMAN-HOTHAM (03)",0]
[7322,null,"NEWMAN-HOTHAM","AW0-007","2024-12-01","2024-12-07","Y","N","N","Y","N","N","AW0","NEWMAN-HOTHAM (03)",0]
[7330,null,"NEWMAN-HOTHAM","AW0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","NEWMAN-HOTHAM (03)",7.0293828201883877E-5]
[7338,null,"MOUSHALL-HOFFMANS","ES0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","MOUSHALL-HOFFMANS (02)",0]
[7343,null,"GARNET-IDA","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","GARNET-IDA (02)",7.0293828201883877E-5]
[7348,null,"DIAMOND-ROSEHILL","ES0-021","2024-12-01","2024-12-07","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (01)",0]
[7355,null,"DIAMOND-ROSEHILL","ES0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","DIAMOND-ROSEHILL (01)",0]
[7363,null,"SPENCER-COOPER","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","SPENCER-COOPER (01)",7.0293828201883877E-5]
[7371,null,"MARY-ROBERTS","ES0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","MARY-ROBERTS (02)",0]
[7376,null,"VALLEY-AUGUSTINE","PV0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","VALLEY-AUGUSTINE (02)",7.0293828201883877E-5]
[7384,null,"VALLEY-AUGUSTINE","PV0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","VALLEY-AUGUSTINE (01)",7.0293828201883877E-5]
[7389,null,"MOONEE-VALLEY","PV0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","MOONEE-VALLEY (02)",0]
[7397,null,"CENTRE WAY-FRAN","PV0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","CENTRE WAY-FRAN (04)",0]
[7405,null,"CENTRE WAY-FRAN","PV0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","CENTRE WAY-FRAN (04)",7.0293828201883877E-5]
[7410,null,"CENTRE WAY-FRAN","PV0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","CENTRE WAY-FRAN (04)",7.0293828201883877E-5]
[7418,null,"KALANG-PLUMPTON","PV0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","KALANG-PLUMPTON (02)",0]
[7426,null,"PEARL-WHEATSHEAF","PV0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","PEARL-WHEATSHEAF (02)",{"$f":"IF(H7427=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":0}]
[7431,null,"PEARL-WHEATSHEAF","PV0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","PEARL-WHEATSHEAF (02)",0]
[7439,null,"JUSTIN-VIEW","PV0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","JUSTIN-VIEW (03)",0]
[7451,null,"CONNELL-HILTON","PV0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","CONNELL-HILTON (01)",7.0293828201883877E-5]
[7452,null,"ASH-WIDFORD","PV0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","ASH-WIDFORD (01)",0]
[7460,null,"HILTON-CHURCHILL","PV0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","HILTON-CHURCHILL (02)",7.0293828201883877E-5]
[7472,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",0]
[7473,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (02)",0]
[7481,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",0]
[7493,null,"DOROTHY-ALEC","CN0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","DOROTHY-ALEC (01)",7.0293828201883877E-5]
[7494,null,"DOROTHY-ALEC","CN0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","DOROTHY-ALEC (01)",7.0293828201883877E-5]
[7501,null,"MONT ALBERT-RAINSFORD","BD0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","MONT ALBERT-RAINSFORD (01)",7.0293828201883877E-5]
[7513,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (01)",7.0293828201883877E-5]
[7514,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (01)",7.0293828201883877E-5]
[7526,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",7.0293828201883877E-5]
[7534,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",7.0293828201883877E-5]
[7539,null,"GRAHAM-GLEN ALLAN","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","GRAHAM-GLEN ALLAN (03)",7.0293828201883877E-5]
[7547,null,"JOFFRE-KITCHENER","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","JOFFRE-KITCHENER (02)",7.0293828201883877E-5]
[7555,null,"TRESCO-BARRY","BD0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","BD0","TRESCO-BARRY (02)",0]
[7560,null,"COBDEN-BARRY","BD0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","COBDEN-BARRY (01)",7.0293828201883877E-5]
[7568,null,"LYDIA-DUNSTAN","BD0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","LYDIA-DUNSTAN (02)",7.0293828201883877E-5]
[7576,null,"WASHINGTON-DOY","BD0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WASHINGTON-DOY (01)",7.0293828201883877E-5]
[7581,null,"WASHINGTON-DOY","BD0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WASHINGTON-DOY (01)",7.0293828201883877E-5]
[7589,null,"HERBERT-GARNER","BD0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","HERBERT-GARNER (01)",7.0293828201883877E-5]
[7594,null,"HAMPDEN-GEACH","BMS-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","HAMPDEN-GEACH (01)",7.0293828201883877E-5]
[7602,null,"YERING-GUILDFORD","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","YERING-GUILDFORD (01)",7.0293828201883877E-5]
[7610,null,"YERING-GUILDFORD","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","YERING-GUILDFORD (02)",7.0293828201883877E-5]
[7615,null,"YERING-GUILDFORD","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","YERING-GUILDFORD (02)",7.0293828201883877E-5]
[7623,null,"WESTMERE-WARNE","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WESTMERE-WARNE (02)",7.0293828201883877E-5]
[7628,null,"WESTMERE-WARNE","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WESTMERE-WARNE (02)",7.0293828201883877E-5]
[7636,null,"NAREEN-PAISLEY","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","NAREEN-PAISLEY (01)",7.0293828201883877E-5]
[7644,null,"WARRAGUL-LISMORE","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WARRAGUL-LISMORE (01)",7.0293828201883877E-5]
[7649,null,"WARRAGUL-LISMORE","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WARRAGUL-LISMORE (01)",7.0293828201883877E-5]
[7656,null,"CORINELLA-BLAIR","BD0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","CORINELLA-BLAIR (01)",7.0293828201883877E-5]
[7664,null,"YEA-KIEWA","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","YEA-KIEWA (01)",7.0293828201883877E-5]
[7669,null,"YEA-KIEWA","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","YEA-KIEWA (01)",7.0293828201883877E-5]
[7677,null,"YINNAR-BARRY","BD0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","YINNAR-BARRY (03)",7.0293828201883877E-5]
[7682,null,"PHILLIP-MILLEWA","BD0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","PHILLIP-MILLEWA (01)",{"$f":"IF(H7683=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[7690,null,"GOSFORD-NICHOLAS","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","GOSFORD-NICHOLAS (03)",7.0293828201883877E-5]
[7698,null,"BLIBURG-SUNSET","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","BLIBURG-SUNSET (02)",7.0293828201883877E-5]
[7703,null,"HENDRICKS-LORRAINE","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","HENDRICKS-LORRAINE (01)",7.0293828201883877E-5]
[7711,null,"HENDRICKS-LORRAINE","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","HENDRICKS-LORRAINE (01)",7.0293828201883877E-5]
[7719,null,"HENDRICKS-LORRAINE","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","HENDRICKS-LORRAINE (01)",7.0293828201883877E-5]
[7724,null,"TIMBOON-RIPPLEBROOK","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","TIMBOON-RIPPLEBROOK (01)",7.0293828201883877E-5]
[7732,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (02)",7.0293828201883877E-5]
[7737,null,"CAMBRIAN-HIGH","PTN-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","PTN","CAMBRIAN-HIGH (02)",0]
[7745,null,"WEBB-CORONATION","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","WEBB-CORONATION (03)",7.0293828201883877E-5]
[7753,null,"MT ALEXANDER-HOMER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","MT ALEXANDER-HOMER (03)",7.0293828201883877E-5]
[7758,null,"FLEET-STUBB NO2","ST0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","FLEET-STUBB NO2 (00)",7.0293828201883877E-5]
[7766,null,"WATTLEGLEN-SPURR","ST0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","WATTLEGLEN-SPURR (01)",7.0293828201883877E-5]
[7778,null,"DUNKELD-PASCOE VALE","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","DUNKELD-PASCOE VALE (02)",7.0293828201883877E-5]
[7779,null,"ROKEWOOD-APPIN","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","ROKEWOOD-APPIN (02)",7.0293828201883877E-5]
[7787,null,"ROKEWOOD-ELLAM","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","ROKEWOOD-ELLAM (01)",7.0293828201883877E-5]
[7799,null,"MALMSBURY-WOODBURN","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","MALMSBURY-WOODBURN (02)",7.0293828201883877E-5]
[7800,null,"MALMSBURY-WOODBURN","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","MALMSBURY-WOODBURN (01)",7.0293828201883877E-5]
[7811,null,"REDESDALE-GALVIN","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","REDESDALE-GALVIN (01)",7.0293828201883877E-5]
[7819,null,"PASCOE VALE-BENDOC","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","PASCOE VALE-BENDOC (02)",7.0293828201883877E-5]
[7820,null,"LOVAT-LONGFORD","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","LOVAT-LONGFORD (02)",7.0293828201883877E-5]
[7832,null,"ERINBANK-DOBIES","BD0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","ERINBANK-DOBIES (02)",7.0293828201883877E-5]
[7840,null,"BRAMCOTE-FORMAN","AW0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","BRAMCOTE-FORMAN (02)",7.0293828201883877E-5]
[7841,null,"BRAMCOTE-FORMAN","AW0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","BRAMCOTE-FORMAN (02)",7.0293828201883877E-5]
[7853,null,"LARGS-MOTHERWELL","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","LARGS-MOTHERWELL (01)",7.0293828201883877E-5]
[7861,null,"LANGTON-GREENVALE","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","LANGTON-GREENVALE (01)",7.0293828201883877E-5]
[7862,null,"LANGTON-GREENVALE","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","LANGTON-GREENVALE (01)",7.0293828201883877E-5]
[7874,null,"SIMMINGTON-KENTMERE","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","SIMMINGTON-KENTMERE (01)",{"$f":"IF(H7875=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[7882,null,"LANGTON-GREENVALE","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","LANGTON-GREENVALE (01)",7.0293828201883877E-5]
[7887,null,"BRADFORD-KIRBY","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","BRADFORD-KIRBY (02)",7.0293828201883877E-5]
[7895,null,"LANGTON-GREENVALE","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","LANGTON-GREENVALE (01)",7.0293828201883877E-5]
[7903,null,"GREENVALE-WALLACE","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","GREENVALE-WALLACE (02)",7.0293828201883877E-5]
[7908,null,"GREENVALE-WALLACE","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","GREENVALE-WALLACE (02)",7.0293828201883877E-5]
[7916,null,"HANDSWORTH-LACKENHTH","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","HANDSWORTH-LACKENHTH (01)",7.0293828201883877E-5]
[7921,null,"FREIGHT-CUSTOM","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (01)",7.0293828201883877E-5]
[7929,null,"FREIGHT-CUSTOM","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (02)",7.0293828201883877E-5]
[7937,null,"HENLEY-CLARKE","BD0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","HENLEY-CLARKE (02)",7.0293828201883877E-5]
[7942,null,"GREENACRE-AYLESBURY","AW0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","GREENACRE-AYLESBURY (02)",7.0293828201883877E-5]
[7950,null,"PRIOR-TAYLOR","AW0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","PRIOR-TAYLOR (02)",7.0293828201883877E-5]
[7958,null,"SAMARA-ELMHURST","AW0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SAMARA-ELMHURST (02)",7.0293828201883877E-5]
[7964,null,"SAMARA-ELMHURST","AW0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SAMARA-ELMHURST (01)",7.0293828201883877E-5]
[7970,null,"SAMARA-ELMHURST","AW0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SAMARA-ELMHURST (02)",7.0293828201883877E-5]
[7975,null,"HARCOURT-SHERBOURNE","AW0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","HARCOURT-SHERBOURNE (02)",7.0293828201883877E-5]
[7983,null,"HARCOURT-SHERBOURNE","AW0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","HARCOURT-SHERBOURNE (01)",7.0293828201883877E-5]
[7991,null,"HENLEY-CLARKE","BD0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","HENLEY-CLARKE (02)",7.0293828201883877E-5]
[7996,null,"HARDY-SNAEFELL","AW0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","HARDY-SNAEFELL (01)",7.0293828201883877E-5]
[8004,null,"DAVID-RACHELLE","AW0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","DAVID-RACHELLE (02)",0]
[8009,null,"DAVID-RACHELLE","AW0-007","2024-12-01","2024-12-07","Y","N","N","Y","N","N","AW0","DAVID-RACHELLE (02)",0]
[8017,null,"RIVIERA-WARRICK","BY0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","RIVIERA-WARRICK (01)",7.0293828201883877E-5]
[8025,null,"AMIS-VISTA","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","AMIS-VISTA (02)",7.0293828201883877E-5]
[8030,null,"NORWOOD-PROSPECT","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","NORWOOD-PROSPECT (02)",7.0293828201883877E-5]
[8038,null,"AMIS-VISTA","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","AMIS-VISTA (02)",7.0293828201883877E-5]
[8046,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (02)",7.0293828201883877E-5]
[8051,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[8059,null,"VALLEY-AUGUSTINE","PV0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","VALLEY-AUGUSTINE (01)",7.0293828201883877E-5]
[8064,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (05)",7.0293828201883877E-5]
[8072,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (05)",7.0293828201883877E-5]
[8080,null,"MOONEE VLY-RACECRS 3","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOONEE VLY-RACECRS 3 (00)",7.0293828201883877E-5]
[8085,null,"BUCKLEY-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-HODDLE (01)",7.0293828201883877E-5]
[8093,null,"SABRE-GARDEN","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SABRE-GARDEN (00)",7.0293828201883877E-5]
[8101,null,"MARY-ROBERTS","ES0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","MARY-ROBERTS (02)",0]
[8106,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[8113,null,"DUNROSSIL-GORTON","SBY-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","DUNROSSIL-GORTON (03)",7.0293828201883877E-5]
[8125,null,"LATROBE-MENZIES","SBY-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","LATROBE-MENZIES (01)",7.0293828201883877E-5]
[8126,null,"LATROBE-MENZIES","SBY-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","LATROBE-MENZIES (01)",7.0293828201883877E-5]
[8134,null,"PASLEY-NEILL","SBY-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","PASLEY-NEILL (02)",7.0293828201883877E-5]
[8146,null,"BURKE-FLINDERS","SBY-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (01)",7.0293828201883877E-5]
[8147,null,"BURKE-FLINDERS","SBY-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (01)",7.0293828201883877E-5]
[8159,null,"GAP-COWPER","SBY-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","GAP-COWPER (02)",7.0293828201883877E-5]
[8167,null,"HILLVIEW RISE-P3","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","HILLVIEW RISE-P3 (00)",7.0293828201883877E-5]
[8168,null,"BLACKHILL RD-P11","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","BLACKHILL RD-P11 (00)",7.0293828201883877E-5]
[8180,null,"COUANGALT RD-P34","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","COUANGALT RD-P34 (00)",7.0293828201883877E-5]
[8188,null,"GISBORNE MELTON RD-P27W2","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","GISBORNE MELTON RD-P27W1N1 (00)",7.0293828201883877E-5]
[8189,null,"GISBORNE MELTON RD-P27W1N1","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","GISBORNE MELTON RD-P27W2 (00)",7.0293828201883877E-5]
[8201,null,"OUTAWOOD RISE-P1","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","OUTAWOOD RISE-P1 (00)",7.0293828201883877E-5]
[8209,null,"OUTAWOOD RISE-P3","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","OUTAWOOD RISE-P3 (00)",7.0293828201883877E-5]
[8214,null,"RUNNYMEDE LA-P5","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","RUNNYMEDE LA-P5 (00)",7.0293828201883877E-5]
[8222,null,"BLACKHILL RD-P23","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","BLACKHILL RD-P23 (00)",7.0293828201883877E-5]
[8230,null,"KARINYA CRT-P3","SBY-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","KARINYA CRT-P3 (00)",7.0293828201883877E-5]
[8235,null,"WILLIAMSONS RD-P4","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","WILLIAMSONS RD-P4 (00)",7.0293828201883877E-5]
[8243,null,"BOGGYGATE RD-P11","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","BOGGYGATE RD-P11 (00)",7.0293828201883877E-5]
[8248,null,"HILLVIEW DR-P5","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","HILLVIEW DR-P5 (00)",7.0293828201883877E-5]
[8256,null,"HAVELOCK RD-P6","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","Y","N","SBY","HAVELOCK RD-P6 (00)",7.0293828201883877E-5]
[8264,null,"LANCEFIELD RD-P51","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","LANCEFIELD RD-P51 (00)",7.0293828201883877E-5]
[8266,null,"CLARK CRT-P3","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","CLARK CRT-P3 (00)",7.0293828201883877E-5]
[8276,null,"BUCKLEY RD-P10","SHM-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","BUCKLEY RD-P10 (00)",7.0293828201883877E-5]
[8284,null,"BULLA-DIGS REST-P19","SHM-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","BULLA-DIGS REST-P19 (00)",7.0293828201883877E-5]
[8289,null,"DUNCANS LA STH-P3","SHM-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","DUNCANS LA STH-P3 (00)",7.0293828201883877E-5]
[8297,null,"MELTON-MEWS","SHM-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","MELTON-MEWS (01)",7.0293828201883877E-5]
[8302,null,"COIMADAI-TAME","SHM-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","COIMADAI-TAME (01)",7.0293828201883877E-5]
[8310,null,"TURNER-MENZIES","SBY-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","TURNER-MENZIES (01)",7.0293828201883877E-5]
[8318,null,"HIGGINS-MCKELL","SBY-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","HIGGINS-MCKELL (01)",7.0293828201883877E-5]
[8323,null,"HIGGINS-MCKELL","SBY-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","HIGGINS-MCKELL (01)",7.0293828201883877E-5]
[8331,null,"REDGUM-DEEP CREEK","COO-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","COO","REDGUM-DEEP CREEK (00)",0]
[8339,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[8344,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",7.0293828201883877E-5]
[8352,null,"WARRAGUL-LISMORE","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WARRAGUL-LISMORE (01)",7.0293828201883877E-5]
[8357,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[8365,null,"MCCOLL-MALPAS","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MCCOLL-MALPAS (02)",7.0293828201883877E-5]
[8373,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[8378,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",0]
[8386,null,"MARGARET-WINIFRED","PV0-022","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","MARGARET-WINIFRED (01)",{"$f":"IF(H8387=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":0}]
[8391,null,"BICENTENNIAL-SHABA","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","BICENTENNIAL-SHABA (02)",7.0293828201883877E-5]
[8399,null,"FANNY-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FANNY-SALISBURY (01)",7.0293828201883877E-5]
[8407,null,"CRAWFORD-ROBINSON","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (02)",7.0293828201883877E-5]
[8412,null,"WEBSTERS RD N-P4","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","WEBSTERS RD N-P4 (00)",7.0293828201883877E-5]
[8421,null,"LOTUS-CASSINIA","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","LOTUS-CASSINIA (01)",7.0293828201883877E-5]
[8427,null,"YARCOMBE-WOKING","ST0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","YARCOMBE-WOKING (01)",7.0293828201883877E-5]
[8432,null,"WINIFRED-GLASS No2","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WINIFRED-GLASS No2 (01)",7.0293828201883877E-5]
[8440,null,"ASCOT VALE 259-REGENT","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ASCOT VALE 259-REGENT (02)",7.0293828201883877E-5]
[8452,null,"HONEYEATER-CASSOWARY","SHM-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","HONEYEATER-CASSOWARY (01)",7.0293828201883877E-5]
[8453,null,"BICENTENNIAL-SHABA","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","BICENTENNIAL-SHABA (03)",7.0293828201883877E-5]
[8461,null,"MANUKA-LIGHTWOOD","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","MANUKA-LIGHTWOOD (04)",7.0293828201883877E-5]
[8473,null,"KELVIN-ALBERT","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KELVIN-ALBERT (02)",7.0293828201883877E-5]
[8474,null,"HASSETT-BORDER","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","HASSETT-BORDER (03)",7.0293828201883877E-5]
[8482,null,"WEBSTERS RD N-P8","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","WEBSTERS RD N-P8 (00)",7.0293828201883877E-5]
[8494,null,"PUNJEL-CALDER","SHM-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","PUNJEL-CALDER (00)",7.0293828201883877E-5]
[8495,null,"BOGGYGATE RD-P11","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","BOGGYGATE RD-P11 (00)",7.0293828201883877E-5]
[8507,null,"WATERSONS RD-P5E1","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","WATERSONS RD-P5E1 (00)",7.0293828201883877E-5]
[8515,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (04)",7.0293828201883877E-5]
[8516,null,"GREENVALE-WALLACE","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","GREENVALE-WALLACE (02)",7.0293828201883877E-5]
[8528,null,"GLEN-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLEN-GLASS (02)",7.0293828201883877E-5]
[8536,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (03)",7.0293828201883877E-5]
[8541,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (02)",7.0293828201883877E-5]
[8549,null,"ROCKWALL-STAGECOACH","SA0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","SA0","ROCKWALL-STAGECOACH (02)",7.0293828201883877E-5]
[8557,null,"MCPHERSON-BENT","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MCPHERSON-BENT (03)",7.0293828201883877E-5]
[8562,null,"NEWLYN-PEMBROKE","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","NEWLYN-PEMBROKE (03)",7.0293828201883877E-5]
[8570,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (02)",7.0293828201883877E-5]
[8576,null,"DEAKIN-SPENCER","ES0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","DEAKIN-SPENCER (03)",0]
[8582,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (01)",7.0293828201883877E-5]
[8590,null,"JOHNSON-BENAUD","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","JOHNSON-BENAUD (02)",7.0293828201883877E-5]
[8595,null,"RACECOURSE RD-P6","SBY-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","RACECOURSE RD-P6 (00)",7.0293828201883877E-5]
[8603,null,"WYONG-CENTREWAY","AW0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WYONG-CENTREWAY (02)",7.0293828201883877E-5]
[8611,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",7.0293828201883877E-5]
[8616,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[8624,null,"WOOD-BROWN","BY0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","WOOD-BROWN (02)",7.0293828201883877E-5]
[8629,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[8637,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[8645,null,"GRAHAM-GLEN ALLAN","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","GRAHAM-GLEN ALLAN (03)",7.0293828201883877E-5]
[8650,null,"DEAKIN-MARY","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","DEAKIN-MARY (02)",7.0293828201883877E-5]
[8658,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (02)",7.0293828201883877E-5]
[8666,null,"LISTON-JOHNSON","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LISTON-JOHNSON (01)",7.0293828201883877E-5]
[8671,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (01)",7.0293828201883877E-5]
[8679,null,"GAP-COWPER","SBY-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","GAP-COWPER (01)",7.0293828201883877E-5]
[8684,null,"NICHOLSON-BRONCO","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","NICHOLSON-BRONCO (03)",7.0293828201883877E-5]
[8692,null,"LAUREL-TYLER","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","LAUREL-TYLER (01)",0]
[8700,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[8705,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (01)",7.0293828201883877E-5]
[8713,null,"ASQUITH-STURDEE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ASQUITH-STURDEE (01)",7.0293828201883877E-5]
[8721,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[8729,null,"ASQUITH-STURDEE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ASQUITH-STURDEE (01)",7.0293828201883877E-5]
[8733,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (01)",7.0293828201883877E-5]
[8738,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (01)",7.0293828201883877E-5]
[8746,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[8754,null,"BIMBADEEN-YALLAMBIE","NH0-002","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",7.0293828201883877E-5]
[8759,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[8767,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[8779,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (01)",7.0293828201883877E-5]
[8780,null,null,null,"2024-12-01","2024-12-07","Y","N","N","N","N","N",null,"THE GLADE-SHERLOWE (01)",0]
[8788,null,"WILLOWTREE-PERSICA","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (04)",7.0293828201883877E-5]
[8800,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[8801,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[8809,null,"FANNY-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FANNY-SALISBURY (01)",7.0293828201883877E-5]
[8821,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[8822,null,"BLAKE-SESTON","NH0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","BLAKE-SESTON (02)",7.0293828201883877E-5]
[8834,null,"GREENVALE-WALLACE","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","GREENVALE-WALLACE (03)",{"$f":"IF(H8835=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[8842,null,"JOHNSON-BENAUD","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","JOHNSON-BENAUD (02)",7.0293828201883877E-5]
[8843,null,"CRANWELL-CARNARVON","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRANWELL-CARNARVON (04)",7.0293828201883877E-5]
[8855,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[8863,null,"ASQUITH-STURDEE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ASQUITH-STURDEE (01)",7.0293828201883877E-5]
[8868,null,"FAWKNER-ROBERTS","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FAWKNER-ROBERTS (02)",7.0293828201883877E-5]
[8876,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[8878,null,"BELLEVUE-SWANSTON","EP0-027","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BELLEVUE-SWANSTON (02)",7.0293828201883877E-5]
[8888,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (02)",7.0293828201883877E-5]
[8896,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[8904,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[8909,null,"MT ALEXANDER 902-WILLOW","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER 902-WILLOW (02)",7.0293828201883877E-5]
[8917,null,"MADDEN-STUDLEY","FW0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","MADDEN-STUDLEY (02)",7.0293828201883877E-5]
[8922,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[8930,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (04)",7.0293828201883877E-5]
[8938,null,"MT ALEXANDER-HOMER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","MT ALEXANDER-HOMER (03)",7.0293828201883877E-5]
[8943,null,"LEDGER-MAJOR","CN0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","LEDGER-MAJOR (01)",7.0293828201883877E-5]
[8951,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[8959,null,"AYR-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","AYR-DAREBIN (02)",7.0293828201883877E-5]
[8964,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[8972,null,"BLAKE-SESTON","NH0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","BLAKE-SESTON (02)",7.0293828201883877E-5]
[8977,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (01)",7.0293828201883877E-5]
[8985,null,"MAGDALA-WOODLAND","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MAGDALA-WOODLAND (02)",7.0293828201883877E-5]
[8993,null,"LOTUS-CASSINIA","BD0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","LOTUS-CASSINIA (01)",7.0293828201883877E-5]
[8998,null,"THE GRANGE-YALLAMBIE","NH0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","THE GRANGE-YALLAMBIE (03)",7.0293828201883877E-5]
[9006,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[9011,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (01)",7.0293828201883877E-5]
[9019,null,"WILLOWTREE-PERSICA","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (01)",7.0293828201883877E-5]
[9029,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[9031,null,"CATHERINE-SAINSBURY","SHM-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","CATHERINE-SAINSBURY (03)",7.0293828201883877E-5]
[9039,null,"DEAKIN-MARY","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","DEAKIN-MARY (02)",7.0293828201883877E-5]
[9047,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (02)",7.0293828201883877E-5]
[9052,null,"ASQUITH-STURDEE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ASQUITH-STURDEE (01)",7.0293828201883877E-5]
[9060,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[9065,null,"KELVIN-ALBERT","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KELVIN-ALBERT (01)",7.0293828201883877E-5]
[9073,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[9081,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[9086,null,"JULIET-BENT","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JULIET-BENT (01)",7.0293828201883877E-5]
[9094,null,"WAKELIN-STREETON","SHM-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","WAKELIN-STREETON (01)",7.0293828201883877E-5]
[9102,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[9107,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[9115,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[9127,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[9128,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[9136,null,"JULIET-BENT","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JULIET-BENT (03)",7.0293828201883877E-5]
[9148,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",7.0293828201883877E-5]
[9149,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",7.0293828201883877E-5]
[9161,null,"BLACKHILL RD-P7E2","SBY-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","BLACKHILL RD-P7E2 (00)",7.0293828201883877E-5]
[9169,null,"ROSS-ELIZABETH","NT0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NT0","ROSS-ELIZABETH (02)",7.0293828201883877E-5]
[9170,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[9182,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (03)",7.0293828201883877E-5]
[9189,null,"ALANBRAE-STONEBRIDGE","AW0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","ALANBRAE-STONEBRIDGE (03)",7.0293828201883877E-5]
[9190,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (01)",7.0293828201883877E-5]
[9202,null,"CRAWFORD-ROBINSON","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (01)",7.0293828201883877E-5]
[9210,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[9215,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",7.0293828201883877E-5]
[9223,null,"HYDE-BRISTOW","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HYDE-BRISTOW (02)",7.0293828201883877E-5]
[9231,null,"FAWKNER-ROBERTS","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FAWKNER-ROBERTS (02)",7.0293828201883877E-5]
[9236,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[9244,null,"MT ALEXANDER 902-WILLOW","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER 902-WILLOW (02)",7.0293828201883877E-5]
[9249,null,"COLLINS-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","OUTHWAITE-MCEWAN (04)",7.0293828201883877E-5]
[9257,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (00)",7.0293828201883877E-5]
[9265,null,"BERRIMA-ROSANNA","NH0-020","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","BERRIMA-ROSANNA (02)",0]
[9270,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[9278,null,"CHAPMAN-GRANDVIEW","PV0-031","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","CHAPMAN-GRANDVIEW (01)",7.0293828201883877E-5]
[9286,null,"MANOEL-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MANOEL-DAREBIN (01)",7.0293828201883877E-5]
[9291,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",7.0293828201883877E-5]
[9299,null,"BLENHEIM-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (02)",0]
[9304,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (01)",7.0293828201883877E-5]
[9312,null,"BREWSTER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-NAPIER (03)",7.0293828201883877E-5]
[9320,null,"GLENGYLE-NICHOLSON","CS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","GLENGYLE-NICHOLSON (02)",7.0293828201883877E-5]
[9325,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (02)",7.0293828201883877E-5]
[9331,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[9340,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[9345,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[9353,null,"BREWSTER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-NAPIER (03)",7.0293828201883877E-5]
[9358,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[9366,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[9374,null,"LYON-MARTINS","NH0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","LYON-MARTINS (02)",7.0293828201883877E-5]
[9379,null,"BROWNING-MOORE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BROWNING-MOORE (02)",7.0293828201883877E-5]
[9387,null,"ALLENBY-ERIN","SHM-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","ALLENBY-ERIN (02)",7.0293828201883877E-5]
[9392,null,"WYONG-CENTREWAY","AW0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WYONG-CENTREWAY (01)",7.0293828201883877E-5]
[9400,null,"SEVERN-BENBOW","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",7.0293828201883877E-5]
[9408,null,"MT ALEXANDER-HOMER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","MT ALEXANDER-HOMER (03)",7.0293828201883877E-5]
[9413,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (01)",7.0293828201883877E-5]
[9421,null,"HOTHAM-RYDER No. 2","AW0-006","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","HOTHAM-RYDER No. 2 (03)",0]
[9429,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (03)",7.0293828201883877E-5]
[9434,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[9442,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (01)",7.0293828201883877E-5]
[9454,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[9455,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[9463,null,"ACACIA-PARKSIDE","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ACACIA-PARKSIDE (01)",7.0293828201883877E-5]
[9475,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[9476,null,"FREIGHT-CUSTOM","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (02)",7.0293828201883877E-5]
[9486,null,"PASCOE VALE-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","PASCOE VALE-MT ALEXANDER (04)",7.0293828201883877E-5]
[9495,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[9496,null,"MCCARRON-FORRESTER","ES0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","MCCARRON-FORRESTER (01)",7.0293828201883877E-5]
[9508,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[9516,null,"JACKA-JOYNT","NH0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","JACKA-JOYNT (01)",7.0293828201883877E-5]
[9517,null,"DARLING-WHITE","FF0-095","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FF0","DARLING-WHITE (03)",0]
[9529,null,"BROADHURST-MCFADZEAN","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROADHURST-MCFADZEAN (02)",7.0293828201883877E-5]
[9537,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (01)",7.0293828201883877E-5]
[9542,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (03)",7.0293828201883877E-5]
[9550,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (03)",7.0293828201883877E-5]
[9558,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[9563,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",7.0293828201883877E-5]
[9571,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (01)",7.0293828201883877E-5]
[9579,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[9584,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (02)",7.0293828201883877E-5]
[9592,null,"WALLIS-KEILOR","ES0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","WALLIS-KEILOR (01)",7.0293828201883877E-5]
[9597,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (01)",7.0293828201883877E-5]
[9605,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[9613,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (01)",7.0293828201883877E-5]
[9618,null,"FINK-CHIFLEY","EP0-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FINK-CHIFLEY (02)",7.0293828201883877E-5]
[9626,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (04)",7.0293828201883877E-5]
[9631,null,"BERRIMA-ROSANNA","NH0-020","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NH0","BERRIMA-ROSANNA (02)",0]
[9639,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (01)",7.0293828201883877E-5]
[9646,null,"DEAKIN-MARY","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","DEAKIN-MARY (02)",7.0293828201883877E-5]
[9651,null,"ROKEWOOD-ELLAM","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","ROKEWOOD-ELLAM (01)",7.0293828201883877E-5]
[9659,null,"BANK-MT ALEXANDER","FT0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","BANK-MT ALEXANDER (03)",7.0293828201883877E-5]
[9667,null,"BLENHEIM-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (01)",0]
[9672,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[9680,null,"DONALD-LAWSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",7.0293828201883877E-5]
[9685,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[9693,null,"ASQUITH-STURDEE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ASQUITH-STURDEE (01)",7.0293828201883877E-5]
[9701,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",7.0293828201883877E-5]
[9706,null,"ROWE-YARRALEA","FF0-093","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","ROWE-YARRALEA (02)",7.0293828201883877E-5]
[9714,null,"EDDY-TAYLOR","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","EDDY-TAYLOR (01)",7.0293828201883877E-5]
[9722,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (02)",7.0293828201883877E-5]
[9727,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[9735,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (03)",7.0293828201883877E-5]
[9740,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[9748,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[9756,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[9761,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[9769,null,"KITCHENER-MURRAY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","KITCHENER-MURRAY (02)",7.0293828201883877E-5]
[9781,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","SOUTH-DERBY (02)",0]
[9782,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",7.0293828201883877E-5]
[9794,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",{"$f":"IF(H9795=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[9801,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (01)",7.0293828201883877E-5]
[9802,null,"BUCKLEY-MCPHERSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-MCPHERSON (04)",7.0293828201883877E-5]
[9810,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",0]
[9822,null,"DELAWARE-MENDIP","CN0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","DELAWARE-MENDIP (03)",7.0293828201883877E-5]
[9823,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[9835,null,"BARNET-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","BARNET-MACKAY (01)",7.0293828201883877E-5]
[9843,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[9844,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (03)",7.0293828201883877E-5]
[9856,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[9864,null,"LAWSON-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LAWSON-SALISBURY (03)",7.0293828201883877E-5]
[9869,null,"KALANG-PLUMPTON","PV0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","KALANG-PLUMPTON (02)",0]
[9877,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (02)",7.0293828201883877E-5]
[9885,null,"BROWNING-GAMON","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","BROWNING-GAMON (02)",7.0293828201883877E-5]
[9890,null,"MOORE-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE-PUCKLE (04)",7.0293828201883877E-5]
[9898,null,"HUTCHESON-THE STRAND","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (01)",7.0293828201883877E-5]
[9906,null,"HODDLE-FLETCHER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (03)",7.0293828201883877E-5]
[9911,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[9919,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KERFERD-RALEIGH (02)",7.0293828201883877E-5]
[9924,null,"KELLAWAY-GORDON","BY0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","KELLAWAY-GORDON (01)",7.0293828201883877E-5]
[9932,null,"HOBBS-BROADHURST","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HOBBS-BROADHURST (02)",7.0293828201883877E-5]
[9940,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[9947,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[9952,null,"BRAY-BARTROP","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRAY-BARTROP (02)",7.0293828201883877E-5]
[9960,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[9965,null,"PERIGRINE-DEEP CREEK","COO-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","COO","PERIGRINE-DEEP CREEK (00)",0]
[9973,null,"AYR-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","AYR-DAREBIN (01)",7.0293828201883877E-5]
[9978,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (01)",7.0293828201883877E-5]
[9986,null,"CAPULET-BENT","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAPULET-BENT (03)",{"$f":"IF(H9987=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[9994,null,"BREWSTER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-NAPIER (03)",7.0293828201883877E-5]
[9999,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[10007,null,"ALMA-ELPHINSTONE","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","ALMA-ELPHINSTONE (02)",7.0293828201883877E-5]
[10012,null,"BUCKLEY-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-MT ALEXANDER (03)",7.0293828201883877E-5]
[10020,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",0]
[10028,null,"ALEXANDER-JOHN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","DICKSON-WILLIAMSTOWN (03)",7.0293828201883877E-5]
[10033,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[10041,null,"NEWCASTLE-DUNDAS","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NEWCASTLE-DUNDAS (02)",7.0293828201883877E-5]
[10049,null,"JOHNSON-BENAUD","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","JOHNSON-BENAUD (01)",7.0293828201883877E-5]
[10054,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",7.0293828201883877E-5]
[10062,null,"McPHERSON-ALEXANDRA 2","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (04)",7.0293828201883877E-5]
[10067,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[10075,null,"MOORE-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE-PUCKLE (03)",7.0293828201883877E-5]
[10083,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (02)",7.0293828201883877E-5]
[10088,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (02)",7.0293828201883877E-5]
[10096,null,"ETZEL-CLYDESDALE","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","ETZEL-CLYDESDALE (01)",7.0293828201883877E-5]
[10103,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[10108,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[10116,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[10128,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",7.0293828201883877E-5]
[10129,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[10137,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",7.0293828201883877E-5]
[10149,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KERFERD-RALEIGH (02)",7.0293828201883877E-5]
[10150,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (01)",7.0293828201883877E-5]
[10162,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",0]
[10170,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[10171,null,"BROADHURST-MCFADZEAN","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","OCONNOR-MACFADZEAN (02)",7.0293828201883877E-5]
[10183,null,"HYDE 258-KENT","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HYDE 258-KENT (02)",7.0293828201883877E-5]
[10191,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",7.0293828201883877E-5]
[10192,null,"MACK-HARMER","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-HARMER (03)",7.0293828201883877E-5]
[10204,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (01)",7.0293828201883877E-5]
[10212,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (01)",7.0293828201883877E-5]
[10217,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[10225,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (02)",7.0293828201883877E-5]
[10233,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (03)",7.0293828201883877E-5]
[10238,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (02)",7.0293828201883877E-5]
[10246,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (03)",7.0293828201883877E-5]
[10249,null,"WORDSWORTH-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WORDSWORTH-MT ALEXANDER (01)",7.0293828201883877E-5]
[10258,null,"CAPULET-BENT","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAPULET-BENT (03)",7.0293828201883877E-5]
[10266,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",7.0293828201883877E-5]
[10271,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[10279,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[10287,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",7.0293828201883877E-5]
[10292,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[10300,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (03)",7.0293828201883877E-5]
[10305,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[10313,null,"THE CROSSWAY-PARK","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","THE CROSSWAY-PARK (01)",7.0293828201883877E-5]
[10321,null,"SOUTHEY-ARDEN","FT0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",7.0293828201883877E-5]
[10326,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[10334,null,"WALLACE-KENILWORTH","FF0-090","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",7.0293828201883877E-5]
[10342,null,"HOBBS-PENTLAND","FE0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",7.0293828201883877E-5]
[10347,null,"BELL-ORIEL","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BELL-ORIEL (01)",7.0293828201883877E-5]
[10355,null,"MARSHALL-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MARSHALL-INVERMAY (01)",7.0293828201883877E-5]
[10360,null,"SUSSEX-HOLMES","ES0-024","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","ES0","SUSSEX-HOLMES (02)",7.0293828201883877E-5]
[10368,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[10376,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[10381,null,"BREX-RADFORD","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BREX-RADFORD (00)",7.0293828201883877E-5]
[10389,null,"BERRY-KEILOR","ES0-026","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","BERRY-KEILOR (03)",0]
[10394,null,"PORTER-DOUGHARTY","NH0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NH0","PORTER-DOUGHARTY (01)",0]
[10404,null,"WATERDALE-GRIFFITHS","EPN-033","2024-12-01","2024-12-07","Y","N","N","Y","N","N","EPN","WATERDALE-GRIFFITHS (01)",0]
[10409,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[10414,null,"ALEXANDER-JOHN","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","DICKSON-WILLIAMSTOWN (03)",7.0293828201883877E-5]
[10422,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[10430,null,"ALEXANDRA-PASCOEVALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALEXANDRA-PASCOEVALE (02)",7.0293828201883877E-5]
[10435,null,"WARNER-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WARNER-GLASS (01)",7.0293828201883877E-5]
[10443,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",7.0293828201883877E-5]
[10455,null,"GELLIBRAND-STEWART","NT0-015","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","GELLIBRAND-STEWART (02)",0]
[10456,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (02)",7.0293828201883877E-5]
[10464,null,"CAPE-YARRA","HB0-031","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","CAPE-YARRA (01)",0]
[10476,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",7.0293828201883877E-5]
[10477,null,"LAWSON-KENDALL","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LAWSON-KENDALL (03)",7.0293828201883877E-5]
[10485,null,"SALWEEN-ELSA","ST0-012","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","ST0","SALWEEN-ELSA (04)",7.0293828201883877E-5]
[10497,null,"CUMBERLAND-KENT","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CUMBERLAND-KENT (04)",0]
[10498,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",{"$f":"IF(H10499=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[10510,null,"RENFEW-ARKLEY","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","RENFEW-ARKLEY (01)",7.0293828201883877E-5]
[10518,null,"COOPER ST-P43","ST0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","COOPER ST-P43 (01)",7.0293828201883877E-5]
[10519,null,"CUMBERLAND-KENT","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CUMBERLAND-KENT (04)",0]
[10531,null,"SALWEEN-ELSA","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","SALWEEN-ELSA (04)",7.0293828201883877E-5]
[10539,null,"HUNT-BAXTER","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",0]
[10544,null,"BARNET-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","BARNET-MACKAY (01)",7.0293828201883877E-5]
[10552,null,"COLLINS-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","COLLINS-WATERDALE (02)",7.0293828201883877E-5]
[10559,null,"PLENTY-HARDIMAN RES","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PLENTY-HARDIMAN RES (01)",7.0293828201883877E-5]
[10564,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[10572,null,"ALBERT-HARROW","EPN-035","2024-12-01","2024-12-07","Y","N","N","Y","N","N","EPN","ALBERT-HARROW (02)",0]
[10580,null,"FINK-CHIFLEY","EP0-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FINK-CHIFLEY (02)",7.0293828201883877E-5]
[10585,null,"CAPE-YARRA","HB0-031","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","CAPE-YARRA (01)",0]
[10593,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",7.0293828201883877E-5]
[10598,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[10606,null,"PASCOE VALE-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","PASCOE VALE-MT ALEXANDER (04)",7.0293828201883877E-5]
[10614,null,"BUCKLEY-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-MT ALEXANDER (01)",7.0293828201883877E-5]
[10619,null,"DONALD-LAWSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",7.0293828201883877E-5]
[10627,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (03)",7.0293828201883877E-5]
[10632,null,"MARY-ROBERTS","ES0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","MARY-ROBERTS (02)",0]
[10640,null,"FREIGHT-CUSTOM","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (01)",7.0293828201883877E-5]
[10648,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (01)",7.0293828201883877E-5]
[10653,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[10661,null,"SALWEEN-ELSA","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","SALWEEN-ELSA (04)",7.0293828201883877E-5]
[10669,null,"FULLWOOD-WHEELER","SBY-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","FULLWOOD-WHEELER (03)",7.0293828201883877E-5]
[10674,null,"DUNCAN-ASCOT VALE","FT0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","DUNCAN-ASCOT VALE (01)",7.0293828201883877E-5]
[10682,null,"MT ALEXANDER 902-WILLOW","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER 902-WILLOW (02)",7.0293828201883877E-5]
[10687,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[10695,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[10703,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",7.0293828201883877E-5]
[10712,null,"SANDOVER-SALWEEN","ST0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","SANDOVER-SALWEEN (04)",7.0293828201883877E-5]
[10715,null,"LAWSON-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LAWSON-SALISBURY (03)",7.0293828201883877E-5]
[10723,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[10728,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[10736,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[10741,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (02)",7.0293828201883877E-5]
[10749,null,"SEXTON-HALSEY","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SEXTON-HALSEY (04)",7.0293828201883877E-5]
[10757,null,"INVERMAY-BELLEVUE","NH0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","INVERMAY-BELLEVUE (01)",0]
[10762,null,"MELTON-MEWS","SHM-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","MELTON-MEWS (04)",7.0293828201883877E-5]
[10770,null,"WILLOWTREE-PERSICA","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (01)",7.0293828201883877E-5]
[10782,null,"JOHNSON-BENAUD","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","JOHNSON-BENAUD (01)",7.0293828201883877E-5]
[10783,null,"RENFEW-ARKLEY","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","RENFEW-ARKLEY (02)",7.0293828201883877E-5]
[10791,null,"RENFEW-ARKLEY","COO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","RENFEW-ARKLEY (02)",7.0293828201883877E-5]
[10803,null,"THE CREST-HILLCREST","SHM-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","THE CREST-HILLCREST (04)",7.0293828201883877E-5]
[10804,null,"SEXTON-HALSEY","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SEXTON-HALSEY (04)",7.0293828201883877E-5]
[10812,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (01)",7.0293828201883877E-5]
[10824,null,"COPE-UCM 1","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","COPE-UCM 1 (02)",7.0293828201883877E-5]
[10825,null,"COPE-UCM 1","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","COPE-UCM 1 (02)",7.0293828201883877E-5]
[10837,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (01)",7.0293828201883877E-5]
[10845,null,"SANDOVER-SALWEEN","ST0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","SANDOVER-SALWEEN (04)",7.0293828201883877E-5]
[10846,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[10858,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[10861,null,"SOUTH-BELL","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","SOUTH-BELL (02)",7.0293828201883877E-5]
[10870,null,"JAMES-WILLIAMSON","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JAMES-WILLIAMSON (01)",7.0293828201883877E-5]
[10878,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[10886,null,"O'CONNOR-WHITBY","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","OCONNOR-MACFADZEAN (04)",0]
[10891,null,"BELL-ORIEL","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BELL-ORIEL (02)",7.0293828201883877E-5]
[10899,null,"BLENHEIM-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (02)",0]
[10907,null,"MARY-BRUCE","PTN-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARY-BRUCE (01)",7.0293828201883877E-5]
[10912,null,"CRAMER-MARKET NO2","PTN-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","CRAMER-MARKET NO2 (01)",7.0293828201883877E-5]
[10920,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[10925,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[10933,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[10941,null,"PRATT-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PRATT-PUCKLE (03)",7.0293828201883877E-5]
[10946,null,"PRATT-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PRATT-PUCKLE (03)",{"$f":"IF(H10947=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[10954,null,"PRATT-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PRATT-PUCKLE (03)",7.0293828201883877E-5]
[10962,null,"BREWSTER-PASCOE VALE","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[10967,null,"LAKES-THE GREENWAY","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","LAKES-THE GREENWAY (04)",7.0293828201883877E-5]
[10975,null,"CHIFLEY 68-RENNICK","EP0-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","CHIFLEY 68-RENNICK (05)",7.0293828201883877E-5]
[10980,null,"DRESS CIRCLE-THE RIDGE 1","COO-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","COO","DRESS CIRCLE-THE RIDGE 1 (01)",0]
[10988,null,"WILLOWTREE-PERSICA","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (04)",7.0293828201883877E-5]
[10996,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUTLER-PASCOE VALE (00)",7.0293828201883877E-5]
[11001,null,"INVERNESS-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERNESS-INVERMAY (02)",7.0293828201883877E-5]
[11009,null,"SOUTH-BELL","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",7.0293828201883877E-5]
[11014,null,"HUME HWY-P69","ST0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","HUME HWY-P69 (01)",7.0293828201883877E-5]
[11021,null,"VANBERG-TENNYSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","VANBERG-TENNYSON (03)",7.0293828201883877E-5]
[11029,null,"PORTER-DOUGHARTY","NH0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","PORTER-DOUGHARTY (02)",0]
[11034,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (02)",7.0293828201883877E-5]
[11042,null,"THE RIDGE-DEEP CREEK 5","COO-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","COO","THE RIDGE-DEEP CREEK 5 (01)",0]
[11050,null,"ROSEHILL-ROSE","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","ROSEHILL-ROSE (02)",7.0293828201883877E-5]
[11055,null,"BLAKE-SESTON","NH0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","BLAKE-SESTON (02)",7.0293828201883877E-5]
[11063,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[11068,null,"MOUSHALL-HOFFMANS","ES0-021","2024-12-01","2024-12-07","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (01)",0]
[11076,null,"WESTS-WILLIAMSON 2","YVE-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","YVE","WESTS-WILLIAMSON 2 (03)",7.0293828201883877E-5]
[11084,null,"WESTS-WILLIAMSON 2","YVE-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","YVE","WESTS-WILLIAMSON 2 (03)",7.0293828201883877E-5]
[11089,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (02)",7.0293828201883877E-5]
[11097,null,"NEWMAN-HOTHAM","AW0-007","2024-12-01","2024-12-07","Y","N","N","Y","N","N","AW0","NEWMAN-HOTHAM (03)",0]
[11105,null,"DONVALE-HAYFIELD","ST0-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","DONVALE-HAYFIELD (01)",7.0293828201883877E-5]
[11110,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (01)",7.0293828201883877E-5]
[11118,null,"EMU RD-P3","SBY-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","EMU RD-P3 (00)",7.0293828201883877E-5]
[11130,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (02)",7.0293828201883877E-5]
[11131,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (02)",7.0293828201883877E-5]
[11139,null,"LILLEE 60-MALLETT","TMA-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","TMA","LILLEE 60-MALLETT (03)",7.0293828201883877E-5]
[11151,null,"LILLEE 60-MALLETT","TMA-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","TMA","LILLEE 60-MALLETT (03)",7.0293828201883877E-5]
[11152,null,"LEBANON-ELDORADO","PV0-022","2024-12-01","2024-12-07","Y","N","N","Y","N","N","PV0","LEBANON-ELDORADO (02)",0]
[11164,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (03)",7.0293828201883877E-5]
[11169,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (03)",7.0293828201883877E-5]
[11172,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (03)",7.0293828201883877E-5]
[11184,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (03)",7.0293828201883877E-5]
[11192,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (03)",7.0293828201883877E-5]
[11193,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (03)",7.0293828201883877E-5]
[11205,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (03)",7.0293828201883877E-5]
[11213,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (03)",7.0293828201883877E-5]
[11218,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (03)",7.0293828201883877E-5]
[11226,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[11234,null,"CARROL-ORRONG","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CARROL-ORRONG (01)",7.0293828201883877E-5]
[11239,null,"BROWNING-MOORE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BROWNING-MOORE (01)",7.0293828201883877E-5]
[11247,null,"BREX-RADFORD","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BREX-RADFORD (00)",7.0293828201883877E-5]
[11252,null,"SCARVELL-PRO HART","SHM-021","2024-12-01","2024-12-07","N","Y","N","N","Y","N","SHM","SCARVELL-PRO HART (02)",7.0293828201883877E-5]
[11260,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[11268,null,"COVENTRY-MALVERN","AW0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","COVENTRY-MALVERN (02)",7.0293828201883877E-5]
[11273,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[11281,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[11289,null,"JOHN-WINIFRED","PV0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","JOHN-WINIFRED (01)",7.0293828201883877E-5]
[11294,null,"DONVALE-HAYFIELD","ST0-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","DONVALE-HAYFIELD (01)",7.0293828201883877E-5]
[11302,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[11307,null,"MALACCA-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","MALACCA-WATERDALE (02)",7.0293828201883877E-5]
[11315,null,"HUME 1445-CAMP","BMS-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","HUME 1445-CAMP (04)",7.0293828201883877E-5]
[11324,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (02)",7.0293828201883877E-5]
[11327,null,"ALBERT-HARROW","EPN-035","2024-12-01","2024-12-07","Y","N","N","Y","N","N","EPN","ALBERT-HARROW (02)",0]
[11335,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[11343,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[11348,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (01)",7.0293828201883877E-5]
[11356,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (03)",7.0293828201883877E-5]
[11361,null,"MOUSHALL-HOFFMANS","ES0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","MOUSHALL-HOFFMANS (02)",0]
[11369,null,"NEWCASTLE-DUNDAS","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NEWCASTLE-DUNDAS (02)",7.0293828201883877E-5]
[11377,null,"BOOMERANG-AIRFORCE","TH0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",7.0293828201883877E-5]
[11382,null,"MT ALEXANDER-HOMER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","MT ALEXANDER-HOMER (04)",7.0293828201883877E-5]
[11390,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (01)",7.0293828201883877E-5]
[11395,null,"SALMON-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALMON-SCHOFIELD (01)",7.0293828201883877E-5]
[11403,null,"BOOMERANG-AIRFORCE","TH0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",7.0293828201883877E-5]
[11411,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (03)",7.0293828201883877E-5]
[11416,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (04)",7.0293828201883877E-5]
[11424,null,"GLASS-NAPIER NO.2","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER NO.2 (02)",7.0293828201883877E-5]
[11432,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[11437,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",7.0293828201883877E-5]
[11445,null,"SEPARATION-PERRY","FF0-093","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","SEPARATION-PERRY (04)",7.0293828201883877E-5]
[11457,null,"LONG ISLAND-ROYAL TROON","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","LONG ISLAND-ROYAL TROON (01)",7.0293828201883877E-5]
[11458,null,"JUSTIN-VIEW","PV0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","JUSTIN-VIEW (03)",{"$f":"IF(H11459=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":0}]
[11466,null,"BLAKE-SESTON","NH0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","BLAKE-SESTON (02)",7.0293828201883877E-5]
[11477,null,"WEST-KINGSLEY","AW0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","WEST-KINGSLEY (01)",0]
[11478,null,"STEELE-STUART","FT0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","FT0","STEELE-STUART (01)",0]
[11490,null,"ASHBY-LOCKSLEY","HB0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","HB0","ASHBY-LOCKSLEY (01)",0]
[11498,null,"PAYWIT-BELLARINE","PTN-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","PAYWIT-BELLARINE (02)",7.0293828201883877E-5]
[11499,null,"REDGUM-DEEP CREEK","COO-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","COO","REDGUM-DEEP CREEK (00)",0]
[11511,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[11519,null,"VIMY-VICKERS","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","VIMY-VICKERS (02)",7.0293828201883877E-5]
[11520,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (01)",7.0293828201883877E-5]
[11532,null,"FANNY-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FANNY-SALISBURY (01)",7.0293828201883877E-5]
[11540,null,"STEWART-PASCOE VALE","PV0-022","2024-12-01","2024-12-07","Y","N","N","Y","N","N","PV0","STEWART-PASCOE VALE (01)",0]
[11545,null,"HOMER-EDDY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HOMER-EDDY (03)",7.0293828201883877E-5]
[11553,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","YALLAMBIE-LOWER PLENTY (01)",0]
[11561,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (02)",7.0293828201883877E-5]
[11566,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[11574,null,"HOMER-EDDY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HOMER-EDDY (03)",7.0293828201883877E-5]
[11582,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (03)",7.0293828201883877E-5]
[11587,null,"BOOMERANG-AIRFORCE","TH0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",7.0293828201883877E-5]
[11595,null,"ASCOT VALE 331-YOUNG","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ASCOT VALE 331-YOUNG (01)",7.0293828201883877E-5]
[11600,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[11608,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[11616,null,"ROSEBERRY-HIGH","PTN-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","ROSEBERRY-HIGH (03)",7.0293828201883877E-5]
[11621,null,"SALMON-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALMON-SCHOFIELD (01)",7.0293828201883877E-5]
[11626,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[11633,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (02)",7.0293828201883877E-5]
[11641,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (04)",7.0293828201883877E-5]
[11649,null,"OXFORD-JUNCTION","NT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","NT0","OXFORD-JUNCTION (01)",7.0293828201883877E-5]
[11654,null,"BOOMERANG-AIRFORCE","TH0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",7.0293828201883877E-5]
[11662,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",7.0293828201883877E-5]
[11670,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[11675,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[11683,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[11688,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[11696,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[11704,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","BOND-LIBERTY (01)",7.0293828201883877E-5]
[11709,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","BOND-LIBERTY (01)",7.0293828201883877E-5]
[11717,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (02)",7.0293828201883877E-5]
[11725,null,"LEWIS-WILLIAMS","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",0]
[11730,null,"CORINELLA-BLAIR","BD0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","CORINELLA-BLAIR (01)",7.0293828201883877E-5]
[11738,null,"HAMPDEN-CROTHERS","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",7.0293828201883877E-5]
[11743,null,"KENNETH-GOWER","EPN-035","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","KENNETH-GOWER (01)",0]
[11751,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (01)",7.0293828201883877E-5]
[11759,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (02)",7.0293828201883877E-5]
[11764,null,"LYSTERFIELD-BEECHWORTH","ST0-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","LYSTERFIELD-BEECHWORTH (01)",7.0293828201883877E-5]
[11772,null,"HUME 1487-THOMPSON","BMS-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","HUME 1487-THOMPSON (02)",7.0293828201883877E-5]
[11779,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",7.0293828201883877E-5]
[11784,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[11792,null,"BOOMERANG-AIRFORCE","TH0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",7.0293828201883877E-5]
[11804,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (02)",7.0293828201883877E-5]
[11805,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (02)",7.0293828201883877E-5]
[11813,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (02)",7.0293828201883877E-5]
[11825,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (02)",7.0293828201883877E-5]
[11826,null,"CLYDEBANK-AFTON","ES0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","CLYDEBANK-AFTON (01)",0]
[11838,null,"ROSEBERRY-HIGH","PTN-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","ROSEBERRY-HIGH (03)",7.0293828201883877E-5]
[11846,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (01)",7.0293828201883877E-5]
[11847,null,"HUME 1487-THOMPSON","BMS-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","HUME 1487-THOMPSON (02)",7.0293828201883877E-5]
[11859,null,"WUNNAMURRA-WONGANELA","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WUNNAMURRA-WONGANELA (01)",7.0293828201883877E-5]
[11867,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",0]
[11872,null,"McPHERSON-ALEXANDRA 2","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (01)",7.0293828201883877E-5]
[11880,null,"MCNABS-ARUNDEL 3","SA0-002","2024-12-01","2024-12-07","N","Y","N","N","N","N","SA0","MCNABS-ARUNDEL 3 (00)",7.0293828201883877E-5]
[11888,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[11893,null,"PARKSIDE-HIGHVIEW","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","PARKSIDE-HIGHVIEW (03)",7.0293828201883877E-5]
[11901,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",7.0293828201883877E-5]
[11909,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[11914,null,"ALAMEIN-SOUTHERN","EPN-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALAMEIN-SOUTHERN (02)",7.0293828201883877E-5]
[11922,null,"BOOMERANG-AIRFORCE","TH0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",7.0293828201883877E-5]
[11927,null,"WESTERN-GLOBAL","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WESTERN-GLOBAL (01)",7.0293828201883877E-5]
[11934,null,"LISTON-JOHNSON","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LISTON-JOHNSON (01)",7.0293828201883877E-5]
[11942,null,"GREEN 103-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN 103-SPARKFORD (01)",7.0293828201883877E-5]
[11947,null,"LAKES-THE GREENWAY","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","LAKES-THE GREENWAY (04)",7.0293828201883877E-5]
[11955,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[11963,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[11968,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (04)",7.0293828201883877E-5]
[11976,null,"ESSEX-DOWNS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-DOWNS (02)",0]
[11981,null,"CORINELLA-BLAIR","BD0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","CORINELLA-BLAIR (01)",7.0293828201883877E-5]
[11989,null,"GREVILLIA-ALBERT","PV0-013","2024-12-01","2024-12-07","Y","N","N","Y","N","N","PV0","GREVILLIA-ALBERT (01)",0]
[11997,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","ALMA-PALMERSTON (02)",0]
[12002,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[12010,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (02)",7.0293828201883877E-5]
[12015,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[12023,null,"ETZEL-CLYDESDALE","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","ETZEL-CLYDESDALE (01)",7.0293828201883877E-5]
[12031,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[12036,null,"ETZEL-CLYDESDALE","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","ETZEL-CLYDESDALE (01)",7.0293828201883877E-5]
[12044,null,"BIRDWOOD-KEILOR","ES0-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","ES0","BIRDWOOD-KEILOR (02)",0]
[12052,null,"QUINN-ST. JAMES","HB0-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","QUINN-ST. JAMES (01)",7.0293828201883877E-5]
[12057,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (00)",7.0293828201883877E-5]
[12065,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (00)",7.0293828201883877E-5]
[12070,null,"SPAVIN DR-P9","SBY-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","SPAVIN DR-P9 (00)",7.0293828201883877E-5]
[12078,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (04)",7.0293828201883877E-5]
[12089,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (04)",7.0293828201883877E-5]
[12090,null,"WOOD-BROWN","BY0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","WOOD-BROWN (02)",7.0293828201883877E-5]
[12098,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",{"$f":"IF(H12099=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[12106,null,"DEEP CREEK-PERIGRINE","COO-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","COO","DEEP CREEK-PERIGRINE (01)",0]
[12111,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (01)",7.0293828201883877E-5]
[12119,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (01)",7.0293828201883877E-5]
[12131,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[12132,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (02)",7.0293828201883877E-5]
[12140,null,"LYSTERFIELD-BEECHWORTH","ST0-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","LYSTERFIELD-BEECHWORTH (04)",7.0293828201883877E-5]
[12152,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[12153,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[12165,null,"DEAKIN-MARY","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","DEAKIN-MARY (03)",7.0293828201883877E-5]
[12173,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (01)",7.0293828201883877E-5]
[12174,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (01)",7.0293828201883877E-5]
[12186,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (04)",7.0293828201883877E-5]
[12194,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (05)",7.0293828201883877E-5]
[12195,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (02)",7.0293828201883877E-5]
[12207,null,"BIRDWOOD-KEILOR","ES0-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","ES0","BIRDWOOD-KEILOR (02)",0]
[12215,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (01)",7.0293828201883877E-5]
[12220,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[12228,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","Y","Y","Y","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[12236,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[12242,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","FW0","ALMA-PALMERSTON (02)",0]
[12248,null,"FLETCHER-NICHOLSON","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-NICHOLSON (01)",7.0293828201883877E-5]
[12253,null,"BRADLEY-MASON","NT0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","BRADLEY-MASON (01)",0]
[12261,null,"WATT-THE AVENUE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","WATT-THE AVENUE (04)",7.0293828201883877E-5]
[12269,null,"PARKSIDE-HIGHVIEW","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","PARKSIDE-HIGHVIEW (04)",7.0293828201883877E-5]
[12274,null,"HALL-MARGARET","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HALL-MARGARET (03)",7.0293828201883877E-5]
[12282,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[12290,null,"RALEIGH 87-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH 87-NAPIER (02)",{"$f":"IF(H12291=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[12295,null,"RALEIGH 87-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH 87-NAPIER (02)",7.0293828201883877E-5]
[12303,null,"RALEIGH 87-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH 87-NAPIER (02)",7.0293828201883877E-5]
[12308,null,"RALEIGH 87-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH 87-NAPIER (02)",7.0293828201883877E-5]
[12316,null,"RALEIGH 87-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH 87-NAPIER (02)",7.0293828201883877E-5]
[12324,null,"ROWE-YARRALEA","FF0-093","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","ROWE-YARRALEA (01)",7.0293828201883877E-5]
[12329,null,"CHARTERIS-ATLEY","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","CHARTERIS-ATLEY (04)",7.0293828201883877E-5]
[12337,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[12345,null,"CHARTERIS-ATLEY","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","CHARTERIS-ATLEY (04)",7.0293828201883877E-5]
[12350,null,"HOMER-EDDY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HOMER-EDDY (02)",7.0293828201883877E-5]
[12358,null,"MARGARET-WINIFRED","PV0-022","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","MARGARET-WINIFRED (01)",0]
[12363,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (01)",7.0293828201883877E-5]
[12371,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (01)",7.0293828201883877E-5]
[12379,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (01)",7.0293828201883877E-5]
[12384,null,"FEATHERPARK-HUNTINGTON","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","FEATHERPARK-HUNTINGTON (02)",7.0293828201883877E-5]
[12391,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (03)",7.0293828201883877E-5]
[12396,null,"NEWTON-CREVELLI","NH0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","NEWTON-CREVELLI (01)",7.0293828201883877E-5]
[12404,null,"HENDERSON-WILSON","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","HENDERSON-WILSON (02)",7.0293828201883877E-5]
[12412,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[12417,null,"CHARTERIS-ATLEY","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","CHARTERIS-ATLEY (04)",7.0293828201883877E-5]
[12425,null,"HUNT-BAXTER","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",0]
[12433,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (02)",7.0293828201883877E-5]
[12438,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[12446,null,"OAKGROVE-HUNTINGTON","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","OAKGROVE-HUNTINGTON (01)",7.0293828201883877E-5]
[12458,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (02)",7.0293828201883877E-5]
[12459,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (02)",7.0293828201883877E-5]
[12467,null,"THISTLE-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (02)",7.0293828201883877E-5]
[12479,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[12480,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[12492,null,"HOMER-EDDY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HOMER-EDDY (02)",7.0293828201883877E-5]
[12500,null,"MERRILANDS-ASQUITH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MERRILANDS-ASQUITH (01)",7.0293828201883877E-5]
[12501,null,"WOOD-BROWN","BY0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","WOOD-BROWN (02)",7.0293828201883877E-5]
[12513,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[12521,null,"DIAMOND-ROSEHILL","ES0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","DIAMOND-ROSEHILL (01)",0]
[12522,null,"OAKGROVE-HUNTINGTON","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","OAKGROVE-HUNTINGTON (03)",7.0293828201883877E-5]
[12534,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (03)",7.0293828201883877E-5]
[12542,null,"HAWKER-COOK","EP0-034","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","HAWKER-COOK (02)",0]
[12544,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (02)",7.0293828201883877E-5]
[12554,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (03)",7.0293828201883877E-5]
[12562,null,"McPHERSON-ALEXANDRA 2","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (02)",7.0293828201883877E-5]
[12567,null,"McPHERSON-ALEXANDRA 2","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (02)",7.0293828201883877E-5]
[12575,null,"McPHERSON-ALEXANDRA 2","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (02)",7.0293828201883877E-5]
[12583,null,"PARKSIDE-HIGHVIEW","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","PARKSIDE-HIGHVIEW (04)",7.0293828201883877E-5]
[12588,null,"HAMILTON-O'FARRELL","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",7.0293828201883877E-5]
[12596,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (04)",7.0293828201883877E-5]
[12601,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (04)",7.0293828201883877E-5]
[12609,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (04)",7.0293828201883877E-5]
[12617,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (03)",7.0293828201883877E-5]
[12622,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","Y","Y","Y","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[12630,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (04)",7.0293828201883877E-5]
[12635,null,"GOLF VIEW-ROEBUCK","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","GOLF VIEW-ROEBUCK (02)",7.0293828201883877E-5]
[12643,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[12651,null,"MARGARET-WINIFRED","PV0-022","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","MARGARET-WINIFRED (01)",0]
[12656,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[12664,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (02)",7.0293828201883877E-5]
[12672,null,"FOCH-TYLER","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",7.0293828201883877E-5]
[12677,null,"RIVERSIDE-WATERVIEW","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","RIVERSIDE-WATERVIEW (02)",7.0293828201883877E-5]
[12685,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (04)",7.0293828201883877E-5]
[12690,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (04)",7.0293828201883877E-5]
[12699,null,"CARROL-ORRONG","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CARROL-ORRONG (01)",7.0293828201883877E-5]
[12705,null,"CARROL-ORRONG","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CARROL-ORRONG (01)",7.0293828201883877E-5]
[12710,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (01)",7.0293828201883877E-5]
[12718,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[12726,null,"GLASGOW-HIGH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GLASGOW-HIGH (00)",7.0293828201883877E-5]
[12731,null,"GRANDISON-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GRANDISON-MT ALEXANDER (01)",7.0293828201883877E-5]
[12739,null,"RALEIGH 87-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH 87-NAPIER (03)",7.0293828201883877E-5]
[12744,null,"RALEIGH 87-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH 87-NAPIER (03)",7.0293828201883877E-5]
[12752,null,"GRANDISON-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GRANDISON-MT ALEXANDER (01)",7.0293828201883877E-5]
[12760,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (02)",7.0293828201883877E-5]
[12765,null,"REDGUM-DEEP CREEK","COO-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","COO","REDGUM-DEEP CREEK (00)",0]
[12773,null,"RALEIGH 87-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH 87-NAPIER (03)",7.0293828201883877E-5]
[12785,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (01)",7.0293828201883877E-5]
[12786,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (02)",7.0293828201883877E-5]
[12794,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (02)",7.0293828201883877E-5]
[12806,null,"LANTANA-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LANTANA-IVANHOE (01)",7.0293828201883877E-5]
[12807,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (02)",7.0293828201883877E-5]
[12815,null,"ROBINS-SHAPIRO","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROBINS-SHAPIRO (02)",7.0293828201883877E-5]
[12827,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (03)",7.0293828201883877E-5]
[12828,null,"THOMAS-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","THOMAS-PASCOE VALE (02)",7.0293828201883877E-5]
[12840,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (02)",7.0293828201883877E-5]
[12848,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[12854,null,"DEAN-MT ALEXANDER","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DEAN-MT ALEXANDER (01)",7.0293828201883877E-5]
[12860,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[12868,null,"BRIDGEHAVEN-WATER GUM","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","BRIDGEHAVEN-WATER GUM (03)",7.0293828201883877E-5]
[12873,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[12881,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (01)",7.0293828201883877E-5]
[12889,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[12894,null,"DAVID-RACHELLE","AW0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","DAVID-RACHELLE (03)",0]
[12902,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[12910,null,"VANTAGE-DASHING","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","VANTAGE-DASHING (03)",7.0293828201883877E-5]
[12915,null,"BLUEBIRD-BEVERIDGE","COO-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","BLUEBIRD-BEVERIDGE (02)",7.0293828201883877E-5]
[12923,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (03)",7.0293828201883877E-5]
[12928,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (01)",7.0293828201883877E-5]
[12936,null,"HENDRICKS-LORRAINE","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","HENDRICKS-LORRAINE (01)",7.0293828201883877E-5]
[12944,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (02)",7.0293828201883877E-5]
[12949,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[12957,null,"MONZA-FLORENCE","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MONZA-FLORENCE (01)",7.0293828201883877E-5]
[12965,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","CORNWALL-HIGH SCHOOL (03)",0]
[12970,null,"PEPPERTREE-LOUDON","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","PEPPERTREE-LOUDON (02)",7.0293828201883877E-5]
[12978,null,"PEPPERTREE-LOUDON","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","PEPPERTREE-LOUDON (01)",7.0293828201883877E-5]
[12983,null,"PEPPERTREE-LOUDON","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","PEPPERTREE-LOUDON (01)",7.0293828201883877E-5]
[12991,null,"RIVERSIDE-WATERVIEW","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","RIVERSIDE-WATERVIEW (03)",7.0293828201883877E-5]
[12999,null,"WHITELAW-BROADWAY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BROADWAY (00)",7.0293828201883877E-5]
[13007,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (04)",7.0293828201883877E-5]
[13011,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[13016,null,"GLASGOW-HIGH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GLASGOW-HIGH (00)",7.0293828201883877E-5]
[13024,null,"GRANDISON-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GRANDISON-MT ALEXANDER (01)",7.0293828201883877E-5]
[13032,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (02)",7.0293828201883877E-5]
[13037,null,"MOUSHALL-HOFFMANS","ES0-021","2024-12-01","2024-12-07","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (01)",0]
[13045,null,"FEATHERPARK-HUNTINGTON","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","FEATHERPARK-HUNTINGTON (02)",7.0293828201883877E-5]
[13053,null,"RIGGALL-APOLLO","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","RIGGALL-APOLLO (01)",7.0293828201883877E-5]
[13058,null,"GLASGOW-HIGH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GLASGOW-HIGH (02)",{"$f":"IF(H13059=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[13066,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (02)",7.0293828201883877E-5]
[13071,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[13079,null,"RIVERSIDE-WATERVIEW","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","RIVERSIDE-WATERVIEW (02)",7.0293828201883877E-5]
[13087,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[13092,null,"BROADHURST-MCFADZEAN","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","OCONNOR-MACFADZEAN (02)",7.0293828201883877E-5]
[13100,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (03)",7.0293828201883877E-5]
[13108,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (02)",7.0293828201883877E-5]
[13113,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","SOUTH-DERBY (02)",0]
[13121,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[13133,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[13134,null,"WEST-KINGSLEY","AW0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","WEST-KINGSLEY (02)",0]
[13142,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (01)",7.0293828201883877E-5]
[13154,null,"GERVASE-PECHAM","PV0-031","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","GERVASE-PECHAM (02)",7.0293828201883877E-5]
[13156,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (02)",7.0293828201883877E-5]
[13166,null,"ELLERSLIE-DUNNE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-DUNNE (01)",7.0293828201883877E-5]
[13174,null,"WEST-KINGSLEY","AW0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","WEST-KINGSLEY (01)",0]
[13175,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (03)",7.0293828201883877E-5]
[13187,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (02)",7.0293828201883877E-5]
[13195,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",0]
[13196,null,"RALEIGH-NAPIER No. 2","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-NAPIER No. 2 (03)",7.0293828201883877E-5]
[13208,null,"RALEIGH-NAPIER No. 2","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-NAPIER No. 2 (03)",7.0293828201883877E-5]
[13216,null,"BLENHEIM-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (01)",0]
[13221,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[13229,null,"JAMES-WILLIAMSON","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JAMES-WILLIAMSON (01)",7.0293828201883877E-5]
[13237,null,"WRIGHT 20-THOMSONS","TMA-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","TMA","WRIGHT 20-THOMSONS (04)",7.0293828201883877E-5]
[13242,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (02)",7.0293828201883877E-5]
[13250,null,"KILMORE-CHARLTON","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WINTER-KERANG (02)",{"$f":"IF(H13251=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[13255,null,"CANISBY-OLRIG","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","CANISBY-OLRIG (04)",7.0293828201883877E-5]
[13263,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (02)",7.0293828201883877E-5]
[13271,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[13276,null,"BARNET-MACKAY","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","BARNET-MACKAY (01)",7.0293828201883877E-5]
[13284,null,"WHITELAW-BROADWAY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BROADWAY (01)",7.0293828201883877E-5]
[13292,null,"DAVIDSON-PERKINS","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAVIDSON-PERKINS (01)",7.0293828201883877E-5]
[13297,null,"KIORA-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KIORA-PASCOE VALE (04)",7.0293828201883877E-5]
[13305,null,"KIORA-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KIORA-PASCOE VALE (04)",7.0293828201883877E-5]
[13309,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[13317,null,"BOSQUET-BALLARAT","BY0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","BY0","BOSQUET-BALLARAT (02)",0]
[13325,null,"KIORA-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KIORA-PASCOE VALE (04)",7.0293828201883877E-5]
[13330,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[13338,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[13346,null,"SEXTON-PARER","AW0-006","2024-12-01","2024-12-07","Y","N","N","Y","N","N","AW0","SEXTON-PARER (01)",0]
[13351,null,"PAMELA-HERBERT","AW0-006","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","PAMELA-HERBERT (02)",0]
[13359,null,"ALBERT-HARROW","EPN-035","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","ALBERT-HARROW (02)",0]
[13364,null,"WRIGHT 20-THOMSONS","TMA-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","TMA","WRIGHT 20-THOMSONS (01)",7.0293828201883877E-5]
[13372,null,"BREWSTER-PASCOE VALE","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-PASCOE VALE (03)",7.0293828201883877E-5]
[13380,null,"ROSENTHAL-HUGHES","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-HUGHES (01)",7.0293828201883877E-5]
[13385,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[13393,null,"BLENHEIM-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (02)",0]
[13398,null,"NEWCASTLE-DUNDAS","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NEWCASTLE-DUNDAS (03)",7.0293828201883877E-5]
[13406,null,"NEWCASTLE-DUNDAS","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NEWCASTLE-DUNDAS (03)",7.0293828201883877E-5]
[13414,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (02)",7.0293828201883877E-5]
[13419,null,"MADDEN-STUDLEY","FW0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","MADDEN-STUDLEY (01)",7.0293828201883877E-5]
[13427,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",7.0293828201883877E-5]
[13435,null,"McPHERSON-ALEXANDRA 2","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (02)",7.0293828201883877E-5]
[13440,null,"ETZEL-CLYDESDALE","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","ETZEL-CLYDESDALE (01)",7.0293828201883877E-5]
[13448,null,"MOORE-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE-PUCKLE (01)",7.0293828201883877E-5]
[13460,null,"DONALD-LAWSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",7.0293828201883877E-5]
[13464,null,"ROSENTHAL-HUGHES","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-HUGHES (01)",7.0293828201883877E-5]
[13468,null,"HUDSONS-HALL","YVE-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","YVE","HUDSONS-HALL (03)",7.0293828201883877E-5]
[13480,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[13481,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[13493,null,"ENCHANT-ALTITUDE","COO-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","COO","ENCHANT-ALTITUDE (03)",7.0293828201883877E-5]
[13501,null,"HUDSONS-HALL","YVE-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","YVE","HUDSONS-HALL (03)",7.0293828201883877E-5]
[13502,null,"HUDSONS-HALL","YVE-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","YVE","HUDSONS-HALL (03)",7.0293828201883877E-5]
[13514,null,"MOORE-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE-PUCKLE (01)",7.0293828201883877E-5]
[13522,null,"MOORE-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE-PUCKLE (01)",7.0293828201883877E-5]
[13523,null,"MOORE-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE-PUCKLE (01)",7.0293828201883877E-5]
[13535,null,"HUDSONS-HALL","YVE-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","YVE","HUDSONS-HALL (03)",7.0293828201883877E-5]
[13543,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[13548,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[13556,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[13564,null,"MOORE-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE-PUCKLE (01)",7.0293828201883877E-5]
[13569,null,"MOORE-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE-PUCKLE (01)",7.0293828201883877E-5]
[13577,null,"MOORE-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE-PUCKLE (01)",7.0293828201883877E-5]
[13585,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[13590,null,"NAPIER 20-FLETCHER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER 20-FLETCHER (06)",7.0293828201883877E-5]
[13598,null,"NAPIER 20-FLETCHER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER 20-FLETCHER (06)",7.0293828201883877E-5]
[13603,null,"NAPIER 20-FLETCHER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER 20-FLETCHER (06)",7.0293828201883877E-5]
[13611,null,"YORK-HYDE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","YORK-HYDE (02)",7.0293828201883877E-5]
[13619,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (01)",7.0293828201883877E-5]
[13623,null,"VANBERG-TENNYSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","VANBERG-TENNYSON (01)",7.0293828201883877E-5]
[13631,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[13636,null,"HUDSONS-HALL","YVE-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","YVE","HUDSONS-HALL (03)",7.0293828201883877E-5]
[13644,null,"GARNET-IDA","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","GARNET-IDA (02)",7.0293828201883877E-5]
[13652,null,"NEWLANDS-MURRAY","CS0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",0]
[13657,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (02)",7.0293828201883877E-5]
[13665,null,"CRAIGIEBURN-CHAMPION","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","CRAIGIEBURN-CHAMPION (02)",7.0293828201883877E-5]
[13673,null,"LENNOX-HYDE","FE0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","LENNOX-HYDE (03)",7.0293828201883877E-5]
[13678,null,"CHAMPION-BRAVEHEART","ST0-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","CHAMPION-BRAVEHEART (04)",7.0293828201883877E-5]
[13686,null,"WISTERIA-CHARTERIS","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","WISTERIA-CHARTERIS (04)",7.0293828201883877E-5]
[13691,null,"MOORE 17-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOORE 17-PUCKLE (05)",7.0293828201883877E-5]
[13699,null,"VANTAGE-DASHING","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","VANTAGE-DASHING (01)",7.0293828201883877E-5]
[13707,null,"VANTAGE-DASHING","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","VANTAGE-DASHING (01)",7.0293828201883877E-5]
[13712,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUTLER-PASCOE VALE (01)",7.0293828201883877E-5]
[13720,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",7.0293828201883877E-5]
[13728,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[13733,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (01)",7.0293828201883877E-5]
[13741,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (01)",7.0293828201883877E-5]
[13746,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (01)",7.0293828201883877E-5]
[13754,null,"WINIFRED-GLASS No2","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WINIFRED-GLASS No2 (02)",7.0293828201883877E-5]
[13762,null,"WINIFRED-GLASS No2","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WINIFRED-GLASS No2 (02)",{"$f":"IF(H13763=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[13772,null,"ADMIRATION-REVERENCE","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","ADMIRATION-REVERENCE (05)",7.0293828201883877E-5]
[13774,null,"ADMIRATION-REVERENCE","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","ADMIRATION-REVERENCE (05)",7.0293828201883877E-5]
[13786,null,"THORPE-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NT0","THORPE-WOODS (01)",0]
[13787,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","YORK-NAPIER (04)",7.0293828201883877E-5]
[13795,null,"MATTHEWS-KEILOR","ES0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","MATTHEWS-KEILOR (01)",7.0293828201883877E-5]
[13807,null,"HUTCHESON-BUCKLEY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HUTCHESON-BUCKLEY (02)",7.0293828201883877E-5]
[13808,null,"BLENHEIM-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (03)",0]
[13816,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (01)",7.0293828201883877E-5]
[13828,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (01)",7.0293828201883877E-5]
[13829,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (01)",7.0293828201883877E-5]
[13841,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[13849,null,"RIVERSIDE-WATERVIEW","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","RIVERSIDE-WATERVIEW (01)",7.0293828201883877E-5]
[13850,null,"GRAHAM-GLEN ALLAN","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","GRAHAM-GLEN ALLAN (03)",7.0293828201883877E-5]
[13862,null,"SEXTON-HALSEY","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","SEXTON-HALSEY (03)",7.0293828201883877E-5]
[13870,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[13875,null,"KIORA-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KIORA-PASCOE VALE (03)",7.0293828201883877E-5]
[13883,null,"WOOD-GREENBELT","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","WOOD-GREENBELT (02)",0]
[13891,null,"WINIFRED-GLASS No2","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WINIFRED-GLASS No2 (01)",7.0293828201883877E-5]
[13896,null,"THERESA-CHRISTOPHER","AW0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","THERESA-CHRISTOPHER (02)",7.0293828201883877E-5]
[13904,null,"ALBERT-HARROW","EPN-035","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","ALBERT-HARROW (02)",0]
[13912,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[13917,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",7.0293828201883877E-5]
[13921,null,"CORNWALL-HIGH SCHOOL","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",0]
[13929,null,"WAIORA-CHURCHILL","NH0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","WAIORA-CHURCHILL (01)",0]
[13937,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (01)",7.0293828201883877E-5]
[13945,null,"WHITFIELD-WHITES","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","WHITFIELD-WHITES (01)",7.0293828201883877E-5]
[13950,null,"WHITFIELD-WHITES","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","WHITFIELD-WHITES (02)",7.0293828201883877E-5]
[13958,null,"WHITFIELD-WHITES","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","WHITFIELD-WHITES (01)",7.0293828201883877E-5]
[13966,null,"WHITFIELD-WHITES","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","WHITFIELD-WHITES (03)",7.0293828201883877E-5]
[13971,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[13979,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[13984,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[13992,null,"GRENHILDA-DOUGLAS","NH0-020","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","GRENHILDA-DOUGLAS (02)",0]
[14000,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (02)",7.0293828201883877E-5]
[14005,null,"BLENHEIM-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (03)",0]
[14013,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (02)",7.0293828201883877E-5]
[14018,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",{"$f":"IF(H14019=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[14026,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (02)",7.0293828201883877E-5]
[14034,null,"MONTGOMERY-MT ALEXANDER #2","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER #2 (02)",7.0293828201883877E-5]
[14039,null,"MONTGOMERY-MT ALEXANDER #2","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER #2 (02)",7.0293828201883877E-5]
[14047,null,"MONTGOMERY-MT ALEXANDER #2","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER #2 (02)",7.0293828201883877E-5]
[14055,null,"MONTGOMERY-MT ALEXANDER #2","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER #2 (02)",7.0293828201883877E-5]
[14060,null,"MONTGOMERY-MT ALEXANDER #2","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER #2 (02)",7.0293828201883877E-5]
[14068,null,"MONTGOMERY-MT ALEXANDER #2","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","MONTGOMERY-MT ALEXANDER #2 (02)",7.0293828201883877E-5]
[14074,null,"MONTGOMERY-MT ALEXANDER #2","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","MONTGOMERY-MT ALEXANDER #2 (02)",7.0293828201883877E-5]
[14080,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[14088,null,"CRAMER-MARKET NO2","PTN-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","CRAMER-MARKET NO2 (01)",7.0293828201883877E-5]
[14093,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[14101,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (04)",7.0293828201883877E-5]
[14113,null,"GLENBARRY 40-ADRIAN","BD0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","GLENBARRY 40-ADRIAN (00)",7.0293828201883877E-5]
[14114,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",0]
[14122,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (01)",7.0293828201883877E-5]
[14134,null,"PARKSIDE-CHARTERIS","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","PARKSIDE-CHARTERIS (02)",7.0293828201883877E-5]
[14135,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (00)",7.0293828201883877E-5]
[14143,null,"RHYOLITE-HIGHPARK","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","RHYOLITE-HIGHPARK (04)",7.0293828201883877E-5]
[14155,null,"MONTGOMERY-MT ALEXANDER #2","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER #2 (02)",7.0293828201883877E-5]
[14156,null,"MONTGOMERY-MT ALEXANDER #2","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER #2 (02)",7.0293828201883877E-5]
[14168,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (02)",7.0293828201883877E-5]
[14176,null,"DEVON-OAK","PV0-031","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","DEVON-OAK (01)",7.0293828201883877E-5]
[14177,null,"DEVON-OAK","PV0-031","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","DEVON-OAK (01)",7.0293828201883877E-5]
[14189,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",7.0293828201883877E-5]
[14197,null,"DAVID-RACHELLE","AW0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","DAVID-RACHELLE (01)",0]
[14198,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (01)",7.0293828201883877E-5]
[14210,null,"BLENHEIM-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (01)",{"$f":"IF(H14211=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":0}]
[14218,null,"ESTEEM-DISTINCTION","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","ESTEEM-DISTINCTION (02)",7.0293828201883877E-5]
[14223,null,"HARRICK-KEILOR PARK","TMA-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TMA","HARRICK-KEILOR PARK (01)",7.0293828201883877E-5]
[14229,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (01)",7.0293828201883877E-5]
[14238,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (01)",7.0293828201883877E-5]
[14243,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[14251,null,"WODONGA-CUTHBERT","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WODONGA-CUTHBERT (01)",7.0293828201883877E-5]
[14256,null,"WESTMINSTER-MILITARY","BY0-014","2024-12-01","2024-12-07","Y","N","N","Y","N","N","BY0","WESTMINSTER-MILITARY (02)",0]
[14264,null,"MANOEL-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MANOEL-DAREBIN (01)",7.0293828201883877E-5]
[14272,null,"HUNT-BAXTER","CS0-009","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","HUNT-BAXTER (05)",0]
[14277,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[14285,null,"MARATHON-GANGES","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON-GANGES (02)",7.0293828201883877E-5]
[14293,null,"MARATHON-GANGES","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON-GANGES (04)",7.0293828201883877E-5]
[14298,null,"DIAMOND-ROSEHILL","ES0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","DIAMOND-ROSEHILL (01)",0]
[14306,null,"PASCOE VALE 314-CAMERON","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE 314-CAMERON (03)",7.0293828201883877E-5]
[14311,null,"LEBANON-ELDORADO","PV0-022","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","LEBANON-ELDORADO (02)",0]
[14319,null,"CHAMPION-RIVERGLEN","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","CHAMPION-RIVERGLEN (01)",7.0293828201883877E-5]
[14327,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","Y","Y","Y","Y","N","N","EP0","TIERNAN-RAGLAN (02)",7.0293828201883877E-5]
[14332,null,"BREWSTER-MT ALEXANDER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BREWSTER-MT ALEXANDER (02)",7.0293828201883877E-5]
[14340,null,"WATERDALE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-BANKSIA (02)",7.0293828201883877E-5]
[14348,null,"WATERDALE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-BANKSIA (02)",7.0293828201883877E-5]
[14353,null,"WATERDALE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-BANKSIA (02)",7.0293828201883877E-5]
[14361,null,"WATERDALE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-BANKSIA (02)",7.0293828201883877E-5]
[14366,null,"WATERDALE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-BANKSIA (02)",7.0293828201883877E-5]
[14374,null,"STEWART-PASCOE VALE","PV0-022","2024-12-01","2024-12-07","Y","N","N","Y","N","N","PV0","STEWART-PASCOE VALE (01)",0]
[14384,null,"PASCOE VALE 314-CAMERON","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE 314-CAMERON (03)",7.0293828201883877E-5]
[14386,null,"PASCOE VALE 314-CAMERON","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE 314-CAMERON (03)",7.0293828201883877E-5]
[14394,null,"PASCOE VALE 314-CAMERON","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE 314-CAMERON (03)",7.0293828201883877E-5]
[14399,null,"PASCOE VALE 314-CAMERON","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE 314-CAMERON (03)",7.0293828201883877E-5]
[14407,null,"PASCOE VALE 314-CAMERON","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE 314-CAMERON (03)",7.0293828201883877E-5]
[14415,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (03)",7.0293828201883877E-5]
[14420,null,"HART-BOWES","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","HART-BOWES (02)",7.0293828201883877E-5]
[14428,null,"GAUJA-ANDAMAN","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","GAUJA-ANDAMAN (02)",7.0293828201883877E-5]
[14436,null,"GAUJA-ANDAMAN","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","GAUJA-ANDAMAN (01)",7.0293828201883877E-5]
[14441,null,"DALEY-BELL","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALEY-BELL (01)",7.0293828201883877E-5]
[14449,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",7.0293828201883877E-5]
[14461,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[14462,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[14470,null,"CASPIAN-MILLAU","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","CASPIAN-MILLAU (04)",7.0293828201883877E-5]
[14482,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (02)",7.0293828201883877E-5]
[14483,null,"DAVIDSON-PERKINS","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAVIDSON-PERKINS (02)",7.0293828201883877E-5]
[14495,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[14503,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (01)",7.0293828201883877E-5]
[14504,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (01)",7.0293828201883877E-5]
[14516,null,"METTLE-SCENERY","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","METTLE-SCENERY (01)",7.0293828201883877E-5]
[14524,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[14525,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[14537,null,"JEFFREY-WESTGARTH","FF0-089","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (03)",7.0293828201883877E-5]
[14544,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (01)",7.0293828201883877E-5]
[14549,null,"MOONEE VLY-RACECRS 3","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOONEE VLY-RACECRS 3 (00)",7.0293828201883877E-5]
[14557,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[14565,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (02)",7.0293828201883877E-5]
[14570,null,"ALBION-GEELONG","FW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","ALBION-GEELONG (01)",7.0293828201883877E-5]
[14578,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (04)",7.0293828201883877E-5]
[14586,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[14591,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[14599,null,"BORONIA-SUGARGUM","SHM-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","BORONIA-SUGARGUM (02)",7.0293828201883877E-5]
[14604,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",7.0293828201883877E-5]
[14612,null,"BLENHEIM-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (03)",0]
[14620,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",7.0293828201883877E-5]
[14625,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (01)",7.0293828201883877E-5]
[14633,null,"ALAMEIN-SOUTHERN","EPN-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALAMEIN-SOUTHERN (02)",7.0293828201883877E-5]
[14638,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (01)",7.0293828201883877E-5]
[14646,null,"PARKSIDE-HIGHVIEW","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","PARKSIDE-HIGHVIEW (04)",7.0293828201883877E-5]
[14654,null,"BLACKMORE-ERROL","KLO-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","BLACKMORE-ERROL (01)",7.0293828201883877E-5]
[14659,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (03)",7.0293828201883877E-5]
[14667,null,"PAINE-LATROBE","NT0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","PAINE-LATROBE (02)",0]
[14675,null,"BELL-ORIEL","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BELL-ORIEL (01)",7.0293828201883877E-5]
[14680,null,"WOOD-GREENBELT","NH0-016","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","WOOD-GREENBELT (02)",0]
[14686,null,"WYONG-CENTREWAY","AW0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","WYONG-CENTREWAY (01)",7.0293828201883877E-5]
[14692,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[14700,null,"DAVIDSON-PERKINS","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAVIDSON-PERKINS (02)",7.0293828201883877E-5]
[14708,null,"BEDFORD-PARER","AW0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","BEDFORD-PARER (01)",7.0293828201883877E-5]
[14713,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[14721,null,"DEVON-OAK","PV0-031","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","DEVON-OAK (01)",7.0293828201883877E-5]
[14729,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[14734,null,"LOCH-WENDORA","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LOCH-WENDORA (03)",7.0293828201883877E-5]
[14742,null,"HOMER-EDDY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HOMER-EDDY (02)",7.0293828201883877E-5]
[14747,null,"HOMER-EDDY","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HOMER-EDDY (02)",7.0293828201883877E-5]
[14755,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[14763,null,"MADISONS-TERRITORY","SHM-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","MADISONS-TERRITORY (01)",7.0293828201883877E-5]
[14768,null,"TURNER-EVANS","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",7.0293828201883877E-5]
[14776,null,"BUNTING-SOMERVILLE 463A","TH0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","BUNTING-SOMERVILLE 463A (01)",7.0293828201883877E-5]
[14788,null,"PEARL-WHEATSHEAF","PV0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","PEARL-WHEATSHEAF (02)",0]
[14789,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[14797,null,"BUNTING-SOMERVILLE 463A","TH0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","BUNTING-SOMERVILLE 463A (01)",7.0293828201883877E-5]
[14809,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (01)",7.0293828201883877E-5]
[14810,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[14818,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (02)",7.0293828201883877E-5]
[14830,null,"WHITE-CHEDDAR","TT0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","TT0","WHITE-CHEDDAR (01)",0]
[14831,null,"EDDY-TAYLOR","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","EDDY-TAYLOR (02)",7.0293828201883877E-5]
[14839,null,"EDDY-TAYLOR","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","EDDY-TAYLOR (02)",7.0293828201883877E-5]
[14850,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",{"$f":"IF(H14851=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[14851,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[14863,null,"EDDY-TAYLOR","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","EDDY-TAYLOR (02)",7.0293828201883877E-5]
[14871,null,"BENDIGO-ALPINE","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (01)",0]
[14876,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[14884,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[14892,null,"MULBERRY-GONA","EPN-033","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","MULBERRY-GONA (03)",0]
[14897,null,"CHAMPION-RIVERGLEN","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","CHAMPION-RIVERGLEN (01)",7.0293828201883877E-5]
[14905,null,"FAWKNER-ROBERTS","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FAWKNER-ROBERTS (02)",7.0293828201883877E-5]
[14913,null,"CALA-HAMPTON","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","CALA-HAMPTON (01)",7.0293828201883877E-5]
[14918,null,"DONALD-LAWSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",7.0293828201883877E-5]
[14926,null,"TRIFT-GREVILLEA","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","TRIFT-GREVILLEA (01)",7.0293828201883877E-5]
[14931,null,"COLLINS-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","OUTHWAITE-MCEWAN (04)",7.0293828201883877E-5]
[14939,null,"GARNET-IDA","ES0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","GARNET-IDA (02)",7.0293828201883877E-5]
[14947,null,"BUCKLEY-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-HODDLE (03)",7.0293828201883877E-5]
[14952,null,"BUCKLEY-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-HODDLE (03)",7.0293828201883877E-5]
[14960,null,"PRATT-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PRATT-PUCKLE (06)",7.0293828201883877E-5]
[14968,null,"PRATT-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PRATT-PUCKLE (06)",7.0293828201883877E-5]
[14973,null,"PRATT-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PRATT-PUCKLE (06)",7.0293828201883877E-5]
[14981,null,"PRATT-PUCKLE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PRATT-PUCKLE (06)",7.0293828201883877E-5]
[14986,null,"BUCKLEY-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-HODDLE (03)",7.0293828201883877E-5]
[14994,null,"BUCKLEY-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-HODDLE (03)",7.0293828201883877E-5]
[15001,null,"WATTLEGLEN-SPURR","ST0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","WATTLEGLEN-SPURR (01)",7.0293828201883877E-5]
[15006,null,"CHEDDAR-MACARTNEY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","CHEDDAR-MACARTNEY (01)",7.0293828201883877E-5]
[15014,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[15019,null,"WATERDALE-GRIFFITHS","EPN-033","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","WATERDALE-GRIFFITHS (01)",0]
[15027,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (01)",7.0293828201883877E-5]
[15035,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[15040,null,"PORTER-DOUGHARTY","NH0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","PORTER-DOUGHARTY (01)",0]
[15048,null,"RALEIGH-HODDLE","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",7.0293828201883877E-5]
[15056,null,"WOODLAND-NAPIER","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-NAPIER (02)",7.0293828201883877E-5]
[15061,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[15069,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[15074,null,"LAWSON-SALISBURY","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LAWSON-SALISBURY (02)",7.0293828201883877E-5]
[15082,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (02)",7.0293828201883877E-5]
[15090,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (02)",7.0293828201883877E-5]
[15095,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (02)",7.0293828201883877E-5]
[15103,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (02)",7.0293828201883877E-5]
[15115,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[15116,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",7.0293828201883877E-5]
[15124,null,"NEWMAN-HOTHAM","AW0-007","2024-12-01","2024-12-07","Y","N","N","Y","N","N","AW0","NEWMAN-HOTHAM (03)",0]
[15136,null,"BUNTING-SOMERVILLE 463A","TH0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","BUNTING-SOMERVILLE 463A (01)",7.0293828201883877E-5]
[15137,null,"BUNTING-SOMERVILLE 463A","TH0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","BUNTING-SOMERVILLE 463A (01)",7.0293828201883877E-5]
[15149,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[15156,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (01)",7.0293828201883877E-5]
[15157,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (01)",7.0293828201883877E-5]
[15169,null,"RAGLAN-ASCOT","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",7.0293828201883877E-5]
[15177,null,"RALEIGH 87-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","RALEIGH 87-NAPIER (02)",7.0293828201883877E-5]
[15178,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (02)",7.0293828201883877E-5]
[15190,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (02)",7.0293828201883877E-5]
[15198,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (02)",7.0293828201883877E-5]
[15199,null,"WATERDALE-AILSA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","WATERDALE-AILSA (02)",7.0293828201883877E-5]
[15211,null,"GELLIES RD-P3","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","GELLIES RD-P3 (00)",7.0293828201883877E-5]
[15219,null,"HYDE-BRISTOW","FE0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","HYDE-BRISTOW (02)",7.0293828201883877E-5]
[15224,null,"RICHARDS-BELL","CS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","RICHARDS-BELL (02)",7.0293828201883877E-5]
[15232,null,"DONALD-LAWSON","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",7.0293828201883877E-5]
[15240,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[15245,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (01)",7.0293828201883877E-5]
[15253,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[15258,null,"LOCH-WENDORA","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","LOCH-WENDORA (01)",7.0293828201883877E-5]
[15266,null,"ALOHA-GREENE","FW0-005","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","ALOHA-GREENE (04)",7.0293828201883877E-5]
[15274,null,"DELAWARE-MENDIP","CN0-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","DELAWARE-MENDIP (01)",0]
[15279,null,"TAYLOR-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","TAYLOR-MT ALEXANDER (02)",7.0293828201883877E-5]
[15287,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (03)",7.0293828201883877E-5]
[15295,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (03)",7.0293828201883877E-5]
[15302,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (03)",7.0293828201883877E-5]
[15307,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (03)",7.0293828201883877E-5]
[15312,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (03)",7.0293828201883877E-5]
[15320,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (03)",7.0293828201883877E-5]
[15328,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (03)",7.0293828201883877E-5]
[15333,null,"MT ALEXANDER-NAPIER","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (03)",7.0293828201883877E-5]
[15341,null,"HARRISON-DAVIDSON","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","HARRISON-DAVIDSON (02)",7.0293828201883877E-5]
[15349,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (01)",7.0293828201883877E-5]
[15354,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[15362,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (02)",{"$f":"IF(H15363=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[15367,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (01)",7.0293828201883877E-5]
[15375,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (01)",7.0293828201883877E-5]
[15383,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",7.0293828201883877E-5]
[15388,null,"WELLINGTON-VICTORIA","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (01)",0]
[15396,null,"MT PLEASANT-BELL","CS0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","CS0","MT PLEASANT-BELL (01)",7.0293828201883877E-5]
[15401,null,"SALTER-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALTER-NAPIER (00)",7.0293828201883877E-5]
[15409,null,"ALBERT-HARROW","EPN-035","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","ALBERT-HARROW (02)",0]
[15417,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (02)",7.0293828201883877E-5]
[15422,null,"FIRST-BULLA","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FIRST-BULLA (02)",7.0293828201883877E-5]
[15430,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[15438,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUTLER-PASCOE VALE (01)",7.0293828201883877E-5]
[15443,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUTLER-PASCOE VALE (01)",7.0293828201883877E-5]
[15451,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUTLER-PASCOE VALE (01)",7.0293828201883877E-5]
[15462,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (01)",7.0293828201883877E-5]
[15463,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (01)",7.0293828201883877E-5]
[15471,null,"INVERMAY-ST VIGEONS","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERMAY-ST VIGEONS (02)",7.0293828201883877E-5]
[15483,null,"PEARL-WHEATSHEAF","PV0-013","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","PEARL-WHEATSHEAF (02)",0]
[15484,null,"TIERNAN-RAGLAN","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","TIERNAN-RAGLAN (02)",7.0293828201883877E-5]
[15496,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (02)",7.0293828201883877E-5]
[15504,null,"EISENHOWER-CHALEYER","NH0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NH0","EISENHOWER-CHALEYER (01)",0]
[15505,null,"JUMP-CART","SHM-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","JUMP-CART (02)",7.0293828201883877E-5]
[15517,null,"ANNE-DALEGLEN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ANNE-DALEGLEN (01)",7.0293828201883877E-5]
[15525,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[15526,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (03)",7.0293828201883877E-5]
[15538,null,"FIELD-GRANDISON","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FIELD-GRANDISON (01)",7.0293828201883877E-5]
[15546,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[15551,null,"DAVIDSON-PERKINS","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAVIDSON-PERKINS (03)",7.0293828201883877E-5]
[15559,null,"FREIGHT-CUSTOM","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (01)",7.0293828201883877E-5]
[15567,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",7.0293828201883877E-5]
[15572,null,"DEVON-OAK","PV0-031","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","DEVON-OAK (01)",7.0293828201883877E-5]
[15580,null,"BIRCH-BROADMEADOWS","AW0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","BIRCH-BROADMEADOWS (01)",7.0293828201883877E-5]
[15588,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",7.0293828201883877E-5]
[15593,null,"MIHIL-VICTORIA","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MIHIL-VICTORIA (02)",7.0293828201883877E-5]
[15601,null,"WODONGA-CUTHBERT","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WODONGA-CUTHBERT (01)",7.0293828201883877E-5]
[15604,null,"FULLER-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FULLER-SCHOFIELD (02)",7.0293828201883877E-5]
[15613,null,"GLASGOW-HIGH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GLASGOW-HIGH (02)",7.0293828201883877E-5]
[15621,null,"MERRILANDS-ASQUITH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MERRILANDS-ASQUITH (01)",7.0293828201883877E-5]
[15626,null,"McPHERSON-ALEXANDRA 2","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (01)",7.0293828201883877E-5]
[15634,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (01)",7.0293828201883877E-5]
[15639,null,"GISBORNE-NORTH","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GISBORNE-NORTH (02)",7.0293828201883877E-5]
[15647,null,"ASCOT VALE 331-YOUNG","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ASCOT VALE 331-YOUNG (01)",7.0293828201883877E-5]
[15655,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[15660,null,"KINGSTON-COLLINSON","TMA-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TMA","KINGSTON-COLLINSON (02)",7.0293828201883877E-5]
[15668,null,"NEWTON-CREVELLI","NH0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NH0","NEWTON-CREVELLI (02)",7.0293828201883877E-5]
[15676,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","BOND-LIBERTY (02)",7.0293828201883877E-5]
[15681,null,"WADHAM-MORELAND","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WADHAM-MORELAND (03)",7.0293828201883877E-5]
[15689,null,"McPHERSON-ALEXANDRA 2","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (01)",7.0293828201883877E-5]
[15694,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[15702,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (01)",7.0293828201883877E-5]
[15710,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",7.0293828201883877E-5]
[15715,null,"MOONEE VLY-RACECRS 4","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOONEE VLY-RACECRS 4 (00)",7.0293828201883877E-5]
[15723,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (01)",7.0293828201883877E-5]
[15728,null,"ARTHUR-BELL","PTN-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","ARTHUR-BELL (03)",7.0293828201883877E-5]
[15736,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","TT0","BROWNING-SCOTT (02)",0]
[15744,null,"O'DOWD-HOWARD","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","O'DOWD-HOWARD (01)",0]
[15749,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[15759,null,"ALBERT 8-14 FOLEY","EP0-035","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT 8-14 FOLEY (01)",7.0293828201883877E-5]
[15764,null,"ALBERT 8-14 FOLEY","EP0-035","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT 8-14 FOLEY (01)",7.0293828201883877E-5]
[15769,null,"ALBERT 8-14 FOLEY","EP0-035","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT 8-14 FOLEY (01)",7.0293828201883877E-5]
[15777,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (01)",7.0293828201883877E-5]
[15789,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",7.0293828201883877E-5]
[15790,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",7.0293828201883877E-5]
[15798,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (01)",7.0293828201883877E-5]
[15810,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (01)",{"$f":"IF(H15811=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[15811,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (01)",7.0293828201883877E-5]
[15819,null,"BEENAK-PURINUAN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BEENAK-PURINUAN (01)",7.0293828201883877E-5]
[15831,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (01)",7.0293828201883877E-5]
[15832,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (01)",7.0293828201883877E-5]
[15844,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[15852,null,"ALBERT 8-14 FOLEY","EP0-035","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT 8-14 FOLEY (01)",7.0293828201883877E-5]
[15853,null,"ALBERT 8-14 FOLEY","EP0-035","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT 8-14 FOLEY (01)",7.0293828201883877E-5]
[15865,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[15873,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[15878,null,"CHAPMAN-BELAIR","PV0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","PV0","CHAPMAN-BELAIR (01)",7.0293828201883877E-5]
[15886,null,"FAWKNER-ROBERTS","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FAWKNER-ROBERTS (02)",7.0293828201883877E-5]
[15894,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (01)",7.0293828201883877E-5]
[15899,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (02)",7.0293828201883877E-5]
[15907,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[15909,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[15910,null,"ALBERT-HARROW","EPN-035","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","ALBERT-HARROW (02)",0]
[15911,null,"ALBERT-HARROW","EPN-035","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","ALBERT-HARROW (02)",0]
[15912,null,"ALBERT-HARROW","EPN-035","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","ALBERT-HARROW (02)",0]
[15913,null,"O'CONNOR-WHITBY","CN0-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",0]
[15914,null,"O'CONNOR-WHITBY","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","OCONNOR-MACFADZEAN (04)",0]
[15915,null,"O'CONNOR-WHITBY","CN0-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",0]
[15916,null,"O'CONNOR-WHITBY","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","OCONNOR-MACFADZEAN (04)",0]
[15917,null,"O'CONNOR-WHITBY","CN0-011","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",0]
[15918,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",7.0293828201883877E-5]
[15919,null,"JAMES-WILLIAMSON","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JAMES-WILLIAMSON (02)",7.0293828201883877E-5]
[15920,null,"MCPHERSON-QUINN","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","MCPHERSON-QUINN (03)",7.0293828201883877E-5]
[15921,null,"O'CONNOR-WHITBY","CN0-011","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","OCONNOR-MACFADZEAN (04)",0]
[15922,null,"STEWART-PASCOE VALE","PV0-022","2024-12-01","2024-12-07","Y","N","N","Y","N","N","PV0","STEWART-PASCOE VALE (01)",0]
[15923,null,"STEWART-PASCOE VALE","PV0-022","2024-12-01","2024-12-07","Y","N","N","Y","N","N","PV0","STEWART-PASCOE VALE (01)",0]
[15924,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (01)",7.0293828201883877E-5]
[15925,null,"BRAY-BARTROP","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRAY-BARTROP (01)",7.0293828201883877E-5]
[15926,null,"WATERDALE-GRIFFITHS","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","WATERDALE-GRIFFITHS (01)",7.0293828201883877E-5]
[15927,null,"ALEXANDRA-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",0]
[15928,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",7.0293828201883877E-5]
[15929,null,"BREARLEY-ROSE","CS0-002","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",0]
[15930,null,"MARGTMARY-MURRAY","CN0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","MARGTMARY-MURRAY (03)",0]
[15931,null,"DAVIDSON-PERKINS","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAVIDSON-PERKINS (01)",7.0293828201883877E-5]
[15932,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[15933,null,"BOND-ATHELSTANE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",7.0293828201883877E-5]
[15934,null,"GRENHILDA-DOUGLAS","NH0-020","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NH0","GRENHILDA-DOUGLAS (02)",0]
[15935,null,"GRENHILDA-DOUGLAS","NH0-020","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","GRENHILDA-DOUGLAS (02)",0]
[15936,null,"THORPE-WOODS","NT0-003","2024-12-01","2024-12-07","Y","N","N","Y","N","N","NT0","NA",0]
[15937,null,"CHATHAM-CANTERBURY","FT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","CHATHAM-CANTERBURY (02)",7.0293828201883877E-5]
[15938,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (02)",{"$f":"IF(H15939=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[15939,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (01)",7.0293828201883877E-5]
[15940,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (02)",7.0293828201883877E-5]
[15941,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[15942,null,"HART-BOWES","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","HART-BOWES (02)",7.0293828201883877E-5]
[15943,null,"QUINN-NOGA","AW0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","QUINN-NOGA (01)",7.0293828201883877E-5]
[15944,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (02)",7.0293828201883877E-5]
[15945,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",0]
[15946,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (04)",7.0293828201883877E-5]
[15947,null,"CAPULET-BENT","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAPULET-BENT (02)",7.0293828201883877E-5]
[15948,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (02)",7.0293828201883877E-5]
[15949,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15950,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15951,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15952,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15953,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15954,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15955,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15956,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15957,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15958,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15959,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15960,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15961,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15962,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15963,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15964,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15965,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15966,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15967,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15968,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15969,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15970,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15971,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15972,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15973,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15974,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15975,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15976,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (01)",7.0293828201883877E-5]
[15977,null,"REX-CHIFLEY","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","REX-CHIFLEY (01)",7.0293828201883877E-5]
[15978,null,"REX-CHIFLEY","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","REX-CHIFLEY (01)",7.0293828201883877E-5]
[15979,null,"REX-CHIFLEY","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","REX-CHIFLEY (01)",7.0293828201883877E-5]
[15980,null,"REX-CHIFLEY","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","REX-CHIFLEY (01)",7.0293828201883877E-5]
[15981,null,"MOYANGUL-GUNGARLAN","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","MOYANGUL-GUNGARLAN (03)",7.0293828201883877E-5]
[15982,null,"KING-BOWES","AW0-005","2024-12-01","2024-12-07","N","Y","N","N","Y","N","AW0","KING-BOWES (01)",7.0293828201883877E-5]
[15983,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[15984,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[15985,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (02)",7.0293828201883877E-5]
[15986,null,"WHITELAW-BROADWAY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BROADWAY (01)",7.0293828201883877E-5]
[15987,null,"WHITELAW-BROADWAY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BROADWAY (01)",7.0293828201883877E-5]
[15988,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (01)",7.0293828201883877E-5]
[15989,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (01)",7.0293828201883877E-5]
[15990,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (04)",7.0293828201883877E-5]
[15991,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (01)",7.0293828201883877E-5]
[15992,null,"ROBERTS-MCNAMARA","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","ROBERTS-MCNAMARA (01)",7.0293828201883877E-5]
[15993,null,"MARATHON 281-HIGHLANDER","ST0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",7.0293828201883877E-5]
[15994,null,"TOORA-IONA","BD0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","TOORA-IONA (02)",7.0293828201883877E-5]
[15995,null,"WATERDALE-LLOYD","EPN-033","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","WATERDALE-LLOYD (01)",0]
[15996,null,"WATERDALE-LLOYD","EPN-033","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","WATERDALE-LLOYD (01)",0]
[15997,null,"HOBSON-HOME","NT0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NT0","HOBSON-HOME (01)",7.0293828201883877E-5]
[15998,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[15999,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[16000,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[16001,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[16002,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",{"$f":"IF(H16003=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[16003,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[16004,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[16005,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[16006,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (03)",7.0293828201883877E-5]
[16007,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",7.0293828201883877E-5]
[16008,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",7.0293828201883877E-5]
[16009,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",7.0293828201883877E-5]
[16010,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",7.0293828201883877E-5]
[16011,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",7.0293828201883877E-5]
[16012,null,"WOODBURN-CAMMS","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WOODBURN-CAMMS (01)",7.0293828201883877E-5]
[16013,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",0]
[16014,null,"PORTER-DOUGHARTY","NH0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","PORTER-DOUGHARTY (02)",0]
[16015,null,"PORTER-DOUGHARTY","NH0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","PORTER-DOUGHARTY (02)",0]
[16016,null,"BORONIA-SUGARGUM","SHM-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","BORONIA-SUGARGUM (01)",7.0293828201883877E-5]
[16017,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (01)",7.0293828201883877E-5]
[16018,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (01)",7.0293828201883877E-5]
[16019,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",7.0293828201883877E-5]
[16020,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",7.0293828201883877E-5]
[16021,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",7.0293828201883877E-5]
[16022,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[16023,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",7.0293828201883877E-5]
[16024,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[16025,null,"FIELD-GRANDISON","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FIELD-GRANDISON (02)",7.0293828201883877E-5]
[16026,null,"LIBERTY-BELL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LIBERTY-BELL (01)",7.0293828201883877E-5]
[16027,null,"FIELD-GRANDISON","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FIELD-GRANDISON (02)",7.0293828201883877E-5]
[16028,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (02)",7.0293828201883877E-5]
[16029,null,"CHATHAM-CANTERBURY","FT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","FT0","CHATHAM-CANTERBURY (02)",7.0293828201883877E-5]
[16030,null,"MACKAY-GLASS","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MACKAY-GLASS (03)",7.0293828201883877E-5]
[16031,null,"LLOYD-MONASH","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",7.0293828201883877E-5]
[16032,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (02)",7.0293828201883877E-5]
[16033,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (02)",7.0293828201883877E-5]
[16034,null,"ELLERSLIE-CASH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ELLERSLIE-CASH (02)",7.0293828201883877E-5]
[16035,null,"McPHERSON-ALEXANDRA 2","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (04)",7.0293828201883877E-5]
[16036,null,"BUTLER-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NA",7.0293828201883877E-5]
[16037,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (02)",7.0293828201883877E-5]
[16038,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (02)",7.0293828201883877E-5]
[16039,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (02)",7.0293828201883877E-5]
[16040,null,"PROGRESS-PASCOE VALE","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PROGRESS-PASCOE VALE (02)",7.0293828201883877E-5]
[16041,null,"HAYES-HOUSTON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HAYES-HOUSTON (03)",7.0293828201883877E-5]
[16042,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[16043,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[16044,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[16045,null,"WEST-KINGSLEY","AW0-007","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","WEST-KINGSLEY (02)",0]
[16046,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",7.0293828201883877E-5]
[16047,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[16048,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[16049,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[16050,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[16051,null,"STEPHEN-PRINCESS","FE0-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","FE0","NA",7.0293828201883877E-5]
[16052,null,"HILTON-WEST","PV0-023","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","HILTON-WEST (03)",0]
[16053,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (02)",7.0293828201883877E-5]
[16054,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[16055,null,"HAIG-GILBERT","PTN-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","HAIG-GILBERT (02)",7.0293828201883877E-5]
[16056,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16057,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[16058,null,"PASCOE VALE-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","PASCOE VALE-MT ALEXANDER (04)",7.0293828201883877E-5]
[16059,null,"COLLINS-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","OUTHWAITE-MCEWAN (03)",7.0293828201883877E-5]
[16060,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (02)",7.0293828201883877E-5]
[16061,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (02)",7.0293828201883877E-5]
[16062,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (01)",7.0293828201883877E-5]
[16063,null,"CALDER-DAVIS","SHM-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","SHM","CALDER-DAVIS (00)",7.0293828201883877E-5]
[16064,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[16065,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[16066,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",{"$f":"IF(H16067=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[16067,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[16068,null,"ROKEWOOD-BALOOK","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","ROKEWOOD-BALOOK (01)",7.0293828201883877E-5]
[16069,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[16070,null,"ETZEL-CLYDESDALE","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","ETZEL-CLYDESDALE (01)",7.0293828201883877E-5]
[16071,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[16072,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (03)",7.0293828201883877E-5]
[16073,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (01)",7.0293828201883877E-5]
[16074,null,"RICHELIEU-ESSEX","FW0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","FW0","RICHELIEU-ESSEX (01)",7.0293828201883877E-5]
[16075,null,"ESSEX-DOWNS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-DOWNS (02)",0]
[16076,null,"LANTANA-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","LANTANA-IVANHOE (02)",7.0293828201883877E-5]
[16077,null,"OUTHWAITE-MCEWAN","EPN-033","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","OUTHWAITE-MCEWAN (01)",0]
[16078,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (01)",7.0293828201883877E-5]
[16079,null,"SALMON-SCHOFIELD","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALMON-SCHOFIELD (01)",7.0293828201883877E-5]
[16080,null,"STANLEY-THE GATE WAREHOUSE","ST0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","STANLEY-THE GATE WAREHOUSE (01)",7.0293828201883877E-5]
[16081,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[16082,null,"MATTHEWS-KEILOR","ES0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","MATTHEWS-KEILOR (03)",7.0293828201883877E-5]
[16083,null,"MATTHEWS-KEILOR","ES0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","MATTHEWS-KEILOR (03)",7.0293828201883877E-5]
[16084,null,"MATTHEWS-KEILOR","ES0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","MATTHEWS-KEILOR (03)",7.0293828201883877E-5]
[16085,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (04)",7.0293828201883877E-5]
[16086,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (04)",7.0293828201883877E-5]
[16087,null,"MOROBE-ALAMEIN","EPN-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","MOROBE-ALAMEIN (03)",7.0293828201883877E-5]
[16088,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (01)",7.0293828201883877E-5]
[16089,null,"KILMORE-CHARLTON","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","KILMORE-CHARLTON (01)",7.0293828201883877E-5]
[16090,null,"LIBERTY-MOROBE","EPN-034","2024-12-01","2024-12-07","Y","N","N","N","N","N","EPN","NA",0]
[16091,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16092,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16093,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16094,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16095,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16096,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16097,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16098,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16099,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16100,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16101,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16102,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16103,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16104,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16105,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16106,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16107,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16108,null,"WASHINGTON-DOY","BD0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","WASHINGTON-DOY (02)",7.0293828201883877E-5]
[16109,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16110,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16111,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16112,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16113,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16114,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16115,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[16116,null,"TRETHOWAN-SMILEY","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","TRETHOWAN-SMILEY (03)",7.0293828201883877E-5]
[16117,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (01)",7.0293828201883877E-5]
[16118,null,"MYDDLETON-GRACE","NH0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","MYDDLETON-GRACE (01)",0]
[16119,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[16120,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[16121,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[16122,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16123,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16124,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16125,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16126,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16127,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16128,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16129,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16130,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",{"$f":"IF(H16131=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[16131,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16132,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16133,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16134,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16135,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16136,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16137,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16138,null,"McPHERSON-KENNA","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","McPHERSON-KENNA (02)",7.0293828201883877E-5]
[16139,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[16140,null,"NEAL-DINAH","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","NEAL-DINAH (01)",7.0293828201883877E-5]
[16141,null,"NEAL-DINAH","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","NEAL-DINAH (01)",7.0293828201883877E-5]
[16142,null,"KING-BOWES","AW0-005","2024-12-01","2024-12-07","N","Y","N","N","Y","N","AW0","KING-BOWES (01)",7.0293828201883877E-5]
[16143,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",7.0293828201883877E-5]
[16144,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",7.0293828201883877E-5]
[16145,null,null,null,"2024-12-01","2024-12-07","N","Y","N","N","N","N",null,"GORDON-WOOD (01)",7.0293828201883877E-5]
[16146,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[16147,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[16148,null,"GRAHAM-GLEN ALLAN","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","GRAHAM-GLEN ALLAN (03)",7.0293828201883877E-5]
[16149,null,"VIEWBANK-BREES","AW0-006","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","VIEWBANK-BREES (01)",0]
[16150,null,"VIEWBANK-BREES","AW0-006","2024-12-01","2024-12-07","Y","N","N","N","N","N","AW0","VIEWBANK-BREES (01)",0]
[16151,null,"VIEWBANK-BREES","AW0-006","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","VIEWBANK-BREES (01)",7.0293828201883877E-5]
[16152,null,"WADHAM-MORELAND","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WADHAM-MORELAND (01)",7.0293828201883877E-5]
[16153,null,"WADHAM-MORELAND","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WADHAM-MORELAND (01)",7.0293828201883877E-5]
[16154,null,"MAGDALA-WOODLAND","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","SALMON-SCHOFIELD (01)",7.0293828201883877E-5]
[16155,null,"SOUTH-DERBY","PV0-024","2024-12-01","2024-12-07","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",0]
[16156,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[16157,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[16158,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[16159,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[16160,null,"NEAL-DINAH","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","NEAL-DINAH (01)",7.0293828201883877E-5]
[16161,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",7.0293828201883877E-5]
[16162,null,"WOODLAND-ALFRED","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","WOODLAND-ALFRED (01)",7.0293828201883877E-5]
[16163,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[16164,null,"FLETCHER-NICHOLSON","NS0-007","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-NICHOLSON (01)",7.0293828201883877E-5]
[16165,null,"BLIBURG-SUNSET","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","BLIBURG-SUNSET (02)",7.0293828201883877E-5]
[16166,null,"BOND-ORIEL","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-ORIEL (03)",7.0293828201883877E-5]
[16167,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16168,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16169,null,"DIAMOND-ROSEHILL","ES0-021","2024-12-01","2024-12-07","Y","N","N","N","N","N","ES0","DIAMOND-ROSEHILL (01)",0]
[16170,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16171,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16172,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16173,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16174,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16175,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16176,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16177,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16178,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16179,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16180,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16181,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16182,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16183,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16184,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16185,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16186,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16187,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16188,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16189,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16190,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16191,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16192,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16193,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16194,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",{"$f":"IF(H16195=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[16195,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16196,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16197,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16198,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16199,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16200,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16201,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16202,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16203,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16204,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16205,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16206,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16207,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16208,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16209,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16210,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16211,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16212,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16213,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16214,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16215,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16216,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16217,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16218,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16219,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16220,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16221,null,"DAPHNE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DAPHNE-BANKSIA (02)",7.0293828201883877E-5]
[16222,null,"ATTERCLIFFE-DERBY","CS0-012","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CS0","ATTERCLIFFE-DERBY (03)",0]
[16223,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (00)",7.0293828201883877E-5]
[16224,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (00)",7.0293828201883877E-5]
[16225,null,"DARLINGTON-RENNIE","CS0-009","2024-12-01","2024-12-07","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",0]
[16226,null,"PASCOE VALE-WOODLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","PASCOE VALE-WOODLAND (01)",7.0293828201883877E-5]
[16227,null,"SUNBURY RD-P237","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","SUNBURY RD-P237 (02)",7.0293828201883877E-5]
[16228,null,"SUNBURY RD-P237","SBY-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","SUNBURY RD-P237 (02)",7.0293828201883877E-5]
[16229,null,"BOOMERANG-AIRFORCE","TH0-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",7.0293828201883877E-5]
[16230,null,"PURINUAN-NUTWOOD","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",7.0293828201883877E-5]
[16231,null,"MARGARET-MURPHY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",7.0293828201883877E-5]
[16232,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[16233,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[16234,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",0]
[16235,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[16236,null,"ROSELAND-IVANHOE","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",7.0293828201883877E-5]
[16237,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (03)",7.0293828201883877E-5]
[16238,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","NA",7.0293828201883877E-5]
[16239,null,"HAMPDEN-CROTHERS","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",7.0293828201883877E-5]
[16240,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","KERFERD-RALEIGH (02)",7.0293828201883877E-5]
[16241,null,"BRADSHAW-MARYBOROUGH","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (02)",7.0293828201883877E-5]
[16242,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[16243,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[16244,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[16245,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[16246,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[16247,null,"CAMERON-PASCOE VALE","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CAMERON-PASCOE VALE (02)",7.0293828201883877E-5]
[16248,null,"BRADLEY-MASON","NT0-017","2024-12-01","2024-12-07","Y","N","N","N","N","N","NT0","BRADLEY-MASON (01)",0]
[16249,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (01)",7.0293828201883877E-5]
[16250,null,"MACK-PICKETT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MACK-PICKETT (02)",7.0293828201883877E-5]
[16251,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[16252,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[16253,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[16254,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[16255,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[16256,null,"GREGORY-PLENTY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","GREGORY-PLENTY (04)",7.0293828201883877E-5]
[16257,null,"COPE-UCM 2","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","COPE-UCM 2 (02)",7.0293828201883877E-5]
[16258,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",{"$f":"IF(H16259=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[16259,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",7.0293828201883877E-5]
[16260,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (02)",7.0293828201883877E-5]
[16261,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (02)",7.0293828201883877E-5]
[16262,null,"KERFERD-RALEIGH","ES0-025","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (02)",7.0293828201883877E-5]
[16263,null,"BLIBURG-SUNSET","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","BLIBURG-SUNSET (02)",7.0293828201883877E-5]
[16264,null,"JELLICOE-OSNEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BANKSIA-OSNEY (01)",7.0293828201883877E-5]
[16265,null,"MOYANGUL-GUNGARLAN","AW0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","MOYANGUL-GUNGARLAN (03)",7.0293828201883877E-5]
[16266,null,"GLEN-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLEN-GLASS (04)",7.0293828201883877E-5]
[16267,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[16268,null,"LUDEMAN-BRAITHWAITE","TT0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","LUDEMAN-BRAITHWAITE (02)",7.0293828201883877E-5]
[16269,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NA",7.0293828201883877E-5]
[16270,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (01)",7.0293828201883877E-5]
[16271,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (92)",7.0293828201883877E-5]
[16272,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (92)",7.0293828201883877E-5]
[16273,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (92)",7.0293828201883877E-5]
[16274,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (92)",7.0293828201883877E-5]
[16275,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (92)",7.0293828201883877E-5]
[16276,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (92)",7.0293828201883877E-5]
[16277,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (92)",7.0293828201883877E-5]
[16278,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (92)",7.0293828201883877E-5]
[16279,null,"GLADSTONE-ASCOT VALE","NS0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (92)",7.0293828201883877E-5]
[16280,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",7.0293828201883877E-5]
[16281,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",7.0293828201883877E-5]
[16282,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",7.0293828201883877E-5]
[16283,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[16284,null,"MOROBE-ALAMEIN","EPN-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","MOROBE-ALAMEIN (03)",7.0293828201883877E-5]
[16285,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",7.0293828201883877E-5]
[16286,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",7.0293828201883877E-5]
[16287,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",7.0293828201883877E-5]
[16288,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",7.0293828201883877E-5]
[16289,null,"BROWNING-SCOTT","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (01)",7.0293828201883877E-5]
[16290,null,"RAVENSCOURT-FULHAM","FF0-083","2024-12-01","2024-12-07","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",7.0293828201883877E-5]
[16291,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (01)",7.0293828201883877E-5]
[16292,null,"GREGORY-PLENTY","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","GREGORY-PLENTY (04)",7.0293828201883877E-5]
[16293,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","NA",7.0293828201883877E-5]
[16294,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[16295,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[16296,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[16297,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","MCCRAE-ELSEY (02)",7.0293828201883877E-5]
[16298,null,"JHONSON-BRENTWOOD","NS0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","JHONSON-BRENTWOOD (02)",7.0293828201883877E-5]
[16299,null,"ROSAMOND-RIVER","BY0-013","2024-12-01","2024-12-07","N","Y","N","N","N","N","BY0","ROSAMOND-RIVER (01)",7.0293828201883877E-5]
[16300,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",0]
[16301,null,"ORIEL-HAWKER","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",7.0293828201883877E-5]
[16302,null,null,null,"2024-12-01","2024-12-07","N","Y","N","N","N","N",null,"NA",7.0293828201883877E-5]
[16303,null,"ALBERT-MT ALEXANDER","NS0-018","2024-12-01","2024-12-07","N","Y","N","N","Y","N","NS0","ALBERT-MT ALEXANDER (01)",7.0293828201883877E-5]
[16304,null,"ATHELSTANE-ROBBINS","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ATHELSTANE-ROBBINS (01)",7.0293828201883877E-5]
[16305,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (02)",7.0293828201883877E-5]
[16306,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (02)",7.0293828201883877E-5]
[16307,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[16308,null,"ALBERT-DUNDAS","EP0-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NA",7.0293828201883877E-5]
[16309,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",7.0293828201883877E-5]
[16310,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",7.0293828201883877E-5]
[16311,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",7.0293828201883877E-5]
[16312,null,"ELLIOT-GRAHAM","BMS-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",7.0293828201883877E-5]
[16313,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (02)",7.0293828201883877E-5]
[16314,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (02)",7.0293828201883877E-5]
[16315,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (02)",7.0293828201883877E-5]
[16316,null,"BUCKLEY-MCPHERSON","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BUCKLEY-MCPHERSON (04)",7.0293828201883877E-5]
[16317,null,"HOLDEN-MILITARY","BY0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","BY0","HOLDEN-MILITARY (02)",0]
[16318,null,null,null,"2024-12-01","2024-12-07","N","Y","N","N","N","N",null,"BELL-QUINN (01)",7.0293828201883877E-5]
[16319,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (03)",7.0293828201883877E-5]
[16320,null,"MARGTMARY-MURRAY","CN0-008","2024-12-01","2024-12-07","Y","N","N","N","N","N","CN0","MARGTMARY-MURRAY (03)",0]
[16321,null,"HOLDEN-MILITARY","BY0-014","2024-12-01","2024-12-07","Y","N","N","N","N","N","BY0","HOLDEN-MILITARY (02)",0]
[16322,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","NA",{"$f":"IF(H16323=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[16323,null,"MERCHISTON-CARNARVON","NS0-016","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","CRANWELL-CARNARVON (02)",7.0293828201883877E-5]
[16324,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[16325,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[16326,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[16327,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",7.0293828201883877E-5]
[16328,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","NA",7.0293828201883877E-5]
[16329,null,"ROSENTHAL-ALLENBY","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","NA",7.0293828201883877E-5]
[16330,null,"GRENHILDA-DOUGLAS","NH0-020","2024-12-01","2024-12-07","Y","N","N","N","N","N","NH0","GRENHILDA-DOUGLAS (02)",0]
[16331,null,"ROYAL-MCMAHON","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ROYAL-MCMAHON (01)",7.0293828201883877E-5]
[16332,null,"ESSEX-LANDELLS","CN0-005","2024-12-01","2024-12-07","Y","N","N","Y","N","N","CN0","ESSEX-LANDELLS (02)",0]
[16333,null,null,null,"2024-12-01","2024-12-07","N","Y","N","N","N","N",null,"NA",7.0293828201883877E-5]
[16334,null,"MCIVOR-KIEWA","BD0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","MCIVOR-KIEWA (01)",7.0293828201883877E-5]
[16335,null,"BLIBURG-SUNSET","BMS-023","2024-12-01","2024-12-07","N","Y","N","N","N","N","BMS","BLIBURG-SUNSET (01)",7.0293828201883877E-5]
[16336,null,"RALEIGH-CHIFLEY","YVE-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","YVE","RALEIGH-CHIFLEY (01)",7.0293828201883877E-5]
[16337,null,"MELCOMBE-BANKSIA","EP0-036","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",7.0293828201883877E-5]
[16338,null,"DELAWARE-MENDIP","CN0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","CN0","DELAWARE-MENDIP (03)",7.0293828201883877E-5]
[16339,null,"ALTONA-ORIEL","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",7.0293828201883877E-5]
[16340,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (01)",7.0293828201883877E-5]
[16341,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (02)",7.0293828201883877E-5]
[16342,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (02)",7.0293828201883877E-5]
[16343,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (02)",7.0293828201883877E-5]
[16344,null,"KILMORE-CHARLTON","TT0-010","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","KILMORE-CHARLTON (01)",7.0293828201883877E-5]
[16345,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (04)",7.0293828201883877E-5]
[16346,null,"ST VIGEONS-BORRIE","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ST VIGEONS-BORRIE (04)",7.0293828201883877E-5]
[16347,null,"EDWIN-ST HELLIER","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (02)",7.0293828201883877E-5]
[16348,null,"RATHCOWN-CHEDDAR","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","RATHCOWN-CHEDDAR (01)",7.0293828201883877E-5]
[16349,null,"RATHCOWN-CHEDDAR","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","RATHCOWN-CHEDDAR (01)",7.0293828201883877E-5]
[16350,null,"DIAMOND-ROSEHILL","ES0-021","2024-12-01","2024-12-07","Y","N","N","Y","N","N","ES0","NA",0]
[16351,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",0]
[16352,null,"ALMA-PALMERSTON","FW0-016","2024-12-01","2024-12-07","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",0]
[16353,null,"RAGLAN-RESERVE","EP0-028","2024-12-01","2024-12-07","N","Y","N","N","Y","N","EP0","RAGLAN-RESERVE (01)",7.0293828201883877E-5]
[16354,null,"INVERNESS-INVERMAY","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","INVERNESS-INVERMAY (02)",7.0293828201883877E-5]
[16355,null,"GORDON-WOOD","PTN-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","GORDON-WOOD (01)",7.0293828201883877E-5]
[16356,null,"FLETCHER-PASCOE VALE","NS0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","FLETCHER-PASCOE VALE (03)",7.0293828201883877E-5]
[16357,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (04)",7.0293828201883877E-5]
[16358,null,"GREEN-SPARKFORD","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","GREEN-SPARKFORD (01)",7.0293828201883877E-5]
[16359,null,"McEWEN-CURTIN","SBY-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","SBY","McEWEN-CURTIN (03)",7.0293828201883877E-5]
[16360,null,"NAPIER-BUTLER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (01)",7.0293828201883877E-5]
[16361,null,"GLASS-NAPIER","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLASS-NAPIER (03)",7.0293828201883877E-5]
[16362,null,"COLLINS-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","OUTHWAITE-MCEWAN (04)",7.0293828201883877E-5]
[16363,null,"PATTERSON-DAVID","PTN-021","2024-12-01","2024-12-07","N","Y","N","N","N","N","PTN","NICHOL-GOWER (01)",7.0293828201883877E-5]
[16364,null,"PARKSIDE-HIGHVIEW","KLO-022","2024-12-01","2024-12-07","N","Y","N","N","N","N","KLO","PARKSIDE-HIGHVIEW (03)",7.0293828201883877E-5]
[16365,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[16366,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","HESLEDEN-AMELIA (03)",7.0293828201883877E-5]
[16367,null,"WATERDALE-GRIFFITHS","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","WATERDALE-GRIFFITHS (02)",7.0293828201883877E-5]
[16368,null,"WATERDALE-GRIFFITHS","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","WATERDALE-GRIFFITHS (02)",7.0293828201883877E-5]
[16369,null,null,null,"2024-12-01","2024-12-07","Y","N","N","N","N","N",null,"NA",0]
[16370,null,"YORK-NAPIER","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","YORK-NAPIER (04)",7.0293828201883877E-5]
[16371,null,"GLEN-GLASS","NS0-008","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLEN-GLASS (01)",7.0293828201883877E-5]
[16372,null,"HESLEDEN-AMELIA","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","NA",7.0293828201883877E-5]
[16373,null,"MCCRAE-ELSEY","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","NA",7.0293828201883877E-5]
[16374,null,"COLLINS-WATERDALE","EPN-033","2024-12-01","2024-12-07","N","Y","N","N","N","N","EPN","NA",7.0293828201883877E-5]
[16375,null,"FORRESTER-HEDDERWICK","ES0-015","2024-12-01","2024-12-07","N","Y","N","N","N","N","ES0","FORRESTER-HEDDERWICK (02)",7.0293828201883877E-5]
[16376,null,"FINTON-ARUNDEL","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (01)",7.0293828201883877E-5]
[16377,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[16378,null,"GREENOCK-DAREBIN","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GREENOCK-DAREBIN (02)",7.0293828201883877E-5]
[16379,null,"BOURNIAN-GRAMMAR","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","BOURNIAN-GRAMMAR (01)",7.0293828201883877E-5]
[16380,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (03)",7.0293828201883877E-5]
[16381,null,null,null,"2024-12-01","2024-12-07","N","Y","N","N","N","N",null,"NEAL-DINAH (01)",7.0293828201883877E-5]
[16382,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (02)",7.0293828201883877E-5]
[16383,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (02)",7.0293828201883877E-5]
[16384,null,"ARGYLE-DAREBIN","TT0-003","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","ARGYLE-DAREBIN (02)",7.0293828201883877E-5]
[16385,null,"DALVEEN-JELLICOE","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","DALVEEN-JELLICOE (01)",7.0293828201883877E-5]
[16386,null,"GOLF-FLAG","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","GOLF-FLAG (02)",{"$f":"IF(H16387=\"Y\",(1/COUNTIF($H$2:$H$16409,\"Y\")),0)","v":7.0293828201883877E-5}]
[16387,null,"COPE-UCM 2","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","COPE-UCM 2 (02)",7.0293828201883877E-5]
[16388,null,"COPE-UCM 2","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","COPE-UCM 2 (02)",7.0293828201883877E-5]
[16389,null,"COPE-UCM 2","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","COPE-UCM 2 (02)",7.0293828201883877E-5]
[16390,null,"COPE-UCM 2","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","COPE-UCM 2 (02)",7.0293828201883877E-5]
[16391,null,"KERNAN-CARNARVON","NS0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","KERNAN-CARNARVON (01)",7.0293828201883877E-5]
[16392,null,"ORIEL-STANLEY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",7.0293828201883877E-5]
[16393,null,"SUSSEX-NEWCASTLE","EP0-037","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","SUSSEX-NEWCASTLE (02)",7.0293828201883877E-5]
[16394,null,"GLENVIEW-UPLAND","NS0-017","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","GLENVIEW-UPLAND (01)",7.0293828201883877E-5]
[16395,null,"ASHLEY-NAPOLEON","TH0-012","2024-12-01","2024-12-07","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",7.0293828201883877E-5]
[16396,null,"MALMSBURY-WOODBURN","BD0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","BD0","MALMSBURY-WOODBURN (02)",7.0293828201883877E-5]
[16397,null,null,null,"2024-12-01","2024-12-07","N","Y","N","N","N","N",null,"TALBOT-WALLACE (04)",7.0293828201883877E-5]
[16398,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[16399,null,"BOND-LIBERTY","EP0-034","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BOND-LIBERTY (03)",7.0293828201883877E-5]
[16400,null,"WHITELAW-BOLDREWOOD","TT0-011","2024-12-01","2024-12-07","N","Y","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",7.0293828201883877E-5]
[16401,null,"ALEXANDRA-WALKER","NS0-009","2024-12-01","2024-12-07","N","Y","N","N","N","N","NS0","MOONEE VLY-RACECRS 1 (03)",7.0293828201883877E-5]
[16402,null,"BRUTHEN-CHIFLEY","EP0-042","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","BRUTHEN-CHIFLEY (00)",7.0293828201883877E-5]
[16403,null,"CHIFLEY 62-RENNICK","EP0-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","CHIFLEY 62-RENNICK (00)",7.0293828201883877E-5]
[16404,null,"REX-CHIFLEY","EP0-041","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","REX-CHIFLEY (02)",7.0293828201883877E-5]
[16405,null,"FREIGHT-CUSTOM","AW0-014","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (02)",7.0293828201883877E-5]
[16406,null,"INTERNATIONAL-T'PARK","AW0-004","2024-12-01","2024-12-07","N","Y","N","N","N","N","AW0","INTERNATIONAL-T'PARK (00)",7.0293828201883877E-5]
[16407,null,"SOMERTON 17-HUME","ST0-024","2024-12-01","2024-12-07","N","Y","N","N","N","N","ST0","SOMERTON 17-HUME (02)",7.0293828201883877E-5]
[16408,null,"CHIFLEY 68-RENNICK","EP0-032","2024-12-01","2024-12-07","N","Y","N","N","N","N","EP0","CHIFLEY 68-RENNICK (05)",7.0293828201883877E-5]

{"sheet":"EDCoP_1-12-2024_mD_High V by DS","index":3,"n_rows":1079,"n_cols":3,"rows_kept":1079,"cut":false,"hidden":false,"merged":[]}
["Max.One.Percentage","Y"]
[]
["Row Labels","Count of NMIs","Sum of Max.One.Percentage (%)"]
["RAGLAN-ASCOT",235,1.6519049627442786E-2]
["ORIEL-STANLEY",171,1.2020244622522174E-2]
["HUTCHESON-BUCKLEY",168,1.180936313791652E-2]
["ELLIOT-GRAHAM",149,1.0473780402080713E-2]
["ALBERT-MT ALEXANDER",147,1.0333192745676944E-2]
["MCCRAE-ELSEY",145,1.0192605089273174E-2]
["DALVEEN-JELLICOE",143,1.0052017432869405E-2]
["MIHIL-VICTORIA",140,9.8411359482637514E-3]
["FLETCHER-PASCOE VALE",138,9.7005482918599822E-3]
["MELCOMBE-BANKSIA",135,9.4896668072543284E-3]
["BOURNIAN-GRAMMAR",132,9.2787853226486746E-3]
["YORK-NAPIER",128,8.9976100098411362E-3]
["TURNER-EVANS",125,8.7867285252354824E-3]
["FULLER-SCHOFIELD",124,8.7164346970335978E-3]
["GREEN-SPARKFORD",124,8.7164346970335978E-3]
["MONTGOMERY-MT ALEXANDER",124,8.7164346970335978E-3]
["BOND-ORIEL",123,8.6461408688317132E-3]
["BOND-LIBERTY",122,8.5758470406298287E-3]
["WHITELAW-BOLDREWOOD",122,8.5758470406298287E-3]
["PURINUAN-NUTWOOD",117,8.2243778996204057E-3]
["BEENAK-PURINUAN",115,8.0837902432166365E-3]
["THOMAS-PASCOE VALE",113,7.9432025868128673E-3]
["ANNE-DALEGLEN",111,7.802614930409099E-3]
["RAVENSCOURT-FULHAM",111,7.802614930409099E-3]
["KERNAN-CARNARVON",110,7.7323211022072152E-3]
["TIERNAN-RAGLAN",108,7.5917334458034478E-3]
["HODDLE-FLETCHER",107,7.5214396176015641E-3]
["GLADSTONE-ASCOT VALE",106,7.4511457893996803E-3]
["HUTCHESON-THE STRAND",101,7.0996766483902617E-3]
["JHONSON-BRENTWOOD",98,6.8887951637846105E-3]
["MARGARET-MURPHY",94,6.6076198509770756E-3]
["ORIEL-HAWKER",93,6.5373260227751919E-3]
["GISBORNE-NORTH",92,6.4670321945733081E-3]
["SUSSEX-NEWCASTLE",91,6.3967383663714244E-3]
["MT ALEXANDER-NAPIER",90,6.3264445381695407E-3]
["WOODLAND-ALFRED",90,6.3264445381695407E-3]
["RALEIGH-HODDLE",89,6.256150709967657E-3]
["SOUTHEY-ARDEN",87,6.1155630535638895E-3]
["WALLACE-KENILWORTH",87,6.1155630535638895E-3]
["INVERMAY-ST VIGEONS",85,5.9749753971601221E-3]
["PROGRESS-PASCOE VALE",84,5.9046815689582383E-3]
["HARRISON-DAVIDSON",82,5.7640939125544709E-3]
["MACK-PICKETT",82,5.7640939125544709E-3]
["GOLF-FLAG",81,5.6938000843525871E-3]
["BUTLER-PASCOE VALE",80,5.6235062561507034E-3]
["BRADSHAW-MARYBOROUGH",80,5.6235062561507034E-3]
["ARGYLE-DAREBIN",78,5.482918599746936E-3]
["GREENOCK-DAREBIN",78,5.482918599746936E-3]
["McPHERSON-KENNA",75,5.2720371151412848E-3]
["SALTER-NAPIER",73,5.1314494587375173E-3]
["BREWSTER-MT ALEXANDER",72,5.0611556305356336E-3]
["ALBERT-DUNDAS",72,5.0611556305356336E-3]
["JEFFREY-WESTGARTH",72,5.0611556305356336E-3]
["TAYLOR-MT ALEXANDER",72,5.0611556305356336E-3]
["THISTLE-MT ALEXANDER",72,5.0611556305356336E-3]
["FINTON-ARUNDEL",70,4.9205679741318661E-3]
["CAMERON-PASCOE VALE",67,4.709686489526215E-3]
["ACACIA-PARKSIDE",66,4.6393926613243312E-3]
["MOORE-PUCKLE",66,4.6393926613243312E-3]
["WARNER-GLASS",66,4.6393926613243312E-3]
["WORDSWORTH-MT ALEXANDER",66,4.6393926613243312E-3]
["HESLEDEN-AMELIA",65,4.5690988331224475E-3]
["HOMER-EDDY",65,4.5690988331224475E-3]
["HALL-MARGARET",65,4.5690988331224475E-3]
["KERFERD-RALEIGH",65,4.5690988331224475E-3]
["CARROL-ORRONG",64,4.4988050049205638E-3]
["MACKAY-GLASS",64,4.4988050049205638E-3]
["ROSENTHAL-ALLENBY",64,4.4988050049205638E-3]
["McPHERSON-ALEXANDRA 2",61,4.2879235203149126E-3]
["ELLERSLIE-CASH",60,4.2176296921130289E-3]
["NAPIER-BUTLER",60,4.2176296921130289E-3]
["ROSELAND-IVANHOE",59,4.1473358639111451E-3]
["DONALD-LAWSON",57,4.0067482075073777E-3]
["FOCH-TYLER",56,3.936454379305494E-3]
["LIBERTY-BELL",56,3.936454379305494E-3]
["MONTGOMERY-MT ALEXANDER #2",56,3.936454379305494E-3]
["ALTONA-ORIEL",55,3.8661605511036098E-3]
["DAPHNE-BANKSIA",55,3.8661605511036098E-3]
["NICHOLSON-BREWSTER",55,3.8661605511036098E-3]
["WATERDALE-AILSA",55,3.8661605511036098E-3]
["BROWNING-SCOTT",54,3.7958667229017261E-3]
["MARSHALL-INVERMAY",54,3.7958667229017261E-3]
["ROYAL-MCMAHON",54,3.7958667229017261E-3]
["RALEIGH 87-NAPIER",54,3.7958667229017261E-3]
["BOOMERANG-AIRFORCE",52,3.6552790664979586E-3]
["BUCKLEY-HODDLE",52,3.6552790664979586E-3]
["LLOYD-MONASH",51,3.5849852382960749E-3]
["PRATT-PUCKLE",51,3.5849852382960749E-3]
["GREEN 103-SPARKFORD",49,3.4443975818923074E-3]
["GLEN-GLASS",49,3.4443975818923074E-3]
["LUDEMAN-BRAITHWAITE",49,3.4443975818923074E-3]
["MANOEL-DAREBIN",49,3.4443975818923074E-3]
["CRAWFORD-ROBINSON",47,3.30380992548854E-3]
["GLASGOW-HIGH",45,3.1632222690847725E-3]
["ASHLEY-NAPOLEON",43,3.0226346126810051E-3]
["PASCOE VALE-WOODLAND",43,3.0226346126810051E-3]
["BROWNING-MOORE",42,2.9523407844791213E-3]
["FAWKNER-ROBERTS",42,2.9523407844791213E-3]
["MT ALEXANDER 902-WILLOW",42,2.9523407844791213E-3]
["HOBBS-BROADHURST",41,2.8820469562772376E-3]
["SALMON-SCHOFIELD",41,2.8820469562772376E-3]
["SOUTH-BELL",41,2.8820469562772376E-3]
["RIDGEWAY-LWR HEIDELBERG",40,2.8117531280753539E-3]
["LAWSON-KENDALL",39,2.7414592998734701E-3]
["BOND-ATHELSTANE",38,2.6711654716715864E-3]
["GLASS-NAPIER",38,2.6711654716715864E-3]
["ATHELSTANE-ROBBINS",37,2.6008716434697027E-3]
["EDWIN-ST HELLIER",37,2.6008716434697027E-3]
["GORDON-WOOD",37,2.6008716434697027E-3]
["LOCH-WENDORA",37,2.6008716434697027E-3]
["VANBERG-TENNYSON",37,2.6008716434697027E-3]
["ST VIGEONS-BORRIE",37,2.6008716434697027E-3]
["WILLOWTREE-PERSICA",37,2.6008716434697027E-3]
["AYR-DAREBIN",36,2.530577815267819E-3]
["NEWCASTLE-DUNDAS",36,2.530577815267819E-3]
["HENDERSON-WILSON",35,2.4602839870659352E-3]
["ALBERT 8-14 FOLEY",34,2.3899901588640515E-3]
["WATERDALE-BANKSIA",34,2.3899901588640515E-3]
["FENTON-MYRNONG",33,2.3196963306621678E-3]
["VANTAGE-DASHING",33,2.3196963306621678E-3]
["CRANWELL-CARNARVON",32,2.2494025024602841E-3]
["SEVERN-BENBOW",32,2.2494025024602841E-3]
["LAWSON-SALISBURY",31,2.1791086742584003E-3]
["PASCOE VALE 314-CAMERON",31,2.1791086742584003E-3]
["KILMORE-CHARLTON",31,2.1791086742584003E-3]
["EDDY-TAYLOR",30,2.1088148460565166E-3]
["ROSEBERRY-HIGH",30,2.1088148460565166E-3]
["CHEDDAR-MACARTNEY",29,2.0385210178546329E-3]
["FREIGHT-CUSTOM",29,2.0385210178546329E-3]
["LISTON-JOHNSON",29,2.0385210178546329E-3]
["KIORA-PASCOE VALE",29,2.0385210178546329E-3]
["WHITELAW-BROADWAY",29,2.0385210178546329E-3]
["ASQUITH-STURDEE",28,1.9682271896527491E-3]
["MARATHON 281-HIGHLANDER",28,1.9682271896527491E-3]
["RIVERSIDE-WATERVIEW",28,1.9682271896527491E-3]
["WASHINGTON-DOY",28,1.9682271896527491E-3]
["BROADHURST-MCFADZEAN",27,1.8979333614508654E-3]
["BLAKE-SESTON",27,1.8979333614508654E-3]
["FANNY-SALISBURY",27,1.8979333614508654E-3]
["HOBBS-PENTLAND",27,1.8979333614508654E-3]
["JOHNSON-BENAUD",26,1.8276395332489815E-3]
["GLASS-NAPIER NO.2",26,1.8276395332489815E-3]
["NAPIER 20-FLETCHER",26,1.8276395332489815E-3]
["ASCOT VALE 331-YOUNG",25,1.7573457050470975E-3]
["RENFEW-ARKLEY",25,1.7573457050470975E-3]
["HUDSONS-HALL",24,1.6870518768452136E-3]
["LANGTON-GREENVALE",24,1.6870518768452136E-3]
["MAGDALA-WOODLAND",24,1.6870518768452136E-3]
["WRIGHT 20-THOMSONS",24,1.6870518768452136E-3]
["STEPHEN-PRINCESS",24,1.6870518768452136E-3]
["BUNTING-SOMERVILLE 463A",23,1.6167580486433296E-3]
["DAVIDSON-PERKINS",23,1.6167580486433296E-3]
["INVERNESS-INVERMAY",23,1.6167580486433296E-3]
["ETZEL-CLYDESDALE",23,1.6167580486433296E-3]
["EAST-HARDING",23,1.6167580486433296E-3]
["ROSENTHAL-HUGHES",23,1.6167580486433296E-3]
["ALPHINGTON-PARK",22,1.5464642204414457E-3]
["CAPULET-BENT",22,1.5464642204414457E-3]
["GREENVALE-WALLACE",22,1.5464642204414457E-3]
["DEAKIN-MARY",22,1.5464642204414457E-3]
["WINIFRED-GLASS No2",22,1.5464642204414457E-3]
["SALTAU-MILLEARA",22,1.5464642204414457E-3]
["WARRAGUL-LISMORE",22,1.5464642204414457E-3]
["COLLINS-WATERDALE",21,1.4761703922395618E-3]
["BREWSTER-NAPIER",21,1.4761703922395618E-3]
["BRAY-BARTROP",21,1.4761703922395618E-3]
["HILLSYDE-LOEMAN",21,1.4761703922395618E-3]
["HAMPDEN-CROTHERS",21,1.4761703922395618E-3]
["MCPHERSON-BENT",21,1.4761703922395618E-3]
["LENNOX-HYDE",21,1.4761703922395618E-3]
["YEA-KIEWA",21,1.4761703922395618E-3]
["BELLEVUE-SWANSTON",20,1.4058765640376778E-3]
["BICENTENNIAL-SHABA",20,1.4058765640376778E-3]
["HENDRICKS-LORRAINE",20,1.4058765640376778E-3]
["JAMES-WILLIAMSON",20,1.4058765640376778E-3]
["WHITE-CHEDDAR",20,1.4058765640376778E-3]
["RALEIGH-NAPIER No. 2",20,1.4058765640376778E-3]
["YERING-GUILDFORD",20,1.4058765640376778E-3]
["SAMARA-ELMHURST",20,1.4058765640376778E-3]
["GLENVIEW-UPLAND",19,1.3355827358357939E-3]
["POWELL-EXCELSIOR",19,1.3355827358357939E-3]
["MT ALEXANDER-HOMER",19,1.3355827358357939E-3]
["WOODLAND-NAPIER",19,1.3355827358357939E-3]
["ROWE-YARRALEA",19,1.3355827358357939E-3]
["ALEXANDER-JOHN",18,1.2652889076339099E-3]
["ANDERSON-BEVERLEY",18,1.2652889076339099E-3]
["BELL-ORIEL",18,1.2652889076339099E-3]
["DELHI-MOOLTAN",18,1.2652889076339099E-3]
["GOSFORD-NICHOLAS",18,1.2652889076339099E-3]
["LOTUS-CASSINIA",18,1.2652889076339099E-3]
["MT ALEXANDER-RUSSELL",18,1.2652889076339099E-3]
["WESTMERE-WARNE",18,1.2652889076339099E-3]
["SANDOVER-SALWEEN",18,1.2652889076339099E-3]
["THOMAS-WILSON",18,1.2652889076339099E-3]
["HARCOURT-SHERBOURNE",17,1.194995079432026E-3]
["WHITFIELD-WHITES",17,1.194995079432026E-3]
["AMIS-VISTA",16,1.124701251230142E-3]
["BURKE-FLINDERS",16,1.124701251230142E-3]
["ALAMEIN-SOUTHERN",16,1.124701251230142E-3]
["GRANDISON-MT ALEXANDER",16,1.124701251230142E-3]
["LAWLEY-PALLANT",16,1.124701251230142E-3]
["SEXTON-HALSEY",16,1.124701251230142E-3]
["(blank)",16,1.124701251230142E-3]
["VALLEY-AUGUSTINE",16,1.124701251230142E-3]
["JULIET-BENT",15,1.0544074230282581E-3]
["FIELD-GRANDISON",15,1.0544074230282581E-3]
["HAMILTON-O'FARRELL",15,1.0544074230282581E-3]
["ERINBANK-DOBIES",15,1.0544074230282581E-3]
["LILLEE 60-MALLETT",15,1.0544074230282581E-3]
["PEPPERTREE-LOUDON",15,1.0544074230282581E-3]
["MATTHEWS-KEILOR",15,1.0544074230282581E-3]
["PARKSIDE-HIGHVIEW",15,1.0544074230282581E-3]
["KELVIN-ALBERT",15,1.0544074230282581E-3]
["SALWEEN-ELSA",15,1.0544074230282581E-3]
["WESTS-WILLIAMSON 2",15,1.0544074230282581E-3]
["ROKEWOOD-ELLAM",15,1.0544074230282581E-3]
["TONGUE-MACKAY",15,1.0544074230282581E-3]
["CORINELLA-BLAIR",14,9.8411359482637414E-4]
["BRIDGEHAVEN-WATER GUM",14,9.8411359482637414E-4]
["ESTEEM-DISTINCTION",14,9.8411359482637414E-4]
["LAKES-THE GREENWAY",14,9.8411359482637414E-4]
["PASCOE VALE-MT ALEXANDER",14,9.8411359482637414E-4]
["NEWTON-CREVELLI",14,9.8411359482637414E-4]
["QUINN-ST. JAMES",14,9.8411359482637414E-4]
["MERRILANDS-ASQUITH",14,9.8411359482637414E-4]
["KING-BOWES",14,9.8411359482637414E-4]
["REDESDALE-GALVIN",14,9.8411359482637414E-4]
["WYONG-CENTREWAY",14,9.8411359482637414E-4]
["WADHAM-MORELAND",14,9.8411359482637414E-4]
["WEBB-CORONATION",14,9.8411359482637414E-4]
["BUCKLEY-MT ALEXANDER",13,9.1381976662449019E-4]
["CENTRE WAY-FRAN",13,9.1381976662449019E-4]
["CHIFLEY 51-53-RAGLAN",13,9.1381976662449019E-4]
["BANK-MT ALEXANDER",13,9.1381976662449019E-4]
["BLIBURG-SUNSET",13,9.1381976662449019E-4]
["DONVALE-HAYFIELD",13,9.1381976662449019E-4]
["FINK-CHIFLEY",13,9.1381976662449019E-4]
["JOHN-WINIFRED",13,9.1381976662449019E-4]
["OWEN-GORDON",13,9.1381976662449019E-4]
["MARY-BRUCE",13,9.1381976662449019E-4]
["LAWLEY-GLASGOW",13,9.1381976662449019E-4]
["WODONGA-CUTHBERT",13,9.1381976662449019E-4]
["BEDWELL-HUGHES",12,8.4352593842260636E-4]
["BELL-QUINN",12,8.4352593842260636E-4]
["DEVON-OAK",12,8.4352593842260636E-4]
["FIRST-BULLA",12,8.4352593842260636E-4]
["POUND-PERISHER",12,8.4352593842260636E-4]
["MELTON-MEWS",12,8.4352593842260636E-4]
["MADDEN-STUDLEY",12,8.4352593842260636E-4]
["REX-CHIFLEY",12,8.4352593842260636E-4]
["SUSSEX-BANYULE",12,8.4352593842260636E-4]
["ALMA-CHANDLER",11,7.7323211022072252E-4]
["BREX-RADFORD",11,7.7323211022072252E-4]
["ALEXANDRA-NORTHERNHAY",11,7.7323211022072252E-4]
["BREWSTER-PASCOE VALE",11,7.7323211022072252E-4]
["CRAMER-MARKET NO2",11,7.7323211022072252E-4]
["BRENTWOOD-WENTWORTH",11,7.7323211022072252E-4]
["BRADFORD-KIRBY",11,7.7323211022072252E-4]
["CALA-HAMPTON",11,7.7323211022072252E-4]
["GARNET-IDA",11,7.7323211022072252E-4]
["MALMSBURY-WOODBURN",11,7.7323211022072252E-4]
["OAKGROVE-HUNTINGTON",11,7.7323211022072252E-4]
["MALACCA-WATERDALE",11,7.7323211022072252E-4]
["THE CROSSWAY-PARK",11,7.7323211022072252E-4]
["ROBINS-SHAPIRO",11,7.7323211022072252E-4]
["THE PARADE-EPSOM",11,7.7323211022072252E-4]
["WESTERN-GLOBAL",11,7.7323211022072252E-4]
["THE CROSSWAY-UPLAND",11,7.7323211022072252E-4]
["COPE-UCM 2",10,7.0293828201883869E-4]
["ALMA-ELPHINSTONE",10,7.0293828201883869E-4]
["AMBLESIDE-MOTHERWELL",10,7.0293828201883869E-4]
["COPE-UCM 1",10,7.0293828201883869E-4]
["CHIFLEY 72-REX",10,7.0293828201883869E-4]
["COPE-MOORE",10,7.0293828201883869E-4]
["CRESSWELL-CAMERON",10,7.0293828201883869E-4]
["DAVERN-O'HEA",10,7.0293828201883869E-4]
["CHALLIS-JUBILLEE",10,7.0293828201883869E-4]
["GRAHAM-GLEN ALLAN",10,7.0293828201883869E-4]
["FEATHERPARK-HUNTINGTON",10,7.0293828201883869E-4]
["HIGGINS-MCKELL",10,7.0293828201883869E-4]
["HUME 1487-THOMPSON",10,7.0293828201883869E-4]
["PASLEY-NEILL",10,7.0293828201883869E-4]
["LATROBE-MENZIES",10,7.0293828201883869E-4]
["PAISLEY 79-FRENCH",10,7.0293828201883869E-4]
["WOOD-BROWN",10,7.0293828201883869E-4]
["TURNER-MENZIES",10,7.0293828201883869E-4]
["RESERVE-DUNDAS",10,7.0293828201883869E-4]
["RIGGALL-APOLLO",10,7.0293828201883869E-4]
["SHAFTESBURY-RALEIGH",10,7.0293828201883869E-4]
["ROXBURGH-ROTHWELL",10,7.0293828201883869E-4]
["WATERDALE-GRIFFITHS",10,7.0293828201883869E-4]
["CHAMPION-ZEST",9,6.3264445381695485E-4]
["BREX 8-RADFORD",9,6.3264445381695485E-4]
["ASCOT VALE 259-REGENT",9,6.3264445381695485E-4]
["ALBERT 28-RAGLAN",9,6.3264445381695485E-4]
["CATHERINE-ANTIONETTA",9,6.3264445381695485E-4]
["BANKSIA-OSNEY",9,6.3264445381695485E-4]
["CENTREWAY-WINGARA",9,6.3264445381695485E-4]
["HILLSIDE-HURTLE",9,6.3264445381695485E-4]
["GREENACRE-AYLESBURY",9,6.3264445381695485E-4]
["FINN-HAUGHTON",9,6.3264445381695485E-4]
["GAUJA-ANDAMAN",9,6.3264445381695485E-4]
["GAP-COWPER",9,6.3264445381695485E-4]
["PETERSON-JACKSON",9,6.3264445381695485E-4]
["MARATHON-GANGES",9,6.3264445381695485E-4]
["MACK-HARMER",9,6.3264445381695485E-4]
["KINGSTON-COLLINSON",9,6.3264445381695485E-4]
["RAVENHILL-KNIGHT",9,6.3264445381695485E-4]
["ROSEHILL-TALBOT",9,6.3264445381695485E-4]
["WHITTON-BOYNE",9,6.3264445381695485E-4]
["STATION-GAMON",9,6.3264445381695485E-4]
["ROSS-ELIZABETH",9,6.3264445381695485E-4]
["RAGLAN-RESERVE",9,6.3264445381695485E-4]
["THE FAIRWAY-DUNNE",9,6.3264445381695485E-4]
["BIRCH-BROADMEADOWS",8,5.6235062561507101E-4]
["CLAYTON-MASCOMA",8,5.6235062561507101E-4]
["ANNADALE-KIRKHAM",8,5.6235062561507101E-4]
["BUCKLEY-MCPHERSON",8,5.6235062561507101E-4]
["CHAMPION-RIVERGLEN",8,5.6235062561507101E-4]
["BEAUMONT-WARATAH",8,5.6235062561507101E-4]
["CONNELL-HILTON",8,5.6235062561507101E-4]
["BANYULE-MCCRAE",8,5.6235062561507101E-4]
["BRAMCOTE-FORMAN",8,5.6235062561507101E-4]
["HAWKHURST-FRANCIS",8,5.6235062561507101E-4]
["HIGHLANDER-STREAMSIDE",8,5.6235062561507101E-4]
["HENLEY-CLARKE",8,5.6235062561507101E-4]
["MERCHISTON-CARNARVON",8,5.6235062561507101E-4]
["QUINN-NOGA",8,5.6235062561507101E-4]
["YARCOMBE-WOKING",8,5.6235062561507101E-4]
["TAGGERTY-MELWOOD",8,5.6235062561507101E-4]
["BIMBADEEN-YALLAMBIE",7,4.9205679741318718E-4]
["CHARTERIS-ATLEY",7,4.9205679741318718E-4]
["BEAUCHAMP-HIGH",7,4.9205679741318718E-4]
["CRAWLEY-HIGH",7,4.9205679741318718E-4]
["DELAWARE-JUSCELINA",7,4.9205679741318718E-4]
["FARRELL-RYDER",7,4.9205679741318718E-4]
["JACKA-JOYNT",7,4.9205679741318718E-4]
["GERVASE-PECHAM",7,4.9205679741318718E-4]
["FLETCHER-NICHOLSON",7,4.9205679741318718E-4]
["McEWEN-CURTIN",7,4.9205679741318718E-4]
["PUNJEL-CALDER",7,4.9205679741318718E-4]
["NICHOLSON-FLETCHER",7,4.9205679741318718E-4]
["METTLE-SCENERY",7,4.9205679741318718E-4]
["MCCARRON-FORRESTER",7,4.9205679741318718E-4]
["WALTHAM-LEE",7,4.9205679741318718E-4]
["WHITFIELD-CRAIGIEBURN",7,4.9205679741318718E-4]
["THERESA-CHRISTOPHER",7,4.9205679741318718E-4]
["SPELLMAN-BRENNAN",7,4.9205679741318718E-4]
["SIMMINGTON-KENTMERE",7,4.9205679741318718E-4]
["RHYOLITE-HIGHPARK",7,4.9205679741318718E-4]
["BEATRICE-JENSEN",6,4.2176296921130329E-4]
["BALMORAL-BRAEMAR",6,4.2176296921130329E-4]
["CHIFLEY 68-RENNICK",6,4.2176296921130329E-4]
["COBDEN-BARRY",6,4.2176296921130329E-4]
["BONVIEW-CARRINGTON",6,4.2176296921130329E-4]
["CHATHAM-CANTERBURY",6,4.2176296921130329E-4]
["DAVIS-MILITARY",6,4.2176296921130329E-4]
["BEECHER-RAGLAN",6,4.2176296921130329E-4]
["BORONIA-SUGARGUM",6,4.2176296921130329E-4]
["HASSETT-BORDER",6,4.2176296921130329E-4]
["HARDING-NICHOLSON",6,4.2176296921130329E-4]
["HART-BOWES",6,4.2176296921130329E-4]
["GREIG-THOMSON",6,4.2176296921130329E-4]
["ELINDA-TUNALEY",6,4.2176296921130329E-4]
["FORREST-HUDSONS",6,4.2176296921130329E-4]
["DOROTHY-ALEC",6,4.2176296921130329E-4]
["NEWMAN-HOTHAM",6,4.2176296921130329E-4]
["NORWOOD-PROSPECT",6,4.2176296921130329E-4]
["MONZA-FLORENCE",6,4.2176296921130329E-4]
["PECK-PASCOE VALE",6,4.2176296921130329E-4]
["LANDY-LICHFIELD",6,4.2176296921130329E-4]
["LANGHAM-CANNING",6,4.2176296921130329E-4]
["PASCOE VALE-KELLAWAY",6,4.2176296921130329E-4]
["LONG ISLAND-ROYAL TROON",6,4.2176296921130329E-4]
["NEWELL-MOORE",6,4.2176296921130329E-4]
["PASCOE VALE-BENDOC",6,4.2176296921130329E-4]
["WERRIBEE-AMBROSE",6,4.2176296921130329E-4]
["YORK-HYDE",6,4.2176296921130329E-4]
["WOOD-SYDNEY 2",6,4.2176296921130329E-4]
["WINGATE-VASEY",6,4.2176296921130329E-4]
["WOODLAND-WALLACE",6,4.2176296921130329E-4]
["WISTERIA-CHARTERIS",6,4.2176296921130329E-4]
["RUDSTONE-ABBEY",6,4.2176296921130329E-4]
["WEEMALA-SHANKLAND",6,4.2176296921130329E-4]
["WATT-THE AVENUE",6,4.2176296921130329E-4]
["BIRMINGHAM-MELBOURNE",5,3.514691410094194E-4]
["CRAIGIEBURN-CHAMPION",5,3.514691410094194E-4]
["CHARTERIS-WARNCLIFFE",5,3.514691410094194E-4]
["BUCHANAN-SALISBURY",5,3.514691410094194E-4]
["ALLENBY-ERIN",5,3.514691410094194E-4]
["BROWN-ROSANNA",5,3.514691410094194E-4]
["BEVERLEY-GREVILLE",5,3.514691410094194E-4]
["DEAKIN-BUCKLEY",5,3.514691410094194E-4]
["GREGORY-PLENTY",5,3.514691410094194E-4]
["GREENSBOROUGH-YALLAMBIE",5,3.514691410094194E-4]
["HYDE-BRISTOW",5,3.514691410094194E-4]
["GREIG-BARTROP",5,3.514691410094194E-4]
["DUNROSSIL-GORTON",5,3.514691410094194E-4]
["HERBERT-GARNER",5,3.514691410094194E-4]
["FLEETWOOD-GREENVALE",5,3.514691410094194E-4]
["HAYES-HOUSTON",5,3.514691410094194E-4]
["FLEET-STUBB NO2",5,3.514691410094194E-4]
["FORRESTER-HEDDERWICK",5,3.514691410094194E-4]
["DOLE-LOCHER",5,3.514691410094194E-4]
["HAIG-GILBERT",5,3.514691410094194E-4]
["GOLF VIEW-ROEBUCK",5,3.514691410094194E-4]
["LYDIA-DUNSTAN",5,3.514691410094194E-4]
["RAGLAN-CSIRO",5,3.514691410094194E-4]
["OXFORD-JUNCTION",5,3.514691410094194E-4]
["LOCK-LAURENCE",5,3.514691410094194E-4]
["OMAR-MITCHELL",5,3.514691410094194E-4]
["MANUKA-LIGHTWOOD",5,3.514691410094194E-4]
["McMAHON-CHEDDAR",5,3.514691410094194E-4]
["NAREEN-PAISLEY",5,3.514691410094194E-4]
["MEROLA 54 -FREEMAN",5,3.514691410094194E-4]
["MCIVOR-KIEWA",5,3.514691410094194E-4]
["MONT ALBERT-SUFFOLK",5,3.514691410094194E-4]
["KATHLEEN-WOOD",5,3.514691410094194E-4]
["MARGARET-WINIFRED",5,3.514691410094194E-4]
["MURRAY-PASCOE VALE",5,3.514691410094194E-4]
["KNOX-GILBERT",5,3.514691410094194E-4]
["LEBANON-ELDORADO",5,3.514691410094194E-4]
["MCKELL-HOLT",5,3.514691410094194E-4]
["MURDOCH-HASSETT",5,3.514691410094194E-4]
["KIAORA-GILBERT",5,3.514691410094194E-4]
["MCPHERSON-QUINN",5,3.514691410094194E-4]
["LYSTERFIELD-BEECHWORTH",5,3.514691410094194E-4]
["RIPPON-HOADLEY",5,3.514691410094194E-4]
["RYAN-MOORE",5,3.514691410094194E-4]
["RICE-HUGHES",5,3.514691410094194E-4]
["THE GRANGE-YALLAMBIE",5,3.514691410094194E-4]
["TENNYSON-TYLER",5,3.514691410094194E-4]
["RIVIERA-WARRICK",5,3.514691410094194E-4]
["THE CROSSWAY-VISTA",5,3.514691410094194E-4]
["ANDERSON-FEHON",4,2.8117531280753551E-4]
["ATHENS-DEVEREAUX",4,2.8117531280753551E-4]
["CANISBY-OLRIG",4,2.8117531280753551E-4]
["COUANGALT RD-P34",4,2.8117531280753551E-4]
["CASPIAN-MILLAU",4,2.8117531280753551E-4]
["BOSQUET-BALLARAT",4,2.8117531280753551E-4]
["ALOHA-GREENE",4,2.8117531280753551E-4]
["BELL 23-CONT PACK CO",4,2.8117531280753551E-4]
["CATHERINE-SAINSBURY",4,2.8117531280753551E-4]
["CLOVELLY-ENFIELD",4,2.8117531280753551E-4]
["DUNCANS LA STH-P3",4,2.8117531280753551E-4]
["GEELONG-QUEENSVILLE",4,2.8117531280753551E-4]
["DORSET-BERKELEY",4,2.8117531280753551E-4]
["ELIZA-EREBUS",4,2.8117531280753551E-4]
["JAMES-INDUSTRIAL GARDENS",4,2.8117531280753551E-4]
["GILLESPIE-MCLEOD",4,2.8117531280753551E-4]
["DROMANA-MATTHEWS",4,2.8117531280753551E-4]
["HUME 1445-CAMP",4,2.8117531280753551E-4]
["HARRICK-KEILOR PARK",4,2.8117531280753551E-4]
["HAMPDEN-GEACH",4,2.8117531280753551E-4]
["GLENGYLE-NICHOLSON",4,2.8117531280753551E-4]
["FERNHILL-BARODA",4,2.8117531280753551E-4]
["PRIOR-TAYLOR",4,2.8117531280753551E-4]
["KINGSLEY-AJ DAVIS RESERVE",4,2.8117531280753551E-4]
["MCCOLL-MALPAS",4,2.8117531280753551E-4]
["MACPHERSON-SHEPHERD",4,2.8117531280753551E-4]
["MOYANGUL-GUNGARLAN",4,2.8117531280753551E-4]
["MCCUBBIN-BLACKMAN",4,2.8117531280753551E-4]
["OUTAWOOD RISE-P3",4,2.8117531280753551E-4]
["LANTANA-IVANHOE",4,2.8117531280753551E-4]
["MOONEE VLY-RACECRS 3",4,2.8117531280753551E-4]
["NEILL-MOUNSEY",4,2.8117531280753551E-4]
["NEWLYN-PEMBROKE",4,2.8117531280753551E-4]
["PURINUAN-BOX",4,2.8117531280753551E-4]
["RAGLAN-DALEY",4,2.8117531280753551E-4]
["MONT ALBERT-RAINSFORD",4,2.8117531280753551E-4]
["PARINGA-JASMINE",4,2.8117531280753551E-4]
["LYON-MARTINS",4,2.8117531280753551E-4]
["MELON-CREMORNE",4,2.8117531280753551E-4]
["MIDDLE-ASCOT VALE",4,2.8117531280753551E-4]
["VICTORY-EREBUS",4,2.8117531280753551E-4]
["RATHCOWN-CHEDDAR",4,2.8117531280753551E-4]
["THE BOULEVARD-GILBERT",4,2.8117531280753551E-4]
["SOMERS-HINKLER",4,2.8117531280753551E-4]
["VANTAGE-ALTAMONT",4,2.8117531280753551E-4]
["SEPARATION-FULHAM",4,2.8117531280753551E-4]
["WOODBURN-CAMMS",4,2.8117531280753551E-4]
["TIMBOON-RIPPLEBROOK",4,2.8117531280753551E-4]
["RETREAT-HAVEN",4,2.8117531280753551E-4]
["TWEDDLE RD-P6",4,2.8117531280753551E-4]
["REES-STREETON",4,2.8117531280753551E-4]
["TRETHOWAN-SMILEY",4,2.8117531280753551E-4]
["ROKEWOOD-APPIN",4,2.8117531280753551E-4]
["SABRE-GARDEN",4,2.8117531280753551E-4]
["STIRLING-GLENCAIRN",4,2.8117531280753551E-4]
["STEVEDORE-STRAND",4,2.8117531280753551E-4]
["DAVIS-HANLEY",3,2.1088148460565162E-4]
["ALEXANDRA-PASCOEVALE",3,2.1088148460565162E-4]
["BULLA-DIGS REST-P21",3,2.1088148460565162E-4]
["BOGGYGATE RD-P10",3,2.1088148460565162E-4]
["BROWNING-GAMON",3,2.1088148460565162E-4]
["BLUEBIRD-BEVERIDGE",3,2.1088148460565162E-4]
["ARDMILLAN-MANTELL",3,2.1088148460565162E-4]
["BLACKMORE-ERROL",3,2.1088148460565162E-4]
["CANTALA-MCCRAE",3,2.1088148460565162E-4]
["CLUNES-MIRBOO",3,2.1088148460565162E-4]
["BOGGYGATE RD-P4E5",3,2.1088148460565162E-4]
["BIRDWOOD-REGENT",3,2.1088148460565162E-4]
["CLARK CRT-P3",3,2.1088148460565162E-4]
["ADMIRATION-REVERENCE",3,2.1088148460565162E-4]
["COPE-GAFFNEY",3,2.1088148460565162E-4]
["ALANBRAE-STONEBRIDGE",3,2.1088148460565162E-4]
["ANSTEY-LOCKTON",3,2.1088148460565162E-4]
["BENSON RD-P9A1",3,2.1088148460565162E-4]
["DALEY-BELL",3,2.1088148460565162E-4]
["BUTTERS-SPRING",3,2.1088148460565162E-4]
["BRUCE-JESSIE",3,2.1088148460565162E-4]
["BEDFORD-PARER",3,2.1088148460565162E-4]
["CAMBRIAN-HIGH",3,2.1088148460565162E-4]
["COHEN-GROVES",3,2.1088148460565162E-4]
["BARNET-MACKAY",3,2.1088148460565162E-4]
["AITKEN-BROOK",3,2.1088148460565162E-4]
["HYDE 258-KENT",3,2.1088148460565162E-4]
["INVERLOCH-MERINO",3,2.1088148460565162E-4]
["DUNCANS LA STH-P1",3,2.1088148460565162E-4]
["FAWKNER-BATMAN",3,2.1088148460565162E-4]
["DOBELL-LINDSAY",3,2.1088148460565162E-4]
["GAVIN-SUNSET",3,2.1088148460565162E-4]
["INTERNATIONAL-T'PARK",3,2.1088148460565162E-4]
["HEATHER-DINAH",3,2.1088148460565162E-4]
["HAVELOCK-BALLARAT",3,2.1088148460565162E-4]
["EVERARD-MAY",3,2.1088148460565162E-4]
["HONEYEATER-CASSOWARY",3,2.1088148460565162E-4]
["EUCALYPTUS-PEPPERMINT",3,2.1088148460565162E-4]
["DELAWARE-MENDIP",3,2.1088148460565162E-4]
["JOFFRE-KITCHENER",3,2.1088148460565162E-4]
["FINNINGLEY-MARHAM",3,2.1088148460565162E-4]
["HARDY-SNAEFELL",3,2.1088148460565162E-4]
["HAZELDENE-CERES",3,2.1088148460565162E-4]
["ESSEX-SWAN",3,2.1088148460565162E-4]
["DUNCANS LA NTH-P5E2",3,2.1088148460565162E-4]
["GOURLAY-SUGAR GUM",3,2.1088148460565162E-4]
["DISTINCTION-CENTURY",3,2.1088148460565162E-4]
["ELLERSLIE-DUNNE",3,2.1088148460565162E-4]
["HILTON-CHURCHILL",3,2.1088148460565162E-4]
["GAP-PRESTON",3,2.1088148460565162E-4]
["GOLEEN-SYDNEY",3,2.1088148460565162E-4]
["HODGSON-AVOCA",3,2.1088148460565162E-4]
["DIXON-DERBY",3,2.1088148460565162E-4]
["EGLINTON-ARGYLE",3,2.1088148460565162E-4]
["HIGHRIDGE-ROBERTS",3,2.1088148460565162E-4]
["HEPBURN-KING",3,2.1088148460565162E-4]
["HAUGHTON-GREVILLE",3,2.1088148460565162E-4]
["HUME HWY-P69",3,2.1088148460565162E-4]
["LOMBARD-JAMES MIRAM",3,2.1088148460565162E-4]
["MOORE 17-PUCKLE",3,2.1088148460565162E-4]
["MOROBE-ALAMEIN",3,2.1088148460565162E-4]
["MIMOSA-LAUREL",3,2.1088148460565162E-4]
["LORRAINE-JOHNSTONE",3,2.1088148460565162E-4]
["OUTAWOOD RISE-P1",3,2.1088148460565162E-4]
["LIBERTY-PERKINS",3,2.1088148460565162E-4]
["PENOLA COLLEGE-GIBSON",3,2.1088148460565162E-4]
["LANGDON-PETERLEE",3,2.1088148460565162E-4]
["NORTHUMBERLAND-FAWKNER",3,2.1088148460565162E-4]
["KERNAN-MARKS",3,2.1088148460565162E-4]
["PAYNE-RYLANDES",3,2.1088148460565162E-4]
["PARKSIDE-CHARTERIS",3,2.1088148460565162E-4]
["MARSHALL-TOORA",3,2.1088148460565162E-4]
["MT PLEASANT-BELL",3,2.1088148460565162E-4]
["QUEEN-RUSSELL",3,2.1088148460565162E-4]
["PARKER-AVOCA",3,2.1088148460565162E-4]
["MALTRAVERS-LOWER HEIDELBERG",3,2.1088148460565162E-4]
["LARGS-MOTHERWELL",3,2.1088148460565162E-4]
["KELLAWAY-GORDON",3,2.1088148460565162E-4]
["LANCE RD-P7E2",3,2.1088148460565162E-4]
["MAGNOLIA-BULLRUSH",3,2.1088148460565162E-4]
["OUTLOOK CRES-P9",3,2.1088148460565162E-4]
["NEAL-DINAH",3,2.1088148460565162E-4]
["LUSCANDER-TORMORVEY",3,2.1088148460565162E-4]
["MALCOLM-ELIZABETH",3,2.1088148460565162E-4]
["ROKEWOOD-BALOOK",3,2.1088148460565162E-4]
["WARD-MAY",3,2.1088148460565162E-4]
["WINDSOR-CECIL",3,2.1088148460565162E-4]
["TILBA-BRUNEL",3,2.1088148460565162E-4]
["TAUNTON-SPRING",3,2.1088148460565162E-4]
["SPRATLING-HENTY",3,2.1088148460565162E-4]
["SCOTIA-BELL",3,2.1088148460565162E-4]
["WAKELIN-STREETON",3,2.1088148460565162E-4]
["ROSAMOND-RIVER",3,2.1088148460565162E-4]
["WUNNAMURRA-WONGANELA",3,2.1088148460565162E-4]
["THE GARLAND-ROYAL",3,2.1088148460565162E-4]
["RICHELIEU-ESSEX",3,2.1088148460565162E-4]
["WARANGA-BLAIR",3,2.1088148460565162E-4]
["SPAVIN DR-P9",3,2.1088148460565162E-4]
["ST HELLIER-UP HEIDELBERG",3,2.1088148460565162E-4]
["VIDA-ALMA",3,2.1088148460565162E-4]
["WALLIS-KEILOR",3,2.1088148460565162E-4]
["WINCHESTER-WHARTON",3,2.1088148460565162E-4]
["WESTLAND RD-P6",3,2.1088148460565162E-4]
["WATSONS RD-P3",3,2.1088148460565162E-4]
["TANGEMERE-MICKLEHAM",3,2.1088148460565162E-4]
["CARDINAL-DALEY",2,1.4058765640376775E-4]
["BUNDOORA PARK-CHILDRENS FARM",2,1.4058765640376775E-4]
["DAYBREAK-HIGHLANDER",2,1.4058765640376775E-4]
["BULLARD RD-P4",2,1.4058765640376775E-4]
["ARGYLE-BROAD",2,1.4058765640376775E-4]
["BRADMAN-CHAPPEL",2,1.4058765640376775E-4]
["CHRISTINA-BARBARA",2,1.4058765640376775E-4]
["BRADLEY-MASON",2,1.4058765640376775E-4]
["COBRAM-LILLIPUT",2,1.4058765640376775E-4]
["CHIFLEY 62-RENNICK",2,1.4058765640376775E-4]
["ARTHUR-SEPARATION",2,1.4058765640376775E-4]
["COLLETT-ROSSITER",2,1.4058765640376775E-4]
["ANSTEY-PHILLIP",2,1.4058765640376775E-4]
["CHIFLEY 22-FINK",2,1.4058765640376775E-4]
["CHURCHILL-COONAMAR",2,1.4058765640376775E-4]
["BOGGYGATE RD-P11",2,1.4058765640376775E-4]
["COGHILL-BULLA",2,1.4058765640376775E-4]
["BLENHEIM-WOODS",2,1.4058765640376775E-4]
["BAILEY-HOPETOUN",2,1.4058765640376775E-4]
["COUANGALT RD-P23",2,1.4058765640376775E-4]
["AUSTIN-SEVERN",2,1.4058765640376775E-4]
["BLACKHILL RD-P11",2,1.4058765640376775E-4]
["ARVERN MEDFIELD No.2",2,1.4058765640376775E-4]
["BUCKLEY RD-P10",2,1.4058765640376775E-4]
["ARTHUR-BELL",2,1.4058765640376775E-4]
["CALDER FWY-P88",2,1.4058765640376775E-4]
["COMPASS-ORIENTEERING",2,1.4058765640376775E-4]
["CHAPMAN-BELAIR",2,1.4058765640376775E-4]
["BUNBURY-DOUGLAS",2,1.4058765640376775E-4]
["DAVIES-MILLER",2,1.4058765640376775E-4]
["CLARENDON-WHITTAKER",2,1.4058765640376775E-4]
["BEECHER-BURGESS CO",2,1.4058765640376775E-4]
["BURNS-WAVERLEY",2,1.4058765640376775E-4]
["BUNDOORA-GOLF COURSE",2,1.4058765640376775E-4]
["BEATTY-DALEY",2,1.4058765640376775E-4]
["BEAUMONT-ROBERTS",2,1.4058765640376775E-4]
["HEATHERLEA-STERLING",2,1.4058765640376775E-4]
["JOSEPHINE-MURPHY",2,1.4058765640376775E-4]
["HENRY-DENNIS",2,1.4058765640376775E-4]
["JACANA-LAHINCH",2,1.4058765640376775E-4]
["HILLVIEW DR-P7",2,1.4058765640376775E-4]
["HADDON HALL-BATEMAN",2,1.4058765640376775E-4]
["DUNFIELD-BERESFORD",2,1.4058765640376775E-4]
["FORDHAM-STRATHMERTON",2,1.4058765640376775E-4]
["DUNCANS LA NTH-P2",2,1.4058765640376775E-4]
["FOKKER-VICKERS",2,1.4058765640376775E-4]
["HOME-WILKINSON",2,1.4058765640376775E-4]
["KARNAK-PEARSON",2,1.4058765640376775E-4]
["GREEN VALLEY-CRAIGIEBURN",2,1.4058765640376775E-4]
["HUTCHINSON-NICHOLSON",2,1.4058765640376775E-4]
["FOSTERS-MIDWAY",2,1.4058765640376775E-4]
["ELLEN-RACHELLE",2,1.4058765640376775E-4]
["GISBORNE MELTON RD-P17E2",2,1.4058765640376775E-4]
["FLOWER-BUCKLEY",2,1.4058765640376775E-4]
["GILCHRIST-CROSBIE",2,1.4058765640376775E-4]
["HILBERT-HARRINGTON",2,1.4058765640376775E-4]
["HILLVIEW DR-P3",2,1.4058765640376775E-4]
["HILLVIEW DR-P5",2,1.4058765640376775E-4]
["GOFF-ELIZABETH",2,1.4058765640376775E-4]
["GISBORNE MELTON RD-P31E2",2,1.4058765640376775E-4]
["FENTON CLOSE-P1",2,1.4058765640376775E-4]
["EDWARDS RD-P3",2,1.4058765640376775E-4]
["HEIDELBERG-KINGSLEY",2,1.4058765640376775E-4]
["EDGAR-SOMERVILLE",2,1.4058765640376775E-4]
["HALL-MT ALEXANDER",2,1.4058765640376775E-4]
["GISBORNE MELTON RD-P27W2",2,1.4058765640376775E-4]
["FREELAND-ELEANOR",2,1.4058765640376775E-4]
["FLAGSTAFF-SWANSTON",2,1.4058765640376775E-4]
["GISBORNE MELTON RD-P20W2",2,1.4058765640376775E-4]
["DEBONAIR-DAPPER",2,1.4058765640376775E-4]
["GISBORNE MELTON-HOBBS",2,1.4058765640376775E-4]
["NICHOLSON-BRONCO",2,1.4058765640376775E-4]
["MORPHETT-DONCASTER",2,1.4058765640376775E-4]
["LIVINGSTONE-ELIZABETH",2,1.4058765640376775E-4]
["NEYLON-ROBERTS",2,1.4058765640376775E-4]
["MOREFIELD CRT-P4",2,1.4058765640376775E-4]
["RAGLAN 45-BEECHER",2,1.4058765640376775E-4]
["MITFORD-PARTON",2,1.4058765640376775E-4]
["PLATEAU-THROWER",2,1.4058765640376775E-4]
["NIMMO-BUCKLEY",2,1.4058765640376775E-4]
["OTWAY-VILLAWOOD",2,1.4058765640376775E-4]
["MORETTI-FORREST",2,1.4058765640376775E-4]
["MICKLEHAM RD-P0250",2,1.4058765640376775E-4]
["PEPPERCRESS-SPEARYS",2,1.4058765640376775E-4]
["MAISIE-LOMBARD",2,1.4058765640376775E-4]
["MERRICKS-ROSEBUD",2,1.4058765640376775E-4]
["O'FARRELL-WILLIAMSTOWN",2,1.4058765640376775E-4]
["MARLBOROUGH-DERBY",2,1.4058765640376775E-4]
["PASCOE VALE-CAMERON",2,1.4058765640376775E-4]
["MCCOLL-TYLER",2,1.4058765640376775E-4]
["MCNABS-ARUNDEL 3",2,1.4058765640376775E-4]
["PALMER RD-P8",2,1.4058765640376775E-4]
["PHILLIP-MILLEWA",2,1.4058765640376775E-4]
["NICHOLSON-GREEN VALLEY",2,1.4058765640376775E-4]
["RACECOURSE RD-P22",2,1.4058765640376775E-4]
["MAY-DAWSON",2,1.4058765640376775E-4]
["LOVAT-LONGFORD",2,1.4058765640376775E-4]
["MOORE-HENTY",2,1.4058765640376775E-4]
["OUTAWOOD RISE-P4",2,1.4058765640376775E-4]
["MARYSTON-SOMERVILLE",2,1.4058765640376775E-4]
["MCGREGOR-PERRY",2,1.4058765640376775E-4]
["KONNER-ERROL",2,1.4058765640376775E-4]
["MCGEORGE RD-P26",2,1.4058765640376775E-4]
["PATTERSON-DAVID",2,1.4058765640376775E-4]
["LOCKSLEY-MALTRAVERS",2,1.4058765640376775E-4]
["KELVERNE-NEWLANDS",2,1.4058765640376775E-4]
["LOCK RD-P19",2,1.4058765640376775E-4]
["NOLANS RD-P2",2,1.4058765640376775E-4]
["MADISONS-TERRITORY",2,1.4058765640376775E-4]
["WALSAL-PLENTY",2,1.4058765640376775E-4]
["ROYAL-GRANDVIEW",2,1.4058765640376775E-4]
["STOKES LA EAST-P1",2,1.4058765640376775E-4]
["STANLEY-THE GATE WAREHOUSE",2,1.4058765640376775E-4]
["ROCKWALL-STAGECOACH",2,1.4058765640376775E-4]
["WEBSTERS RD N-P10A",2,1.4058765640376775E-4]
["SUNMOTH-DEBONAIR",2,1.4058765640376775E-4]
["SPLENDOUR-MONTEREY",2,1.4058765640376775E-4]
["TOORA-IONA",2,1.4058765640376775E-4]
["SPENCER-COOPER",2,1.4058765640376775E-4]
["WATER FERN-BUTTERCUP",2,1.4058765640376775E-4]
["WILLS-DARWIN",2,1.4058765640376775E-4]
["THE BOULEVARD-NEVILLE",2,1.4058765640376775E-4]
["SOUTH-DERBY",2,1.4058765640376775E-4]
["SUSSEX-HOLMES",2,1.4058765640376775E-4]
["SOMMEVILLE-McCONNELL",2,1.4058765640376775E-4]
["STOKES LA EAST-P4",2,1.4058765640376775E-4]
["SOMERTON RD-P116E1",2,1.4058765640376775E-4]
["VIMY-VICKERS",2,1.4058765640376775E-4]
["SNYDER-TULLA PARK",2,1.4058765640376775E-4]
["WATERSONS RD-P3W1",2,1.4058765640376775E-4]
["YINNAR-BARRY",2,1.4058765640376775E-4]
["WILFRED-CEDRIC",2,1.4058765640376775E-4]
["SHELLEY-NOGA",2,1.4058765640376775E-4]
["WESTLAND RD-P2",2,1.4058765640376775E-4]
["WATTLEGLEN-SPURR",2,1.4058765640376775E-4]
["THE CIRCUIT-JOEL",2,1.4058765640376775E-4]
["SETTLERS WAY-P4",2,1.4058765640376775E-4]
["RIDDELL RD-P74",2,1.4058765640376775E-4]
["SEPARATION-SHIERS",2,1.4058765640376775E-4]
["WINSTON-JASON",2,1.4058765640376775E-4]
["SEPARATION-PERRY",2,1.4058765640376775E-4]
["SUNSHINE-MARKET No 2",2,1.4058765640376775E-4]
["TULLA 14-BEVERAGE",2,1.4058765640376775E-4]
["SUNBURY RD-P237",2,1.4058765640376775E-4]
["SANTOLIN-REBECCA",2,1.4058765640376775E-4]
["RALEIGH-CHIFLEY",2,1.4058765640376775E-4]
["WILLIAMSONS RD-P4",2,1.4058765640376775E-4]
["RAILWAY-RYE",2,1.4058765640376775E-4]
["TOWER-HEIDELBERG",2,1.4058765640376775E-4]
["SALISBURY-WILLIAMSTOWN",2,1.4058765640376775E-4]
["SALISBURY-JACK",2,1.4058765640376775E-4]
["BURTON-OAKLAND",1,7.0293828201883877E-5]
["ARTHUR-PARK",1,7.0293828201883877E-5]
["CALDER-DAVIS",1,7.0293828201883877E-5]
["AIRDRIE-GALASHIELS",1,7.0293828201883877E-5]
["CRAMER-MARKET",1,7.0293828201883877E-5]
["COUANGALT RD-P16",1,7.0293828201883877E-5]
["BUSHFIELD-KYABRAM",1,7.0293828201883877E-5]
["CALDER FWY-P15",1,7.0293828201883877E-5]
["COUANGALT RD-P14",1,7.0293828201883877E-5]
["BULLA-DIGS REST-P19",1,7.0293828201883877E-5]
["BLACKHILL RD-P7E2",1,7.0293828201883877E-5]
["BUCKLAND WAY-P8",1,7.0293828201883877E-5]
["BULLARD RD-P1",1,7.0293828201883877E-5]
["COMPTON-LEAMINGTON",1,7.0293828201883877E-5]
["DARVALL-WAIORA",1,7.0293828201883877E-5]
["BENSON RD-P15",1,7.0293828201883877E-5]
["COVENTRY-MALVERN",1,7.0293828201883877E-5]
["BENSON RD-P1",1,7.0293828201883877E-5]
["BROOKLYN 31-HUME",1,7.0293828201883877E-5]
["COLBERT-FLEXOVIT CO",1,7.0293828201883877E-5]
["BORONIA-LABURNUM",1,7.0293828201883877E-5]
["CHAPMAN-GRANDVIEW",1,7.0293828201883877E-5]
["COUANGALT RD-P22",1,7.0293828201883877E-5]
["CORTINA-MONTE CARLO",1,7.0293828201883877E-5]
["BRIDGEHAVEN-HUMBER",1,7.0293828201883877E-5]
["BELL-ALBERT",1,7.0293828201883877E-5]
["ANDERSON-MONASH",1,7.0293828201883877E-5]
["BELL 99-NATIONAL BANK",1,7.0293828201883877E-5]
["AMEILY-LEAMINGTON",1,7.0293828201883877E-5]
["BRUTHEN-CHIFLEY",1,7.0293828201883877E-5]
["CLIFTON-JEAN",1,7.0293828201883877E-5]
["BOLOGNA-PAVIA",1,7.0293828201883877E-5]
["COLLEEN-FAHEY",1,7.0293828201883877E-5]
["COLBERT 33-BARRY",1,7.0293828201883877E-5]
["CHIFLEY-FINK",1,7.0293828201883877E-5]
["BEECHER-DUNDAS 1",1,7.0293828201883877E-5]
["CAMBERWELL-McCRACKEN",1,7.0293828201883877E-5]
["BOLDREWOOD-McMAHON",1,7.0293828201883877E-5]
["CHARTERIS-BURKE",1,7.0293828201883877E-5]
["COIMADAI-TAME",1,7.0293828201883877E-5]
["COPELAND-BAMFORD",1,7.0293828201883877E-5]
["BOGGYGATE RD-P5",1,7.0293828201883877E-5]
["CARSON-LINDENOW",1,7.0293828201883877E-5]
["CHAMPION-BRAVEHEART",1,7.0293828201883877E-5]
["CULLEN-MARY",1,7.0293828201883877E-5]
["COMMERCIAL-CATHERINE",1,7.0293828201883877E-5]
["BLACKWOOD-POWELL",1,7.0293828201883877E-5]
["CHALLIS-SPEIGHT",1,7.0293828201883877E-5]
["CLIFTON-WATERDALE",1,7.0293828201883877E-5]
["BULLA-DIGS REST-P10",1,7.0293828201883877E-5]
["BLACKHILL RD-P33",1,7.0293828201883877E-5]
["BUNDOORA PARK-MUSEUM",1,7.0293828201883877E-5]
["ANN-ERROL",1,7.0293828201883877E-5]
["BEATRICE-FEHON",1,7.0293828201883877E-5]
["CAROLE JOY-SPRING",1,7.0293828201883877E-5]
["BATMAN-BUCKLEY",1,7.0293828201883877E-5]
["BLACKHILL RD-P23",1,7.0293828201883877E-5]
["DARLING-MARIBYRNONG",1,7.0293828201883877E-5]
["COUANGALT RD-P19",1,7.0293828201883877E-5]
["BOGGYGATE RD-P3",1,7.0293828201883877E-5]
["CAPRICORN-PALMERSTON",1,7.0293828201883877E-5]
["COCKATOO-COMPASS",1,7.0293828201883877E-5]
["COOPER ST-P43",1,7.0293828201883877E-5]
["BANKSIA-LIBERTY",1,7.0293828201883877E-5]
["ALMURTA-KYABRAM",1,7.0293828201883877E-5]
["CAVENDISH-TAFE COLL",1,7.0293828201883877E-5]
["COUANGALT RD-P12",1,7.0293828201883877E-5]
["BANCHORY-MELFIN",1,7.0293828201883877E-5]
["ALEXANDRA-WALKER",1,7.0293828201883877E-5]
["BOGGYGATE RD-P2",1,7.0293828201883877E-5]
["DAVID-RACHELLE",1,7.0293828201883877E-5]
["BALLYMENA-KIRKHAM",1,7.0293828201883877E-5]
["ALBION-GEELONG",1,7.0293828201883877E-5]
["CONDER-DOBELL",1,7.0293828201883877E-5]
["COURTNEY-PHILLIP",1,7.0293828201883877E-5]
["BUCKLEY-THE CROSSWAY",1,7.0293828201883877E-5]
["ALBERT 6-FOLEY",1,7.0293828201883877E-5]
["BUCKLEY-PHILLIP",1,7.0293828201883877E-5]
["COUANGALT RD-P39",1,7.0293828201883877E-5]
["CHEETHAM-CORONET",1,7.0293828201883877E-5]
["CASTLEHILL-HELMSDALE",1,7.0293828201883877E-5]
["BENSON RD-P9A3",1,7.0293828201883877E-5]
["BENSON RD-P9A2",1,7.0293828201883877E-5]
["COURTIS-MELBOURNE",1,7.0293828201883877E-5]
["BERGEN-NORDIC",1,7.0293828201883877E-5]
["BENSON RD-P9E3",1,7.0293828201883877E-5]
["DUFFY-BARRY",1,7.0293828201883877E-5]
["GELLIES RD-P3",1,7.0293828201883877E-5]
["HARDIMAN-ALBERMARLE",1,7.0293828201883877E-5]
["HILLVIEW RISE-P3",1,7.0293828201883877E-5]
["DUNKELD-PASCOE VALE",1,7.0293828201883877E-5]
["HUME-NORTHBOURNE",1,7.0293828201883877E-5]
["DORCHESTER-BANBURY",1,7.0293828201883877E-5]
["GLENBARRY 40-ADRIAN",1,7.0293828201883877E-5]
["HAVELOCK RD-P11",1,7.0293828201883877E-5]
["HOWARD LA-P2",1,7.0293828201883877E-5]
["EASTLEIGH-NORWOOD",1,7.0293828201883877E-5]
["FLANNERY-DEVEREAUX",1,7.0293828201883877E-5]
["FULLWOOD-WHEELER",1,7.0293828201883877E-5]
["HALSEY-RADFORD",1,7.0293828201883877E-5]
["DREDGE-TORMEY",1,7.0293828201883877E-5]
["HORNSBY-BAMFORD",1,7.0293828201883877E-5]
["FREDERICK-JUSTIN 3",1,7.0293828201883877E-5]
["HUME-GRAND",1,7.0293828201883877E-5]
["HANDSWORTH-LACKENHTH",1,7.0293828201883877E-5]
["HUME-CAMPBELL",1,7.0293828201883877E-5]
["ELATA-BEVERAGE",1,7.0293828201883877E-5]
["HAIG-ELLIOTT",1,7.0293828201883877E-5]
["GEELONG-McDONALD",1,7.0293828201883877E-5]
["GISBORNE MELTON-P33E1",1,7.0293828201883877E-5]
["EAGLEMONT-THE RIGHI",1,7.0293828201883877E-5]
["HEAD-NAPIER",1,7.0293828201883877E-5]
["HOBSON-HOME",1,7.0293828201883877E-5]
["DEAN-MT ALEXANDER",1,7.0293828201883877E-5]
["HARRICK 80-KEILOR PARK",1,7.0293828201883877E-5]
["FERGUSON-THE PARADE",1,7.0293828201883877E-5]
["FULLARTON-WALTERS",1,7.0293828201883877E-5]
["GROSVENOR-FLORENCE",1,7.0293828201883877E-5]
["FRENSHAM-HARBORNE",1,7.0293828201883877E-5]
["FENTON HILL RD-P7",1,7.0293828201883877E-5]
["FREIGHT 55-FLEET",1,7.0293828201883877E-5]
["FENTON HILL RD-P6",1,7.0293828201883877E-5]
["HENTY-GILBERT",1,7.0293828201883877E-5]
["FENTON HILL RD-P3",1,7.0293828201883877E-5]
["HANNAM-BICKERTON",1,7.0293828201883877E-5]
["FENTON CLOSE-P3",1,7.0293828201883877E-5]
["HAVELOCK RD-P5",1,7.0293828201883877E-5]
["HILLCREST-MICKLEHAM",1,7.0293828201883877E-5]
["ELEVATION-GILDED",1,7.0293828201883877E-5]
["FEHON-SOMERVILLE",1,7.0293828201883877E-5]
["GERTZ-BURNETT",1,7.0293828201883877E-5]
["FEHON-ANDERSON",1,7.0293828201883877E-5]
["JUMP-CART",1,7.0293828201883877E-5]
["HILLCREST-ARJAY",1,7.0293828201883877E-5]
["GEELONG-MALDEN",1,7.0293828201883877E-5]
["GISBORNE MELTON RD-P27W1N1",1,7.0293828201883877E-5]
["HIGHLAND RD-P4",1,7.0293828201883877E-5]
["GISBORNE MELTON RD-P27E2",1,7.0293828201883877E-5]
["JUKES-LANIGAN",1,7.0293828201883877E-5]
["GISBORNE MELTON RD-P27E1",1,7.0293828201883877E-5]
["GRANDVIEW-HOLMES",1,7.0293828201883877E-5]
["GISBORNE MELTON RD-P24W1",1,7.0293828201883877E-5]
["HUME 1498-BOLINDA",1,7.0293828201883877E-5]
["GISBORNE MELTON RD-P24E4",1,7.0293828201883877E-5]
["DUNCANS LA NTH-P3",1,7.0293828201883877E-5]
["EVANS 60-BROOK",1,7.0293828201883877E-5]
["DUNCAN-ASCOT VALE",1,7.0293828201883877E-5]
["GISBORNE MELTON RD-P24E3",1,7.0293828201883877E-5]
["DUCHESS-THE REGENCY",1,7.0293828201883877E-5]
["GISBORNE MELTON RD-P24E2",1,7.0293828201883877E-5]
["DRIVER-THE FAIRWAY",1,7.0293828201883877E-5]
["GISBORNE MELTON RD-P23",1,7.0293828201883877E-5]
["DOYLE-NORTH",1,7.0293828201883877E-5]
["HUME-BALDWIN",1,7.0293828201883877E-5]
["FREIGHT-FLEET",1,7.0293828201883877E-5]
["GISBORNE MELTON RD-P20E2",1,7.0293828201883877E-5]
["JELLICOE-OSNEY",1,7.0293828201883877E-5]
["ENDEAVOUR-WESTFIELD",1,7.0293828201883877E-5]
["HARDY-BENSTON",1,7.0293828201883877E-5]
["ENCHANT-ALTITUDE",1,7.0293828201883877E-5]
["GORDON-SHARPS",1,7.0293828201883877E-5]
["EMU RD-P3",1,7.0293828201883877E-5]
["DIMBOOLA-PASCOE VALE",1,7.0293828201883877E-5]
["KARINYA CRT-P3",1,7.0293828201883877E-5]
["HUME-PARAMOUNT CO",1,7.0293828201883877E-5]
["HOLDEN RD-P2",1,7.0293828201883877E-5]
["GODLEY-BROADHURST",1,7.0293828201883877E-5]
["HAVELOCK RD-P6",1,7.0293828201883877E-5]
["GILCHRIST-ELIZABETH",1,7.0293828201883877E-5]
["DEAN-FRANCIS",1,7.0293828201883877E-5]
["GISBORNE MELTON RD-P5",1,7.0293828201883877E-5]
["JESICA 49-VANESSA",1,7.0293828201883877E-5]
["GISBORNE MELTON RD-P31W2",1,7.0293828201883877E-5]
["GISBORNE MELTON-P34",1,7.0293828201883877E-5]
["MALBEC-THE SKYLINE",1,7.0293828201883877E-5]
["MOORE RD-P7",1,7.0293828201883877E-5]
["PAYWIT-BELLARINE",1,7.0293828201883877E-5]
["MAFFRA-P36",1,7.0293828201883877E-5]
["MOONEE-ASCOT VALE",1,7.0293828201883877E-5]
["KEILOR-MC CULLOCH",1,7.0293828201883877E-5]
["LEDGER-MAJOR",1,7.0293828201883877E-5]
["KEILOR-GOLF P5",1,7.0293828201883877E-5]
["MARARA-HIGHLANDER",1,7.0293828201883877E-5]
["MIRANDA-MAIS",1,7.0293828201883877E-5]
["MCGEORGE RD-P5",1,7.0293828201883877E-5]
["PEEL-DOUGLAS",1,7.0293828201883877E-5]
["PADDINGTON-WILLANDRA",1,7.0293828201883877E-5]
["MELBOURNE-DAVIES",1,7.0293828201883877E-5]
["NEWCASTLE-ELIZABETH",1,7.0293828201883877E-5]
["MACKENZIE-RADFORD",1,7.0293828201883877E-5]
["MT AITKEN RD-P16",1,7.0293828201883877E-5]
["PINE-MARSHALL",1,7.0293828201883877E-5]
["NEWMAN-SHOWERS",1,7.0293828201883877E-5]
["MACEDON-POWLETT",1,7.0293828201883877E-5]
["PLENTY-HARDIMAN RES",1,7.0293828201883877E-5]
["NAPOLI-VERONA",1,7.0293828201883877E-5]
["LANCEFIELD RD-P51",1,7.0293828201883877E-5]
["OLIVE-VIOLA",1,7.0293828201883877E-5]
["OUTAWOOD RISE-P7",1,7.0293828201883877E-5]
["PARKSIDE-STERLING",1,7.0293828201883877E-5]
["MOONEE VLY-RACECRS 4",1,7.0293828201883877E-5]
["OLD STOCK-COTSWOLDS",1,7.0293828201883877E-5]
["RACECOURSE RD-P6",1,7.0293828201883877E-5]
["NAMBOUR DR-P4",1,7.0293828201883877E-5]
["MOMMSEN RD-P3",1,7.0293828201883877E-5]
["OLD GEELONG-JONES",1,7.0293828201883877E-5]
["NORTHBOURNE 210-AINSLIE",1,7.0293828201883877E-5]
["RACECOURSE RD-P2",1,7.0293828201883877E-5]
["PAMELA-HERBERT",1,7.0293828201883877E-5]
["OUTAWOOD RISE-P6",1,7.0293828201883877E-5]
["MARIGOLD-ALDER",1,7.0293828201883877E-5]
["MASCOMA-STRATHNAVER",1,7.0293828201883877E-5]
["MELTON HWY-P59",1,7.0293828201883877E-5]
["MCNAMARA-ROBERTS",1,7.0293828201883877E-5]
["PASCOE-BLACK",1,7.0293828201883877E-5]
["MILLAR-DERBY",1,7.0293828201883877E-5]
["PALMER RD-P16E3",1,7.0293828201883877E-5]
["LOCKSLEY-KINSALE",1,7.0293828201883877E-5]
["MELTON HWY-P46",1,7.0293828201883877E-5]
["MT RIDLEY RD-P4",1,7.0293828201883877E-5]
["LANCEFIELD RD-P62",1,7.0293828201883877E-5]
["LOCKHEED-BOEING",1,7.0293828201883877E-5]
["LANCEFIELD RD-P50",1,7.0293828201883877E-5]
["MARTIN-GOWER",1,7.0293828201883877E-5]
["NEWCASTLE-MELBOURNE",1,7.0293828201883877E-5]
["MCNABS-ARUNDEL 2",1,7.0293828201883877E-5]
["KOALA-PELICAN",1,7.0293828201883877E-5]
["MT HOLDEN-P2",1,7.0293828201883877E-5]
["KITCHENER-MURRAY",1,7.0293828201883877E-5]
["RAGLAN-CHIFLEY",1,7.0293828201883877E-5]
["PERRY-VERDON",1,7.0293828201883877E-5]
["MT GISBORNE RD-P20",1,7.0293828201883877E-5]
["PERIGRINE-DEEP CREEK",1,7.0293828201883877E-5]
["LIMPOPA-DESNA",1,7.0293828201883877E-5]
["MALCOLM 51-ARI",1,7.0293828201883877E-5]
["PARKLANDS-KELVIN",1,7.0293828201883877E-5]
["OUTLOOK CRES-P3",1,7.0293828201883877E-5]
["MCKELL-RIDDELL",1,7.0293828201883877E-5]
["KENSWICK-MAHLAN",1,7.0293828201883877E-5]
["MARKS-YORK",1,7.0293828201883877E-5]
["NORTHUMBERLAND-ARNDT",1,7.0293828201883877E-5]
["PETERBOROUGH-TRINITY",1,7.0293828201883877E-5]
["PLATEAU 41-THROWER",1,7.0293828201883877E-5]
["LENA-ODONNELL",1,7.0293828201883877E-5]
["KATUNGA-HAMILTON",1,7.0293828201883877E-5]
["NEWCASTLE-BELL",1,7.0293828201883877E-5]
["NELSON-LYON",1,7.0293828201883877E-5]
["MICKLEHAM-SCAMPTON",1,7.0293828201883877E-5]
["TASMAN-MIDLAND",1,7.0293828201883877E-5]
["ROCKGLEN WAY P2",1,7.0293828201883877E-5]
["WATSONS RD-P5A",1,7.0293828201883877E-5]
["SETTLEMENT RD-P33E2",1,7.0293828201883877E-5]
["WALTER-ARRAN 2",1,7.0293828201883877E-5]
["STATION-HALL",1,7.0293828201883877E-5]
["READING-STAINSBY",1,7.0293828201883877E-5]
["SPELLMAN-CECIL",1,7.0293828201883877E-5]
["THE EYRIE-LAWRENCE",1,7.0293828201883877E-5]
["TULSA-MEDINAH",1,7.0293828201883877E-5]
["THE CREST-HILLCREST",1,7.0293828201883877E-5]
["SEARCH-OLD CALDER",1,7.0293828201883877E-5]
["RICHARDS-BELL",1,7.0293828201883877E-5]
["SCOVELL-CATHCART",1,7.0293828201883877E-5]
["RENNIE-GLENORA",1,7.0293828201883877E-5]
["VANESSA-JESICA",1,7.0293828201883877E-5]
["TWEDDLE RD-P3",1,7.0293828201883877E-5]
["SCHOOL-TRAP",1,7.0293828201883877E-5]
["ROMSEY-KEON",1,7.0293828201883877E-5]
["SCARVELL-PRO HART",1,7.0293828201883877E-5]
["SOMERTON 17-HUME",1,7.0293828201883877E-5]
["SARONVALE-HAWKESBURY",1,7.0293828201883877E-5]
["ROBERTS-MCNAMARA",1,7.0293828201883877E-5]
["WEBSTERS RD N-P28",1,7.0293828201883877E-5]
["TWEDDLE RD-P7",1,7.0293828201883877E-5]
["TRUMPER-KOKODA",1,7.0293828201883877E-5]
["ST LEONARDS-EPSOM",1,7.0293828201883877E-5]
["TRIFT-GREVILLEA",1,7.0293828201883877E-5]
["SHUTER-PUCKLE",1,7.0293828201883877E-5]
["WAVERLEY-ELECTRIC",1,7.0293828201883877E-5]
["RESERVOIR RD-P52",1,7.0293828201883877E-5]
["TREADWELL-DUDLEY",1,7.0293828201883877E-5]
["VINE-SHEPHERD",1,7.0293828201883877E-5]
["SOUTHERN-MEDWAY",1,7.0293828201883877E-5]
["WEBSTERS RD N-P21",1,7.0293828201883877E-5]
["TOUMLIN-MARTINS",1,7.0293828201883877E-5]
["SHADFORD-LITCHFIELD",1,7.0293828201883877E-5]
["VIEWBANK-BREES",1,7.0293828201883877E-5]
["SETTLEMENT RD-P33E3",1,7.0293828201883877E-5]
["STH CIRCULAR-HINTON",1,7.0293828201883877E-5]
["YELLOWGUM-BANKSIA",1,7.0293828201883877E-5]
["SAHI-CLEELAND",1,7.0293828201883877E-5]
["WARATAH-CAROL",1,7.0293828201883877E-5]
["TYSON-HEPBURN",1,7.0293828201883877E-5]
["ROCKGLEN WAY P4",1,7.0293828201883877E-5]
["WATERSONS RD-P6W1",1,7.0293828201883877E-5]
["WESTERN AVE-P30A",1,7.0293828201883877E-5]
["RUSSELL-PINE",1,7.0293828201883877E-5]
["WESTERN 21-GLOBAL",1,7.0293828201883877E-5]
["RUSSELL-BARKLY",1,7.0293828201883877E-5]
["RIVERBANK-BREAM",1,7.0293828201883877E-5]
["RUNNYMEDE LA-P5",1,7.0293828201883877E-5]
["VICTORIA-SOMERVILLE 3",1,7.0293828201883877E-5]
["WATERSONS RD-P5E1",1,7.0293828201883877E-5]
["SLATER-PRENDERGAST",1,7.0293828201883877E-5]
["SOUTH CIRCULAR-CARRICK",1,7.0293828201883877E-5]
["RICHARDSON-RESERVOIR",1,7.0293828201883877E-5]
["STANHOPE-ELPHINSTONE",1,7.0293828201883877E-5]
["YALLAMBIE-LOWER PLENTY",1,7.0293828201883877E-5]
["WATERSONS RD-P3S1",1,7.0293828201883877E-5]
["RHYOLITE-BANJOLINA",1,7.0293828201883877E-5]
["WILFRED-LOWER HEIDELBERG",1,7.0293828201883877E-5]
["WEBSTERS RD S-P2",1,7.0293828201883877E-5]
["SOMERVILLE-JULIAN",1,7.0293828201883877E-5]
["WEBSTERS RD N-P8",1,7.0293828201883877E-5]
["ROSS-DAVIDSON",1,7.0293828201883877E-5]
["SYDNEY-ROSSHIRE",1,7.0293828201883877E-5]
["ROSLYN-WOODS",1,7.0293828201883877E-5]
["SHOWMAN-BLOOMDALE",1,7.0293828201883877E-5]
["WILDWOOD RD N-P6",1,7.0293828201883877E-5]
["VINE-JIKA",1,7.0293828201883877E-5]
["STAMFORD-ACADEMY",1,7.0293828201883877E-5]
["SHEILA-MURRAY",1,7.0293828201883877E-5]
["THE PARADE-UNION",1,7.0293828201883877E-5]
["SHADFORTH-RALEIGH",1,7.0293828201883877E-5]
["WESTLAND RD-P3",1,7.0293828201883877E-5]
["STEPHEN-SCHILD",1,7.0293828201883877E-5]
["ROSEHILL-ROSE",1,7.0293828201883877E-5]
["WEBSTERS RD N-P4",1,7.0293828201883877E-5]
["SOMERTON RD-P111",1,7.0293828201883877E-5]
["WESTERN-QUARRY",1,7.0293828201883877E-5]
["Grand Total",14226,1.000000000000135]

{"sheet":"EDCoP_1-12-2024_mD_High V by ZS","index":4,"n_rows":35,"n_cols":3,"rows_kept":35,"cut":false,"hidden":false,"merged":[]}
["Max.One.Percentage","Y"]
[]
["Row Labels","Count of NMIs","Sum of Max.One.Percentage (%)"]
["NS0",4716,0.33150569380011358]
["TT0",2335,0.1641360888514016]
["EP0",2322,0.16322226908477697]
["AW0",520,3.6552790664979636E-2]
["BD0",442,3.1069872065232897E-2]
["PTN",352,2.4743427527063284E-2]
["ST0",350,2.4602839870659515E-2]
["FF0",327,2.2986081822016169E-2]
["SBY",293,2.0596091663152093E-2]
["FE0",257,1.8065513847884247E-2]
["BMS",246,1.7292281737663517E-2]
["FT0",215,1.5113173063405096E-2]
["EPN",212,1.4902291578799442E-2]
["ES0",212,1.4902291578799442E-2]
["COO",165,1.1598481653310866E-2]
["HB0",159,1.1176718684099559E-2]
["TH0",149,1.0473780402080713E-2]
["SHM",136,9.559960635456213E-3]
["PV0",118,8.2946717278222903E-3]
["KLO",111,7.802614930409099E-3]
["CN0",97,6.8185013355827268E-3]
["NH0",92,6.4670321945733081E-3]
["FW0",90,6.3264445381695407E-3]
["BY0",68,4.7799803177280987E-3]
["TMA",64,4.4988050049205638E-3]
["NT0",63,4.42851117671868E-3]
["YVE",55,3.8661605511036098E-3]
["CS0",36,2.530577815267819E-3]
["(blank)",16,1.124701251230142E-3]
["SA0",7,4.9205679741318718E-4]
["WT0",1,7.0293828201883877E-5]
["Grand Total",14226,1.000000000000135]

{"sheet":"EDCoP_2-2-2025_MD_Low V","index":5,"n_rows":28155,"n_cols":16,"rows_kept":4500,"cut":true,"hidden":false,"merged":[],"bounds":{"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0}}
[null,null,"Substation","HV.Feeder","Start.Time","End.Time","Min.One.Percentage","Max.One.Percentage","One.Percentage.Interection","Min.Consecutive.Violation","Max.Consecutive.Violation","Consecutive.Violation.Intersection","ZS","Circuit","Min.One.Percentage (%)","Min.Consecutive.Violation (%)"]
[1,null,"ROSEBERRY-HIGH","PTN-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","ROSEBERRY-HIGH (01)",{"$f":"IF(G2=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J2=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[2,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (01)",{"$f":"IF(G3=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J3=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[3,null,"CAMPBELL-FRANCIS","YVE-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","YVE","CAMPBELL-FRANCIS (01)",0,0]
[4,null,"SUNSHINE-MARKET No 2","TH0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","SUNSHINE-MARKET No 2 (02)",0,0]
[5,null,"FREDERICK-JUSTIN 3","TH0-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","FREDERICK-JUSTIN 3 (01)",0,0]
[6,null,"JAMES-INDUSTRIAL GARDENS","TH0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","JAMES-INDUSTRIAL GARDENS (02)",0,0]
[7,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MARGTMARY-MURRAY (03)",4.4620945071616617E-5,0]
[8,null,"HIGH 883-MELB WATER","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HIGH 883-MELB WATER (01)",4.4620945071616617E-5,0]
[9,null,"BREX 8-RADFORD","TT0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","BREX 8-RADFORD (01)",0,0]
[10,null,"BREX 8-RADFORD","TT0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","BREX 8-RADFORD (01)",0,0]
[11,null,"ALBERT-DUNDAS","EP0-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",0,0]
[12,null,"RESERVE-DUNDAS","EP0-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","RESERVE-DUNDAS (01)",0,0]
[13,null,"CHIFLEY 51-53-RAGLAN","EP0-035","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","CHIFLEY 51-53-RAGLAN (02)",0,0]
[14,null,"CHIFLEY 72-REX","EP0-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","CHIFLEY 72-REX (00)",0,0]
[15,null,"RESERVE-DUNDAS","EP0-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","RESERVE-DUNDAS (01)",0,0]
[16,null,"HUDSONS-HALL","YVE-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","YVE","HUDSONS-HALL (01)",0,0]
[17,null,"MARKS-YORK","NS0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","YORK-NAPIER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18,null,"WALLIS-KEILOR","ES0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","WALLIS-KEILOR (03)",0,0]
[19,null,"HUME 1445-CAMP","BMS-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","HUME 1445-CAMP (03)",0,0]
[20,null,"SOMERTON PARK-LEADER","ST0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","SOMERTON PARK-LEADER (02)",0,0]
[21,null,"SOMERTON PARK-LEADER","ST0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","SOMERTON PARK-LEADER (02)",0,0]
[22,null,"SOMERTON PARK-LEADER","ST0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","SOMERTON PARK-LEADER (02)",0,0]
[23,null,"INTERNATIONAL-T'PARK","AW0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","INTERNATIONAL-T'PARK (00)",0,0]
[24,null,"INTERNATIONAL-T'PARK","AW0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","INTERNATIONAL-T'PARK (00)",0,0]
[25,null,"FLORENCE-LINCOLN","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","FLORENCE-LINCOLN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26,null,"MT ALEXANDER-NAPIER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (01)",0,0]
[27,null,"GLENELG 66-MAFFRA","BD0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","GLENELG 66-MAFFRA (01)",0,0]
[28,null,"SOMERTON PARK-LEADER","ST0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","SOMERTON PARK-LEADER (00)",0,0]
[29,null,"JESICA 49-VANESSA","BD0-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","JESICA 49-VANESSA (01)",0,0]
[30,null,"FREIGHT-CUSTOM","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (01)",0,0]
[31,null,"INTERNATIONAL-T'PARK","AW0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","INTERNATIONAL-T'PARK (00)",0,0]
[32,null,"ELATA-BEVERAGE","AW0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ELATA-BEVERAGE (02)",0,0]
[33,null,"EVANS 60-BROOK","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","EVANS 60-BROOK (04)",0,0]
[34,null,"SOMERTON PARK-LEADER","ST0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","SOMERTON PARK-LEADER (01)",0,0]
[35,null,"RESERVOIR RD-P52","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","RESERVOIR RD-P52 (00)",0,0]
[36,null,"MT ALEXANDER-HOMER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MT ALEXANDER-HOMER (03)",0,0]
[37,null,"GLENELG 66-MAFFRA","BD0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","GLENELG 66-MAFFRA (02)",0,0]
[38,null,"NORTHBOURNE 146-REX","ST0-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","NORTHBOURNE 146-REX (01)",0,0]
[39,null,"ALBERT 62-OVANDO","PTN-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","ALBERT 62-OVANDO (03)",4.4620945071616617E-5,0]
[40,null,"MT ALEXANDER-HOMER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MT ALEXANDER-HOMER (03)",0,0]
[41,null,"INTERNATIONAL-T'PARK","AW0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","INTERNATIONAL-T'PARK (00)",0,0]
[42,null,"ROSEBERRY-HIGH","PTN-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","ROSEBERRY-HIGH (03)",0,0]
[43,null,"HUME-CAMPBELL","BD0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","HUME-CAMPBELL (02)",0,0]
[44,null,"MEROLA 54 -FREEMAN","BD0-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","MEROLA 54 -FREEMAN (01)",0,0]
[45,null,"JAMES-INDUSTRIAL GARDENS","TH0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","JAMES-INDUSTRIAL GARDENS (02)",0,0]
[46,null,"GOULBURN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","GOULBURN-PALMERSTON (04)",4.4620945071616617E-5,0]
[47,null,"STEWART-PASCOE VALE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","STEWART-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[48,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,0]
[49,null,"SEVERN-BENBOW","FE0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","SEVERN-BENBOW (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[50,null,"ST HELLIER-UP HEIDELBERG","NH0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","ST HELLIER-UP HEIDELBERG (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[51,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[52,null,"FORRESTER-HEDDERWICK","ES0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FORRESTER-HEDDERWICK (03)",4.4620945071616617E-5,0]
[53,null,"BEATRICE-JENSEN","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BEATRICE-JENSEN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[54,null,"MCKENNA-MILITARY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","MCKENNA-MILITARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[55,null,"BICENTENNIAL-SHABA","BD0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","BICENTENNIAL-SHABA (04)",0,0]
[56,null,"MCGREGOR-PERRY","FF0-083","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","MCGREGOR-PERRY (01)",4.4620945071616617E-5,0]
[57,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[58,null,"MYRTLE-REGENT","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","MYRTLE-REGENT (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[59,null,"THOMPSON-NORTH","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","THOMPSON-NORTH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[60,null,"FOSTERS-MIDWAY","TMA-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TMA","FOSTERS-MIDWAY (01)",4.4620945071616617E-5,0]
[61,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[62,null,"DOUGLAS-PASCOE VALE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DOUGLAS-PASCOE VALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[63,null,"ROYAL-BULLA","ES0-025","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ROYAL-BULLA (02)",4.4620945071616617E-5,0]
[64,null,"BERRY-KEILOR","ES0-026","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BERRY-KEILOR (03)",4.4620945071616617E-5,0]
[65,null,"KNIGHT-BAYVIEW","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","KNIGHT-BAYVIEW (02)",4.4620945071616617E-5,0]
[66,null,"THE BOULEVARD-GILBERT","HB0-024","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","HB0","THE BOULEVARD-GILBERT (01)",{"$f":"IF(G67=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J67=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[67,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[68,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MOUSHALL-NOLAN (02)",4.4620945071616617E-5,0]
[69,null,"WEBB-CORONATION","FW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","WEBB-CORONATION (03)",0,0]
[70,null,"GENEVA-COMO","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","GENEVA-COMO (02)",4.4620945071616617E-5,0]
[71,null,"SALISBURY-JACK","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","SALISBURY-JACK (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[72,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,0]
[73,null,"JAMES-NAIRN","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","JAMES-NAIRN (02)",4.4620945071616617E-5,0]
[74,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","ETZEL-CLYDESDALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[75,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[76,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","WATT-THE AVENUE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[77,null,"BEECROFT-ASHFORD","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","BEECROFT-ASHFORD (02)",0,0]
[78,null,"YALLAMBIE-WENDOVER","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","YALLAMBIE-WENDOVER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[79,null,"KENNEDY-CHAPMAN","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KENNEDY-CHAPMAN (01)",4.4620945071616617E-5,0]
[80,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[81,null,"MARY-ROBERTS","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MARY-ROBERTS (01)",4.4620945071616617E-5,0]
[82,null,"EAST-HARDING","FT0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","EAST-HARDING (02)",0,0]
[83,null,"DONALD-LAWSON","NS0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",0,0]
[84,null,"CHEDDAR-JINGHI","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","CHEDDAR-JINGHI (03)",4.4620945071616617E-5,0]
[85,null,"MCNAMARA-ROBERTS","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","MCNAMARA-ROBERTS (02)",4.4620945071616617E-5,0]
[86,null,"CENTRE-HOWARD","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","CENTRE-HOWARD (02)",4.4620945071616617E-5,0]
[87,null,"HOLMWOOD-SOMERVILLE","TH0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","HOLMWOOD-SOMERVILLE (00)",0,0]
[88,null,"ROSENTHAL-HUGHES","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ROSENTHAL-HUGHES (02)",4.4620945071616617E-5,0]
[89,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[90,null,"ROSELAND-IVANHOE","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",4.4620945071616617E-5,0]
[91,null,"BEETHAM-PROSPECT","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BEETHAM-PROSPECT (02)",4.4620945071616617E-5,0]
[92,null,"SHADFORTH-RALEIGH","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","SHADFORTH-RALEIGH (02)",4.4620945071616617E-5,0]
[93,null,"GLADSTONE-ASCOT VALE","NS0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (01)",0,0]
[94,null,"HILLCREST-ROYAL","SHM-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","HILLCREST-ROYAL (04)",4.4620945071616617E-5,0]
[95,null,"KALANG-PLUMPTON","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KALANG-PLUMPTON (02)",4.4620945071616617E-5,0]
[96,null,"FRASER-BOWES","AW0-001","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","FRASER-BOWES (01)",4.4620945071616617E-5,0]
[97,null,"COLLINS-WATERDALE","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","COLLINS-WATERDALE (02)",0,0]
[98,null,"BROADHURST-MCFADZEAN","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","OCONNOR-MACFADZEAN (03)",4.4620945071616617E-5,0]
[99,null,"HILTON-CHURCHILL","PV0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","PV0","HILTON-CHURCHILL (01)",0,0]
[100,null,"NUNAN-KIRBY","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","NUNAN-KIRBY (02)",4.4620945071616617E-5,0]
[101,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[102,null,"OWEN-GORDON","FE0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","OWEN-GORDON (01)",0,0]
[103,null,"PINE-MARSHALL","HB0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","PINE-MARSHALL (01)",4.4620945071616617E-5,0]
[104,null,"BREX 8-RADFORD","TT0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","BREX 8-RADFORD (01)",0,0]
[105,null,"GELLIBRAND-VICTORIA","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","GELLIBRAND-VICTORIA (03)",4.4620945071616617E-5,0]
[106,null,"MYRTLE-REGENT","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","MYRTLE-REGENT (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[107,null,"ST VIGEONS-BORRIE","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ST VIGEONS-BORRIE (01)",4.4620945071616617E-5,0]
[108,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","McGOWAN-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[109,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-NOLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[110,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[111,null,"CHARLES-NORTH","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","CHARLES-NORTH (01)",0,0]
[112,null,"RENNISON-CASTLEY","BY0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","RENNISON-CASTLEY (02)",4.4620945071616617E-5,0]
[113,null,"MOUNT-BELL","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MOUNT-BELL (01)",4.4620945071616617E-5,0]
[114,null,"HENTY-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","HENTY-GILBERT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[115,null,"ASHLEY-CENTRAL WEST NO.1","TH0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TH0","ASHLEY-CENTRAL WEST NO.1 (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[116,null,"CHARLES-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","CHARLES-EPSOM (02)",4.4620945071616617E-5,0]
[117,null,"ANDERSON-BOLINGBROKE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","ANDERSON-BOLINGBROKE (02)",4.4620945071616617E-5,0]
[118,null,"DARLING-EGLINTON","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DARLING-EGLINTON (01)",4.4620945071616617E-5,0]
[119,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","HODDLE-FLETCHER (01)",4.4620945071616617E-5,0]
[120,null,"GAP-PRESTON","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","GAP-PRESTON (02)",0,0]
[121,null,"CALLANDER CL-P2","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","CALLANDER CL-P2 (00)",0,0]
[122,null,"CHEDDAR-JINGHI","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","CHEDDAR-JINGHI (03)",4.4620945071616617E-5,0]
[123,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MARGTMARY-MURRAY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[124,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","ETZEL-CLYDESDALE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[125,null,"CHAPMAN-GRANDVIEW","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CHAPMAN-GRANDVIEW (01)",4.4620945071616617E-5,0]
[126,null,"SANDERSON-ROBERTS","TH0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TH0","SANDERSON-ROBERTS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[127,null,"DAISY-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DAISY-BUCKLEY (02)",4.4620945071616617E-5,0]
[128,null,"JOHNSON-BENAUD","BD0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","JOHNSON-BENAUD (02)",0,0]
[129,null,"BANKSIA-LIBERTY","EP0-034","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","BANKSIA-LIBERTY (02)",4.4620945071616617E-5,0]
[130,null,"EAST-THACKERAY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","EAST-THACKERAY (02)",{"$f":"IF(G131=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J131=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[131,null,"SPRATLING-HENTY","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","SPRATLING-HENTY (01)",4.4620945071616617E-5,0]
[132,null,"HOTHAM-RYDER No. 2","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HOTHAM-RYDER No. 2 (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[133,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[134,null,"RAVENSCOURT-FULHAM","FF0-083","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",0,0]
[135,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[136,null,"GOULBURN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","GOULBURN-PALMERSTON (03)",4.4620945071616617E-5,0]
[137,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[138,null,"RIGGALL-APOLLO","BD0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","RIGGALL-APOLLO (02)",0,0]
[139,null,"THORNYCROFT-LEADER","ST0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","THORNYCROFT-LEADER (00)",0,0]
[140,null,"WALKER-NEWCASTLE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WALKER-NEWCASTLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[141,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[142,null,"THE ESPLANADE-PLANTATION","YVE-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","THE ESPLANADE-PLANTATION (02)",4.4620945071616617E-5,0]
[143,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",0,0]
[144,null,"GOULBURN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","GOULBURN-PALMERSTON (04)",4.4620945071616617E-5,0]
[145,null,"GREENSBOROUGH-DRYSDALE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GREENSBOROUGH-DRYSDALE (02)",4.4620945071616617E-5,0]
[146,null,"MONZA-FLORENCE","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","MONZA-FLORENCE (01)",4.4620945071616617E-5,0]
[147,null,"CUDGEWA-BORVA","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","CUDGEWA-BORVA (01)",4.4620945071616617E-5,0]
[148,null,"LIVINGSTONE-ELIZABETH","CN0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","CN0","LIVINGSTONE-ELIZABETH (01)",0,0]
[149,null,"MARYSTON-SOMERVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","MARYSTON-SOMERVILLE (01)",4.4620945071616617E-5,0]
[150,null,"CRAWFORD-ROBINSON","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (02)",0,0]
[151,null,"SOMERVILLE-JULIAN","FW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","SOMERVILLE-JULIAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[152,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[153,null,"THE ESPLANADE-PLANTATION","YVE-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","THE ESPLANADE-PLANTATION (01)",4.4620945071616617E-5,0]
[154,null,"ELATA-BEVERAGE","AW0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ELATA-BEVERAGE (01)",0,0]
[155,null,"HENLEY-CLARKE","BD0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","HENLEY-CLARKE (02)",0,0]
[156,null,"SUSSEX-BANYULE","HB0-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","HB0","SUSSEX-BANYULE (02)",0,0]
[157,null,"FINN-HAUGHTON","HB0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","FINN-HAUGHTON (01)",4.4620945071616617E-5,0]
[158,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-NOLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[159,null,"JOHNSTON-NEWCASTLE","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","JOHNSTON-NEWCASTLE (02)",4.4620945071616617E-5,0]
[160,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[161,null,"BROWNING-GAMON","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","BROWNING-GAMON (03)",0,0]
[162,null,"PUNJEL-CALDER","SHM-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","PUNJEL-CALDER (00)",0,0]
[163,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[164,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-NOLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[165,null,"ST KINNORD-ALMA","ES0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","ST KINNORD-ALMA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[166,null,"DAVID-RACHELLE","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","DAVID-RACHELLE (01)",4.4620945071616617E-5,0]
[167,null,"BRADFORD-KIRBY","COO-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","COO","BRADFORD-KIRBY (02)",0,0]
[168,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MOUSHALL-NOLAN (01)",4.4620945071616617E-5,0]
[169,null,"HANSEN-GLAMIS","FW0-008","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","FW0","HANSEN-GLAMIS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[170,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","STEELE-STUART (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[171,null,"NIMMO-BUCKLEY","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BUCKLEY-PRICE (02)",4.4620945071616617E-5,0]
[172,null,"MARIE-MURPHY","PV0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","MARIE-MURPHY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[173,null,"WEST-JOHN","PV0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","WEST-JOHN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[174,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[175,null,"GELLIBRAND-VICTORIA","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","GELLIBRAND-VICTORIA (01)",4.4620945071616617E-5,0]
[176,null,"EDWIN-GILLIES","FF0-087","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","EDWIN-GILLIES (03)",4.4620945071616617E-5,0]
[177,null,"CAPRICORN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","CAPRICORN-PALMERSTON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[178,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[179,null,"RUTHVEN-WAIORA","NH0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","RUTHVEN-WAIORA (04)",4.4620945071616617E-5,0]
[180,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[181,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (03)",4.4620945071616617E-5,0]
[182,null,"KATHLEEN-WOOD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","KATHLEEN-WOOD (01)",4.4620945071616617E-5,0]
[183,null,"FINN-HAUGHTON","HB0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","FINN-HAUGHTON (01)",4.4620945071616617E-5,0]
[184,null,"PLUNKETT-O'KEEFE","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","PLUNKETT-O'KEEFE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[185,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",0,0]
[186,null,"FERGUSON-ROSEBERRY","ES0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","FERGUSON-ROSEBERRY (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[187,null,"ALTONA-ORIEL","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","ALTONA-ORIEL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[188,null,"LAUREL-TYLER","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","LAUREL-TYLER (01)",4.4620945071616617E-5,0]
[189,null,"MYRTLE-REGENT","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","MYRTLE-REGENT (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[190,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","HODDLE-FLETCHER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[191,null,"HIGH 883-MELB WATER","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HIGH 883-MELB WATER (01)",4.4620945071616617E-5,0]
[192,null,"SYDNEY-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SYDNEY-MURRAY (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[193,null,"WILLOWTREE-PERSICA","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (04)",0,0]
[194,null,"PEARL-WHEATSHEAF","PV0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","PEARL-WHEATSHEAF (02)",{"$f":"IF(G195=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J195=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[195,null,"BELGROVE-OVANDO","PTN-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","BELGROVE-OVANDO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[196,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[197,null,"LOCKSLEY-MALTRAVERS","HB0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","LOCKSLEY-MALTRAVERS (02)",4.4620945071616617E-5,0]
[198,null,"FENTON-MYRNONG","FT0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","FENTON-MYRNONG (03)",0,0]
[199,null,"RIVER-HOME","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","RIVER-HOME (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[200,null,"GLENSIDE-CANNING","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","GLENSIDE-CANNING (01)",4.4620945071616617E-5,0]
[201,null,"BAILEY-HOPETOUN","HB0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","HB0","BAILEY-HOPETOUN (02)",0,0]
[202,null,"SOUDAN-HIGH","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SOUDAN-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[203,null,"MARY-NIMMO","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MARY-NIMMO (02)",4.4620945071616617E-5,0]
[204,null,"OWEN-GORDON","FE0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","OWEN-GORDON (01)",0,0]
[205,null,"GENEVA-COMO","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","GENEVA-COMO (02)",4.4620945071616617E-5,0]
[206,null,"RENNIE-JOHN","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","RENNIE-JOHN (01)",4.4620945071616617E-5,0]
[207,null,"HOBBS-PENTLAND","FE0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",0,0]
[208,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,0]
[209,null,"FERGUSON-ROSEBERRY","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FERGUSON-ROSEBERRY (04)",4.4620945071616617E-5,0]
[210,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[211,null,"BIRDWOOD-REGENT","CN0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BIRDWOOD-REGENT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[212,null,"HILTON-WEST","PV0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-WEST (02)",4.4620945071616617E-5,0]
[213,null,"SECOND-EVE","ST0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ST0","SECOND-EVE (01)",4.4620945071616617E-5,0]
[214,null,"STATION-HAMILTON","FE0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","STATION-HAMILTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[215,null,"NEWMAN-HOTHAM","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NEWMAN-HOTHAM (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[216,null,"ATHOL-EDGAR","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ATHOL-EDGAR (02)",4.4620945071616617E-5,0]
[217,null,"INVERMAY-MT IDA","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","INVERMAY-MT IDA (02)",4.4620945071616617E-5,0]
[218,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[219,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[220,null,"GOULBURN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","GOULBURN-PALMERSTON (04)",4.4620945071616617E-5,0]
[221,null,"FORRESTER-DEAKIN","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","FORRESTER-DEAKIN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[222,null,"ELATA-BEVERAGE","AW0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ELATA-BEVERAGE (01)",0,0]
[223,null,"BEATTY-MELBOURNE","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","BEATTY-MELBOURNE (03)",4.4620945071616617E-5,0]
[224,null,"RUTHVEN-WAIORA","NH0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","RUTHVEN-WAIORA (04)",4.4620945071616617E-5,0]
[225,null,"CLYDEBANK-AFTON","ES0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","CLYDEBANK-AFTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[226,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[227,null,"HAMPDEN-CROTHERS","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",0,0]
[228,null,"NEWMAN-HOTHAM","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NEWMAN-HOTHAM (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[229,null,"OWEN-GORDON","FE0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","OWEN-GORDON (01)",0,0]
[230,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","NT0","CHALLIS-JUBILLEE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[231,null,"PERRY-VERDON","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","PERRY-VERDON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[232,null,"BOND-ATHELSTANE","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","BOND-ATHELSTANE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[233,null,"JOHN-WINIFRED","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","JOHN-WINIFRED (02)",4.4620945071616617E-5,0]
[234,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[235,null,"BULLA-DUBLIN","ES0-025","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BULLA-DUBLIN (02)",4.4620945071616617E-5,0]
[236,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[237,null,"GREENSBOROUGH-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","NH0","GREENSBOROUGH-YALLAMBIE (01)",0,0]
[238,null,"ARTHUR-FAWKNER","ES0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","ARTHUR-FAWKNER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[239,null,"ANGLISS-SANDERSON","TH0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TH0","ANGLISS-SANDERSON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[240,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","YALLAMBIE-LOWER PLENTY (01)",4.4620945071616617E-5,0]
[241,null,"BRAIDHILL-WINDSOR","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BRAIDHILL-WINDSOR (02)",4.4620945071616617E-5,0]
[242,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[243,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","ETZEL-CLYDESDALE (02)",4.4620945071616617E-5,0]
[244,null,"BURKE-FLINDERS","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (03)",0,0]
[245,null,"SEPARATION-FULHAM","FF0-093","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","SEPARATION-FULHAM (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[246,null,"DOUGLAS-PASCOE VALE","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","DOUGLAS-PASCOE VALE (01)",4.4620945071616617E-5,0]
[247,null,"LAUREL-TYLER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","LAUREL-TYLER (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[248,null,"HUTCHESON-THE STRAND","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",0,0]
[249,null,"RAILWAY-RYE","BD0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","RAILWAY-RYE (02)",0,0]
[250,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[251,null,"ESSEX-SWAN","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","ESSEX-SWAN (01)",0,0]
[252,null,"CAPRICORN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","CAPRICORN-PALMERSTON (03)",4.4620945071616617E-5,0]
[253,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,0]
[254,null,"LOCH-REYNARDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LOCH-REYNARDS (02)",4.4620945071616617E-5,0]
[255,null,"WESTMERE-WARNE","BD0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BD0","WESTMERE-WARNE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[256,null,"GRAHAM-GLEN ALLAN","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","GRAHAM-GLEN ALLAN (03)",0,0]
[257,null,"MYDDLETON-GRACE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","MYDDLETON-GRACE (01)",4.4620945071616617E-5,0]
[258,null,"DERMOT-CORMAC","PTN-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","DERMOT-CORMAC (02)",{"$f":"IF(G259=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J259=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[259,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (01)",0,0]
[260,null,"MOROBE-ALAMEIN","EPN-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","MOROBE-ALAMEIN (03)",0,0]
[261,null,"BRADSHAW-MARY","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BRADSHAW-MARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[262,null,"FLETCHER-PASCOE VALE","NS0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","FLETCHER-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[263,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[264,null,"HIGGINS-RUTHVEN","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","HIGGINS-RUTHVEN (01)",0,0]
[265,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","McGOWAN-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[266,null,"SHADFORTH-RALEIGH","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","SHADFORTH-RALEIGH (01)",4.4620945071616617E-5,0]
[267,null,"ELLESMERE-INVERMAY","NH0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","ELLESMERE-INVERMAY (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[268,null,"VICTORIA-RAILWAY","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","VICTORIA-RAILWAY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[269,null,"SOUTHEY-ARDEN","FT0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (02)",0,0]
[270,null,"MURRAY-PASCOE VALE","NS0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","MURRAY-PASCOE VALE (04)",4.4620945071616617E-5,0]
[271,null,"NOTTINGHAM-RACECOURSE","FT0-031","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","NOTTINGHAM-RACECOURSE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[272,null,"BLACKSHAWS-ELIZABETH","YVE-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","YVE","BLACKSHAWS-ELIZABETH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[273,null,"INVERMAY-MT IDA","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","INVERMAY-MT IDA (04)",4.4620945071616617E-5,0]
[274,null,"ESSEX-SWAN","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","ESSEX-SWAN (01)",0,0]
[275,null,"TIERNAN-RAGLAN","EP0-037","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","TIERNAN-RAGLAN (01)",4.4620945071616617E-5,0]
[276,null,"RESERVE-DUNDAS","EP0-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","RESERVE-DUNDAS (01)",0,0]
[277,null,"MACK-PICKETT","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","MACK-PICKETT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[278,null,"ROKEWOOD-ELLAM","BD0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","ROKEWOOD-ELLAM (02)",0,0]
[279,null,"WALLIS-KEILOR","ES0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","WALLIS-KEILOR (01)",0,0]
[280,null,"CAPRICORN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","CAPRICORN-PALMERSTON (03)",4.4620945071616617E-5,0]
[281,null,"HILLCREST-ROYAL","SHM-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","HILLCREST-ROYAL (04)",4.4620945071616617E-5,0]
[282,null,"TONKIN-SUSSEX","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","TONKIN-SUSSEX (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[283,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","WATT-THE AVENUE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[284,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MALCOLM-ELIZABETH (02)",4.4620945071616617E-5,0]
[285,null,"DEAKIN-MARY","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DEAKIN-MARY (02)",4.4620945071616617E-5,0]
[286,null,"FERGUSON-TOWNHALL","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","FERGUSON-TOWNHALL (01)",4.4620945071616617E-5,0]
[287,null,"DEAKIN-BUCKLEY","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DEAKIN-BUCKLEY (01)",4.4620945071616617E-5,0]
[288,null,"ALAMEDA-HILLSIDE","YVE-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","ALAMEDA-HILLSIDE (02)",4.4620945071616617E-5,0]
[289,null,"GILBANK-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","GILBANK-GILBERT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[290,null,"ASHLEY-NAPOLEON","TH0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TH0","ASHLEY-NAPOLEON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[291,null,"FERNHILL-BARODA","FT0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","FERNHILL-BARODA (01)",0,0]
[292,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[293,null,"ANSTEY-PHILLIP","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ANSTEY-PHILLIP (02)",4.4620945071616617E-5,0]
[294,null,"THISTLE-MT ALEXANDER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (01)",0,0]
[295,null,"PATTERSON-DAVID","PTN-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","NICHOL-GOWER (01)",4.4620945071616617E-5,0]
[296,null,"SOMERS-HINKLER","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","SOMERS-HINKLER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[297,null,"MOONEE-VALLEY","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MOONEE-VALLEY (02)",4.4620945071616617E-5,0]
[298,null,"ADELINE-KOROROIT","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","ADELINE-KOROROIT (02)",4.4620945071616617E-5,0]
[299,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[300,null,"FERGUSON-ROSEBERRY","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FERGUSON-ROSEBERRY (04)",4.4620945071616617E-5,0]
[301,null,"PASLEY-NEILL","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","PASLEY-NEILL (02)",0,0]
[302,null,"SUSSEX-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","SUSSEX-HOLMES (02)",4.4620945071616617E-5,0]
[303,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,0]
[304,null,"RAGLAN-RESERVE","EP0-028","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","RAGLAN-RESERVE (01)",0,0]
[305,null,"MCIVOR-OAKHILL","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MCIVOR-OAKHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[306,null,"BROADHURST-MCFADZEAN","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","OCONNOR-MACFADZEAN (02)",4.4620945071616617E-5,0]
[307,null,"KILMORE-CHARLTON","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","KILMORE-CHARLTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[308,null,"HUTCHESON-THE STRAND","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",0,0]
[309,null,"FINLAYSON-BRAIDHILL","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","FINLAYSON-BRAIDHILL (03)",4.4620945071616617E-5,0]
[310,null,"TUCKER-LYNCH","CN0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","TUCKER-LYNCH (02)",4.4620945071616617E-5,0]
[311,null,"CENTRE-HOWARD","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CENTRE-HOWARD (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[312,null,"NAPOLEON-BRUNSWICK","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","NAPOLEON-BRUNSWICK (04)",4.4620945071616617E-5,0]
[313,null,"JACKA-MCCRACKEN","ES0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","JACKA-MCCRACKEN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[314,null,"TAYLOR-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",0,0]
[315,null,"LOWER PLENTY-MOUNTVIEW","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","LOWER PLENTY-MOUNTVIEW (01)",4.4620945071616617E-5,0]
[316,null,"MADDEN-STUDLEY","FW0-017","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","MADDEN-STUDLEY (02)",0,0]
[317,null,"MARKS-YORK","NS0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","MARKS-YORK (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[318,null,"FEHON-SOMERVILLE","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","FEHON-SOMERVILLE (01)",0,0]
[319,null,"DAVERN-O'HEA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DAVERN-O'HEA (01)",4.4620945071616617E-5,0]
[320,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,0]
[321,null,"CHAPMAN-BELAIR","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CHAPMAN-BELAIR (02)",4.4620945071616617E-5,0]
[322,null,"LARGS-MOTHERWELL","COO-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","LARGS-MOTHERWELL (01)",{"$f":"IF(G323=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J323=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[323,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","STEELE-STUART (03)",4.4620945071616617E-5,0]
[324,null,"RAVENSCOURT-FULHAM","FF0-083","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",0,0]
[325,null,"HILTON-CHURCHILL","PV0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","PV0","HILTON-CHURCHILL (01)",0,0]
[326,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MALCOLM-ELIZABETH (02)",4.4620945071616617E-5,0]
[327,null,"EVERARD-MAY","PV0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","EVERARD-MAY (02)",4.4620945071616617E-5,0]
[328,null,"CHARTERIS-WARNCLIFFE","HB0-024","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","HB0","CHARTERIS-WARNCLIFFE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[329,null,"BRASSEY CRT-P5E2","COO-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","COO","BRASSEY CRT-P5E2 (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[330,null,"CORNWALL-HIGH SCHOOL","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[331,null,"WOOD-GREENBELT","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","WOOD-GREENBELT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[332,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[333,null,"WILLIAM-MASON","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WILLIAM-MASON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[334,null,"DUNDEE-MEADE","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","DUNDEE-MEADE (03)",4.4620945071616617E-5,0]
[335,null,"MIRAMS-UNION","FT0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","MIRAMS-UNION (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[336,null,"ESSEX-SWAN","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","ESSEX-SWAN (01)",0,0]
[337,null,"BUCKLEY-THE CROSSWAY","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","BUCKLEY-THE CROSSWAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[338,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MARGTMARY-MURRAY (03)",4.4620945071616617E-5,0]
[339,null,"ARDEN-LOWER PLENTY","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","ARDEN-LOWER PLENTY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[340,null,"WAVERLEY-HOLMES","ES0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","WAVERLEY-HOLMES (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[341,null,"DORRINGTON-PLENTY","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DORRINGTON-PLENTY (02)",4.4620945071616617E-5,0]
[342,null,"BURKE-FLINDERS","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (02)",0,0]
[343,null,"HANSEN-GLAMIS","FW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","HANSEN-GLAMIS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[344,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[345,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WALHALLA-MORELAND (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[346,null,"BRUCE-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BRUCE-REYNARD (02)",4.4620945071616617E-5,0]
[347,null,"DEAKIN-SPENCER","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DEAKIN-SPENCER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[348,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",0,0]
[349,null,"TONKIN-SUSSEX","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","TONKIN-SUSSEX (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[350,null,"TURNER-EVANS","NS0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",0,0]
[351,null,"BEVERLEY-GREVILLE","HB0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","BEVERLEY-GREVILLE (01)",4.4620945071616617E-5,0]
[352,null,"LAUREL-TYLER","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","LAUREL-TYLER (01)",4.4620945071616617E-5,0]
[353,null,"MOUNT-BELL","CS0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MOUNT-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[354,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[355,null,"FINN-HAUGHTON","HB0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","FINN-HAUGHTON (03)",4.4620945071616617E-5,0]
[356,null,"RUSSELL-BARKLY","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","RUSSELL-BARKLY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[357,null,"NEWSOM-STANFORD","ES0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","NEWSOM-STANFORD (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[358,null,"LEWIS-WILLIAMS","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",4.4620945071616617E-5,0]
[359,null,"LEAKE-RICHARDSON","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","LEAKE-RICHARDSON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[360,null,"SNELL-WATT","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","SNELL-WATT (02)",4.4620945071616617E-5,0]
[361,null,"EIRENE-FRANCIS","FW0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","EIRENE-FRANCIS (02)",4.4620945071616617E-5,0]
[362,null,"CORNWALL-HIGH SCHOOL","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[363,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[364,null,"ANTHONY-BELLAIR","FT0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","ANTHONY-BELLAIR (01)",4.4620945071616617E-5,0]
[365,null,"ST HELLIER-UP HEIDELBERG","NH0-017","2025-02-02","2025-02-08","N","Y","N","N","N","N","NH0","ST HELLIER-UP HEIDELBERG (01)",0,0]
[366,null,"ERINBANK-DOBIES","BD0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","ERINBANK-DOBIES (02)",0,0]
[367,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WILLOW-LINDA (02)",4.4620945071616617E-5,0]
[368,null,"RICHELIEU-ESSEX","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","RICHELIEU-ESSEX (02)",4.4620945071616617E-5,0]
[369,null,"BIMBADEEN-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[370,null,"THE GRANGE-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","THE GRANGE-YALLAMBIE (03)",4.4620945071616617E-5,0]
[371,null,"MITCHELL-OAKOVER","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-OAKOVER (01)",4.4620945071616617E-5,0]
[372,null,"ARTHUR-ELIZABETH","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ARTHUR-ELIZABETH (01)",4.4620945071616617E-5,0]
[373,null,"JACK-FORD","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","JACK-FORD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[374,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[375,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[376,null,"CHARTERIS-BURKE","HB0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","CHARTERIS-BURKE (01)",4.4620945071616617E-5,0]
[377,null,"CRAMER-GILBERT","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CRAMER-GILBERT (02)",4.4620945071616617E-5,0]
[378,null,"KONAGADERRA RD-P43","COO-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","KONAGADERRA RD-P43 (00)",4.4620945071616617E-5,0]
[379,null,"SEVERN-SOMERVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","SEVERN-SOMERVILLE (03)",4.4620945071616617E-5,0]
[380,null,"ASH-WIDFORD","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","ASH-WIDFORD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[381,null,"JELLICOE-OSNEY","EP0-034","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","JELLICOE-OSNEY (02)",4.4620945071616617E-5,0]
[382,null,"CLIFTON-WATERDALE","HB0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","CLIFTON-WATERDALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[383,null,"MIDDLE-ASCOT VALE","FT0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","MIDDLE-ASCOT VALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[384,null,"CUMBERLAND-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CUMBERLAND-KENT (04)",4.4620945071616617E-5,0]
[385,null,"NORTH-THOMAS","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NORTH-THOMAS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[386,null,"CARWARP-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CARWARP-ERSKINE (02)",{"$f":"IF(G387=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J387=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[387,null,"SEVERN-BENBOW","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",0,0]
[388,null,"SUSSEX-BANYULE","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","SUSSEX-BANYULE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[389,null,"RALEIGH-HODDLE","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",0,0]
[390,null,"SOUTH-BELL","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",0,0]
[391,null,"BRADSHAW-MARY","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BRADSHAW-MARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[392,null,"ELDORADO-STRELDON","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","ELDORADO-STRELDON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[393,null,"FERGUSON-ROSEBERRY","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FERGUSON-ROSEBERRY (04)",4.4620945071616617E-5,0]
[394,null,"GILBANK-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","GILBANK-GILBERT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[395,null,"BEETHAM-PROSPECT","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BEETHAM-PROSPECT (02)",4.4620945071616617E-5,0]
[396,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",4.4620945071616617E-5,0]
[397,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[398,null,"PURINUAN-NUTWOOD","TT0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (01)",0,0]
[399,null,"JACKSON-THOMSON","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","JACKSON-THOMSON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[400,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[401,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[402,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[403,null,"PETERSON-JACKSON","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","PETERSON-JACKSON (01)",4.4620945071616617E-5,0]
[404,null,"BERRY-KEILOR","ES0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BERRY-KEILOR (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[405,null,"BRADSHAW-MARY","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BRADSHAW-MARY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[406,null,"DAISY-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DAISY-BUCKLEY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[407,null,"STEPHEN-PRINCESS","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (02)",0,0]
[408,null,"INTERVALE-ARCADE","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","INTERVALE-ARCADE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[409,null,"HENDERSON-WILSON","TT0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","HENDERSON-WILSON (02)",0,0]
[410,null,"TURNER-EVANS","NS0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",0,0]
[411,null,"RICHELIEU-JACKSON","FW0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","RICHELIEU-JACKSON (02)",4.4620945071616617E-5,0]
[412,null,"HILLSYDE-LOEMAN","NS0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","HILLSYDE-LOEMAN (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[413,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","CS0","PORTLAND-MUNRO (01)",0,0]
[414,null,"WOODLAND-NAPIER","NS0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","WOODLAND-NAPIER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[415,null,"PEARL-WHEATSHEAF","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","PEARL-WHEATSHEAF (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[416,null,"QUINN-NOGA","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","QUINN-NOGA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[417,null,"SOUTHEY-ARDEN","FT0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",0,0]
[418,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[419,null,"TOWER-HEIDELBERG","FF0-088","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","TOWER-HEIDELBERG (01)",4.4620945071616617E-5,0]
[420,null,"TONKIN-SUSSEX","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","TONKIN-SUSSEX (02)",4.4620945071616617E-5,0]
[421,null,"GRAVES-MARKET","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","GRAVES-MARKET (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[422,null,"HUTCHESON-THE STRAND","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",0,0]
[423,null,"FLORENCE-LINCOLN","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FLORENCE-LINCOLN (02)",4.4620945071616617E-5,0]
[424,null,"LOCKSLEY-MALTRAVERS","HB0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","LOCKSLEY-MALTRAVERS (02)",4.4620945071616617E-5,0]
[425,null,"NIMMO-BUCKLEY","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BUCKLEY-PRICE (01)",4.4620945071616617E-5,0]
[426,null,"ROSS-ELIZABETH","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","ROSS-ELIZABETH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[427,null,"HEATHCOTE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HEATHCOTE-KENT (01)",4.4620945071616617E-5,0]
[428,null,"GENEVA-COMO","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","GENEVA-COMO (02)",4.4620945071616617E-5,0]
[429,null,"WILLIAM-MASON","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WILLIAM-MASON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[430,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","HODDLE-FLETCHER (01)",4.4620945071616617E-5,0]
[431,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",0,0]
[432,null,"DOLE-LOCHER","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","DOLE-LOCHER (03)",4.4620945071616617E-5,0]
[433,null,"ANSTEY-PHILLIP","TT0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ANSTEY-PHILLIP (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[434,null,"THISTLE-MT ALEXANDER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (01)",0,0]
[435,null,"HOOD-MCBRYDE","CN0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HOOD-MCBRYDE (02)",4.4620945071616617E-5,0]
[436,null,"SOUTH-BELL","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",0,0]
[437,null,"ARGYLE-BROAD","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ARGYLE-BROAD (01)",4.4620945071616617E-5,0]
[438,null,"ANGLISS-SANDERSON","TH0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TH0","ANGLISS-SANDERSON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[439,null,"MONASH-BONAR","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MONASH-BONAR (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[440,null,"TROVATELLO-NOLANS","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","TROVATELLO-NOLANS (01)",0,0]
[441,null,"WALLACE-KENILWORTH","FF0-090","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",0,0]
[442,null,"WAIORA-CHURCHILL","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","WAIORA-CHURCHILL (01)",4.4620945071616617E-5,0]
[443,null,"DELAWARE-MENDIP","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","DELAWARE-MENDIP (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[444,null,"HYDE 258-KENT","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","HYDE 258-KENT (02)",0,0]
[445,null,"JUSTIN-VIEW","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","JUSTIN-VIEW (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[446,null,"HILBERT-HARRINGTON","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILBERT-HARRINGTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[447,null,"BRADSHAW-MARYBOROUGH","TT0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","BRADSHAW-MARYBOROUGH (02)",0,0]
[448,null,"ARBOR-MACEY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","ARBOR-MACEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[449,null,"SUSSEX-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","SUSSEX-HOLMES (02)",4.4620945071616617E-5,0]
[450,null,"SNELL-WATT","PV0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SNELL-WATT (02)",{"$f":"IF(G451=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J451=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[451,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (01)",0,0]
[452,null,"ALBION-GEELONG","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ALBION-GEELONG (01)",4.4620945071616617E-5,0]
[453,null,"SUSSEX-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","SUSSEX-HOLMES (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[454,null,"CAPRICORN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","CAPRICORN-PALMERSTON (03)",4.4620945071616617E-5,0]
[455,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,0]
[456,null,"SALTAU-MILLEARA","AW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","SALTAU-MILLEARA (02)",0,0]
[457,null,"WILLOWTREE-PERSICA","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (01)",0,0]
[458,null,"BOND-LIBERTY","EP0-034","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","EP0","FORD-SPARKFORD (01)",4.4620945071616617E-5,0]
[459,null,"AMEILY-LEAMINGTON","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","AMEILY-LEAMINGTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[460,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[461,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","McGOWAN-MURRAY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[462,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",0,0]
[463,null,"DORSET-DERBY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DORSET-DERBY (02)",4.4620945071616617E-5,0]
[464,null,"ARTHUR-ELIZABETH","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ARTHUR-ELIZABETH (01)",4.4620945071616617E-5,0]
[465,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[466,null,"THE ESPLANADE-PLANTATION","YVE-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","THE ESPLANADE-PLANTATION (01)",4.4620945071616617E-5,0]
[467,null,"YARRALEA-GIBSON","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","YARRALEA-GIBSON (01)",4.4620945071616617E-5,0]
[468,null,"PEEL-DOUGLAS","NT0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","PEEL-DOUGLAS (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[469,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[470,null,"VISION-MASCOMA","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","VISION-MASCOMA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[471,null,"CRESSWELL-CAMERON","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","CRESSWELL-CAMERON (02)",0,0]
[472,null,"ALEXANDRA-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ALEXANDRA-LANDELLS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[473,null,"ATTERCLIFFE-DERBY","CS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","ATTERCLIFFE-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[474,null,"HOME-WILKINSON","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","HOME-WILKINSON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[475,null,"ARGYLE-BROAD","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ARGYLE-BROAD (01)",4.4620945071616617E-5,0]
[476,null,"BRADMAN-CHAPPEL","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BRADMAN-CHAPPEL (02)",0,0]
[477,null,"ST LEONARDS-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ST LEONARDS-EPSOM (03)",4.4620945071616617E-5,0]
[478,null,"LOCKSLEY-MALTRAVERS","HB0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","LOCKSLEY-MALTRAVERS (02)",4.4620945071616617E-5,0]
[479,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[480,null,"GELLIBRAND-VICTORIA","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","GELLIBRAND-VICTORIA (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[481,null,"COHEN-GROVES","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","COHEN-GROVES (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[482,null,"GARNET-IDA","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GARNET-IDA (02)",4.4620945071616617E-5,0]
[483,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[484,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[485,null,"CORNISH-LIGAR","SBY-012","2025-02-02","2025-02-08","N","N","N","Y","N","N","SBY","CORNISH-LIGAR (01)",0,9.4304036212749905E-5]
[486,null,"COUANGALT RD-P19","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","COUANGALT RD-P19 (00)",0,0]
[487,null,"PARKVIEW-HEIDELBERG","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","PARKVIEW-HEIDELBERG (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[488,null,"PASLEY-NEILL","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","PASLEY-NEILL (02)",0,0]
[489,null,"CRESWICK-LATROBE","FE0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","CRESWICK-LATROBE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[490,null,"CANTALA-MCCRAE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","CANTALA-MCCRAE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[491,null,"ATHELSTANE-ROBBINS","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","ATHELSTANE-ROBBINS (02)",4.4620945071616617E-5,0]
[492,null,"DORSET-BERKELEY","HB0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","DORSET-BERKELEY (02)",4.4620945071616617E-5,0]
[493,null,"SYLVESTER-GORDON","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","SYLVESTER-GORDON (02)",4.4620945071616617E-5,0]
[494,null,"WHITE-DUKE","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","WHITE-DUKE (02)",4.4620945071616617E-5,0]
[495,null,"BOLDREWOOD-McMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","BOLDREWOOD-McMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[496,null,"DARLING-FULHAM","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","DARLING-FULHAM (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[497,null,"CHANDOS-BREADALBANE","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","CHANDOS-BREADALBANE (02)",4.4620945071616617E-5,0]
[498,null,"CAPRICORN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","CAPRICORN-PALMERSTON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[499,null,"HILLSIDE-HURTLE","ES0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","HILLSIDE-HURTLE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[500,null,"FIRST-BARKLY","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","FIRST-BARKLY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[501,null,"FREIGHT-CUSTOM","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (01)",0,0]
[502,null,"COBRAM-LILLIPUT","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","COBRAM-LILLIPUT (02)",4.4620945071616617E-5,0]
[503,null,"ANSTEY-PHILLIP","TT0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ANSTEY-PHILLIP (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[504,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[505,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[506,null,"RICHELIEU-JACKSON","FW0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","RICHELIEU-JACKSON (02)",4.4620945071616617E-5,0]
[507,null,"WEBB-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-QUEENSVILLE (04)",4.4620945071616617E-5,0]
[508,null,"CAMBRIAN-HIGH","PTN-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","CAMBRIAN-HIGH (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[509,null,"EFFINGHAM-WILKINS","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","EFFINGHAM-WILKINS (01)",4.4620945071616617E-5,0]
[510,null,"STUART-ORMOND","FT0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","STUART-ORMOND (01)",4.4620945071616617E-5,0]
[511,null,"INVERMAY-MT IDA","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","INVERMAY-MT IDA (04)",4.4620945071616617E-5,0]
[512,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","WATT-THE AVENUE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[513,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[514,null,"BLOOMFIELD-ROSAMOND","YVE-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","BLOOMFIELD-ROSAMOND (01)",{"$f":"IF(G515=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J515=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[515,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[516,null,"CUMBERLAND-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CUMBERLAND-KENT (01)",4.4620945071616617E-5,0]
[517,null,"KATHLEEN-WOOD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","KATHLEEN-WOOD (02)",4.4620945071616617E-5,0]
[518,null,"WILLIAM-MASON","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WILLIAM-MASON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[519,null,"HILLSIDE-HURTLE","ES0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","HILLSIDE-HURTLE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[520,null,"ASHLEY-EDWARDES","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ASHLEY-EDWARDES (01)",4.4620945071616617E-5,0]
[521,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[522,null,"HART-BOWES","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","HART-BOWES (03)",4.4620945071616617E-5,0]
[523,null,"COURTIS-MELBOURNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","COURTIS-MELBOURNE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[524,null,"NEWMAN-HOTHAM","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NEWMAN-HOTHAM (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[525,null,"HANSEN-GLAMIS","FW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","HANSEN-GLAMIS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[526,null,"QUINN-CLARKS","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","QUINN-CLARKS (01)",4.4620945071616617E-5,0]
[527,null,"THE GRANGE-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","THE GRANGE-YALLAMBIE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[528,null,"DELAWARE-MENDIP","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","DELAWARE-MENDIP (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[529,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[530,null,"EFFINGHAM-WILKINS","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","EFFINGHAM-WILKINS (01)",4.4620945071616617E-5,0]
[531,null,"SEPARATION-SHIERS","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","SEPARATION-SHIERS (01)",4.4620945071616617E-5,0]
[532,null,"BREX 8-RADFORD","TT0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","BREX 8-RADFORD (02)",0,0]
[533,null,"ERIC-ADA","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","McGOWAN-MURRAY (03)",4.4620945071616617E-5,0]
[534,null,"WEBB-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-QUEENSVILLE (02)",4.4620945071616617E-5,0]
[535,null,"MIRAMS-UNION","FT0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","MIRAMS-UNION (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[536,null,"DOYLE-NORTH","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","DOYLE-NORTH (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[537,null,"RICHELIEU-ESSEX","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","RICHELIEU-ESSEX (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[538,null,"LEBANON-FENACRE","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","LEBANON-FENACRE (03)",4.4620945071616617E-5,0]
[539,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HODDLE-FLETCHER (01)",0,0]
[540,null,"FOSTERS-MIDWAY","TMA-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TMA","FOSTERS-MIDWAY (01)",4.4620945071616617E-5,0]
[541,null,"FARM-HOME","NT0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","FARM-HOME (01)",4.4620945071616617E-5,0]
[542,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","ETZEL-CLYDESDALE (01)",4.4620945071616617E-5,0]
[543,null,"HILTON-WIDFORD","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-WIDFORD (02)",4.4620945071616617E-5,0]
[544,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,0]
[545,null,"TAYLOR-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",0,0]
[546,null,"CLIFTON-WATERDALE","HB0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","CLIFTON-WATERDALE (02)",4.4620945071616617E-5,0]
[547,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[548,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,0]
[549,null,"SEVERN-SOMERVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","SEVERN-SOMERVILLE (03)",4.4620945071616617E-5,0]
[550,null,"CLUNES-MIRBOO","BD0-010","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","CLUNES-MIRBOO (01)",0,0]
[551,null,"JOHN-WINIFRED","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","JOHN-WINIFRED (02)",4.4620945071616617E-5,0]
[552,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[553,null,"HUTCHESON-THE STRAND","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (03)",0,0]
[554,null,"GARNET-EMERALD","ES0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GARNET-EMERALD (02)",4.4620945071616617E-5,0]
[555,null,"RUDSTONE-ABBEY","COO-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","RUDSTONE-ABBEY (01)",4.4620945071616617E-5,0]
[556,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[557,null,"LYDIA-DUNSTAN","BD0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BD0","LYDIA-DUNSTAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[558,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[559,null,"DAISY-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DAISY-BUCKLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[560,null,"WEBB-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-QUEENSVILLE (02)",4.4620945071616617E-5,0]
[561,null,"CAPRICORN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","CAPRICORN-PALMERSTON (03)",4.4620945071616617E-5,0]
[562,null,"SOUTH-BELL","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",0,0]
[563,null,"FORRESTER-COOPER","ES0-025","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FORRESTER-COOPER (01)",4.4620945071616617E-5,0]
[564,null,"MANUKA-LIGHTWOOD","BD0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","MANUKA-LIGHTWOOD (02)",0,0]
[565,null,"DENYS-GLYNDA","CN0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DENYS-GLYNDA (02)",4.4620945071616617E-5,0]
[566,null,"PROSPECT-PASCOE VALE","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","PROSPECT-PASCOE VALE (01)",4.4620945071616617E-5,0]
[567,null,"NOVIAN-MARAMA","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","NOVIAN-MARAMA (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[568,null,"THE GRANGE-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","THE GRANGE-YALLAMBIE (03)",4.4620945071616617E-5,0]
[569,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GLENMORE-KINLOCK (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[570,null,"BRAMCOTE-FORMAN","AW0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","BRAMCOTE-FORMAN (03)",0,0]
[571,null,"BECCLES-ANDERSON","CN0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BECCLES-ANDERSON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[572,null,"BERRIMA-ROSANNA","NH0-020","2025-02-02","2025-02-08","N","N","N","Y","N","N","NH0","BERRIMA-ROSANNA (02)",0,9.4304036212749905E-5]
[573,null,"GRANDVIEW-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GRANDVIEW-HOLMES (03)",4.4620945071616617E-5,0]
[574,null,"WEST-JOHN","PV0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","WEST-JOHN (02)",4.4620945071616617E-5,0]
[575,null,"QUEEN-RUSSELL","NT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","QUEEN-RUSSELL (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[576,null,"DOYLE-NORTH","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","DOYLE-NORTH (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[577,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[578,null,"LAUREL-TYLER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","LAUREL-TYLER (04)",{"$f":"IF(G579=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J579=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[579,null,"SEXTON-HALSEY","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","SEXTON-HALSEY (03)",0,0]
[580,null,"FINTON-ARUNDEL","TT0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (02)",0,0]
[581,null,"COOMA-GOWER","PTN-014","2025-02-02","2025-02-08","N","N","N","Y","N","N","PTN","COOMA-GOWER (02)",0,9.4304036212749905E-5]
[582,null,"BANYULE-MCCRAE","HB0-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","HB0","BANYULE-MCCRAE (01)",0,0]
[583,null,"WALKER-NEWCASTLE","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","WALKER-NEWCASTLE (02)",4.4620945071616617E-5,0]
[584,null,"JEFFREY-WESTGARTH","FF0-089","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (03)",0,0]
[585,null,"BEATRICE-JENSEN","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BEATRICE-JENSEN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[586,null,"QUINN-NOGA","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","QUINN-NOGA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[587,null,"LOCKSLEY-KINSALE","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","LOCKSLEY-KINSALE (02)",4.4620945071616617E-5,0]
[588,null,"SALISBURY-JACK","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","SALISBURY-JACK (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[589,null,"PLENTY-RESERVOIR COLLEGE","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","PLENTY-RESERVOIR COLLEGE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[590,null,"GREENSBOROUGH-DRYSDALE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GREENSBOROUGH-DRYSDALE (02)",4.4620945071616617E-5,0]
[591,null,"FENTON-MYRNONG","FT0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","FENTON-MYRNONG (01)",4.4620945071616617E-5,0]
[592,null,"RALEIGH-HODDLE","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",0,0]
[593,null,"QUEEN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","QUEEN-REYNARD (02)",4.4620945071616617E-5,0]
[594,null,"ANGUS-MIDDLE","PV0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","ANGUS-MIDDLE (03)",4.4620945071616617E-5,0]
[595,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[596,null,"DELAWARE-MENDIP","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","DELAWARE-MENDIP (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[597,null,"DUNFIELD-BERESFORD","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","DUNFIELD-BERESFORD (01)",4.4620945071616617E-5,0]
[598,null,"LEVER-QUEEN","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-QUEEN (03)",4.4620945071616617E-5,0]
[599,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[600,null,"LIVINGSTONE-ELIZABETH","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","LIVINGSTONE-ELIZABETH (01)",4.4620945071616617E-5,0]
[601,null,"LEVER-QUEEN","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-QUEEN (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[602,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","STEELE-STUART (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[603,null,"GRANDVIEW-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","GRANDVIEW-HOLMES (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[604,null,"BRADLEY-MASON","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BRADLEY-MASON (01)",4.4620945071616617E-5,0]
[605,null,"HUTCHESON-THE STRAND","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (01)",0,0]
[606,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[607,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[608,null,"YEA-KIEWA","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","YEA-KIEWA (01)",4.4620945071616617E-5,0]
[609,null,"WALKER-NEWCASTLE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WALKER-NEWCASTLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[610,null,"KATHLEEN-WOOD","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","KATHLEEN-WOOD (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[611,null,"WILLIAM-JUKES","CN0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","WILLIAM-JUKES (01)",4.4620945071616617E-5,0]
[612,null,"CAPRICORN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","CAPRICORN-PALMERSTON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[613,null,"TURNER-EVANS","NS0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",0,0]
[614,null,"CAPTAIN PEARSON-PINE","COO-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","CAPTAIN PEARSON-PINE (02)",4.4620945071616617E-5,0]
[615,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[616,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[617,null,"CANTALA-MCCRAE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","CANTALA-MCCRAE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[618,null,"BERRY-KEILOR","ES0-026","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BERRY-KEILOR (03)",4.4620945071616617E-5,0]
[619,null,"MIRAMS-UNION","FT0-026","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","MIRAMS-UNION (01)",4.4620945071616617E-5,0]
[620,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MARGTMARY-MURRAY (03)",4.4620945071616617E-5,0]
[621,null,"COLE-OSBORNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","COLE-OSBORNE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[622,null,"ROXBURGH-ROTHWELL","FT0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","ROXBURGH-ROTHWELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[623,null,"SUFFOLK-DONGOLA","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","SUFFOLK-DONGOLA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[624,null,"GAP-COWPER","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","GAP-COWPER (02)",0,0]
[625,null,"DIXON-DERBY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DIXON-DERBY (01)",4.4620945071616617E-5,0]
[626,null,"BRADLEY-MASON","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BRADLEY-MASON (01)",4.4620945071616617E-5,0]
[627,null,"CASTLETON 21-HAVILAH","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CASTLETON 21-HAVILAH (02)",4.4620945071616617E-5,0]
[628,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[629,null,"BLOOMFIELD-ROSAMOND","YVE-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","YVE","BLOOMFIELD-ROSAMOND (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[630,null,"GLASS-NAPIER NO.2","NS0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","GLASS-NAPIER NO.2 (02)",0,0]
[631,null,"ANDERSON-BOLINGBROKE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","O'HEA-CUMBERLAND (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[632,null,"BOND-LIBERTY","EP0-034","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","EP0","FORD-SPARKFORD (01)",4.4620945071616617E-5,0]
[633,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[634,null,"BELGROVE-OVANDO","PTN-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","BELGROVE-OVANDO (02)",4.4620945071616617E-5,0]
[635,null,"COLLINS-WATERDALE","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","COLLINS-WATERDALE (02)",0,0]
[636,null,"KATOOMBA-SUTHERLAND","PV0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KATOOMBA-SUTHERLAND (02)",4.4620945071616617E-5,0]
[637,null,"GELLIBRAND-STEWART","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","GELLIBRAND-STEWART (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[638,null,"SALTAU-MILLEARA","AW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","SALTAU-MILLEARA (02)",0,0]
[639,null,"ANDERSON-BEVERLEY","HB0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","ANDERSON-BEVERLEY (01)",4.4620945071616617E-5,0]
[640,null,"KERFERD-RALEIGH","ES0-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","KERFERD-RALEIGH (02)",0,0]
[641,null,"HOLROYD-O'HEA","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HOLROYD-O'HEA (03)",4.4620945071616617E-5,0]
[642,null,"SOUDAN-HIGH","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SOUDAN-HIGH (01)",{"$f":"IF(G643=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J643=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[643,null,"LLOYD-MONASH","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","LLOYD-MONASH (02)",0,0]
[644,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","O'DOWD-HOWARD (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[645,null,"CAPRICORN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","CAPRICORN-PALMERSTON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[646,null,"INTERNATIONAL-T'PARK","AW0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","INTERNATIONAL-T'PARK (00)",0,0]
[647,null,"MCCUBBIN-WENTWORTH","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","MCCUBBIN-WENTWORTH (01)",4.4620945071616617E-5,0]
[648,null,"CORNWALL-HIGH SCHOOL","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",4.4620945071616617E-5,0]
[649,null,"BERRY-LORNE","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BERRY-LORNE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[650,null,"WESTMINSTER-MILITARY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","WESTMINSTER-MILITARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[651,null,"LANDELLS-MARTIN","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","LANDELLS-MARTIN (04)",4.4620945071616617E-5,0]
[652,null,"ST LEONARDS-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ST LEONARDS-EPSOM (03)",4.4620945071616617E-5,0]
[653,null,"LEWIS-WILLIAMS","CS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEWIS-WILLIAMS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[654,null,"MIRAMS-UNION","FT0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","MIRAMS-UNION (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[655,null,"MT ALEXANDER-HOMER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MT ALEXANDER-HOMER (03)",0,0]
[656,null,"PRESTON-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PRESTON-MUNRO (02)",4.4620945071616617E-5,0]
[657,null,"RALEIGH-HODDLE","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (00)",0,0]
[658,null,"SALISBURY-WILLIAMSTOWN","FE0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","SALISBURY-WILLIAMSTOWN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[659,null,"GARNET-IDA","ES0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","GARNET-IDA (03)",0,0]
[660,null,"ROSEHILL-ROSE","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ROSEHILL-ROSE (02)",0,0]
[661,null,"ALOHA-WATT","FE0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","FE0","ALOHA-WATT (01)",4.4620945071616617E-5,0]
[662,null,"HARDY-SNAEFELL","AW0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","HARDY-SNAEFELL (01)",4.4620945071616617E-5,0]
[663,null,"CLARKE-RUPERT","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","CLARKE-RUPERT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[664,null,"PERIGRINE-DEEP CREEK","COO-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","COO","PERIGRINE-DEEP CREEK (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[665,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MARGTMARY-MURRAY (03)",4.4620945071616617E-5,0]
[666,null,"DONCASTER-WALTER","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DONCASTER-WALTER (02)",4.4620945071616617E-5,0]
[667,null,"EISENHOWER-CHALEYER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","EISENHOWER-CHALEYER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[668,null,"ORIEL-STANLEY","EP0-034","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","ORIEL-STANLEY (02)",4.4620945071616617E-5,0]
[669,null,"DALKEITH-GORDON","AW0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","DALKEITH-GORDON (02)",4.4620945071616617E-5,0]
[670,null,"HAWTHORN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HAWTHORN-REYNARD (01)",4.4620945071616617E-5,0]
[671,null,"DIAMOND-ROSEHILL","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[672,null,"LEAKE-RICHARDSON","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","LEAKE-RICHARDSON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[673,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[674,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (01)",4.4620945071616617E-5,0]
[675,null,"CAPE-ST JAMES","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CAPE-ST JAMES (03)",4.4620945071616617E-5,0]
[676,null,"MCNAMARA-ROBERTS","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","MCNAMARA-ROBERTS (02)",4.4620945071616617E-5,0]
[677,null,"FORREST-HUDSONS","YVE-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","YVE","FORREST-HUDSONS (04)",0,0]
[678,null,"WEST-KINGSLEY","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","WEST-KINGSLEY (01)",4.4620945071616617E-5,0]
[679,null,"SUNSHINE-MARKET No 2","TH0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","SUNSHINE-MARKET No 2 (02)",0,0]
[680,null,"ALMA-YARRA","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","ALMA-YARRA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[681,null,"FLOWER-BUCKLEY","ES0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FLOWER-BUCKLEY (03)",4.4620945071616617E-5,0]
[682,null,"GRANGE-CRAMER","CS0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRANGE-CRAMER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[683,null,"RESERVOIR-WILSON","SBY-032","2025-02-02","2025-02-08","Y","N","N","N","N","N","SBY","RESERVOIR-WILSON (02)",4.4620945071616617E-5,0]
[684,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[685,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","McGOWAN-MURRAY (01)",4.4620945071616617E-5,0]
[686,null,"DAREBIN-STRADBROKE","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","DAREBIN-STRADBROKE (01)",4.4620945071616617E-5,0]
[687,null,"LIBERTY-PERKINS","EP0-034","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","LIBERTY-PERKINS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[688,null,"WEBB-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-QUEENSVILLE (04)",4.4620945071616617E-5,0]
[689,null,"REYNARD-ROYAL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-ROYAL (02)",4.4620945071616617E-5,0]
[690,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HODDLE-FLETCHER (01)",0,0]
[691,null,"SNELL-WATT","PV0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SNELL-WATT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[692,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[693,null,"HUTCHESON-THE STRAND","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (01)",0,0]
[694,null,"PARKVIEW-HEIDELBERG","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","PARKVIEW-HEIDELBERG (02)",4.4620945071616617E-5,0]
[695,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (01)",0,0]
[696,null,"VINCENT-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","VINCENT-BELL (03)",4.4620945071616617E-5,0]
[697,null,"SCHOOL-TRAP","COO-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","COO","SCHOOL-TRAP (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[698,null,"CARWARP-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CARWARP-ERSKINE (02)",4.4620945071616617E-5,0]
[699,null,"EFFINGHAM-WILKINS","NT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","EFFINGHAM-WILKINS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[700,null,"ERSKINE-GLENCAIRN","COO-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","ERSKINE-GLENCAIRN (01)",4.4620945071616617E-5,0]
[701,null,"MCCOLL-MALPAS","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","MCCOLL-MALPAS (02)",4.4620945071616617E-5,0]
[702,null,"BIMBADEEN-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",4.4620945071616617E-5,0]
[703,null,"KERFERD-RALEIGH","ES0-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (01)",0,0]
[704,null,"LAWSON-SALISBURY","NS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","LAWSON-SALISBURY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[705,null,"ALBERT-DUNDAS","EP0-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","ALBERT-DUNDAS (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[706,null,"BEATRICE-JENSEN","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BEATRICE-JENSEN (01)",{"$f":"IF(G707=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J707=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[707,null,"TRACEY-ELLIOT","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","TRACEY-ELLIOT (01)",4.4620945071616617E-5,0]
[708,null,"ANTHONY-BELLAIR","FT0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","ANTHONY-BELLAIR (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[709,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[710,null,"KALANG-PLUMPTON","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KALANG-PLUMPTON (02)",4.4620945071616617E-5,0]
[711,null,"FLETCHER-PASCOE VALE","NS0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","FLETCHER-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[712,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,0]
[713,null,"FLETCHER-PASCOE VALE","NS0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","FLETCHER-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[714,null,"VIEWBANK-BREES","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","VIEWBANK-BREES (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[715,null,"WALLACE-KENILWORTH","FF0-090","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",0,0]
[716,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",0,0]
[717,null,"PEARL-WHEATSHEAF","PV0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","PEARL-WHEATSHEAF (02)",4.4620945071616617E-5,0]
[718,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",0,0]
[719,null,"THE CROSSWAY-UPLAND","NS0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","THE CROSSWAY-UPLAND (03)",4.4620945071616617E-5,0]
[720,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[721,null,"ARGYLE-BROAD","FW0-016","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","ARGYLE-BROAD (01)",0,0]
[722,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[723,null,"GALLERY GATE-PERONINE","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GALLERY GATE-PERONINE (03)",4.4620945071616617E-5,0]
[724,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[725,null,"CRESWICK-LATROBE","FE0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","CRESWICK-LATROBE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[726,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,0]
[727,null,"COVENTRY-MALVERN","AW0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","COVENTRY-MALVERN (02)",0,0]
[728,null,"BEVERLEY-GREVILLE","HB0-023","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","HB0","BEVERLEY-GREVILLE (01)",4.4620945071616617E-5,0]
[729,null,"HARCOURT-SHERBOURNE","AW0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","HARCOURT-SHERBOURNE (02)",0,0]
[730,null,"BRUNEL-TRUMAN","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","BRUNEL-TRUMAN (01)",4.4620945071616617E-5,0]
[731,null,"WALKER-NEWCASTLE","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","WALKER-NEWCASTLE (02)",4.4620945071616617E-5,0]
[732,null,"CARWARP-MAY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CARWARP-MAY (04)",4.4620945071616617E-5,0]
[733,null,"PARK-BOTANIC","SHM-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","PARK-BOTANIC (02)",4.4620945071616617E-5,0]
[734,null,"CHALLIS-SPEIGHT","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-SPEIGHT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[735,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[736,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GLENMORE-KINLOCK (03)",4.4620945071616617E-5,0]
[737,null,"BULLA-DUBLIN","ES0-025","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BULLA-DUBLIN (02)",4.4620945071616617E-5,0]
[738,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",0,0]
[739,null,"CHARLES-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","CHARLES-EPSOM (02)",4.4620945071616617E-5,0]
[740,null,"MALMSBURY-WOODBURN","BD0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","MALMSBURY-WOODBURN (01)",0,0]
[741,null,"ARTHUR-FAWKNER","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ARTHUR-FAWKNER (01)",4.4620945071616617E-5,0]
[742,null,"LATROBE-MENZIES","SBY-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SBY","LATROBE-MENZIES (01)",4.4620945071616617E-5,0]
[743,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","STEELE-STUART (04)",4.4620945071616617E-5,0]
[744,null,"KALANG-PLUMPTON","PV0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","KALANG-PLUMPTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[745,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[746,null,"EIRENE-FRANCIS","FW0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","EIRENE-FRANCIS (01)",4.4620945071616617E-5,0]
[747,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,0]
[748,null,"HAMPDEN-CROTHERS","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",0,0]
[749,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","YALLAMBIE-LOWER PLENTY (02)",4.4620945071616617E-5,0]
[750,null,"RUSSELL-BARKLY","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","RUSSELL-BARKLY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[751,null,"RATHCOWN-CHEDDAR","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","RATHCOWN-CHEDDAR (01)",4.4620945071616617E-5,0]
[752,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (01)",0,0]
[753,null,"SOUTH-BELL","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",0,0]
[754,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[755,null,"CASTLETON 21-HAVILAH","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CASTLETON 21-HAVILAH (02)",4.4620945071616617E-5,0]
[756,null,"JACKSON-THOMSON","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","JACKSON-THOMSON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[757,null,"ALBERT-HARROW","EPN-035","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","ALBERT-HARROW (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[758,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (02)",4.4620945071616617E-5,0]
[759,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[760,null,"BECKET-ANSELM","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","BECKET-ANSELM (03)",4.4620945071616617E-5,0]
[761,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HODDLE-FLETCHER (01)",0,0]
[762,null,"THE ESPLANADE-PLANTATION","YVE-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","THE ESPLANADE-PLANTATION (01)",4.4620945071616617E-5,0]
[763,null,"CANTALA-MCCRAE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","CANTALA-MCCRAE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[764,null,"GORDON-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GORDON-BELL (02)",4.4620945071616617E-5,0]
[765,null,"CUMBERLAND-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CUMBERLAND-KENT (01)",4.4620945071616617E-5,0]
[766,null,"CAPRICORN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","CAPRICORN-PALMERSTON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[767,null,"GORDON-WOOD","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","GORDON-WOOD (02)",0,0]
[768,null,"CARWARP-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","CARWARP-ERSKINE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[769,null,"ESSEX-DUDLEY","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ESSEX-DUDLEY (03)",4.4620945071616617E-5,0]
[770,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",{"$f":"IF(G771=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J771=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[771,null,"HENTY-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","HENTY-GILBERT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[772,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","YALLAMBIE-LOWER PLENTY (02)",4.4620945071616617E-5,0]
[773,null,"FREIGHT-CUSTOM","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (02)",0,0]
[774,null,"RALEIGH-HODDLE","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",0,0]
[775,null,"BERRIMA-ROSANNA","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BERRIMA-ROSANNA (02)",4.4620945071616617E-5,0]
[776,null,"THE CROSSWAY-UPLAND","NS0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","THE CROSSWAY-UPLAND (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[777,null,"WEBB-CORONATION","FW0-008","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","FW0","WEBB-CORONATION (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[778,null,"BEATRICE-JENSEN","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BEATRICE-JENSEN (01)",4.4620945071616617E-5,0]
[779,null,"SOMERS-HINKLER","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","SOMERS-HINKLER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[780,null,"WILLIAM-MASON","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WILLIAM-MASON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[781,null,"SHERWOOD-THORESBY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","SHERWOOD-THORESBY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[782,null,"DUDLEY-GREEN","FF0-090","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","DUDLEY-GREEN (02)",4.4620945071616617E-5,0]
[783,null,"PENGANA-LOONGANA","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","PENGANA-LOONGANA (02)",4.4620945071616617E-5,0]
[784,null,"OXFORD-JUNCTION","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","OXFORD-JUNCTION (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[785,null,"GAVIN-SUNSET","BMS-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","BMS","GAVIN-SUNSET (02)",4.4620945071616617E-5,0]
[786,null,"ERIC-ADA","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","McGOWAN-MURRAY (03)",4.4620945071616617E-5,0]
[787,null,"BRAMCOTE-FORMAN","AW0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","BRAMCOTE-FORMAN (02)",0,0]
[788,null,"LAUREL-TYLER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","LAUREL-TYLER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[789,null,"BELMONT-DELLA TORRE","FF0-090","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","BELMONT-DELLA TORRE (03)",4.4620945071616617E-5,0]
[790,null,"WODONGA-CUTHBERT","BD0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","WODONGA-CUTHBERT (01)",0,0]
[791,null,"BLAKE-DAVIS","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BLAKE-DAVIS (02)",4.4620945071616617E-5,0]
[792,null,"ROSS-ELIZABETH","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","ROSS-ELIZABETH (01)",4.4620945071616617E-5,0]
[793,null,"DARLING-FULHAM","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","DARLING-FULHAM (01)",4.4620945071616617E-5,0]
[794,null,"DONCASTER-WALTER","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DONCASTER-WALTER (02)",4.4620945071616617E-5,0]
[795,null,"GENEVA-COMO","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","GENEVA-COMO (02)",4.4620945071616617E-5,0]
[796,null,"ANDERSON-BOLINGBROKE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","ANDERSON-BOLINGBROKE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[797,null,"PORTER-DOUGHARTY","NH0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","PORTER-DOUGHARTY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[798,null,"WASHINGTON-DOY","BD0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","WASHINGTON-DOY (01)",0,0]
[799,null,"GILBANK-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","GILBANK-GILBERT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[800,null,"CENTRAL-GEELONG","FE0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","CENTRAL-GEELONG (02)",0,0]
[801,null,"GOULBURN-SHAND","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","GOULBURN-SHAND (03)",4.4620945071616617E-5,0]
[802,null,"RAVENSCOURT-FULHAM","FF0-083","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",0,0]
[803,null,"LLOYD-MONASH","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","LLOYD-MONASH (02)",0,0]
[804,null,"BRAY-BARTROP","TT0-008","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","TT0","BRAY-BARTROP (01)",4.4620945071616617E-5,0]
[805,null,"STANGER-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","STANGER-ADENEY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[806,null,"LEWIS-WILLIAMS","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEWIS-WILLIAMS (01)",4.4620945071616617E-5,0]
[807,null,"MYRTLE-REGENT","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","MYRTLE-REGENT (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[808,null,"YALLAMBIE-WENDOVER","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","YALLAMBIE-WENDOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[809,null,"PARSONS-STUBBS","FT0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","PARSONS-STUBBS (02)",4.4620945071616617E-5,0]
[810,null,"FORRESTER-COOPER","ES0-025","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FORRESTER-COOPER (01)",4.4620945071616617E-5,0]
[811,null,"BOLINGBROKE-BURGUNDY","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BOLINGBROKE-BURGUNDY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[812,null,"ASHLEY-NAPOLEON","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",0,0]
[813,null,"SOUDAN-HIGH","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SOUDAN-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[814,null,"GOULBURN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","GOULBURN-PALMERSTON (04)",4.4620945071616617E-5,0]
[815,null,"DIXON-DERBY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DIXON-DERBY (01)",4.4620945071616617E-5,0]
[816,null,"NEWCASTLE-ELIZABETH","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","NEWCASTLE-ELIZABETH (02)",4.4620945071616617E-5,0]
[817,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[818,null,"AMIS-VISTA","AW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","AMIS-VISTA (02)",0,0]
[819,null,"HEATHCOTE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HEATHCOTE-KENT (02)",4.4620945071616617E-5,0]
[820,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (03)",4.4620945071616617E-5,0]
[821,null,"DARLING-FULHAM","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","DARLING-FULHAM (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[822,null,"HILTON-WIDFORD","PV0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","HILTON-WIDFORD (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[823,null,"MCKELL-HOLT","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","MCKELL-HOLT (01)",0,0]
[824,null,"JUDITH-BREES","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","JUDITH-BREES (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[825,null,"THE GLADE-SHERLOWE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","THE GLADE-SHERLOWE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[826,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[827,null,"PEARL-WHEATSHEAF","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","PEARL-WHEATSHEAF (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[828,null,"KNIGHT-BAYVIEW","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","KNIGHT-BAYVIEW (02)",4.4620945071616617E-5,0]
[829,null,"BECCLES-ANDERSON","CN0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BECCLES-ANDERSON (03)",4.4620945071616617E-5,0]
[830,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MOUSHALL-NOLAN (02)",4.4620945071616617E-5,0]
[831,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[832,null,"ALEXANDRA-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ALEXANDRA-LANDELLS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[833,null,"FLINDERS-WENTWORTH","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","FLINDERS-WENTWORTH (02)",0,0]
[834,null,"RILL-OLIVE","NH0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","RILL-OLIVE (01)",{"$f":"IF(G835=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J835=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[835,null,"BLAKE-DAVIS","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BLAKE-DAVIS (02)",4.4620945071616617E-5,0]
[836,null,"CHARLES-BENAMBRA","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CHARLES-BENAMBRA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[837,null,"SALTAU-MILLEARA","AW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","SALTAU-MILLEARA (02)",0,0]
[838,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[839,null,"SALMON-SCHOFIELD","NS0-016","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","SALMON-SCHOFIELD (02)",0,0]
[840,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,0]
[841,null,"BERRY-LORNE","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BERRY-LORNE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[842,null,"ASHLEY-CENTRAL WEST NO.1","TH0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TH0","ASHLEY-CENTRAL WEST NO.1 (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[843,null,"DAREBIN-STRADBROKE","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","DAREBIN-STRADBROKE (01)",4.4620945071616617E-5,0]
[844,null,"WEBB-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-QUEENSVILLE (02)",4.4620945071616617E-5,0]
[845,null,"DAVID-RACHELLE","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","DAVID-RACHELLE (01)",4.4620945071616617E-5,0]
[846,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[847,null,"DEAKIN-MARY","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DEAKIN-MARY (02)",4.4620945071616617E-5,0]
[848,null,"CHARTERIS-WARNCLIFFE","HB0-024","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","HB0","CHARTERIS-WARNCLIFFE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[849,null,"PORTER-DOUGHARTY","NH0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","PORTER-DOUGHARTY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[850,null,"ELLEN-RACHELLE","AW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ELLEN-RACHELLE (01)",0,0]
[851,null,"BOSQUET-BALLARAT","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","BOSQUET-BALLARAT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[852,null,"GLADSTONE-CHAPMAN","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","GLADSTONE-CHAPMAN (01)",4.4620945071616617E-5,0]
[853,null,"ESSEX-DOWNS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-DOWNS (02)",4.4620945071616617E-5,0]
[854,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",0,0]
[855,null,"BEVERLEY-GREVILLE","HB0-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","HB0","BEVERLEY-GREVILLE (02)",0,0]
[856,null,"PASCOE VALE-BENDOC","BD0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","PASCOE VALE-BENDOC (02)",4.4620945071616617E-5,0]
[857,null,"SAMARA-ELMHURST","AW0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","SAMARA-ELMHURST (02)",0,0]
[858,null,"KERR-DEVEREAUX","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KERR-DEVEREAUX (02)",4.4620945071616617E-5,0]
[859,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[860,null,"GLASS-NAPIER","NS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","GLASS-NAPIER (01)",4.4620945071616617E-5,0]
[861,null,"JACK-FORD","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","JACK-FORD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[862,null,"MUNRO-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","MUNRO-ERSKINE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[863,null,"HILLSIDE-HURTLE","ES0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","HILLSIDE-HURTLE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[864,null,"WATERSONS RD-P3W1","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","WATERSONS RD-P3W1 (00)",0,0]
[865,null,"HAUGHTON-GREVILLE","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","HAUGHTON-GREVILLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[866,null,"MAJOR-HUME","CN0-004","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MAJOR-HUME (04)",4.4620945071616617E-5,0]
[867,null,"CARTWRIGHT-PASCOE VALE","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CARTWRIGHT-PASCOE VALE (02)",4.4620945071616617E-5,0]
[868,null,"MYRTLE-REGENT","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","MYRTLE-REGENT (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[869,null,"GLASS-NAPIER","NS0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","GLASS-NAPIER (01)",0,0]
[870,null,"GOULBURN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","GOULBURN-PALMERSTON (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[871,null,"SALISBURY-JACK","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","SALISBURY-JACK (01)",4.4620945071616617E-5,0]
[872,null,"JOHNSTON-NEWCASTLE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","JOHNSTON-NEWCASTLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[873,null,"HIGH-SEVERN","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","HIGH-SEVERN (02)",4.4620945071616617E-5,0]
[874,null,"GELLIBRAND-STEWART","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","GELLIBRAND-STEWART (01)",4.4620945071616617E-5,0]
[875,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,0]
[876,null,"BREX-RADFORD","TT0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","BREX-RADFORD (00)",0,0]
[877,null,"CULLEN-MARY","YVE-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","YVE","CULLEN-MARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[878,null,"LATROBE-MENZIES","SBY-012","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","SBY","LATROBE-MENZIES (01)",4.4620945071616617E-5,0]
[879,null,"ROSELAND-IVANHOE","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","ROSELAND-IVANHOE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[880,null,"FLORENCE-LINCOLN","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","FLORENCE-LINCOLN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[881,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","STEELE-STUART (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[882,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[883,null,"CHARLES-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","CHARLES-EPSOM (02)",4.4620945071616617E-5,0]
[884,null,"KALANG-PLUMPTON","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KALANG-PLUMPTON (01)",4.4620945071616617E-5,0]
[885,null,"CHAPMAN-GRANDVIEW","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CHAPMAN-GRANDVIEW (01)",4.4620945071616617E-5,0]
[886,null,"STEEL-THE AVENUE","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","STEEL-THE AVENUE (02)",4.4620945071616617E-5,0]
[887,null,"SHERWOOD-THORESBY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","SHERWOOD-THORESBY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[888,null,"BROADHURST-MCFADZEAN","TT0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","OCONNOR-MACFADZEAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[889,null,"MCIVOR-OAKHILL","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MCIVOR-OAKHILL (01)",4.4620945071616617E-5,0]
[890,null,"GRAVES-MARKET","ES0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GRAVES-MARKET (01)",4.4620945071616617E-5,0]
[891,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[892,null,"WALKER-NEWCASTLE","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","WALKER-NEWCASTLE (02)",4.4620945071616617E-5,0]
[893,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[894,null,"HILLCREST-ROYAL","SHM-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","HILLCREST-ROYAL (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[895,null,"MAY-SPRING","PTN-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","MAY-SPRING (03)",4.4620945071616617E-5,0]
[896,null,"ROSS-ELIZABETH","NT0-017","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","NT0","ROSS-ELIZABETH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[897,null,"GARNET-MURIEL","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GARNET-MURIEL (03)",4.4620945071616617E-5,0]
[898,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GLENMORE-KINLOCK (03)",{"$f":"IF(G899=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J899=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[899,null,"DOYLE-NORTH","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","DOYLE-NORTH (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[900,null,"TONKIN-MASHOOBRA","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","TONKIN-MASHOOBRA (01)",4.4620945071616617E-5,0]
[901,null,"SEPARATION-FULHAM","FF0-093","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","SEPARATION-FULHAM (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[902,null,"LOCKSLEY-KINSALE","CN0-007","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","CN0","LOCKSLEY-KINSALE (02)",4.4620945071616617E-5,0]
[903,null,"DOVER-WATERLOO","NT0-004","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","DOVER-WATERLOO (02)",4.4620945071616617E-5,0]
[904,null,"ESSEX-SWAN","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","ESSEX-SWAN (02)",0,0]
[905,null,"ELATA-BEVERAGE","AW0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ELATA-BEVERAGE (02)",0,0]
[906,null,"ALMOND-CONIFER","FW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ALMOND-CONIFER (01)",4.4620945071616617E-5,0]
[907,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,0]
[908,null,"EISENHOWER-CHALEYER","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","EISENHOWER-CHALEYER (01)",4.4620945071616617E-5,0]
[909,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GLENMORE-KINLOCK (03)",4.4620945071616617E-5,0]
[910,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MARGTMARY-MURRAY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[911,null,"BEAUCHAMP-HIGH","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","BEAUCHAMP-HIGH (01)",4.4620945071616617E-5,0]
[912,null,"RUSSELL-BARKLY","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","RUSSELL-BARKLY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[913,null,"LANCEFIELD RD-P50","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","LANCEFIELD RD-P50 (00)",0,0]
[914,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,0]
[915,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[916,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[917,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (01)",4.4620945071616617E-5,0]
[918,null,"THE BOULEVARD-NEVILLE","HB0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","THE BOULEVARD-NEVILLE (02)",4.4620945071616617E-5,0]
[919,null,"GREVILLIA-ALBERT","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","GREVILLIA-ALBERT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[920,null,"PARKVIEW-HEIDELBERG","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","PARKVIEW-HEIDELBERG (01)",4.4620945071616617E-5,0]
[921,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[922,null,"SUSSEX-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","SUSSEX-HOLMES (02)",4.4620945071616617E-5,0]
[923,null,"BROWN-ROSANNA","HB0-032","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","BROWN-ROSANNA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[924,null,"HAMILTON-O'FARRELL","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",0,0]
[925,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ESSEX-LANDELLS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[926,null,"CHAPMAN-BELAIR","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CHAPMAN-BELAIR (02)",4.4620945071616617E-5,0]
[927,null,"JENNINGS-ARDMILLAN","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","JENNINGS-ARDMILLAN (02)",4.4620945071616617E-5,0]
[928,null,"HEIDELBERG-KINGSLEY","HB0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","HB0","HEIDELBERG-KINGSLEY (03)",0,0]
[929,null,"CHAUVEL-GLASGOW","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","CHAUVEL-GLASGOW (04)",4.4620945071616617E-5,0]
[930,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",4.4620945071616617E-5,0]
[931,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[932,null,"GLOUCESTER-HENTY","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","GLOUCESTER-HENTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[933,null,"THE ESPLANADE-PLANTATION","YVE-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","YVE","THE ESPLANADE-PLANTATION (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[934,null,"CORNISH-LIGAR","SBY-012","2025-02-02","2025-02-08","N","N","N","Y","N","N","SBY","CORNISH-LIGAR (02)",0,9.4304036212749905E-5]
[935,null,"EDWIN-GILLIES","FF0-087","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","EDWIN-GILLIES (01)",4.4620945071616617E-5,0]
[936,null,"CAROLE JOY-SPRING","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CAROLE JOY-SPRING (02)",4.4620945071616617E-5,0]
[937,null,"BANNON-RETREAT","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BANNON-RETREAT (02)",0,0]
[938,null,"MUNRO-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","MUNRO-ERSKINE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[939,null,"WEBB-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-QUEENSVILLE (02)",4.4620945071616617E-5,0]
[940,null,"ASCOT VALE 331-YOUNG","NS0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ASCOT VALE 331-YOUNG (01)",0,0]
[941,null,"HAWKHURST-FRANCIS","FW0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","HAWKHURST-FRANCIS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[942,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[943,null,"EDWARD-CASH","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","EDWARD-CASH (02)",4.4620945071616617E-5,0]
[944,null,"ST HELLIER-UP HEIDELBERG","NH0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","ST HELLIER-UP HEIDELBERG (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[945,null,"EGLINTON-ARGYLE","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","EGLINTON-ARGYLE (03)",4.4620945071616617E-5,0]
[946,null,"LLOYD-MONASH","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",0,0]
[947,null,"HOBBS-PENTLAND","FE0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",0,0]
[948,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[949,null,"VIEWBANK-BREES","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","VIEWBANK-BREES (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[950,null,"LENNOX-HYDE","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","LENNOX-HYDE (03)",0,0]
[951,null,"WILLOWTREE-PERSICA","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (01)",0,0]
[952,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ETZEL-CLYDESDALE (03)",0,0]
[953,null,"FINNINGLEY-MARHAM","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FINNINGLEY-MARHAM (02)",0,0]
[954,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[955,null,"FORRESTER-HEDDERWICK","ES0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BUCKLEY-ABERDEEN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[956,null,"REYNARD-ROYAL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-ROYAL (01)",4.4620945071616617E-5,0]
[957,null,"STEWART-PASCOE VALE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","STEWART-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[958,null,"OWEN-GORDON","FE0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","OWEN-GORDON (01)",0,0]
[959,null,"BOND-LIBERTY","EP0-034","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","EP0","FORD-SPARKFORD (01)",4.4620945071616617E-5,0]
[960,null,"SOMERVILLE-JULIAN","FW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","SOMERVILLE-JULIAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[961,null,"GELLIBRAND-STEWART","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","GELLIBRAND-STEWART (02)",4.4620945071616617E-5,0]
[962,null,"PASLEY-NEILL","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","PASLEY-NEILL (02)",{"$f":"IF(G963=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J963=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[963,null,"THORPE-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","THORPE-WOODS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[964,null,"MCCRAE-ELSEY","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","MCCRAE-ELSEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[965,null,"NEWMAN-HOTHAM","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NEWMAN-HOTHAM (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[966,null,"MILLAR-DERBY","AW0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","MILLAR-DERBY (02)",0,0]
[967,null,"ASHLEY-CENTRAL WEST NO.1","TH0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TH0","ASHLEY-CENTRAL WEST NO.1 (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[968,null,"SECOND-EVE","ST0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ST0","SECOND-EVE (01)",4.4620945071616617E-5,0]
[969,null,"WEBB-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-QUEENSVILLE (02)",4.4620945071616617E-5,0]
[970,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,0]
[971,null,"STEEL-THE AVENUE","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","STEEL-THE AVENUE (03)",4.4620945071616617E-5,0]
[972,null,"HIGGINS-MCKELL","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","HIGGINS-MCKELL (01)",0,0]
[973,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","YALLAMBIE-LOWER PLENTY (01)",4.4620945071616617E-5,0]
[974,null,"NEILL-MOUNSEY","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","NEILL-MOUNSEY (02)",0,0]
[975,null,"FETTLING-COOPER","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","FETTLING-COOPER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[976,null,"ASHLEY-CENTRAL WEST NO.1","TH0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TH0","ASHLEY-CENTRAL WEST NO.1 (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[977,null,"BRAMCOTE-FORMAN","AW0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","BRAMCOTE-FORMAN (01)",0,0]
[978,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,0]
[979,null,"RYDER-NOLAN","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","RYDER-NOLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[980,null,"ELLESMERE-CARRICK","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","ELLESMERE-CARRICK (02)",4.4620945071616617E-5,0]
[981,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[982,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[983,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MARGTMARY-MURRAY (03)",4.4620945071616617E-5,0]
[984,null,"PRINCE-KEILOR","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","PRINCE-KEILOR (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[985,null,"ESSEX-DOWNS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-DOWNS (02)",4.4620945071616617E-5,0]
[986,null,"ALMA-CHANDLER","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","ALMA-CHANDLER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[987,null,"AYR-DAREBIN","TT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","AYR-DAREBIN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[988,null,"SUFFOLK-DONGOLA","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","SUFFOLK-DONGOLA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[989,null,"SUSSEX-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","SUSSEX-HOLMES (02)",4.4620945071616617E-5,0]
[990,null,"RENNIE-JOHN","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","RENNIE-JOHN (01)",4.4620945071616617E-5,0]
[991,null,"BELGROVE-OVANDO","PTN-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","BELGROVE-OVANDO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[992,null,"RILL-OLIVE","NH0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","RILL-OLIVE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[993,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","HODDLE-FLETCHER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[994,null,"RAGLAN-ASCOT","EP0-037","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (02)",0,0]
[995,null,"LANTANA-IVANHOE","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","LANTANA-IVANHOE (01)",4.4620945071616617E-5,0]
[996,null,"AYR-DAREBIN","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","AYR-DAREBIN (02)",4.4620945071616617E-5,0]
[997,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[998,null,"MIRAMS-UNION","FT0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","MIRAMS-UNION (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[999,null,"THE BOULEVARD-AFTON","ES0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","THE BOULEVARD-AFTON (00)",4.4620945071616617E-5,0]
[1000,null,"JOFFRE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","JOFFRE-KENT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1001,null,"CARWARP-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","CARWARP-ERSKINE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1002,null,"THE FAIRWAY-DUNNE","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","THE FAIRWAY-DUNNE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1003,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MOUSHALL-NOLAN (01)",4.4620945071616617E-5,0]
[1004,null,"CHARLES-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","CHARLES-EPSOM (02)",4.4620945071616617E-5,0]
[1005,null,"MEROLA 54 -FREEMAN","BD0-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","MEROLA 54 -FREEMAN (02)",0,0]
[1006,null,"WINCHESTER-LAURA","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","WINCHESTER-LAURA (01)",4.4620945071616617E-5,0]
[1007,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1008,null,"OLIVE-VIOLA","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","OLIVE-VIOLA (02)",4.4620945071616617E-5,0]
[1009,null,"HUDSONS-HICK","YVE-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","YVE","HUDSONS-HICK (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1010,null,"GREENACRE-AYLESBURY","AW0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","GREENACRE-AYLESBURY (02)",4.4620945071616617E-5,0]
[1011,null,"KATUNGA-HAMILTON","BD0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","KATUNGA-HAMILTON (02)",0,0]
[1012,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HODDLE-FLETCHER (01)",0,0]
[1013,null,"PAYWIT-BELLARINE","PTN-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","PAYWIT-BELLARINE (02)",4.4620945071616617E-5,0]
[1014,null,"WOODS-CHALLIS","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","WOODS-CHALLIS (01)",4.4620945071616617E-5,0]
[1015,null,"THE ESPLANADE-PLANTATION","YVE-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","THE ESPLANADE-PLANTATION (01)",4.4620945071616617E-5,0]
[1016,null,"ARBOR-MACEY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","ARBOR-MACEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1017,null,"CUDGEWA-BORVA","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","CUDGEWA-BORVA (01)",4.4620945071616617E-5,0]
[1018,null,"THISTLE-MT ALEXANDER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (01)",0,0]
[1019,null,"DIAMOND-ROSEHILL","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1020,null,"HAMPDEN-CROTHERS","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",0,0]
[1021,null,"OWEN-GORDON","FE0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","OWEN-GORDON (01)",0,0]
[1022,null,"KALANG-PLUMPTON","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KALANG-PLUMPTON (02)",4.4620945071616617E-5,0]
[1023,null,"ALMA-PALMERSTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1024,null,"JOHNSTON-NEWCASTLE","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","JOHNSTON-NEWCASTLE (02)",4.4620945071616617E-5,0]
[1025,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (03)",4.4620945071616617E-5,0]
[1026,null,"BEAUCHAMP-HIGH","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","BEAUCHAMP-HIGH (01)",{"$f":"IF(G1027=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1027=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[1027,null,"HUTCHESON-THE STRAND","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",0,0]
[1028,null,"ALEXANDRA-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",4.4620945071616617E-5,0]
[1029,null,"BIRDWOOD-REGENT","CN0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BIRDWOOD-REGENT (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1030,null,"THE RIDGE-DEEP CREEK 2","COO-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","COO","THE RIDGE-DEEP CREEK 2 (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1031,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[1032,null,"GLASS-NAPIER NO.2","NS0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","GLASS-NAPIER NO.2 (02)",0,0]
[1033,null,"HILLSIDE-HURTLE","ES0-013","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","ES0","HILLSIDE-HURTLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1034,null,"MORRIS-MCMAHONS","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","SHORE-MCMAHONS (02)",4.4620945071616617E-5,0]
[1035,null,"DORSET-BERKELEY","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","DORSET-BERKELEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1036,null,"LALUMA-MCCARRON","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","LALUMA-MCCARRON (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[1037,null,"GLASS-NAPIER","NS0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","GLASS-NAPIER (01)",0,0]
[1038,null,"ALMA-PALMERSTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1039,null,"RENNIE-JOHN","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","RENNIE-JOHN (01)",4.4620945071616617E-5,0]
[1040,null,"LEVER-QUEEN","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-QUEEN (03)",4.4620945071616617E-5,0]
[1041,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WALHALLA-MORELAND (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1042,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WALHALLA-MORELAND (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1043,null,"MOORE-EAST","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","NA",4.4620945071616617E-5,0]
[1044,null,"MOORE-EAST","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MOORE-EAST (02)",4.4620945071616617E-5,0]
[1045,null,"MOORE-EAST","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MOORE-EAST (02)",4.4620945071616617E-5,0]
[1046,null,"RIDGEWAY-LWR HEIDELBERG","HB0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","HB0","RIDGEWAY-LWR HEIDELBERG (02)",0,0]
[1047,null,"GLENGYLE-NICHOLSON","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GLENGYLE-NICHOLSON (03)",4.4620945071616617E-5,0]
[1048,null,"CAMPBELL-DE CARLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","CAMPBELL-DE CARLE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1049,null,"CAMPBELL-DE CARLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CAMPBELL-DE CARLE (01)",4.4620945071616617E-5,0]
[1050,null,"DE CARLE-RENNIE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DE CARLE-RENNIE (02)",4.4620945071616617E-5,0]
[1051,null,"DE CARLE-RENNIE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DE CARLE-RENNIE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1052,null,"RENNIE-GLENORA","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","RENNIE-GLENORA (02)",4.4620945071616617E-5,0]
[1053,null,"RENNIE-GLENORA","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","RENNIE-GLENORA (02)",4.4620945071616617E-5,0]
[1054,null,"STEWART-OSBORNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","STEWART-OSBORNE (02)",4.4620945071616617E-5,0]
[1055,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1056,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1057,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1058,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1059,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1060,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1061,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1062,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1063,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1064,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1065,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1066,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1067,null,"SEVERN-SOMERVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","SEVERN-SOMERVILLE (03)",4.4620945071616617E-5,0]
[1068,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1069,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1070,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1071,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1072,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1073,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1074,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[1075,null,"EDWARD-CASH","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","EDWARD-CASH (02)",4.4620945071616617E-5,0]
[1076,null,"EDWARD-CASH","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","EDWARD-CASH (02)",4.4620945071616617E-5,0]
[1077,null,"EDWARD-CASH","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","EDWARD-CASH (02)",4.4620945071616617E-5,0]
[1078,null,"EDWARD-CASH","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","EDWARD-CASH (02)",4.4620945071616617E-5,0]
[1079,null,"EDWARD-CASH","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","EDWARD-CASH (02)",4.4620945071616617E-5,0]
[1080,null,"EDWARD-CASH","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","EDWARD-CASH (02)",4.4620945071616617E-5,0]
[1081,null,"EDWARD-CASH","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","EDWARD-CASH (02)",4.4620945071616617E-5,0]
[1082,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WILLOW-LINDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1083,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WILLOW-LINDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1084,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WILLOW-LINDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1085,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WILLOW-LINDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1086,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WILLOW-LINDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1087,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WILLOW-LINDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1088,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WILLOW-LINDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1089,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WILLOW-LINDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1090,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WILLOW-LINDA (01)",{"$f":"IF(G1091=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1091=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[1091,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WILLOW-LINDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1092,null,"DARLING-MARIBYRNONG","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DARLING-MARIBYRNONG (02)",4.4620945071616617E-5,0]
[1093,null,"WIMPORT-MARTIN","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","WIMPORT-MARTIN (01)",4.4620945071616617E-5,0]
[1094,null,"HILLSYDE-LOEMAN","NS0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","HILLSYDE-LOEMAN (01)",4.4620945071616617E-5,0]
[1095,null,"STATION-HALL","CS0-005","2025-02-02","2025-02-08","N","Y","N","N","N","N","CS0","STATION-HALL (01)",0,0]
[1096,null,"BANKSIA-GLENARD","HB0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","BANKSIA-GLENARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1097,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WILLOW-LINDA (02)",4.4620945071616617E-5,0]
[1098,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WILLOW-LINDA (02)",4.4620945071616617E-5,0]
[1099,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WILLOW-LINDA (02)",4.4620945071616617E-5,0]
[1100,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WILLOW-LINDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1101,null,"WILLOW-LINDA","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WILLOW-LINDA (01)",4.4620945071616617E-5,0]
[1102,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1103,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1104,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1105,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1106,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1107,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1108,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1109,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1110,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1111,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1112,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1113,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1114,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1115,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,0]
[1116,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,0]
[1117,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,0]
[1118,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,0]
[1119,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,0]
[1120,null,"CLARENDON-SELBOURNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CLARENDON-SELBOURNE (01)",4.4620945071616617E-5,0]
[1121,null,"CLARENDON-SELBOURNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CLARENDON-SELBOURNE (01)",4.4620945071616617E-5,0]
[1122,null,"CLARENDON-SELBOURNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CLARENDON-SELBOURNE (01)",4.4620945071616617E-5,0]
[1123,null,"CLARENDON-SELBOURNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CLARENDON-SELBOURNE (01)",4.4620945071616617E-5,0]
[1124,null,"CLARENDON-SELBOURNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CLARENDON-SELBOURNE (01)",4.4620945071616617E-5,0]
[1125,null,"CLARENDON-SELBOURNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CLARENDON-SELBOURNE (01)",4.4620945071616617E-5,0]
[1126,null,"LEVER-QUEEN","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-QUEEN (03)",4.4620945071616617E-5,0]
[1127,null,"LEVER-QUEEN","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-QUEEN (03)",4.4620945071616617E-5,0]
[1128,null,"HAWTHORN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HAWTHORN-REYNARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1129,null,"HAWTHORN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HAWTHORN-REYNARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1130,null,"HAWTHORN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HAWTHORN-REYNARD (01)",4.4620945071616617E-5,0]
[1131,null,"HAWTHORN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HAWTHORN-REYNARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1132,null,"HAWTHORN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HAWTHORN-REYNARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1133,null,"HAWTHORN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HAWTHORN-REYNARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1134,null,"HAWTHORN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HAWTHORN-REYNARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1135,null,"HAWTHORN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HAWTHORN-REYNARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1136,null,"LEVER-QUEEN","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-QUEEN (03)",4.4620945071616617E-5,0]
[1137,null,"LEVER-QUEEN","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-QUEEN (03)",4.4620945071616617E-5,0]
[1138,null,"LEVER-QUEEN","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-QUEEN (03)",4.4620945071616617E-5,0]
[1139,null,"LEVER-QUEEN","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-QUEEN (03)",4.4620945071616617E-5,0]
[1140,null,"LEVER-QUEEN","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-QUEEN (03)",4.4620945071616617E-5,0]
[1141,null,"LEVER-QUEEN","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-QUEEN (03)",4.4620945071616617E-5,0]
[1142,null,"LEVER-QUEEN","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-QUEEN (03)",4.4620945071616617E-5,0]
[1143,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1144,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (02)",4.4620945071616617E-5,0]
[1145,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (02)",4.4620945071616617E-5,0]
[1146,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (01)",4.4620945071616617E-5,0]
[1147,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (01)",4.4620945071616617E-5,0]
[1148,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (02)",4.4620945071616617E-5,0]
[1149,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1150,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (02)",4.4620945071616617E-5,0]
[1151,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1152,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1153,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1154,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",{"$f":"IF(G1155=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1155=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[1155,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,0]
[1156,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1157,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1158,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1159,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1160,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1161,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,0]
[1162,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,0]
[1163,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,0]
[1164,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,0]
[1165,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,0]
[1166,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1167,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1168,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1169,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1170,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1171,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1172,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (03)",4.4620945071616617E-5,0]
[1173,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1174,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1175,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1176,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1177,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1178,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1179,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1180,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1181,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1182,null,"REYNARD-ROYAL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-ROYAL (02)",4.4620945071616617E-5,0]
[1183,null,"REYNARD-ROYAL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-ROYAL (02)",4.4620945071616617E-5,0]
[1184,null,"REYNARD-ROYAL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-ROYAL (02)",4.4620945071616617E-5,0]
[1185,null,"REYNARD-ROYAL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-ROYAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1186,null,"PORTER-DOUGHARTY","NH0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","PORTER-DOUGHARTY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1187,null,"REYNARD-ROYAL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-ROYAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1188,null,"REYNARD-ROYAL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-ROYAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1189,null,"REYNARD-ROYAL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-ROYAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1190,null,"REYNARD-ROYAL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-ROYAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1191,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,0]
[1192,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1193,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1194,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1195,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1196,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1197,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1198,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1199,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1200,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1201,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1202,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1203,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,0]
[1204,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1205,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1206,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1207,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1208,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1209,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1210,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1211,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1212,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1213,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1214,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1215,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1216,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1217,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1218,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",{"$f":"IF(G1219=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1219=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[1219,null,"MUNRO-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","MUNRO-ERSKINE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1220,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","STEELE-STUART (04)",4.4620945071616617E-5,0]
[1221,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1222,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1223,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1224,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1225,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1226,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1227,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WARD-LOUISVILLE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1228,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1229,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1230,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1231,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1232,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1233,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1234,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1235,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1236,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1237,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1238,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1239,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1240,null,"DIAMOND-ROSEHILL","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1241,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (03)",4.4620945071616617E-5,0]
[1242,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (03)",4.4620945071616617E-5,0]
[1243,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (03)",4.4620945071616617E-5,0]
[1244,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (03)",4.4620945071616617E-5,0]
[1245,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1246,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1247,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,0]
[1248,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,0]
[1249,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,0]
[1250,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1251,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1252,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1253,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1254,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1255,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRAHAM-WOODLANDS (01)",4.4620945071616617E-5,0]
[1256,null,"MALMSBURY-WOODBURN","BD0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","MALMSBURY-WOODBURN (02)",0,0]
[1257,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1258,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1259,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1260,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1261,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1262,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1263,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,0]
[1264,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1265,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1266,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1267,null,"SOUDAN-HIGH","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SOUDAN-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1268,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1269,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1270,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1271,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1272,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1273,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1274,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1275,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1276,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1277,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[1278,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1279,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,0]
[1280,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,0]
[1281,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,0]
[1282,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (02)",{"$f":"IF(G1283=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1283=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[1283,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,0]
[1284,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (01)",0,0]
[1285,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WALHALLA-MORELAND (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1286,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (01)",4.4620945071616617E-5,0]
[1287,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (01)",4.4620945071616617E-5,0]
[1288,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (01)",4.4620945071616617E-5,0]
[1289,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (01)",4.4620945071616617E-5,0]
[1290,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (01)",4.4620945071616617E-5,0]
[1291,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (01)",4.4620945071616617E-5,0]
[1292,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (01)",4.4620945071616617E-5,0]
[1293,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (01)",4.4620945071616617E-5,0]
[1294,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (01)",4.4620945071616617E-5,0]
[1295,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (01)",4.4620945071616617E-5,0]
[1296,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARD-LOUISVILLE (01)",4.4620945071616617E-5,0]
[1297,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1298,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1299,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1300,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1301,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1302,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1303,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1304,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1305,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1306,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1307,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1308,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1309,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1310,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1311,null,"WALTHAM-LEE","FT0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","WALTHAM-LEE (01)",0,0]
[1312,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1313,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1314,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1315,null,"COONANS-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COONANS-WOODLANDS (01)",4.4620945071616617E-5,0]
[1316,null,"FINN-HAUGHTON","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","FINN-HAUGHTON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1317,null,"HILLVIEW-PURCHES","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HILLVIEW-PURCHES (02)",4.4620945071616617E-5,0]
[1318,null,"HILLVIEW-PURCHES","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HILLVIEW-PURCHES (02)",4.4620945071616617E-5,0]
[1319,null,"HILLVIEW-PURCHES","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HILLVIEW-PURCHES (02)",4.4620945071616617E-5,0]
[1320,null,"HILLVIEW-PURCHES","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HILLVIEW-PURCHES (02)",4.4620945071616617E-5,0]
[1321,null,"HILLVIEW-PURCHES","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HILLVIEW-PURCHES (02)",4.4620945071616617E-5,0]
[1322,null,"DAISY-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DAISY-BUCKLEY (02)",4.4620945071616617E-5,0]
[1323,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1324,null,"TENNYSON-TYLER","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","TENNYSON-TYLER (01)",4.4620945071616617E-5,0]
[1325,null,"THE BOULEVARD-PARKSTONE","NS0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","THE BOULEVARD-PARKSTONE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1326,null,"THE BOULEVARD-PARKSTONE","NS0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","THE BOULEVARD-PARKSTONE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1327,null,"THE BOULEVARD-PARKSTONE","NS0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","THE BOULEVARD-PARKSTONE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1328,null,"THE BOULEVARD-PARKSTONE","NS0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","THE BOULEVARD-PARKSTONE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1329,null,"THE BOULEVARD-PARKSTONE","NS0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","THE BOULEVARD-PARKSTONE (03)",4.4620945071616617E-5,0]
[1330,null,"THE BOULEVARD-PARKSTONE","NS0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","THE BOULEVARD-PARKSTONE (03)",4.4620945071616617E-5,0]
[1331,null,"THE BOULEVARD-PARKSTONE","NS0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","THE BOULEVARD-PARKSTONE (03)",4.4620945071616617E-5,0]
[1332,null,"THE BOULEVARD-PARKSTONE","NS0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","THE BOULEVARD-PARKSTONE (03)",4.4620945071616617E-5,0]
[1333,null,"RATHCOWN-CHEDDAR","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","RATHCOWN-CHEDDAR (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1334,null,"LOCH-REYNARDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LOCH-REYNARDS (02)",4.4620945071616617E-5,0]
[1335,null,"LOCH-REYNARDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LOCH-REYNARDS (02)",4.4620945071616617E-5,0]
[1336,null,"LOCH-REYNARDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LOCH-REYNARDS (02)",4.4620945071616617E-5,0]
[1337,null,"LOCH-REYNARDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LOCH-REYNARDS (02)",4.4620945071616617E-5,0]
[1338,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DEAKIN-BERRY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1339,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DEAKIN-BERRY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1340,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (02)",4.4620945071616617E-5,0]
[1341,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,0]
[1342,null,"MELTON HWY-P2","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","MELTON HWY-P2 (02)",4.4620945071616617E-5,0]
[1343,null,"CONIFER-PRIMULA","FW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CONIFER-PRIMULA (03)",4.4620945071616617E-5,0]
[1344,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DEAKIN-BERRY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1345,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (02)",4.4620945071616617E-5,0]
[1346,null,"OMAR-MITCHELL","BY0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","OMAR-MITCHELL (02)",{"$f":"IF(G1347=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1347=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[1347,null,"RAVENSCOURT-FULHAM","FF0-083","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",0,0]
[1348,null,"BELL-ORIEL","EP0-041","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","BELL-ORIEL (01)",0,0]
[1349,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MARGTMARY-MURRAY (03)",4.4620945071616617E-5,0]
[1350,null,"YARRA-DOVER","NT0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","YARRA-DOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1351,null,"WARD-LOUISVILLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WARD-LOUISVILLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1352,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (01)",4.4620945071616617E-5,0]
[1353,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,0]
[1354,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1355,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1356,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1357,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1358,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1359,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1360,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1361,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1362,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1363,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1364,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,0]
[1365,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,0]
[1366,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,0]
[1367,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,0]
[1368,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,0]
[1369,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,0]
[1370,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,0]
[1371,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1372,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,0]
[1373,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,0]
[1374,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,0]
[1375,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1376,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1377,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1378,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1379,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1380,null,"DOLE-LOCHER","TT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","DOLE-LOCHER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1381,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1382,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1383,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1384,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1385,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1386,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1387,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,0]
[1388,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1389,null,"SHEFFIELD-COBURG","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SHEFFIELD-COBURG (03)",4.4620945071616617E-5,0]
[1390,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (01)",4.4620945071616617E-5,0]
[1391,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (01)",4.4620945071616617E-5,0]
[1392,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (01)",4.4620945071616617E-5,0]
[1393,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (01)",4.4620945071616617E-5,0]
[1394,null,"CREVILLI-SUMMERHILL","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CREVILLI-SUMMERHILL (01)",4.4620945071616617E-5,0]
[1395,null,"BLIBURG-SUNSET","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","BLIBURG-SUNSET (02)",0,0]
[1396,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (01)",4.4620945071616617E-5,0]
[1397,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (01)",4.4620945071616617E-5,0]
[1398,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (02)",4.4620945071616617E-5,0]
[1399,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (02)",4.4620945071616617E-5,0]
[1400,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (02)",4.4620945071616617E-5,0]
[1401,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (02)",4.4620945071616617E-5,0]
[1402,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (02)",4.4620945071616617E-5,0]
[1403,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (02)",4.4620945071616617E-5,0]
[1404,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (02)",4.4620945071616617E-5,0]
[1405,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (02)",4.4620945071616617E-5,0]
[1406,null,"JEFFREY-WESTGARTH","FF0-089","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (03)",0,0]
[1407,null,"SHEFFIELD-COBURG","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SHEFFIELD-COBURG (03)",4.4620945071616617E-5,0]
[1408,null,"SHEFFIELD-COBURG","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SHEFFIELD-COBURG (03)",4.4620945071616617E-5,0]
[1409,null,"SHEFFIELD-COBURG","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHEFFIELD-COBURG (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1410,null,"SHEFFIELD-COBURG","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHEFFIELD-COBURG (03)",{"$f":"IF(G1411=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1411=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[1411,null,"GLADSTONE-HARDING","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GLADSTONE-HARDING (01)",4.4620945071616617E-5,0]
[1412,null,"ARBOR-HEIDELBERG","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","ARBOR-HEIDELBERG (01)",4.4620945071616617E-5,0]
[1413,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,0]
[1414,null,"EAST-THACKERAY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","EAST-THACKERAY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1415,null,"SYDNEY-ROSSHIRE","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","SYDNEY-ROSSHIRE (01)",4.4620945071616617E-5,0]
[1416,null,"MCIVOR-KIEWA","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","MCIVOR-KIEWA (02)",4.4620945071616617E-5,0]
[1417,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,0]
[1418,null,"THE BOULEVARD-NEVILLE","HB0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","THE BOULEVARD-NEVILLE (01)",4.4620945071616617E-5,0]
[1419,null,"ALVA-URQUHART","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","ALVA-URQUHART (02)",4.4620945071616617E-5,0]
[1420,null,"ALVA-URQUHART","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","ALVA-URQUHART (02)",4.4620945071616617E-5,0]
[1421,null,"ALVA-URQUHART","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","ALVA-URQUHART (02)",4.4620945071616617E-5,0]
[1422,null,"EAST-EXETER","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","EAST-EXETER (01)",4.4620945071616617E-5,0]
[1423,null,"ETKA-MARK","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","ETKA-MARK (03)",4.4620945071616617E-5,0]
[1424,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1425,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1426,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1427,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1428,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1429,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1430,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1431,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1432,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1433,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1434,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1435,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1436,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1437,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1438,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1439,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1440,null,"HUTCHINSON-NICHOLSON","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUTCHINSON-NICHOLSON (01)",4.4620945071616617E-5,0]
[1441,null,"BULLA-DUBLIN","ES0-025","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BULLA-DUBLIN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1442,null,"HILLVIEW DR-P3","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","Y","N","SBY","HILLVIEW DR-P3 (00)",0,0]
[1443,null,"MCCOLL-MALPAS","PTN-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","MCCOLL-MALPAS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1444,null,"DEANS-SYDNEY","CS0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEANS-SYDNEY (01)",4.4620945071616617E-5,0]
[1445,null,"STEVEDORE-STRAND","NT0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","STEVEDORE-STRAND (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1446,null,"ERIC-ADA","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","McGOWAN-MURRAY (02)",4.4620945071616617E-5,0]
[1447,null,"ERIC-ADA","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","McGOWAN-MURRAY (02)",4.4620945071616617E-5,0]
[1448,null,"ERIC-ADA","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","McGOWAN-MURRAY (02)",4.4620945071616617E-5,0]
[1449,null,"ERIC-ADA","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","McGOWAN-MURRAY (02)",4.4620945071616617E-5,0]
[1450,null,"ERIC-ADA","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","McGOWAN-MURRAY (02)",4.4620945071616617E-5,0]
[1451,null,"ERIC-ADA","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","McGOWAN-MURRAY (03)",4.4620945071616617E-5,0]
[1452,null,"SYDNEY-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SYDNEY-MURRAY (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[1453,null,"SYDNEY-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SYDNEY-MURRAY (04)",4.4620945071616617E-5,0]
[1454,null,"SYDNEY-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SYDNEY-MURRAY (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[1455,null,"SYDNEY-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SYDNEY-MURRAY (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[1456,null,"SYDNEY-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SYDNEY-MURRAY (04)",4.4620945071616617E-5,0]
[1457,null,"SYDNEY-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SYDNEY-MURRAY (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[1458,null,"SYDNEY-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SYDNEY-MURRAY (04)",4.4620945071616617E-5,0]
[1459,null,"SYDNEY-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SYDNEY-MURRAY (04)",4.4620945071616617E-5,0]
[1460,null,"SYDNEY-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SYDNEY-MURRAY (04)",4.4620945071616617E-5,0]
[1461,null,"HEATHCOTE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HEATHCOTE-KENT (02)",4.4620945071616617E-5,0]
[1462,null,"HILLSIDE-HURTLE","ES0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","HILLSIDE-HURTLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1463,null,"GILBANK-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","GILBANK-GILBERT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1464,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,0]
[1465,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,0]
[1466,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,0]
[1467,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,0]
[1468,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1469,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1470,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1471,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1472,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1473,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1474,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",{"$f":"IF(G1475=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1475=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[1475,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1476,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1477,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1478,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1479,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1480,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1481,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1482,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,0]
[1483,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,0]
[1484,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,0]
[1485,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,0]
[1486,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,0]
[1487,null,"MALACCA-WATERDALE","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","MALACCA-WATERDALE (03)",0,0]
[1488,null,"GOLEEN-SYDNEY","CN0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","CN0","GOLEEN-SYDNEY (03)",0,0]
[1489,null,"GOLEEN-SYDNEY","CN0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","CN0","GOLEEN-SYDNEY (03)",0,0]
[1490,null,"GOLEEN-SYDNEY","CN0-002","2025-02-02","2025-02-08","N","Y","N","Y","N","N","CN0","GOLEEN-SYDNEY (03)",0,9.4304036212749905E-5]
[1491,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,0]
[1492,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,0]
[1493,null,"GOLEEN-SYDNEY","CN0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","CN0","GOLEEN-SYDNEY (03)",0,0]
[1494,null,"GOLEEN-SYDNEY","CN0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","CN0","GOLEEN-SYDNEY (03)",0,0]
[1495,null,"SYMONS-GILBERT","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","SYMONS-GILBERT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[1496,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1497,null,"BRADLEY-MASON","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BRADLEY-MASON (01)",4.4620945071616617E-5,0]
[1498,null,"MANLY-MATHIESON","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MANLY-MATHIESON (02)",4.4620945071616617E-5,0]
[1499,null,"MATHIESON-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MATHIESON-SYDNEY (04)",4.4620945071616617E-5,0]
[1500,null,"MATHIESON-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MATHIESON-SYDNEY (04)",4.4620945071616617E-5,0]
[1501,null,"MATHIESON-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MATHIESON-SYDNEY (04)",4.4620945071616617E-5,0]
[1502,null,"MATHIESON-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MATHIESON-SYDNEY (04)",4.4620945071616617E-5,0]
[1503,null,"MATHIESON-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MATHIESON-SYDNEY (04)",4.4620945071616617E-5,0]
[1504,null,"MATHIESON-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MATHIESON-SYDNEY (04)",4.4620945071616617E-5,0]
[1505,null,"MATHIESON-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MATHIESON-SYDNEY (04)",4.4620945071616617E-5,0]
[1506,null,"MATHIESON-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MATHIESON-SYDNEY (04)",4.4620945071616617E-5,0]
[1507,null,"JACKA-JOYNT","NH0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","JACKA-JOYNT (01)",4.4620945071616617E-5,0]
[1508,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,0]
[1509,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1510,null,"PETERSON-JACKSON","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","PETERSON-JACKSON (01)",4.4620945071616617E-5,0]
[1511,null,"HAWDON-BROWN","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","HAWDON-BROWN (01)",4.4620945071616617E-5,0]
[1512,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1513,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1514,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1515,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1516,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1517,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1518,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1519,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1520,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1521,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1522,null,"CARR-NEWLANDS","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","CARR-NEWLANDS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1523,null,"MORRIS-MCMAHONS","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MORRIS-MCMAHONS (01)",4.4620945071616617E-5,0]
[1524,null,"MORRIS-MCMAHONS","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MORRIS-MCMAHONS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1525,null,"MORRIS-MCMAHONS","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MORRIS-MCMAHONS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1526,null,"MORRIS-MCMAHONS","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MORRIS-MCMAHONS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1527,null,"MORRIS-MCMAHONS","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MORRIS-MCMAHONS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1528,null,"MORRIS-MCMAHONS","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MORRIS-MCMAHONS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1529,null,"MORRIS-MCMAHONS","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MORRIS-MCMAHONS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1530,null,"MORRIS-MCMAHONS","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MORRIS-MCMAHONS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1531,null,"MORRIS-MCMAHONS","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MORRIS-MCMAHONS (02)",4.4620945071616617E-5,0]
[1532,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1533,null,"CARR-NEWLANDS","CS0-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","CS0","CARR-NEWLANDS (02)",0,0]
[1534,null,"CARR-NEWLANDS","CS0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SHORE-MCMAHONS (03)",4.4620945071616617E-5,0]
[1535,null,"CARR-NEWLANDS","CS0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SHORE-MCMAHONS (03)",4.4620945071616617E-5,0]
[1536,null,"CARR-NEWLANDS","CS0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SHORE-MCMAHONS (03)",4.4620945071616617E-5,0]
[1537,null,"MORRIS-MCMAHONS","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MORRIS-MCMAHONS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1538,null,"DARLING-FULHAM","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","DARLING-FULHAM (01)",{"$f":"IF(G1539=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1539=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[1539,null,"HOME-WILKINSON","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","HOME-WILKINSON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1540,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1541,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1542,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1543,null,"NEWLANDS-MURRAY","CS0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","NEWLANDS-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1544,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1545,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","McGOWAN-MURRAY (03)",4.4620945071616617E-5,0]
[1546,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MALCOLM-ELIZABETH (02)",4.4620945071616617E-5,0]
[1547,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (04)",4.4620945071616617E-5,0]
[1548,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (04)",4.4620945071616617E-5,0]
[1549,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (04)",4.4620945071616617E-5,0]
[1550,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (04)",4.4620945071616617E-5,0]
[1551,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (04)",4.4620945071616617E-5,0]
[1552,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (04)",4.4620945071616617E-5,0]
[1553,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (04)",4.4620945071616617E-5,0]
[1554,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1555,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1556,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1557,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1558,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1559,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1560,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1561,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1562,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1563,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1564,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1565,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1566,null,"GOFF-ELIZABETH","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GOFF-ELIZABETH (02)",4.4620945071616617E-5,0]
[1567,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1568,null,"THE CROSSWAY-VISTA","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","THE CROSSWAY-VISTA (03)",4.4620945071616617E-5,0]
[1569,null,"MOASCAR-GALLIPOLI","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MOASCAR-GALLIPOLI (02)",4.4620945071616617E-5,0]
[1570,null,"PRESTON-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PRESTON-MUNRO (02)",4.4620945071616617E-5,0]
[1571,null,"GILBANK-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","GILBANK-GILBERT (01)",4.4620945071616617E-5,0]
[1572,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (02)",4.4620945071616617E-5,0]
[1573,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (02)",4.4620945071616617E-5,0]
[1574,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (02)",4.4620945071616617E-5,0]
[1575,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (02)",4.4620945071616617E-5,0]
[1576,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (02)",4.4620945071616617E-5,0]
[1577,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1578,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1579,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[1580,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[1581,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[1582,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[1583,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,0]
[1584,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,0]
[1585,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,0]
[1586,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,0]
[1587,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,0]
[1588,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[1589,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[1590,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[1591,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[1592,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1593,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1594,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1595,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1596,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1597,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1598,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1599,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1600,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1601,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1602,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BAXTER-SYDNEY (03)",{"$f":"IF(G1603=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1603=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[1603,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1604,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1605,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1606,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1607,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1608,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","CS0","BAXTER-SYDNEY (03)",0,0]
[1609,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1610,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","CS0","BAXTER-SYDNEY (03)",0,0]
[1611,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1612,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1613,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1614,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1615,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1616,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1617,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1618,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1619,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1620,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","CS0","BAXTER-SYDNEY (03)",0,0]
[1621,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1622,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1623,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1624,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1625,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1626,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1627,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1628,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1629,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1630,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1631,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1632,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1633,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1634,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1635,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1636,null,"STIRLING-GLENCAIRN","COO-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","COO","STIRLING-GLENCAIRN (01)",0,0]
[1637,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1638,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1639,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[1640,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1641,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1642,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","CS0","BAXTER-SYDNEY (03)",0,0]
[1643,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",0,0]
[1644,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,0]
[1645,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,0]
[1646,null,"HUNT-BAXTER","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HUNT-BAXTER (05)",4.4620945071616617E-5,0]
[1647,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1648,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1649,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,0]
[1650,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,0]
[1651,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,0]
[1652,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1653,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1654,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[1655,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1656,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[1657,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[1658,null,"TONKIN-SUSSEX","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","TONKIN-SUSSEX (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1659,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1660,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1661,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[1662,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1663,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1664,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[1665,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[1666,null,"BOLDREWOOD-McMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","BOLDREWOOD-McMAHON (02)",{"$f":"IF(G1667=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1667=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[1667,null,"THISTLE-MT ALEXANDER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (01)",0,0]
[1668,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1669,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1670,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1671,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1672,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1673,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1674,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1675,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1676,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1677,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1678,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1679,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,0]
[1680,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,0]
[1681,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,0]
[1682,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,0]
[1683,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,0]
[1684,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1685,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1686,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1687,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[1688,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[1689,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[1690,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[1691,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[1692,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[1693,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[1694,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[1695,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[1696,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[1697,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[1698,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (01)",4.4620945071616617E-5,0]
[1699,null,"GREENSBOROUGH-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GREENSBOROUGH-YALLAMBIE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[1700,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,0]
[1701,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1702,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,0]
[1703,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1704,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,0]
[1705,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1706,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,0]
[1707,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,0]
[1708,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (02)",4.4620945071616617E-5,0]
[1709,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1710,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1711,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1712,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1713,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1714,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1715,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1716,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1717,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1718,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1719,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1720,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1721,null,"HOBSON-HOME","NT0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","HOBSON-HOME (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1722,null,"PRESTON-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PRESTON-MUNRO (02)",4.4620945071616617E-5,0]
[1723,null,"PRESTON-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PRESTON-MUNRO (02)",4.4620945071616617E-5,0]
[1724,null,"PRESTON-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PRESTON-MUNRO (02)",4.4620945071616617E-5,0]
[1725,null,"PRESTON-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PRESTON-MUNRO (02)",4.4620945071616617E-5,0]
[1726,null,"PRESTON-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PRESTON-MUNRO (02)",4.4620945071616617E-5,0]
[1727,null,"PRESTON-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PRESTON-MUNRO (02)",4.4620945071616617E-5,0]
[1728,null,"QUEEN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","QUEEN-REYNARD (02)",4.4620945071616617E-5,0]
[1729,null,"QUEEN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","QUEEN-REYNARD (02)",4.4620945071616617E-5,0]
[1730,null,"QUEEN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","QUEEN-REYNARD (02)",{"$f":"IF(G1731=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1731=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[1731,null,"QUEEN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","QUEEN-REYNARD (02)",4.4620945071616617E-5,0]
[1732,null,"QUEEN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","QUEEN-REYNARD (02)",4.4620945071616617E-5,0]
[1733,null,"QUEEN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","QUEEN-REYNARD (02)",4.4620945071616617E-5,0]
[1734,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,0]
[1735,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1736,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1737,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","CS0","PORTLAND-MUNRO (01)",0,0]
[1738,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1739,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1740,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1741,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1742,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1743,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1744,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1745,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1746,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,0]
[1747,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,0]
[1748,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1749,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1750,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1751,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1752,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1753,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1754,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,0]
[1755,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,0]
[1756,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,0]
[1757,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,0]
[1758,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,0]
[1759,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,0]
[1760,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,0]
[1761,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,0]
[1762,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1763,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1764,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1765,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1766,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1767,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1768,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1769,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1770,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1771,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1772,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1773,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1774,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1775,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1776,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1777,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1778,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1779,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1780,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1781,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1782,null,"PORTLAND-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PORTLAND-MUNRO (01)",4.4620945071616617E-5,0]
[1783,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1784,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1785,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1786,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1787,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1788,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1789,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1790,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[1791,null,"BRUCE-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BRUCE-REYNARD (01)",4.4620945071616617E-5,0]
[1792,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[1793,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1794,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",{"$f":"IF(G1795=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1795=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[1795,null,"GORDON-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GORDON-BELL (02)",4.4620945071616617E-5,0]
[1796,null,"GORDON-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GORDON-BELL (02)",4.4620945071616617E-5,0]
[1797,null,"GORDON-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GORDON-BELL (02)",4.4620945071616617E-5,0]
[1798,null,"GORDON-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GORDON-BELL (02)",4.4620945071616617E-5,0]
[1799,null,"GORDON-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GORDON-BELL (02)",4.4620945071616617E-5,0]
[1800,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1801,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1802,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1803,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1804,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1805,null,"BRUCE-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BRUCE-REYNARD (01)",4.4620945071616617E-5,0]
[1806,null,"BRUCE-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BRUCE-REYNARD (01)",4.4620945071616617E-5,0]
[1807,null,"BRUCE-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BRUCE-REYNARD (01)",4.4620945071616617E-5,0]
[1808,null,"BRUCE-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BRUCE-REYNARD (01)",4.4620945071616617E-5,0]
[1809,null,"BRUCE-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BRUCE-REYNARD (01)",4.4620945071616617E-5,0]
[1810,null,"BRUCE-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BRUCE-REYNARD (01)",4.4620945071616617E-5,0]
[1811,null,"JUKES-BONWICK","CN0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","JUKES-BONWICK (01)",4.4620945071616617E-5,0]
[1812,null,"BRUCE-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BRUCE-REYNARD (02)",4.4620945071616617E-5,0]
[1813,null,null,null,"2025-02-02","2025-02-08","Y","N","N","N","N","N",null,null,4.4620945071616617E-5,0]
[1814,null,"BRUCE-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BRUCE-REYNARD (02)",4.4620945071616617E-5,0]
[1815,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,0]
[1816,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,0]
[1817,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,0]
[1818,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,0]
[1819,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1820,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,0]
[1821,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,0]
[1822,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,0]
[1823,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,0]
[1824,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1825,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1826,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1827,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1828,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1829,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,0]
[1830,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1831,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1832,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1833,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1834,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1835,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1836,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1837,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1838,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1839,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1840,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1841,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1842,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1843,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1844,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1845,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,0]
[1846,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,0]
[1847,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,0]
[1848,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1849,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1850,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1851,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,0]
[1852,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,0]
[1853,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1854,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1855,null,"BAMFIELD-COLLINS","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","BAMFIELD-COLLINS (02)",4.4620945071616617E-5,0]
[1856,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[1857,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[1858,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (04)",{"$f":"IF(G1859=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1859=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[1859,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1860,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1861,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1862,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1863,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1864,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1865,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1866,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1867,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1868,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1869,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1870,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1871,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1872,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1873,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1874,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1875,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1876,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1877,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1878,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1879,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1880,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1881,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1882,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1883,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1884,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1885,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1886,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1887,null,"REYNARD-SPRINGHALL","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-SPRINGHALL (02)",4.4620945071616617E-5,0]
[1888,null,"HILLVIEW-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HILLVIEW-REYNARD (02)",4.4620945071616617E-5,0]
[1889,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1890,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1891,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1892,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1893,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1894,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1895,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1896,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1897,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1898,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1899,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1900,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1901,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1902,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1903,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1904,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1905,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1906,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1907,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1908,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1909,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1910,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1911,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1912,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1913,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1914,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1915,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,0]
[1916,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1917,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1918,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1919,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1920,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1921,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,0]
[1922,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (02)",{"$f":"IF(G1923=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1923=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[1923,null,"THISTLE-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","THISTLE-HACKETT (04)",4.4620945071616617E-5,0]
[1924,null,"THISTLE-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","THISTLE-HACKETT (04)",4.4620945071616617E-5,0]
[1925,null,"THISTLE-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","THISTLE-HACKETT (04)",4.4620945071616617E-5,0]
[1926,null,"THISTLE-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","THISTLE-HACKETT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[1927,null,"THISTLE-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","THISTLE-HACKETT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[1928,null,"THISTLE-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","THISTLE-HACKETT (04)",4.4620945071616617E-5,0]
[1929,null,"MOASCAR-GALLIPOLI","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MOASCAR-GALLIPOLI (02)",4.4620945071616617E-5,0]
[1930,null,"MOASCAR-GALLIPOLI","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MOASCAR-GALLIPOLI (02)",4.4620945071616617E-5,0]
[1931,null,"MOASCAR-GALLIPOLI","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MOASCAR-GALLIPOLI (02)",4.4620945071616617E-5,0]
[1932,null,"MOASCAR-GALLIPOLI","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MOASCAR-GALLIPOLI (02)",4.4620945071616617E-5,0]
[1933,null,"MOASCAR-GALLIPOLI","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MOASCAR-GALLIPOLI (02)",4.4620945071616617E-5,0]
[1934,null,"MOASCAR-GALLIPOLI","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MOASCAR-GALLIPOLI (02)",4.4620945071616617E-5,0]
[1935,null,"REGENT-HIGH","PTN-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","REGENT-HIGH (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1936,null,"ALEXANDRA-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ALEXANDRA-LANDELLS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1937,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,0]
[1938,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,0]
[1939,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1940,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,0]
[1941,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1942,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1943,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1944,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1945,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1946,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1947,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,0]
[1948,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1949,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1950,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1951,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1952,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1953,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,0]
[1954,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,0]
[1955,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,0]
[1956,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,0]
[1957,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,0]
[1958,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,0]
[1959,null,"MAHONEYS-KATHRYN","BMS-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","BMS","MAHONEYS-KATHRYN (02)",4.4620945071616617E-5,0]
[1960,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[1961,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1962,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1963,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1964,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1965,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1966,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1967,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1968,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1969,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1970,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1971,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[1972,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SHACKELL-BELL (03)",4.4620945071616617E-5,0]
[1973,null,"CANTALA-MCCRAE","NH0-008","2025-02-02","2025-02-08","N","N","N","Y","N","N","NH0","CANTALA-MCCRAE (04)",0,9.4304036212749905E-5]
[1974,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SHACKELL-BELL (02)",4.4620945071616617E-5,0]
[1975,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SHACKELL-BELL (02)",4.4620945071616617E-5,0]
[1976,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SHACKELL-BELL (02)",4.4620945071616617E-5,0]
[1977,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SHACKELL-BELL (02)",4.4620945071616617E-5,0]
[1978,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","SHACKELL-BELL (02)",4.4620945071616617E-5,0]
[1979,null,"PRESTON-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PRESTON-MUNRO (03)",4.4620945071616617E-5,0]
[1980,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1981,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1982,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1983,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1984,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1985,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1986,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","WATT-THE AVENUE (01)",{"$f":"IF(G1987=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J1987=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[1987,null,"VINCENT-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","VINCENT-BELL (04)",4.4620945071616617E-5,0]
[1988,null,"VINCENT-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","VINCENT-BELL (04)",4.4620945071616617E-5,0]
[1989,null,"VINCENT-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","VINCENT-BELL (04)",4.4620945071616617E-5,0]
[1990,null,"VINCENT-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","VINCENT-BELL (04)",4.4620945071616617E-5,0]
[1991,null,"VINCENT-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","VINCENT-BELL (04)",4.4620945071616617E-5,0]
[1992,null,"VINCENT-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","VINCENT-BELL (04)",4.4620945071616617E-5,0]
[1993,null,"VINCENT-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","VINCENT-BELL (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[1994,null,"VINCENT-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","VINCENT-BELL (04)",4.4620945071616617E-5,0]
[1995,null,"BOSQUET-BALLARAT","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","BOSQUET-BALLARAT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1996,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1997,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1998,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[1999,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2009,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[2023,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[2030,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[2046,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (01)",4.4620945071616617E-5,0]
[2053,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2066,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2088,null,"VINCENT-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","VINCENT-BELL (04)",4.4620945071616617E-5,0]
[2095,null,"SHACKELL-BELL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SHACKELL-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2111,null,"BOLINGBROKE-BURGUNDY","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BOLINGBROKE-BURGUNDY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2118,null,"DAVERN-O'HEA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DAVERN-O'HEA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2138,null,"GREENWOOD-O'HEA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GREENWOOD-O'HEA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2149,null,"GREENWOOD-O'HEA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GREENWOOD-O'HEA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2160,null,"WARATAH-DERBY","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WARATAH-DERBY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2167,null,"GREENWOOD-O'HEA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GREENWOOD-O'HEA (02)",4.4620945071616617E-5,0]
[2183,null,"O'HEA-CUMBERLAND","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","O'HEA-CUMBERLAND (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[2203,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2206,null,"SOUDAN-HIGH","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SOUDAN-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2228,null,"SOUDAN-HIGH","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SOUDAN-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2232,null,"SOUDAN-HIGH","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SOUDAN-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2248,null,"WILSON-GILMOUR","CS0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WILSON-GILMOUR (01)",4.4620945071616617E-5,0]
[2268,null,"MCDONALD-GAFFNEY","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MCDONALD-GAFFNEY (01)",4.4620945071616617E-5,0]
[2271,null,"LEWIS-WILLIAMS","CS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEWIS-WILLIAMS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2291,null,"LEWIS-WILLIAMS","CS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEWIS-WILLIAMS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2295,null,"LEWIS-WILLIAMS","CS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEWIS-WILLIAMS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2313,null,"HOLROYD-O'HEA","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","HOLROYD-O'HEA (03)",4.4620945071616617E-5,0]
[2320,null,"HOLROYD-O'HEA","CS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HOLROYD-O'HEA (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[2340,null,"BICENTENNIAL-SHABA","BD0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","BICENTENNIAL-SHABA (02)",0,0]
[2356,null,"NOVIAN-MARAMA","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","NOVIAN-MARAMA (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[2364,null,"NOVIAN-MARAMA","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","NOVIAN-MARAMA (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[2378,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,0]
[2385,null,"O'HEA-CUMBERLAND","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","O'HEA-CUMBERLAND (02)",4.4620945071616617E-5,0]
[2405,null,"OWEN-GORDON","FE0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","OWEN-GORDON (01)",0,0]
[2421,null,"PETERSON-JACKSON","CN0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","CN0","PETERSON-JACKSON (01)",0,0]
[2428,null,"MCCOLL-MALPAS","PTN-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","MCCOLL-MALPAS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2443,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","McGOWAN-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2450,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","McGOWAN-MURRAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2470,null,"FOCH-TYLER","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",0,0]
[2486,null,"LIVINGSTONE-ELIZABETH","CN0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","CN0","LIVINGSTONE-ELIZABETH (01)",0,0]
[2493,null,"ARTHUR-ELIZABETH","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ARTHUR-ELIZABETH (03)",4.4620945071616617E-5,0]
[2500,null,"ARTHUR-ELIZABETH","CN0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ARTHUR-ELIZABETH (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2514,null,"ARTHUR-ELIZABETH","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ARTHUR-ELIZABETH (01)",4.4620945071616617E-5,0]
[2535,null,"RILL-OLIVE","NH0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","RILL-OLIVE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2538,null,"MANLY-MATHIESON","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MANLY-MATHIESON (02)",4.4620945071616617E-5,0]
[2558,null,"WEBB-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-QUEENSVILLE (01)",4.4620945071616617E-5,0]
[2565,null,"DAVERN-O'HEA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DAVERN-O'HEA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2581,null,"ANDERSON-BOLINGBROKE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","ANDERSON-BOLINGBROKE (02)",4.4620945071616617E-5,0]
[2593,null,"ANDERSON-BOLINGBROKE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","ANDERSON-BOLINGBROKE (01)",4.4620945071616617E-5,0]
[2607,null,"JOHNSON-BENAUD","BD0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","JOHNSON-BENAUD (04)",0,0]
[2623,null,"FERGUSON-TOWNHALL","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","FERGUSON-TOWNHALL (01)",4.4620945071616617E-5,0]
[2630,null,"TONKIN-MASHOOBRA","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","TONKIN-MASHOOBRA (01)",4.4620945071616617E-5,0]
[2646,null,"TONKIN-MASHOOBRA","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","TONKIN-MASHOOBRA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2666,null,"TONKIN-SUSSEX","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","TONKIN-SUSSEX (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[2672,null,"ALEXANDRA-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ALEXANDRA-LANDELLS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2688,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","SOUTH-DERBY (02)",4.4620945071616617E-5,0]
[2695,null,"ALBION-GEELONG","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ALBION-GEELONG (01)",4.4620945071616617E-5,0]
[2711,null,"CUMBERLAND-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CUMBERLAND-KENT (04)",4.4620945071616617E-5,0]
[2718,null,"DORSET-DERBY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DORSET-DERBY (02)",4.4620945071616617E-5,0]
[2741,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ESSEX-LANDELLS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2753,null,"ATTERCLIFFE-DERBY","CS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","ATTERCLIFFE-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[2760,null,"ATTERCLIFFE-DERBY","CS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","ATTERCLIFFE-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[2780,null,"ATTERCLIFFE-DERBY","CS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","ATTERCLIFFE-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[2783,null,"GRANDVIEW-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GRANDVIEW-HOLMES (03)",4.4620945071616617E-5,0]
[2803,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ESSEX-LANDELLS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2812,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ESSEX-LANDELLS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2825,null,"PEEL-DOUGLAS","NT0-004","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","PEEL-DOUGLAS (02)",4.4620945071616617E-5,0]
[2845,null,"ALEXANDRA-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ALEXANDRA-LANDELLS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2848,null,"HEATHCOTE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HEATHCOTE-KENT (01)",4.4620945071616617E-5,0]
[2868,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",4.4620945071616617E-5,0]
[2875,null,"IRVINE-GAFFNEY","CS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","IRVINE-GAFFNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[2891,null,"OLIVE-SYLVAN","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","OLIVE-SYLVAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2897,null,"OLIVE-SYLVAN","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","OLIVE-SYLVAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[2913,null,"LANDELLS-MARTIN","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","LANDELLS-MARTIN (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[2933,null,"CUMBERLAND-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CUMBERLAND-KENT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[2940,null,"CUMBERLAND-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CUMBERLAND-KENT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[2956,null,"ALEXANDRA-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ALEXANDRA-LANDELLS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2970,null,"ALEXANDRA-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ALEXANDRA-LANDELLS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2978,null,"ALEXANDRA-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ALEXANDRA-LANDELLS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[2998,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3005,null,"CAMDON-NORTON","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CAMDON-NORTON (02)",4.4620945071616617E-5,0]
[3021,null,"CAMDON-NORTON","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","CAMDON-NORTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3028,null,"CAMDON-NORTON","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CAMDON-NORTON (01)",4.4620945071616617E-5,0]
[3049,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (03)",4.4620945071616617E-5,0]
[3063,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (02)",4.4620945071616617E-5,0]
[3070,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (02)",4.4620945071616617E-5,0]
[3086,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[3093,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3106,null,"CORNWALL-HIGH SCHOOL","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[3115,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,0]
[3135,null,"JOFFRE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","JOFFRE-KENT (02)",4.4620945071616617E-5,0]
[3142,null,"SHERWOOD-THORESBY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","SHERWOOD-THORESBY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[3158,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,0]
[3178,null,"KINGSTON-COLLINSON","TMA-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TMA","KINGSTON-COLLINSON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[3189,null,"QUEEN-RUSSELL","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","QUEEN-RUSSELL (03)",4.4620945071616617E-5,0]
[3200,null,"MCDONALD-GAFFNEY","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MCDONALD-GAFFNEY (01)",4.4620945071616617E-5,0]
[3207,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[3223,null,"FREIGHT-CUSTOM","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (02)",0,0]
[3243,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3246,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[3268,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","WATT-THE AVENUE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3272,null,"ROSENTHAL-ALLENBY","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",4.4620945071616617E-5,0]
[3288,null,"ESSEX-SWAN","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","ESSEX-SWAN (01)",0,0]
[3295,null,"ALMA-PALMERSTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[3315,null,"ASHLEY-CENTRAL WEST NO.1","TH0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TH0","ASHLEY-CENTRAL WEST NO.1 (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[3331,null,"CLARKE-RUPERT","FW0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CLARKE-RUPERT (01)",4.4620945071616617E-5,0]
[3335,null,"RUSSELL-BARKLY","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","RUSSELL-BARKLY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[3353,null,"SUFFOLK-DONGOLA","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","SUFFOLK-DONGOLA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3360,null,"ARGYLE-BROAD","FW0-016","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","ARGYLE-BROAD (01)",0,0]
[3380,null,"ARGYLE-BROAD","FW0-016","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","ARGYLE-BROAD (01)",0,0]
[3396,null,"ASHLEY-NAPOLEON","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",0,0]
[3403,null,"BLANDFORD-ESSEX","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","BLANDFORD-ESSEX (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3418,null,"BLANDFORD-ESSEX","FW0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","BLANDFORD-ESSEX (03)",4.4620945071616617E-5,0]
[3425,null,"MITCHELL-ROWE","BY0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","MITCHELL-ROWE (01)",4.4620945071616617E-5,0]
[3445,null,"ASHLEY-NAPOLEON","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",0,0]
[3461,null,"RUSSELL-BARKLY","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","RUSSELL-BARKLY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[3468,null,"ESSEX-SWAN","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","ESSEX-SWAN (02)",0,0]
[3483,null,"ESSEX-DUDLEY","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ESSEX-DUDLEY (03)",4.4620945071616617E-5,0]
[3490,null,"SOUDAN-ESSEX","FW0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","SOUDAN-ESSEX (01)",4.4620945071616617E-5,0]
[3510,null,"ALMA-PALMERSTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[3513,null,"RICHELIEU-ESSEX","FW0-016","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","FW0","RICHELIEU-ESSEX (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3533,null,"CRESWICK-LATROBE","FE0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","CRESWICK-LATROBE (01)",0,0]
[3540,null,"CENTRAL-GEELONG","FE0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","CENTRAL-GEELONG (02)",0,0]
[3554,null,"OWEN-GORDON","FE0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","OWEN-GORDON (01)",0,0]
[3575,null,"RYAN-MOORE","FE0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","RYAN-MOORE (02)",0,0]
[3582,null,"ALEXANDER-JOHN","FE0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","FE0","DICKSON-WILLIAMSTOWN (03)",4.4620945071616617E-5,0]
[3598,null,"STATION-GAMON","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","STATION-GAMON (02)",0,0]
[3605,null,"HOBBS-PENTLAND","FE0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",0,0]
[3621,null,"HOBBS-PENTLAND","FE0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",0,0]
[3633,null,"STEPHEN-PRINCESS","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (02)",0,0]
[3647,null,"BEATRICE-FEHON","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","BEATRICE-FEHON (02)",0,0]
[3663,null,"HAMILTON-O'FARRELL","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",0,0]
[3670,null,"O'FARRELL-WILLIAMSTOWN","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","O'FARRELL-WILLIAMSTOWN (01)",0,0]
[3686,null,"LENNOX-HYDE","FE0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","LENNOX-HYDE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[3693,null,"FEHON-ANDERSON","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","FEHON-ANDERSON (01)",0,0]
[3712,null,"STEPHEN-PRINCESS","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (01)",0,0]
[3728,null,"LENNOX-HYDE","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","LENNOX-HYDE (03)",0,0]
[3735,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3755,null,"NEYLON-ROBERTS","FW0-017","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","NEYLON-ROBERTS (02)",0,0]
[3758,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3778,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",{"$f":"IF(G3779=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J3779=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[3783,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3800,null,"EIRENE-FRANCIS","FW0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","EIRENE-FRANCIS (04)",4.4620945071616617E-5,0]
[3820,null,"HIGH-SEVERN","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","HIGH-SEVERN (02)",4.4620945071616617E-5,0]
[3823,null,"SEVERN-SOMERVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","SEVERN-SOMERVILLE (03)",4.4620945071616617E-5,0]
[3843,null,"WEBB-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-QUEENSVILLE (01)",4.4620945071616617E-5,0]
[3852,null,"WEBB-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-QUEENSVILLE (01)",4.4620945071616617E-5,0]
[3865,null,"EIRENE-FRANCIS","FW0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","EIRENE-FRANCIS (02)",4.4620945071616617E-5,0]
[3872,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","FE0","WATT-THE AVENUE (02)",4.4620945071616617E-5,0]
[3888,null,"EIRENE-FRANCIS","FW0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","EIRENE-FRANCIS (01)",4.4620945071616617E-5,0]
[3908,null,"GEELONG-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","GEELONG-QUEENSVILLE (01)",4.4620945071616617E-5,0]
[3915,null,"GEELONG-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","GEELONG-QUEENSVILLE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3931,null,"HAWKHURST-FRANCIS","FW0-013","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","FW0","HAWKHURST-FRANCIS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3937,null,"HAWKHURST-FRANCIS","FW0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","HAWKHURST-FRANCIS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[3953,null,"HANSEN-GLAMIS","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","HANSEN-GLAMIS (01)",4.4620945071616617E-5,0]
[3973,null,"SEVERN-BENBOW","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","SEVERN-BENBOW (02)",0,0]
[3980,null,"BRUNEL-TRUMAN","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","BRUNEL-TRUMAN (01)",4.4620945071616617E-5,0]
[3996,null,"WEBB-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-QUEENSVILLE (04)",4.4620945071616617E-5,0]
[4010,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4022,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4038,null,"ANGLISS-SANDERSON","TH0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TH0","ANGLISS-SANDERSON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[4045,null,"SEVERN-BENBOW","FE0-012","2025-02-02","2025-02-08","N","N","N","Y","N","N","FE0","SEVERN-BENBOW (01)",0,9.4304036212749905E-5]
[4061,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","WATT-THE AVENUE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4068,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","WATT-THE AVENUE (02)",0,0]
[4089,null,"MARYSTON-SOMERVILLE","FW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","MARYSTON-SOMERVILLE (01)",0,0]
[4090,null,"MARYSTON-SOMERVILLE","FW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","MARYSTON-SOMERVILLE (01)",0,0]
[4110,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4126,null,"ALOHA-GREENE","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ALOHA-GREENE (03)",4.4620945071616617E-5,0]
[4133,null,"HANSEN-GLAMIS","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","HANSEN-GLAMIS (03)",4.4620945071616617E-5,0]
[4153,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4160,null,"CONIFER-PRIMULA","FW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CONIFER-PRIMULA (03)",4.4620945071616617E-5,0]
[4175,null,"ALMOND-CONIFER","FW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ALMOND-CONIFER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4182,null,"ALMOND-CONIFER","FW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ALMOND-CONIFER (01)",4.4620945071616617E-5,0]
[4198,null,"KELLAWAY-ROSAMOND","BY0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","KELLAWAY-ROSAMOND (02)",4.4620945071616617E-5,0]
[4218,null,"BOSQUET-BALLARAT","BY0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","BOSQUET-BALLARAT (02)",4.4620945071616617E-5,0]
[4229,null,"JACKSON-THOMSON","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","JACKSON-THOMSON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4240,null,"MADDEN-STUDLEY","FW0-017","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","MADDEN-STUDLEY (02)",0,0]
[4247,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","CLARENDON-WHITTAKER (03)",4.4620945071616617E-5,0]
[4263,null,"HAMPDEN-CROTHERS","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",0,0]
[4270,null,"BLOOMFIELD-ROSAMOND","YVE-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","BLOOMFIELD-ROSAMOND (01)",4.4620945071616617E-5,0]
[4290,null,"BURTON-OAKLAND","YVE-022","2025-02-02","2025-02-08","N","N","N","Y","N","N","YVE","BURTON-OAKLAND (01)",{"$f":"IF(G4291=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J4291=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[4296,null,"DALE-CHICAGO","YVE-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","YVE","DALE-CHICAGO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4312,null,"THE ESPLANADE-PLANTATION","YVE-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","THE ESPLANADE-PLANTATION (01)",4.4620945071616617E-5,0]
[4328,null,"ESSEX-SWAN","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","ESSEX-SWAN (02)",0,0]
[4335,null,"MADDEN-STUDLEY","FW0-017","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","MADDEN-STUDLEY (02)",0,0]
[4355,null,"MACPHERSON-SHEPHERD","FE0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","FE0","MACPHERSON-SHEPHERD (02)",4.4620945071616617E-5,0]
[4371,null,"THE BOULEVARD-WARNCLIFFE","HB0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","THE BOULEVARD-WARNCLIFFE (02)",4.4620945071616617E-5,0]
[4375,null,"BANKSIA-GLENARD","HB0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","BANKSIA-GLENARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4393,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,0]
[4400,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","MELCOMBE-BANKSIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4420,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",4.4620945071616617E-5,0]
[4436,null,"CLIFTON-WATERDALE","HB0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","CLIFTON-WATERDALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4443,null,"CLIFTON-WATERDALE","HB0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","CLIFTON-WATERDALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4454,null,"LANTANA-IVANHOE","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","LANTANA-IVANHOE (01)",4.4620945071616617E-5,0]
[4465,null,"CLIFTON-WATERDALE","HB0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","CLIFTON-WATERDALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4485,null,"JELLICOE-WATERDALE","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","JELLICOE-WATERDALE (02)",4.4620945071616617E-5,0]
[4488,null,"CLIFTON-WATERDALE","HB0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","CLIFTON-WATERDALE (01)",4.4620945071616617E-5,0]
[4508,null,"ROSELAND-IVANHOE","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (01)",4.4620945071616617E-5,0]
[4515,null,"JELLICOE-OSNEY","EP0-034","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","JELLICOE-OSNEY (02)",4.4620945071616617E-5,0]
[4537,null,"ATHELSTANE-ROBBINS","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","ATHELSTANE-ROBBINS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4550,null,"HAWKER-COOK","EP0-034","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","HAWKER-COOK (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4553,null,"ORIEL-HAWKER","EP0-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","ORIEL-HAWKER (02)",0,0]
[4573,null,"BOND-ATHELSTANE","EP0-036","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",0,0]
[4580,null,"BOND-LIBERTY","EP0-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",0,0]
[4594,null,"BOND-ATHELSTANE","EP0-036","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",0,0]
[4615,null,"GREEN-SPARKFORD","EP0-034","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","GREEN-SPARKFORD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4622,null,"BOND-ATHELSTANE","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","BOND-ATHELSTANE (04)",4.4620945071616617E-5,0]
[4638,null,"ORIEL-STANLEY","EP0-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","ORIEL-STANLEY (02)",0,0]
[4645,null,"BOND-ATHELSTANE","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","BOND-ATHELSTANE (04)",4.4620945071616617E-5,0]
[4661,null,"PINE-MARSHALL","HB0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","HB0","PINE-MARSHALL (02)",0,0]
[4673,null,"WATERDALE-THE BOULEVARD","HB0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","WATERDALE-THE BOULEVARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4687,null,"CHARTERIS-BURKE","HB0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","CHARTERIS-BURKE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4703,null,"CHARTERIS-BURKE","HB0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","CHARTERIS-BURKE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4710,null,"WILFRED-LOWER HEIDELBERG","HB0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","HB0","WILFRED-LOWER HEIDELBERG (02)",0,0]
[4730,null,"THE BOULEVARD-WARNCLIFFE","HB0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","THE BOULEVARD-WARNCLIFFE (01)",4.4620945071616617E-5,0]
[4733,null,"THE BOULEVARD-NEVILLE","HB0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","THE BOULEVARD-NEVILLE (01)",4.4620945071616617E-5,0]
[4752,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4768,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4775,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4795,null,"LOCKSLEY-MALTRAVERS","HB0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","LOCKSLEY-MALTRAVERS (02)",4.4620945071616617E-5,0]
[4798,null,"LOCKSLEY-MALTRAVERS","HB0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","LOCKSLEY-MALTRAVERS (02)",4.4620945071616617E-5,0]
[4818,null,"OUTHWAITE-ORIEL","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","OUTHWAITE-ORIEL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4823,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",4.4620945071616617E-5,0]
[4840,null,"WALLACE-KENILWORTH","FF0-090","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","WALLACE-KENILWORTH (02)",0,0]
[4847,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4863,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[4883,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4890,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4902,null,"ALTONA-ORIEL","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","ALTONA-ORIEL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[4912,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","MULBERRY-GONA (03)",4.4620945071616617E-5,0]
[4928,null,"ALAMEIN-SOUTHERN","EPN-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","ALAMEIN-SOUTHERN (03)",0,0]
[4948,null,"EDEN-BELL","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","EDEN-BELL (02)",4.4620945071616617E-5,0]
[4955,null,"ALTONA-KOKODA","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","ALTONA-KOKODA (03)",4.4620945071616617E-5,0]
[4971,null,"WATERDALE-LLOYD","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","WATERDALE-LLOYD (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[4977,null,"COLLINS-WATERDALE","EPN-033","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","EPN","OUTHWAITE-MCEWAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[4997,null,"DARLING-WHITE","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","DARLING-WHITE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[5013,null,"DARLING-WHITE","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","DARLING-WHITE (02)",4.4620945071616617E-5,0]
[5020,null,"DARLING-WHITE","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","DARLING-WHITE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5036,null,"SEPARATION-FULHAM","FF0-093","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","SEPARATION-FULHAM (01)",0,0]
[5050,null,"SEPARATION-SHIERS","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","SEPARATION-SHIERS (02)",4.4620945071616617E-5,0]
[5062,null,"WINGROVE-KELVIN","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","WINGROVE-KELVIN (02)",4.4620945071616617E-5,0]
[5065,null,"WINGROVE-KELVIN","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","WINGROVE-KELVIN (02)",4.4620945071616617E-5,0]
[5085,null,"WINGROVE-KELVIN","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","WINGROVE-KELVIN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5101,null,"PARKLANDS-KELVIN","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","PARKLANDS-KELVIN (02)",4.4620945071616617E-5,0]
[5108,null,"DARLING-WHITE","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","DARLING-WHITE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[5117,null,"ARTHUR-SEPARATION","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","ARTHUR-SEPARATION (02)",4.4620945071616617E-5,0]
[5130,null,"MCGREGOR-PERRY","FF0-083","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","MCGREGOR-PERRY (01)",4.4620945071616617E-5,0]
[5150,null,"RAVENSCOURT-FULHAM","FF0-083","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",0,0]
[5157,null,"SEPARATION-FULHAM","FF0-093","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","SEPARATION-FULHAM (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[5173,null,"WINGROVE-KELVIN","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","WINGROVE-KELVIN (02)",4.4620945071616617E-5,0]
[5193,null,"YARRALEA-GIBSON","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","YARRALEA-GIBSON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[5200,null,"YARRALEA-GIBSON","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","YARRALEA-GIBSON (01)",4.4620945071616617E-5,0]
[5215,null,"GENEVA-COMO","FF0-093","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","GENEVA-COMO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5222,null,"PARKVIEW-HEIDELBERG","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","PARKVIEW-HEIDELBERG (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[5238,null,"THE RIGHI-CASTLE","HB0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","THE RIGHI-CASTLE (02)",4.4620945071616617E-5,0]
[5245,null,"THE EYRIE-SUMMIT","HB0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","THE EYRIE-SUMMIT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5261,null,"LIBERTY-PERKINS","EP0-034","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","LIBERTY-PERKINS (01)",4.4620945071616617E-5,0]
[5279,null,"PLUNKETT-O'KEEFE","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","PLUNKETT-O'KEEFE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5287,null,"WATERDALE-GRIFFITHS","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","WATERDALE-GRIFFITHS (01)",0,0]
[5303,null,"ALPHINGTON-PARK","FF0-088","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","FF0","ALPHINGTON-PARK (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5310,null,"ALPHINGTON-PARK","FF0-088","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","FF0","ALPHINGTON-PARK (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5330,null,"JEFFREY-WESTGARTH","FF0-089","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (03)",0,0]
[5336,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[5352,null,"BERRIMA-ROSANNA","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BERRIMA-ROSANNA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5368,null,"GRENHILDA-DOUGLAS","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GRENHILDA-DOUGLAS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5375,null,"GRENHILDA-DOUGLAS","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GRENHILDA-DOUGLAS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5395,null,"DORSET-BERKELEY","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","DORSET-BERKELEY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5411,null,"DORSET-BERKELEY","HB0-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","HB0","DORSET-BERKELEY (02)",0,0]
[5415,null,"DORSET-BERKELEY","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","DORSET-BERKELEY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5424,null,"DORSET-BERKELEY","HB0-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","HB0","DORSET-BERKELEY (01)",0,0]
[5440,null,"DORSET-BERKELEY","HB0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","DORSET-BERKELEY (01)",4.4620945071616617E-5,0]
[5460,null,"FINN-HAUGHTON","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","FINN-HAUGHTON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[5463,null,"FINN-HAUGHTON","HB0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","FINN-HAUGHTON (03)",4.4620945071616617E-5,0]
[5483,null,"QUINN-ST. JAMES","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","QUINN-ST. JAMES (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[5494,null,"ANDERSON-BEVERLEY","HB0-023","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","HB0","ANDERSON-BEVERLEY (03)",4.4620945071616617E-5,0]
[5505,null,"HODGSON-AVOCA","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","HODGSON-AVOCA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5525,null,"HODGSON-AVOCA","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","HODGSON-AVOCA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[5528,null,"HODGSON-AVOCA","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","HODGSON-AVOCA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[5548,null,"HAUGHTON-GREVILLE","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","HAUGHTON-GREVILLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5555,null,"HODGSON-AVOCA","HB0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","HODGSON-AVOCA (01)",4.4620945071616617E-5,0]
[5577,null,"RILL-OLIVE","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","RILL-OLIVE (01)",4.4620945071616617E-5,0]
[5590,null,"DAREBIN-STRADBROKE","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","DAREBIN-STRADBROKE (01)",4.4620945071616617E-5,0]
[5597,null,"RILL-OLIVE","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","RILL-OLIVE (02)",4.4620945071616617E-5,0]
[5613,null,"UP H'BERG-ST HELLIER","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","UP H'BERG-ST HELLIER (01)",4.4620945071616617E-5,0]
[5620,null,"RILL-OLIVE","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","RILL-OLIVE (01)",4.4620945071616617E-5,0]
[5636,null,"LOWER PLENTY-MOUNTVIEW","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","LOWER PLENTY-MOUNTVIEW (01)",4.4620945071616617E-5,0]
[5644,null,"RILL-OLIVE","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","RILL-OLIVE (01)",4.4620945071616617E-5,0]
[5662,null,"BEETHAM-PROSPECT","NH0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BEETHAM-PROSPECT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5678,null,"BEETHAM-PROSPECT","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BEETHAM-PROSPECT (02)",4.4620945071616617E-5,0]
[5685,null,"INVERMAY-MT IDA","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","INVERMAY-MT IDA (02)",4.4620945071616617E-5,0]
[5701,null,"DARVALL-WAIORA","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","DARVALL-WAIORA (02)",4.4620945071616617E-5,0]
[5713,null,"DARVALL-WAIORA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","DARVALL-WAIORA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5727,null,"INVERMAY-BELLEVUE","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","INVERMAY-BELLEVUE (01)",4.4620945071616617E-5,0]
[5743,null,"COLLINS-WATERDALE","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","OUTHWAITE-MCEWAN (03)",4.4620945071616617E-5,0]
[5750,null,"LLOYD-MONASH","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","LLOYD-MONASH (02)",0,0]
[5770,null,"ST HELLIER-UP HEIDELBERG","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","ST HELLIER-UP HEIDELBERG (01)",4.4620945071616617E-5,0]
[5773,null,"ST HELLIER-UP HEIDELBERG","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","ST HELLIER-UP HEIDELBERG (01)",4.4620945071616617E-5,0]
[5792,null,"ST HELLIER-UP HEIDELBERG","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","ST HELLIER-UP HEIDELBERG (01)",4.4620945071616617E-5,0]
[5808,null,"ST HELLIER-UP HEIDELBERG","NH0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","ST HELLIER-UP HEIDELBERG (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[5815,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[5822,null,"BERRIMA-ROSANNA","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BERRIMA-ROSANNA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5838,null,"BERRIMA-ROSANNA","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BERRIMA-ROSANNA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5858,null,"BANYULE-MCCRAE","HB0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","BANYULE-MCCRAE (01)",4.4620945071616617E-5,0]
[5871,null,"CANTALA-MCCRAE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","CANTALA-MCCRAE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5880,null,"CANTALA-MCCRAE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CANTALA-MCCRAE (02)",4.4620945071616617E-5,0]
[5887,null,"SUSSEX-BANYULE","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","SUSSEX-BANYULE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5903,null,"GRAHAM-ULRICH","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GRAHAM-ULRICH (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[5923,null,"NELSON-LYON","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","NELSON-LYON (02)",4.4620945071616617E-5,0]
[5930,null,"NELSON-LYON","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","NELSON-LYON (02)",4.4620945071616617E-5,0]
[5942,null,"ROBERN-ROSEBUD","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","ROBERN-ROSEBUD (01)",4.4620945071616617E-5,0]
[5952,null,"LENA-ODONNELL","NH0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","NH0","LENA-ODONNELL (03)",0,0]
[5968,null,"WINSTON-JASON","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","WINSTON-JASON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[5988,null,"CASTLETON 21-HAVILAH","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CASTLETON 21-HAVILAH (02)",4.4620945071616617E-5,0]
[5995,null,"CASTLETON 21-HAVILAH","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CASTLETON 21-HAVILAH (02)",4.4620945071616617E-5,0]
[6011,null,"MYDDLETON-GRACE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","MYDDLETON-GRACE (01)",4.4620945071616617E-5,0]
[6021,null,"MYDDLETON-GRACE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","MYDDLETON-GRACE (01)",4.4620945071616617E-5,0]
[6037,null,"THE GLADE-SHERLOWE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","THE GLADE-SHERLOWE (01)",4.4620945071616617E-5,0]
[6040,null,"THE GLADE-SHERLOWE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","THE GLADE-SHERLOWE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[6060,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","YALLAMBIE-LOWER PLENTY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[6076,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","YALLAMBIE-LOWER PLENTY (01)",4.4620945071616617E-5,0]
[6090,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","YALLAMBIE-LOWER PLENTY (02)",4.4620945071616617E-5,0]
[6102,null,"BIMBADEEN-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[6105,null,"BIMBADEEN-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[6125,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","YALLAMBIE-LOWER PLENTY (02)",4.4620945071616617E-5,0]
[6132,null,"BIMBADEEN-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[6148,null,"BIMBADEEN-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",4.4620945071616617E-5,0]
[6157,null,"FINLAYSON-BRAIDHILL","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","FINLAYSON-BRAIDHILL (03)",4.4620945071616617E-5,0]
[6170,null,"KENTWOOD-ALBANY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","KENTWOOD-ALBANY (02)",4.4620945071616617E-5,0]
[6190,null,"YALLAMBIE-JANICE","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","YALLAMBIE-JANICE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[6197,null,"YALLAMBIE-JANICE","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","YALLAMBIE-JANICE (01)",4.4620945071616617E-5,0]
[6213,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[6220,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,0]
[6240,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,0]
[6255,null,"BRAIDHILL-WINDSOR","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BRAIDHILL-WINDSOR (02)",4.4620945071616617E-5,0]
[6262,null,"MUNRO-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","MUNRO-ERSKINE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[6278,null,"MUNRO-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","MUNRO-ERSKINE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[6285,null,"BELLEVUE-DAVIES","NH0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BELLEVUE-DAVIES (01)",4.4620945071616617E-5,0]
[6305,null,"GRANDVIEW-LONGVIEW","NH0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GRANDVIEW-LONGVIEW (02)",4.4620945071616617E-5,0]
[6319,null,"RUTHVEN-WAIORA","NH0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","RUTHVEN-WAIORA (04)",4.4620945071616617E-5,0]
[6327,null,"JACKA-JOYNT","NH0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","JACKA-JOYNT (01)",4.4620945071616617E-5,0]
[6343,null,"CASTLETON 21-HAVILAH","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","CASTLETON 21-HAVILAH (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[6350,null,"BIMBADEEN-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BIMBADEEN-YALLAMBIE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[6370,null,"ARDEN-LOWER PLENTY","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","ARDEN-LOWER PLENTY (01)",4.4620945071616617E-5,0]
[6386,null,"BRASSEY-PYALONG","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BRASSEY-PYALONG (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[6398,null,"FINLAYSON-BRAIDHILL","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","FINLAYSON-BRAIDHILL (03)",4.4620945071616617E-5,0]
[6408,null,"SOMERS-HINKLER","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","SOMERS-HINKLER (02)",4.4620945071616617E-5,0]
[6415,null,"LINDSAY-TORBAY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","LINDSAY-TORBAY (01)",4.4620945071616617E-5,0]
[6435,null,"LLOYD-MONASH","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",0,0]
[6438,null,"MUNRO-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","MUNRO-ERSKINE (02)",4.4620945071616617E-5,0]
[6455,null,"CARWARP-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","CARWARP-ERSKINE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[6464,null,"CARWARP-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CARWARP-ERSKINE (02)",4.4620945071616617E-5,0]
[6480,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[6500,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,0]
[6503,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,0]
[6523,null,"MUNRO-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","MUNRO-ERSKINE (02)",4.4620945071616617E-5,0]
[6534,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[6545,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,0]
[6565,null,"GRAHAM-ULRICH","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GRAHAM-ULRICH (02)",4.4620945071616617E-5,0]
[6572,null,"SHORT-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","SHORT-DUNVEGAN (02)",4.4620945071616617E-5,0]
[6588,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","YALLAMBIE-LOWER PLENTY (01)",4.4620945071616617E-5,0]
[6595,null,"HOOPER-DUNVEGAN","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","HOOPER-DUNVEGAN (01)",4.4620945071616617E-5,0]
[6605,null,"YALLAMBIE-WENDOVER","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","YALLAMBIE-WENDOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[6617,null,"MYDDLETON-GRACE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","MYDDLETON-GRACE (01)",4.4620945071616617E-5,0]
[6637,null,"RUTHERFORD-LILLIAN","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","RUTHERFORD-LILLIAN (02)",4.4620945071616617E-5,0]
[6653,null,"HAWDON-BROWN","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","HAWDON-BROWN (01)",4.4620945071616617E-5,0]
[6660,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GLENMORE-KINLOCK (03)",4.4620945071616617E-5,0]
[6676,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GLENMORE-KINLOCK (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[6684,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GLENMORE-KINLOCK (03)",4.4620945071616617E-5,0]
[6702,null,"THE GLADE-SHERLOWE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","THE GLADE-SHERLOWE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[6718,null,"THE GLADE-SHERLOWE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","THE GLADE-SHERLOWE (02)",4.4620945071616617E-5,0]
[6725,null,"THE GLADE-SHERLOWE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","THE GLADE-SHERLOWE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[6745,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GLENMORE-KINLOCK (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[6748,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GLENMORE-KINLOCK (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[6763,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GLENMORE-KINLOCK (03)",4.4620945071616617E-5,0]
[6783,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,0]
[6790,null,"JACKA-JOYNT","NH0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","JACKA-JOYNT (01)",4.4620945071616617E-5,0]
[6797,null,"BOND-ATHELSTANE","EP0-036","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","BOND-ATHELSTANE (01)",0,0]
[6813,null,"ELLESMERE-INVERMAY","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","ELLESMERE-INVERMAY (04)",4.4620945071616617E-5,0]
[6832,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GLENMORE-KINLOCK (03)",4.4620945071616617E-5,0]
[6835,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GLENMORE-KINLOCK (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[6855,null,"YALLAMBIE-WENDOVER","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","YALLAMBIE-WENDOVER (01)",4.4620945071616617E-5,0]
[6862,null,"CARWARP-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CARWARP-ERSKINE (02)",4.4620945071616617E-5,0]
[6878,null,"ANDERSON-BEVERLEY","HB0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ANDERSON-BEVERLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[6898,null,"MUNRO-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","MUNRO-ERSKINE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[6911,null,"HIGH 883-MELB WATER","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HIGH 883-MELB WATER (01)",4.4620945071616617E-5,0]
[6920,null,"HAWKER-ELLISON","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","HAWKER-ELLISON (02)",4.4620945071616617E-5,0]
[6927,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MARGTMARY-MURRAY (03)",4.4620945071616617E-5,0]
[6943,null,"FETTLING-COOPER","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","FETTLING-COOPER (02)",4.4620945071616617E-5,0]
[6963,null,"SHEFFIELD-MAY","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","SHEFFIELD-MAY (02)",4.4620945071616617E-5,0]
[6970,null,"BIRDWOOD-REGENT","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BIRDWOOD-REGENT (04)",4.4620945071616617E-5,0]
[6982,null,"BIRDWOOD-REGENT","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BIRDWOOD-REGENT (03)",4.4620945071616617E-5,0]
[6992,null,"BIRDWOOD-REGENT","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BIRDWOOD-REGENT (03)",4.4620945071616617E-5,0]
[7012,null,"BIRDWOOD-REGENT","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BIRDWOOD-REGENT (02)",4.4620945071616617E-5,0]
[7015,null,"BIRDWOOD-REGENT","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BIRDWOOD-REGENT (02)",4.4620945071616617E-5,0]
[7035,null,"POWELL-EXCELSIOR","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","POWELL-EXCELSIOR (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[7051,null,"GILBANK-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","GILBANK-GILBERT (02)",4.4620945071616617E-5,0]
[7061,null,"GILBANK-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","GILBANK-GILBERT (02)",4.4620945071616617E-5,0]
[7077,null,"MYRTLE-REGENT","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","MYRTLE-REGENT (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[7080,null,"POWELL-EXCELSIOR","PTN-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","POWELL-EXCELSIOR (02)",0,0]
[7100,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MARGTMARY-MURRAY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[7116,null,"FETTLING-COOPER","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","FETTLING-COOPER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7123,null,"BONVIEW-CARRINGTON","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BONVIEW-CARRINGTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7140,null,"KNOX-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KNOX-GILBERT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7145,null,"KNOX-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KNOX-GILBERT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7165,null,"SYMONS-GILBERT","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","SYMONS-GILBERT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[7172,null,"SYMONS-GILBERT","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","SYMONS-GILBERT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[7188,null,"SYMONS-GILBERT","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","SYMONS-GILBERT (01)",4.4620945071616617E-5,0]
[7197,null,"SYMONS-GILBERT","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","SYMONS-GILBERT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[7210,null,"CHARLES-BENAMBRA","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CHARLES-BENAMBRA (02)",4.4620945071616617E-5,0]
[7230,null,"CHARLES-BENAMBRA","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CHARLES-BENAMBRA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7237,null,"CHARLES-BENAMBRA","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CHARLES-BENAMBRA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7253,null,"MOUNT-BELL","CS0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MOUNT-BELL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[7260,null,"GRANGE-CRAMER","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRANGE-CRAMER (01)",4.4620945071616617E-5,0]
[7276,null,"MOUNT-BELL","CS0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MOUNT-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7295,null,"MOUNT-BELL","CS0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MOUNT-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7302,null,"BURGESS-GILBERT","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BURGESS-GILBERT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7318,null,"MOUNT-BELL","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MOUNT-BELL (01)",4.4620945071616617E-5,0]
[7325,null,"BRUCE-GILBERT","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BRUCE-GILBERT (02)",4.4620945071616617E-5,0]
[7345,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,0]
[7359,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[7367,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[7383,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[7390,null,"ROBESON-KENDALL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","ROBESON-KENDALL (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[7410,null,"BONVIEW-CARRINGTON","CN0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","CN0","BONVIEW-CARRINGTON (01)",0,0]
[7413,null,"BONVIEW-HENTY","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BONVIEW-HENTY (02)",4.4620945071616617E-5,0]
[7426,null,"HENTY-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","HENTY-GILBERT (02)",{"$f":"IF(G7427=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J7427=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[7439,null,"GLOUCESTER-HENTY","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","GLOUCESTER-HENTY (01)",4.4620945071616617E-5,0]
[7455,null,"GLOUCESTER-HENTY","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","GLOUCESTER-HENTY (02)",4.4620945071616617E-5,0]
[7475,null,"ASHLEY-EDWARDES","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ASHLEY-EDWARDES (02)",4.4620945071616617E-5,0]
[7478,null,"ASHLEY-EDWARDES","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ASHLEY-EDWARDES (02)",4.4620945071616617E-5,0]
[7495,null,"CAROLE JOY-SPRING","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CAROLE JOY-SPRING (01)",4.4620945071616617E-5,0]
[7504,null,"CAROLE JOY-SPRING","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CAROLE JOY-SPRING (01)",4.4620945071616617E-5,0]
[7520,null,"OLIVE-VIOLA","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","OLIVE-VIOLA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7540,null,"BEDWELL-HUGHES","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","BEDWELL-HUGHES (02)",4.4620945071616617E-5,0]
[7543,null,"BEDWELL-HUGHES","TT0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","BEDWELL-HUGHES (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7563,null,"ANSTEY-PHILLIP","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ANSTEY-PHILLIP (02)",4.4620945071616617E-5,0]
[7574,null,"ANSTEY-PHILLIP","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ANSTEY-PHILLIP (02)",4.4620945071616617E-5,0]
[7585,null,"ANSTEY-PHILLIP","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ANSTEY-PHILLIP (02)",4.4620945071616617E-5,0]
[7592,null,"CLAREMONT-MOIRA","TT0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","CLAREMONT-MOIRA (02)",0,0]
[7612,null,"ROSENTHAL-HUGHES","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ROSENTHAL-HUGHES (02)",4.4620945071616617E-5,0]
[7628,null,"ROSENTHAL-ALLENBY","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",4.4620945071616617E-5,0]
[7635,null,"ROSENTHAL-ALLENBY","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",4.4620945071616617E-5,0]
[7645,null,"ROSENTHAL-ALLENBY","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROSENTHAL-ALLENBY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[7657,null,"ROSENTHAL-HUGHES","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ROSENTHAL-HUGHES (01)",4.4620945071616617E-5,0]
[7677,null,"TRACEY-ELLIOT","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","TRACEY-ELLIOT (01)",4.4620945071616617E-5,0]
[7693,null,"LAWLEY-GLASGOW","TT0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","LAWLEY-GLASGOW (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[7700,null,"ASHLEY-EDWARDES","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ASHLEY-EDWARDES (01)",4.4620945071616617E-5,0]
[7720,null,"BREX-RADFORD","TT0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","BREX-RADFORD (00)",0,0]
[7724,null,"BREX 8-RADFORD","TT0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","BREX 8-RADFORD (01)",0,0]
[7742,null,"LAWLEY-GLASGOW","TT0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","LAWLEY-GLASGOW (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7758,null,"HALSEY-RADFORD","TT0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","HALSEY-RADFORD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[7765,null,"MONZA-FLORENCE","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","MONZA-FLORENCE (01)",4.4620945071616617E-5,0]
[7772,null,"MONZA-FLORENCE","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","MONZA-FLORENCE (01)",4.4620945071616617E-5,0]
[7788,null,"BRAY-BARTROP","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","BRAY-BARTROP (02)",4.4620945071616617E-5,0]
[7803,null,"AMEILY-LEAMINGTON","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","AMEILY-LEAMINGTON (01)",4.4620945071616617E-5,0]
[7810,null,"AMEILY-LEAMINGTON","CN0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","CN0","AMEILY-LEAMINGTON (02)",{"$f":"IF(G7811=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J7811=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[7830,null,"BROADHURST-MCFADZEAN","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","BROADHURST-MCFADZEAN (02)",4.4620945071616617E-5,0]
[7837,null,"TRACEY-ELLIOT","TT0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","TRACEY-ELLIOT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[7853,null,"WHITBY-BARTON","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","WHITBY-BARTON (02)",4.4620945071616617E-5,0]
[7872,null,"O'CONNOR-WHITBY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[7879,null,"BROADHURST-MCFADZEAN","TT0-008","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","TT0","OCONNOR-MACFADZEAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[7895,null,"O'CONNOR-WHITBY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[7902,null,"BROADHURST-MCFADZEAN","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","OCONNOR-MACFADZEAN (03)",4.4620945071616617E-5,0]
[7918,null,"DREDGE-TORMEY","TT0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","DREDGE-TORMEY (01)",0,0]
[7938,null,"ROSEBERRY-HIGH","PTN-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","ROSEBERRY-HIGH (03)",{"$f":"IF(G7939=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J7939=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[7939,null,"BEAUCHAMP-HIGH","PTN-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","BEAUCHAMP-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[7960,null,"CAMBRIAN-HIGH","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","CAMBRIAN-HIGH (02)",4.4620945071616617E-5,0]
[7967,null,"TENNYSON-TYLER","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","TENNYSON-TYLER (01)",4.4620945071616617E-5,0]
[7987,null,"FOCH-TYLER","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",0,0]
[7990,null,"FOCH-TYLER","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","FOCH-TYLER (01)",0,0]
[8010,null,"MCIVOR-OAKHILL","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MCIVOR-OAKHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8022,null,"NORTHERNHAY-OAKHILL","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","NORTHERNHAY-OAKHILL (02)",4.4620945071616617E-5,0]
[8032,null,"NORTHERNHAY-OAKHILL","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","NORTHERNHAY-OAKHILL (02)",4.4620945071616617E-5,0]
[8052,null,"HOME-WILKINSON","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","HOME-WILKINSON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8055,null,"HOME-WILKINSON","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","HOME-WILKINSON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8075,null,"GISBORNE-NORTH","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","GISBORNE-NORTH (02)",4.4620945071616617E-5,0]
[8091,null,"DELAWARE-MENDIP","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DELAWARE-MENDIP (03)",4.4620945071616617E-5,0]
[8101,null,"WILKINSON-BENDIGO","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","WILKINSON-BENDIGO (01)",4.4620945071616617E-5,0]
[8117,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","O'DOWD-HOWARD (02)",4.4620945071616617E-5,0]
[8120,null,"EAST-THACKERAY","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","EAST-THACKERAY (04)",4.4620945071616617E-5,0]
[8140,null,"DELAWARE-MENDIP","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DELAWARE-MENDIP (01)",4.4620945071616617E-5,0]
[8147,null,"EAST-THACKERAY","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","EAST-THACKERAY (02)",4.4620945071616617E-5,0]
[8163,null,"DELAWARE-MENDIP","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","DELAWARE-MENDIP (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8180,null,"CENTRE-HOWARD","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CENTRE-HOWARD (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[8185,null,"DELAWARE-MENDIP","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","DELAWARE-MENDIP (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8205,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","O'DOWD-HOWARD (02)",4.4620945071616617E-5,0]
[8212,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","O'DOWD-HOWARD (02)",4.4620945071616617E-5,0]
[8228,null,"GOULBURN-SHAND","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","GOULBURN-SHAND (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[8237,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","O'DOWD-HOWARD (01)",4.4620945071616617E-5,0]
[8250,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","O'DOWD-HOWARD (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[8270,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","O'DOWD-HOWARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8277,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","O'DOWD-HOWARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8293,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[8300,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,0]
[8316,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[8335,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8342,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8358,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8365,null,"WHITE-CHEDDAR","TT0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","WHITE-CHEDDAR (04)",0,0]
[8385,null,"MCCRAE-ELSEY","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","MCCRAE-ELSEY (03)",4.4620945071616617E-5,0]
[8399,null,"MACK-PICKETT","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","MACK-PICKETT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[8407,null,"FINTON-ARUNDEL","TT0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (02)",0,0]
[8414,null,"FINTON-ARUNDEL","TT0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","FINTON-ARUNDEL (02)",0,0]
[8430,null,"BRIDGETON-TUNALEY","TT0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","BRIDGETON-TUNALEY (01)",0,0]
[8450,null,"ST VIGEONS-BORRIE","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ST VIGEONS-BORRIE (01)",{"$f":"IF(G8451=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J8451=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[8453,null,"ST VIGEONS-BORRIE","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ST VIGEONS-BORRIE (01)",4.4620945071616617E-5,0]
[8466,null,"CHEDDAR-JINGHI","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","NA",4.4620945071616617E-5,0]
[8479,null,"LAURIE-PURINUAN","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","LAURIE-PURINUAN (01)",4.4620945071616617E-5,0]
[8495,null,"PURINUAN-NUTWOOD","TT0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","PURINUAN-NUTWOOD (02)",0,0]
[8515,null,"BOLDREWOOD-McMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","BOLDREWOOD-McMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8518,null,"BOLDREWOOD-McMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","BOLDREWOOD-McMAHON (01)",4.4620945071616617E-5,0]
[8538,null,"BOLDREWOOD-McMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","BOLDREWOOD-McMAHON (02)",4.4620945071616617E-5,0]
[8545,null,"BOLDREWOOD-McMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","BOLDREWOOD-McMAHON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[8560,null,"PLENTY-RESERVOIR COLLEGE","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","PLENTY-RESERVOIR COLLEGE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8567,null,"KILMORE-CHARLTON","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","KILMORE-CHARLTON (02)",4.4620945071616617E-5,0]
[8587,null,"BROWNING-SCOTT","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","BROWNING-SCOTT (01)",4.4620945071616617E-5,0]
[8603,null,"BROWNING-SCOTT","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","BROWNING-SCOTT (01)",4.4620945071616617E-5,0]
[8614,null,"BROWNING-SCOTT","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","BROWNING-SCOTT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[8625,null,"THE FAIRWAY-DUNNE","TT0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","THE FAIRWAY-DUNNE (01)",0,0]
[8632,null,"THE FAIRWAY-DUNNE","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","THE FAIRWAY-DUNNE (01)",4.4620945071616617E-5,0]
[8652,null,"THE FAIRWAY-DUNNE","TT0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","THE FAIRWAY-DUNNE (02)",0,0]
[8668,null,"THE FAIRWAY-DUNNE","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","THE FAIRWAY-DUNNE (02)",4.4620945071616617E-5,0]
[8675,null,"DORRINGTON-PLENTY","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DORRINGTON-PLENTY (02)",4.4620945071616617E-5,0]
[8685,null,"EISENHOWER-CHALEYER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","EISENHOWER-CHALEYER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8697,null,"DORRINGTON-PLENTY","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DORRINGTON-PLENTY (02)",4.4620945071616617E-5,0]
[8717,null,"CHALEYER-ASHTON","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CHALEYER-ASHTON (03)",4.4620945071616617E-5,0]
[8733,null,"CREVILLI-SUMMERHILL","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CREVILLI-SUMMERHILL (01)",4.4620945071616617E-5,0]
[8740,null,"BEATRICE-JENSEN","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BEATRICE-JENSEN (01)",4.4620945071616617E-5,0]
[8747,null,"BEATRICE-JENSEN","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BEATRICE-JENSEN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[8764,null,"LAUREL-TYLER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","LAUREL-TYLER (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[8782,null,"FOCH-TYLER","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","FOCH-TYLER (03)",0,0]
[8785,null,"FOCH-TYLER","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",0,0]
[8805,null,"BLAKE-DAVIS","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BLAKE-DAVIS (02)",4.4620945071616617E-5,0]
[8812,null,"LAUREL-TYLER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","LAUREL-TYLER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[8828,null,"MCCOLL-MALPAS","PTN-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","MCCOLL-MALPAS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[8843,null,"MCCOLL-MALPAS","PTN-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","MCCOLL-MALPAS (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[8854,null,"KATHLEEN-WOOD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","KATHLEEN-WOOD (01)",4.4620945071616617E-5,0]
[8870,null,"WOOD-GREENBELT","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","WOOD-GREENBELT (02)",4.4620945071616617E-5,0]
[8877,null,"WOOD-GREENBELT","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","WOOD-GREENBELT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[8893,null,"WOOD-GREENBELT","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","WOOD-GREENBELT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[8913,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[8922,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[8935,null,"BEATRICE-JENSEN","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BEATRICE-JENSEN (02)",4.4620945071616617E-5,0]
[8942,null,"KATHLEEN-WOOD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","KATHLEEN-WOOD (01)",4.4620945071616617E-5,0]
[8958,null,"KATHLEEN-WOOD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","KATHLEEN-WOOD (02)",4.4620945071616617E-5,0]
[8965,null,"KATHLEEN-WOOD","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","KATHLEEN-WOOD (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[8979,null,"KATHLEEN-WOOD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","KATHLEEN-WOOD (02)",4.4620945071616617E-5,0]
[9000,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[9007,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[9027,null,"BEAUCHAMP-HIGH","PTN-011","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","PTN","BEAUCHAMP-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9030,null,"KENNETH-GOWER","EPN-035","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","KENNETH-GOWER (01)",4.4620945071616617E-5,0]
[9050,null,"SYLVESTER-GORDON","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","SYLVESTER-GORDON (02)",4.4620945071616617E-5,0]
[9062,null,"ALBERT-HARROW","EPN-035","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","ALBERT-HARROW (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[9072,null,"BELGROVE-OVANDO","PTN-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","BELGROVE-OVANDO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[9092,null,"SOUTH-BELL","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",0,0]
[9095,null,"SOUTH-BELL","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","SOUTH-BELL (03)",0,0]
[9115,null,"BELGROVE-OVANDO","PTN-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","BELGROVE-OVANDO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[9122,null,"MIHIL-VICTORIA","EP0-037","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","MIHIL-VICTORIA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9141,null,"DERMOT-CORMAC","PTN-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","DERMOT-CORMAC (02)",4.4620945071616617E-5,0]
[9144,null,"MIHIL-VICTORIA","EP0-037","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","MIHIL-VICTORIA (01)",4.4620945071616617E-5,0]
[9160,null,"ALBERT-DUNDAS","EP0-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",0,0]
[9180,null,"CHIFLEY 51-53-RAGLAN","EP0-035","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","CHIFLEY 51-53-RAGLAN (02)",0,0]
[9187,null,"VICTORIA-FOLEY","EP0-037","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","VICTORIA-FOLEY (03)",4.4620945071616617E-5,0]
[9203,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","McGOWAN-MURRAY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9220,null,"QUEEN-RUSSELL","NT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","QUEEN-RUSSELL (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[9225,null,"WILLIAM-MASON","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WILLIAM-MASON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[9245,null,"WINDSOR-CECIL","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WINDSOR-CECIL (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[9252,null,"FERGUSON-TOWNHALL","NT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","FERGUSON-TOWNHALL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9268,null,"ELECTRA-PASCO","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","ELECTRA-PASCO (02)",4.4620945071616617E-5,0]
[9275,null,"GIFFARD-OSBORNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","GIFFARD-OSBORNE (04)",4.4620945071616617E-5,0]
[9287,null,"STEWART-OSBORNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","STEWART-OSBORNE (02)",4.4620945071616617E-5,0]
[9310,null,"COLE-OSBORNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","COLE-OSBORNE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9317,null,"GIFFARD-OSBORNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","GIFFARD-OSBORNE (03)",4.4620945071616617E-5,0]
[9333,null,"GELLIBRAND-STEWART","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","GELLIBRAND-STEWART (02)",4.4620945071616617E-5,0]
[9340,null,"GELLIBRAND-STEWART","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","GELLIBRAND-STEWART (01)",4.4620945071616617E-5,0]
[9356,null,"VICTORIA-RAILWAY","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","VICTORIA-RAILWAY (01)",4.4620945071616617E-5,0]
[9362,null,"STEWART-OSBORNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","STEWART-OSBORNE (01)",4.4620945071616617E-5,0]
[9382,null,"PARK-INGLIS","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","PARK-INGLIS (02)",4.4620945071616617E-5,0]
[9398,null,"ADELINE-KOROROIT","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","ADELINE-KOROROIT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9405,null,"FERGUSON-TOWNHALL","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","FERGUSON-TOWNHALL (02)",4.4620945071616617E-5,0]
[9425,null,"BUNBURY-DOUGLAS","NT0-004","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","NT0","BUNBURY-DOUGLAS (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[9427,null,"BUNBURY-DOUGLAS","NT0-004","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","NT0","BUNBURY-DOUGLAS (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[9447,null,"QUEEN-RUSSELL","NT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","QUEEN-RUSSELL (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[9454,null,"LATROBE-YARRA","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","LATROBE-YARRA (01)",4.4620945071616617E-5,0]
[9470,null,"COURTIS-MELBOURNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","COURTIS-MELBOURNE (04)",4.4620945071616617E-5,0]
[9490,null,"YARRA-DOVER","NT0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","YARRA-DOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9493,null,"STEVEDORE-DOVER","NT0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","STEVEDORE-DOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9506,null,"QUEEN-RUSSELL","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","QUEEN-RUSSELL (04)",4.4620945071616617E-5,0]
[9519,null,"QUEEN-RUSSELL","NT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","QUEEN-RUSSELL (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[9535,null,"QUEEN-RUSSELL","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","QUEEN-RUSSELL (03)",4.4620945071616617E-5,0]
[9542,null,"ALMA-CHANDLER","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","ALMA-CHANDLER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[9562,null,"ALMA-YARRA","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","ALMA-YARRA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9578,null,"MELBOURNE-DAVIES","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","MELBOURNE-DAVIES (02)",4.4620945071616617E-5,0]
[9585,null,"PEEL-DOUGLAS","NT0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","PEEL-DOUGLAS (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[9600,null,"EFFINGHAM-WILKINS","NT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","EFFINGHAM-WILKINS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9607,null,"EFFINGHAM-WILKINS","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","EFFINGHAM-WILKINS (01)",4.4620945071616617E-5,0]
[9627,null,"FARM-HOME","NT0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","FARM-HOME (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9643,null,"HUDSONS-HICK","YVE-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","YVE","HUDSONS-HICK (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[9650,null,"HUDSONS-HICK","YVE-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","YVE","HUDSONS-HICK (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[9668,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","WATT-THE AVENUE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9672,null,"BLACKSHAWS-ELIZABETH","YVE-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","YVE","BLACKSHAWS-ELIZABETH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9692,null,"ROSS-ELIZABETH","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","ROSS-ELIZABETH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9708,null,"NEWCASTLE-ELIZABETH","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","NEWCASTLE-ELIZABETH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9715,null,"NEWCASTLE-ELIZABETH","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","NEWCASTLE-ELIZABETH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9733,null,"WALKER-NEWCASTLE","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","WALKER-NEWCASTLE (02)",4.4620945071616617E-5,0]
[9737,null,"WILLIAM-JUNCTION","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WILLIAM-JUNCTION (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9757,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[9760,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9780,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[9787,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9804,null,"THORPE-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","THORPE-WOODS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9822,null,"BRADLEY-MASON","NT0-017","2025-02-02","2025-02-08","N","Y","N","N","N","N","NT0","BRADLEY-MASON (03)",0,0]
[9829,null,"BRADLEY-MASON","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BRADLEY-MASON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9845,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[9852,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9868,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9883,null,"CHALLIS-SPEIGHT","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","CHALLIS-SPEIGHT (01)",4.4620945071616617E-5,0]
[9894,null,"JACK-FORD","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","JACK-FORD (02)",4.4620945071616617E-5,0]
[9910,null,"CHALLIS-SPEIGHT","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","CHALLIS-SPEIGHT (02)",4.4620945071616617E-5,0]
[9917,null,"JACK-FORD","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","JACK-FORD (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[9933,null,"SALISBURY-JACK","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","SALISBURY-JACK (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[9940,null,"SALISBURY-JACK","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","SALISBURY-JACK (01)",4.4620945071616617E-5,0]
[9962,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","CHALLIS-JUBILLEE (02)",4.4620945071616617E-5,0]
[9975,null,"WILLIAM-MASON","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WILLIAM-MASON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[9982,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[10002,null,"WILLIAM-JUNCTION","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WILLIAM-JUNCTION (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[10005,null,"PEEL-DOUGLAS","NT0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","PEEL-DOUGLAS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[10025,null,"CHARLES-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","CHARLES-EPSOM (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[10033,null,"MARY-ROBERTS","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MARY-ROBERTS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[10047,null,"GREENACRE-AYLESBURY","AW0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","GREENACRE-AYLESBURY (02)",0,0]
[10067,null,"JOHNSON-BENAUD","BD0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","JOHNSON-BENAUD (01)",0,0]
[10070,null,"RIPPON-HOADLEY","FE0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","RIPPON-HOADLEY (02)",0,0]
[10090,null,"EFFINGHAM-WILKINS","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","EFFINGHAM-WILKINS (01)",4.4620945071616617E-5,0]
[10102,null,"WINSTON-JASON","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","WINSTON-JASON (01)",4.4620945071616617E-5,0]
[10112,null,"JACK-FORD","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","JACK-FORD (02)",4.4620945071616617E-5,0]
[10119,null,"FEHON-ANDERSON","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","FEHON-ANDERSON (01)",0,0]
[10135,null,"YERING-GUILDFORD","BD0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","YERING-GUILDFORD (01)",0,0]
[10155,null,"SEVERN-SOMERVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","SEVERN-SOMERVILLE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[10162,null,"HAMPDEN-CROTHERS","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (02)",0,0]
[10181,null,"CLIFTON-WATERDALE","HB0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","CLIFTON-WATERDALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[10184,null,"RUSSELL-BARKLY","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","RUSSELL-BARKLY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[10200,null,"MIMOSA-LAUREL","BD0-016","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","MIMOSA-LAUREL (01)",0,0]
[10220,null,"QUINN-CLARKS","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","QUINN-CLARKS (03)",4.4620945071616617E-5,0]
[10227,null,"ATTERCLIFFE-DERBY","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",4.4620945071616617E-5,0]
[10243,null,"HAWTHORN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HAWTHORN-REYNARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[10248,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[10269,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,0]
[10285,null,"JOHN-WINIFRED","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","JOHN-WINIFRED (02)",4.4620945071616617E-5,0]
[10292,null,"CRAWFORD-ROBINSON","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","CRAWFORD-ROBINSON (02)",0,0]
[10308,null,"HAWTHORN-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","HAWTHORN-REYNARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[10315,null,"KERFERD-RALEIGH","ES0-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (02)",0,0]
[10327,null,"SOUTHEY-ARDEN","FT0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",0,0]
[10337,null,"SOUTHEY-ARDEN","FT0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (02)",0,0]
[10357,null,"ANTHONY-BELLAIR","FT0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","ANTHONY-BELLAIR (01)",4.4620945071616617E-5,0]
[10373,null,"ANTHONY-BELLAIR","FT0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","ANTHONY-BELLAIR (02)",4.4620945071616617E-5,0]
[10380,null,"ANTHONY-BELLAIR","FT0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","ANTHONY-BELLAIR (02)",4.4620945071616617E-5,0]
[10400,null,"PARSONS-STUBBS","FT0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","PARSONS-STUBBS (02)",4.4620945071616617E-5,0]
[10410,null,"WALTHAM-LEE","FT0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","WALTHAM-LEE (01)",0,0]
[10422,null,"WALTHAM-LEE","FT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","WALTHAM-LEE (01)",4.4620945071616617E-5,0]
[10429,null,"WALTHAM-LEE","FT0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","WALTHAM-LEE (01)",0,0]
[10445,null,"FENTON-MYRNONG","FT0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","FENTON-MYRNONG (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[10465,null,"WOODSTOCK-GLADSTONE","AW0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","WOODSTOCK-GLADSTONE (01)",0,0]
[10467,null,"BAYVIEW-MARIBYRNONG","FT0-026","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","BAYVIEW-MARIBYRNONG (01)",4.4620945071616617E-5,0]
[10487,null,"MOONEE-ASCOT VALE","FT0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","MOONEE-ASCOT VALE (01)",0,0]
[10494,null,"MIDDLE-ASCOT VALE","FT0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","MIDDLE-ASCOT VALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[10510,null,"EAST-HARDING","FT0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","EAST-HARDING (02)",0,0]
[10517,null,"MIDDLE-ASCOT VALE","FT0-026","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","MIDDLE-ASCOT VALE (03)",0,0]
[10533,null,"ROXBURGH-ROTHWELL","FT0-026","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","ROXBURGH-ROTHWELL (01)",4.4620945071616617E-5,0]
[10546,null,"ROXBURGH-ROTHWELL","FT0-026","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","ROXBURGH-ROTHWELL (01)",0,0]
[10559,null,"ROXBURGH-ROTHWELL","FT0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","ROXBURGH-ROTHWELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[10575,null,"ROXBURGH-ROTHWELL","FT0-026","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","ROXBURGH-ROTHWELL (02)",0,0]
[10582,null,"EPSOM-ST LEONARDS","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","EPSOM-ST LEONARDS (02)",4.4620945071616617E-5,0]
[10602,null,"CHARLES-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","CHARLES-EPSOM (02)",4.4620945071616617E-5,0]
[10618,null,"DONCASTER-WALTER","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DONCASTER-WALTER (02)",4.4620945071616617E-5,0]
[10625,null,"DONCASTER-WALTER","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DONCASTER-WALTER (02)",4.4620945071616617E-5,0]
[10640,null,"HILLSIDE-HURTLE","ES0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","HILLSIDE-HURTLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[10647,null,"HILLSIDE-HURTLE","ES0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","HILLSIDE-HURTLE (02)",4.4620945071616617E-5,0]
[10667,null,"NEWSOM-STANFORD","ES0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","NEWSOM-STANFORD (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[10683,null,"JAMES-NAIRN","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","JAMES-NAIRN (02)",4.4620945071616617E-5,0]
[10690,null,"DONCASTER-MYROSS","ES0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DONCASTER-MYROSS (03)",{"$f":"IF(G10691=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J10691=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[10704,null,"MORPHETT-DONCASTER","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MORPHETT-DONCASTER (02)",4.4620945071616617E-5,0]
[10712,null,"CHARLES-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","CHARLES-EPSOM (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[10732,null,"ST LEONARDS-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ST LEONARDS-EPSOM (03)",4.4620945071616617E-5,0]
[10735,null,"ST LEONARDS-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","ST LEONARDS-EPSOM (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[10755,null,"ST LEONARDS-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ST LEONARDS-EPSOM (02)",4.4620945071616617E-5,0]
[10762,null,"FERGUSON-ROSEBERRY","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FERGUSON-ROSEBERRY (04)",4.4620945071616617E-5,0]
[10775,null,"FERGUSON-ROSEBERRY","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FERGUSON-ROSEBERRY (04)",4.4620945071616617E-5,0]
[10797,null,"CHARLES-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","CHARLES-EPSOM (02)",4.4620945071616617E-5,0]
[10800,null,"CHARLES-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","CHARLES-EPSOM (02)",4.4620945071616617E-5,0]
[10820,null,"EGLINTON-ARGYLE","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","EGLINTON-ARGYLE (04)",4.4620945071616617E-5,0]
[10827,null,"EGLINTON-ARGYLE","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","EGLINTON-ARGYLE (03)",4.4620945071616617E-5,0]
[10844,null,"DARLING-EGLINTON","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DARLING-EGLINTON (01)",4.4620945071616617E-5,0]
[10862,null,"GRANDVIEW-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","GRANDVIEW-HOLMES (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[10869,null,"GRANDVIEW-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GRANDVIEW-HOLMES (03)",4.4620945071616617E-5,0]
[10885,null,"WINCHESTER-LAURA","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","WINCHESTER-LAURA (01)",4.4620945071616617E-5,0]
[10892,null,"ATHOL-EDGAR","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ATHOL-EDGAR (02)",4.4620945071616617E-5,0]
[10908,null,"BROWNING-MOORE","NS0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","BROWNING-MOORE (01)",4.4620945071616617E-5,0]
[10923,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","STEELE-STUART (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[10934,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","STEELE-STUART (03)",4.4620945071616617E-5,0]
[10950,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","STEELE-STUART (01)",4.4620945071616617E-5,0]
[10957,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","STEELE-STUART (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[10977,null,"ARDMILLAN-MANTELL","ES0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","ARDMILLAN-MANTELL (01)",0,0]
[10980,null,"SUSSEX-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","SUSSEX-HOLMES (02)",4.4620945071616617E-5,0]
[11002,null,"WAVERLEY-HOLMES","ES0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","WAVERLEY-HOLMES (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[11015,null,"SUSSEX-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","SUSSEX-HOLMES (01)",4.4620945071616617E-5,0]
[11022,null,"PARK-PENLEIGH","ES0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","PARK-PENLEIGH (03)",4.4620945071616617E-5,0]
[11042,null,"JENNINGS-ARDMILLAN","ES0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","JENNINGS-ARDMILLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[11045,null,"JENNINGS-ARDMILLAN","ES0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","JENNINGS-ARDMILLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[11065,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",0,0]
[11073,null,"HALL-MARGARET","NS0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HALL-MARGARET (02)",0,0]
[11087,null,"MCPHERSON-BENT","NS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","MCPHERSON-BENT (01)",4.4620945071616617E-5,0]
[11094,null,"JULIET-BENT","NS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","JULIET-BENT (01)",4.4620945071616617E-5,0]
[11110,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (01)",0,0]
[11130,null,"SALMON-NAPIER","NS0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","SALMON-NAPIER (02)",4.4620945071616617E-5,0]
[11137,null,"SALMON-SCHOFIELD","NS0-016","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","SALMON-SCHOFIELD (01)",0,0]
[11152,null,"SALMON-NAPIER","NS0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","SALMON-NAPIER (02)",4.4620945071616617E-5,0]
[11159,null,"SALMON-NAPIER","NS0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","SALMON-NAPIER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[11175,null,"GLASS-NAPIER","NS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","GLASS-NAPIER (01)",4.4620945071616617E-5,0]
[11195,null,"MACKAY-GLASS","NS0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","MACKAY-GLASS (03)",4.4620945071616617E-5,0]
[11202,null,"NAPIER-BUTLER","NS0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","NAPIER-BUTLER (02)",{"$f":"IF(G11203=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J11203=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[11221,null,"RALEIGH-HODDLE","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",0,0]
[11224,null,"RALEIGH-HODDLE","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","RALEIGH-HODDLE (01)",0,0]
[11240,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HODDLE-FLETCHER (01)",0,0]
[11260,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","HODDLE-FLETCHER (01)",4.4620945071616617E-5,0]
[11267,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (01)",0,0]
[11283,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","Y","N","NS0","HODDLE-FLETCHER (01)",0,0]
[11288,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HODDLE-FLETCHER (01)",0,0]
[11309,null,"VANBERG-TENNYSON","NS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","VANBERG-TENNYSON (01)",4.4620945071616617E-5,0]
[11312,null,"DONALD-LAWSON","NS0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",0,0]
[11332,null,"VANBERG-TENNYSON","NS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","VANBERG-TENNYSON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11348,null,"SHAMROCK-ROSE","ES0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","SHAMROCK-ROSE (03)",4.4620945071616617E-5,0]
[11355,null,"THISTLE-MT ALEXANDER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (01)",0,0]
[11367,null,"FLORENCE-LINCOLN","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FLORENCE-LINCOLN (02)",4.4620945071616617E-5,0]
[11377,null,"FLORENCE-LINCOLN","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","FLORENCE-LINCOLN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[11397,null,"DAISY-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DAISY-BUCKLEY (01)",4.4620945071616617E-5,0]
[11404,null,"MCCRACKEN-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MCCRACKEN-BUCKLEY (01)",4.4620945071616617E-5,0]
[11420,null,"LEAKE-RICHARDSON","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","LEAKE-RICHARDSON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11440,null,"JACKA-MCCRACKEN","ES0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","JACKA-MCCRACKEN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[11450,null,"FLORENCE-LINCOLN","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","FLORENCE-LINCOLN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11462,null,"FORRESTER-HEDDERWICK","ES0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","FORRESTER-HEDDERWICK (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[11469,null,"FORRESTER-HEDDERWICK","ES0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","FORRESTER-HEDDERWICK (02)",0,0]
[11485,null,"MCCRACKEN-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MCCRACKEN-BUCKLEY (01)",4.4620945071616617E-5,0]
[11492,null,"LALUMA-MCCARRON","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","LALUMA-MCCARRON (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[11508,null,"DAISY-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DAISY-BUCKLEY (02)",4.4620945071616617E-5,0]
[11529,null,"DAISY-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DAISY-BUCKLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11534,null,"DAISY-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DAISY-BUCKLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11550,null,"DAISY-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DAISY-BUCKLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11557,null,"DAISY-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DAISY-BUCKLEY (01)",4.4620945071616617E-5,0]
[11577,null,"ST KINNORD-ALMA","ES0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ST KINNORD-ALMA (01)",4.4620945071616617E-5,0]
[11586,null,"HAMLYN-VIDA","ES0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","HAMLYN-VIDA (01)",{"$f":"IF(G11587=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J11587=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[11599,null,"BUCKLEY-ABERDEEN","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BUCKLEY-ABERDEEN (04)",4.4620945071616617E-5,0]
[11615,null,"ARTHUR-FAWKNER","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ARTHUR-FAWKNER (01)",4.4620945071616617E-5,0]
[11622,null,"JEAN-FAWKNER","ES0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","JEAN-FAWKNER (03)",4.4620945071616617E-5,0]
[11642,null,"HIGHRIDGE-ROBERTS","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","HIGHRIDGE-ROBERTS (03)",0,0]
[11658,null,"ROBERTS-MCNAMARA","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ROBERTS-MCNAMARA (01)",0,0]
[11665,null,"MCNAMARA-ROBERTS","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","MCNAMARA-ROBERTS (02)",4.4620945071616617E-5,0]
[11680,null,"HILBERT-HARRINGTON","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILBERT-HARRINGTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[11687,null,"HILBERT-HARRINGTON","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILBERT-HARRINGTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[11707,null,"HILLSIDE-ROBERTS","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILLSIDE-ROBERTS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11710,null,"HILLSIDE-ROBERTS","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILLSIDE-ROBERTS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11730,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","ETZEL-CLYDESDALE (01)",4.4620945071616617E-5,0]
[11744,null,"KING-BOWES","AW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","KING-BOWES (01)",4.4620945071616617E-5,0]
[11752,null,"FRASER-BOWES","AW0-001","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","FRASER-BOWES (01)",4.4620945071616617E-5,0]
[11772,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","ETZEL-CLYDESDALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[11775,null,"NORTH-THOMAS","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","NORTH-THOMAS (01)",4.4620945071616617E-5,0]
[11795,null,"HILBERT-HARRINGTON","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILBERT-HARRINGTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11802,null,"WEST-KINGSLEY","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","WEST-KINGSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11815,null,"HILBERT-HARRINGTON","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILBERT-HARRINGTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11837,null,"HILBERT-HARRINGTON","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILBERT-HARRINGTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11844,null,"HILBERT-HARRINGTON","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","HILBERT-HARRINGTON (01)",4.4620945071616617E-5,0]
[11860,null,"SEXTON-PARER","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","SEXTON-PARER (03)",4.4620945071616617E-5,0]
[11867,null,"SEXTON-PARER","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","SEXTON-PARER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[11883,null,"SEXTON-PARER","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","SEXTON-PARER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11894,null,"SEXTON-PARER","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","SEXTON-PARER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[11909,null,"WARATAH-CAROL","AW0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","WARATAH-CAROL (02)",4.4620945071616617E-5,0]
[11925,null,"JILLIAN-DAWSON","AW0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","JILLIAN-DAWSON (02)",0,0]
[11932,null,"BURVALE-CATHERINE","AW0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","BURVALE-CATHERINE (02)",0,0]
[11948,null,"BIRDWOOD-KEILOR","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BIRDWOOD-KEILOR (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[11963,null,"GREVILLE-KEILOR","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","GREVILLE-KEILOR (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[11974,null,"KERFERD-RALEIGH","ES0-025","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","OSHANNASSY-KERFERD (01)",4.4620945071616617E-5,0]
[11990,null,"BERRY-KEILOR","ES0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BERRY-KEILOR (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[11997,null,"KERFERD-RALEIGH","ES0-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","KERFERD-RALEIGH (01)",0,0]
[12017,null,"ROYAL-BULLA","ES0-025","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ROYAL-BULLA (02)",4.4620945071616617E-5,0]
[12020,null,"ROYAL-BULLA","ES0-025","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ROYAL-BULLA (02)",4.4620945071616617E-5,0]
[12042,null,"BULLA-DUBLIN","ES0-025","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BULLA-DUBLIN (02)",4.4620945071616617E-5,0]
[12055,null,"YORK-NAPIER","NS0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","YORK-NAPIER (04)",0,0]
[12062,null,"HAYES-HOUSTON","NS0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","HAYES-HOUSTON (04)",4.4620945071616617E-5,0]
[12069,null,"HAYES-HOUSTON","NS0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","HAYES-HOUSTON (02)",4.4620945071616617E-5,0]
[12085,null,"WOODLAND-NAPIER","NS0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","WOODLAND-NAPIER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[12105,null,"BOURNIAN-GRAMMAR","NS0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","BOURNIAN-GRAMMAR (01)",4.4620945071616617E-5,0]
[12109,null,"HILLSYDE-LOEMAN","NS0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","HILLSYDE-LOEMAN (01)",4.4620945071616617E-5,0]
[12127,null,"THE CROSSWAY-UPLAND","NS0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","THE CROSSWAY-UPLAND (02)",4.4620945071616617E-5,0]
[12134,null,"THE CROSSWAY-UPLAND","NS0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","THE CROSSWAY-UPLAND (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[12150,null,"KENNEDY-WILLIAM","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KENNEDY-WILLIAM (02)",4.4620945071616617E-5,0]
[12170,null,"MARIE-MURPHY","PV0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","MARIE-MURPHY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[12177,null,"MARIE-MURPHY","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MARIE-MURPHY (01)",4.4620945071616617E-5,0]
[12192,null,"FRANCIS-VINCENT","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","FRANCIS-VINCENT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[12199,null,"FRANCIS-VINCENT","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","FRANCIS-VINCENT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[12215,null,"JOHN-WINIFRED","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","JOHN-WINIFRED (02)",4.4620945071616617E-5,0]
[12235,null,"LEBANON-FENACRE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","LEBANON-FENACRE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12242,null,"LEBANON-FENACRE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","LEBANON-FENACRE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12258,null,"STRATHAIRD-MASCOMA","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","STRATHAIRD-MASCOMA (01)",4.4620945071616617E-5,0]
[12271,null,"CLAYTON-MASCOMA","AW0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","CLAYTON-MASCOMA (01)",4.4620945071616617E-5,0]
[12284,null,"CLAYTON-MASCOMA","AW0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","CLAYTON-MASCOMA (01)",4.4620945071616617E-5,0]
[12287,null,"CLAYTON-MASCOMA","AW0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","CLAYTON-MASCOMA (01)",0,0]
[12307,null,"MENARRA-LAMART","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MENARRA-LAMART (03)",4.4620945071616617E-5,0]
[12323,null,"VISION-MASCOMA","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","VISION-MASCOMA (02)",4.4620945071616617E-5,0]
[12328,null,"LEBANON-ELDORADO","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","LEBANON-ELDORADO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12349,null,"LEBANON-FENACRE","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","LEBANON-FENACRE (04)",4.4620945071616617E-5,0]
[12352,null,"STEWART-PASCOE VALE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","STEWART-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[12372,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[12388,null,"JESSIE-HERMIONE","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","JESSIE-HERMIONE (02)",4.4620945071616617E-5,0]
[12395,null,"SNELL-WATT","PV0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SNELL-WATT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12407,null,"MERBEIN-SUSSEX","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MERBEIN-SUSSEX (01)",4.4620945071616617E-5,0]
[12417,null,"VICTORY-FOSTERS","TMA-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TMA","VICTORY-FOSTERS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[12437,null,"FOSTERS-ELIZA","TMA-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TMA","FOSTERS-ELIZA (04)",4.4620945071616617E-5,0]
[12444,null,"KINGSTON-COLLINSON","TMA-011","2025-02-02","2025-02-08","N","Y","N","N","Y","N","TMA","KINGSTON-COLLINSON (02)",0,0]
[12460,null,"KINGSTON-COLLINSON","TMA-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","TMA","KINGSTON-COLLINSON (01)",0,0]
[12467,null,"KINGSTON-COLLINSON","TMA-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TMA","KINGSTON-COLLINSON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12490,null,"QUINN-CLARKS","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","QUINN-CLARKS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12502,null,"MOYANGUL-GUNGARLAN","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","MOYANGUL-GUNGARLAN (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[12509,null,"CUDGEWA-BORVA","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","CUDGEWA-BORVA (01)",4.4620945071616617E-5,0]
[12525,null,"CUDGEWA-BORVA","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","CUDGEWA-BORVA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[12532,null,"CUDGEWA-BORVA","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","CUDGEWA-BORVA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[12552,null,"CENTREWAY-WINGARA","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","CENTREWAY-WINGARA (03)",4.4620945071616617E-5,0]
[12557,null,"QUINN-CLARKS","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","QUINN-CLARKS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12574,null,"PAMELA-HERBERT","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","PAMELA-HERBERT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12590,null,"DAVID-RACHELLE","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","DAVID-RACHELLE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[12597,null,"QUINN-NOGA","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","QUINN-NOGA (02)",4.4620945071616617E-5,0]
[12617,null,"QUINN-NOGA","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","QUINN-NOGA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[12626,null,"QUINN-NOGA","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NA",4.4620945071616617E-5,9.4304036212749905E-5]
[12639,null,"DAVID-RACHELLE","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","DAVID-RACHELLE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[12655,null,"QUINN-NOGA","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","QUINN-NOGA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[12662,null,"JUDITH-BREES","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","JUDITH-BREES (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12682,null,"ROSEHILL-TALBOT","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ROSEHILL-TALBOT (01)",0,0]
[12685,null,"ROSEHILL-TALBOT","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ROSEHILL-TALBOT (01)",0,0]
[12705,null,"ELLEN-RACHELLE","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","ELLEN-RACHELLE (01)",4.4620945071616617E-5,0]
[12711,null,"ELLEN-RACHELLE","AW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ELLEN-RACHELLE (02)",0,0]
[12727,null,"SALTAU-MILLEARA","AW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","SALTAU-MILLEARA (01)",0,0]
[12747,null,"BUCKLEY-THE CROSSWAY","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","BUCKLEY-THE CROSSWAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12750,null,"THE CROSSWAY-VISTA","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","THE CROSSWAY-VISTA (03)",4.4620945071616617E-5,0]
[12770,null,"THOMPSON-NORTH","BY0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","THOMPSON-NORTH (01)",4.4620945071616617E-5,0]
[12784,null,"HOLDEN-MILITARY","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","HOLDEN-MILITARY (01)",4.4620945071616617E-5,0]
[12792,null,"RIVIERA-MILLEARA","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","RIVIERA-MILLEARA (03)",4.4620945071616617E-5,0]
[12812,null,"DAVIS-MILITARY","BY0-014","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","BY0","DAVIS-MILITARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12819,null,"DAVIS-MILITARY","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","DAVIS-MILITARY (03)",4.4620945071616617E-5,0]
[12835,null,"ARBOR-MACEY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","ARBOR-MACEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[12842,null,"ARBOR-MACEY","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","ARBOR-MACEY (01)",4.4620945071616617E-5,0]
[12855,null,"GLENSIDE-CANNING","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","GLENSIDE-CANNING (01)",4.4620945071616617E-5,0]
[12864,null,"DOYLE-RIDLEY","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","DOYLE-RIDLEY (01)",4.4620945071616617E-5,0]
[12884,null,"DOYLE-NORTH","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","DOYLE-NORTH (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12900,null,"ROGERSON-THOMPSON","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","ROGERSON-THOMPSON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12907,null,"ROGERSON-THOMPSON","BY0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","ROGERSON-THOMPSON (02)",4.4620945071616617E-5,0]
[12923,null,"RHONDA-CANNING","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","RHONDA-CANNING (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12934,null,"RHONDA-CANNING","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","RHONDA-CANNING (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12949,null,"ROGERSON-THOMPSON","BY0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","ROGERSON-THOMPSON (02)",4.4620945071616617E-5,0]
[12965,null,"RHONDA-CANNING","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","RHONDA-CANNING (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[12972,null,"CHRISTINA-BARBARA","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","CHRISTINA-BARBARA (03)",4.4620945071616617E-5,0]
[12992,null,"CHRISTINA-BARBARA","BY0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BY0","CHRISTINA-BARBARA (01)",0,0]
[13003,null,"CHRISTINA-BARBARA","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","CHRISTINA-BARBARA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[13014,null,"WHITE-DUKE","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","WHITE-DUKE (02)",4.4620945071616617E-5,0]
[13030,null,"ARTHUR-FAWKNER","ES0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","ARTHUR-FAWKNER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[13037,null,"CLIFTON-JEAN","ES0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","NA",4.4620945071616617E-5,9.4304036212749905E-5]
[13044,null,"CLIFTON-JEAN","ES0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","CLIFTON-JEAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[13060,null,"PROSPECT-BUCKLEY","ES0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","PROSPECT-BUCKLEY (01)",4.4620945071616617E-5,0]
[13070,null,"CLYDEBANK-AFTON","ES0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","CLYDEBANK-AFTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[13082,null,"CLYDEBANK-AFTON","ES0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","CLYDEBANK-AFTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13102,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13109,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13125,null,"NEWMAN-HOTHAM","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NEWMAN-HOTHAM (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13145,null,"THE AVENUE-KEILOR","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","THE AVENUE-KEILOR (02)",4.4620945071616617E-5,0]
[13149,null,"NEWMAN-HOTHAM","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","NEWMAN-HOTHAM (02)",4.4620945071616617E-5,0]
[13167,null,"FARRELL-RYDER","AW0-006","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","AW0","FARRELL-RYDER (03)",4.4620945071616617E-5,0]
[13174,null,"HOTHAM-RYDER No. 2","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HOTHAM-RYDER No. 2 (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[13190,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[13210,null,"GARNET-MURIEL","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GARNET-MURIEL (03)",4.4620945071616617E-5,0]
[13217,null,"KELVIN-ALBERT","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","KELVIN-ALBERT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13232,null,"DIAMOND-ROSEHILL","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[13239,null,"DIAMOND-ROSEHILL","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13259,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-NOLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13262,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-NOLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13282,null,"DEAKIN-SPENCER","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DEAKIN-SPENCER (03)",4.4620945071616617E-5,0]
[13298,null,"BRADSHAW-MARY","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BRADSHAW-MARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13311,null,"BIRDWOOD-KEILOR","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BIRDWOOD-KEILOR (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13324,null,"BRADSHAW-MARY","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BRADSHAW-MARY (03)",4.4620945071616617E-5,0]
[13327,null,"BRADSHAW-MARY","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BRADSHAW-MARY (03)",4.4620945071616617E-5,0]
[13347,null,"GRAVES-MARKET","ES0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GRAVES-MARKET (03)",4.4620945071616617E-5,0]
[13363,null,"GRAVES-MARKET","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","GRAVES-MARKET (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13368,null,"GRAVES-MARKET","ES0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GRAVES-MARKET (02)",4.4620945071616617E-5,0]
[13389,null,"FORRESTER-HEDDERWICK","ES0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","FORRESTER-COOPER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[13392,null,"FORRESTER-HEDDERWICK","ES0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FORRESTER-HEDDERWICK (01)",4.4620945071616617E-5,0]
[13412,null,"BECKET-ANSELM","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","BECKET-ANSELM (03)",4.4620945071616617E-5,0]
[13419,null,"VALLEY-AUGUSTINE","PV0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","PV0","VALLEY-AUGUSTINE (02)",0,0]
[13435,null,"CHAPMAN-BELAIR","PV0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","CHAPMAN-BELAIR (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[13447,null,"RIDGEWAY-MARRSON","PV0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","RIDGEWAY-MARRSON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13457,null,"MOONEE-VALLEY","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MOONEE-VALLEY (02)",4.4620945071616617E-5,0]
[13477,null,"MOONEE-VALLEY","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MOONEE-VALLEY (02)",4.4620945071616617E-5,0]
[13484,null,"MOONEE-VALLEY","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MOONEE-VALLEY (02)",4.4620945071616617E-5,0]
[13500,null,"CENTRE WAY-FRAN","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CENTRE WAY-FRAN (04)",4.4620945071616617E-5,0]
[13507,null,"CENTRE WAY-FRAN","PV0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","CENTRE WAY-FRAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[13530,null,"CHAPMAN-BELAIR","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CHAPMAN-BELAIR (01)",4.4620945071616617E-5,0]
[13542,null,"KENNEDY-WILLIAM","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KENNEDY-WILLIAM (02)",4.4620945071616617E-5,0]
[13549,null,"KENNEDY-WILLIAM","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KENNEDY-WILLIAM (01)",4.4620945071616617E-5,0]
[13565,null,"KENNEDY-WILLIAM","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KENNEDY-WILLIAM (01)",4.4620945071616617E-5,0]
[13572,null,"ILLAWARRA-PASCOEVALE","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","ILLAWARRA-PASCOEVALE (01)",4.4620945071616617E-5,0]
[13592,null,"KALANG-PLUMPTON","PV0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","KALANG-PLUMPTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13597,null,"KALANG-PLUMPTON","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KALANG-PLUMPTON (02)",4.4620945071616617E-5,0]
[13614,null,"KALANG-PLUMPTON","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KALANG-PLUMPTON (02)",4.4620945071616617E-5,0]
[13630,null,"KALANG-PLUMPTON","PV0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","KALANG-PLUMPTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13637,null,"PEARL-WHEATSHEAF","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","PEARL-WHEATSHEAF (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[13657,null,"THE GRANGE-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","THE GRANGE-YALLAMBIE (03)",4.4620945071616617E-5,0]
[13660,null,"ASH-WIDFORD","PV0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","ASH-WIDFORD (01)",4.4620945071616617E-5,0]
[13676,null,"HILTON-WEST","PV0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-WEST (02)",4.4620945071616617E-5,0]
[13686,null,"CONNELL-HILTON","PV0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CONNELL-HILTON (01)",4.4620945071616617E-5,0]
[13702,null,"HILTON-WIDFORD","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-WIDFORD (03)",4.4620945071616617E-5,0]
[13722,null,"BEATTY-MELBOURNE","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","BEATTY-MELBOURNE (03)",4.4620945071616617E-5,0]
[13725,null,"BEATTY-MELBOURNE","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","BEATTY-MELBOURNE (03)",4.4620945071616617E-5,0]
[13745,null,"HILTON-CHURCHILL","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-CHURCHILL (01)",4.4620945071616617E-5,0]
[13751,null,"HILTON-CHURCHILL","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-CHURCHILL (01)",4.4620945071616617E-5,0]
[13767,null,"EVELL-MORLEY","PV0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","EVELL-MORLEY (02)",4.4620945071616617E-5,0]
[13787,null,"WARD-MAY","PV0-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","PV0","WARD-MAY (02)",0,0]
[13790,null,"WEST-JOHN","PV0-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","PV0","WEST-JOHN (02)",0,0]
[13810,null,"EVELL-OGDEN","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","EVELL-OGDEN (02)",4.4620945071616617E-5,0]
[13824,null,"EVELL-MORLEY","PV0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","EVELL-MORLEY (01)",4.4620945071616617E-5,0]
[13832,null,"NORTH-RICHMOND","PV0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","NORTH-RICHMOND (04)",4.4620945071616617E-5,0]
[13839,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,0]
[13859,null,"KATOOMBA-SUTHERLAND","PV0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KATOOMBA-SUTHERLAND (04)",4.4620945071616617E-5,0]
[13875,null,"ANGUS-MIDDLE","PV0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","ANGUS-MIDDLE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[13882,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[13895,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[13904,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,0]
[13924,null,"BERRY-LORNE","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BERRY-LORNE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[13940,null,"JUKES-LANIGAN","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","JUKES-LANIGAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[13947,null,"JUKES-LANIGAN","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","JUKES-LANIGAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[13967,null,"JAMES-MAJOR","CN0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","JAMES-MAJOR (02)",4.4620945071616617E-5,0]
[13974,null,"PITT-MAJOR","CN0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","PITT-MAJOR (03)",4.4620945071616617E-5,0]
[13989,null,"TYRELL-MCBRYDE","CN0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","TYRELL-MCBRYDE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[14005,null,"WINN-MAJOR","CN0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","WINN-MAJOR (02)",4.4620945071616617E-5,0]
[14012,null,"MAJOR-HUME","CN0-004","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MAJOR-HUME (04)",4.4620945071616617E-5,0]
[14019,null,"DENYS-GLYNDA","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","DENYS-GLYNDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[14035,null,"LOWSON-MINONA","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","LOWSON-MINONA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[14053,null,"DISNEY-HUME","CN0-004","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DISNEY-HUME (04)",4.4620945071616617E-5,0]
[14057,null,"DISNEY-HUME","CN0-004","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DISNEY-HUME (04)",4.4620945071616617E-5,0]
[14077,null,"DENYS-GLYNDA","CN0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DENYS-GLYNDA (03)",4.4620945071616617E-5,0]
[14084,null,"JUKES-LANIGAN","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","JUKES-LANIGAN (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[14100,null,"BECCLES-ANDERSON","CN0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BECCLES-ANDERSON (03)",4.4620945071616617E-5,0]
[14110,null,"BECCLES-ANDERSON","CN0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BECCLES-ANDERSON (02)",4.4620945071616617E-5,0]
[14126,null,"PALMER-HEDLEY","CN0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","PALMER-HEDLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[14142,null,"PALMER-HEDLEY","CN0-004","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","PALMER-HEDLEY (02)",4.4620945071616617E-5,0]
[14149,null,"CAMP 50-HUME","BMS-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","CAMP 50-HUME (01)",0,0]
[14165,null,"WODONGA-CUTHBERT","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","WODONGA-CUTHBERT (01)",4.4620945071616617E-5,0]
[14185,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",0,0]
[14189,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","Y","N","BMS","ELLIOT-GRAHAM (03)",0,0]
[14207,null,"WAVERLEY-ELECTRIC","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","WAVERLEY-ELECTRIC (02)",0,0]
[14214,null,"DACELO-GIBSON","BMS-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","BMS","DACELO-GIBSON (02)",4.4620945071616617E-5,0]
[14230,null,"JOFFRE-KITCHENER","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","JOFFRE-KITCHENER (03)",4.4620945071616617E-5,0]
[14237,null,"JOFFRE-KITCHENER","BD0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","JOFFRE-KITCHENER (02)",0,0]
[14257,null,"LYDIA-DUNSTAN","BD0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BD0","LYDIA-DUNSTAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[14272,null,"DUNSTAN-BARRY","BD0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","DUNSTAN-BARRY (02)",4.4620945071616617E-5,0]
[14279,null,"WASHINGTON-DOY","BD0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","WASHINGTON-DOY (01)",0,0]
[14299,null,"HERBERT-GARNER","BD0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","HERBERT-GARNER (01)",0,0]
[14302,null,"HAMPDEN-GEACH","BMS-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","HAMPDEN-GEACH (01)",0,0]
[14322,null,"YERING-GUILDFORD","BD0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","YERING-GUILDFORD (01)",0,0]
[14338,null,"YERING-GUILDFORD","BD0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","YERING-GUILDFORD (02)",{"$f":"IF(G14339=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J14339=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[14351,null,"WESTMERE-WARNE","BD0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","WESTMERE-WARNE (02)",4.4620945071616617E-5,0]
[14364,null,"WESTMERE-WARNE","BD0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","WESTMERE-WARNE (02)",0,0]
[14367,null,"WESTMERE-WARNE","BD0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BD0","WESTMERE-WARNE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[14387,null,"WARRAGUL-LISMORE","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","WARRAGUL-LISMORE (01)",4.4620945071616617E-5,0]
[14394,null,"WARRAGUL-LISMORE","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","WARRAGUL-LISMORE (01)",4.4620945071616617E-5,0]
[14410,null,"WARRAGUL-LISMORE","BD0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","WARRAGUL-LISMORE (02)",0,0]
[14418,null,"MCIVOR-KIEWA","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","MCIVOR-KIEWA (02)",4.4620945071616617E-5,0]
[14432,null,"YEA-KIEWA","BD0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","YEA-KIEWA (01)",0,0]
[14452,null,"WARANGA-BLAIR","BD0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BD0","WARANGA-BLAIR (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[14459,null,"FREELAND-ELEANOR","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","FREELAND-ELEANOR (02)",0,0]
[14475,null,"LANDY-LICHFIELD","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","LANDY-LICHFIELD (02)",0,0]
[14487,null,"BROOK-JOHNSTONE","BMS-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","BMS","BROOK-JOHNSTONE (01)",4.4620945071616617E-5,0]
[14497,null,"LORRAINE-JOHNSTONE","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","LORRAINE-JOHNSTONE (02)",0,0]
[14517,null,"TIMBOON-RIPPLEBROOK","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","TIMBOON-RIPPLEBROOK (02)",0,0]
[14524,null,"ALMA-CHANDLER","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","ALMA-CHANDLER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[14540,null,"DARLING-FULHAM","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","DARLING-FULHAM (01)",4.4620945071616617E-5,0]
[14547,null,"CUDGEWA-BORVA","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","CUDGEWA-BORVA (01)",4.4620945071616617E-5,0]
[14566,null,"THICKINS-NORTHUMBERLAND","PV0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","THICKINS-NORTHUMBERLAND (02)",4.4620945071616617E-5,0]
[14582,null,"BANBURY-HURSLEY","ST0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ST0","BANBURY-HURSLEY (01)",4.4620945071616617E-5,0]
[14589,null,"SUMMERHILL RD-P192","COO-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","COO","SUMMERHILL RD-P192 (00)",0,0]
[14605,null,"PINES-KEYSBOROUGH","ST0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ST0","PINES-KEYSBOROUGH (02)",4.4620945071616617E-5,0]
[14612,null,"ROCK-DIANNE","ST0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ST0","ROCK-DIANNE (02)",4.4620945071616617E-5,0]
[14632,null,"EASTGATE-HOTHLYN","ST0-022","2025-02-02","2025-02-08","N","N","N","Y","N","N","ST0","EASTGATE-HOTHLYN (01)",0,9.4304036212749905E-5]
[14637,null,"WOODBURN-CAMMS","BD0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","WOODBURN-CAMMS (02)",0,0]
[14654,null,"PASCOE VALE-BENDOC","BD0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BD0","PASCOE VALE-BENDOC (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[14670,null,"PASCOE VALE-BENDOC","BD0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","PASCOE VALE-BENDOC (02)",0,0]
[14677,null,"PASCOE VALE-BENDOC","BD0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","PASCOE VALE-BENDOC (02)",4.4620945071616617E-5,0]
[14697,null,"COOPER ST-P43","ST0-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","COOPER ST-P43 (01)",0,0]
[14700,null,"SHADFORTH-RALEIGH","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","SHADFORTH-RALEIGH (02)",4.4620945071616617E-5,0]
[14716,null,"CHISHOLM-ERINBANK","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","CHISHOLM-ERINBANK (02)",4.4620945071616617E-5,0]
[14726,null,"CHISHOLM-ERINBANK","BD0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BD0","CHISHOLM-ERINBANK (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[14742,null,"ERINBANK-DOBIES","BD0-007","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","BD0","ERINBANK-DOBIES (02)",4.4620945071616617E-5,0]
[14762,null,"BEECROFT-ASHFORD","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","BEECROFT-ASHFORD (01)",0,0]
[14765,null,"BRAMCOTE-FORMAN","AW0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","BRAMCOTE-FORMAN (01)",0,0]
[14785,null,"LARGS-MOTHERWELL","COO-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","COO","LARGS-MOTHERWELL (01)",0,0]
[14795,null,"MICKLEHAM RD-P0250","COO-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","COO","MICKLEHAM RD-P0250 (00)",0,0]
[14807,null,"HEVERSHAM-BIRTLEY","COO-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","HEVERSHAM-BIRTLEY (03)",4.4620945071616617E-5,0]
[14814,null,"RUDSTONE-ABBEY","COO-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","RUDSTONE-ABBEY (02)",4.4620945071616617E-5,0]
[14834,null,"ARNCLIFFE-LEEDS","COO-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","ARNCLIFFE-LEEDS (02)",4.4620945071616617E-5,0]
[14850,null,"KONAGADERRA-TEA ROOM","COO-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","KONAGADERRA-TEA ROOM (00)",{"$f":"IF(G14851=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J14851=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[14864,null,"DIANNE-DAWSON","TMA-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","TMA","DIANNE-DAWSON (02)",4.4620945071616617E-5,0]
[14872,null,"FINNINGLEY-MARHAM","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FINNINGLEY-MARHAM (02)",0,0]
[14879,null,"HANDSWORTH-LACKENHTH","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","HANDSWORTH-LACKENHTH (02)",0,0]
[14899,null,"FREIGHT-CUSTOM","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (02)",0,0]
[14915,null,"ELLESMERE-CARRICK","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","ELLESMERE-CARRICK (02)",4.4620945071616617E-5,0]
[14922,null,"DUNFIELD-BERESFORD","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","DUNFIELD-BERESFORD (01)",4.4620945071616617E-5,0]
[14935,null,"DUNFIELD-BERESFORD","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","DUNFIELD-BERESFORD (01)",4.4620945071616617E-5,0]
[14944,null,"HENLEY-CLARKE","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","HENLEY-CLARKE (02)",4.4620945071616617E-5,0]
[14964,null,"GREENACRE-AYLESBURY","AW0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","GREENACRE-AYLESBURY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[14980,null,"SOUTH CIRCULAR-CARRICK","AW0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","SOUTH CIRCULAR-CARRICK (02)",0,0]
[14987,null,"PRIOR-TAYLOR","AW0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","PRIOR-TAYLOR (02)",0,0]
[14994,null,"SAMARA-ELMHURST","AW0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","SAMARA-ELMHURST (02)",0,0]
[15014,null,"HARCOURT-SHERBOURNE","AW0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","HARCOURT-SHERBOURNE (02)",0,0]
[15029,null,"WILTSHIRE-DUNFIELD","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","WILTSHIRE-DUNFIELD (02)",4.4620945071616617E-5,0]
[15032,null,"WILTSHIRE-DUNFIELD","BD0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","WILTSHIRE-DUNFIELD (02)",4.4620945071616617E-5,0]
[15052,null,"HARDY-SNAEFELL","AW0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","HARDY-SNAEFELL (01)",0,0]
[15059,null,"WARATAH-CAROL","AW0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","SYCAMORE-BROADMEADOWS (01)",4.4620945071616617E-5,0]
[15075,null,"DAVID-RACHELLE","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","DAVID-RACHELLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[15093,null,"THE CROSSWAY-VISTA","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","THE CROSSWAY-VISTA (02)",4.4620945071616617E-5,0]
[15101,null,"RIVIERA-WARRICK","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","RIVIERA-WARRICK (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[15117,null,"BUCKLEY-THE CROSSWAY","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","BUCKLEY-THE CROSSWAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[15124,null,"BUCKLEY-THE CROSSWAY","BY0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","BUCKLEY-THE CROSSWAY (02)",4.4620945071616617E-5,0]
[15140,null,"THE CROSSWAY-PARK","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","THE CROSSWAY-PARK (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[15160,null,"THE CROSSWAY-PARK","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","THE CROSSWAY-PARK (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[15172,null,"THE CROSSWAY-PARK","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","THE CROSSWAY-PARK (02)",4.4620945071616617E-5,0]
[15182,null,"ARCADE-PROSPECT","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","ARCADE-PROSPECT (02)",4.4620945071616617E-5,0]
[15189,null,"THE CROSSWAY-PARK","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","THE CROSSWAY-PARK (02)",4.4620945071616617E-5,0]
[15205,null,"CASTLETON 21-HAVILAH","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CASTLETON 21-HAVILAH (02)",4.4620945071616617E-5,0]
[15212,null,"GLADSTONE-ASCOT VALE","NS0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","GLADSTONE-ASCOT VALE (05)",0,0]
[15229,null,"GRAVES-MARKET","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","GRAVES-MARKET (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[15247,null,"DUNROSSIL-GORTON","SBY-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","DUNROSSIL-GORTON (03)",0,0]
[15254,null,"LATROBE-MENZIES","SBY-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SBY","LATROBE-MENZIES (01)",4.4620945071616617E-5,0]
[15274,null,"TULSA-MEDINAH","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","TULSA-MEDINAH (01)",0,0]
[15277,null,"FLINDERS-WENTWORTH","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","FLINDERS-WENTWORTH (02)",0,0]
[15297,null,"NEILL-MOUNSEY","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","NEILL-MOUNSEY (02)",0,0]
[15312,null,"PASLEY-NEILL","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","PASLEY-NEILL (02)",0,0]
[15319,null,"BURKE-FLINDERS","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (03)",0,0]
[15339,null,"BURKE-FLINDERS","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (03)",0,0]
[15342,null,"ELIZABETH-LEICHARDT","SBY-032","2025-02-02","2025-02-08","Y","N","N","N","N","N","SBY","ELIZABETH-LEICHARDT (02)",4.4620945071616617E-5,0]
[15362,null,"CHARTER-WILSONS","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","CHARTER-WILSONS (02)",{"$f":"IF(G15363=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J15363=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[15378,null,"GAP-PRESTON","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","GAP-PRESTON (01)",0,0]
[15379,null,"GAP-PRESTON","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","GAP-PRESTON (01)",0,0]
[15391,null,"RESERVOIR-WILSON","SBY-032","2025-02-02","2025-02-08","Y","N","N","N","N","N","SBY","RESERVOIR-WILSON (02)",4.4620945071616617E-5,0]
[15407,null,"CORNISH-LIGAR","SBY-012","2025-02-02","2025-02-08","N","N","N","Y","N","N","SBY","CORNISH-LIGAR (01)",0,9.4304036212749905E-5]
[15427,null,"BENSON RD-P9A1","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BENSON RD-P9A1 (02)",0,0]
[15434,null,"TWEDDLE RD-P6","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","TWEDDLE RD-P6 (00)",0,0]
[15450,null,"GISBORNE MELTON RD-P20W2","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","GISBORNE MELTON RD-P20W2 (00)",0,0]
[15458,null,"OUTAWOOD RISE-P1","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","OUTAWOOD RISE-P1 (00)",0,0]
[15472,null,"RUNNYMEDE LA-P5","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","RUNNYMEDE LA-P5 (00)",0,0]
[15492,null,"KERRIE RD-P7","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","KERRIE RD-P7 (00)",0,0]
[15499,null,"SETTLEMENT RD-P33E3","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","SETTLEMENT RD-P33E3 (00)",0,0]
[15515,null,"RACECOURSE-EMU","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","RACECOURSE-EMU (00)",0,0]
[15522,null,"STOKES LA EAST-P4","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","STOKES LA EAST-P4 (00)",0,0]
[15537,null,"FENTON CLOSE-P1","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","FENTON CLOSE-P1 (00)",0,0]
[15557,null,"CALDER FWY-P15","SHM-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","CALDER FWY-P15 (00)",0,0]
[15564,null,"HIGHLAND RD-P4","SA0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","SA0","HIGHLAND RD-P4 (00)",0,0]
[15580,null,"CHANDOS-BREADALBANE","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","CHANDOS-BREADALBANE (02)",4.4620945071616617E-5,0]
[15587,null,"KINTORE-ALDRIDGE","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","KINTORE-ALDRIDGE (03)",0,0]
[15606,null,"TURNER-MENZIES","SBY-012","2025-02-02","2025-02-08","N","Y","N","N","Y","N","SBY","TURNER-MENZIES (01)",0,0]
[15609,null,"HIGGINS-MCKELL","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","HIGGINS-MCKELL (02)",0,0]
[15629,null,"HIGGINS-MCKELL","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","HIGGINS-MCKELL (02)",0,0]
[15645,null,"CULLEN-MARY","YVE-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","YVE","CULLEN-MARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[15652,null,"TAYLOR-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",0,0]
[15672,null,"WARRAGUL-LISMORE","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","WARRAGUL-LISMORE (01)",4.4620945071616617E-5,0]
[15677,null,"HAMLYN-VIDA","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","HAMLYN-VIDA (01)",4.4620945071616617E-5,0]
[15694,null,"PORTER-DOUGHARTY","NH0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","PORTER-DOUGHARTY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[15701,null,"LATROBE-YARRA","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","LATROBE-YARRA (01)",4.4620945071616617E-5,0]
[15717,null,"GRAVES-MARKET","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","GRAVES-MARKET (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[15737,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[15740,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,0]
[15756,null,"DENYS-GLYNDA","CN0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DENYS-GLYNDA (02)",4.4620945071616617E-5,0]
[15766,null,"VIEWBANK-BREES","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","VIEWBANK-BREES (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[15782,null,"DAISY-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DAISY-BUCKLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[15789,null,"SPAVIN DR-P9","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","SPAVIN DR-P9 (00)",0,0]
[15809,null,"EVANS 60-BROOK","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","EVANS 60-BROOK (04)",0,0]
[15825,null,"MANUKA-LIGHTWOOD","BD0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","MANUKA-LIGHTWOOD (02)",0,0]
[15835,null,"ROSTELLA-NORWOOD","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","ROSTELLA-NORWOOD (01)",4.4620945071616617E-5,0]
[15847,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[15854,null,"BELMONT-BAYSWATER","FT0-035","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","BELMONT-BAYSWATER (02)",0,0]
[15874,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",{"$f":"IF(G15875=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J15875=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[15890,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[15897,null,"PASLEY-NEILL","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","PASLEY-NEILL (02)",0,0]
[15906,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-NOLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[15919,null,"PUNJEL-CALDER","SHM-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","PUNJEL-CALDER (00)",0,0]
[15939,null,"DENYS-GLYNDA","CN0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DENYS-GLYNDA (01)",4.4620945071616617E-5,0]
[15955,null,"GRAHAM-GIBSON","BMS-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","BMS","GRAHAM-GIBSON (02)",4.4620945071616617E-5,0]
[15962,null,"BERRY-KEILOR","ES0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BERRY-KEILOR (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[15971,null,"NEWLYN-PEMBROKE","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","NEWLYN-PEMBROKE (03)",0,0]
[15984,null,"DUNDEE-MEADE","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","DUNDEE-MEADE (02)",4.4620945071616617E-5,0]
[16004,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-NOLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[16007,null,"STEWART-PASCOE VALE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","STEWART-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[16027,null,"DUNDEE-MEADE","SHM-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","DUNDEE-MEADE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[16034,null,"WARATAH-CAROL","AW0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","SYCAMORE-BROADMEADOWS (01)",4.4620945071616617E-5,0]
[16054,null,"HOTHAM-RYDER No. 2","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HOTHAM-RYDER No. 2 (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[16069,null,"RACECOURSE RD-P6","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","RACECOURSE RD-P6 (00)",0,0]
[16072,null,"KELVIN-ALBERT","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","KELVIN-ALBERT (02)",4.4620945071616617E-5,0]
[16092,null,"HOFFMANS-KEILOR","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","HOFFMANS-KEILOR (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[16099,null,"BUCKLEY-ABERDEEN","ES0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BUCKLEY-ABERDEEN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[16115,null,"BUCKLEY-THE CROSSWAY","BY0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","BUCKLEY-THE CROSSWAY (02)",4.4620945071616617E-5,0]
[16133,null,"LAUREL-TYLER","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","LAUREL-TYLER (04)",4.4620945071616617E-5,0]
[16141,null,"BLAKE-DAVIS","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BLAKE-DAVIS (02)",4.4620945071616617E-5,0]
[16157,null,"GALLERY GATE-PERONINE","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GALLERY GATE-PERONINE (03)",4.4620945071616617E-5,0]
[16164,null,"GALLERY GATE-PERONINE","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GALLERY GATE-PERONINE (03)",4.4620945071616617E-5,0]
[16180,null,"COURTIS-MELBOURNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","COURTIS-MELBOURNE (01)",4.4620945071616617E-5,0]
[16187,null,"ALAMEIN-SOUTHERN","EPN-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","ALAMEIN-SOUTHERN (02)",0,0]
[16200,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (03)",4.4620945071616617E-5,0]
[16222,null,"CARWARP-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CARWARP-ERSKINE (02)",4.4620945071616617E-5,0]
[16229,null,"LAUREL-TYLER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","LAUREL-TYLER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[16249,null,"LEBANON-FENACRE","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","LEBANON-FENACRE (02)",4.4620945071616617E-5,0]
[16252,null,"ARNCLIFFE-WATERHOUSE","COO-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","ARNCLIFFE-WATERHOUSE (04)",4.4620945071616617E-5,0]
[16272,null,"OLIVE-SYLVAN","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","OLIVE-SYLVAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[16283,null,"BREX-RADFORD","TT0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","BREX-RADFORD (00)",0,0]
[16294,null,"THE GRANGE-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","THE GRANGE-YALLAMBIE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[16314,null,"ARDEN-LOWER PLENTY","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","ARDEN-LOWER PLENTY (01)",4.4620945071616617E-5,0]
[16317,null,"WESTMINSTER-MILITARY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","WESTMINSTER-MILITARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[16337,null,"STEWART-PASCOE VALE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","STEWART-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[16352,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[16359,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[16366,null,"JACKSON-STURDEE","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","JACKSON-STURDEE (02)",4.4620945071616617E-5,0]
[16382,null,"COLLEGE-BREES","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","COLLEGE-BREES (03)",4.4620945071616617E-5,0]
[16402,null,"RUTHERFORD-LILLIAN","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","RUTHERFORD-LILLIAN (02)",4.4620945071616617E-5,0]
[16409,null,"GRAHAM-GLEN ALLAN","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","GRAHAM-GLEN ALLAN (03)",0,0]
[16419,null,"DEEP CREEK-REDGUM","COO-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","COO","DEEP CREEK-REDGUM (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[16431,null,"BOND-LIBERTY","EP0-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","FORD-SPARKFORD (01)",0,0]
[16447,null,"BERRIMA-ROSANNA","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BERRIMA-ROSANNA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[16467,null,"PUNJEL-CALDER","SHM-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","PUNJEL-CALDER (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[16474,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[16490,null,"STEVEDORE-STRAND","NT0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","STEVEDORE-STRAND (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[16498,null,"MCCRAE-ELSEY","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","MCCRAE-ELSEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[16512,null,"EFFINGHAM-WILKINS","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","EFFINGHAM-WILKINS (01)",4.4620945071616617E-5,0]
[16532,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,0]
[16539,null,"BRASSEY-PYALONG","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BRASSEY-PYALONG (01)",4.4620945071616617E-5,0]
[16555,null,"BRADLEY-MASON","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BRADLEY-MASON (01)",4.4620945071616617E-5,0]
[16562,null,"JELLICOE-WATERDALE","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","JELLICOE-WATERDALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[16577,null,"NORTH-THOMAS","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NORTH-THOMAS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[16584,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[16604,null,"ANDERSON-BOLINGBROKE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","ANDERSON-BOLINGBROKE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[16620,null,"WALHALLA-MORELAND","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WALHALLA-MORELAND (01)",4.4620945071616617E-5,0]
[16627,null,"MARY-ROBERTS","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MARY-ROBERTS (01)",4.4620945071616617E-5,0]
[16647,null,"PUNJEL-CALDER","SHM-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","PUNJEL-CALDER (00)",0,0]
[16660,null,"CARWARP-MAY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CARWARP-MAY (04)",4.4620945071616617E-5,0]
[16669,null,"OUTLOOK CRES-P9","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","OUTLOOK CRES-P9 (00)",0,0]
[16676,null,"RIDDELL RD-P74","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","RIDDELL RD-P74 (00)",0,0]
[16692,null,"DUNDEE-MEADE","SHM-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","DUNDEE-MEADE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[16712,null,"HOTHAM-RYDER No. 2","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","HOTHAM-RYDER No. 2 (03)",4.4620945071616617E-5,0]
[16717,null,"GOULBURN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","GOULBURN-PALMERSTON (03)",4.4620945071616617E-5,0]
[16734,null,"WATTLEVALLEY-JAMES","SHM-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","WATTLEVALLEY-JAMES (01)",4.4620945071616617E-5,0]
[16741,null,"FOCH-QUEEN","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","FOCH-QUEEN (03)",4.4620945071616617E-5,0]
[16757,null,"ALBERT-DUNDAS","EP0-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (01)",0,0]
[16764,null,"DUNDEE-MEADE","SHM-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","DUNDEE-MEADE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[16780,null,"DROMANA-MATTHEWS","AW0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","DROMANA-MATTHEWS (02)",0,0]
[16796,null,"HUTCHESON-THE STRAND","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","HUTCHESON-THE STRAND (02)",0,0]
[16806,null,"KONAGADERRA RD-P46E2","COO-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","COO","KONAGADERRA RD-P46E2 (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[16822,null,"WARATAH-CAROL","AW0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","SYCAMORE-BROADMEADOWS (01)",4.4620945071616617E-5,0]
[16829,null,"WILLOWTREE-PERSICA","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (01)",0,0]
[16849,null,"MCNAMARA-ELIZABETH","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MCNAMARA-ELIZABETH (01)",4.4620945071616617E-5,0]
[16865,null,"EVANS 60-BROOK","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","EVANS 60-BROOK (01)",0,0]
[16875,null,"ROSS-ELIZABETH","NT0-017","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","NT0","ROSS-ELIZABETH (02)",4.4620945071616617E-5,0]
[16887,null,"HENDRICKS-LORRAINE","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","Y","N","BMS","HENDRICKS-LORRAINE (01)",0,0]
[16894,null,"BRUNEL-TRUMAN","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","BRUNEL-TRUMAN (01)",4.4620945071616617E-5,0]
[16914,null,"OWEN-GORDON","FE0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","OWEN-GORDON (01)",0,0]
[16930,null,"MIRAMS-UNION","FT0-026","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","MIRAMS-UNION (01)",4.4620945071616617E-5,0]
[16937,null,"WHITBY-BARTON","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","WHITBY-BARTON (02)",4.4620945071616617E-5,0]
[16954,null,"STEWART-OSBORNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","STEWART-OSBORNE (01)",4.4620945071616617E-5,0]
[16959,null,"DARLING-WHITE","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","DARLING-WHITE (03)",4.4620945071616617E-5,0]
[16979,null,"MASON-HIGH","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MASON-HIGH (01)",4.4620945071616617E-5,0]
[16982,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","McGOWAN-MURRAY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17002,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17009,null,"DARLING-FULHAM","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","DARLING-FULHAM (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17025,null,"SALMON-NAPIER","NS0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","SALMON-NAPIER (02)",4.4620945071616617E-5,0]
[17044,null,"ALBION-GEELONG","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ALBION-GEELONG (01)",4.4620945071616617E-5,0]
[17047,null,"THE ESPLANADE-PLANTATION","YVE-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","THE ESPLANADE-PLANTATION (01)",4.4620945071616617E-5,0]
[17067,null,"GENEVA-COMO","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","GENEVA-COMO (02)",4.4620945071616617E-5,0]
[17074,null,"WEEMALA-SHANKLAND","BD0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","WEEMALA-SHANKLAND (02)",0,0]
[17094,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[17109,null,"SEVERN-SOMERVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","SEVERN-SOMERVILLE (03)",4.4620945071616617E-5,0]
[17116,null,"BANNON-RETREAT","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BANNON-RETREAT (02)",0,0]
[17132,null,"ALBERT-DUNDAS","EP0-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","ALBERT-DUNDAS (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[17139,null,"HILLSIDE-HURTLE","ES0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","HILLSIDE-HURTLE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17155,null,"TIERNAN-RAGLAN","EP0-037","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","TIERNAN-RAGLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[17173,null,"HILLSIDE-ROBERTS","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILLSIDE-ROBERTS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17181,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17197,null,"LYON-MARTINS","NH0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","NH0","LYON-MARTINS (02)",0,0]
[17204,null,"TAYLOR-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",0,0]
[17220,null,"FLETCHER-PASCOE VALE","NS0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","FLETCHER-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17227,null,"LOCKSLEY-KINSALE","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","LOCKSLEY-KINSALE (01)",4.4620945071616617E-5,0]
[17240,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","O'DOWD-HOWARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17262,null,"DARLING-WHITE","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","DARLING-WHITE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[17269,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","O'DOWD-HOWARD (02)",4.4620945071616617E-5,0]
[17289,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",0,0]
[17292,null,"FREIGHT-CUSTOM","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (01)",0,0]
[17312,null,"HILLSIDE-ROBERTS","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","HILLSIDE-ROBERTS (02)",4.4620945071616617E-5,0]
[17323,null,"FLETCHER-PASCOE VALE","NS0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","FLETCHER-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17334,null,"FLETCHER-PASCOE VALE","NS0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","FLETCHER-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17341,null,"DARLING-FULHAM","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","DARLING-FULHAM (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17357,null,"DONALD-LAWSON","NS0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",0,0]
[17377,null,"MOORE 9-MATTHEWS","AW0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","MOORE 9-MATTHEWS (01)",0,0]
[17384,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,0]
[17402,null,"MARKS-YORK","NS0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","MARKS-YORK (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[17406,null,"MYRTLE-REGENT","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","MYRTLE-REGENT (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[17422,null,"BLAKE-DAVIS","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BLAKE-DAVIS (02)",4.4620945071616617E-5,0]
[17442,null,"GRAVES-MARKET","ES0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GRAVES-MARKET (02)",4.4620945071616617E-5,0]
[17449,null,"NEAL-DINAH","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NEAL-DINAH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17459,null,"COBURG-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","COBURG-RENNIE (01)",4.4620945071616617E-5,0]
[17471,null,"ERIC-ADA","CS0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","McGOWAN-MURRAY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[17487,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,0]
[17507,null,"NUNAN-KIRBY","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","NUNAN-KIRBY (02)",4.4620945071616617E-5,0]
[17514,null,"BURKE-FLINDERS","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (01)",0,0]
[17530,null,"DARLING-FULHAM","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","DARLING-FULHAM (01)",4.4620945071616617E-5,0]
[17538,null,"PARK-COMBERMERE","ES0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","PARK-COMBERMERE (02)",{"$f":"IF(G17539=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J17539=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[17556,null,"WALLIS-KEILOR","ES0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","WALLIS-KEILOR (01)",0,0]
[17559,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17579,null,"WEBB-CORONATION","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-CORONATION (03)",4.4620945071616617E-5,0]
[17595,null,"PASCOE VALE-MT ALEXANDER","NS0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","PASCOE VALE-MT ALEXANDER (04)",0,0]
[17602,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","CALA-HAMPTON (01)",{"$f":"IF(G17603=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J17603=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[17617,null,"HAMILTON-O'FARRELL","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",0,0]
[17624,null,"CAMPBELL-DE CARLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CAMPBELL-DE CARLE (01)",4.4620945071616617E-5,0]
[17644,null,"DONCASTER-MYROSS","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DONCASTER-MYROSS (01)",4.4620945071616617E-5,0]
[17651,null,"ROSS-ELIZABETH","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","ROSS-ELIZABETH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17667,null,"PARKVIEW-HEIDELBERG","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","PARKVIEW-HEIDELBERG (02)",4.4620945071616617E-5,0]
[17687,null,"EIRENE-FRANCIS","FW0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","EIRENE-FRANCIS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17688,null,"REYNARD-PHILLIPS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-PHILLIPS (01)",4.4620945071616617E-5,0]
[17709,null,"EAST-HARDING","FT0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","EAST-HARDING (01)",0,0]
[17716,null,"SOUTHEY-ARDEN","FT0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","SOUTHEY-ARDEN (01)",0,0]
[17732,null,"BURKE-FLINDERS","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (03)",0,0]
[17739,null,"THE FAIRWAY-DUNNE","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","THE FAIRWAY-DUNNE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17757,null,"DAVERN-O'HEA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DAVERN-O'HEA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17774,null,"HOBBS-PENTLAND","FE0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","HOBBS-PENTLAND (01)",0,0]
[17781,null,"GLENMORE-KINLOCK","NH0-002","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","NH0","GLENMORE-KINLOCK (03)",4.4620945071616617E-5,0]
[17797,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[17804,null,"GENEVA-COMO","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","GENEVA-COMO (02)",4.4620945071616617E-5,0]
[17824,null,"GIFFARD-OSBORNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","GIFFARD-OSBORNE (04)",4.4620945071616617E-5,0]
[17836,null,"CHARLTON-BOLDREWOOD","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","CHARLTON-BOLDREWOOD (02)",4.4620945071616617E-5,0]
[17846,null,"CHIFLEY 72-REX","EP0-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","CHIFLEY 72-REX (00)",0,0]
[17862,null,"HAMILTON-O'FARRELL","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","HAMILTON-O'FARRELL (02)",0,0]
[17869,null,"DEAKIN-BUCKLEY","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DEAKIN-BUCKLEY (01)",4.4620945071616617E-5,0]
[17889,null,"SOMERVILLE-JULIAN","FW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","SOMERVILLE-JULIAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[17905,null,"MCGREGOR-PERRY","FF0-083","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","MCGREGOR-PERRY (01)",0,0]
[17915,null,"KENNEDY-CHAPMAN","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KENNEDY-CHAPMAN (01)",4.4620945071616617E-5,0]
[17927,null,"SYMONS-GILBERT","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","SYMONS-GILBERT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[17934,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","HODDLE-FLETCHER (01)",4.4620945071616617E-5,0]
[17954,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[17957,null,"EDWARD-CASH","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","EDWARD-CASH (02)",4.4620945071616617E-5,0]
[17977,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","STEELE-STUART (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[17994,null,"NEWMAN-HOTHAM","AW0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","NEWMAN-HOTHAM (03)",0,0]
[17999,null,"GOULBURN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","GOULBURN-PALMERSTON (04)",4.4620945071616617E-5,0]
[18019,null,"DAVERN-O'HEA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DAVERN-O'HEA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18022,null,"EAST-THACKERAY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","EAST-THACKERAY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18042,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","REYNARD-DONNE (03)",4.4620945071616617E-5,0]
[18049,null,"ASHBY-LOCKSLEY","HB0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","ASHBY-LOCKSLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18065,null,"MEROLA 54 -FREEMAN","BD0-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","MEROLA 54 -FREEMAN (02)",0,0]
[18084,null,"DORSET-DERBY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DORSET-DERBY (02)",4.4620945071616617E-5,0]
[18091,null,"MCCRAE-ELSEY","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","MCCRAE-ELSEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18107,null,"RUSSELL-BARKLY","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","RUSSELL-BARKLY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18114,null,"WEBB-QUEENSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","WEBB-QUEENSVILLE (02)",{"$f":"IF(G18115=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J18115=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[18134,null,"HILTON-CHURCHILL","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-CHURCHILL (01)",4.4620945071616617E-5,0]
[18136,null,"BULLA-DUBLIN","ES0-025","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BULLA-DUBLIN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18156,null,"GOSFORD-NICHOLAS","BD0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","GOSFORD-NICHOLAS (02)",0,0]
[18172,null,"ARGYLE-BROAD","FW0-016","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","ARGYLE-BROAD (01)",0,0]
[18179,null,"HILTON-WIDFORD","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-WIDFORD (03)",4.4620945071616617E-5,0]
[18195,null,"HEMAR-BRAMSHAW","SHM-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","HEMAR-BRAMSHAW (01)",4.4620945071616617E-5,0]
[18201,null,"DONCASTER-WALTER","ES0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DONCASTER-WALTER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18221,null,"GRANGE-CRAMER","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GRANGE-CRAMER (01)",4.4620945071616617E-5,0]
[18237,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,0]
[18244,null,"RAGLAN-ASCOT","EP0-037","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","RAGLAN-ASCOT (01)",0,0]
[18264,null,"ALEXANDER-JOHN","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","DICKSON-WILLIAMSTOWN (03)",0,0]
[18267,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",0,0]
[18280,null,"LEVER-GORDON","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","LEVER-GORDON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18302,null,"SEPARATION-PERRY","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","SEPARATION-PERRY (03)",4.4620945071616617E-5,0]
[18309,null,"THE BOULEVARD-GILBERT","HB0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","THE BOULEVARD-GILBERT (01)",4.4620945071616617E-5,0]
[18316,null,"TYRELL-MCBRYDE","CN0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","TYRELL-MCBRYDE (01)",4.4620945071616617E-5,0]
[18332,null,"ESSEX-DUDLEY","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ESSEX-DUDLEY (03)",4.4620945071616617E-5,0]
[18352,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18363,null,"EGLINTON-ARGYLE","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","EGLINTON-ARGYLE (04)",4.4620945071616617E-5,0]
[18374,null,"SALISBURY-JACK","NT0-003","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","NT0","SALISBURY-JACK (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18381,null,"KERFERD-RALEIGH","ES0-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (01)",0,0]
[18397,null,"BERRIMA-ROSANNA","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BERRIMA-ROSANNA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18417,null,"WARRAGUL-LISMORE","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","WARRAGUL-LISMORE (01)",4.4620945071616617E-5,0]
[18424,null,"THE FAIRWAY-DUNNE","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","THE FAIRWAY-DUNNE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18442,null,"TURNER-EVANS","NS0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","TURNER-EVANS (01)",0,0]
[18446,null,"PARKLANDS-KELVIN","FF0-093","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","PARKLANDS-KELVIN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18462,null,"ARGYLE-BROAD","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ARGYLE-BROAD (01)",4.4620945071616617E-5,0]
[18482,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ESSEX-LANDELLS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18489,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18499,null,"ST LEONARDS-UNION","FT0-026","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","ST LEONARDS-UNION (03)",4.4620945071616617E-5,0]
[18511,null,"BAXTER-SYDNEY","CS0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BAXTER-SYDNEY (03)",4.4620945071616617E-5,0]
[18531,null,"ROSENTHAL-ALLENBY","TT0-010","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","ROSENTHAL-ALLENBY (01)",0,0]
[18534,null,"ARGYLE-DAREBIN","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",4.4620945071616617E-5,0]
[18554,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[18570,null,"GLASGOW-HIGH","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","GLASGOW-HIGH (01)",4.4620945071616617E-5,0]
[18578,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18596,null,"BERRY-LORNE","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BERRY-LORNE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18599,null,"CHALLIS-SPEIGHT","NT0-017","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","NT0","CHALLIS-SPEIGHT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18619,null,"BANK-MT ALEXANDER","FT0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","BANK-MT ALEXANDER (03)",0,0]
[18635,null,"CASTLETON 21-HAVILAH","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CASTLETON 21-HAVILAH (02)",4.4620945071616617E-5,0]
[18642,null,"CAPRICORN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","CAPRICORN-PALMERSTON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[18657,null,"TAYLOR-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","TAYLOR-MT ALEXANDER (01)",0,0]
[18664,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","YALLAMBIE-LOWER PLENTY (02)",4.4620945071616617E-5,0]
[18684,null,"MARIBYRNONG-WALTER","ES0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MARIBYRNONG-WALTER (01)",4.4620945071616617E-5,0]
[18691,null,"MERBEIN-SUSSEX","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MERBEIN-SUSSEX (01)",4.4620945071616617E-5,0]
[18707,null,"OMAR-MITCHELL","BY0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","OMAR-MITCHELL (02)",4.4620945071616617E-5,0]
[18714,null,"ANDERSON-BOLINGBROKE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","ANDERSON-BOLINGBROKE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18728,null,"THICKINS-NORTHUMBERLAND","PV0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","THICKINS-NORTHUMBERLAND (02)",4.4620945071616617E-5,0]
[18749,null,"JOFFRE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","JOFFRE-KENT (01)",4.4620945071616617E-5,0]
[18756,null,"PICKETT-HICKFORD","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","PICKETT-HICKFORD (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18772,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","FE0","WATT-THE AVENUE (03)",4.4620945071616617E-5,0]
[18779,null,"DOLE-LOCHER","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","DOLE-LOCHER (03)",4.4620945071616617E-5,0]
[18799,null,"QUEEN-RUSSELL","NT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","QUEEN-RUSSELL (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[18807,null,"YARRALEA-GIBSON","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","YARRALEA-GIBSON (01)",4.4620945071616617E-5,0]
[18821,null,"SUSSEX-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","ES0","SUSSEX-HOLMES (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18837,null,"WESTMERE-WARNE","BD0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BD0","WESTMERE-WARNE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18844,null,"DOYLE-NORTH","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","DOYLE-NORTH (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18864,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18876,null,"HILTON-WIDFORD","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-WIDFORD (02)",4.4620945071616617E-5,0]
[18886,null,"BERRIMA-ROSANNA","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BERRIMA-ROSANNA (02)",4.4620945071616617E-5,0]
[18902,null,"WAMBA-THE BOULEVARD","HB0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","WAMBA-THE BOULEVARD (02)",4.4620945071616617E-5,0]
[18909,null,"CHAPMAN-GRANDVIEW","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CHAPMAN-GRANDVIEW (01)",4.4620945071616617E-5,0]
[18929,null,"DIAMOND-ROSEHILL","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18932,null,"THE RIDGE-DEEP CREEK 2","COO-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","THE RIDGE-DEEP CREEK 2 (01)",4.4620945071616617E-5,0]
[18955,null,"RUSSELL-BARKLY","FW0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","RUSSELL-BARKLY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[18958,null,"GENEVA-COMO","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","GENEVA-COMO (02)",4.4620945071616617E-5,0]
[18974,null,"SOUDAN-HIGH","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SOUDAN-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[18994,null,"PASLEY-NEILL","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","PASLEY-NEILL (00)",0,0]
[18997,null,"LAWLEY-GLASGOW","TT0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","LAWLEY-GLASGOW (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19017,null,"VINEYARD RD-P42","SHM-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","VINEYARD RD-P42 (00)",0,0]
[19022,null,"CARTWRIGHT-PASCOE VALE","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CARTWRIGHT-PASCOE VALE (01)",4.4620945071616617E-5,0]
[19039,null,"SOUDAN-HIGH","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SOUDAN-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19059,null,"SALWEEN-ELSA","ST0-012","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","ST0","SALWEEN-ELSA (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[19062,null,"CUMBERLAND-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CUMBERLAND-KENT (04)",4.4620945071616617E-5,0]
[19082,null,"PARSONS-STUBBS","FT0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","PARSONS-STUBBS (02)",4.4620945071616617E-5,0]
[19089,null,"EARL-GRANGE","KLO-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","KLO","EARL-GRANGE (03)",4.4620945071616617E-5,0]
[19105,null,"BOLINGBROKE-BURGUNDY","CS0-002","2025-02-02","2025-02-08","N","Y","N","N","N","N","CS0","BOLINGBROKE-BURGUNDY (02)",0,0]
[19111,null,"BIRCH-GILBERT","CS0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BIRCH-GILBERT (02)",4.4620945071616617E-5,0]
[19131,null,"CUMBERLAND-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CUMBERLAND-KENT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[19147,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19154,null,"HAWDON-BROWN","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","HAWDON-BROWN (01)",4.4620945071616617E-5,0]
[19170,null,"HILLSYDE-LOEMAN","NS0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","HILLSYDE-LOEMAN (01)",4.4620945071616617E-5,0]
[19184,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[19196,null,"OLIVE-SYLVAN","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","OLIVE-SYLVAN (02)",4.4620945071616617E-5,0]
[19212,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19219,null,"ROWE-YARRALEA","FF0-093","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","ROWE-YARRALEA (01)",0,0]
[19239,null,"BARWON-PLENTY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BARWON-PLENTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[19241,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[19261,null,"OLIVE-VIOLA","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","OLIVE-VIOLA (02)",4.4620945071616617E-5,0]
[19277,null,"BELMONT-BAYSWATER","FT0-035","2025-02-02","2025-02-08","N","Y","N","N","N","N","FT0","BELMONT-BAYSWATER (01)",0,0]
[19284,null,"PASCOE VALE-MT ALEXANDER","NS0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","PASCOE VALE-MT ALEXANDER (04)",0,0]
[19291,null,"GREVILLE-KEILOR","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","GREVILLE-KEILOR (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[19307,null,"INTERNATIONAL-T'PARK","AW0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","INTERNATIONAL-T'PARK (00)",0,0]
[19320,null,"LAKES-THE GREENWAY","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","LAKES-THE GREENWAY (03)",0,0]
[19329,null,"DUNDEE-MEADE","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","DUNDEE-MEADE (03)",4.4620945071616617E-5,0]
[19349,null,"MONARCH-EAGLEVIEW","KLO-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","KLO","MONARCH-EAGLEVIEW (04)",4.4620945071616617E-5,0]
[19356,null,"BAYVIEW-GELLIBRAND","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BAYVIEW-GELLIBRAND (03)",4.4620945071616617E-5,0]
[19372,null,"CORNISH-LIGAR","SBY-012","2025-02-02","2025-02-08","N","N","N","Y","N","N","SBY","CORNISH-LIGAR (01)",0,9.4304036212749905E-5]
[19392,null,"CHAPMAN-BELAIR","PV0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","CHAPMAN-BELAIR (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19399,null,"THE RIDGE-DEEP CREEK 5","COO-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","COO","THE RIDGE-DEEP CREEK 5 (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19414,null,"SEPARATION-PERRY","FF0-093","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","SEPARATION-PERRY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19421,null,"MACK-PICKETT","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","MACK-PICKETT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[19437,null,"BANNON-RETREAT","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BANNON-RETREAT (02)",0,0]
[19457,null,"WATTLEVALLEY-JAMES","SHM-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","WATTLEVALLEY-JAMES (01)",4.4620945071616617E-5,0]
[19464,null,"PHILLIP-STRACHEN","SBY-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","SBY","PHILLIP-STRACHEN (02)",4.4620945071616617E-5,0]
[19482,null,"CHATFIELD-KINGSVILLE","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CHATFIELD-KINGSVILLE (01)",4.4620945071616617E-5,0]
[19486,null,"GRAHAM-GIBSON","BMS-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","BMS","GRAHAM-GIBSON (02)",4.4620945071616617E-5,0]
[19502,null,"SYMONS-GILBERT","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","SYMONS-GILBERT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[19509,null,"MELTON-MEWS","SHM-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","MELTON-MEWS (04)",0,0]
[19529,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (02)",0,0]
[19545,null,"CAPRICORN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","CAPRICORN-PALMERSTON (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[19549,null,"SOUDAN-HIGH","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","SOUDAN-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19571,null,"DAISY-BUCKLEY","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DAISY-BUCKLEY (02)",4.4620945071616617E-5,0]
[19574,null,"FULLARTON-WALTERS","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","FULLARTON-WALTERS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19594,null,"THOMPSON-CECIL","NT0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","NT0","THOMPSON-CECIL (01)",0,0]
[19610,null,"THE RIDGE-DEEP CREEK 4","COO-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","COO","THE RIDGE-DEEP CREEK 4 (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19618,null,"BRASSEY-PYALONG","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BRASSEY-PYALONG (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19636,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,0]
[19639,null,"SOUTH-BELL","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","SOUTH-BELL (02)",0,0]
[19659,null,"CHALEYER-ASHTON","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CHALEYER-ASHTON (03)",4.4620945071616617E-5,0]
[19666,null,"QUINN-CLARKS","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","QUINN-CLARKS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19682,null,"FOCH-TYLER","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","FOCH-TYLER (02)",0,0]
[19697,null,"WILLOWTREE-PERSICA","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (04)",0,0]
[19704,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","WATT-THE AVENUE (02)",0,0]
[19724,null,"THE RIDGE-DEEP CREEK 5","COO-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","COO","THE RIDGE-DEEP CREEK 5 (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19731,null,"MARY-BRUCE","PTN-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARY-BRUCE (01)",0,0]
[19747,null,"WALLIS-KEILOR","ES0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","WALLIS-KEILOR (03)",0,0]
[19754,null,"CRAMER-MARKET NO2","PTN-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","CRAMER-MARKET NO2 (01)",0,0]
[19768,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","O'DOWD-HOWARD (02)",4.4620945071616617E-5,0]
[19789,null,"PARKLANDS-KELVIN","FF0-093","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","PARKLANDS-KELVIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19796,null,"MCIVOR-KIEWA","BD0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","MCIVOR-KIEWA (01)",0,0]
[19812,null,"ORIEL-STANLEY","EP0-034","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","ORIEL-STANLEY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[19819,null,"ALOHA-GREENE","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ALOHA-GREENE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[19839,null,"SANDOVER-SALWEEN","ST0-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","ST0","SANDOVER-SALWEEN (04)",4.4620945071616617E-5,0]
[19847,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-DONNE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19861,null,"KING-BOWES","AW0-005","2025-02-02","2025-02-08","N","Y","N","N","Y","N","AW0","KING-BOWES (01)",0,0]
[19877,null,"ANDERSON-BOLINGBROKE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","ANDERSON-BOLINGBROKE (02)",4.4620945071616617E-5,0]
[19884,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[19904,null,"EARL-GRANGE","KLO-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","KLO","EARL-GRANGE (02)",4.4620945071616617E-5,0]
[19907,null,"CAPRICORN-PALMERSTON","SHM-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","CAPRICORN-PALMERSTON (03)",4.4620945071616617E-5,0]
[19926,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,0]
[19933,null,"HODDLE-FLETCHER","NS0-018","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","HODDLE-FLETCHER (01)",4.4620945071616617E-5,0]
[19949,null,"MATTHEWS-KEILOR","ES0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","MATTHEWS-KEILOR (03)",0,0]
[19969,null,"HEPBURN-KING","BD0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","HEPBURN-KING (02)",4.4620945071616617E-5,0]
[19972,null,"ALBERT-DUNDAS","EP0-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","ALBERT-DUNDAS (03)",0,0]
[19995,null,"OUTHWAITE-ORIEL","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","OUTHWAITE-ORIEL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[19998,null,"DICKERSON-TUCKER","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","DICKERSON-TUCKER (01)",4.4620945071616617E-5,0]
[20014,null,"ALMA-PALMERSTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[20034,null,"MCCOLL-TYLER","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","MCCOLL-TYLER (03)",{"$f":"IF(G20035=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J20035=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[20037,null,"DONVALE-HAYFIELD","ST0-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","DONVALE-HAYFIELD (01)",0,0]
[20057,null,"BOOMERANG-AIRFORCE","TH0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",0,0]
[20062,null,"ARBOR-MACEY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","ARBOR-MACEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[20079,null,"REYNARD-DONNE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","REYNARD-DONNE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[20086,null,"HANSON-GOBLE","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","HANSON-GOBLE (01)",4.4620945071616617E-5,0]
[20106,null,"LILLEE 60-MALLETT","TMA-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","TMA","LILLEE 60-MALLETT (03)",0,0]
[20122,null,"EISENHOWER-CHALEYER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","EISENHOWER-CHALEYER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[20129,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (03)",0,0]
[20145,null,"EISENHOWER-CHALEYER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","EISENHOWER-CHALEYER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[20151,null,"SYMONS-GILBERT","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","SYMONS-GILBERT (04)",4.4620945071616617E-5,0]
[20171,null,"ELATA-BEVERAGE","AW0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ELATA-BEVERAGE (02)",0,0]
[20187,null,"BRAIDHILL-WINDSOR","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BRAIDHILL-WINDSOR (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[20194,null,"CONDER-DOBELL","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","CONDER-DOBELL (03)",4.4620945071616617E-5,0]
[20210,null,"SCARVELL-PRO HART","SHM-021","2025-02-02","2025-02-08","N","Y","N","N","Y","N","SHM","SCARVELL-PRO HART (02)",0,0]
[20224,null,"STEVEDORE-MELBOURNE","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","STEVEDORE-MELBOURNE (02)",4.4620945071616617E-5,0]
[20236,null,"SCARVELL-PRO HART","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","SCARVELL-PRO HART (02)",4.4620945071616617E-5,0]
[20252,null,"BOOMERANG-AIRFORCE","TH0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",0,0]
[20259,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (03)",4.4620945071616617E-5,0]
[20266,null,"JELLICOE-OSNEY","EP0-034","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","JELLICOE-OSNEY (02)",4.4620945071616617E-5,0]
[20282,null,"BEATRICE-JENSEN","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BEATRICE-JENSEN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[20303,null,"TOWER-HEIDELBERG","FF0-088","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","TOWER-HEIDELBERG (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[20304,null,"GRAHAM 138-SYLVIA","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GRAHAM 138-SYLVIA (01)",4.4620945071616617E-5,0]
[20324,null,"MACK-PICKETT","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","MACK-PICKETT (02)",4.4620945071616617E-5,0]
[20331,null,"BRADLEY-MASON","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BRADLEY-MASON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[20347,null,"FRENCH-PAISLEY","FE0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","FRENCH-PAISLEY (03)",0,0]
[20360,null,"WEBSTERS RD S-P2","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","WEBSTERS RD S-P2 (00)",0,0]
[20373,null,"RYDER-NOLAN","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","RYDER-NOLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[20389,null,"COPE-MOORE","AW0-001","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","COPE-MOORE (03)",0,0]
[20396,null,"DICKERSON-TUCKER","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","DICKERSON-TUCKER (01)",4.4620945071616617E-5,0]
[20412,null,"GARNET-EMERALD","ES0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GARNET-EMERALD (02)",4.4620945071616617E-5,0]
[20432,null,"ESSEX-DOWNS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-DOWNS (02)",4.4620945071616617E-5,0]
[20439,null,"O'CONNOR-WHITBY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[20454,null,"CRESSWELL-CAMERON","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","CRESSWELL-CAMERON (02)",0,0]
[20461,null,"MT ALEXANDER-HOMER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MT ALEXANDER-HOMER (04)",0,0]
[20477,null,"MARY-NIMMO","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MARY-NIMMO (02)",4.4620945071616617E-5,0]
[20484,null,"THOMPSON-NORTH","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","THOMPSON-NORTH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[20504,null,"JUKES-LANIGAN","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","JUKES-LANIGAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[20510,null,"WAIORA-DOUGHARTY","NH0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","WAIORA-DOUGHARTY (01)",4.4620945071616617E-5,0]
[20526,null,"CORNWALL-HIGH SCHOOL","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[20546,null,"COHEN-GROVES","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","COHEN-GROVES (01)",{"$f":"IF(G20547=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J20547=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[20549,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[20569,null,"O'CONNOR-WHITBY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","O'CONNOR-WHITBY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[20585,null,"ALMA-CHANDLER","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","ALMA-CHANDLER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[20589,null,"DOYLE-RIDLEY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","DOYLE-RIDLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[20611,null,"GARNET-IDA","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GARNET-IDA (02)",4.4620945071616617E-5,0]
[20614,null,"NEPEAN-FREDA","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","NEPEAN-FREDA (01)",0,0]
[20634,null,"BOOMERANG-AIRFORCE","TH0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",0,0]
[20641,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (01)",4.4620945071616617E-5,0]
[20657,null,"BOOMERANG-AIRFORCE","TH0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",0,0]
[20668,null,"ZAMMIT-O'HAIRE","SHM-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","ZAMMIT-O'HAIRE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[20679,null,"FRANCIS-VINCENT","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","FRANCIS-VINCENT (01)",4.4620945071616617E-5,0]
[20699,null,"SUFFOLK-THOMSON","FW0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","SUFFOLK-THOMSON (04)",4.4620945071616617E-5,0]
[20706,null,"CUMBERLAND-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CUMBERLAND-KENT (01)",4.4620945071616617E-5,0]
[20722,null,"SALMON-NAPIER","NS0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","SALMON-NAPIER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[20737,null,"CORNWALL-HIGH SCHOOL","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[20744,null,"LEBANON-FENACRE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","LEBANON-FENACRE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[20764,null,"JACKA-MCCRACKEN","ES0-026","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","JACKA-MCCRACKEN (02)",4.4620945071616617E-5,0]
[20771,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","YALLAMBIE-LOWER PLENTY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[20787,null,"BOOMERANG-AIRFORCE","TH0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",0,0]
[20794,null,"JOHN-WINIFRED","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","JOHN-WINIFRED (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[20816,null,"CUMBERLAND-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CUMBERLAND-KENT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[20829,null,"ASCOT VALE 331-YOUNG","NS0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ASCOT VALE 331-YOUNG (01)",0,0]
[20836,null,"LANDELLS-MARTIN","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","LANDELLS-MARTIN (04)",4.4620945071616617E-5,0]
[20852,null,"HAWDON-BROWN","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","HAWDON-BROWN (01)",4.4620945071616617E-5,0]
[20859,null,"INVERMAY-MT IDA","NH0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","INVERMAY-MT IDA (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[20879,null,"FORDHAM-STRATHMERTON","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","FORDHAM-STRATHMERTON (01)",4.4620945071616617E-5,0]
[20887,null,"CHARLES-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","CHARLES-EPSOM (01)",4.4620945071616617E-5,0]
[20901,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,0]
[20917,null,"CHARTERIS-BURKE","HB0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","CHARTERIS-BURKE (01)",4.4620945071616617E-5,0]
[20924,null,"DEAKIN-SPENCER","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DEAKIN-SPENCER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[20944,null,"BRADSHAW-MARY","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BRADSHAW-MARY (03)",4.4620945071616617E-5,0]
[20947,null,"BIRDWOOD-REGENT","CN0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BIRDWOOD-REGENT (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[20966,null,"DONALD-LAWSON","NS0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","DONALD-LAWSON (02)",0,0]
[20973,null,"KENNEDY-WILLIAM","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KENNEDY-WILLIAM (01)",4.4620945071616617E-5,0]
[20989,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21009,null,"BOND-LIBERTY","EP0-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","BOND-LIBERTY (01)",0,0]
[21012,null,"BOND-LIBERTY","EP0-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","BOND-LIBERTY (01)",0,0]
[21032,null,"BRASSEY-PYALONG","NH0-020","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BRASSEY-PYALONG (01)",4.4620945071616617E-5,0]
[21045,null,"SUFFOLK-DONGOLA","FW0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","SUFFOLK-DONGOLA (01)",4.4620945071616617E-5,0]
[21054,null,"SOUTH-BELL","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","SOUTH-BELL (00)",0,0]
[21061,null,"DONCASTER-WALTER","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DONCASTER-WALTER (02)",4.4620945071616617E-5,0]
[21081,null,"KENNETH-GOWER","EPN-035","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","KENNETH-GOWER (01)",4.4620945071616617E-5,0]
[21097,null,"SUSSEX-HOLMES","ES0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","SUSSEX-HOLMES (02)",4.4620945071616617E-5,0]
[21102,null,"ANDERSON-BOLINGBROKE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","ANDERSON-BOLINGBROKE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21119,null,"HUME 1487-THOMPSON","BMS-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","HUME 1487-THOMPSON (02)",0,0]
[21126,null,"DOLE-LOCHER","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","DOLE-LOCHER (03)",4.4620945071616617E-5,0]
[21146,null,"NEWCASTLE-ELIZABETH","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","NEWCASTLE-ELIZABETH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21162,null,"MT ALEXANDER-NAPIER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (02)",0,0]
[21169,null,"MT ALEXANDER-NAPIER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (02)",0,0]
[21185,null,"OAK-CONISTON","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","OAK-CONISTON (03)",4.4620945071616617E-5,0]
[21191,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,0]
[21211,null,"EAST-THACKERAY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","EAST-THACKERAY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[21227,null,"ERINBANK-DOBIES","BD0-007","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","BD0","ERINBANK-DOBIES (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[21234,null,"WUNNAMURRA-WONGANELA","AW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","WUNNAMURRA-WONGANELA (01)",4.4620945071616617E-5,0]
[21241,null,"GREEN-BOURKE","COO-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","COO","GREEN-BOURKE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21264,null,"SUFFOLK-DONGOLA","FW0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","SUFFOLK-DONGOLA (01)",4.4620945071616617E-5,0]
[21276,null,"NEPEAN-FREDA","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","NEPEAN-FREDA (01)",0,0]
[21279,null,"ALBERT-BUCKLEY","FE0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","ALBERT-BUCKLEY (02)",0,0]
[21299,null,"PARKSIDE-HIGHVIEW","KLO-022","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","KLO","PARKSIDE-HIGHVIEW (03)",4.4620945071616617E-5,0]
[21306,null,"SNELL-WATT","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","SNELL-WATT (02)",4.4620945071616617E-5,0]
[21322,null,"WOODS-CHALLIS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WOODS-CHALLIS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21331,null,"ARGYLE-BROAD","FW0-016","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","ARGYLE-BROAD (01)",0,0]
[21344,null,"GREEN-SPARKFORD","EP0-034","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","FORD-SPARKFORD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21364,null,"WESTERN-GLOBAL","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","WESTERN-GLOBAL (01)",0,0]
[21371,null,"WESTERN-GLOBAL","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","WESTERN-GLOBAL (01)",0,0]
[21387,null,"DOMAIN-LYGON","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","DOMAIN-LYGON (03)",4.4620945071616617E-5,0]
[21407,null,"HARBURY-EDWARDES","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HARBURY-EDWARDES (02)",4.4620945071616617E-5,0]
[21410,null,"THE RIDGE-DEEP CREEK 3","COO-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","COO","THE RIDGE-DEEP CREEK 3 (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21429,null,"IVAN-MASCOMA","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","IVAN-MASCOMA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[21436,null,"FARRELL-RYDER","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FARRELL-RYDER (01)",0,0]
[21452,null,"WARRAGUL-LISMORE","BD0-011","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","BD0","WARRAGUL-LISMORE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21459,null,"STEANE-ALBERT","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STEANE-ALBERT (03)",4.4620945071616617E-5,0]
[21479,null,"RYDER-NOLAN","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","RYDER-NOLAN (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[21494,null,"DAVID-NORTH","PV0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","KATOOMBA-SUTHERLAND (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[21501,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","STEELE-STUART (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21521,null,"HAWKER-MCNAMARA","AW0-001","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","HAWKER-MCNAMARA (02)",4.4620945071616617E-5,0]
[21524,null,"DAVERN-O'HEA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DAVERN-O'HEA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21544,null,"MARY-ROBERTS","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MARY-ROBERTS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[21550,null,"FLORENCE-LINCOLN","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FLORENCE-LINCOLN (02)",4.4620945071616617E-5,0]
[21566,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","STEELE-STUART (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[21586,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21589,null,"MARY-ROBERTS","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MARY-ROBERTS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[21609,null,"GREENSBOROUGH-YALLAMBIE","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GREENSBOROUGH-YALLAMBIE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[21625,null,"MOORE 9-MATTHEWS","AW0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","MOORE 9-MATTHEWS (01)",0,0]
[21629,null,"LINDSAY-GLENROY","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","LINDSAY-GLENROY (02)",4.4620945071616617E-5,0]
[21638,null,"BUNDOORA-GOLF COURSE","TT0-003","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","BUNDOORA-GOLF COURSE (01)",0,0]
[21654,null,"COUANGALT RD-P6","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","COUANGALT RD-P6 (00)",0,0]
[21674,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (00)",0,0]
[21681,null,"HILLCREST-ROYAL","SHM-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","HILLCREST-ROYAL (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[21697,null,"ESSEX-SWAN","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","ESSEX-SWAN (01)",0,0]
[21708,null,"LONG ISLAND-ROYAL TROON","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","LONG ISLAND-ROYAL TROON (01)",0,0]
[21719,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21739,null,"MARY-ROBERTS","ES0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MARY-ROBERTS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[21746,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21762,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (01)",{"$f":"IF(G21763=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J21763=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[21769,null,"CUMBERLAND-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CUMBERLAND-KENT (01)",4.4620945071616617E-5,0]
[21787,null,"MERCIER-CHARLES","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MERCIER-CHARLES (02)",4.4620945071616617E-5,0]
[21804,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","CLARENDON-WHITTAKER (01)",4.4620945071616617E-5,0]
[21811,null,"MARGARET-WINIFRED","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MARGARET-WINIFRED (01)",4.4620945071616617E-5,0]
[21827,null,"WAVERLEY-HOLMES","ES0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","WAVERLEY-HOLMES (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[21834,null,"BOND-LIBERTY","EP0-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","BOND-LIBERTY (02)",0,0]
[21844,null,"SEXTON-PARER","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","SEXTON-PARER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21856,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",4.4620945071616617E-5,0]
[21876,null,"CLIFTON-JEAN","ES0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","CLIFTON-JEAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[21892,null,"HILTON-JUSTIN","PV0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-JUSTIN (02)",4.4620945071616617E-5,0]
[21899,null,"RAVENSCOURT-FULHAM","FF0-083","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",0,0]
[21919,null,"THE EYRIE-SUMMIT","HB0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","THE EYRIE-SUMMIT (02)",4.4620945071616617E-5,0]
[21927,null,"MCNAMARA-ELIZABETH","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MCNAMARA-ELIZABETH (02)",4.4620945071616617E-5,0]
[21941,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","Y","N","AW0","ETZEL-CLYDESDALE (03)",0,0]
[21948,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","ETZEL-CLYDESDALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[21964,null,"CHALEYER-ASHTON","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CHALEYER-ASHTON (03)",4.4620945071616617E-5,0]
[21984,null,"ALMA-PALMERSTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[21987,null,"CORNWALL-HIGH SCHOOL","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CORNWALL-HIGH SCHOOL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[22006,null,"BRADLEY-MASON","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BRADLEY-MASON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22013,null,"HEATHCOTE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HEATHCOTE-KENT (02)",4.4620945071616617E-5,0]
[22029,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MAYFIELD-MUNRO (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22036,null,"LYSTERFIELD-BEECHWORTH","ST0-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","LYSTERFIELD-BEECHWORTH (04)",0,0]
[22052,null,"MELTON HWY-P46","SHM-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","MELTON HWY-P46 (00)",0,0]
[22072,null,"SEXTON-PARER","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","SEXTON-PARER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22085,null,"MIRANDA-MAIS","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","MIRANDA-MAIS (01)",4.4620945071616617E-5,0]
[22094,null,"KILMORE-CHARLTON","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","KILMORE-CHARLTON (02)",4.4620945071616617E-5,0]
[22101,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22121,null,"FULLARTON-WALTERS","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","FULLARTON-WALTERS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22137,null,"ANDERSON-FEHON","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","ANDERSON-FEHON (02)",0,0]
[22144,null,"EVANS 60-BROOK","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","EVANS 60-BROOK (04)",0,0]
[22156,null,"STRATHMERTON-LEISURE CENTRE","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","STRATHMERTON-LEISURE CENTRE (01)",4.4620945071616617E-5,0]
[22166,null,"ROCK-DIANNE","ST0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ST0","ROCK-DIANNE (02)",4.4620945071616617E-5,0]
[22186,null,"DAVERN-O'HEA","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DAVERN-O'HEA (01)",4.4620945071616617E-5,0]
[22202,null,"VICTORY-FOSTERS","TMA-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TMA","VICTORY-FOSTERS (01)",4.4620945071616617E-5,0]
[22209,null,"PEARL-WHEATSHEAF","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","PEARL-WHEATSHEAF (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[22221,null,"WOODS-CHALLIS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WOODS-CHALLIS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22231,null,"CUMBERLAND-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","CUMBERLAND-KENT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[22251,null,"DAVERN-O'HEA","CS0-002","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","CS0","DAVERN-O'HEA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22254,null,"CULLEN-MARY","YVE-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","CULLEN-MARY (01)",4.4620945071616617E-5,0]
[22274,null,"THISTLE-MT ALEXANDER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (02)",{"$f":"IF(G22275=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J22275=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[22281,null,"THISTLE-MT ALEXANDER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","THISTLE-MT ALEXANDER (02)",0,0]
[22304,null,"MELTON HWY-P2","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","MELTON HWY-P2 (03)",4.4620945071616617E-5,0]
[22316,null,"GOLF VIEW-ROEBUCK","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","GOLF VIEW-ROEBUCK (04)",0,0]
[22319,null,"SYDNEY-ROSSHIRE","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WOODS-CHALLIS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22339,null,"ALOHA-WATT","FE0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","FE0","ALOHA-WATT (01)",4.4620945071616617E-5,0]
[22346,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[22362,null,"JOFFRE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","JOFFRE-KENT (02)",4.4620945071616617E-5,0]
[22371,null,"MONT ALBERT-SUFFOLK","BD0-016","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","MONT ALBERT-SUFFOLK (02)",0,0]
[22388,null,"GLASGOW-HIGH","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","GLASGOW-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22404,null,"NEWMAN-HOTHAM","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NEWMAN-HOTHAM (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[22411,null,"FORDHAM-STRATHMERTON","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","FORDHAM-STRATHMERTON (01)",4.4620945071616617E-5,0]
[22427,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","CLARENDON-WHITTAKER (03)",4.4620945071616617E-5,0]
[22434,null,"BIRDWOOD-KEILOR","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BIRDWOOD-KEILOR (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[22450,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",0,0]
[22469,null,"AMAR-MASCOMA","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","AMAR-MASCOMA (01)",4.4620945071616617E-5,0]
[22476,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22496,null,"DEAKIN-BERRY","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","DEAKIN-BERRY (02)",4.4620945071616617E-5,0]
[22499,null,"HOLDEN-MILITARY","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","HOLDEN-MILITARY (01)",4.4620945071616617E-5,0]
[22519,null,"LEBANON-ELDORADO","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","LEBANON-ELDORADO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[22533,null,"BURNS-WAVERLEY","ES0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","BURNS-WAVERLEY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[22541,null,"ESSEX-DOWNS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-DOWNS (02)",4.4620945071616617E-5,0]
[22561,null,"GOLF VIEW-ROEBUCK","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","GOLF VIEW-ROEBUCK (04)",0,0]
[22564,null,"ATTERCLIFFE-DERBY","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",4.4620945071616617E-5,0]
[22584,null,"MITCHELL-HACKETT","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MITCHELL-HACKETT (01)",4.4620945071616617E-5,0]
[22590,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22606,null,"BROWNING-SCOTT","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","BROWNING-SCOTT (01)",4.4620945071616617E-5,0]
[22613,null,"GRAVES-MARKET","ES0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GRAVES-MARKET (02)",4.4620945071616617E-5,0]
[22629,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22649,null,"HAMLYN-VIDA","ES0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","HAMLYN-VIDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22656,null,"BREARLEY-BALMORAL","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-BALMORAL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[22669,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","WATT-THE AVENUE (01)",0,0]
[22678,null,"HIGH 883-MELB WATER","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HIGH 883-MELB WATER (01)",4.4620945071616617E-5,0]
[22694,null,"GAFFNEY-HIGINBOTHAM","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","GAFFNEY-HIGINBOTHAM (02)",4.4620945071616617E-5,0]
[22714,null,"TREADWELL-DUDLEY","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","TREADWELL-DUDLEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[22721,null,"WALTER-ARRAN 2","FE0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","WALTER-ARRAN 2 (02)",0,0]
[22737,null,"KERNAN-CARNARVON","NS0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","KERNAN-CARNARVON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22748,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","WATT-THE AVENUE (04)",0,0]
[22759,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[22779,null,"CANTERBURY-BUNDANOON","SBY-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","SBY","CANTERBURY-BUNDANOON (02)",4.4620945071616617E-5,0]
[22786,null,"LOCKHEED-BOEING","AW0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","LOCKHEED-BOEING (02)",{"$f":"IF(G22787=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J22787=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[22802,null,"BALLYMENA-KIRKHAM","COO-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","BALLYMENA-KIRKHAM (04)",4.4620945071616617E-5,0]
[22809,null,"BRADSHAW-MARY","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BRADSHAW-MARY (03)",4.4620945071616617E-5,0]
[22827,null,"LANDELLS-MARTIN","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","LANDELLS-MARTIN (04)",4.4620945071616617E-5,0]
[22831,null,"BOND-ORIEL","EP0-034","2025-02-02","2025-02-08","Y","Y","Y","Y","N","N","EP0","BOND-ORIEL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[22851,null,"ALMA-YARRA","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","ALMA-YARRA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22867,null,"THORPE-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","THORPE-WOODS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22874,null,"ALLAN-CLIFTON","ES0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ALLAN-CLIFTON (02)",4.4620945071616617E-5,0]
[22884,null,"ANDERSON-BOLINGBROKE","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","O'HEA-CUMBERLAND (02)",4.4620945071616617E-5,0]
[22896,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[22916,null,"FORRESTER-COOPER","ES0-025","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","FORRESTER-COOPER (01)",4.4620945071616617E-5,0]
[22923,null,"HILTON-JUSTIN","PV0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-JUSTIN (02)",4.4620945071616617E-5,0]
[22939,null,"HENDRICKS-LORRAINE","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","Y","N","BMS","HENDRICKS-LORRAINE (01)",0,0]
[22959,null,"YEA-KIEWA","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","YEA-KIEWA (01)",4.4620945071616617E-5,0]
[22967,null,"DEAKIN-SPENCER","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DEAKIN-SPENCER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[22981,null,"VANTAGE-DASHING","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","VANTAGE-DASHING (02)",0,0]
[22988,null,"MUNRO-ERSKINE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","MUNRO-ERSKINE (02)",4.4620945071616617E-5,0]
[23004,null,"EISENHOWER-CHALEYER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","EISENHOWER-CHALEYER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23011,null,"NAPOLI-SAN MARCO","COO-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","NAPOLI-SAN MARCO (04)",4.4620945071616617E-5,0]
[23027,null,"GRANGE-CRAMER","CS0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","GRANGE-CRAMER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23046,null,"VANTAGE-DASHING","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","VANTAGE-DASHING (04)",0,0]
[23053,null,"TREADWELL-DUDLEY","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","TREADWELL-DUDLEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[23069,null,"CAMDON-NORTON","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","CAMDON-NORTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23076,null,"NAPOLI-SAN MARCO","COO-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","COO","NAPOLI-SAN MARCO (03)",4.4620945071616617E-5,0]
[23096,null,"CHAMPION-ZEST","ST0-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","CHAMPION-ZEST (02)",0,0]
[23112,null,"HESLEDEN-AMELIA","NS0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","HESLEDEN-AMELIA (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[23125,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23134,null,"BIRCH-BROADMEADOWS","AW0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","BIRCH-BROADMEADOWS (01)",0,0]
[23141,null,"ROCKGLEN WAY P4","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","ROCKGLEN WAY P4 (00)",0,0]
[23161,null,"HART-BOWES","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","HART-BOWES (02)",0,0]
[23177,null,"WATERDALE-LLOYD","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","WATERDALE-LLOYD (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[23184,null,"LENNOX-HYDE","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","LENNOX-HYDE (03)",0,0]
[23196,null,"ALBERT-HARROW","EPN-035","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","ALBERT-HARROW (02)",4.4620945071616617E-5,0]
[23206,null,"ALEXANDRA-NORTHERNHAY","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ALEXANDRA-NORTHERNHAY (02)",4.4620945071616617E-5,0]
[23226,null,"ROXBURGH-ROTHWELL","FT0-026","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FT0","ROXBURGH-ROTHWELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[23229,null,"BIRDWOOD-KEILOR","ES0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BIRDWOOD-KEILOR (03)",4.4620945071616617E-5,0]
[23249,null,"ALMA-CHANDLER","NT0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","ALMA-CHANDLER (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[23261,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[23271,null,"LENNOX-HYDE","FE0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","LENNOX-HYDE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[23291,null,"MCCRAE-ELSEY","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","MCCRAE-ELSEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[23294,null,"MCCRAE-ELSEY","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","MCCRAE-ELSEY (03)",4.4620945071616617E-5,0]
[23314,null,"YERING-GUILDFORD","BD0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","YERING-GUILDFORD (02)",4.4620945071616617E-5,0]
[23321,null,"CORNISH-LIGAR","SBY-012","2025-02-02","2025-02-08","N","N","N","Y","N","N","SBY","CORNISH-LIGAR (01)",0,9.4304036212749905E-5]
[23332,null,"ESMALE-LEBANON","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","ESMALE-LEBANON (02)",4.4620945071616617E-5,0]
[23356,null,"LOUIS-MARSHALL","AW0-005","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","LOUIS-MARSHALL (01)",0,0]
[23363,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","CLARENDON-WHITTAKER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23379,null,"STEEL-THE AVENUE","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","STEEL-THE AVENUE (02)",4.4620945071616617E-5,0]
[23386,null,"BRADSHAW-MARY","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BRADSHAW-MARY (01)",4.4620945071616617E-5,0]
[23402,null,"KEADY-SYDNEY","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","KEADY-SYDNEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[23411,null,"ANDERSON-BOLINGBROKE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","O'HEA-CUMBERLAND (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[23428,null,"PARKLANDS-KELVIN","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","PARKLANDS-KELVIN (02)",4.4620945071616617E-5,0]
[23444,null,"WRIGHT 20-THOMSONS","TMA-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","TMA","WRIGHT 20-THOMSONS (04)",0,0]
[23451,null,"ARTHUR-FAWKNER","ES0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","ARTHUR-FAWKNER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23467,null,"PICKETT-HICKFORD","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","PICKETT-HICKFORD (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[23474,null,"MERBEIN-SUSSEX","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MERBEIN-SUSSEX (01)",4.4620945071616617E-5,0]
[23490,null,"SEPARATION-PERRY","FF0-093","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","SEPARATION-PERRY (04)",{"$f":"IF(G23491=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J23491=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[23509,null,"MCCRAE-ELSEY","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","MCCRAE-ELSEY (03)",4.4620945071616617E-5,0]
[23516,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[23536,null,"MOUNT-BELL","CS0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MOUNT-BELL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23539,null,"MOUNT-BELL","CS0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MOUNT-BELL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23559,null,"KING-MCCRACKEN","ES0-026","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","KING-MCCRACKEN (01)",4.4620945071616617E-5,0]
[23573,null,"GARNET-IDA","ES0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","GARNET-IDA (04)",0,0]
[23581,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[23588,null,"WRIGHT 20-THOMSONS","TMA-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","TMA","WRIGHT 20-THOMSONS (01)",0,0]
[23604,null,"PEEL-DOUGLAS","NT0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","PEEL-DOUGLAS (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[23624,null,"PAMELA-HERBERT","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","PAMELA-HERBERT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[23638,null,"TREADWELL-DUDLEY","ES0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","TREADWELL-DUDLEY (03)",4.4620945071616617E-5,0]
[23646,null,"KERFERD-RALEIGH","ES0-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","KERFERD-RALEIGH (02)",0,0]
[23653,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23669,null,"MACK-PICKETT","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","MACK-PICKETT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[23689,null,"GRANDVIEW-LONGVIEW","NH0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GRANDVIEW-LONGVIEW (02)",4.4620945071616617E-5,0]
[23696,null,"ST HELLIER-UP HEIDELBERG","NH0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","ST HELLIER-UP HEIDELBERG (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23709,null,"SNELL-WATT","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","SNELL-WATT (02)",4.4620945071616617E-5,0]
[23718,null,"HILLCREST-ROYAL","SHM-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","HILLCREST-ROYAL (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[23734,null,"DIAMOND-ROSEHILL","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23754,null,"BEATRICE-FEHON","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","BEATRICE-FEHON (02)",0,0]
[23761,null,"KINGSLEY-ROBERTS","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","KINGSLEY-ROBERTS (01)",4.4620945071616617E-5,0]
[23777,null,"DIAMOND-ROSEHILL","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23788,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[23803,null,"ROSEBERRY-HIGH","PTN-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","ROSEBERRY-HIGH (01)",0,0]
[23806,null,"ROSEBERRY-HIGH","PTN-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","ROSEBERRY-HIGH (01)",0,0]
[23826,null,"CORNISH-LIGAR","SBY-012","2025-02-02","2025-02-08","N","N","N","Y","N","N","SBY","CORNISH-LIGAR (01)",0,9.4304036212749905E-5]
[23842,null,"HUDSONS-HALL","YVE-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","YVE","HUDSONS-HALL (03)",0,0]
[23849,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MALCOLM-ELIZABETH (02)",4.4620945071616617E-5,0]
[23867,null,"NEWMAN-HOTHAM","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NEWMAN-HOTHAM (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[23871,null,"CHAMPION-ZEST","ST0-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","CHAMPION-ZEST (02)",0,0]
[23891,null,"HIGHLANDER-STREAMSIDE","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","HIGHLANDER-STREAMSIDE (03)",0,0]
[23907,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-LANDELLS (02)",4.4620945071616617E-5,0]
[23914,null,"GARNET-IDA","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","GARNET-IDA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[23934,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","CLARENDON-WHITTAKER (01)",4.4620945071616617E-5,0]
[23938,null,"RAVENSCOURT-FULHAM","FF0-083","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (01)",{"$f":"IF(G23939=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J23939=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[23956,null,"HIGHLANDER-STREAMSIDE","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","HIGHLANDER-STREAMSIDE (04)",0,0]
[23963,null,"HIGHLANDER-STREAMSIDE","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","HIGHLANDER-STREAMSIDE (04)",0,0]
[23979,null,"CAMPBELL-DE CARLE","CS0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","CAMPBELL-DE CARLE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[23986,null,"THORPE-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","THORPE-WOODS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[24007,null,"KINGSTON-COLLINSON","TMA-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TMA","KINGSTON-COLLINSON (02)",4.4620945071616617E-5,0]
[24021,null,"SEPARATION-PERRY","FF0-093","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","SEPARATION-PERRY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[24028,null,"HUDSONS-HALL","YVE-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","YVE","HUDSONS-HALL (03)",0,0]
[24044,null,"ARBOR-MACEY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","ARBOR-MACEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[24051,null,"HANSEN-GLAMIS","FW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","HANSEN-GLAMIS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[24071,null,"PARKVIEW-HEIDELBERG","FF0-095","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","PARKVIEW-HEIDELBERG (01)",4.4620945071616617E-5,0]
[24086,null,"CRAIGIEBURN-CHAMPION","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","CRAIGIEBURN-CHAMPION (02)",0,0]
[24093,null,"LENNOX-HYDE","FE0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","LENNOX-HYDE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[24109,null,"ESTEEM-DISTINCTION","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","ESTEEM-DISTINCTION (02)",0,0]
[24116,null,"ESTEEM-DISTINCTION","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","ESTEEM-DISTINCTION (02)",0,0]
[24136,null,"VANTAGE-DASHING","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","VANTAGE-DASHING (01)",0,0]
[24152,null,"VANTAGE-DASHING","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","VANTAGE-DASHING (01)",0,0]
[24153,null,"ALBERT-HARROW","EPN-035","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","ALBERT-HARROW (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[24174,null,"BOOMERANG-AIRFORCE","TH0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (02)",0,0]
[24181,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (01)",0,0]
[24201,null,"O'CONNOR-WHITBY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[24204,null,"CHAMPION-ZEST","ST0-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","CHAMPION-ZEST (02)",0,0]
[24224,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[24232,null,"HUDSONS-HALL","YVE-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","YVE","HUDSONS-HALL (03)",0,0]
[24246,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[24266,null,"ALOHA-GREENE","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ALOHA-GREENE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[24269,null,"HEATHER-CYPRESS","FW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","HEATHER-CYPRESS (01)",4.4620945071616617E-5,0]
[24289,null,"WARATAH-DERBY","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WARATAH-DERBY (03)",4.4620945071616617E-5,0]
[24296,null,"ESSEX-DUDLEY","FW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ESSEX-DUDLEY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[24315,null,"MAYFIELD-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","MAYFIELD-MUNRO (01)",4.4620945071616617E-5,0]
[24331,null,"GLADSTONE-CHAPMAN","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","GLADSTONE-CHAPMAN (01)",4.4620945071616617E-5,0]
[24334,null,"YALLAMBIE-LOWER PLENTY","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","YALLAMBIE-LOWER PLENTY (01)",4.4620945071616617E-5,0]
[24354,null,"YEA-KIEWA","BD0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","YEA-KIEWA (01)",0,0]
[24361,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[24372,null,"SEPARATION-PERRY","FF0-093","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","SEPARATION-PERRY (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[24383,null,"SEXTON-HALSEY","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","SEXTON-HALSEY (03)",0,0]
[24403,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","EDWIN-ST HELLIER (02)",4.4620945071616617E-5,0]
[24419,null,"GERVASE-PECHAM","PV0-031","2025-02-02","2025-02-08","N","Y","N","N","N","N","PV0","GERVASE-PECHAM (02)",0,0]
[24426,null,"WOOD-GREENBELT","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","WOOD-GREENBELT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[24442,null,"OUTHWAITE-MCEWAN","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","OUTHWAITE-MCEWAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[24451,null,"DENYS-GLYNDA","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","DENYS-GLYNDA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[24468,null,"BLOOMFIELD-ROSAMOND","YVE-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","BLOOMFIELD-ROSAMOND (01)",4.4620945071616617E-5,0]
[24484,null,"REGINA-BELLEVUE","NH0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","REGINA-BELLEVUE (02)",4.4620945071616617E-5,0]
[24491,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[24511,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","CLARENDON-WHITTAKER (03)",4.4620945071616617E-5,0]
[24514,null,"WAIORA-CHURCHILL","NH0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","WAIORA-CHURCHILL (01)",{"$f":"IF(G24515=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J24515=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[24530,null,"WHITFIELD-WHITES","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","WHITFIELD-WHITES (02)",0,0]
[24549,null,"WHITFIELD-CRAIGIEBURN","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","WHITFIELD-CRAIGIEBURN (04)",0,0]
[24556,null,"WHITFIELD-CRAIGIEBURN","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","WHITFIELD-CRAIGIEBURN (04)",0,0]
[24563,null,"MCGEORGE RD-P26","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","MCGEORGE RD-P26 (00)",0,0]
[24579,null,"WOOD-GREENBELT","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","WOOD-GREENBELT (02)",4.4620945071616617E-5,0]
[24599,null,"ASHLEY-EDWARDES","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ASHLEY-EDWARDES (02)",4.4620945071616617E-5,0]
[24613,null,"DEAKIN-SPENCER","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DEAKIN-SPENCER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[24621,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (03)",4.4620945071616617E-5,0]
[24628,null,"GYLES-ESSEX","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","GYLES-ESSEX (03)",4.4620945071616617E-5,0]
[24644,null,"MONTGOMERY-MT ALEXANDER #2","NS0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER #2 (02)",0,0]
[24664,null,"MONTGOMERY-MT ALEXANDER #2","NS0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER #2 (02)",0,0]
[24671,null,"MONTGOMERY-MT ALEXANDER #2","NS0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER #2 (02)",0,0]
[24680,null,"WARATAH-CAROL","AW0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","SYCAMORE-BROADMEADOWS (01)",4.4620945071616617E-5,0]
[24693,null,"PEPPERCRESS-SPEARYS","SHM-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","PEPPERCRESS-SPEARYS (04)",0,0]
[24709,null,"COOMA-GOWER","PTN-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","COOMA-GOWER (02)",4.4620945071616617E-5,0]
[24729,null,"GARNET-EMERALD","ES0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GARNET-EMERALD (02)",4.4620945071616617E-5,0]
[24736,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[24749,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MOUSHALL-NOLAN (02)",4.4620945071616617E-5,0]
[24758,null,"RHYOLITE-HIGHPARK","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","RHYOLITE-HIGHPARK (04)",0,0]
[24778,null,"WYMLET-LYNCH","CN0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","WYMLET-LYNCH (02)",4.4620945071616617E-5,0]
[24781,null,"WHITELAW-BOLDREWOOD","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",4.4620945071616617E-5,0]
[24801,null,"PORTER-DOUGHARTY","NH0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","PORTER-DOUGHARTY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[24817,null,"DALKEITH-GORDON","AW0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","DALKEITH-GORDON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[24828,null,"RYDER-NOLAN","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","RYDER-NOLAN (02)",4.4620945071616617E-5,0]
[24843,null,"SYLVESTER-GORDON","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","SYLVESTER-GORDON (02)",4.4620945071616617E-5,0]
[24846,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[24866,null,"HIGHRIDGE-ROBERTS","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","HIGHRIDGE-ROBERTS (03)",0,0]
[24882,null,"DOUGLAS-PASCOE VALE","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","DOUGLAS-PASCOE VALE (01)",4.4620945071616617E-5,0]
[24889,null,"VICTORY-FOSTERS","TMA-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TMA","VICTORY-FOSTERS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[24907,null,"JELLICOE-WATERDALE","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","JELLICOE-WATERDALE (02)",4.4620945071616617E-5,0]
[24911,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","CLARENDON-WHITTAKER (01)",4.4620945071616617E-5,0]
[24931,null,"CHAPMAN-BELAIR","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CHAPMAN-BELAIR (02)",4.4620945071616617E-5,0]
[24938,null,"OUTHWAITE-ORIEL","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","OUTHWAITE-ORIEL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[24954,null,"CENTREWAY-WINGARA","AW0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","CENTREWAY-WINGARA (04)",0,0]
[24961,null,"BELL-ALBERT","EP0-042","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","BELL-ALBERT (02)",0,0]
[24978,null,"YORK-NAPIER","NS0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","YORK-NAPIER (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[24996,null,"WYONG-CENTREWAY","AW0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","WYONG-CENTREWAY (01)",0,0]
[25003,null,"MARIE-MURPHY","PV0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","MARIE-MURPHY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25019,null,"KALANG-PLUMPTON","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KALANG-PLUMPTON (02)",4.4620945071616617E-5,0]
[25026,null,"IVANHOE-WESTLEY","HB0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","HB0","IVANHOE-WESTLEY (02)",{"$f":"IF(G25027=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J25027=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[25042,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[25057,null,"DELAWARE-JUSCELINA","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","DELAWARE-JUSCELINA (02)",0,0]
[25068,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,0]
[25084,null,"JACK-FORD","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","JACK-FORD (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[25091,null,"ERIC-ADA","CS0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","McGOWAN-MURRAY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[25111,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","CLARENDON-WHITTAKER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25126,null,"VANTAGE-ALTAMONT","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","VANTAGE-ALTAMONT (01)",0,0]
[25133,null,"LAHINCH-WIDFORD","BMS-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","BMS","LAHINCH-WIDFORD (01)",4.4620945071616617E-5,0]
[25149,null,"MARGARET-WINIFRED","PV0-022","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","PV0","MARGARET-WINIFRED (04)",4.4620945071616617E-5,0]
[25156,null,"ARVERN MEDFIELD No.2","BY0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BY0","ARVERN MEDFIELD No.2 (02)",0,0]
[25176,null,"JOFFRE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","JOFFRE-KENT (01)",4.4620945071616617E-5,0]
[25179,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","WATT-THE AVENUE (02)",0,0]
[25193,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[25205,null,"CHAPMAN-GRANDVIEW","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CHAPMAN-GRANDVIEW (01)",4.4620945071616617E-5,0]
[25221,null,"DELAWARE-JUSCELINA","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","DELAWARE-JUSCELINA (03)",0,0]
[25241,null,"STEEL-THE AVENUE","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","STEEL-THE AVENUE (02)",4.4620945071616617E-5,0]
[25244,null,"BRUNEL-TRUMAN","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","BRUNEL-TRUMAN (01)",4.4620945071616617E-5,0]
[25264,null,"ROSAMOND-RIVER","BY0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","ROSAMOND-RIVER (01)",4.4620945071616617E-5,0]
[25272,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25286,null,"STEWART-PASCOE VALE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","STEWART-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25306,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BLENHEIM-WOODS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25309,null,"STANGER-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","STANGER-ADENEY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[25329,null,"JOFFRE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","JOFFRE-KENT (02)",4.4620945071616617E-5,0]
[25336,null,"WILLIAM-JUNCTION","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WILLIAM-JUNCTION (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25355,null,"YORK-NAPIER","NS0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","YORK-NAPIER (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[25358,null,"CAMDON-NORTON","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","CAMDON-NORTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25378,null,"ESSEX-DUDLEY","FW0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ESSEX-DUDLEY (03)",4.4620945071616617E-5,0]
[25394,null,"TENNYSON-TYLER","PTN-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","TENNYSON-TYLER (01)",4.4620945071616617E-5,0]
[25401,null,"MARGARET-WINIFRED","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MARGARET-WINIFRED (01)",4.4620945071616617E-5,0]
[25417,null,"METTLE-SCENERY","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","METTLE-SCENERY (03)",0,0]
[25434,null,"TRUMPER-KOKODA","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","TRUMPER-KOKODA (03)",0,0]
[25443,null,"JEFFREY-WESTGARTH","FF0-089","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (03)",0,0]
[25459,null,"STEPHEN-PRINCESS","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","STEPHEN-PRINCESS (02)",0,0]
[25466,null,"RILL-OLIVE","NH0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","RILL-OLIVE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25486,null,"OLIVE-SYLVAN","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","OLIVE-SYLVAN (02)",4.4620945071616617E-5,0]
[25491,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,0]
[25508,null,"EVELL-MORLEY","PV0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","EVELL-MORLEY (02)",4.4620945071616617E-5,0]
[25524,null,"LANDELLS-MARTIN","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","LANDELLS-MARTIN (04)",4.4620945071616617E-5,0]
[25531,null,"FULLWOOD-WHEELER","SBY-032","2025-02-02","2025-02-08","Y","N","N","N","N","N","SBY","FULLWOOD-WHEELER (04)",4.4620945071616617E-5,0]
[25538,null,"MASON-HIGH","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MASON-HIGH (01)",{"$f":"IF(G25539=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J25539=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[25554,null,"BELGROVE-OVANDO","PTN-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","BELGROVE-OVANDO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[25570,null,"WILKINSON-BENDIGO","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","WILKINSON-BENDIGO (01)",4.4620945071616617E-5,0]
[25576,null,"WATERDALE-LLOYD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","WATERDALE-LLOYD (01)",4.4620945071616617E-5,0]
[25596,null,"ST HELLIER-UP HEIDELBERG","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","ST HELLIER-UP HEIDELBERG (01)",4.4620945071616617E-5,0]
[25603,null,"HEATHER-DINAH","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","HEATHER-DINAH (01)",4.4620945071616617E-5,0]
[25619,null,"NERISSA-SNELL","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","NERISSA-SNELL (02)",4.4620945071616617E-5,0]
[25639,null,"MCGEORGE RD-P25","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","MCGEORGE RD-P25 (00)",0,0]
[25649,null,"THORPE-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","THORPE-WOODS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25661,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",0,0]
[25668,null,"MARGARET-WINIFRED","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MARGARET-WINIFRED (01)",4.4620945071616617E-5,0]
[25684,null,"WESTMINSTER-MILITARY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","WESTMINSTER-MILITARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[25704,null,"BERNARD-BROADWAY","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","BERNARD-BROADWAY (03)",4.4620945071616617E-5,0]
[25711,null,"WOODS-CHALLIS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WOODS-CHALLIS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25720,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[25733,null,"BRADLEY-MASON","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BRADLEY-MASON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25749,null,"BRADLEY-MASON","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BRADLEY-MASON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25756,null,"WOOD-GREENBELT","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","WOOD-GREENBELT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[25776,null,"KIRBISTER-GAFFNEY","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","KIRBISTER-GAFFNEY (03)",4.4620945071616617E-5,0]
[25792,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","STRATHALLAN-WILSON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25799,null,"CHEDDAR-JINGHI","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CHEDDAR-JINGHI (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[25818,null,"MATTHEWS-KEILOR","ES0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","MATTHEWS-KEILOR (01)",0,0]
[25821,null,"EGLINTON-ARGYLE","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","EGLINTON-ARGYLE (03)",4.4620945071616617E-5,0]
[25841,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[25857,null,"BERNARD-BROADWAY","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","BERNARD-BROADWAY (03)",4.4620945071616617E-5,0]
[25868,null,"VINEYARD RD-P31","SHM-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","VINEYARD RD-P31 (00)",0,0]
[25883,null,"PASCOE-BLACK","BD0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BD0","PASCOE-BLACK (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[25886,null,"HERBERT-GARNER","BD0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","HERBERT-GARNER (01)",0,0]
[25906,null,"HIGHLANDER-DELAWARE","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","HIGHLANDER-DELAWARE (02)",0,0]
[25913,null,"STEANE-ALBERT","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STEANE-ALBERT (03)",4.4620945071616617E-5,0]
[25929,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25947,null,"MCNAMARA-ROBERTS","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","MCNAMARA-ROBERTS (02)",4.4620945071616617E-5,0]
[25951,null,"BUNTING-SOMERVILLE 463A","TH0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","BUNTING-SOMERVILLE 463A (01)",0,0]
[25971,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[25978,null,"EAST-THACKERAY","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","EAST-THACKERAY (04)",4.4620945071616617E-5,0]
[25994,null,"JOFFRE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","JOFFRE-KENT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26001,null,"CLYDEBANK-AFTON","ES0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","CLYDEBANK-AFTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26018,null,"HILLSIDE-ROBERTS","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILLSIDE-ROBERTS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26036,null,"VANTAGE-DASHING","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","VANTAGE-DASHING (01)",0,0]
[26043,null,"JOFFRE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","JOFFRE-KENT (01)",4.4620945071616617E-5,0]
[26059,null,"NEWMAN-HOTHAM","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NEWMAN-HOTHAM (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26066,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26086,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","O'DOWD-HOWARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26097,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26108,null,"METTLE-SCENERY","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","METTLE-SCENERY (02)",0,0]
[26124,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","O'DOWD-HOWARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26131,null,"ALMA-WAVERLEY","ES0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","ALMA-WAVERLEY (02)",4.4620945071616617E-5,0]
[26151,null,"CARTWRIGHT-PASCOE VALE","PV0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","CARTWRIGHT-PASCOE VALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26154,null,"ROGERSON-THOMPSON","BY0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","ROGERSON-THOMPSON (02)",4.4620945071616617E-5,0]
[26176,null,"DARLING-WHITE","FF0-095","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FF0","DARLING-WHITE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[26189,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",0,0]
[26196,null,"PLENTY-RESERVOIR COLLEGE","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","PLENTY-RESERVOIR COLLEGE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26216,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26219,null,"WOOD-SYDNEY 2","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","WOOD-SYDNEY 2 (01)",4.4620945071616617E-5,0]
[26233,null,"STEWART-PASCOE VALE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","STEWART-PASCOE VALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26245,null,"DOUGLAS-PASCOE VALE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DOUGLAS-PASCOE VALE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26261,null,"BRAIDHILL-WINDSOR","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","BRAIDHILL-WINDSOR (02)",4.4620945071616617E-5,0]
[26281,null,"PORTER-DOUGHARTY","NH0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","PORTER-DOUGHARTY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26284,null,"RICHARDS-BELL","CS0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","RICHARDS-BELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26304,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,0]
[26312,null,"WILLIAM-JUNCTION","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","WILLIAM-JUNCTION (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26326,null,"PEARL-WHEATSHEAF","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","PEARL-WHEATSHEAF (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26333,null,"BIRDWOOD-REGENT","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BIRDWOOD-REGENT (02)",4.4620945071616617E-5,0]
[26353,null,"HAVELOCK-BALLARAT","BY0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BY0","HAVELOCK-BALLARAT (02)",0,0]
[26369,null,"ARGYLE-DAREBIN","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",4.4620945071616617E-5,0]
[26376,null,"EAST-THACKERAY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","EAST-THACKERAY (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[26395,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26398,null,"GREEN-SPARKFORD","EP0-034","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","GREEN-SPARKFORD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26418,null,"EGLINTON-ARGYLE","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","EGLINTON-ARGYLE (04)",4.4620945071616617E-5,0]
[26434,null,"BUNTING-SOMERVILLE 463A","TH0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","BUNTING-SOMERVILLE 463A (01)",{"$f":"IF(G26435=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J26435=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[26441,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26457,null,"McPHERSON-ALEXANDRA 2","NS0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","McPHERSON-ALEXANDRA 2 (01)",0,0]
[26462,null,"DEAKIN-SPENCER","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DEAKIN-SPENCER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[26483,null,"FORDHAM-STRATHMERTON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","FORDHAM-STRATHMERTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26499,null,"KATHLEEN-WOOD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","KATHLEEN-WOOD (02)",4.4620945071616617E-5,0]
[26506,null,"JEFFREY-WESTGARTH","FF0-089","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","JEFFREY-WESTGARTH (03)",0,0]
[26513,null,"GELLIES RD-P3","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","GELLIES RD-P3 (00)",0,0]
[26529,null,"WELLINGTON-VICTORIA","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","WELLINGTON-VICTORIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26541,null,"GOSFORD-NICHOLAS","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","GOSFORD-NICHOLAS (02)",4.4620945071616617E-5,0]
[26551,null,"MOUSHALL-HOFFMANS","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","MOUSHALL-HOFFMANS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26571,null,"MCCRAE-ELSEY","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","MCCRAE-ELSEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26578,null,"RATHCOWN-CHEDDAR","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","RATHCOWN-CHEDDAR (01)",4.4620945071616617E-5,0]
[26594,null,"DELAWARE-MENDIP","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","DELAWARE-MENDIP (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26610,null,"MT ALEXANDER-NAPIER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (03)",0,0]
[26620,null,"MT ALEXANDER-NAPIER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (03)",0,0]
[26636,null,"MT ALEXANDER-NAPIER","NS0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MT ALEXANDER-NAPIER (03)",0,0]
[26643,null,"DUNDEE-MEADE","SHM-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","SHM","DUNDEE-MEADE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[26659,null,"ARTHUR-ELIZABETH","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ARTHUR-ELIZABETH (03)",4.4620945071616617E-5,0]
[26679,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","MULBERRY-GONA (03)",4.4620945071616617E-5,0]
[26689,null,"NOVIAN-MARAMA","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","NOVIAN-MARAMA (03)",4.4620945071616617E-5,0]
[26701,null,"PICKETT-HICKFORD","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","PICKETT-HICKFORD (02)",4.4620945071616617E-5,0]
[26708,null,"LOWSON-MINONA","CN0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","LOWSON-MINONA (02)",4.4620945071616617E-5,0]
[26724,null,"FRANCIS-VINCENT","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","FRANCIS-VINCENT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26731,null,"BAYVIEW-TOBRUK","NT0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BAYVIEW-TOBRUK (02)",4.4620945071616617E-5,0]
[26751,null,"MACK-PICKETT","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","MACK-PICKETT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26760,null,"ANSTEY-PHILLIP","TT0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ANSTEY-PHILLIP (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26773,null,"PORTER-DOUGHARTY","NH0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","PORTER-DOUGHARTY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26793,null,"BIRCH-BROADMEADOWS","AW0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","BIRCH-BROADMEADOWS (01)",0,0]
[26796,null,"BOSQUET-BALLARAT","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","BOSQUET-BALLARAT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26816,null,"STRATHALLAN-WILSON","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","STRATHALLAN-WILSON (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[26832,null,"DAVID-RACHELLE","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","DAVID-RACHELLE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26839,null,"HIGGINS-MCKELL","SBY-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","HIGGINS-MCKELL (02)",0,0]
[26858,null,"HANSEN-GLAMIS","FW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","HANSEN-GLAMIS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26861,null,"PEARL-WHEATSHEAF","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","PEARL-WHEATSHEAF (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26881,null,"CRESWICK-LATROBE","FE0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FE0","CRESWICK-LATROBE (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[26897,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[26904,null,"SALISBURY-JACK","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","SALISBURY-JACK (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26918,null,"LEBANON-ELDORADO","PV0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","PV0","LEBANON-ELDORADO (02)",0,0]
[26926,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","MULBERRY-GONA (01)",4.4620945071616617E-5,0]
[26946,null,"MIRANDA-MAIS","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","MIRANDA-MAIS (01)",{"$f":"IF(G26947=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J26947=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[26953,null,"LEBANON-FENACRE","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","LEBANON-FENACRE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[26969,null,"LIBERTY-PERKINS","EP0-034","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","LIBERTY-PERKINS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[26975,null,"KOORA-BAMAL","SHM-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","KOORA-BAMAL (02)",0,0]
[26991,null,"LEBANON-FENACRE","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","LEBANON-FENACRE (02)",4.4620945071616617E-5,0]
[27011,null,"EAST-THACKERAY","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","EAST-THACKERAY (01)",4.4620945071616617E-5,0]
[27018,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","Y","N","BMS","ELLIOT-GRAHAM (03)",0,0]
[27034,null,"BROWNING-SCOTT","TT0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","TT0","BROWNING-SCOTT (02)",0,0]
[27041,null,"GYLES-ESSEX","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","GYLES-ESSEX (01)",4.4620945071616617E-5,0]
[27054,null,"LOCH-REYNARDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","LOCH-REYNARDS (02)",4.4620945071616617E-5,0]
[27076,null,"BUSHRANGER-CATTLECROSSING","SHM-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","BUSHRANGER-CATTLECROSSING (03)",0,0]
[27083,null,"JOHN-WINIFRED","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","JOHN-WINIFRED (03)",4.4620945071616617E-5,0]
[27099,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","BENDIGO-ALPINE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27106,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (01)",0,0]
[27126,null,"GRENHILDA-DOUGLAS","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GRENHILDA-DOUGLAS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27137,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,0]
[27148,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27164,null,"WHITELAW-BOLDREWOOD","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","WHITELAW-BOLDREWOOD (01)",4.4620945071616617E-5,0]
[27171,null,"ASCOT VALE 331-YOUNG","NS0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ASCOT VALE 331-YOUNG (01)",0,0]
[27191,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MARGTMARY-MURRAY (03)",4.4620945071616617E-5,0]
[27194,null,"FORDHAM-STRATHMERTON","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","FORDHAM-STRATHMERTON (01)",4.4620945071616617E-5,0]
[27216,null,"WALKER-NEWCASTLE","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","WALKER-NEWCASTLE (02)",4.4620945071616617E-5,0]
[27220,null,"KIAORA-GILBERT","CN0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","CN0","KIAORA-GILBERT (02)",0,0]
[27236,null,"SALISBURY-WILLIAMSTOWN","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","SALISBURY-WILLIAMSTOWN (04)",0,0]
[27256,null,"MCCRAE-ELSEY","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","MCCRAE-ELSEY (03)",4.4620945071616617E-5,0]
[27259,null,"HEATHER-DINAH","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HEATHER-DINAH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27279,null,"GRAVES-MARKET","ES0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","GRAVES-MARKET (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27283,null,"O'DOWD-HOWARD","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","O'DOWD-HOWARD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27301,null,"BUSHRANGER-CATTLECROSSING","SHM-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","BUSHRANGER-CATTLECROSSING (04)",0,0]
[27308,null,"COUANGALT RD-P19","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","COUANGALT RD-P19 (00)",0,0]
[27324,null,"DOYLE-NORTH","BY0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","DOYLE-NORTH (02)",4.4620945071616617E-5,0]
[27344,null,"ALBERT 8-14 FOLEY","EP0-035","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","ALBERT 8-14 FOLEY (01)",0,0]
[27352,null,"BREARLEY-ROSE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","BREARLEY-ROSE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27366,null,"NIMMO-BUCKLEY","ES0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","BUCKLEY-PRICE (01)",4.4620945071616617E-5,0]
[27373,null,"ST JAMES-WOBURN","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","ST JAMES-WOBURN (04)",4.4620945071616617E-5,0]
[27393,null,"GRENHILDA-DOUGLAS","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GRENHILDA-DOUGLAS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27409,null,"CHARTERIS-BURKE","HB0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","CHARTERIS-BURKE (01)",4.4620945071616617E-5,0]
[27416,null,"GLASGOW-HIGH","TT0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","GLASGOW-HIGH (01)",4.4620945071616617E-5,0]
[27435,null,"ALBERT 8-14 FOLEY","EP0-035","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","ALBERT 8-14 FOLEY (01)",0,0]
[27438,null,"ALBERT 8-14 FOLEY","EP0-035","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","ALBERT 8-14 FOLEY (01)",0,0]
[27458,null,"ARTHUR-SEPARATION","FF0-093","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","ARTHUR-SEPARATION (02)",{"$f":"IF(G27459=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J27459=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[27474,null,"SYMONS-GILBERT","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","SYMONS-GILBERT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27481,null,"FAWKNER-ROBERTS","AW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FAWKNER-ROBERTS (02)",0,0]
[27488,null,"BOLDREWOOD-McMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","BOLDREWOOD-McMAHON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27502,null,"O'CONNOR-WHITBY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[27523,null,"WOLSELEY-THE AVENUE","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","WOLSELEY-THE AVENUE (01)",4.4620945071616617E-5,0]
[27526,null,"WALKER-NEWCASTLE","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","WALKER-NEWCASTLE (02)",4.4620945071616617E-5,0]
[27546,null,"BEATRICE-JENSEN","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BEATRICE-JENSEN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27553,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (02)",4.4620945071616617E-5,0]
[27569,null,"MCIVOR-OAKHILL","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MCIVOR-OAKHILL (01)",4.4620945071616617E-5,0]
[27581,null,"MARATHON 281-HIGHLANDER","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",0,0]
[27591,null,"MARATHON 281-HIGHLANDER","ST0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","MARATHON 281-HIGHLANDER (01)",0,0]
[27611,null,"ALTONA-ORIEL","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",0,0]
[27618,null,"BELGROVE-OVANDO","PTN-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","BELGROVE-OVANDO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27634,null,"JULIET-BENT","NS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NS0","JULIET-BENT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27654,null,"WATERDALE-LLOYD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","WATERDALE-LLOYD (01)",4.4620945071616617E-5,0]
[27655,null,"HOBSON-HOME","NT0-016","2025-02-02","2025-02-08","N","Y","N","N","N","N","NT0","HOBSON-HOME (01)",0,0]
[27656,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27657,null,"CHAPMAN-BELAIR","PV0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","CHAPMAN-BELAIR (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27658,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",4.4620945071616617E-5,0]
[27659,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",0,0]
[27660,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",0,0]
[27661,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",4.4620945071616617E-5,0]
[27662,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",0,0]
[27663,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",0,0]
[27664,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",4.4620945071616617E-5,0]
[27665,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (01)",0,0]
[27666,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ESSEX-LANDELLS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27667,null,"ROCK-DIANNE","ST0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ST0","ROCK-DIANNE (02)",4.4620945071616617E-5,0]
[27668,null,"ALEXANDRA-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ALEXANDRA-LANDELLS (01)",4.4620945071616617E-5,0]
[27669,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27670,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27671,null,"MURRAY-BONWICK","CN0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MURRAY-BONWICK (03)",4.4620945071616617E-5,0]
[27672,null,"DEAKIN-SPENCER","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DEAKIN-SPENCER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27673,null,"PRESTON-MUNRO","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","PRESTON-MUNRO (02)",4.4620945071616617E-5,0]
[27674,null,"LLOYD-MONASH","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",0,0]
[27675,null,"LLOYD-MONASH","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",0,0]
[27676,null,"RICHELIEU-ESSEX","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","RICHELIEU-ESSEX (02)",4.4620945071616617E-5,0]
[27677,null,"RICHELIEU-ESSEX","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","RICHELIEU-ESSEX (02)",4.4620945071616617E-5,0]
[27678,null,"DAVIS-MILITARY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","DAVIS-MILITARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27679,null,"MALCOLM-ELIZABETH","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MALCOLM-ELIZABETH (02)",4.4620945071616617E-5,0]
[27680,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27681,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27682,null,"MARKS-YORK","NS0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","MARKS-YORK (01)",4.4620945071616617E-5,0]
[27683,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","ETZEL-CLYDESDALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27684,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","ETZEL-CLYDESDALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27685,null,"HILTON-WIDFORD","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-WIDFORD (03)",4.4620945071616617E-5,0]
[27686,null,"HILBERT-HARRINGTON","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILBERT-HARRINGTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27687,null,"GARNET-IDA","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","GARNET-IDA (02)",4.4620945071616617E-5,0]
[27688,null,"GILBANK-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","GILBANK-GILBERT (01)",4.4620945071616617E-5,0]
[27689,null,"GILBANK-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","GILBANK-GILBERT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27690,null,"GRENHILDA-DOUGLAS","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GRENHILDA-DOUGLAS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27691,null,"STEWART-PASCOE VALE","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","STEWART-PASCOE VALE (01)",4.4620945071616617E-5,0]
[27692,null,"RICHELIEU-ESSEX","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","RICHELIEU-ESSEX (02)",4.4620945071616617E-5,0]
[27693,null,"LLOYD-MONASH","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","LLOYD-MONASH (01)",0,0]
[27694,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","CLYDE-MASON (02)",4.4620945071616617E-5,0]
[27695,null,"BLACK-MC MAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","BLACK-MC MAHON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27696,null,"MCCOLL-MALPAS","PTN-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","NA",4.4620945071616617E-5,9.4304036212749905E-5]
[27697,null,"McPHERSON-ALEXANDRA 2","NS0-009","2025-02-02","2025-02-08","N","Y","N","N","Y","N","NS0","McPHERSON-ALEXANDRA 2 (04)",0,0]
[27698,null,"SPENCER-ROBERTS","ES0-025","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","NA",4.4620945071616617E-5,0]
[27699,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","ETZEL-CLYDESDALE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27700,null,"ALEXANDRA-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ALEXANDRA-LANDELLS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27701,null,"HAIG-GILBERT","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","HAIG-GILBERT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27702,null,"NELSON-LYON","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","NELSON-LYON (04)",4.4620945071616617E-5,0]
[27703,null,"BEATRICE-JENSEN","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BEATRICE-JENSEN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27704,null,"BEATRICE-JENSEN","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BEATRICE-JENSEN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27705,null,"THE BOULEVARD-AFTON","ES0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","THE BOULEVARD-AFTON (00)",4.4620945071616617E-5,0]
[27706,null,"JUKES-LANIGAN","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","JUKES-LANIGAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[27707,null,"ALTONA-ORIEL","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",0,0]
[27708,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[27709,null,"JACKA-MCCRACKEN","ES0-026","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","JACKA-MCCRACKEN (02)",4.4620945071616617E-5,0]
[27710,null,"ARGYLE-DAREBIN","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",4.4620945071616617E-5,0]
[27711,null,"ARGYLE-DAREBIN","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",4.4620945071616617E-5,0]
[27712,null,"WILKINSON-BENDIGO","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","WILKINSON-BENDIGO (01)",4.4620945071616617E-5,0]
[27713,null,"MACEDON-POWLETT","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","MACEDON-POWLETT (01)",0,0]
[27714,null,"ESSEX-DOWNS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ESSEX-DOWNS (02)",{"$f":"IF(G27715=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J27715=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[27715,null,"HILTON-WEST","PV0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-WEST (03)",4.4620945071616617E-5,0]
[27716,null,"NEAL-DINAH","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NEAL-DINAH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27717,null,"WEST-JOHN","PV0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","WEST-JOHN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27718,null,"ALTONA-ORIEL","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",0,0]
[27719,null,"WILLIAM-MASON","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","WILLIAM-MASON (02)",4.4620945071616617E-5,0]
[27720,null,"SHELLEY-NOGA","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","SHELLEY-NOGA (01)",4.4620945071616617E-5,0]
[27721,null,"ROGERSON-THOMPSON","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","ROGERSON-THOMPSON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27722,null,"PASCOE VALE-MT ALEXANDER","NS0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","PASCOE VALE-MT ALEXANDER (04)",0,0]
[27723,null,"KEILOR-MC CULLOCH","ES0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","KEILOR-MC CULLOCH (03)",4.4620945071616617E-5,0]
[27724,null,"KEILOR-MC CULLOCH","ES0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","KEILOR-MC CULLOCH (03)",4.4620945071616617E-5,0]
[27725,null,"SUNBURY RD-P68A","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","SUNBURY RD-P68A (00)",0,0]
[27726,null,"ARBOR-MACEY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","ARBOR-MACEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27727,null,"HEATHCOTE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HEATHCOTE-KENT (02)",4.4620945071616617E-5,0]
[27728,null,"RYDER-NOLAN","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","RYDER-NOLAN (02)",4.4620945071616617E-5,0]
[27729,null,"CALDER-DAVIS","SHM-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","SHM","CALDER-DAVIS (00)",0,0]
[27730,null,"ALTONA-ORIEL","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","ALTONA-ORIEL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27731,null,"ESSEX-DOWNS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-DOWNS (02)",4.4620945071616617E-5,0]
[27732,null,"CENTREWAY-WINGARA","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","CENTREWAY-WINGARA (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27733,null,"ETZEL-CLYDESDALE","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","ETZEL-CLYDESDALE (01)",0,0]
[27734,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (02)",0,0]
[27735,null,"MCCRAE-ELSEY","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","MCCRAE-ELSEY (03)",4.4620945071616617E-5,0]
[27736,null,"MCCRAE-ELSEY","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","MCCRAE-ELSEY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27737,null,"OMAR-MITCHELL","BY0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","OMAR-MITCHELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27738,null,"OMAR-MITCHELL","BY0-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","OMAR-MITCHELL (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27739,null,"SYMONS-GILBERT","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","SYMONS-GILBERT (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[27740,null,"BELGROVE-OVANDO","PTN-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","BELGROVE-OVANDO (02)",4.4620945071616617E-5,0]
[27741,null,"RICHELIEU-ESSEX","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","RICHELIEU-ESSEX (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27742,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","CLARENDON-WHITTAKER (03)",4.4620945071616617E-5,0]
[27743,null,"HOLDEN-MILITARY","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","HOLDEN-MILITARY (01)",4.4620945071616617E-5,0]
[27744,null,"ESSEX-DOWNS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-DOWNS (02)",4.4620945071616617E-5,0]
[27745,null,"LANDELLS-MARTIN","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","LANDELLS-MARTIN (03)",4.4620945071616617E-5,0]
[27746,null,"LANTANA-IVANHOE","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","LANTANA-IVANHOE (02)",4.4620945071616617E-5,0]
[27747,null,"LINDSAY-GLENROY","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","LINDSAY-GLENROY (02)",4.4620945071616617E-5,0]
[27748,null,"LINDSAY-GLENROY","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","LINDSAY-GLENROY (02)",4.4620945071616617E-5,0]
[27749,null,"PINE-HENTY","CN0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","PINE-HENTY (02)",4.4620945071616617E-5,0]
[27750,null,"FINNINGLEY-MARHAM","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FINNINGLEY-MARHAM (02)",0,0]
[27751,null,"OUTHWAITE-MCEWAN","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","OUTHWAITE-MCEWAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27752,null,"SOMERS-HINKLER","NH0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","SOMERS-HINKLER (02)",4.4620945071616617E-5,0]
[27753,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","FE0","WATT-THE AVENUE (02)",4.4620945071616617E-5,0]
[27754,null,"STANLEY-THE GATE WAREHOUSE","ST0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","STANLEY-THE GATE WAREHOUSE (01)",0,0]
[27755,null,"LANTANA-IVANHOE","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","LANTANA-IVANHOE (02)",4.4620945071616617E-5,0]
[27756,null,"ALTONA-ORIEL","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",0,0]
[27757,null,"MATTHEWS-KEILOR","ES0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","MATTHEWS-KEILOR (03)",0,0]
[27758,null,"MATTHEWS-KEILOR","ES0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","MATTHEWS-KEILOR (03)",0,0]
[27759,null,"JUKES-LANIGAN","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","JUKES-LANIGAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27760,null,"JUKES-LANIGAN","CN0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","JUKES-LANIGAN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27761,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (02)",0,0]
[27762,null,"MOROBE-ALAMEIN","EPN-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","MOROBE-ALAMEIN (03)",0,0]
[27763,null,"ROSELAND-IVANHOE","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","ROSELAND-IVANHOE (03)",4.4620945071616617E-5,0]
[27764,null,"PATTERSON-DAVID","PTN-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","NICHOL-GOWER (01)",4.4620945071616617E-5,0]
[27765,null,"JACK-FORD","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","JACK-FORD (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27766,null,"PASCOE VALE-BENDOC","BD0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BD0","PASCOE VALE-BENDOC (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27767,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,0]
[27768,null,"HART-BOWES","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","HART-BOWES (02)",0,0]
[27769,null,"CHAPMAN-BELAIR","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","CHAPMAN-BELAIR (02)",4.4620945071616617E-5,0]
[27770,null,"YORK- EASTGATE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","YORK- EASTGATE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27771,null,"OLYMPIA-SUNSHINE","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","OLYMPIA-SUNSHINE (02)",0,0]
[27772,null,"OLYMPIA-SUNSHINE","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","OLYMPIA-SUNSHINE (02)",0,0]
[27773,null,"THORPE-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","THORPE-WOODS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27774,null,"THORPE-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","THORPE-WOODS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27775,null,"LANDY-LICHFIELD","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","LANDY-LICHFIELD (02)",0,0]
[27776,null,"MYDDLETON-GRACE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","MYDDLETON-GRACE (01)",4.4620945071616617E-5,0]
[27777,null,"BRADLEY-MASON","NT0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BRADLEY-MASON (03)",4.4620945071616617E-5,0]
[27778,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",{"$f":"IF(G27779=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J27779=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[27779,null,"YORK- EASTGATE","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","YORK- EASTGATE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27780,null,"CAMDON-NORTON","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CAMDON-NORTON (01)",4.4620945071616617E-5,0]
[27781,null,"CAMDON-NORTON","CS0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","CAMDON-NORTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27782,null,"ALMOND-CONIFER","FW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ALMOND-CONIFER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27783,null,"GRAHAM-GIBSON","BMS-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","BMS","GRAHAM-GIBSON (02)",4.4620945071616617E-5,0]
[27784,null,"DOYLE-NORTH","BY0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","DOYLE-NORTH (02)",4.4620945071616617E-5,0]
[27785,null,"WASHINGTON-DOY","BD0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","WASHINGTON-DOY (02)",0,0]
[27786,null,"STEVEDORE-STRAND","NT0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","STEVEDORE-STRAND (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27787,null,"NERISSA-SNELL","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","NERISSA-SNELL (02)",4.4620945071616617E-5,0]
[27788,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27789,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27790,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27791,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,0]
[27792,null,"ALTONA-ORIEL","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",0,0]
[27793,null,"TRETHOWAN-SMILEY","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","TRETHOWAN-SMILEY (03)",0,0]
[27794,null,"ALMOND-CONIFER","FW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","ALMOND-CONIFER (01)",4.4620945071616617E-5,0]
[27795,null,"DIAMOND-ROSEHILL","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27796,null,"MYDDLETON-GRACE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","MYDDLETON-GRACE (01)",4.4620945071616617E-5,0]
[27797,null,"CENTREWAY-WINGARA","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","CENTREWAY-WINGARA (03)",4.4620945071616617E-5,0]
[27798,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","WATT-THE AVENUE (02)",0,0]
[27799,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",0,0]
[27800,null,"BOND-ORIEL","EP0-034","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","BOND-ORIEL (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27801,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27802,null,"NEAL-DINAH","AW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","NEAL-DINAH (01)",0,0]
[27803,null,"NEAL-DINAH","AW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","NEAL-DINAH (01)",0,0]
[27804,null,"HILBERT-HARRINGTON","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILBERT-HARRINGTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27805,null,"STEPHEN-BERRY","FE0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","NA",0,0]
[27806,null,"KATHLEEN-WOOD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","KATHLEEN-WOOD (01)",4.4620945071616617E-5,0]
[27807,null,"EPSOM-ST LEONARDS","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","EPSOM-ST LEONARDS (02)",4.4620945071616617E-5,0]
[27808,null,"KING-BOWES","AW0-005","2025-02-02","2025-02-08","N","Y","N","N","Y","N","AW0","KING-BOWES (01)",0,0]
[27809,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (03)",0,0]
[27810,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","Y","N","BMS","ELLIOT-GRAHAM (03)",0,0]
[27811,null,"GORDON-WOOD","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","GORDON-WOOD (01)",0,0]
[27812,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","MELCOMBE-BANKSIA (02)",4.4620945071616617E-5,0]
[27813,null,"BIRDWOOD-REGENT","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","NA",4.4620945071616617E-5,0]
[27814,null,"FRANCIS-VINCENT","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","FRANCIS-VINCENT (01)",4.4620945071616617E-5,0]
[27815,null,"FRANCIS-VINCENT","PV0-022","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","FRANCIS-VINCENT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27816,null,"GRAHAM-GLEN ALLAN","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","GRAHAM-GLEN ALLAN (03)",0,0]
[27817,null,"WEST-KINGSLEY","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","WEST-KINGSLEY (01)",4.4620945071616617E-5,0]
[27818,null,"GOSFORD-NICHOLAS","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","GOSFORD-NICHOLAS (02)",4.4620945071616617E-5,0]
[27819,null,"GOSFORD-NICHOLAS","BD0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","GOSFORD-NICHOLAS (02)",0,0]
[27820,null,"VIEWBANK-BREES","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","VIEWBANK-BREES (01)",0,0]
[27821,null,"VIEWBANK-BREES","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","VIEWBANK-BREES (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27822,null,"VIEWBANK-BREES","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","VIEWBANK-BREES (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27823,null,"VIEWBANK-BREES","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","VIEWBANK-BREES (01)",0,0]
[27824,null,"FARRELL-RYDER","AW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","FARRELL-RYDER (03)",4.4620945071616617E-5,0]
[27825,null,"BELGROVE-OVANDO","PTN-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","BELGROVE-OVANDO (02)",4.4620945071616617E-5,0]
[27826,null,"GLADSTONE-CHAPMAN","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","GLADSTONE-CHAPMAN (01)",4.4620945071616617E-5,0]
[27827,null,"SALISBURY-JACK","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","SALISBURY-JACK (01)",4.4620945071616617E-5,0]
[27828,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27829,null,"SOUTH-DERBY","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","SOUTH-DERBY (03)",4.4620945071616617E-5,0]
[27830,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[27831,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[27832,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[27833,null,"NEAL-DINAH","AW0-008","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","NEAL-DINAH (01)",0,0]
[27834,null,"ESSEX-DOWNS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-DOWNS (02)",4.4620945071616617E-5,0]
[27835,null,"LAUREL-TYLER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","LAUREL-TYLER (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[27836,null,"LAUREL-TYLER","NH0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","LAUREL-TYLER (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[27837,null,"RILL-OLIVE","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","RILL-OLIVE (01)",4.4620945071616617E-5,0]
[27838,null,"BRAMCOTE-FORMAN","AW0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","BRAMCOTE-FORMAN (01)",0,0]
[27839,null,"HILTON-WIDFORD","PV0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","HILTON-WIDFORD (02)",4.4620945071616617E-5,0]
[27840,null,"LANDY-LICHFIELD","BMS-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BMS","LANDY-LICHFIELD (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27841,null,"LANDY-LICHFIELD","BMS-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BMS","LANDY-LICHFIELD (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27842,null,"LANDY-LICHFIELD","BMS-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BMS","LANDY-LICHFIELD (02)",{"$f":"IF(G27843=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J27843=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[27843,null,"BLIBURG-SUNSET","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","BLIBURG-SUNSET (02)",0,0]
[27844,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27845,null,"DIAMOND-ROSEHILL","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27846,null,"ATTERCLIFFE-DERBY","CS0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","ATTERCLIFFE-DERBY (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27847,null,"RILL-OLIVE","NH0-017","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","RILL-OLIVE (01)",4.4620945071616617E-5,0]
[27848,null,"LOCK-LAURENCE","AW0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","LOCK-LAURENCE (02)",0,0]
[27849,null,"DARLINGTON-RENNIE","CS0-009","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","DARLINGTON-RENNIE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27850,null,"WEST-KINGSLEY","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","WEST-KINGSLEY (01)",4.4620945071616617E-5,0]
[27851,null,"MERBEIN-SUSSEX","PV0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MERBEIN-SUSSEX (01)",4.4620945071616617E-5,0]
[27852,null,"HILLSIDE-ROBERTS","AW0-007","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","HILLSIDE-ROBERTS (02)",0,0]
[27853,null,"O'CONNOR-WHITBY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[27854,null,"O'CONNOR-WHITBY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[27855,null,"CONIFER-PRIMULA","FW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CONIFER-PRIMULA (03)",4.4620945071616617E-5,0]
[27856,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (02)",4.4620945071616617E-5,0]
[27857,null,"SUNBURY RD-P237","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","SUNBURY RD-P237 (02)",0,0]
[27858,null,"SUNBURY RD-P237","SBY-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","SUNBURY RD-P237 (02)",0,0]
[27859,null,"BOOMERANG-AIRFORCE","TH0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","BOOMERANG-AIRFORCE (01)",0,0]
[27860,null,"VALLEY-AUGUSTINE","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","VALLEY-AUGUSTINE (02)",4.4620945071616617E-5,0]
[27861,null,"MOORE 9-MATTHEWS","AW0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","MOORE 9-MATTHEWS (01)",0,0]
[27862,null,"GLADSTONE-CHAPMAN","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","GLADSTONE-CHAPMAN (01)",4.4620945071616617E-5,0]
[27863,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27864,null,"MARGARET-MURPHY","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","MARGARET-MURPHY (02)",0,0]
[27865,null,"ROSELAND-IVANHOE","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","ROSELAND-IVANHOE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27866,null,"ROSELAND-IVANHOE","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","ROSELAND-IVANHOE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27867,null,"COLLINGWOOD-DOUGLAS","NT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","COLLINGWOOD-DOUGLAS (03)",4.4620945071616617E-5,0]
[27868,null,"MERBEIN-SUSSEX","PV0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","PV0","MERBEIN-SUSSEX (01)",0,0]
[27869,null,"DIAMOND-ROSEHILL","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27870,null,"COHEN-GROVES","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","COHEN-GROVES (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27871,null,"HAMPDEN-CROTHERS","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",0,0]
[27872,null,"WARRAGUL-LISMORE","BD0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","WARRAGUL-LISMORE (02)",0,0]
[27873,null,"KERFERD-RALEIGH","ES0-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","KERFERD-RALEIGH (02)",0,0]
[27874,null,"CORNISH-LIGAR","SBY-012","2025-02-02","2025-02-08","N","N","N","Y","N","N","SBY","CORNISH-LIGAR (01)",0,9.4304036212749905E-5]
[27875,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27876,null,"JOFFRE-KITCHENER","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","JOFFRE-KITCHENER (03)",4.4620945071616617E-5,0]
[27877,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",0,0]
[27878,null,"BRADLEY-MASON","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","BRADLEY-MASON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27879,null,"MACK-PICKETT","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","MACK-PICKETT (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27880,null,"MIRANDA-MAIS","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","MIRANDA-MAIS (01)",4.4620945071616617E-5,0]
[27881,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27882,null,"HOOD-BOWES","AW0-001","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","HOOD-BOWES (02)",0,0]
[27883,null,"ASHLEY-CENTRAL WEST NO.1","TH0-012","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TH0","ASHLEY-CENTRAL WEST NO.1 (05)",4.4620945071616617E-5,9.4304036212749905E-5]
[27884,null,"KEILOR-MC CULLOCH","ES0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","KEILOR-MC CULLOCH (03)",4.4620945071616617E-5,0]
[27885,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","MELCOMBE-BANKSIA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27886,null,"LIBERTY-PERKINS","EP0-034","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","LIBERTY-PERKINS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27887,null,"KERFERD-RALEIGH","ES0-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (02)",0,0]
[27888,null,"KERFERD-RALEIGH","ES0-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (02)",0,0]
[27889,null,"KERFERD-RALEIGH","ES0-025","2025-02-02","2025-02-08","N","Y","N","N","N","N","ES0","OSHANNASSY-KERFERD (02)",0,0]
[27890,null,"BLIBURG-SUNSET","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","BLIBURG-SUNSET (02)",0,0]
[27891,null,"ARTHUR-FAWKNER","ES0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","ARTHUR-FAWKNER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27892,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27893,null,"HUGHES-FRANCIS","YVE-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","HUGHES-FRANCIS (01)",4.4620945071616617E-5,0]
[27894,null,"WEST-KINGSLEY","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","WEST-KINGSLEY (01)",4.4620945071616617E-5,0]
[27895,null,"DEAKIN-SPENCER","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DEAKIN-SPENCER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27896,null,"DEAKIN-SPENCER","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DEAKIN-SPENCER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27897,null,"CLINGIN-CREVELLI","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CLINGIN-CREVELLI (03)",4.4620945071616617E-5,0]
[27898,null,"KATHLEEN-WOOD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","KATHLEEN-WOOD (02)",4.4620945071616617E-5,0]
[27899,null,"KATHLEEN-WOOD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","KATHLEEN-WOOD (02)",4.4620945071616617E-5,0]
[27900,null,"HEATHER-DINAH","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HEATHER-DINAH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27901,null,"BOND-LIBERTY","EP0-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","NA",0,0]
[27902,null,"ORIEL-TOBRUK","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","ORIEL-TOBRUK (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27903,null,"DEAKIN-SPENCER","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DEAKIN-SPENCER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27904,null,"BRUCE-REYNARD","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","BRUCE-REYNARD (02)",4.4620945071616617E-5,0]
[27905,null,"BEAUCHAMP-HIGH","PTN-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","BEAUCHAMP-HIGH (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27906,null,"DIXON-DERBY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DIXON-DERBY (01)",{"$f":"IF(G27907=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J27907=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[27907,null,"MONTGOMERY-MT ALEXANDER","NS0-015","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","MONTGOMERY-MT ALEXANDER (02)",0,0]
[27908,null,"MITCHELLS-SIMPSON 1","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","MITCHELLS-SIMPSON 1 (04)",0,0]
[27909,null,"MITCHELLS-SIMPSON 1","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","MITCHELLS-SIMPSON 1 (04)",0,0]
[27910,null,null,null,"2025-02-02","2025-02-08","Y","N","N","N","N","N",null,"BENDIGO-ALPINE (02)",4.4620945071616617E-5,0]
[27911,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","CLARENDON-WHITTAKER (03)",4.4620945071616617E-5,0]
[27912,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","CLARENDON-WHITTAKER (03)",4.4620945071616617E-5,0]
[27913,null,"MOROBE-ALAMEIN","EPN-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","MOROBE-ALAMEIN (03)",0,0]
[27914,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[27915,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[27916,null,"CARROL-WHITELAW","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","CARROL-WHITELAW (00)",4.4620945071616617E-5,9.4304036212749905E-5]
[27917,null,null,null,"2025-02-02","2025-02-08","N","Y","N","N","N","N",null,"SUNBURY RD-P68A (03)",0,0]
[27918,null,"MITCHELLS-SIMPSON 1","SBY-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","MITCHELLS-SIMPSON 1 (04)",0,0]
[27919,null,"RAVENSCOURT-FULHAM","FF0-083","2025-02-02","2025-02-08","N","Y","N","N","N","N","FF0","RAVENSCOURT-FULHAM (02)",0,0]
[27920,null,"JONES-OLD GEELONG No.2","TH0-021","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","JONES-OLD GEELONG No.2 (03)",0,0]
[27921,null,"SMILEY-GERBERT","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","SMILEY-GERBERT (02)",0,0]
[27922,null,"JOFFRE-KITCHENER","BD0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BD0","JOFFRE-KITCHENER (03)",4.4620945071616617E-5,0]
[27923,null,"ROSAMOND-RIVER","BY0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","ROSAMOND-RIVER (01)",4.4620945071616617E-5,0]
[27924,null,"ROSAMOND-RIVER","BY0-013","2025-02-02","2025-02-08","N","Y","N","N","N","N","BY0","ROSAMOND-RIVER (01)",0,0]
[27925,null,"CASTLETON 21-HAVILAH","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","CASTLETON 21-HAVILAH (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27926,null,"CASTLETON 21-HAVILAH","NH0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","CASTLETON 21-HAVILAH (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27927,null,"HILLSIDE-ROBERTS","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILLSIDE-ROBERTS (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27928,null,"TONKIN-MASHOOBRA","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","TONKIN-MASHOOBRA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27929,null,"DELAWARE-MENDIP","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","DELAWARE-MENDIP (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27930,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,0]
[27931,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27932,null,"JUKES-LANIGAN","CN0-010","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","JUKES-LANIGAN (04)",4.4620945071616617E-5,0]
[27933,null,"FETTLING-COOPER","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","FETTLING-COOPER (02)",4.4620945071616617E-5,0]
[27934,null,"FETTLING-COOPER","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","FETTLING-COOPER (02)",4.4620945071616617E-5,0]
[27935,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27936,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27937,null,"CHARLES-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","CHARLES-EPSOM (01)",4.4620945071616617E-5,0]
[27938,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ESSEX-LANDELLS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27939,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","WATT-THE AVENUE (03)",0,0]
[27940,null,"ATTERCLIFFE-DERBY","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",4.4620945071616617E-5,0]
[27941,null,"ARTHUR-FAWKNER","ES0-023","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","ARTHUR-FAWKNER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27942,null,"MOUNT-BELL","CS0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MOUNT-BELL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27943,null,"DELAWARE-MENDIP","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DELAWARE-MENDIP (01)",4.4620945071616617E-5,0]
[27944,null,"CHALEYER-ASHTON","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","CHALEYER-ASHTON (03)",4.4620945071616617E-5,0]
[27945,null,"DONCASTER-MYROSS","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","DONCASTER-MYROSS (03)",4.4620945071616617E-5,0]
[27946,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27947,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27948,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","MULBERRY-GONA (03)",4.4620945071616617E-5,0]
[27949,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","MULBERRY-GONA (03)",4.4620945071616617E-5,0]
[27950,null,"DELAWARE-MENDIP","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","DELAWARE-MENDIP (01)",4.4620945071616617E-5,0]
[27951,null,"ALBERT-MT ALEXANDER","NS0-018","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALBERT-MT ALEXANDER (01)",0,0]
[27952,null,"ILLAWARRA-PASCOEVALE","PV0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","ILLAWARRA-PASCOEVALE (01)",4.4620945071616617E-5,0]
[27953,null,"BIRCH-BROADMEADOWS","AW0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","BIRCH-BROADMEADOWS (02)",0,0]
[27954,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","FE0","WATT-THE AVENUE (02)",4.4620945071616617E-5,0]
[27955,null,"ALTONA-ORIEL","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",0,0]
[27956,null,"HILBERT-HARRINGTON","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILBERT-HARRINGTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27957,null,"DOYLE-RIDLEY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","NA",4.4620945071616617E-5,9.4304036212749905E-5]
[27958,null,"MOROBE-ALAMEIN","EPN-034","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","MOROBE-ALAMEIN (03)",0,0]
[27959,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",0,0]
[27960,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",0,0]
[27961,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",0,0]
[27962,null,"ELLIOT-GRAHAM","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","ELLIOT-GRAHAM (02)",0,0]
[27963,null,"ARDEN-LOWER PLENTY","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","ARDEN-LOWER PLENTY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27964,null,"ALTONA-ORIEL","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (02)",0,0]
[27965,null,"BIRCH-BROADMEADOWS","AW0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","BIRCH-BROADMEADOWS (02)",0,0]
[27966,null,"HOLDEN-MILITARY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","HOLDEN-MILITARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27967,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,0]
[27968,null,"MOUSHALL-NOLAN","ES0-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","MOUSHALL-NOLAN (02)",4.4620945071616617E-5,0]
[27969,null,"DIXON-DERBY","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","NA",4.4620945071616617E-5,0]
[27970,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","MARGTMARY-MURRAY (03)",{"$f":"IF(G27971=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J27971=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":9.4304036212749905E-5}]
[27971,null,"MARGTMARY-MURRAY","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MARGTMARY-MURRAY (03)",4.4620945071616617E-5,0]
[27972,null,"KENNEDY-WILLIAM","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","KENNEDY-WILLIAM (01)",4.4620945071616617E-5,0]
[27973,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27974,null,"BELGROVE-OVANDO","PTN-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","BELGROVE-OVANDO (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27975,null,"HOLDEN-MILITARY","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","HOLDEN-MILITARY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27976,null,"TONKIN-SUSSEX","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","TONKIN-SUSSEX (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[27977,null,"PALMER-HEDLEY","CN0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","PALMER-HEDLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27978,null,"FLINDERS-WENTWORTH","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","Y","N","SBY","FLINDERS-WENTWORTH (01)",0,0]
[27979,null,"BURKE-FLINDERS","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (03)",0,0]
[27980,null,"BURKE-FLINDERS","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (03)",0,0]
[27981,null,"BURKE-FLINDERS","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (03)",0,0]
[27982,null,"BURKE-FLINDERS","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (03)",0,0]
[27983,null,"WATERDALE-LLOYD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","WATERDALE-LLOYD (03)",4.4620945071616617E-5,0]
[27984,null,"WATERDALE-LLOYD","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","WATERDALE-LLOYD (03)",4.4620945071616617E-5,0]
[27985,null,"MOUNT-BELL","CS0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","NA",4.4620945071616617E-5,0]
[27986,null,"BURKE-FLINDERS","SBY-032","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","BURKE-FLINDERS (03)",0,0]
[27987,null,"BROADHURST-MCFADZEAN","TT0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","BROADHURST-MCFADZEAN (02)",4.4620945071616617E-5,0]
[27988,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,0]
[27989,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27990,null,"DANIN-AUSTIN","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","DANIN-AUSTIN (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27991,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27992,null,"PALMER-HEDLEY","CN0-004","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","PALMER-HEDLEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27993,null,"GRENHILDA-DOUGLAS","NH0-020","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","GRENHILDA-DOUGLAS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27994,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27995,null,"ROYAL-MCMAHON","TT0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","ROYAL-MCMAHON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[27996,null,"ESSEX-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","ESSEX-LANDELLS (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[27997,null,"ATTERCLIFFE-DERBY","CS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","ATTERCLIFFE-DERBY (03)",4.4620945071616617E-5,0]
[27998,null,"MCIVOR-KIEWA","BD0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","MCIVOR-KIEWA (01)",0,0]
[27999,null,"BLIBURG-SUNSET","BMS-023","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","BLIBURG-SUNSET (01)",0,0]
[28000,null,"RALEIGH-CHIFLEY","YVE-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","YVE","RALEIGH-CHIFLEY (01)",0,0]
[28001,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","CLARENDON-WHITTAKER (03)",4.4620945071616617E-5,0]
[28002,null,"TREADWELL-DUDLEY","ES0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","TREADWELL-DUDLEY (03)",4.4620945071616617E-5,0]
[28003,null,"CHARLES-BENAMBRA","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CHARLES-BENAMBRA (02)",4.4620945071616617E-5,0]
[28004,null,"CHARLES-BENAMBRA","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CHARLES-BENAMBRA (02)",4.4620945071616617E-5,0]
[28005,null,"MELCOMBE-BANKSIA","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","MELCOMBE-BANKSIA (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28006,null,"GREVILLIA-ALBERT","PV0-013","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","GREVILLIA-ALBERT (01)",4.4620945071616617E-5,0]
[28007,null,"NORTHUMBERLAND-FAWKNER","PV0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","PV0","NORTHUMBERLAND-FAWKNER (03)",0,0]
[28008,null,"EGLINTON-ARGYLE","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","EGLINTON-ARGYLE (04)",4.4620945071616617E-5,0]
[28009,null,"DELAWARE-MENDIP","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","DELAWARE-MENDIP (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[28010,null,"MELTON HWY-P2","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","MELTON HWY-P2 (03)",4.4620945071616617E-5,0]
[28011,null,"MELTON HWY-P2","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","MELTON HWY-P2 (03)",4.4620945071616617E-5,0]
[28012,null,"MELTON HWY-P2","SHM-021","2025-02-02","2025-02-08","Y","N","N","N","N","N","SHM","MELTON HWY-P2 (03)",4.4620945071616617E-5,0]
[28013,null,"CAMDON-NORTON","CS0-002","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","CAMDON-NORTON (01)",4.4620945071616617E-5,0]
[28014,null,"JACANA-LAHINCH","BMS-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","BMS","JACANA-LAHINCH (01)",0,0]
[28015,null,"ARGYLE-DAREBIN","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",4.4620945071616617E-5,0]
[28016,null,"ARGYLE-DAREBIN","TT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ARGYLE-DAREBIN (01)",4.4620945071616617E-5,0]
[28017,null,"STEANE-ALBERT","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STEANE-ALBERT (03)",4.4620945071616617E-5,0]
[28018,null,"STEANE-ALBERT","NH0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","STEANE-ALBERT (03)",4.4620945071616617E-5,0]
[28019,null,"ALTONA-ORIEL","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",0,0]
[28020,null,"ALTONA-ORIEL","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","ALTONA-ORIEL (01)",0,0]
[28021,null,"CHARLES-EPSOM","ES0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","NA",4.4620945071616617E-5,0]
[28022,null,"VALLEY-AUGUSTINE","PV0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","VALLEY-AUGUSTINE (02)",4.4620945071616617E-5,0]
[28023,null,"BANKSIA-LIBERTY","EP0-034","2025-02-02","2025-02-08","Y","N","N","N","N","N","EP0","BANKSIA-LIBERTY (01)",4.4620945071616617E-5,0]
[28024,null,"O'CONNOR-WHITBY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[28025,null,"O'CONNOR-WHITBY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[28026,null,"O'CONNOR-WHITBY","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","OCONNOR-MACFADZEAN (04)",4.4620945071616617E-5,9.4304036212749905E-5]
[28027,null,"O'CONNOR-WHITBY","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","OCONNOR-MACFADZEAN (04)",4.4620945071616617E-5,0]
[28028,null,"WEST-KINGSLEY","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","WEST-KINGSLEY (01)",4.4620945071616617E-5,0]
[28029,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","FE0","WATT-THE AVENUE (02)",0,0]
[28030,null,"WATT-THE AVENUE","FE0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","FE0","WATT-THE AVENUE (02)",4.4620945071616617E-5,0]
[28031,null,"MOUNT-BELL","CS0-003","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CS0","MOUNT-BELL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28032,null,"CHALLIS-JUBILLEE","NT0-017","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NT0","CHALLIS-JUBILLEE (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[28033,null,"CLIFTON-JEAN","ES0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","CLIFTON-JEAN (01)",4.4620945071616617E-5,0]
[28034,null,"EDWIN-ST HELLIER","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","EDWIN-ST HELLIER (02)",{"$f":"IF(G28035=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":0},{"$f":"IF(J28035=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[28035,null,"CHARTERIS-BURKE","HB0-024","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","CHARTERIS-BURKE (01)",4.4620945071616617E-5,0]
[28036,null,"SALMON-NAPIER","NS0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","SALMON-NAPIER (02)",4.4620945071616617E-5,0]
[28037,null,"PEARCEDALE 59-COLERAINE","BD0-010","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","PEARCEDALE 59-COLERAINE (04)",0,0]
[28038,null,"STEELE-STUART","FT0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","FT0","STEELE-STUART (01)",4.4620945071616617E-5,0]
[28039,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28040,null,"CLARENDON-WHITTAKER","BY0-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","CLARENDON-WHITTAKER (03)",4.4620945071616617E-5,0]
[28041,null,"MARGARET-WINIFRED","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MARGARET-WINIFRED (04)",4.4620945071616617E-5,0]
[28042,null,"MARGARET-WINIFRED","PV0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","PV0","MARGARET-WINIFRED (04)",0,0]
[28043,null,"MARGARET-WINIFRED","PV0-022","2025-02-02","2025-02-08","Y","N","N","N","N","N","PV0","MARGARET-WINIFRED (04)",4.4620945071616617E-5,0]
[28044,null,"MARGARET-WINIFRED","PV0-022","2025-02-02","2025-02-08","N","Y","N","N","N","N","PV0","MARGARET-WINIFRED (04)",0,0]
[28045,null,"ALMA-PALMERSTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28046,null,"ALMA-PALMERSTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ALMA-PALMERSTON (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28047,null,"DOYLE-NORTH","BY0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","DOYLE-NORTH (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28048,null,"RAGLAN-RESERVE","EP0-028","2025-02-02","2025-02-08","N","Y","N","N","N","N","EP0","RAGLAN-RESERVE (01)",0,0]
[28049,null,null,null,"2025-02-02","2025-02-08","Y","N","N","N","N","N",null,"CLIFTON-JEAN (01)",4.4620945071616617E-5,0]
[28050,null,"ARTHUR-ELIZABETH","CN0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ARTHUR-ELIZABETH (02)",4.4620945071616617E-5,0]
[28051,null,"GILBANK-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","GILBANK-GILBERT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28052,null,"GORDON-WOOD","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","GORDON-WOOD (01)",0,0]
[28053,null,"ROGERSON-THOMPSON","BY0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","ROGERSON-THOMPSON (02)",4.4620945071616617E-5,0]
[28054,null,"MCNAMARA-RUTHVEN","NH0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","MCNAMARA-RUTHVEN (02)",4.4620945071616617E-5,0]
[28055,null,"SEXTON-PARER","AW0-006","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","SEXTON-PARER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28056,null,"DEAKIN-SPENCER","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DEAKIN-SPENCER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[28057,null,"HAMPDEN-CROTHERS","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","HAMPDEN-CROTHERS (01)",0,0]
[28058,null,"GILBANK-GILBERT","CN0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","GILBANK-GILBERT (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28059,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28060,null,"CONIFER-PRIMULA","FW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CONIFER-PRIMULA (03)",4.4620945071616617E-5,0]
[28061,null,"JULIET-BENT","NS0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","NS0","JULIET-BENT (01)",4.4620945071616617E-5,0]
[28062,null,"ESSEX-DOWNS","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","ESSEX-DOWNS (02)",4.4620945071616617E-5,0]
[28063,null,"McEWEN-CURTIN","SBY-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","SBY","McEWEN-CURTIN (03)",0,0]
[28064,null,"ALEXANDRA-LANDELLS","CN0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","NA",4.4620945071616617E-5,9.4304036212749905E-5]
[28065,null,"MCGREGOR-PERRY","FF0-083","2025-02-02","2025-02-08","Y","N","N","N","N","N","FF0","MCGREGOR-PERRY (01)",4.4620945071616617E-5,0]
[28066,null,"CONIFER-PRIMULA","FW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CONIFER-PRIMULA (03)",4.4620945071616617E-5,0]
[28067,null,"COLLINS-WATERDALE","EPN-033","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","EPN","OUTHWAITE-MCEWAN (04)",4.4620945071616617E-5,0]
[28068,null,"CAPE-YARRA","HB0-031","2025-02-02","2025-02-08","Y","N","N","N","N","N","HB0","CAPE-YARRA (01)",4.4620945071616617E-5,0]
[28069,null,"OUTHWAITE-ORIEL","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","NA",4.4620945071616617E-5,0]
[28070,null,"BRAIDHILL-WINDSOR","NH0-002","2025-02-02","2025-02-08","Y","N","N","Y","N","N","NH0","BRAIDHILL-WINDSOR (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28071,null,"PATTERSON-DAVID","PTN-021","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","PTN","NICHOL-GOWER (01)",4.4620945071616617E-5,0]
[28072,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28073,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28074,null,"BLENHEIM-WOODS","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","BLENHEIM-WOODS (03)",4.4620945071616617E-5,0]
[28075,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28076,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28077,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28078,null,"FOSTERS-ELIZA","TMA-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TMA","FOSTERS-ELIZA (04)",4.4620945071616617E-5,0]
[28079,null,"ORIEL-STANLEY","EP0-034","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","ORIEL-STANLEY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28080,null,"MAJOR-HUME","CN0-004","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","MAJOR-HUME (04)",4.4620945071616617E-5,0]
[28081,null,"WATERDALE-GRIFFITHS","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","WATERDALE-GRIFFITHS (02)",0,0]
[28082,null,"WATERDALE-GRIFFITHS","EPN-033","2025-02-02","2025-02-08","N","Y","N","N","N","N","EPN","WATERDALE-GRIFFITHS (02)",0,0]
[28083,null,"WARATAH-CAROL","AW0-009","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","SYCAMORE-BROADMEADOWS (01)",4.4620945071616617E-5,0]
[28084,null,"GRAHAM-WOODLANDS","CS0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CS0","NA",4.4620945071616617E-5,0]
[28085,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,0]
[28086,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,0]
[28087,null,"GREENSBOROUGH-DRYSDALE","NH0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","NH0","GREENSBOROUGH-DRYSDALE (02)",4.4620945071616617E-5,0]
[28088,null,"NEWMAN-HOTHAM","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NA",4.4620945071616617E-5,9.4304036212749905E-5]
[28089,null,"PEARL-WHEATSHEAF","PV0-013","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PV0","PEARL-WHEATSHEAF (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28090,null,"GOULBURN-SHAND","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","GOULBURN-SHAND (03)",4.4620945071616617E-5,0]
[28091,null,"GOULBURN-SHAND","CN0-011","2025-02-02","2025-02-08","Y","N","N","Y","N","N","CN0","GOULBURN-SHAND (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[28092,null,"HARBURY-EDWARDES","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HARBURY-EDWARDES (02)",4.4620945071616617E-5,0]
[28093,null,"HARBURY-EDWARDES","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HARBURY-EDWARDES (02)",4.4620945071616617E-5,0]
[28094,null,"HARBURY-EDWARDES","CN0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HARBURY-EDWARDES (02)",4.4620945071616617E-5,0]
[28095,null,"CHARLES-BENAMBRA","CN0-008","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","CHARLES-BENAMBRA (02)",4.4620945071616617E-5,0]
[28096,null,"ST VIGEONS-BORRIE","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","ST VIGEONS-BORRIE (02)",4.4620945071616617E-5,0]
[28097,null,"CENTREWAY-WINGARA","AW0-007","2025-02-02","2025-02-08","Y","N","N","N","N","N","AW0","CENTREWAY-WINGARA (03)",4.4620945071616617E-5,0]
[28098,null,"BLOOMFIELD-ROSAMOND","YVE-015","2025-02-02","2025-02-08","Y","N","N","N","N","N","YVE","BLOOMFIELD-ROSAMOND (01)",{"$f":"IF(G28099=\"Y\",(1/COUNTIF($G$2:$G$28155,\"Y\")),0)","v":4.4620945071616617E-5},{"$f":"IF(J28099=\"Y\",(1/COUNTIF($J$2:$J$28155,\"Y\")),0)","v":0}]
[28099,null,"HEATHCOTE-KENT","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","HEATHCOTE-KENT (01)",4.4620945071616617E-5,0]
[28100,null,"DOVER-WATERLOO","NT0-004","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","DOVER-WATERLOO (02)",4.4620945071616617E-5,0]
[28101,null,"FORRESTER-HEDDERWICK","ES0-015","2025-02-02","2025-02-08","Y","Y","Y","N","N","N","ES0","FORRESTER-HEDDERWICK (02)",4.4620945071616617E-5,0]
[28102,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28103,null,"PROSPECT-BUCKLEY","ES0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","PROSPECT-BUCKLEY (04)",4.4620945071616617E-5,0]
[28104,null,"PROSPECT-BUCKLEY","ES0-012","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","PROSPECT-BUCKLEY (04)",4.4620945071616617E-5,0]
[28105,null,"NEWMAN-HOTHAM","AW0-007","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","NA",4.4620945071616617E-5,9.4304036212749905E-5]
[28106,null,"GOSFORD-NICHOLAS","BD0-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","NA",0,0]
[28107,null,"PLENTY-RESERVOIR COLLEGE","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","PLENTY-RESERVOIR COLLEGE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28108,null,"PLENTY-RESERVOIR COLLEGE","TT0-010","2025-02-02","2025-02-08","Y","N","N","Y","N","N","TT0","PLENTY-RESERVOIR COLLEGE (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28109,null,null,null,"2025-02-02","2025-02-08","N","Y","N","N","N","N",null,"NEAL-DINAH (01)",0,0]
[28110,null,"MONASH-BONAR","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MONASH-BONAR (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28111,null,"EDEN-BELL","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","EDEN-BELL (02)",4.4620945071616617E-5,0]
[28112,null,"EDEN-BELL","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","EDEN-BELL (02)",4.4620945071616617E-5,0]
[28113,null,"DEAKIN-SPENCER","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DEAKIN-SPENCER (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[28114,null,"CONIFER-PRIMULA","FW0-006","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CONIFER-PRIMULA (03)",4.4620945071616617E-5,0]
[28115,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28116,null,"NEYLON-ROBERTS","FW0-017","2025-02-02","2025-02-08","N","Y","N","N","N","N","FW0","NA",0,0]
[28117,null,"HENDERSON-MELROSE","AW0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","HENDERSON-MELROSE (01)",0,0]
[28118,null,"CHEDDAR-JINGHI","TT0-011","2025-02-02","2025-02-08","Y","N","N","N","N","N","TT0","CHEDDAR-JINGHI (03)",4.4620945071616617E-5,0]
[28119,null,"ORIEL-STANLEY","EP0-034","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","ORIEL-STANLEY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28120,null,"AUSTRAL-OAKOVER","PTN-015","2025-02-02","2025-02-08","Y","N","N","Y","N","N","PTN","AUSTRAL-OAKOVER (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28121,null,"ASHLEY-NAPOLEON","TH0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","TH0","ASHLEY-NAPOLEON (01)",0,0]
[28122,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,0]
[28123,null,"CALA-HAMPTON","FW0-016","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","CALA-HAMPTON (01)",4.4620945071616617E-5,0]
[28124,null,"MALMSBURY-WOODBURN","BD0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","BD0","MALMSBURY-WOODBURN (02)",0,0]
[28125,null,"LLOYD-MONASH","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","LLOYD-MONASH (01)",4.4620945071616617E-5,0]
[28126,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EPN","MULBERRY-GONA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28127,null,"MULBERRY-GONA","EPN-033","2025-02-02","2025-02-08","Y","N","N","N","N","N","EPN","MULBERRY-GONA (01)",4.4620945071616617E-5,0]
[28128,null,"ALBERT-DUNDAS","EP0-033","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","ALBERT-DUNDAS (03)",4.4620945071616617E-5,9.4304036212749905E-5]
[28129,null,"BRUNEL-TRUMAN","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","BRUNEL-TRUMAN (01)",4.4620945071616617E-5,0]
[28130,null,"BRUNEL-TRUMAN","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","BRUNEL-TRUMAN (01)",4.4620945071616617E-5,0]
[28131,null,"BRUNEL-TRUMAN","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","BRUNEL-TRUMAN (01)",4.4620945071616617E-5,0]
[28132,null,"BRUNEL-TRUMAN","FW0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","FW0","BRUNEL-TRUMAN (01)",4.4620945071616617E-5,0]
[28133,null,"GORDON-WOOD","PTN-011","2025-02-02","2025-02-08","N","Y","N","N","N","N","PTN","GORDON-WOOD (01)",0,0]
[28134,null,"DIAMOND-ROSEHILL","ES0-021","2025-02-02","2025-02-08","Y","N","N","Y","N","N","ES0","DIAMOND-ROSEHILL (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28135,null,"CHRISTINA-BARBARA","BY0-014","2025-02-02","2025-02-08","Y","N","N","Y","N","N","BY0","CHRISTINA-BARBARA (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28136,null,"HILBERT-HARRINGTON","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILBERT-HARRINGTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28137,null,"HILBERT-HARRINGTON","AW0-008","2025-02-02","2025-02-08","Y","N","N","Y","N","N","AW0","HILBERT-HARRINGTON (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28138,null,null,null,"2025-02-02","2025-02-08","Y","N","N","Y","N","N",null,"BRASSEY-PYALONG (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28139,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28140,null,"ANGLISS-ADENEY","FW0-005","2025-02-02","2025-02-08","Y","N","N","Y","N","N","FW0","ANGLISS-ADENEY (01)",4.4620945071616617E-5,9.4304036212749905E-5]
[28141,null,"WOODS-MADDOX No.2","NT0-003","2025-02-02","2025-02-08","Y","N","N","N","N","N","NT0","WOODS-MADDOX No.2 (01)",4.4620945071616617E-5,0]
[28142,null,"BENDIGO-ALPINE","CN0-005","2025-02-02","2025-02-08","Y","N","N","N","N","N","CN0","BENDIGO-ALPINE (03)",4.4620945071616617E-5,0]
[28143,null,"EGLINTON-ARGYLE","ES0-023","2025-02-02","2025-02-08","Y","N","N","N","N","N","ES0","EGLINTON-ARGYLE (03)",4.4620945071616617E-5,0]
[28144,null,"WILKINSON-LIBERTY","EP0-036","2025-02-02","2025-02-08","Y","N","N","Y","N","N","EP0","WILKINSON-LIBERTY (02)",4.4620945071616617E-5,9.4304036212749905E-5]
[28145,null,null,null,"2025-02-02","2025-02-08","Y","N","N","N","N","N",null,"SOUDAN-HIGH (01)",4.4620945071616617E-5,0]
[28146,null,"WILLOWTREE-PERSICA","AW0-006","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","WILLOWTREE-PERSICA (01)",0,0]
[28147,null,"FREIGHT-CUSTOM","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (02)",0,0]
[28148,null,"ARBOR-MACEY","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","ARBOR-MACEY (01)",4.4620945071616617E-5,0]
[28149,null,"ARBOR-MACEY","BY0-014","2025-02-02","2025-02-08","Y","N","N","N","N","N","BY0","ARBOR-MACEY (01)",4.4620945071616617E-5,0]
[28150,null,"ALEXANDRA-WALKER","NS0-009","2025-02-02","2025-02-08","N","Y","N","N","N","N","NS0","ALEXANDRA-WALKER (04)",0,0]
[28151,null,"MOORE 9-MATTHEWS","AW0-012","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","MOORE 9-MATTHEWS (02)",0,0]
[28152,null,"FREIGHT-CUSTOM","AW0-014","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","FREIGHT-CUSTOM (02)",0,0]
[28153,null,"INTERNATIONAL-T'PARK","AW0-004","2025-02-02","2025-02-08","N","Y","N","N","N","N","AW0","INTERNATIONAL-T'PARK (00)",0,0]
[28154,null,"SOMERTON 17-HUME","ST0-024","2025-02-02","2025-02-08","N","Y","N","N","N","N","ST0","SOMERTON 17-HUME (02)",0,0]

{"sheet":"Low V contribution by DSS","index":6,"n_rows":1120,"n_cols":4,"rows_kept":1120,"cut":false,"hidden":false,"merged":[]}
[]
["Min.One.Percentage","Y",null,"Augmentation required"]
[]
["Row Labels","Count of NMIs","Sum of Min.One.Percentage (%)"]
["CHALLIS-JUBILLEE",166,7.4070768818883716E-3]
["BENDIGO-ALPINE",153,6.8270045959573523E-3]
["BLENHEIM-WOODS",141,6.2915532550979498E-3]
["O'DOWD-HOWARD",136,6.0684485297398654E-3]
["SOUTH-DERBY",128,5.7114809691669304E-3]
["MELCOMBE-BANKSIA",119,5.3098924635223786E-3]
["ROYAL-MCMAHON",118,5.2652715184507617E-3]
["WILKINSON-LIBERTY",114,5.0867877381642942E-3]
["RILL-OLIVE",110,4.9083039578778267E-3]
["ANGLISS-ADENEY",110,4.9083039578778267E-3]
["DELAWARE-MENDIP",107,4.7744411226629761E-3]
["MOUSHALL-HOFFMANS",105,4.6851992325197423E-3]
["DANIN-AUSTIN",105,4.6851992325197423E-3]
["HILBERT-HARRINGTON",102,4.5513363973048917E-3]
["STRATHALLAN-WILSON",101,4.5067154522332748E-3]
["AUSTRAL-OAKOVER",99,4.4174735620900411E-3]
["CUMBERLAND-KENT",99,4.4174735620900411E-3]
["SYMONS-GILBERT",96,4.2836107268751904E-3]
["MULBERRY-GONA",95,4.2389897818035736E-3]
["ALEXANDRA-LANDELLS",95,4.2389897818035736E-3]
["BEATRICE-JENSEN",95,4.2389897818035736E-3]
["WELLINGTON-VICTORIA",94,4.1943688367319567E-3]
["NEWMAN-HOTHAM",92,4.1051269465887229E-3]
["YALLAMBIE-LOWER PLENTY",91,4.0605060015171061E-3]
["HOOPER-DUNVEGAN",90,4.0158850564454892E-3]
["BOLDREWOOD-McMAHON",90,4.0158850564454892E-3]
["MOUSHALL-NOLAN",88,3.9266431663022554E-3]
["MAYFIELD-MUNRO",85,3.7927803310874061E-3]
["MOUNT-BELL",85,3.7927803310874061E-3]
["DEAKIN-SPENCER",85,3.7927803310874061E-3]
["ANDERSON-BOLINGBROKE",85,3.7927803310874061E-3]
["BRADLEY-MASON",85,3.7927803310874061E-3]
["STEELE-STUART",84,3.7481593860157897E-3]
["ATTERCLIFFE-DERBY",82,3.6589174958725568E-3]
["CHARLES-EPSOM",82,3.6589174958725568E-3]
["BERRIMA-ROSANNA",81,3.6142965508009404E-3]
["ETZEL-CLYDESDALE",79,3.5250546606577075E-3]
["BREARLEY-ROSE",79,3.5250546606577075E-3]
["CARROL-WHITELAW",78,3.480433715586091E-3]
["DAISY-BUCKLEY",76,3.3911918254428582E-3]
["BIRDWOOD-REGENT",76,3.3911918254428582E-3]
["WATT-THE AVENUE",75,3.3465708803712417E-3]
["BROADHURST-MCFADZEAN",75,3.3465708803712417E-3]
["LAUREL-TYLER",73,3.2573289902280088E-3]
["DIAMOND-ROSEHILL",73,3.2573289902280088E-3]
["ASHBY-LOCKSLEY",72,3.2127080451563924E-3]
["ESSEX-LANDELLS",71,3.168087100084776E-3]
["BIRDWOOD-KEILOR",71,3.168087100084776E-3]
["GRAVES-MARKET",70,3.1234661550131595E-3]
["SUFFOLK-DONGOLA",69,3.0788452099415431E-3]
["DAVID-RACHELLE",69,3.0788452099415431E-3]
["BIMBADEEN-YALLAMBIE",69,3.0788452099415431E-3]
["BRADSHAW-MARY",69,3.0788452099415431E-3]
["ST HELLIER-UP HEIDELBERG",68,3.0342242648699266E-3]
["LEVER-GORDON",68,3.0342242648699266E-3]
["FERGUSON-ROSEBERRY",68,3.0342242648699266E-3]
["KATHLEEN-WOOD",68,3.0342242648699266E-3]
["GLENMORE-KINLOCK",67,2.9896033197983102E-3]
["ORIEL-STANLEY",65,2.9003614296550773E-3]
["EAST-THACKERAY",65,2.9003614296550773E-3]
["BAXTER-SYDNEY",65,2.9003614296550773E-3]
["ROSELAND-IVANHOE",64,2.8557404845834609E-3]
["ARTHUR-ELIZABETH",64,2.8557404845834609E-3]
["BELGROVE-OVANDO",64,2.8557404845834609E-3]
["EIRENE-FRANCIS",63,2.8111195395118444E-3]
["ARTHUR-FAWKNER",63,2.8111195395118444E-3]
["ALBERT-HARROW",62,2.766498594440228E-3]
["GILBANK-GILBERT",61,2.7218776493686116E-3]
["LEBANON-FENACRE",60,2.6772567042969951E-3]
["LANDELLS-MARTIN",60,2.6772567042969951E-3]
["MALCOLM-ELIZABETH",60,2.6772567042969951E-3]
["KALANG-PLUMPTON",60,2.6772567042969951E-3]
["CORNWALL-HIGH SCHOOL",60,2.6772567042969951E-3]
["ANSTEY-PHILLIP",60,2.6772567042969951E-3]
["WOOD-GREENBELT",59,2.6326357592253787E-3]
["CAROLE JOY-SPRING",59,2.6326357592253787E-3]
["BRUNEL-TRUMAN",59,2.6326357592253787E-3]
["SEXTON-PARER",58,2.5880148141537622E-3]
["SUSSEX-HOLMES",58,2.5880148141537622E-3]
["MUNRO-ERSKINE",58,2.5880148141537622E-3]
["JOHN-WINIFRED",58,2.5880148141537622E-3]
["FLORENCE-LINCOLN",58,2.5880148141537622E-3]
["HODGSON-AVOCA",58,2.5880148141537622E-3]
["DARLING-WHITE",58,2.5880148141537622E-3]
["BLOOMFIELD-ROSAMOND",58,2.5880148141537622E-3]
["CHARLES-BENAMBRA",58,2.5880148141537622E-3]
["STEWART-PASCOE VALE",57,2.5433938690821458E-3]
["THE GLADE-SHERLOWE",57,2.5433938690821458E-3]
["MYRTLE-REGENT",57,2.5433938690821458E-3]
["CASTLETON 21-HAVILAH",57,2.5433938690821458E-3]
["CALA-HAMPTON",57,2.5433938690821458E-3]
["DAVERN-O'HEA",56,2.4987729240105293E-3]
["YALLAMBIE-WENDOVER",55,2.4541519789389129E-3]
["WEBB-QUEENSVILLE",55,2.4541519789389129E-3]
["QUEEN-RUSSELL",55,2.4541519789389129E-3]
["DOUGLAS-PASCOE VALE",55,2.4541519789389129E-3]
["DARLING-FULHAM",55,2.4541519789389129E-3]
["PEARL-WHEATSHEAF",54,2.4095310338672965E-3]
["CAMDON-NORTON",54,2.4095310338672965E-3]
["CARWARP-ERSKINE",54,2.4095310338672965E-3]
["O'CONNOR-WHITBY",53,2.36491008879568E-3]
["EISENHOWER-CHALEYER",53,2.36491008879568E-3]
["CHAPMAN-BELAIR",52,2.3202891437240636E-3]
["CLIFTON-WATERDALE",52,2.3202891437240636E-3]
["MARGTMARY-MURRAY",51,2.2756681986524471E-3]
["CLARENDON-WHITTAKER",51,2.2756681986524471E-3]
["SHACKELL-BELL",50,2.2310472535808307E-3]
["HILTON-WIDFORD",50,2.2310472535808307E-3]
["ASHLEY-EDWARDES",50,2.2310472535808307E-3]
["SOUDAN-HIGH",49,2.1864263085092143E-3]
["ROXBURGH-ROTHWELL",49,2.1864263085092143E-3]
["HANSEN-GLAMIS",49,2.1864263085092143E-3]
["JOFFRE-KENT",49,2.1864263085092143E-3]
["GENEVA-COMO",49,2.1864263085092143E-3]
["CLIFTON-JEAN",49,2.1864263085092143E-3]
["BREARLEY-BALMORAL",49,2.1864263085092143E-3]
["WILLIAM-MASON",48,2.1418053634375978E-3]
["PEEL-DOUGLAS",48,2.1418053634375978E-3]
["QUINN-NOGA",48,2.1418053634375978E-3]
["MCCRAE-ELSEY",48,2.1418053634375978E-3]
["GRANGE-CRAMER",48,2.1418053634375978E-3]
["BEAUCHAMP-HIGH",48,2.1418053634375978E-3]
["CANTALA-MCCRAE",48,2.1418053634375978E-3]
["WEST-JOHN",47,2.0971844183659814E-3]
["MYDDLETON-GRACE",47,2.0971844183659814E-3]
["REYNARD-PHILLIPS",46,2.0525634732943649E-3]
["WARD-LOUISVILLE",46,2.0525634732943649E-3]
["THORPE-WOODS",46,2.0525634732943649E-3]
["INVERMAY-MT IDA",46,2.0525634732943649E-3]
["JUKES-LANIGAN",46,2.0525634732943649E-3]
["BROWNING-SCOTT",46,2.0525634732943649E-3]
["BOSQUET-BALLARAT",46,2.0525634732943649E-3]
["CHEDDAR-JINGHI",46,2.0525634732943649E-3]
["BRASSEY-PYALONG",46,2.0525634732943649E-3]
["PLENTY-RESERVOIR COLLEGE",45,2.0079425282227485E-3]
["PORTLAND-MUNRO",45,2.0079425282227485E-3]
["JACK-FORD",45,2.0079425282227485E-3]
["GRAHAM-WOODLANDS",45,2.0079425282227485E-3]
["CLYDEBANK-AFTON",45,2.0079425282227485E-3]
["THE FAIRWAY-DUNNE",44,1.9633215831511321E-3]
["YALLAMBIE-JANICE",44,1.9633215831511321E-3]
["PAMELA-HERBERT",44,1.9633215831511321E-3]
["DONCASTER-WALTER",44,1.9633215831511321E-3]
["HOTHAM-RYDER No. 2",44,1.9633215831511321E-3]
["CUDGEWA-BORVA",44,1.9633215831511321E-3]
["TONKIN-MASHOOBRA",43,1.9187006380795156E-3]
["MARGARET-WINIFRED",43,1.9187006380795156E-3]
["MACK-PICKETT",43,1.9187006380795156E-3]
["DORSET-BERKELEY",43,1.9187006380795156E-3]
["DENYS-GLYNDA",43,1.9187006380795156E-3]
["CHARTERIS-BURKE",43,1.9187006380795156E-3]
["BRAIDHILL-WINDSOR",43,1.9187006380795156E-3]
["WESTMINSTER-MILITARY",42,1.874079693007899E-3]
["REYNARD-SPRINGHALL",42,1.874079693007899E-3]
["FORRESTER-HEDDERWICK",42,1.874079693007899E-3]
["ESSEX-DOWNS",42,1.874079693007899E-3]
["ANTHONY-BELLAIR",42,1.874079693007899E-3]
["ROGERSON-THOMPSON",41,1.8294587479362823E-3]
["GRENHILDA-DOUGLAS",41,1.8294587479362823E-3]
["ALMA-PALMERSTON",41,1.8294587479362823E-3]
["THE ESPLANADE-PLANTATION",40,1.7848378028646656E-3]
["VICTORY-FOSTERS",40,1.7848378028646656E-3]
["MITCHELL-HACKETT",40,1.7848378028646656E-3]
["KENNEDY-WILLIAM",40,1.7848378028646656E-3]
["GOULBURN-PALMERSTON",40,1.7848378028646656E-3]
["EFFINGHAM-WILKINS",40,1.7848378028646656E-3]
["RHONDA-CANNING",39,1.740216857793049E-3]
["KEADY-SYDNEY",39,1.740216857793049E-3]
["ALMA-CHANDLER",39,1.740216857793049E-3]
["SEPARATION-PERRY",38,1.6955959127214323E-3]
["WILLIAM-JUNCTION",38,1.6955959127214323E-3]
["WOLSELEY-THE AVENUE",38,1.6955959127214323E-3]
["LEWIS-WILLIAMS",38,1.6955959127214323E-3]
["OLIVE-SYLVAN",38,1.6955959127214323E-3]
["FETTLING-COOPER",38,1.6955959127214323E-3]
["DOYLE-NORTH",38,1.6955959127214323E-3]
["GRANDVIEW-HOLMES",38,1.6955959127214323E-3]
["CAPRICORN-PALMERSTON",38,1.6955959127214323E-3]
["WARRAGUL-LISMORE",37,1.6509749676498157E-3]
["SALMON-NAPIER",37,1.6509749676498157E-3]
["REYNARD-DONNE",37,1.6509749676498157E-3]
["ST LEONARDS-EPSOM",37,1.6509749676498157E-3]
["WALKER-NEWCASTLE",37,1.6509749676498157E-3]
["SALISBURY-JACK",37,1.6509749676498157E-3]
["RICHELIEU-ESSEX",37,1.6509749676498157E-3]
["QUINN-CLARKS",37,1.6509749676498157E-3]
["MARY-ROBERTS",37,1.6509749676498157E-3]
["PALMER-HEDLEY",37,1.6509749676498157E-3]
["HAWDON-BROWN",37,1.6509749676498157E-3]
["HODDLE-FLETCHER",37,1.6509749676498157E-3]
["ARGYLE-BROAD",37,1.6509749676498157E-3]
["WARATAH-DERBY",36,1.606354022578199E-3]
["WEST-KINGSLEY",36,1.606354022578199E-3]
["MONARCH-EAGLEVIEW",36,1.606354022578199E-3]
["DEAKIN-BERRY",36,1.606354022578199E-3]
["CENTRE-HOWARD",36,1.606354022578199E-3]
["THE CROSSWAY-PARK",35,1.5617330775065824E-3]
["WINGROVE-KELVIN",35,1.5617330775065824E-3]
["STEWART-OSBORNE",35,1.5617330775065824E-3]
["KILMORE-CHARLTON",35,1.5617330775065824E-3]
["EGLINTON-ARGYLE",35,1.5617330775065824E-3]
["GREEN-SPARKFORD",35,1.5617330775065824E-3]
["HEATHCOTE-KENT",35,1.5617330775065824E-3]
["COURTIS-MELBOURNE",35,1.5617330775065824E-3]
["ARTHUR-SEPARATION",35,1.5617330775065824E-3]
["DARLINGTON-RENNIE",35,1.5617330775065824E-3]
["WATERDALE-GRIFFITHS",34,1.5171121324349657E-3]
["ROSENTHAL-HUGHES",34,1.5171121324349657E-3]
["MCCOLL-MALPAS",34,1.5171121324349657E-3]
["CARTWRIGHT-PASCOE VALE",34,1.5171121324349657E-3]
["ADELINE-KOROROIT",34,1.5171121324349657E-3]
["THE BOULEVARD-GILBERT",33,1.472491187363349E-3]
["LENNOX-HYDE",33,1.472491187363349E-3]
["PARKVIEW-HEIDELBERG",33,1.472491187363349E-3]
["HOLDEN-MILITARY",33,1.472491187363349E-3]
["BERRY-KEILOR",33,1.472491187363349E-3]
["BRAY-BARTROP",33,1.472491187363349E-3]
["SHADFORTH-RALEIGH",32,1.4278702422917324E-3]
["WATERDALE-LLOYD",32,1.4278702422917324E-3]
["OMAR-MITCHELL",32,1.4278702422917324E-3]
["KINGSTON-COLLINSON",32,1.4278702422917324E-3]
["LAWLEY-GLASGOW",32,1.4278702422917324E-3]
["HILLSIDE-HURTLE",32,1.4278702422917324E-3]
["HILLSIDE-ROBERTS",32,1.4278702422917324E-3]
["ANGLISS-SANDERSON",32,1.4278702422917324E-3]
["ANDERSON-BEVERLEY",32,1.4278702422917324E-3]
["RICHARDS-BELL",31,1.3832492972201157E-3]
["RUSSELL-BARKLY",31,1.3832492972201157E-3]
["WALHALLA-MORELAND",31,1.3832492972201157E-3]
["PICKETT-HICKFORD",31,1.3832492972201157E-3]
["GOULBURN-SHAND",31,1.3832492972201157E-3]
["DUNDEE-MEADE",31,1.3832492972201157E-3]
["BUCKLEY-THE CROSSWAY",31,1.3832492972201157E-3]
["BOND-LIBERTY",31,1.3832492972201157E-3]
["ASH-WIDFORD",31,1.3832492972201157E-3]
["ALPHINGTON-PARK",31,1.3832492972201157E-3]
["ASHLEY-CENTRAL WEST NO.1",31,1.3832492972201157E-3]
["ARBOR-MACEY",31,1.3832492972201157E-3]
["WAVERLEY-HOLMES",30,1.3386283521484991E-3]
["RUTHERFORD-LILLIAN",30,1.3386283521484991E-3]
["YARRA-DOVER",30,1.3386283521484991E-3]
["PORTER-DOUGHARTY",30,1.3386283521484991E-3]
["PARKLANDS-KELVIN",30,1.3386283521484991E-3]
["NOVIAN-MARAMA",30,1.3386283521484991E-3]
["DONCASTER-MYROSS",30,1.3386283521484991E-3]
["GEELONG-QUEENSVILLE",30,1.3386283521484991E-3]
["HUNT-BAXTER",30,1.3386283521484991E-3]
["FRANCIS-VINCENT",30,1.3386283521484991E-3]
["DOYLE-RIDLEY",30,1.3386283521484991E-3]
["GYLES-ESSEX",30,1.3386283521484991E-3]
["COLE-OSBORNE",30,1.3386283521484991E-3]
["DARVALL-WAIORA",30,1.3386283521484991E-3]
["AYR-DAREBIN",30,1.3386283521484991E-3]
["DAVID-NORTH",30,1.3386283521484991E-3]
["TENNYSON-TYLER",29,1.2940074070768824E-3]
["YARRALEA-GIBSON",29,1.2940074070768824E-3]
["ZAMMIT-O'HAIRE",29,1.2940074070768824E-3]
["LEBANON-ELDORADO",29,1.2940074070768824E-3]
["NORTH-THOMAS",29,1.2940074070768824E-3]
["MCDONALD-GAFFNEY",29,1.2940074070768824E-3]
["CHRISTINA-BARBARA",29,1.2940074070768824E-3]
["BECKET-ANSELM",29,1.2940074070768824E-3]
["ROSENTHAL-ALLENBY",28,1.2493864620052658E-3]
["SOMERS-HINKLER",28,1.2493864620052658E-3]
["MARIE-MURPHY",28,1.2493864620052658E-3]
["NEWCASTLE-ELIZABETH",28,1.2493864620052658E-3]
["NEWSOM-STANFORD",28,1.2493864620052658E-3]
["REGINA-BELLEVUE",28,1.2493864620052658E-3]
["FORRESTER-COOPER",28,1.2493864620052658E-3]
["JULIET-BENT",28,1.2493864620052658E-3]
["FLETCHER-PASCOE VALE",28,1.2493864620052658E-3]
["JACKSON-THOMSON",28,1.2493864620052658E-3]
["FORRESTER-DEAKIN",28,1.2493864620052658E-3]
["DIXON-DERBY",28,1.2493864620052658E-3]
["GARNET-EMERALD",28,1.2493864620052658E-3]
["GIFFARD-OSBORNE",28,1.2493864620052658E-3]
["BOND-ATHELSTANE",28,1.2493864620052658E-3]
["GELLIBRAND-STEWART",27,1.2047655169336491E-3]
["ESSEX-DUDLEY",27,1.2047655169336491E-3]
["ALMOND-CONIFER",27,1.2047655169336491E-3]
["BERRY-LORNE",27,1.2047655169336491E-3]
["BLACK-MC MAHON",27,1.2047655169336491E-3]
["BECCLES-ANDERSON",27,1.2047655169336491E-3]
["BOND-ORIEL",27,1.2047655169336491E-3]
["ROBERTS-MCNAMARA",26,1.1601445718620324E-3]
["TREADWELL-DUDLEY",26,1.1601445718620324E-3]
["O'HEA-CUMBERLAND",26,1.1601445718620324E-3]
["LALUMA-MCCARRON",26,1.1601445718620324E-3]
["GRAHAM-ULRICH",26,1.1601445718620324E-3]
["GOFF-ELIZABETH",26,1.1601445718620324E-3]
["BLACKSHAWS-ELIZABETH",26,1.1601445718620324E-3]
["COONANS-WOODLANDS",26,1.1601445718620324E-3]
["BLAKE-DAVIS",26,1.1601445718620324E-3]
["VINCENT-BELL",25,1.1155236267904158E-3]
["ROSS-ELIZABETH",25,1.1155236267904158E-3]
["KENNEDY-CHAPMAN",25,1.1155236267904158E-3]
["NEWLANDS-MURRAY",25,1.1155236267904158E-3]
["OUTHWAITE-ORIEL",25,1.1155236267904158E-3]
["PLUNKETT-O'KEEFE",25,1.1155236267904158E-3]
["LAURIE-PURINUAN",25,1.1155236267904158E-3]
["JACKA-MCCRACKEN",25,1.1155236267904158E-3]
["JACKA-JOYNT",25,1.1155236267904158E-3]
["HOME-WILKINSON",25,1.1155236267904158E-3]
["FINLAYSON-BRAIDHILL",25,1.1155236267904158E-3]
["GALLERY GATE-PERONINE",25,1.1155236267904158E-3]
["GREENWOOD-O'HEA",25,1.1155236267904158E-3]
["COBURG-RENNIE",25,1.1155236267904158E-3]
["CENTRE WAY-FRAN",25,1.1155236267904158E-3]
["CONIFER-PRIMULA",25,1.1155236267904158E-3]
["BUCKLEY-ABERDEEN",25,1.1155236267904158E-3]
["CHALLIS-SPEIGHT",25,1.1155236267904158E-3]
["BRUCE-REYNARD",25,1.1155236267904158E-3]
["SYDNEY-ROSSHIRE",24,1.0709026817187991E-3]
["SHEFFIELD-MAY",24,1.0709026817187991E-3]
["VALLEY-AUGUSTINE",24,1.0709026817187991E-3]
["RUTHVEN-WAIORA",24,1.0709026817187991E-3]
["RYDER-NOLAN",24,1.0709026817187991E-3]
["ST JAMES-WOBURN",24,1.0709026817187991E-3]
["PASCOE VALE-BENDOC",24,1.0709026817187991E-3]
["MCKENNA-MILITARY",24,1.0709026817187991E-3]
["MARKS-YORK",24,1.0709026817187991E-3]
["MONZA-FLORENCE",24,1.0709026817187991E-3]
["HENLEY-CLARKE",24,1.0709026817187991E-3]
["HAWKHURST-FRANCIS",24,1.0709026817187991E-3]
["COHEN-GROVES",24,1.0709026817187991E-3]
["CHAPMAN-GRANDVIEW",24,1.0709026817187991E-3]
["BURNS-WAVERLEY",24,1.0709026817187991E-3]
["WEBB-CORONATION",23,1.0262817366471825E-3]
["RIDGEWAY-MARRSON",23,1.0262817366471825E-3]
["MCNAMARA-ROBERTS",23,1.0262817366471825E-3]
["NORTHERNHAY-OAKHILL",23,1.0262817366471825E-3]
["MOONEE-VALLEY",23,1.0262817366471825E-3]
["NAPOLI-SAN MARCO",23,1.0262817366471825E-3]
["HAWKER-COOK",23,1.0262817366471825E-3]
["FLOWER-BUCKLEY",23,1.0262817366471825E-3]
["INVERMAY-BELLEVUE",23,1.0262817366471825E-3]
["ERSKINE-ARGYLL",23,1.0262817366471825E-3]
["CENTREWAY-WINGARA",23,1.0262817366471825E-3]
["VISION-MASCOMA",22,9.8166079157556581E-4]
["YORK-NAPIER",22,9.8166079157556581E-4]
["WARATAH-CAROL",22,9.8166079157556581E-4]
["LIBERTY-PERKINS",22,9.8166079157556581E-4]
["ERIC-ADA",22,9.8166079157556581E-4]
["EVELL-MORLEY",22,9.8166079157556581E-4]
["HILLSYDE-LOEMAN",22,9.8166079157556581E-4]
["DORRINGTON-PLENTY",22,9.8166079157556581E-4]
["GLADSTONE-CHAPMAN",22,9.8166079157556581E-4]
["EPSOM-ST LEONARDS",22,9.8166079157556581E-4]
["CLINGIN-CREVELLI",22,9.8166079157556581E-4]
["DEAKIN-BUCKLEY",22,9.8166079157556581E-4]
["CAPE-YARRA",22,9.8166079157556581E-4]
["CLARKE-RUPERT",22,9.8166079157556581E-4]
["THE CROSSWAY-UPLAND",21,9.3703984650394926E-4]
["SUFFOLK-THOMSON",21,9.3703984650394926E-4]
["THE GRANGE-YALLAMBIE",21,9.3703984650394926E-4]
["SECOND-EVE",21,9.3703984650394926E-4]
["WHITE-CHEDDAR",21,9.3703984650394926E-4]
["MCCRACKEN-BUCKLEY",21,9.3703984650394926E-4]
["MIRAMS-UNION",21,9.3703984650394926E-4]
["PARSONS-STUBBS",21,9.3703984650394926E-4]
["NIMMO-BUCKLEY",21,9.3703984650394926E-4]
["LANTANA-IVANHOE",21,9.3703984650394926E-4]
["LOCKSLEY-MALTRAVERS",21,9.3703984650394926E-4]
["NUNAN-KIRBY",21,9.3703984650394926E-4]
["JOFFRE-KITCHENER",21,9.3703984650394926E-4]
["HUTCHINSON-NICHOLSON",21,9.3703984650394926E-4]
["HENTY-GILBERT",21,9.3703984650394926E-4]
["DORSET-DERBY",21,9.3703984650394926E-4]
["GLOUCESTER-HENTY",21,9.3703984650394926E-4]
["CHATFIELD-KINGSVILLE",21,9.3703984650394926E-4]
["CRESWICK-LATROBE",21,9.3703984650394926E-4]
["CULLEN-MARY",21,9.3703984650394926E-4]
["CHISHOLM-ERINBANK",21,9.3703984650394926E-4]
["SEVERN-SOMERVILLE",20,8.9241890143233261E-4]
["SNELL-WATT",20,8.9241890143233261E-4]
["VIEW-SUFFOLK",20,8.9241890143233261E-4]
["TONKIN-SUSSEX",20,8.9241890143233261E-4]
["OXFORD-JUNCTION",20,8.9241890143233261E-4]
["RATHCOWN-CHEDDAR",20,8.9241890143233261E-4]
["PHILLIP-STRACHEN",20,8.9241890143233261E-4]
["LOWSON-MINONA",20,8.9241890143233261E-4]
["LLOYD-MONASH",20,8.9241890143233261E-4]
["HILTON-CHURCHILL",20,8.9241890143233261E-4]
["JELLICOE-WATERDALE",20,8.9241890143233261E-4]
["JESSIE-HERMIONE",20,8.9241890143233261E-4]
["FINN-HAUGHTON",20,8.9241890143233261E-4]
["FERGUSON-TOWNHALL",20,8.9241890143233261E-4]
["BEETHAM-PROSPECT",20,8.9241890143233261E-4]
["DAVIS-MILITARY",20,8.9241890143233261E-4]
["CREVILLI-SUMMERHILL",20,8.9241890143233261E-4]
["WOODS-CHALLIS",19,8.4779795636071595E-4]
["SUSSEX-BANYULE",19,8.4779795636071595E-4]
["WHITBY-BARTON",19,8.4779795636071595E-4]
["SALWEEN-ELSA",19,8.4779795636071595E-4]
["WOODLAND-NAPIER",19,8.4779795636071595E-4]
["STEVEDORE-DOVER",19,8.4779795636071595E-4]
["TOWER-HEIDELBERG",19,8.4779795636071595E-4]
["WINN-MAJOR",19,8.4779795636071595E-4]
["RICHELIEU-JACKSON",19,8.4779795636071595E-4]
["VIEWBANK-BREES",19,8.4779795636071595E-4]
["LOWSON-TYSON",19,8.4779795636071595E-4]
["KELVIN-ALBERT",19,8.4779795636071595E-4]
["MERBEIN-SUSSEX",19,8.4779795636071595E-4]
["OLIVE-VIOLA",19,8.4779795636071595E-4]
["PERRY-VERDON",19,8.4779795636071595E-4]
["HAUGHTON-GREVILLE",19,8.4779795636071595E-4]
["DOLE-LOCHER",19,8.4779795636071595E-4]
["EDWIN-ST HELLIER",19,8.4779795636071595E-4]
["FORDHAM-STRATHMERTON",19,8.4779795636071595E-4]
["BURGESS-GILBERT",19,8.4779795636071595E-4]
["ROSAMOND-RIVER",18,8.0317701128909929E-4]
["SEPARATION-FULHAM",18,8.0317701128909929E-4]
["ST VIGEONS-BORRIE",18,8.0317701128909929E-4]
["WINSTON-JASON",18,8.0317701128909929E-4]
["WHITE-DUKE",18,8.0317701128909929E-4]
["WESTMERE-WARNE",18,8.0317701128909929E-4]
["PASCOE-BLACK",18,8.0317701128909929E-4]
["KNOX-GILBERT",18,8.0317701128909929E-4]
["NELSON-LYON",18,8.0317701128909929E-4]
["HAMLYN-VIDA",18,8.0317701128909929E-4]
["IRVINE-GAFFNEY",18,8.0317701128909929E-4]
["JENNINGS-ARDMILLAN",18,8.0317701128909929E-4]
["EARL-GRANGE",18,8.0317701128909929E-4]
["HAIG-GILBERT",18,8.0317701128909929E-4]
["FOCH-QUEEN",18,8.0317701128909929E-4]
["HEATHER-DINAH",18,8.0317701128909929E-4]
["HOLROYD-O'HEA",18,8.0317701128909929E-4]
["FULLARTON-WALTERS",18,8.0317701128909929E-4]
["DUNFIELD-BERESFORD",18,8.0317701128909929E-4]
["BEVERLEY-GREVILLE",18,8.0317701128909929E-4]
["ANGUS-MIDDLE",18,8.0317701128909929E-4]
["ALMA-YARRA",18,8.0317701128909929E-4]
["RIVIERA-WARRICK",17,7.5855606621748263E-4]
["WARRENS BROOK-SPEARGRASS",17,7.5855606621748263E-4]
["WINDSOR-CECIL",17,7.5855606621748263E-4]
["WALTHAM-LEE",17,7.5855606621748263E-4]
["STANGER-ADENEY",17,7.5855606621748263E-4]
["WILLOW-LINDA",17,7.5855606621748263E-4]
["THE BOULEVARD-NEVILLE",17,7.5855606621748263E-4]
["KNIGHT-BAYVIEW",17,7.5855606621748263E-4]
["MENARRA-LAMART",17,7.5855606621748263E-4]
["MELTON HWY-P2",17,7.5855606621748263E-4]
["NEAL-DINAH",17,7.5855606621748263E-4]
["MOORE-EAST",17,7.5855606621748263E-4]
["NOTTINGHAM-RACECOURSE",17,7.5855606621748263E-4]
["PRESTON-MUNRO",17,7.5855606621748263E-4]
["MARY-NIMMO",17,7.5855606621748263E-4]
["GREVILLE-KEILOR",17,7.5855606621748263E-4]
["FRASER-BOWES",17,7.5855606621748263E-4]
["HUDSONS-HICK",17,7.5855606621748263E-4]
["CATHERINE-SAINSBURY",17,7.5855606621748263E-4]
["BIRMINGHAM-MELBOURNE",17,7.5855606621748263E-4]
["CHARTERIS-WARNCLIFFE",17,7.5855606621748263E-4]
["BEATTY-MELBOURNE",17,7.5855606621748263E-4]
["ROSEHILL-TALBOT",16,7.1393512114586598E-4]
["WOODS-MADDOX No.2",16,7.1393512114586598E-4]
["WAIORA-DOUGHARTY",16,7.1393512114586598E-4]
["SOMERVILLE-JULIAN",16,7.1393512114586598E-4]
["WOOD-BROWN",16,7.1393512114586598E-4]
["TYRELL-MCBRYDE",16,7.1393512114586598E-4]
["LIVINGSTONE-ELIZABETH",16,7.1393512114586598E-4]
["LOCKHEED-BOEING",16,7.1393512114586598E-4]
["KELLAWAY-ROSAMOND",16,7.1393512114586598E-4]
["GISBORNE-NORTH",16,7.1393512114586598E-4]
["HAYES-HOUSTON",16,7.1393512114586598E-4]
["FULLWOOD-WHEELER",16,7.1393512114586598E-4]
["GARNET-IDA",16,7.1393512114586598E-4]
["JUSTIN-VIEW",16,7.1393512114586598E-4]
["FREYER-POWER",16,7.1393512114586598E-4]
["FLINDERS-THE WALK",16,7.1393512114586598E-4]
["HAWTHORN-REYNARD",16,7.1393512114586598E-4]
["ELLESMERE-CARRICK",16,7.1393512114586598E-4]
["CONNELL-HILTON",16,7.1393512114586598E-4]
["BOLINGBROKE-BURGUNDY",16,7.1393512114586598E-4]
["BELLEVUE-DAVIES",16,7.1393512114586598E-4]
["BROMYARD-DREW",16,7.1393512114586598E-4]
["ALOHA-WATT",16,7.1393512114586598E-4]
["STEEL-THE AVENUE",15,6.6931417607424932E-4]
["STUART-ORMOND",15,6.6931417607424932E-4]
["TIERNAN-RAGLAN",15,6.6931417607424932E-4]
["YORK- EASTGATE",15,6.6931417607424932E-4]
["LYDIA-DUNSTAN",15,6.6931417607424932E-4]
["LEVER-QUEEN",15,6.6931417607424932E-4]
["MASON-HIGH",15,6.6931417607424932E-4]
["LOWER PLENTY-MOUNTVIEW",15,6.6931417607424932E-4]
["MORRIS-MCMAHONS",15,6.6931417607424932E-4]
["PERIGRINE-DEEP CREEK",15,6.6931417607424932E-4]
["HARBURY-EDWARDES",15,6.6931417607424932E-4]
["EVELL-OGDEN",15,6.6931417607424932E-4]
["GARNET-MURIEL",15,6.6931417607424932E-4]
["ARDEN-LOWER PLENTY",15,6.6931417607424932E-4]
["ATHELSTANE-ROBBINS",15,6.6931417607424932E-4]
["CONDER-DOBELL",15,6.6931417607424932E-4]
["BULLA-DUBLIN",15,6.6931417607424932E-4]
["DALE-CHICAGO",15,6.6931417607424932E-4]
["CHALEYER-ASHTON",15,6.6931417607424932E-4]
["CARWARP-MAY",15,6.6931417607424932E-4]
["ARNCLIFFE-WATERHOUSE",15,6.6931417607424932E-4]
["CLAYTON-MASCOMA",15,6.6931417607424932E-4]
["THE EYRIE-SUMMIT",14,6.2469323100263266E-4]
["ROYAL-BULLA",14,6.2469323100263266E-4]
["WUNNAMURRA-WONGANELA",14,6.2469323100263266E-4]
["STEELE CREEK-BASALT",14,6.2469323100263266E-4]
["ROBERN-ROSEBUD",14,6.2469323100263266E-4]
["SHERWOOD-THORESBY",14,6.2469323100263266E-4]
["POWELL-EXCELSIOR",14,6.2469323100263266E-4]
["KINGSLEY-ROBERTS",14,6.2469323100263266E-4]
["OAK-CONISTON",14,6.2469323100263266E-4]
["KENNETH-GOWER",14,6.2469323100263266E-4]
["ERINBANK-DOBIES",14,6.2469323100263266E-4]
["GLASS-NAPIER",14,6.2469323100263266E-4]
["HOFFMANS-KEILOR",14,6.2469323100263266E-4]
["ELLEN-RACHELLE",14,6.2469323100263266E-4]
["GELLIBRAND-VICTORIA",14,6.2469323100263266E-4]
["JOHNSTON-NEWCASTLE",14,6.2469323100263266E-4]
["HIGH 883-MELB WATER",14,6.2469323100263266E-4]
["HILLCREST-ROYAL",14,6.2469323100263266E-4]
["BELMONT-BAYSWATER",14,6.2469323100263266E-4]
["COLLEGE-BREES",14,6.2469323100263266E-4]
["ASQUITH-STURDEE",14,6.2469323100263266E-4]
["ALTONA-ORIEL",14,6.2469323100263266E-4]
["BOLOGNA-PAVIA",14,6.2469323100263266E-4]
["BUNBURY-DOUGLAS",14,6.2469323100263266E-4]
["ALOHA-GREENE",14,6.2469323100263266E-4]
["CHANDOS-BREADALBANE",14,6.2469323100263266E-4]
["WATERDALE-THE BOULEVARD",13,5.80072285931016E-4]
["VICTORIA-RAILWAY",13,5.80072285931016E-4]
["SANDERSON-ROBERTS",13,5.80072285931016E-4]
["TUCKER-LYNCH",13,5.80072285931016E-4]
["TRACEY-ELLIOT",13,5.80072285931016E-4]
["YERING-GUILDFORD",13,5.80072285931016E-4]
["ROCK-DIANNE",13,5.80072285931016E-4]
["SANDOVER-SALWEEN",13,5.80072285931016E-4]
["SEPARATION-SHIERS",13,5.80072285931016E-4]
["MAJOR-HUME",13,5.80072285931016E-4]
["LINDSAY-TORBAY",13,5.80072285931016E-4]
["LATROBE-YARRA",13,5.80072285931016E-4]
["MCIVOR-OAKHILL",13,5.80072285931016E-4]
["PROSPECT-BUCKLEY",13,5.80072285931016E-4]
["LAWSON-SALISBURY",13,5.80072285931016E-4]
["RENOWN-KERFERD",13,5.80072285931016E-4]
["MCCOLL-TYLER",13,5.80072285931016E-4]
["RALEIGH-WILLS",13,5.80072285931016E-4]
["MELBOURNE-DAVIES",13,5.80072285931016E-4]
["PARK-PENLEIGH",13,5.80072285931016E-4]
["PINE-MARSHALL",13,5.80072285931016E-4]
["GREENSBOROUGH-YALLAMBIE",13,5.80072285931016E-4]
["GLASGOW-HIGH",13,5.80072285931016E-4]
["FARM-HOME",13,5.80072285931016E-4]
["EDWIN-GILLIES",13,5.80072285931016E-4]
["GREENACRE-AYLESBURY",13,5.80072285931016E-4]
["GRAHAM 138-SYLVIA",13,5.80072285931016E-4]
["ELLESMERE-INVERMAY",13,5.80072285931016E-4]
["HOBSON-HOME",13,5.80072285931016E-4]
["BAYVIEW-MARIBYRNONG",13,5.80072285931016E-4]
["CAMBRIAN-HIGH",13,5.80072285931016E-4]
["THISTLE-HACKETT",12,5.3545134085939935E-4]
["THE BOULEVARD-AFTON",12,5.3545134085939935E-4]
["THOMPSON-NORTH",12,5.3545134085939935E-4]
["ROSEHILL-ROSE",12,5.3545134085939935E-4]
["WILKINSON-BENDIGO",12,5.3545134085939935E-4]
["WOOD-LUNETTE",12,5.3545134085939935E-4]
["MAGDALA-WOODLAND",12,5.3545134085939935E-4]
["QUEEN-REYNARD",12,5.3545134085939935E-4]
["MIDDLE-ASCOT VALE",12,5.3545134085939935E-4]
["PINE-HENTY",12,5.3545134085939935E-4]
["MONASH-BONAR",12,5.3545134085939935E-4]
["LEAKE-RICHARDSON",12,5.3545134085939935E-4]
["LATROBE-MENZIES",12,5.3545134085939935E-4]
["PATTERSON-DAVID",12,5.3545134085939935E-4]
["GREVILLIA-ALBERT",12,5.3545134085939935E-4]
["JENNIFER-ANDERSON",12,5.3545134085939935E-4]
["EVERARD-MAY",12,5.3545134085939935E-4]
["ESMALE-LEBANON",12,5.3545134085939935E-4]
["FOSTERS-MIDWAY",12,5.3545134085939935E-4]
["HEPBURN-KING",12,5.3545134085939935E-4]
["DREDGE-TORMEY",12,5.3545134085939935E-4]
["GOSFORD-NICHOLAS",12,5.3545134085939935E-4]
["HANSON-GOBLE",12,5.3545134085939935E-4]
["JELLICOE-OSNEY",12,5.3545134085939935E-4]
["HILTON-WEST",12,5.3545134085939935E-4]
["BLUEGUM-BELLEVIEW",12,5.3545134085939935E-4]
["DALKEITH-GORDON",12,5.3545134085939935E-4]
["BAYVIEW-TOBRUK",12,5.3545134085939935E-4]
["CANTERBURY-BUNDANOON",12,5.3545134085939935E-4]
["BLANDFORD-ESSEX",12,5.3545134085939935E-4]
["ALBION-GEELONG",12,5.3545134085939935E-4]
["REYNARD-ROYAL",11,4.9083039578778269E-4]
["WARANGA-BLAIR",11,4.9083039578778269E-4]
["SYLVESTER-GORDON",11,4.9083039578778269E-4]
["STRATHMERTON-LEISURE CENTRE",11,4.9083039578778269E-4]
["YEA-KIEWA",11,4.9083039578778269E-4]
["SYDNEY-MURRAY",11,4.9083039578778269E-4]
["RENNIE-JOHN",11,4.9083039578778269E-4]
["NICHOLSON-BREWSTER",11,4.9083039578778269E-4]
["KERR-DEVEREAUX",11,4.9083039578778269E-4]
["PARK-COMBERMERE",11,4.9083039578778269E-4]
["ERSKINE-GLENCAIRN",11,4.9083039578778269E-4]
["GRAHAM-GIBSON",11,4.9083039578778269E-4]
["FENTON-MYRNONG",11,4.9083039578778269E-4]
["DIANNE-DAWSON",11,4.9083039578778269E-4]
["EAMES-CYPRESS",11,4.9083039578778269E-4]
["HALSEY-RADFORD",11,4.9083039578778269E-4]
["JAMES-NAIRN",11,4.9083039578778269E-4]
["DICKERSON-TUCKER",11,4.9083039578778269E-4]
["FULHAM-WINGROVE",11,4.9083039578778269E-4]
["HESLEDEN-AMELIA",11,4.9083039578778269E-4]
["JUNE-MCBRYDE",11,4.9083039578778269E-4]
["HIGHRIDGE-ROBERTS",11,4.9083039578778269E-4]
["ETKA-MARK",11,4.9083039578778269E-4]
["EDWARD-CASH",11,4.9083039578778269E-4]
["CAMPBELL-DE CARLE",11,4.9083039578778269E-4]
["BEDFORD-PARER",11,4.9083039578778269E-4]
["DARLING-EGLINTON",11,4.9083039578778269E-4]
["BOWEN-HOLMES",11,4.9083039578778269E-4]
["ARCADE-SOUTH GATEWAY",11,4.9083039578778269E-4]
["COOMA-GOWER",11,4.9083039578778269E-4]
["THE AVENUE-KEILOR",10,4.4620945071616609E-4]
["RUDSTONE-ABBEY",10,4.4620945071616609E-4]
["SALISBURY-WILLIAMSTOWN",10,4.4620945071616609E-4]
["TOUMLIN-MARTINS",10,4.4620945071616609E-4]
["WILSON-GILMOUR",10,4.4620945071616609E-4]
["STATION-HAMILTON",10,4.4620945071616609E-4]
["VALENCIA-MELBOURNE",10,4.4620945071616609E-4]
["VALLEY LAKE-STEELE CREEK",10,4.4620945071616609E-4]
["THE BOULEVARD-WARNCLIFFE",10,4.4620945071616609E-4]
["KENNY-COGHILL",10,4.4620945071616609E-4]
["REDGUM-DEEP CREEK",10,4.4620945071616609E-4]
["NEILL-MOUNSEY",10,4.4620945071616609E-4]
["RENNISON-CASTLEY",10,4.4620945071616609E-4]
["MERCIER-GAFFNEY No1",10,4.4620945071616609E-4]
["NORTH-RICHMOND",10,4.4620945071616609E-4]
["PRINCE-KEILOR",10,4.4620945071616609E-4]
["MCNAMARA-ELIZABETH",10,4.4620945071616609E-4]
["LOCKSLEY-KINSALE",10,4.4620945071616609E-4]
["MIHIL-VICTORIA",10,4.4620945071616609E-4]
["INTERVALE-ARCADE",10,4.4620945071616609E-4]
["HIGH-SEVERN",10,4.4620945071616609E-4]
["KATOOMBA-SUTHERLAND",10,4.4620945071616609E-4]
["HILTON-JUSTIN",10,4.4620945071616609E-4]
["BASIL-WOODS",10,4.4620945071616609E-4]
["BEDWELL-HUGHES",10,4.4620945071616609E-4]
["DARLING-MARIBYRNONG",10,4.4620945071616609E-4]
["BAMFIELD-COLLINS",10,4.4620945071616609E-4]
["BALLYMENA-KIRKHAM",10,4.4620945071616609E-4]
["ATHOL-EDGAR",10,4.4620945071616609E-4]
["CLARENDON-SELBOURNE",10,4.4620945071616609E-4]
["WINCHESTER-LAURA",9,4.0158850564454948E-4]
["SHAMROCK-ROSE",9,4.0158850564454948E-4]
["THE CROSSWAY-VISTA",9,4.0158850564454948E-4]
["STEANE-ALBERT",9,4.0158850564454948E-4]
["WILTSHIRE-DUNFIELD",9,4.0158850564454948E-4]
["RIVIERA-MILLEARA",9,4.0158850564454948E-4]
["WINGROVE-ARTHUR",9,4.0158850564454948E-4]
["STRATHAIRD-MASCOMA",9,4.0158850564454948E-4]
["SUMMIT-VICTORIA",9,4.0158850564454948E-4]
["(blank)",9,4.0158850564454948E-4]
["QUINN-ST. JAMES",9,4.0158850564454948E-4]
["MIRANDA-MAIS",9,4.0158850564454948E-4]
["MARYSTON-SOMERVILLE",9,4.0158850564454948E-4]
["MOASCAR-GALLIPOLI",9,4.0158850564454948E-4]
["MAY-SPRING",9,4.0158850564454948E-4]
["LARGS-MOTHERWELL",9,4.0158850564454948E-4]
["KERNAN-CARNARVON",9,4.0158850564454948E-4]
["MATHIESON-SYDNEY",9,4.0158850564454948E-4]
["DOVER-WATERLOO",9,4.0158850564454948E-4]
["HARDY-SNAEFELL",9,4.0158850564454948E-4]
["DUDLEY-GREEN",9,4.0158850564454948E-4]
["GAVIN-SUNSET",9,4.0158850564454948E-4]
["EDEN-BELL",9,4.0158850564454948E-4]
["EAST-EXETER",9,4.0158850564454948E-4]
["DRESS CIRCLE-THE RIDGE 1",9,4.0158850564454948E-4]
["DROMANA-GAFFNEY",9,4.0158850564454948E-4]
["BONVIEW-CARRINGTON",9,4.0158850564454948E-4]
["BROWNING-MOORE",9,4.0158850564454948E-4]
["CHARMAINE-BORDEAUX",9,4.0158850564454948E-4]
["CARR-NEWLANDS",9,4.0158850564454948E-4]
["ALEXANDRA-NORTHERNHAY",9,4.0158850564454948E-4]
["BARWON-PLENTY",9,4.0158850564454948E-4]
["COLTHUR-BANBURY",9,4.0158850564454948E-4]
["ARGYLE-DAREBIN",9,4.0158850564454948E-4]
["AMAR-MASCOMA",9,4.0158850564454948E-4]
["VIOLET-BUCKLEY",8,3.5696756057293288E-4]
["WYMLET-LYNCH",8,3.5696756057293288E-4]
["WOORITE-MILLEARA",8,3.5696756057293288E-4]
["WHITELAW-BOLDREWOOD",8,3.5696756057293288E-4]
["THE RIDGE-DEEP CREEK 5",8,3.5696756057293288E-4]
["THICKINS-NORTHUMBERLAND",8,3.5696756057293288E-4]
["THE BOULEVARD-PARKSTONE",8,3.5696756057293288E-4]
["SHORT-DUNVEGAN",8,3.5696756057293288E-4]
["KING-BOWES",8,3.5696756057293288E-4]
["LENA-ODONNELL",8,3.5696756057293288E-4]
["MCFADZEAN-HURLEY",8,3.5696756057293288E-4]
["NAPIER-BUTLER",8,3.5696756057293288E-4]
["PETERSON-JACKSON",8,3.5696756057293288E-4]
["MITCHELL-ROWE",8,3.5696756057293288E-4]
["PARKER-AITKEN",8,3.5696756057293288E-4]
["HEATHER-CYPRESS",8,3.5696756057293288E-4]
["GLENVIEW-UPLAND",8,3.5696756057293288E-4]
["GRANDVIEW-LONGVIEW",8,3.5696756057293288E-4]
["DERMOT-CORMAC",8,3.5696756057293288E-4]
["JUDITH-BREES",8,3.5696756057293288E-4]
["FLINDERS-WENTWORTH",8,3.5696756057293288E-4]
["FARRELL-RYDER",8,3.5696756057293288E-4]
["GAFFNEY-HIGINBOTHAM",8,3.5696756057293288E-4]
["GORDON-BELL",8,3.5696756057293288E-4]
["GLENSIDE-CANNING",8,3.5696756057293288E-4]
["HAWKER-MCNAMARA",8,3.5696756057293288E-4]
["FERNHILL-BARODA",8,3.5696756057293288E-4]
["BAYVIEW-GELLIBRAND",8,3.5696756057293288E-4]
["ARCADE-PROSPECT",8,3.5696756057293288E-4]
["BRAEMAR-MCCRACKEN",8,3.5696756057293288E-4]
["DACELO-GIBSON",8,3.5696756057293288E-4]
["DAREBIN-STRADBROKE",8,3.5696756057293288E-4]
["ALBERT-DUNDAS",8,3.5696756057293288E-4]
["ARNCLIFFE-LEEDS",8,3.5696756057293288E-4]
["ALEXANDER-JOHN",8,3.5696756057293288E-4]
["SEXTON-HALSEY",7,3.1234661550131628E-4]
["VANBERG-TENNYSON",7,3.1234661550131628E-4]
["ROBERTS-MARKET",7,3.1234661550131628E-4]
["SCOTIA-BELL",7,3.1234661550131628E-4]
["ST KINNORD-ALMA",7,3.1234661550131628E-4]
["STEVEDORE-MELBOURNE",7,3.1234661550131628E-4]
["WOODS-MADDOX No.1",7,3.1234661550131628E-4]
["RESERVOIR-WILSON",7,3.1234661550131628E-4]
["THE RIDGE-DEEP CREEK 2",7,3.1234661550131628E-4]
["STEVEDORE-STRAND",7,3.1234661550131628E-4]
["VICTORIA-FOLEY",7,3.1234661550131628E-4]
["ST LEONARDS-UNION",7,3.1234661550131628E-4]
["RIVER-HOME",7,3.1234661550131628E-4]
["WOLVERTON-BERESFORD",7,3.1234661550131628E-4]
["QUEEN-LINCOLN",7,3.1234661550131628E-4]
["PUNJEL-CALDER",7,3.1234661550131628E-4]
["KIAORA-GILBERT",7,3.1234661550131628E-4]
["MOONEE-ASCOT VALE",7,3.1234661550131628E-4]
["MCNAMARA-RUTHVEN",7,3.1234661550131628E-4]
["MCGREGOR-PERRY",7,3.1234661550131628E-4]
["MCIVOR-KIEWA",7,3.1234661550131628E-4]
["PARK-INGLIS",7,3.1234661550131628E-4]
["LOCH-REYNARDS",7,3.1234661550131628E-4]
["ELDORADO-STRELDON",7,3.1234661550131628E-4]
["ILLAWARRA-PASCOEVALE",7,3.1234661550131628E-4]
["DRESS CIRCLE-THE RIDGE 2",7,3.1234661550131628E-4]
["DISNEY-HUME",7,3.1234661550131628E-4]
["IVAN-MASCOMA",7,3.1234661550131628E-4]
["FRIER-PLENTY",7,3.1234661550131628E-4]
["HOOD-MCBRYDE",7,3.1234661550131628E-4]
["FOSTERS-ELIZA",7,3.1234661550131628E-4]
["COLLINS-WATERDALE",7,3.1234661550131628E-4]
["ANNE-DALEGLEN",7,3.1234661550131628E-4]
["COBRAM-LILLIPUT",7,3.1234661550131628E-4]
["BONVIEW-HENTY",7,3.1234661550131628E-4]
["BOURNIAN-GRAMMAR",7,3.1234661550131628E-4]
["ALLAN-CLIFTON",7,3.1234661550131628E-4]
["STEWART-LITTLE OSBORNE",6,2.6772567042969967E-4]
["WILLOUGHBY-EDWARDES",6,2.6772567042969967E-4]
["ROSTELLA-NORWOOD",6,2.6772567042969967E-4]
["THE RIDGE-DEEP CREEK 1",6,2.6772567042969967E-4]
["THE RIDGE-DEEP CREEK 3",6,2.6772567042969967E-4]
["WOOD-SYDNEY 2",6,2.6772567042969967E-4]
["THE RIGHI-CASTLE",6,2.6772567042969967E-4]
["WILFRED-CEDRIC",6,2.6772567042969967E-4]
["SPRATLING-HENTY",6,2.6772567042969967E-4]
["UP H'BERG-ST HELLIER",6,2.6772567042969967E-4]
["WATTLEVALLEY-JAMES",6,2.6772567042969967E-4]
["WESTGATE-HATTER",6,2.6772567042969967E-4]
["LYONS-WEST",6,2.6772567042969967E-4]
["MARKET-COLLINS",6,2.6772567042969967E-4]
["MARIBYRNONG-WALTER",6,2.6772567042969967E-4]
["NERISSA-SNELL",6,2.6772567042969967E-4]
["OSBORNE-GARDEN",6,2.6772567042969967E-4]
["MOYANGUL-GUNGARLAN",6,2.6772567042969967E-4]
["OUTHWAITE-MCEWAN",6,2.6772567042969967E-4]
["ELECTRA-PASCO",6,2.6772567042969967E-4]
["HART-BOWES",6,2.6772567042969967E-4]
["HEMAR-BRAMSHAW",6,2.6772567042969967E-4]
["HILLCREST-PLUMPTON",6,2.6772567042969967E-4]
["DE CARLE-RENNIE",6,2.6772567042969967E-4]
["BROWN-ROSANNA",6,2.6772567042969967E-4]
["ANDERSON-MONASH",6,2.6772567042969967E-4]
["CORONET-EDINBURGH",6,2.6772567042969967E-4]
["BOLINGBROKE-CUMBERLAND",6,2.6772567042969967E-4]
["BURGUNDY-MARTIN",6,2.6772567042969967E-4]
["BRUCE-GILBERT",6,2.6772567042969967E-4]
["BANKSIA-GLENARD",6,2.6772567042969967E-4]
["BANBURY-HURSLEY",6,2.6772567042969967E-4]
["THE RIDGE-DEEP CREEK 4",5,2.2310472535808307E-4]
["SOUDAN-ESSEX",5,2.2310472535808307E-4]
["SIM-GEORGE",5,2.2310472535808307E-4]
["SHEFFIELD-COBURG",5,2.2310472535808307E-4]
["SPENCER-ROBERTS",5,2.2310472535808307E-4]
["ROSANNA-ARDEN",5,2.2310472535808307E-4]
["TASMAN-MIDLAND",5,2.2310472535808307E-4]
["SCARBOROUGH-BUCKINGHAM",5,2.2310472535808307E-4]
["MANLY-MATHIESON",5,2.2310472535808307E-4]
["MCPHERSON-BENT",5,2.2310472535808307E-4]
["LOCH-WENDORA",5,2.2310472535808307E-4]
["MURRAY-BONWICK",5,2.2310472535808307E-4]
["MURRAY-PASCOE VALE",5,2.2310472535808307E-4]
["NAPOLEON-BRUNSWICK",5,2.2310472535808307E-4]
["LUDEMAN-BRAITHWAITE",5,2.2310472535808307E-4]
["MORETTI-FORREST",5,2.2310472535808307E-4]
["PITT-MAJOR",5,2.2310472535808307E-4]
["MACPHERSON-SHEPHERD",5,2.2310472535808307E-4]
["HOTHAM-MARIBYRNONG",5,2.2310472535808307E-4]
["GLENPARK-OUTLOOK",5,2.2310472535808307E-4]
["HIGGINS-MCKELL",5,2.2310472535808307E-4]
["HILLVIEW-PURCHES",5,2.2310472535808307E-4]
["DOMAIN-LYGON",5,2.2310472535808307E-4]
["ERINBANK-ALVIE",5,2.2310472535808307E-4]
["ALAMEDA-HILLSIDE",5,2.2310472535808307E-4]
["ALMA-WAVERLEY",5,2.2310472535808307E-4]
["BANK-WATTLEGLEN",5,2.2310472535808307E-4]
["BANNON-RETREAT",5,2.2310472535808307E-4]
["BANKSIA-LIBERTY",5,2.2310472535808307E-4]
["BANYULE-MCCRAE",5,2.2310472535808307E-4]
["CLARENDON-SYDNEY",5,2.2310472535808307E-4]
["BIRCH-GILBERT",5,2.2310472535808307E-4]
["DEAKIN-MARY",5,2.2310472535808307E-4]
["CAPE-ST JAMES",5,2.2310472535808307E-4]
["SCHOOL-TRAP",4,1.7848378028646647E-4]
["RETREAT-HAVEN",4,1.7848378028646647E-4]
["UNION-GILBERT",4,1.7848378028646647E-4]
["WILFRED-LOWER HEIDELBERG",4,1.7848378028646647E-4]
["WAIORA-CHURCHILL",4,1.7848378028646647E-4]
["WODONGA-CUTHBERT",4,1.7848378028646647E-4]
["SAN REMO-RIVIERA",4,1.7848378028646647E-4]
["TURNER-MENZIES",4,1.7848378028646647E-4]
["SANTA MONICA-LAGUNA",4,1.7848378028646647E-4]
["TRESCO-BARRY",4,1.7848378028646647E-4]
["WILSON-ARGYLE",4,1.7848378028646647E-4]
["MERCIER-CHARLES",4,1.7848378028646647E-4]
["PALANA-PENGANA",4,1.7848378028646647E-4]
["PENGANA-LOONGANA",4,1.7848378028646647E-4]
["PINES-KEYSBOROUGH",4,1.7848378028646647E-4]
["KIRBISTER-GAFFNEY",4,1.7848378028646647E-4]
["LANDY-LICHFIELD",4,1.7848378028646647E-4]
["KING-MCCRACKEN",4,1.7848378028646647E-4]
["PATTISON-VINE",4,1.7848378028646647E-4]
["LANCEWOOD-BRENTWICK",4,1.7848378028646647E-4]
["PROSPECT-PASCOE VALE",4,1.7848378028646647E-4]
["KERFERD-RALEIGH",4,1.7848378028646647E-4]
["MITCHELL-OAKOVER",4,1.7848378028646647E-4]
["GRANDVIEW-PASCOE VALE",4,1.7848378028646647E-4]
["JAMES-MAJOR",4,1.7848378028646647E-4]
["GODLEY-BROADHURST",4,1.7848378028646647E-4]
["GREEN-BOURKE",4,1.7848378028646647E-4]
["JEAN-FAWKNER",4,1.7848378028646647E-4]
["HERBERT-GARNER",4,1.7848378028646647E-4]
["INGOT-PLUMPTON",4,1.7848378028646647E-4]
["IVANHOE-WESTLEY",4,1.7848378028646647E-4]
["GOURLAY-MELTON",4,1.7848378028646647E-4]
["HEVERSHAM-BIRTLEY",4,1.7848378028646647E-4]
["FERGUSON-CHAPMAN",4,1.7848378028646647E-4]
["BRUCE-WAVERLEY",4,1.7848378028646647E-4]
["BARDWELL DR-P11",4,1.7848378028646647E-4]
["BERNARD-BROADWAY",4,1.7848378028646647E-4]
["CORNISH-LIGAR",4,1.7848378028646647E-4]
["ALLIMA-ELONERA",4,1.7848378028646647E-4]
["CANNES-CAPRI",4,1.7848378028646647E-4]
["BELMONT-DELLA TORRE",4,1.7848378028646647E-4]
["CRAMER-GILBERT",4,1.7848378028646647E-4]
["ALTONA-KOKODA",4,1.7848378028646647E-4]
["THE EYRIE-LAWRENCE",3,1.3386283521484986E-4]
["SUNMOTH-DEBONAIR",3,1.3386283521484986E-4]
["WIMPORT-MARTIN",3,1.3386283521484986E-4]
["VAUCLUSE-LENOAK",3,1.3386283521484986E-4]
["SHAFTESBURY-RALEIGH",3,1.3386283521484986E-4]
["STATION-CARTWRIGHT",3,1.3386283521484986E-4]
["ST GEORGES-TAFE COLLEGE",3,1.3386283521484986E-4]
["RENOWN-MITCHELL",3,1.3386283521484986E-4]
["MOORE-HENTY",3,1.3386283521484986E-4]
["LACY-CANNING",3,1.3386283521484986E-4]
["LEDGER-MAJOR",3,1.3386283521484986E-4]
["MARYBOROUGH-DUNNE",3,1.3386283521484986E-4]
["LINDSAY-GLENROY",3,1.3386283521484986E-4]
["KENTWOOD-ALBANY",3,1.3386283521484986E-4]
["MILLER-HORNE",3,1.3386283521484986E-4]
["MACKAY-GLASS",3,1.3386283521484986E-4]
["NEPEAN-WELLESLEY",3,1.3386283521484986E-4]
["MONTGOMERY-EDWIN",3,1.3386283521484986E-4]
["MARGARET-MURPHY",3,1.3386283521484986E-4]
["MOUNT-DEVON",3,1.3386283521484986E-4]
["LAHINCH-WIDFORD",3,1.3386283521484986E-4]
["LANGHAM-CANNING",3,1.3386283521484986E-4]
["RAMU-PACIFIC",3,1.3386283521484986E-4]
["MAHONEYS-KATHRYN",3,1.3386283521484986E-4]
["PARKSIDE-HIGHVIEW",3,1.3386283521484986E-4]
["LANGTON-GREENVALE",3,1.3386283521484986E-4]
["JUDY-CHURCHILL",3,1.3386283521484986E-4]
["FREDA-WIDFORD",3,1.3386283521484986E-4]
["FIRST-BARKLY",3,1.3386283521484986E-4]
["DUNSTAN-BARRY",3,1.3386283521484986E-4]
["EDWARD-GREENSBOROUGH",3,1.3386283521484986E-4]
["HAWKER-ELLISON",3,1.3386283521484986E-4]
["DEEP CREEK-PERIGRINE",3,1.3386283521484986E-4]
["ELIZABETH-LEICHARDT",3,1.3386283521484986E-4]
["GREENSBOROUGH-DRYSDALE",3,1.3386283521484986E-4]
["KEILOR-MC CULLOCH",3,1.3386283521484986E-4]
["ANNADALE-KIRKHAM",3,1.3386283521484986E-4]
["BIZANA-FONTEIN",3,1.3386283521484986E-4]
["ALVA-URQUHART",3,1.3386283521484986E-4]
["BORLASE-DRYSDALE",3,1.3386283521484986E-4]
["DAVIES-MILLER",3,1.3386283521484986E-4]
["CHARLTON-BOLDREWOOD",3,1.3386283521484986E-4]
["COLLINGWOOD-DOUGLAS",3,1.3386283521484986E-4]
["CHISHOLM-OSBORNE",3,1.3386283521484986E-4]
["CAMERON-MATTHEWS",3,1.3386283521484986E-4]
["SCARVELL-PRO HART",2,8.9241890143233234E-5]
["SEVERN-BENBOW",2,8.9241890143233234E-5]
["WILLIAM-JUKES",2,8.9241890143233234E-5]
["STURDEE-ASCOT VALE",2,8.9241890143233234E-5]
["THE REGENCY-KING",2,8.9241890143233234E-5]
["WALTER-ARRAN 2",2,8.9241890143233234E-5]
["WILLETT-SUMMIT",2,8.9241890143233234E-5]
["STANLEY-DOVER",2,8.9241890143233234E-5]
["WASHINGTON-MILLER",2,8.9241890143233234E-5]
["WHITTON-BOYNE",2,8.9241890143233234E-5]
["WOOD-RAGLAN",2,8.9241890143233234E-5]
["SCOTT-PARK",2,8.9241890143233234E-5]
["TEMPLEWOOD-WEYBURN",2,8.9241890143233234E-5]
["TEMPLEWOOD-FENWICK",2,8.9241890143233234E-5]
["ROBESON-KENDALL",2,8.9241890143233234E-5]
["VICTORY-EREBUS",2,8.9241890143233234E-5]
["TILBA-BRUNEL",2,8.9241890143233234E-5]
["KONAGADERRA RD-P50E3",2,8.9241890143233234E-5]
["NORWOOD-PROSPECT",2,8.9241890143233234E-5]
["NORTH-BARWON",2,8.9241890143233234E-5]
["KINGSTON-WILLIAMSTOWN",2,8.9241890143233234E-5]
["NICHOL-GOWER",2,8.9241890143233234E-5]
["KONAGADERRA RD-P39E2",2,8.9241890143233234E-5]
["MELTON-MEWS",2,8.9241890143233234E-5]
["ORIEL-HAWKER",2,8.9241890143233234E-5]
["KONAGADERRA-TEA ROOM",2,8.9241890143233234E-5]
["MCCUBBIN-WENTWORTH",2,8.9241890143233234E-5]
["KONAGADERRA RD-P42E1",2,8.9241890143233234E-5]
["MOUNTAIN VIEW-DAVIES",2,8.9241890143233234E-5]
["KONAGADERRA RD-P46E2",2,8.9241890143233234E-5]
["MOUNT-YARRA",2,8.9241890143233234E-5]
["LILY-SUSSEX",2,8.9241890143233234E-5]
["MCINTOSH 42-MATTHEWS",2,8.9241890143233234E-5]
["MASCOMA-STRATHNAVER",2,8.9241890143233234E-5]
["LANGS-VICTORY 2",2,8.9241890143233234E-5]
["KINGSLEY-KAVEL",2,8.9241890143233234E-5]
["PAYWIT-BELLARINE",2,8.9241890143233234E-5]
["KONAGADERRA-YUROKE",2,8.9241890143233234E-5]
["RENNIE-GLENORA",2,8.9241890143233234E-5]
["PAINE-LATROBE",2,8.9241890143233234E-5]
["PERRY-GORDON",2,8.9241890143233234E-5]
["PAINE-MELBOURNE",2,8.9241890143233234E-5]
["JUNE-COLLINS",2,8.9241890143233234E-5]
["HUGHES-FRANCIS",2,8.9241890143233234E-5]
["HILTON-RICHMOND",2,8.9241890143233234E-5]
["DEEP CREEK 320-REDGUM",2,8.9241890143233234E-5]
["GISH-MIDDLE",2,8.9241890143233234E-5]
["GLENGYLE-NICHOLSON",2,8.9241890143233234E-5]
["HURTLE-NEWSOM",2,8.9241890143233234E-5]
["HIGGINS-RUTHVEN",2,8.9241890143233234E-5]
["INDWE-PARAMOUNT",2,8.9241890143233234E-5]
["JUKES-BONWICK",2,8.9241890143233234E-5]
["GELLIBRAND-ALLENBY",2,8.9241890143233234E-5]
["DEEP CREEK-REDGUM",2,8.9241890143233234E-5]
["FORREST-HUDSONS",2,8.9241890143233234E-5]
["HILBERT-ROBERTS",2,8.9241890143233234E-5]
["GOTHA-ST HELLIER",2,8.9241890143233234E-5]
["AMEILY-LEAMINGTON",2,8.9241890143233234E-5]
["BALLARAT-OVENS",2,8.9241890143233234E-5]
["BRISTOL-SOUTH",2,8.9241890143233234E-5]
["DANSON-WINSTON",2,8.9241890143233234E-5]
["BROOK-JOHNSTONE",2,8.9241890143233234E-5]
["BARRY-WHITBY",2,8.9241890143233234E-5]
["BRIDGETON-TUNALEY",2,8.9241890143233234E-5]
["BATMAN-BUCKLEY",2,8.9241890143233234E-5]
["CROCKET-HOTHLYN",2,8.9241890143233234E-5]
["BAMFIELD-OUTHWAITE",2,8.9241890143233234E-5]
["ARVERN-MEDFIELD",2,8.9241890143233234E-5]
["CARNARVON-LLOYD",2,8.9241890143233234E-5]
["ALBERT 62-OVANDO",2,8.9241890143233234E-5]
["ARBOR-HEIDELBERG",2,8.9241890143233234E-5]
["DARNLEY-JOY",2,8.9241890143233234E-5]
["CLOVELLY-ENFIELD",2,8.9241890143233234E-5]
["TUDOR-PLUMPTON",1,4.4620945071616617E-5]
["TURIN-MESSINA",1,4.4620945071616617E-5]
["SHELLEY-NOGA",1,4.4620945071616617E-5]
["STUDLEY-CARN",1,4.4620945071616617E-5]
["STOREY-MENDIP",1,4.4620945071616617E-5]
["SCOVELL-CATHCART",1,4.4620945071616617E-5]
["WYONG-CENTREWAY",1,4.4620945071616617E-5]
["WATTLEBIRD-BROOKVALE",1,4.4620945071616617E-5]
["SHEPPARD-SHORTS",1,4.4620945071616617E-5]
["ROYAL-YORKSHIRE",1,4.4620945071616617E-5]
["VERDON-FERGUSON",1,4.4620945071616617E-5]
["WELLESLEY-SANDPIPER",1,4.4620945071616617E-5]
["STRATFORD-EAST",1,4.4620945071616617E-5]
["SPELLMAN-CECIL",1,4.4620945071616617E-5]
["RIDGE-NORTH",1,4.4620945071616617E-5]
["WATERDALE-SOUTHERN",1,4.4620945071616617E-5]
["WAMBA-THE BOULEVARD",1,4.4620945071616617E-5]
["WILLIAM-HEDDERWICK",1,4.4620945071616617E-5]
["RIDDELL RD-P106E1",1,4.4620945071616617E-5]
["SUMMERHILL-BARKLY",1,4.4620945071616617E-5]
["STREETON-MACKENNEL",1,4.4620945071616617E-5]
["UPPER HEIDELBERG-LOCHABAR",1,4.4620945071616617E-5]
["SAPPHIRE-ROSEHILL",1,4.4620945071616617E-5]
["TIMINS-OSHANASSY",1,4.4620945071616617E-5]
["VENTNOR-OAKOVER",1,4.4620945071616617E-5]
["STONEY-SALTWATER",1,4.4620945071616617E-5]
["RHYOLITE-BANJOLINA",1,4.4620945071616617E-5]
["WESTON-WHEATLEY",1,4.4620945071616617E-5]
["SANDPIPER-CARDIGAN",1,4.4620945071616617E-5]
["REGENT-HIGH",1,4.4620945071616617E-5]
["MARJORY-MCBRYDE",1,4.4620945071616617E-5]
["LOGAN-BACKHAUS",1,4.4620945071616617E-5]
["MCNAB-INVERNESS",1,4.4620945071616617E-5]
["MCBRYDE 134-MAJOR",1,4.4620945071616617E-5]
["KONAGADERRA RD-P42E3",1,4.4620945071616617E-5]
["KIERNAN-UPP HEIDELBERG",1,4.4620945071616617E-5]
["LYTTON-PASCOE VALE",1,4.4620945071616617E-5]
["MICKLEHAM RD-P0156",1,4.4620945071616617E-5]
["NEYLON-ROBERTS",1,4.4620945071616617E-5]
["LEAMINGTON-EPSTEIN",1,4.4620945071616617E-5]
["MCCOMAS-ALBERT",1,4.4620945071616617E-5]
["RAY-O'HEA",1,4.4620945071616617E-5]
["LONGSTAFF-STREETON",1,4.4620945071616617E-5]
["NAPOLI-VERONA",1,4.4620945071616617E-5]
["NICHOLSON-LYONS",1,4.4620945071616617E-5]
["NAREEN-PAISLEY",1,4.4620945071616617E-5]
["MCPHERSON-QUINN",1,4.4620945071616617E-5]
["KOROROIT-LEMMON",1,4.4620945071616617E-5]
["ORIEL-TOBRUK",1,4.4620945071616617E-5]
["MCKELL-RIDDELL",1,4.4620945071616617E-5]
["MADDEN-BULLA",1,4.4620945071616617E-5]
["RAILWAY-CHARLES",1,4.4620945071616617E-5]
["PARKER-AVOCA",1,4.4620945071616617E-5]
["RAMSAY-FAWKNER",1,4.4620945071616617E-5]
["MORPHETT-DONCASTER",1,4.4620945071616617E-5]
["MILES-LIVINGSTONE",1,4.4620945071616617E-5]
["KONAGADERRA RD-P39",1,4.4620945071616617E-5]
["PARK-BOTANIC",1,4.4620945071616617E-5]
["PRISTINE-ALLURE",1,4.4620945071616617E-5]
["NEW-THE AVENUE",1,4.4620945071616617E-5]
["KONAGADERRA-P59",1,4.4620945071616617E-5]
["KONAGADERRA RD-P43",1,4.4620945071616617E-5]
["MARSHALL-TOORA",1,4.4620945071616617E-5]
["LACELLES-WINSTON",1,4.4620945071616617E-5]
["OUTAWOOD RISE-P6",1,4.4620945071616617E-5]
["OUTAWOOD RISE-P7",1,4.4620945071616617E-5]
["FAIRY-WATERDALE",1,4.4620945071616617E-5]
["EDGAR-HIGH",1,4.4620945071616617E-5]
["HUME 1825-SOMERTON 1",1,4.4620945071616617E-5]
["GEELONG-OLD GEELONG",1,4.4620945071616617E-5]
["DERRY-ABERDEEN",1,4.4620945071616617E-5]
["FREEMAN-LIZA",1,4.4620945071616617E-5]
["HARRICKS-ALISON",1,4.4620945071616617E-5]
["FIELD-GRANDISON",1,4.4620945071616617E-5]
["DUMFRIES-QUEENSFERRY",1,4.4620945071616617E-5]
["JACKSON-STATION",1,4.4620945071616617E-5]
["GLADSTONE-HARDING",1,4.4620945071616617E-5]
["JACKSON-STURDEE",1,4.4620945071616617E-5]
["HILLVIEW-REYNARD",1,4.4620945071616617E-5]
["EASTERN-KINGSWOOD",1,4.4620945071616617E-5]
["KEILOR-NYAH",1,4.4620945071616617E-5]
["HALL-BURBANK",1,4.4620945071616617E-5]
["HUME 144-OHERNS",1,4.4620945071616617E-5]
["DEEP CREEK-KONAGADERRA 2",1,4.4620945071616617E-5]
["HARRISON-DAVIDSON",1,4.4620945071616617E-5]
["HAMILTON-O'FARRELL",1,4.4620945071616617E-5]
["GREEN-REC RESERVE",1,4.4620945071616617E-5]
["DUFFY-BARRY",1,4.4620945071616617E-5]
["EDMONDS-NEW BOULEVARD",1,4.4620945071616617E-5]
["HANMER-ELECTRA",1,4.4620945071616617E-5]
["GREEN-STYMIE",1,4.4620945071616617E-5]
["FITZROY-GOURLAY",1,4.4620945071616617E-5]
["KANGAROO-HIGHLANDER",1,4.4620945071616617E-5]
["GRANITE-VALLEY LAKE",1,4.4620945071616617E-5]
["IRONBARK-RUTHERFORD",1,4.4620945071616617E-5]
["FLEETWOOD-HEVERSHAM",1,4.4620945071616617E-5]
["GREVILLEA-PLUM",1,4.4620945071616617E-5]
["GISBORNE MELTON RD-P14E2",1,4.4620945071616617E-5]
["HEAD-NAPIER",1,4.4620945071616617E-5]
["HAROLD-HURTLE",1,4.4620945071616617E-5]
["COUANGALT RD-P38",1,4.4620945071616617E-5]
["ASHLEY-NAPOLEON",1,4.4620945071616617E-5]
["AIRDRIE-GALASHIELS",1,4.4620945071616617E-5]
["CRAIGIEBURN RD-P70",1,4.4620945071616617E-5]
["CORNISH-ANDERSONS",1,4.4620945071616617E-5]
["CHARTER-WILSONS",1,4.4620945071616617E-5]
["CARLTON-DARNLEY",1,4.4620945071616617E-5]
["BRASSEY CRT-P4",1,4.4620945071616617E-5]
["CASTLEWELLAN-BORONIA",1,4.4620945071616617E-5]
["BRASSEY CRT-P5E2",1,4.4620945071616617E-5]
["BECKWITH-PARKVIEW",1,4.4620945071616617E-5]
["CLYDE-MASON",1,4.4620945071616617E-5]
["BANKSIA-LOWER HEIDELBERG",1,4.4620945071616617E-5]
["BRASSEY CRT-P8E1",1,4.4620945071616617E-5]
["DEANS-SYDNEY",1,4.4620945071616617E-5]
["BURGUNDY-STRADBROKE",1,4.4620945071616617E-5]
["CAMBERWELL-McCRACKEN",1,4.4620945071616617E-5]
["ARVERN MEDFIELD No.2",1,4.4620945071616617E-5]
["BONA-VINCENT",1,4.4620945071616617E-5]
["CLYDE-THE ESPLANADE",1,4.4620945071616617E-5]
["CLARKE-SOMERSET",1,4.4620945071616617E-5]
["CARROL-ROYAL",1,4.4620945071616617E-5]
["BARDWELL DR-P15E2",1,4.4620945071616617E-5]
["BURNETT-NORTHPARK",1,4.4620945071616617E-5]
["BRADSHAW-MARYBOROUGH",1,4.4620945071616617E-5]
["CHAUVEL-GLASGOW",1,4.4620945071616617E-5]
["BANFF-DON",1,4.4620945071616617E-5]
["CAPTAIN PEARSON-PINE",1,4.4620945071616617E-5]
["BARDWELL DR-P16E",1,4.4620945071616617E-5]
["CARAWA-MICKLEHAM",1,4.4620945071616617E-5]
["ANSTEY-LOCKTON",1,4.4620945071616617E-5]
["CARDINAL-GLENROY",1,4.4620945071616617E-5]
["BEETHAM-LOWER PLENTY",1,4.4620945071616617E-5]
["BUCHANAN-SALISBURY",1,4.4620945071616617E-5]
["Grand Total",22411,1.0000000000002025]

{"sheet":"Low V contribution by ZSS","index":7,"n_rows":34,"n_cols":3,"rows_kept":34,"cut":false,"hidden":false,"merged":[]}
["Min.One.Percentage","Y"]
[]
["Row Labels","Count of NMIs","Sum of Min.One.Percentage (%)"]
["CN0",2657,0.11855785105527922]
["NH0",2321,0.10356521351121711]
["CS0",2223,9.9192360894199E-2]
["ES0",2199,9.8121458212480278E-2]
["PV0",1640,7.3178349917448385E-2]
["NT0",1559,6.9564053366647699E-2]
["AW0",1335,5.9568961670606296E-2]
["TT0",1301,5.8051849538171441E-2]
["FW0",1044,4.6584266654766796E-2]
["BY0",720,3.2127080451564052E-2]
["EP0",644,2.8735888626121236E-2]
["HB0",619,2.7620364999330814E-2]
["FF0",502,2.239971442595164E-2]
["PTN",501,2.2355093480880023E-2]
["EPN",497,2.2176609700593555E-2]
["NS0",396,1.7669894248360251E-2]
["BD0",386,1.7223684797644082E-2]
["FT0",358,1.597429833563881E-2]
["SHM",342,1.5260363214492942E-2]
["COO",235,1.0485922091829936E-2]
["YVE",207,9.2365356298246635E-3]
["FE0",184,8.2102538931774754E-3]
["SBY",138,6.1576904198830992E-3]
["TMA",104,4.6405782874481254E-3]
["ST0",99,4.4174735620900411E-3]
["TH0",83,3.7035384409441732E-3]
["KLO",61,2.7218776493686116E-3]
["BMS",43,1.9187006380795156E-3]
["(blank)",9,4.0158850564454948E-4]
["SA0",4,1.7848378028646647E-4]
["Grand Total",22411,1.0000000000002025]

{"sheet":"Extreme Low V by DSS contributi","index":8,"n_rows":677,"n_cols":3,"rows_kept":677,"cut":false,"hidden":false,"merged":[]}
["Min.Consecutive.Violation","Y"]
[]
["Row Labels","Count of NMIs","(%)"]
["CHALLIS-JUBILLEE",146,1.3768389287061466E-2]
["ROYAL-MCMAHON",110,1.0373443983402475E-2]
["ANGLISS-ADENEY",110,1.0373443983402475E-2]
["BLENHEIM-WOODS",104,9.807619766125977E-3]
["BENDIGO-ALPINE",102,9.6190116937004775E-3]
["MOUSHALL-HOFFMANS",99,9.3360995850622283E-3]
["WILKINSON-LIBERTY",98,9.2417955488494786E-3]
["MELCOMBE-BANKSIA",91,8.5816672953602305E-3]
["HILBERT-HARRINGTON",90,8.4873632591474808E-3]
["DANIN-AUSTIN",88,8.2987551867219813E-3]
["O'DOWD-HOWARD",83,7.8272350056582327E-3]
["NEWMAN-HOTHAM",80,7.5443228970199826E-3]
["ALEXANDRA-LANDELLS",78,7.3557148245944831E-3]
["MULBERRY-GONA",77,7.2614107883817334E-3]
["AUSTRAL-OAKOVER",77,7.2614107883817334E-3]
["DEAKIN-SPENCER",76,7.1671067521689837E-3]
["CARROL-WHITELAW",74,6.9784986797434842E-3]
["BEATRICE-JENSEN",73,6.8841946435307345E-3]
["DIAMOND-ROSEHILL",68,6.4126744624669859E-3]
["ASHBY-LOCKSLEY",67,6.3183704262542361E-3]
["SOUTH-DERBY",65,6.1297623538287367E-3]
["SYMONS-GILBERT",61,5.7525462089777378E-3]
["ATTERCLIFFE-DERBY",61,5.7525462089777378E-3]
["STEELE-STUART",60,5.658242172764988E-3]
["BOLDREWOOD-McMAHON",59,5.5639381365522383E-3]
["ETZEL-CLYDESDALE",57,5.3753300641267389E-3]
["MYRTLE-REGENT",56,5.2810260279139891E-3]
["STEWART-PASCOE VALE",56,5.2810260279139891E-3]
["CORNISH-LIGAR",56,5.2810260279139891E-3]
["BIMBADEEN-YALLAMBIE",56,5.2810260279139891E-3]
["MOUNT-BELL",55,5.1867219917012394E-3]
["BERRIMA-ROSANNA",55,5.1867219917012394E-3]
["WATT-THE AVENUE",54,5.0924179554884897E-3]
["CUMBERLAND-KENT",54,5.0924179554884897E-3]
["BREARLEY-ROSE",53,4.9981139192757399E-3]
["ANDERSON-BOLINGBROKE",51,4.8095058468502405E-3]
["DELAWARE-MENDIP",51,4.8095058468502405E-3]
["MOUSHALL-NOLAN",50,4.7152018106374908E-3]
["BRADLEY-MASON",50,4.7152018106374908E-3]
["ST HELLIER-UP HEIDELBERG",49,4.620897774424741E-3]
["ORIEL-STANLEY",47,4.4322897019992416E-3]
["O'CONNOR-WHITBY",47,4.4322897019992416E-3]
["PEARL-WHEATSHEAF",47,4.4322897019992416E-3]
["DAISY-BUCKLEY",47,4.4322897019992416E-3]
["WELLINGTON-VICTORIA",46,4.3379856657864918E-3]
["THORPE-WOODS",46,4.3379856657864918E-3]
["YALLAMBIE-LOWER PLENTY",46,4.3379856657864918E-3]
["ALMA-PALMERSTON",46,4.3379856657864918E-3]
["EAST-THACKERAY",46,4.3379856657864918E-3]
["BELGROVE-OVANDO",46,4.3379856657864918E-3]
["HOOPER-DUNVEGAN",46,4.3379856657864918E-3]
["CORNWALL-HIGH SCHOOL",45,4.2436816295737421E-3]
["ESSEX-LANDELLS",45,4.2436816295737421E-3]
["PEEL-DOUGLAS",43,4.0550735571482427E-3]
["BIRDWOOD-KEILOR",43,4.0550735571482427E-3]
["CLIFTON-WATERDALE",43,4.0550735571482427E-3]
["DAVERN-O'HEA",43,4.0550735571482427E-3]
["SOUDAN-HIGH",42,3.9607695209354929E-3]
["MAYFIELD-MUNRO",41,3.8664654847227432E-3]
["DAVID-RACHELLE",41,3.8664654847227432E-3]
["CALA-HAMPTON",41,3.8664654847227432E-3]
["LEVER-GORDON",40,3.7721614485099935E-3]
["RILL-OLIVE",40,3.7721614485099935E-3]
["BEAUCHAMP-HIGH",40,3.7721614485099935E-3]
["QUEEN-RUSSELL",39,3.6778574122972437E-3]
["ARTHUR-FAWKNER",39,3.6778574122972437E-3]
["GRAVES-MARKET",39,3.6778574122972437E-3]
["SEXTON-PARER",38,3.583553376084494E-3]
["KALANG-PLUMPTON",37,3.4892493398717443E-3]
["WOOD-GREENBELT",37,3.4892493398717443E-3]
["EISENHOWER-CHALEYER",37,3.4892493398717443E-3]
["DOUGLAS-PASCOE VALE",37,3.4892493398717443E-3]
["GILBANK-GILBERT",37,3.4892493398717443E-3]
["SHACKELL-BELL",36,3.3949453036589946E-3]
["WESTMINSTER-MILITARY",36,3.3949453036589946E-3]
["QUINN-NOGA",36,3.3949453036589946E-3]
["ANSTEY-PHILLIP",36,3.3949453036589946E-3]
["CHARLES-BENAMBRA",36,3.3949453036589946E-3]
["SUFFOLK-DONGOLA",34,3.2063372312334951E-3]
["RHONDA-CANNING",34,3.2063372312334951E-3]
["PLENTY-RESERVOIR COLLEGE",34,3.2063372312334951E-3]
["WILLIAM-MASON",34,3.2063372312334951E-3]
["BIRDWOOD-REGENT",34,3.2063372312334951E-3]
["ROXBURGH-ROTHWELL",33,3.1120331950207454E-3]
["ALBERT-HARROW",33,3.1120331950207454E-3]
["BRASSEY-PYALONG",33,3.1120331950207454E-3]
["PORTLAND-MUNRO",32,3.0177291588079956E-3]
["SALISBURY-JACK",32,3.0177291588079956E-3]
["THE GLADE-SHERLOWE",31,2.9234251225952459E-3]
["MARY-ROBERTS",31,2.9234251225952459E-3]
["MCCRAE-ELSEY",31,2.9234251225952459E-3]
["MUNRO-ERSKINE",31,2.9234251225952459E-3]
["BROADHURST-MCFADZEAN",31,2.9234251225952459E-3]
["BOSQUET-BALLARAT",31,2.9234251225952459E-3]
["DONCASTER-WALTER",31,2.9234251225952459E-3]
["VICTORY-FOSTERS",30,2.8291210863824962E-3]
["PORTER-DOUGHARTY",30,2.8291210863824962E-3]
["LAUREL-TYLER",30,2.8291210863824962E-3]
["GRENHILDA-DOUGLAS",30,2.8291210863824962E-3]
["STRATHALLAN-WILSON",29,2.7348170501697465E-3]
["LEWIS-WILLIAMS",29,2.7348170501697465E-3]
["JUKES-LANIGAN",29,2.7348170501697465E-3]
["ASHLEY-CENTRAL WEST NO.1",29,2.7348170501697465E-3]
["CARWARP-ERSKINE",29,2.7348170501697465E-3]
["DARLING-WHITE",29,2.7348170501697465E-3]
["WARATAH-DERBY",28,2.6405130139569967E-3]
["PALMER-HEDLEY",28,2.6405130139569967E-3]
["LAWLEY-GLASGOW",28,2.6405130139569967E-3]
["JACK-FORD",28,2.6405130139569967E-3]
["CLIFTON-JEAN",28,2.6405130139569967E-3]
["CAROLE JOY-SPRING",28,2.6405130139569967E-3]
["FORRESTER-HEDDERWICK",27,2.546208977744247E-3]
["ARGYLE-BROAD",27,2.546208977744247E-3]
["BRADSHAW-MARY",27,2.546208977744247E-3]
["CANTALA-MCCRAE",27,2.546208977744247E-3]
["DAVID-NORTH",27,2.546208977744247E-3]
["RUSSELL-BARKLY",26,2.4519049415314973E-3]
["PAMELA-HERBERT",26,2.4519049415314973E-3]
["THE CROSSWAY-PARK",26,2.4519049415314973E-3]
["SUSSEX-HOLMES",26,2.4519049415314973E-3]
["FLETCHER-PASCOE VALE",26,2.4519049415314973E-3]
["JOHN-WINIFRED",26,2.4519049415314973E-3]
["HODGSON-AVOCA",26,2.4519049415314973E-3]
["CENTRE-HOWARD",26,2.4519049415314973E-3]
["BERRY-KEILOR",26,2.4519049415314973E-3]
["ANGLISS-SANDERSON",26,2.4519049415314973E-3]
["HANSEN-GLAMIS",26,2.4519049415314973E-3]
["CHARTERIS-BURKE",26,2.4519049415314973E-3]
["CLYDEBANK-AFTON",26,2.4519049415314973E-3]
["CAMDON-NORTON",26,2.4519049415314973E-3]
["YALLAMBIE-JANICE",25,2.3576009053187475E-3]
["MACK-PICKETT",25,2.3576009053187475E-3]
["LEBANON-FENACRE",25,2.3576009053187475E-3]
["YALLAMBIE-WENDOVER",25,2.3576009053187475E-3]
["MCCOLL-MALPAS",25,2.3576009053187475E-3]
["YARRA-DOVER",25,2.3576009053187475E-3]
["LENNOX-HYDE",25,2.3576009053187475E-3]
["WATERDALE-GRIFFITHS",25,2.3576009053187475E-3]
["HOTHAM-RYDER No. 2",25,2.3576009053187475E-3]
["CHEDDAR-JINGHI",25,2.3576009053187475E-3]
["BLACKSHAWS-ELIZABETH",25,2.3576009053187475E-3]
["FERGUSON-ROSEBERRY",25,2.3576009053187475E-3]
["NEWLANDS-MURRAY",24,2.2632968691059978E-3]
["OLIVE-SYLVAN",24,2.2632968691059978E-3]
["MALCOLM-ELIZABETH",24,2.2632968691059978E-3]
["WEST-JOHN",24,2.2632968691059978E-3]
["HILLSIDE-HURTLE",24,2.2632968691059978E-3]
["GRAHAM-WOODLANDS",24,2.2632968691059978E-3]
["GLENMORE-KINLOCK",24,2.2632968691059978E-3]
["SEVERN-BENBOW",23,2.1689928328932481E-3]
["LANDELLS-MARTIN",23,2.1689928328932481E-3]
["WAVERLEY-HOLMES",23,2.1689928328932481E-3]
["WILLIAM-JUNCTION",23,2.1689928328932481E-3]
["ROSELAND-IVANHOE",23,2.1689928328932481E-3]
["DORSET-BERKELEY",23,2.1689928328932481E-3]
["HILLSIDE-ROBERTS",23,2.1689928328932481E-3]
["GREENWOOD-O'HEA",23,2.1689928328932481E-3]
["ARTHUR-ELIZABETH",23,2.1689928328932481E-3]
["FLORENCE-LINCOLN",23,2.1689928328932481E-3]
["WATERDALE-LLOYD",22,2.0746887966804984E-3]
["RICHARDS-BELL",22,2.0746887966804984E-3]
["KEADY-SYDNEY",22,2.0746887966804984E-3]
["SEPARATION-PERRY",22,2.0746887966804984E-3]
["GEELONG-QUEENSVILLE",22,2.0746887966804984E-3]
["GREEN-SPARKFORD",22,2.0746887966804984E-3]
["FETTLING-COOPER",22,2.0746887966804984E-3]
["CHAPMAN-BELAIR",22,2.0746887966804984E-3]
["ALMA-CHANDLER",22,2.0746887966804984E-3]
["GRANGE-CRAMER",22,2.0746887966804984E-3]
["NEWSOM-STANFORD",21,1.9803847604677486E-3]
["RICHELIEU-ESSEX",21,1.9803847604677486E-3]
["BOND-ORIEL",21,1.9803847604677486E-3]
["BUCKLEY-THE CROSSWAY",21,1.9803847604677486E-3]
["CUDGEWA-BORVA",21,1.9803847604677486E-3]
["BRAIDHILL-WINDSOR",21,1.9803847604677486E-3]
["ALPHINGTON-PARK",21,1.9803847604677486E-3]
["CHALLIS-SPEIGHT",21,1.9803847604677486E-3]
["GOULBURN-SHAND",21,1.9803847604677486E-3]
["QUINN-CLARKS",20,1.8860807242549987E-3]
["MARIE-MURPHY",20,1.8860807242549987E-3]
["KINGSTON-COLLINSON",20,1.8860807242549987E-3]
["REYNARD-SPRINGHALL",20,1.8860807242549987E-3]
["ASH-WIDFORD",20,1.8860807242549987E-3]
["HOME-WILKINSON",20,1.8860807242549987E-3]
["ADELINE-KOROROIT",20,1.8860807242549987E-3]
["ARBOR-MACEY",20,1.8860807242549987E-3]
["CASTLETON 21-HAVILAH",20,1.8860807242549987E-3]
["DOYLE-NORTH",20,1.8860807242549987E-3]
["LALUMA-MCCARRON",19,1.7917766880422487E-3]
["THE FAIRWAY-DUNNE",19,1.7917766880422487E-3]
["O'HEA-CUMBERLAND",19,1.7917766880422487E-3]
["BREARLEY-BALMORAL",19,1.7917766880422487E-3]
["DARLINGTON-RENNIE",19,1.7917766880422487E-3]
["CAPE-YARRA",19,1.7917766880422487E-3]
["ARTHUR-SEPARATION",19,1.7917766880422487E-3]
["COHEN-GROVES",19,1.7917766880422487E-3]
["HENTY-GILBERT",19,1.7917766880422487E-3]
["OMAR-MITCHELL",18,1.6974726518294988E-3]
["MARGTMARY-MURRAY",18,1.6974726518294988E-3]
["PARKLANDS-KELVIN",18,1.6974726518294988E-3]
["MITCHELL-HACKETT",18,1.6974726518294988E-3]
["FORRESTER-COOPER",18,1.6974726518294988E-3]
["BERRY-LORNE",18,1.6974726518294988E-3]
["ALMOND-CONIFER",18,1.6974726518294988E-3]
["GRANDVIEW-HOLMES",18,1.6974726518294988E-3]
["COLE-OSBORNE",18,1.6974726518294988E-3]
["HAWKHURST-FRANCIS",18,1.6974726518294988E-3]
["RYDER-NOLAN",17,1.6031686156167489E-3]
["WINGROVE-KELVIN",17,1.6031686156167489E-3]
["ROBERTS-MCNAMARA",17,1.6031686156167489E-3]
["WOODLAND-NAPIER",17,1.6031686156167489E-3]
["SALWEEN-ELSA",17,1.6031686156167489E-3]
["SUSSEX-BANYULE",17,1.6031686156167489E-3]
["VIEWBANK-BREES",17,1.6031686156167489E-3]
["OUTHWAITE-ORIEL",17,1.6031686156167489E-3]
["CRESWICK-LATROBE",17,1.6031686156167489E-3]
["HUNT-BAXTER",17,1.6031686156167489E-3]
["CHARLES-EPSOM",17,1.6031686156167489E-3]
["DARVALL-WAIORA",17,1.6031686156167489E-3]
["JULIET-BENT",17,1.6031686156167489E-3]
["TOWER-HEIDELBERG",16,1.5088645794039989E-3]
["PASCOE VALE-BENDOC",16,1.5088645794039989E-3]
["SEPARATION-FULHAM",16,1.5088645794039989E-3]
["BOND-ATHELSTANE",16,1.5088645794039989E-3]
["HILTON-WIDFORD",16,1.5088645794039989E-3]
["BAXTER-SYDNEY",16,1.5088645794039989E-3]
["CARTWRIGHT-PASCOE VALE",16,1.5088645794039989E-3]
["PERIGRINE-DEEP CREEK",15,1.414560543191249E-3]
["KNOX-GILBERT",15,1.414560543191249E-3]
["NEWCASTLE-ELIZABETH",15,1.414560543191249E-3]
["ANDERSON-BEVERLEY",15,1.414560543191249E-3]
["HEATHER-DINAH",15,1.414560543191249E-3]
["EFFINGHAM-WILKINS",15,1.414560543191249E-3]
["BLOOMFIELD-ROSAMOND",15,1.414560543191249E-3]
["JACKSON-THOMSON",15,1.414560543191249E-3]
["JOFFRE-KENT",15,1.414560543191249E-3]
["DENYS-GLYNDA",15,1.414560543191249E-3]
["WALKER-NEWCASTLE",14,1.320256506978499E-3]
["KENNEDY-CHAPMAN",14,1.320256506978499E-3]
["WOODS-CHALLIS",14,1.320256506978499E-3]
["WOOD-BROWN",14,1.320256506978499E-3]
["NOVIAN-MARAMA",14,1.320256506978499E-3]
["PASCOE-BLACK",14,1.320256506978499E-3]
["SOMERVILLE-JULIAN",14,1.320256506978499E-3]
["ST LEONARDS-EPSOM",14,1.320256506978499E-3]
["JUSTIN-VIEW",14,1.320256506978499E-3]
["ALMA-YARRA",14,1.320256506978499E-3]
["HAWTHORN-REYNARD",14,1.320256506978499E-3]
["GREVILLE-KEILOR",14,1.320256506978499E-3]
["CHISHOLM-ERINBANK",14,1.320256506978499E-3]
["DARLING-FULHAM",14,1.320256506978499E-3]
["GELLIBRAND-STEWART",14,1.320256506978499E-3]
["AYR-DAREBIN",14,1.320256506978499E-3]
["BURNS-WAVERLEY",14,1.320256506978499E-3]
["JENNINGS-ARDMILLAN",14,1.320256506978499E-3]
["NEAL-DINAH",13,1.2259524707657491E-3]
["WEST-KINGSLEY",13,1.2259524707657491E-3]
["WALHALLA-MORELAND",13,1.2259524707657491E-3]
["WHITE-CHEDDAR",13,1.2259524707657491E-3]
["LIBERTY-PERKINS",13,1.2259524707657491E-3]
["ROSS-ELIZABETH",13,1.2259524707657491E-3]
["ALTONA-ORIEL",13,1.2259524707657491E-3]
["ANGUS-MIDDLE",13,1.2259524707657491E-3]
["HOLDEN-MILITARY",13,1.2259524707657491E-3]
["CHRISTINA-BARBARA",13,1.2259524707657491E-3]
["CATHERINE-SAINSBURY",13,1.2259524707657491E-3]
["TREADWELL-DUDLEY",12,1.1316484345529991E-3]
["TONKIN-SUSSEX",12,1.1316484345529991E-3]
["ROGERSON-THOMPSON",12,1.1316484345529991E-3]
["LYDIA-DUNSTAN",12,1.1316484345529991E-3]
["PICKETT-HICKFORD",12,1.1316484345529991E-3]
["WILLOW-LINDA",12,1.1316484345529991E-3]
["RIVIERA-WARRICK",12,1.1316484345529991E-3]
["MARGARET-WINIFRED",12,1.1316484345529991E-3]
["ROSENTHAL-ALLENBY",12,1.1316484345529991E-3]
["LEBANON-ELDORADO",12,1.1316484345529991E-3]
["ZAMMIT-O'HAIRE",12,1.1316484345529991E-3]
["STEWART-OSBORNE",12,1.1316484345529991E-3]
["JELLICOE-WATERDALE",12,1.1316484345529991E-3]
["CAPRICORN-PALMERSTON",12,1.1316484345529991E-3]
["BURGESS-GILBERT",12,1.1316484345529991E-3]
["ESSEX-DUDLEY",12,1.1316484345529991E-3]
["DOYLE-RIDLEY",12,1.1316484345529991E-3]
["HUDSONS-HICK",12,1.1316484345529991E-3]
["DONCASTER-MYROSS",12,1.1316484345529991E-3]
["GENEVA-COMO",12,1.1316484345529991E-3]
["FRANCIS-VINCENT",12,1.1316484345529991E-3]
["JACKA-MCCRACKEN",12,1.1316484345529991E-3]
["GYLES-ESSEX",12,1.1316484345529991E-3]
["CULLEN-MARY",12,1.1316484345529991E-3]
["FULLARTON-WALTERS",12,1.1316484345529991E-3]
["MCDONALD-GAFFNEY",11,1.0373443983402492E-3]
["NORTH-THOMAS",11,1.0373443983402492E-3]
["WESTMERE-WARNE",11,1.0373443983402492E-3]
["KILMORE-CHARLTON",11,1.0373443983402492E-3]
["MIRAMS-UNION",11,1.0373443983402492E-3]
["LAURIE-PURINUAN",11,1.0373443983402492E-3]
["SALISBURY-WILLIAMSTOWN",11,1.0373443983402492E-3]
["SYDNEY-ROSSHIRE",11,1.0373443983402492E-3]
["MORRIS-MCMAHONS",11,1.0373443983402492E-3]
["HOFFMANS-KEILOR",11,1.0373443983402492E-3]
["HILLCREST-ROYAL",11,1.0373443983402492E-3]
["GLOUCESTER-HENTY",11,1.0373443983402492E-3]
["BUNBURY-DOUGLAS",11,1.0373443983402492E-3]
["COOMA-GOWER",11,1.0373443983402492E-3]
["HAIG-GILBERT",11,1.0373443983402492E-3]
["PLUNKETT-O'KEEFE",10,9.4304036212749924E-4]
["TONKIN-MASHOOBRA",10,9.4304036212749924E-4]
["KATHLEEN-WOOD",10,9.4304036212749924E-4]
["OLIVE-VIOLA",10,9.4304036212749924E-4]
["VISION-MASCOMA",10,9.4304036212749924E-4]
["YORK- EASTGATE",10,9.4304036212749924E-4]
["WARRAGUL-LISMORE",10,9.4304036212749924E-4]
["REDGUM-DEEP CREEK",10,9.4304036212749924E-4]
["POWELL-EXCELSIOR",10,9.4304036212749924E-4]
["RIDGEWAY-MARRSON",10,9.4304036212749924E-4]
["PHILLIP-STRACHEN",10,9.4304036212749924E-4]
["BLACK-MC MAHON",10,9.4304036212749924E-4]
["HAWKER-COOK",10,9.4304036212749924E-4]
["ASQUITH-STURDEE",10,9.4304036212749924E-4]
["HESLEDEN-AMELIA",10,9.4304036212749924E-4]
["DAVIS-MILITARY",10,9.4304036212749924E-4]
["GRAHAM-ULRICH",10,9.4304036212749924E-4]
["DUNDEE-MEADE",10,9.4304036212749924E-4]
["GREENSBOROUGH-YALLAMBIE",10,9.4304036212749924E-4]
["HAUGHTON-GREVILLE",10,9.4304036212749924E-4]
["JENNIFER-ANDERSON",10,9.4304036212749924E-4]
["ANTHONY-BELLAIR",10,9.4304036212749924E-4]
["HODDLE-FLETCHER",10,9.4304036212749924E-4]
["CLARENDON-WHITTAKER",10,9.4304036212749924E-4]
["EIRENE-FRANCIS",10,9.4304036212749924E-4]
["HENLEY-CLARKE",10,9.4304036212749924E-4]
["EVELL-OGDEN",10,9.4304036212749924E-4]
["BECCLES-ANDERSON",10,9.4304036212749924E-4]
["HAMLYN-VIDA",10,9.4304036212749924E-4]
["CENTRE WAY-FRAN",10,9.4304036212749924E-4]
["BOLINGBROKE-BURGUNDY",10,9.4304036212749924E-4]
["KERNAN-CARNARVON",9,8.4873632591474929E-4]
["ROSEHILL-ROSE",9,8.4873632591474929E-4]
["REYNARD-DONNE",9,8.4873632591474929E-4]
["LEAKE-RICHARDSON",9,8.4873632591474929E-4]
["SHERWOOD-THORESBY",9,8.4873632591474929E-4]
["THE ESPLANADE-PLANTATION",9,8.4873632591474929E-4]
["MCNAMARA-ROBERTS",9,8.4873632591474929E-4]
["MONASH-BONAR",9,8.4873632591474929E-4]
["WINDSOR-CECIL",9,8.4873632591474929E-4]
["TIERNAN-RAGLAN",9,8.4873632591474929E-4]
["OXFORD-JUNCTION",9,8.4873632591474929E-4]
["BEETHAM-PROSPECT",9,8.4873632591474929E-4]
["BROWNING-SCOTT",9,8.4873632591474929E-4]
["BELMONT-BAYSWATER",9,8.4873632591474929E-4]
["ARDEN-LOWER PLENTY",9,8.4873632591474929E-4]
["FORRESTER-DEAKIN",9,8.4873632591474929E-4]
["EGLINTON-ARGYLE",9,8.4873632591474929E-4]
["HOBSON-HOME",9,8.4873632591474929E-4]
["COURTIS-MELBOURNE",9,8.4873632591474929E-4]
["LLOYD-MONASH",8,7.5443228970199934E-4]
["THOMPSON-NORTH",8,7.5443228970199934E-4]
["NUNAN-KIRBY",8,7.5443228970199934E-4]
["THE RIDGE-DEEP CREEK 5",8,7.5443228970199934E-4]
["WOLSELEY-THE AVENUE",8,7.5443228970199934E-4]
["LOCKHEED-BOEING",8,7.5443228970199934E-4]
["SALMON-NAPIER",8,7.5443228970199934E-4]
["QUINN-ST. JAMES",8,7.5443228970199934E-4]
["MIDDLE-ASCOT VALE",8,7.5443228970199934E-4]
["SNELL-WATT",8,7.5443228970199934E-4]
["WINSTON-JASON",8,7.5443228970199934E-4]
["SHEFFIELD-MAY",8,7.5443228970199934E-4]
["SANDERSON-ROBERTS",8,7.5443228970199934E-4]
["PRINCE-KEILOR",8,7.5443228970199934E-4]
["PROSPECT-BUCKLEY",8,7.5443228970199934E-4]
["LOWSON-TYSON",8,7.5443228970199934E-4]
["WARD-LOUISVILLE",8,7.5443228970199934E-4]
["SOMERS-HINKLER",8,7.5443228970199934E-4]
["JOHNSTON-NEWCASTLE",8,7.5443228970199934E-4]
["FERGUSON-TOWNHALL",8,7.5443228970199934E-4]
["GOULBURN-PALMERSTON",8,7.5443228970199934E-4]
["BRAY-BARTROP",8,7.5443228970199934E-4]
["FINLAYSON-BRAIDHILL",8,7.5443228970199934E-4]
["DORRINGTON-PLENTY",8,7.5443228970199934E-4]
["MARKS-YORK",7,6.601282534892494E-4]
["MAGDALA-WOODLAND",7,6.601282534892494E-4]
["LIVINGSTONE-ELIZABETH",7,6.601282534892494E-4]
["PARK-COMBERMERE",7,6.601282534892494E-4]
["RUTHVEN-WAIORA",7,6.601282534892494E-4]
["TENNYSON-TYLER",7,6.601282534892494E-4]
["MIHIL-VICTORIA",7,6.601282534892494E-4]
["YARRALEA-GIBSON",7,6.601282534892494E-4]
["WEBB-CORONATION",7,6.601282534892494E-4]
["MCCOLL-TYLER",7,6.601282534892494E-4]
["ROBERN-ROSEBUD",7,6.601282534892494E-4]
["OAK-CONISTON",7,6.601282534892494E-4]
["ROSEHILL-TALBOT",7,6.601282534892494E-4]
["YORK-NAPIER",7,6.601282534892494E-4]
["FULHAM-WINGROVE",7,6.601282534892494E-4]
["DRESS CIRCLE-THE RIDGE 1",7,6.601282534892494E-4]
["HALSEY-RADFORD",7,6.601282534892494E-4]
["GREENACRE-AYLESBURY",7,6.601282534892494E-4]
["CENTREWAY-WINGARA",7,6.601282534892494E-4]
["DOLE-LOCHER",7,6.601282534892494E-4]
["CHARTERIS-WARNCLIFFE",7,6.601282534892494E-4]
["CAMBRIAN-HIGH",7,6.601282534892494E-4]
["DARLING-EGLINTON",7,6.601282534892494E-4]
["FENTON-MYRNONG",7,6.601282534892494E-4]
["BULLA-DUBLIN",7,6.601282534892494E-4]
["DRESS CIRCLE-THE RIDGE 2",7,6.601282534892494E-4]
["THISTLE-HACKETT",6,5.6582421727649945E-4]
["THE CROSSWAY-UPLAND",6,5.6582421727649945E-4]
["STEVEDORE-STRAND",6,5.6582421727649945E-4]
["WARANGA-BLAIR",6,5.6582421727649945E-4]
["MOONEE-VALLEY",6,5.6582421727649945E-4]
["MOYANGUL-GUNGARLAN",6,5.6582421727649945E-4]
["WOOD-LUNETTE",6,5.6582421727649945E-4]
["WATERDALE-THE BOULEVARD",6,5.6582421727649945E-4]
["RATHCOWN-CHEDDAR",6,5.6582421727649945E-4]
["PARKVIEW-HEIDELBERG",6,5.6582421727649945E-4]
["IVAN-MASCOMA",6,5.6582421727649945E-4]
["BRUNEL-TRUMAN",6,5.6582421727649945E-4]
["ARNCLIFFE-WATERHOUSE",6,5.6582421727649945E-4]
["FLINDERS-THE WALK",6,5.6582421727649945E-4]
["INTERVALE-ARCADE",6,5.6582421727649945E-4]
["FLOWER-BUCKLEY",6,5.6582421727649945E-4]
["JUDITH-BREES",6,5.6582421727649945E-4]
["BOND-LIBERTY",6,5.6582421727649945E-4]
["BLANDFORD-ESSEX",6,5.6582421727649945E-4]
["GIFFARD-OSBORNE",6,5.6582421727649945E-4]
["BUCKLEY-ABERDEEN",6,5.6582421727649945E-4]
["ALEXANDER-JOHN",6,5.6582421727649945E-4]
["INVERMAY-BELLEVUE",6,5.6582421727649945E-4]
["BANKSIA-GLENARD",6,5.6582421727649945E-4]
["ALOHA-GREENE",6,5.6582421727649945E-4]
["HANSON-GOBLE",6,5.6582421727649945E-4]
["ERIC-ADA",6,5.6582421727649945E-4]
["ATHELSTANE-ROBBINS",6,5.6582421727649945E-4]
["ERINBANK-DOBIES",6,5.6582421727649945E-4]
["REYNARD-PHILLIPS",5,4.7152018106374951E-4]
["STUART-ORMOND",5,4.7152018106374951E-4]
["SEVERN-SOMERVILLE",5,4.7152018106374951E-4]
["NORTH-RICHMOND",5,4.7152018106374951E-4]
["SCOTIA-BELL",5,4.7152018106374951E-4]
["NEILL-MOUNSEY",5,4.7152018106374951E-4]
["REYNARD-ROYAL",5,4.7152018106374951E-4]
["THE BOULEVARD-GILBERT",5,4.7152018106374951E-4]
["WINN-MAJOR",5,4.7152018106374951E-4]
["VANBERG-TENNYSON",5,4.7152018106374951E-4]
["SYDNEY-MURRAY",5,4.7152018106374951E-4]
["KINGSLEY-ROBERTS",5,4.7152018106374951E-4]
["SECOND-EVE",5,4.7152018106374951E-4]
["PARK-PENLEIGH",5,4.7152018106374951E-4]
["LATROBE-YARRA",5,4.7152018106374951E-4]
["ROSENTHAL-HUGHES",5,4.7152018106374951E-4]
["MCIVOR-OAKHILL",5,4.7152018106374951E-4]
["THE RIDGE-DEEP CREEK 1",5,4.7152018106374951E-4]
["NORTHERNHAY-OAKHILL",5,4.7152018106374951E-4]
["THE RIDGE-DEEP CREEK 3",5,4.7152018106374951E-4]
["STEVEDORE-DOVER",5,4.7152018106374951E-4]
["STANGER-ADENEY",5,4.7152018106374951E-4]
["BANNON-RETREAT",5,4.7152018106374951E-4]
["INVERMAY-MT IDA",5,4.7152018106374951E-4]
["ALBERT-DUNDAS",5,4.7152018106374951E-4]
["BAMFIELD-COLLINS",5,4.7152018106374951E-4]
["ELDORADO-STRELDON",5,4.7152018106374951E-4]
["FREYER-POWER",5,4.7152018106374951E-4]
["HILLSYDE-LOEMAN",5,4.7152018106374951E-4]
["CAMPBELL-DE CARLE",5,4.7152018106374951E-4]
["EARL-GRANGE",5,4.7152018106374951E-4]
["GREVILLIA-ALBERT",5,4.7152018106374951E-4]
["CLARKE-RUPERT",5,4.7152018106374951E-4]
["DEAKIN-BERRY",5,4.7152018106374951E-4]
["DEAKIN-BUCKLEY",5,4.7152018106374951E-4]
["BURTON-OAKLAND",5,4.7152018106374951E-4]
["NOTTINGHAM-RACECOURSE",4,3.7721614485099962E-4]
["OUTHWAITE-MCEWAN",4,3.7721614485099962E-4]
["MENARRA-LAMART",4,3.7721614485099962E-4]
["RIVER-HOME",4,3.7721614485099962E-4]
["REGINA-BELLEVUE",4,3.7721614485099962E-4]
["KENNY-COGHILL",4,3.7721614485099962E-4]
["THE RIDGE-DEEP CREEK 4",4,3.7721614485099962E-4]
["THE BOULEVARD-PARKSTONE",4,3.7721614485099962E-4]
["TURNER-MENZIES",4,3.7721614485099962E-4]
["PUNJEL-CALDER",4,3.7721614485099962E-4]
["KELVIN-ALBERT",4,3.7721614485099962E-4]
["ROYAL-BULLA",4,3.7721614485099962E-4]
["PINE-HENTY",4,3.7721614485099962E-4]
["THE GRANGE-YALLAMBIE",4,3.7721614485099962E-4]
["ST KINNORD-ALMA",4,3.7721614485099962E-4]
["THE RIDGE-DEEP CREEK 2",4,3.7721614485099962E-4]
["LANTANA-IVANHOE",4,3.7721614485099962E-4]
["JACKA-JOYNT",4,3.7721614485099962E-4]
["ARCADE-SOUTH GATEWAY",4,3.7721614485099962E-4]
["ASHLEY-EDWARDES",4,3.7721614485099962E-4]
["JUNE-MCBRYDE",4,3.7721614485099962E-4]
["BONVIEW-CARRINGTON",4,3.7721614485099962E-4]
["BEVERLEY-GREVILLE",4,3.7721614485099962E-4]
["ELLESMERE-INVERMAY",4,3.7721614485099962E-4]
["CHATFIELD-KINGSVILLE",4,3.7721614485099962E-4]
["ELLESMERE-CARRICK",4,3.7721614485099962E-4]
["FRIER-PLENTY",4,3.7721614485099962E-4]
["FINN-HAUGHTON",4,3.7721614485099962E-4]
["FARM-HOME",4,3.7721614485099962E-4]
["ST JAMES-WOBURN",3,2.8291210863824973E-4]
["MONARCH-EAGLEVIEW",3,2.8291210863824973E-4]
["KNIGHT-BAYVIEW",3,2.8291210863824973E-4]
["LANDY-LICHFIELD",3,2.8291210863824973E-4]
["THE BOULEVARD-WARNCLIFFE",3,2.8291210863824973E-4]
["PERRY-VERDON",3,2.8291210863824973E-4]
["THE AVENUE-KEILOR",3,2.8291210863824973E-4]
["YERING-GUILDFORD",3,2.8291210863824973E-4]
["LAWSON-SALISBURY",3,2.8291210863824973E-4]
["THE EYRIE-SUMMIT",3,2.8291210863824973E-4]
["MCNAMARA-RUTHVEN",3,2.8291210863824973E-4]
["VALLEY LAKE-STEELE CREEK",3,2.8291210863824973E-4]
["WILTSHIRE-DUNFIELD",3,2.8291210863824973E-4]
["SCHOOL-TRAP",3,2.8291210863824973E-4]
["(blank)",3,2.8291210863824973E-4]
["MYDDLETON-GRACE",3,2.8291210863824973E-4]
["THE BOULEVARD-AFTON",3,2.8291210863824973E-4]
["TRACEY-ELLIOT",3,2.8291210863824973E-4]
["IVANHOE-WESTLEY",3,2.8291210863824973E-4]
["GELLIBRAND-VICTORIA",3,2.8291210863824973E-4]
["BROMYARD-DREW",3,2.8291210863824973E-4]
["GRAHAM 138-SYLVIA",3,2.8291210863824973E-4]
["DUNFIELD-BERESFORD",3,2.8291210863824973E-4]
["BOURNIAN-GRAMMAR",3,2.8291210863824973E-4]
["EDWIN-ST HELLIER",3,2.8291210863824973E-4]
["FORDHAM-STRATHMERTON",3,2.8291210863824973E-4]
["BROWN-ROSANNA",3,2.8291210863824973E-4]
["FULLWOOD-WHEELER",3,2.8291210863824973E-4]
["HOLROYD-O'HEA",3,2.8291210863824973E-4]
["DEEP CREEK-PERIGRINE",3,2.8291210863824973E-4]
["IRVINE-GAFFNEY",3,2.8291210863824973E-4]
["ESSEX-DOWNS",3,2.8291210863824973E-4]
["FIRST-BARKLY",3,2.8291210863824973E-4]
["BIZANA-FONTEIN",3,2.8291210863824973E-4]
["BARDWELL DR-P11",3,2.8291210863824973E-4]
["CONIFER-PRIMULA",3,2.8291210863824973E-4]
["ERSKINE-ARGYLL",3,2.8291210863824973E-4]
["PITT-MAJOR",2,1.8860807242549981E-4]
["PRESTON-MUNRO",2,1.8860807242549981E-4]
["STANFORD-NORTH WEALD",2,1.8860807242549981E-4]
["MCIVOR-KIEWA",2,1.8860807242549981E-4]
["KONAGADERRA RD-P39E2",2,1.8860807242549981E-4]
["MOUNT-YARRA",2,1.8860807242549981E-4]
["VALLEY-AUGUSTINE",2,1.8860807242549981E-4]
["PARKER-AITKEN",2,1.8860807242549981E-4]
["MCKENNA-MILITARY",2,1.8860807242549981E-4]
["THE BOULEVARD-NEVILLE",2,1.8860807242549981E-4]
["TYRELL-MCBRYDE",2,1.8860807242549981E-4]
["WUNNAMURRA-WONGANELA",2,1.8860807242549981E-4]
["UP H'BERG-ST HELLIER",2,1.8860807242549981E-4]
["NIMMO-BUCKLEY",2,1.8860807242549981E-4]
["STEWART-LITTLE OSBORNE",2,1.8860807242549981E-4]
["RENOWN-KERFERD",2,1.8860807242549981E-4]
["VICTORIA-RAILWAY",2,1.8860807242549981E-4]
["KONAGADERRA RD-P42E1",2,1.8860807242549981E-4]
["WOORITE-MILLEARA",2,1.8860807242549981E-4]
["KONAGADERRA RD-P46E2",2,1.8860807242549981E-4]
["SHEFFIELD-COBURG",2,1.8860807242549981E-4]
["STEELE CREEK-BASALT",2,1.8860807242549981E-4]
["PETERSON-JACKSON",2,1.8860807242549981E-4]
["NELSON-LYON",2,1.8860807242549981E-4]
["BEDWELL-HUGHES",2,1.8860807242549981E-4]
["GALLERY GATE-PERONINE",2,1.8860807242549981E-4]
["BASIL-WOODS",2,1.8860807242549981E-4]
["CARR-NEWLANDS",2,1.8860807242549981E-4]
["DALKEITH-GORDON",2,1.8860807242549981E-4]
["BEDFORD-PARER",2,1.8860807242549981E-4]
["COLLINS-WATERDALE",2,1.8860807242549981E-4]
["DREDGE-TORMEY",2,1.8860807242549981E-4]
["HAWKER-MCNAMARA",2,1.8860807242549981E-4]
["GRANDVIEW-LONGVIEW",2,1.8860807242549981E-4]
["GLASGOW-HIGH",2,1.8860807242549981E-4]
["DEEP CREEK-REDGUM",2,1.8860807242549981E-4]
["CLAYTON-MASCOMA",2,1.8860807242549981E-4]
["COLLINGWOOD-DOUGLAS",2,1.8860807242549981E-4]
["BELLEVUE-DAVIES",2,1.8860807242549981E-4]
["BAYVIEW-MARIBYRNONG",2,1.8860807242549981E-4]
["DICKERSON-TUCKER",2,1.8860807242549981E-4]
["HAYES-HOUSTON",2,1.8860807242549981E-4]
["GARNET-IDA",2,1.8860807242549981E-4]
["MONZA-FLORENCE",1,9.4304036212749905E-5]
["MOUNTAIN VIEW-DAVIES",1,9.4304036212749905E-5]
["WAIORA-CHURCHILL",1,9.4304036212749905E-5]
["RAMSAY-FAWKNER",1,9.4304036212749905E-5]
["PERRY-GORDON",1,9.4304036212749905E-5]
["REGENT-HIGH",1,9.4304036212749905E-5]
["NAPIER-BUTLER",1,9.4304036212749905E-5]
["STRATHMERTON-LEISURE CENTRE",1,9.4304036212749905E-5]
["LOWSON-MINONA",1,9.4304036212749905E-5]
["WARRENS BROOK-SPEARGRASS",1,9.4304036212749905E-5]
["PINE-MARSHALL",1,9.4304036212749905E-5]
["MILLER-HORNE",1,9.4304036212749905E-5]
["LANGDON-PETERLEE",1,9.4304036212749905E-5]
["LEVER-QUEEN",1,9.4304036212749905E-5]
["MCFADZEAN-HURLEY",1,9.4304036212749905E-5]
["RENNIE-JOHN",1,9.4304036212749905E-5]
["VINCENT-BELL",1,9.4304036212749905E-5]
["NICHOLSON-LYONS",1,9.4304036212749905E-5]
["LOCKSLEY-KINSALE",1,9.4304036212749905E-5]
["ROSAMOND-RIVER",1,9.4304036212749905E-5]
["SCOTT-PARK",1,9.4304036212749905E-5]
["TUCKER-LYNCH",1,9.4304036212749905E-5]
["RUTHERFORD-LILLIAN",1,9.4304036212749905E-5]
["MCBRYDE 134-MAJOR",1,9.4304036212749905E-5]
["SIM-GEORGE",1,9.4304036212749905E-5]
["WESTGATE-HATTER",1,9.4304036212749905E-5]
["MCCRACKEN-BUCKLEY",1,9.4304036212749905E-5]
["KONAGADERRA RD-P42E3",1,9.4304036212749905E-5]
["SANDOVER-SALWEEN",1,9.4304036212749905E-5]
["SHADFORTH-RALEIGH",1,9.4304036212749905E-5]
["MOONEE-ASCOT VALE",1,9.4304036212749905E-5]
["UNION-GILBERT",1,9.4304036212749905E-5]
["MARIBYRNONG-WALTER",1,9.4304036212749905E-5]
["LACY-CANNING",1,9.4304036212749905E-5]
["MERBEIN-SUSSEX",1,9.4304036212749905E-5]
["SHEPPARD-SHORTS",1,9.4304036212749905E-5]
["ROBESON-KENDALL",1,9.4304036212749905E-5]
["WHITE-DUKE",1,9.4304036212749905E-5]
["PAINE-LATROBE",1,9.4304036212749905E-5]
["WHITELAW-BOLDREWOOD",1,9.4304036212749905E-5]
["ORIEL-HAWKER",1,9.4304036212749905E-5]
["WILDWOOD RD S-P16",1,9.4304036212749905E-5]
["ORIEL-TOBRUK",1,9.4304036212749905E-5]
["WILFRED-CEDRIC",1,9.4304036212749905E-5]
["RALEIGH-WILLS",1,9.4304036212749905E-5]
["WILFRED-LOWER HEIDELBERG",1,9.4304036212749905E-5]
["SCOVELL-CATHCART",1,9.4304036212749905E-5]
["VALENCIA-MELBOURNE",1,9.4304036212749905E-5]
["STATION-HAMILTON",1,9.4304036212749905E-5]
["RIDDELL RD-P106E1",1,9.4304036212749905E-5]
["COLTHUR-BANBURY",1,9.4304036212749905E-5]
["BARDWELL DR-P15E2",1,9.4304036212749905E-5]
["ASHLEY-NAPOLEON",1,9.4304036212749905E-5]
["GOSFORD-NICHOLAS",1,9.4304036212749905E-5]
["BRASSEY CRT-P5E2",1,9.4304036212749905E-5]
["HIGH 883-MELB WATER",1,9.4304036212749905E-5]
["HEMAR-BRAMSHAW",1,9.4304036212749905E-5]
["ALBERT 62-OVANDO",1,9.4304036212749905E-5]
["EASTGATE-HOTHLYN",1,9.4304036212749905E-5]
["HILLCREST-PLUMPTON",1,9.4304036212749905E-5]
["GREEN-STYMIE",1,9.4304036212749905E-5]
["BAYVIEW-TOBRUK",1,9.4304036212749905E-5]
["ALMURTA-KYABRAM",1,9.4304036212749905E-5]
["GAFFNEY-HIGINBOTHAM",1,9.4304036212749905E-5]
["HEATHCOTE-KENT",1,9.4304036212749905E-5]
["GEELONG-OLD GEELONG",1,9.4304036212749905E-5]
["ELLEN-RACHELLE",1,9.4304036212749905E-5]
["CAMBERWELL-McCRACKEN",1,9.4304036212749905E-5]
["HENRY-DENNIS",1,9.4304036212749905E-5]
["HILTON-WEST",1,9.4304036212749905E-5]
["HAWDON-BROWN",1,9.4304036212749905E-5]
["BORLASE-DRYSDALE",1,9.4304036212749905E-5]
["BARWON-PLENTY",1,9.4304036212749905E-5]
["BRASSEY CRT-P8E1",1,9.4304036212749905E-5]
["DAREBIN-STRADBROKE",1,9.4304036212749905E-5]
["GREEN-BOURKE",1,9.4304036212749905E-5]
["ANSTEY-LOCKTON",1,9.4304036212749905E-5]
["BIRMINGHAM-MELBOURNE",1,9.4304036212749905E-5]
["AMEILY-LEAMINGTON",1,9.4304036212749905E-5]
["COLLEGE-BREES",1,9.4304036212749905E-5]
["DALE-CHICAGO",1,9.4304036212749905E-5]
["DROMANA-GAFFNEY",1,9.4304036212749905E-5]
["DIXON-DERBY",1,9.4304036212749905E-5]
["FAIRY-WATERDALE",1,9.4304036212749905E-5]
["JOFFRE-KITCHENER",1,9.4304036212749905E-5]
["DUDLEY-GREEN",1,9.4304036212749905E-5]
["GODLEY-BROADHURST",1,9.4304036212749905E-5]
["HARRISON-DAVIDSON",1,9.4304036212749905E-5]
["GOLEEN-SYDNEY",1,9.4304036212749905E-5]
["BRASSEY CRT-P4",1,9.4304036212749905E-5]
["ATHOL-EDGAR",1,9.4304036212749905E-5]
["ALOHA-WATT",1,9.4304036212749905E-5]
["DE CARLE-RENNIE",1,9.4304036212749905E-5]
["Grand Total",10604,1.0000000000002416]

{"sheet":"Extreme Low V by ZSS contri","index":9,"n_rows":33,"n_cols":3,"rows_kept":33,"cut":false,"hidden":false,"merged":[]}
["Min.Consecutive.Violation","Y"]
[]
["Row Labels","Count of NMIs","Sum of Min.Consecutive.Violation (%)"]
["AW0",721,6.7993210109393118E-2]
["BD0",119,1.1222180309317223E-2]
["BMS",3,2.8291210863824973E-4]
["BY0",315,2.970577140701643E-2]
["CN0",1245,0.11740852508487125]
["COO",95,8.9588834402112294E-3]
["CS0",1013,9.5529988683514519E-2]
["EP0",392,3.6967182195398289E-2]
["EPN",256,2.4141833270464094E-2]
["ES0",1096,0.10335722368917231]
["FE0",139,1.3108261033572217E-2]
["FF0",206,1.942663145982652E-2]
["FT0",150,1.4145605431912464E-2]
["FW0",478,4.5077329309694915E-2]
["HB0",315,2.970577140701643E-2]
["KLO",9,8.4873632591474929E-4]
["NH0",963,9.0814786872877293E-2]
["NS0",147,1.3862693323274215E-2]
["NT0",893,8.4213504337985176E-2]
["PTN",314,2.9611467370803678E-2]
["PV0",689,6.4975480950585293E-2]
["SBY",85,8.0158430780837321E-3]
["SHM",83,7.8272350056582327E-3]
["ST0",25,2.3576009053187475E-3]
["TH0",68,6.4126744624669859E-3]
["TMA",50,4.7152018106374908E-3]
["TT0",652,6.1486231610713669E-2]
["YVE",80,7.5443228970199826E-3]
["(blank)",3,2.8291210863824973E-4]
["Grand Total",10604,1.0000000000002416]

{"sheet":"Under-Voltage Augmentation","index":10,"n_rows":48,"n_cols":12,"rows_kept":48,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,"Direct Costs only"]
[null,null,null,"20-21","21-22","22-23","23-24","24-25","Total","Status",null,"Number of PQ substations addressed"]
[null,null,null,null,null,null,null,null,"$","@30/6/25"]
[]
[null,"BAA-PQA-000034","Active Voltage Control",{"$f":"VLOOKUP(B7,'2020-21'!G:J,4,0)","v":44520.99},{"$f":"VLOOKUP(B7,'2021-22'!G:I,3,0)","v":35880.559999999998},null,null,null,{"$f":"SUM(D7:H7)","v":80401.549999999988},"CLSD"]
[null,"BAA-PQA-000039","MINOR PQA WORK",{"$f":"VLOOKUP(B8,'2020-21'!G:J,4,0)","v":19742.14},null,null,null,null,19742.14,"CLSD"]
[null,"BAA-PQA-000040","RELIEF OF HOME-TAIT & COLLINGWOOD-HOME",{"$f":"VLOOKUP(B9,'2020-21'!G:J,4,0)","v":5365.06},{"$f":"VLOOKUP(B9,'2021-22'!G:I,3,0)","v":17545.240000000002},{"$f":"VLOOKUP(B9,'2022-23'!G:J,4,0)","v":158804.68},{"$f":"VLOOKUP(B9,'2023-24'!G:J,4,0)","v":237667.03},null,419382.01,"CLSD",null,2]
[null,"BAA-PQA-000042","RELIEF OF FEHON-SOMERVILLE",{"$f":"VLOOKUP(B10,'2020-21'!G:J,4,0)","v":111102.62},{"$f":"VLOOKUP(B10,'2021-22'!G:I,3,0)","v":180686.77},null,null,null,291789.39,"CLSD"]
[null,"BAA-PQA-000043","RELIEF OF CARROL-ORRONG & CARROL-WHITELA",null,{"$f":"VLOOKUP(B11,'2021-22'!G:I,3,0)","v":111152.08},{"$f":"VLOOKUP(B11,'2022-23'!G:J,4,0)","v":13955.36},null,null,125107.44,"CLSD"]
[null,"BAA-PQA-000044","RELIEF OF GRAHAM 138-SYLVIA",{"$f":"VLOOKUP(B12,'2020-21'!G:J,4,0)","v":185295.45},{"$f":"VLOOKUP(B12,'2021-22'!G:I,3,0)","v":44433.2},null,null,null,229728.65000000002,"CLSD"]
[null,"BAA-PQA-000046","RELIEF OF ALOHA-WATT",{"$f":"VLOOKUP(B13,'2020-21'!G:J,4,0)","v":134980.12},null,null,null,null,134980.12,"CLSD"]
[null,"BAA-PQA-000047","RELIEF OF WEBB-QUEENSVILLE",{"$f":"VLOOKUP(B14,'2020-21'!G:J,4,0)","v":119774.03},{"$f":"VLOOKUP(B14,'2021-22'!G:I,3,0)","v":23687.09},null,null,null,{"$f":"SUM(E14:H14)","v":23687.09},"CLSD"]
[null,"BAA-PQA-000049","RELIEF OF MELBOURNE-PASCO",null,{"$f":"VLOOKUP(B15,'2021-22'!G:I,3,0)","v":15208.41},{"$f":"VLOOKUP(B15,'2022-23'!G:J,4,0)","v":228908.12},{"$f":"VLOOKUP(B15,'2023-24'!G:J,4,0)","v":110436.13},null,354552.66000000003,"CLSD",null,2]
[null,"BAA-PQA-000050","RELIEF OF MELROSE-SOMERS",null,null,{"$f":"VLOOKUP(B16,'2022-23'!G:J,4,0)","v":12586.6},{"$f":"VLOOKUP(B16,'2023-24'!G:J,4,0)","v":200723.27},null,213309.87,"CLSD",null,2]
[null,"BAA-PQA-000051","RELIEF OF FINLAYSON-BRAIDHILL",null,null,{"$f":"VLOOKUP(B17,'2022-23'!G:J,4,0)","v":19512.93},{"$f":"VLOOKUP(B17,'2023-24'!G:J,4,0)","v":360099.83},null,379612.76,"CLSD",null,1]
[null,"BAA-PQA-000052","RELIEF OF SUSSEX-NEWCASTLE",null,null,{"$f":"VLOOKUP(B18,'2022-23'!G:J,4,0)","v":281.26},{"$f":"VLOOKUP(B18,'2023-24'!G:J,4,0)","v":196471.56},{"$f":"VLOOKUP(B18,'2024-25'!G:J,4,0)","v":338355.31},535108.13,{"$f":"VLOOKUP(B18,'2024-25'!G:I,3,0)","v":"CLSD"},null,2]
[null,"BAA-PQA-000053","RELIEF OF KIERNAN_UPP HEIDELBERG",null,null,{"$f":"VLOOKUP(B19,'2022-23'!G:J,4,0)","v":211.3},{"$f":"VLOOKUP(B19,'2023-24'!G:J,4,0)","v":41030.300000000003},{"$f":"VLOOKUP(B19,'2024-25'!G:J,4,0)","v":442127.56},483369.16000000003,{"$f":"VLOOKUP(B19,'2024-25'!G:I,3,0)","v":"CLSD"},null,1]
[null,"BAA-PQA-000054","RELIEF OF WESTGATE-HATTER",null,null,{"$f":"VLOOKUP(B20,'2022-23'!G:J,4,0)","v":211.3},{"$f":"VLOOKUP(B20,'2023-24'!G:J,4,0)","v":120758.15},{"$f":"VLOOKUP(B20,'2024-25'!G:J,4,0)","v":122692.42},243661.87,{"$f":"VLOOKUP(B20,'2024-25'!G:I,3,0)","v":"CLSD"},null,2]
[null,"BAA-PQA-000055","RELIEF OF MCCRAE-ELSEY",null,null,{"$f":"VLOOKUP(B21,'2022-23'!G:J,4,0)","v":211.3},{"$f":"VLOOKUP(B21,'2023-24'!G:J,4,0)","v":36652.36},{"$f":"VLOOKUP(B21,'2024-25'!G:J,4,0)","v":908946.63},945810.29,{"$f":"VLOOKUP(B21,'2024-25'!G:I,3,0)","v":"CLSD"},null,2]
[null,"BAA-PQA-000056","RELIEF OF ERIC-ADA",null,null,{"$f":"VLOOKUP(B22,'2022-23'!G:J,4,0)","v":281.26},{"$f":"VLOOKUP(B22,'2023-24'!G:J,4,0)","v":245404.18},{"$f":"VLOOKUP(B22,'2024-25'!G:J,4,0)","v":102400.93},348086.37,{"$f":"VLOOKUP(B22,'2024-25'!G:I,3,0)","v":"CLSD"},null,2]
[null,"BAA-PQA-000057","RE LOCATE THE PQM METER",null,null,null,{"$f":"VLOOKUP(B23,'2023-24'!G:J,4,0)","v":21731.64},null,21731.64,"CLSD"]
[null,"BAA-PQA-000061","RELIEF OF KITCHENER-MURRAY",null,null,null,{"$f":"VLOOKUP(B24,'2023-24'!G:J,4,0)","v":2644.83},{"$f":"VLOOKUP(B24,'2024-25'!G:J,4,0)","v":714725.46},717370.28999999992,{"$f":"VLOOKUP(B24,'2024-25'!G:I,3,0)","v":"REL"}]
[null,"BAA-PQA-000062","RELIEF OF PLENTY RESERVOIR COLLEGE",null,null,null,{"$f":"VLOOKUP(B25,'2023-24'!G:J,4,0)","v":12692.34},{"$f":"VLOOKUP(B25,'2024-25'!G:J,4,0)","v":143069.45000000001},155761.79,{"$f":"VLOOKUP(B25,'2024-25'!G:I,3,0)","v":"REL"}]
[null,"BAA-PQA-000068","RELIEF OF WAIORA-DOUGHARTY",null,null,null,null,{"$f":"VLOOKUP(B26,'2024-25'!G:J,4,0)","v":74060.240000000005},74060.240000000005,{"$f":"VLOOKUP(B26,'2024-25'!G:I,3,0)","v":"REL"}]
[null,"BAA-PQA-000070","RELIEF OF BEAUCHAMP-HIGH",null,null,null,null,{"$f":"VLOOKUP(B27,'2024-25'!G:J,4,0)","v":280.77999999999997},280.77999999999997,{"$f":"VLOOKUP(B27,'2024-25'!G:I,3,0)","v":"REL"}]
[null,"BAA-PQA-000071","RELIEF OF BLENHEIM-WOODS",null,null,null,null,{"$f":"VLOOKUP(B28,'2024-25'!G:J,4,0)","v":438096.33},438096.33,{"$f":"VLOOKUP(B28,'2024-25'!G:I,3,0)","v":"REL"}]
[null,"BAA-PQA-000072","YARRA BEND FF ELSPEC G4 EOF PQM RELOC",null,null,null,null,{"$f":"VLOOKUP(B29,'2024-25'!G:J,4,0)","v":25},25,{"$f":"VLOOKUP(B29,'2024-25'!G:I,3,0)","v":"REL"}]
[null,"BAA-PQA-000073","RELIEF OF ST LEONARDS-EPSOM",null,null,null,null,{"$f":"VLOOKUP(B30,'2024-25'!G:J,4,0)","v":148147.92000000001},148147.92000000001,{"$f":"VLOOKUP(B30,'2024-25'!G:I,3,0)","v":"REL"}]
[null,"BAA-PQA-000074","RELIEF OF O'CONNOR-WHITBY",null,null,null,null,{"$f":"VLOOKUP(B31,'2024-25'!G:J,4,0)","v":95837.23},95837.23,{"$f":"VLOOKUP(B31,'2024-25'!G:I,3,0)","v":"REL"}]
[null,"BAA-PQA-000075","RELIEF OF HAWDON-BROWN",null,null,null,null,{"$f":"VLOOKUP(B32,'2024-25'!G:J,4,0)","v":5720.73},5720.73,{"$f":"VLOOKUP(B32,'2024-25'!G:I,3,0)","v":"REL"}]
[null,"BAA-PQA-000076","RELIEF OF JOFFRE-KENT",null,null,null,null,{"$f":"VLOOKUP(B33,'2024-25'!G:J,4,0)","v":13697.82},13697.82,{"$f":"VLOOKUP(B33,'2024-25'!G:I,3,0)","v":"REL"}]
[null,"BAA-PQA-000077","RELIEF OF CHALLIS-JUBILLEE",null,null,null,null,{"$f":"VLOOKUP(B34,'2024-25'!G:J,4,0)","v":5038.8999999999996},5038.8999999999996,{"$f":"VLOOKUP(B34,'2024-25'!G:I,3,0)","v":"REL"}]
[null,"BAA-PQA-000083","RELIEF OF WATT-THE AVENUE",null,null,null,null,{"$f":"VLOOKUP(B35,'2024-25'!G:J,4,0)","v":256.73},256.73,{"$f":"VLOOKUP(B35,'2024-25'!G:I,3,0)","v":"REL"}]
[null,"BAA-PQA-000085","RELIEF OF THORPE-WOODS",null,null,null,null,{"$f":"VLOOKUP(B36,'2024-25'!G:J,4,0)","v":455.04},455.04,{"$f":"VLOOKUP(B36,'2024-25'!G:I,3,0)","v":"REL"}]
[]
[]
[]
[]
[null,null,null,null,null,null,null,"Total",{"$f":"SUM(I9,I15,I16,I17,I18,I19,I20,I21,I22)","v":3922893.1200000006},null,null,{"$f":"SUM(L9,L15,L16,L17,L18,L19,L20,L21,L22)","v":16}]
[null,null,null,null,null,null,null,"Unit cost ($2024, direct cost without overheads, per DSS with PQA)",{"$f":"I41/L41","v":245180.82000000004}]
[]
[]
[null,null,null,null,null,null,null,"Augmentation required to deliver 15.98% under-voltage improvement with updated DSS augmentation unit rate of $245k per DSS"]
[null,null,null,null,null,null,null,"Unit cost ($2024, direct cost without overheads, per DSS with PQA)",{"$f":"I42","v":245180.82000000004}]
[null,null,null,null,null,null,null,"Number of DSS augmentation to deliver 15.98% improvement to meet 5% compliance",35]
[null,null,null,null,null,null,null,"One-off total capex required to deliver improvement to maintain EDCoP under-voltage 5% compliance ($2024, direct cost without overheads)",{"$f":"I46*I47","v":8581328.7000000011}]

{"sheet":"2024-25","index":11,"n_rows":96,"n_cols":10,"rows_kept":96,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[null,null,null,"Select Report from below:"]
[null,null,null,"Period: ","Start","007.2024","End","006.2025"]
[]
[null,null,null,"","","","","","","SCS/ACS Capex Exclude Overheads"]
[null,null,null,"WBS - Regulatory Category C (MAT)",null,"WBS - Mat Code","Work Breakdown Structure Element (WBS Element)",null,"WBS - System Status","AUD"]
[null,null,null,"C44","AUGEX","DOA","BAA-DOA-000023","Augment BTS-FF 22kV Loop - Sub Trans","REL",156875.4]
[null,null,null,null,null,null,"BAA-DOA-000024","KTS-BY-ES 66kV loop capacity constraint","CLSD",152248]
[null,null,null,null,null,null,"BAA-DOA-000030","DC11 - New ST-CBN-ADC-SSS lines","REL",1257099.49]
[null,null,null,null,null,"DSH","BAA-DSH-000006","Install Voltage Regulator – SBY13","REL",28481.16]
[null,null,null,null,null,null,"BAA-DSH-000021","COO & KLO REFCL Feeder Works","CLSD",839547.72]
[null,null,null,null,null,null,"BAA-DSH-000022","RECONFIGURE FEEDER - SBY-024","REL",4467463.09]
[null,null,null,null,null,null,"BAA-DSH-000026","KLO21 Reconfiguration","TECO",3424.33]
[null,null,null,null,null,null,"BAA-DSH-000031","EP Conversion Stage 7","REL",3696.46]
[null,null,null,null,null,null,"BAA-DSH-000036","KLO21 Reconfiguration - Stage 2","REL",465477.88]
[null,null,null,null,null,null,"BAA-DSH-000037","COO11 Replace Voltage Regulator","REL",111814]
[null,null,null,null,null,null,"BAA-DSH-000053","New feeder SHM-013","REL",4904.6899999999996]
[null,null,null,null,null,null,"BAA-DSH-000054","New feeder SBY-014","REL",6345.32]
[null,null,null,null,null,null,"BAA-DSH-000062","Augment Feeder KLO-23","REL",3760.09]
[null,null,null,null,null,null,"BAA-DSH-000065","AUGMENT FEEDER FT21","REL",20506.169999999998]
[null,null,null,null,null,null,"BAA-DSH-000066","COMMUNITY BATTERIES FS","REL",14363.4]
[null,null,null,null,null,null,"BAA-DSH-000068","New feeder PTN-12","REL",8902.1]
[null,null,null,null,null,null,"BAA-DSH-000069","New Feeder SBY15","REL",4716]
[null,null,null,null,null,null,"BAA-DSH-000070","Augment Feeder FF0-093","REL",4068]
[null,null,null,null,null,null,"BAA-DSH-000071","KLO22 Reconfiguration","REL",1922173.24]
[null,null,null,null,null,null,"BAA-DSH-800079","New Feeder HB21","TECO",467151.35]
[null,null,null,null,null,"DSJ","BAA-DSJ-000235","HBRA'23 Distribution Substation Augment","TECO",1082651.27]
[null,null,null,null,null,null,"BAA-DSJ-000236","2023 MINOR WORKS - DSJ","CLSD",-918.4]
[null,null,null,null,null,null,"BAA-DSJ-000237","RELIEF OF LEBANON-FENACRE","CLSD",222431.61]
[null,null,null,null,null,null,"BAA-DSJ-000238","RELIEF OF MARSHALL-INVERMAY","CLSD",182478.97]
[null,null,null,null,null,null,"BAA-DSJ-000239","RELIEF OF GELLIBRAND-VICTORIA","CLSD",190726.1]
[null,null,null,null,null,null,"BAA-DSJ-000241","RELIEF OF CARR-NEWLANDS","REL",286288.15000000002]
[null,null,null,null,null,null,"BAA-DSJ-000242","RELIEF OF MALCOLM-ELIZABETH","REL",263445.92]
[null,null,null,null,null,null,"BAA-DSJ-000243","RELIEF OF OAK-CONISTON","CLSD",267367.13]
[null,null,null,null,null,null,"BAA-DSJ-000244","RELIEF OF PARKLANDS-KELVIN","REL",45445.4]
[null,null,null,null,null,null,"BAA-DSJ-000245","RELIEF OF DAVERN-O’HEA","REL",86363.520000000004]
[null,null,null,null,null,null,"BAA-DSJ-000246","2024 MINOR WORKS - DSJ","CLSD",226549.45]
[null,null,null,null,null,null,"BAA-DSJ-000249","RELIEF OF GRANGE-CRAMER","REL",5395.08]
[null,null,null,null,null,null,"BAA-DSJ-000250","RELIEF OF NIMMO-BUCKLEY","REL",64290.3]
[null,null,null,null,null,null,"BAA-DSJ-000254","RELIEF OF PARSONS-STUBBS","CLSD",80393.240000000005]
[null,null,null,null,null,null,"BAA-DSJ-000256","HBRA'25 Distro Subst Augment Batch 2","REL",601297.21]
[null,null,null,null,null,null,"BAA-DSJ-000257","RELIEF OF WELLINGTON-VICTORIA","REL",3189.32]
[null,null,null,null,null,null,"BAA-DSJ-000260","MINOR WORKS 2025","REL",83071.710000000006]
[null,null,null,null,null,null,"BAA-DSJ-000266","RELIEF OF ST HELLIER-UPPER HEIDELBERG","REL",1263.3599999999999]
[null,null,null,null,null,null,"BAA-DSJ-000267","RELIEF OF DEAKIN-SPENCER","REL",4236.49]
[null,null,null,null,null,"DSL","BAA-DSL-000014","RELIEF OF DEAN-SYDNEY","REL",-4606.82]
[null,null,null,null,null,null,"BAA-DSL-000015","COMMUNITY BATTERY - FLEMINGTON","REL",664838.14]
[null,null,null,null,null,null,"BAA-DSL-000016","COMMUNITY BATTERY - COBURG","REL",1170591.8600000001]
[null,null,null,null,null,null,"BAA-DSL-000017","COMMUNITY BATTERY - BELLFIELD","CLSD",1296031.58]
[null,null,null,null,null,null,"BAA-DSL-000018","COMMUNITY BATTERY - ALPHINGTON","REL",914787.45]
[null,null,null,null,null,null,"BAA-DSL-000020","RELOCATION OF GREENVALE BESS","REL",77303.14]
[null,null,null,null,null,null,"BAA-DSL-000021","RELIEF OF MIDDLE-ASCOT VALE","CLSD",73628.259999999995]
[null,null,null,null,null,null,"BAA-DSL-000022","Relief Of Centre-Howard","CLSD",308599.37]
[null,null,null,null,null,null,"BAA-DSL-000024","RELIEF OF SHEFFIELD-COBURG","CLSD",255337.73]
[null,null,null,null,null,null,"BAA-DSL-000025","RELIEF OF RENNIE-JOHN","CLSD",134093.89000000001]
[null,null,null,null,null,null,"BAA-DSL-000026","RELIEF OF GOSFORD-NICHOLAS","CLSD",253710.98]
[null,null,null,null,null,"DZA","BAA-DZA-000039","EP CONVERSION STAGE 6","REL",6459908.8099999996]
[null,null,null,null,null,null,"BAA-DZA-000044","FF NO.4 6.6KV BUS","REL",5132323.59]
[null,null,null,null,null,null,"BAA-DZA-000059","Upgrade SBY No.1 & 3 transf to 20/33 MVA","REL",7560]
[null,null,null,null,null,null,"BAA-DZA-000063","New Craigieburn (CBN) Zone Sub","REL",284116.64]
[null,null,null,null,null,null,"BAA-DZA-000069","DC11 - Craigieburn","REL",13990007.640000001]
[null,null,null,null,null,null,"BAA-DZA-800028","REFCL Works at COO","CLSD",43830.84]
[null,null,null,null,null,null,"BAA-DZA-888888","Capacity Development - DZA","REL",-78021.649999999994]
[null,null,null,null,null,"PQA","BAA-PQA-000052","RELIEF OF SUSSEX-NEWCASTLE","CLSD",338355.31]
[null,null,null,null,null,null,"BAA-PQA-000053","RELIEF OF KIERNAN_UPP HEIDELBERG","CLSD",442127.56]
[null,null,null,null,null,null,"BAA-PQA-000054","RELIEF OF WESTGATE-HATTER","CLSD",122692.42]
[null,null,null,null,null,null,"BAA-PQA-000055","RELIEF OF MCCRAE-ELSEY","CLSD",908946.63]
[null,null,null,null,null,null,"BAA-PQA-000056","RELIEF OF ERIC-ADA","CLSD",102400.93]
[null,null,null,null,null,null,"BAA-PQA-000061","RELIEF OF KITCHENER-MURRAY","REL",714725.46]
[null,null,null,null,null,null,"BAA-PQA-000062","RELIEF OF PLENTY RESERVOIR COLLEGE","REL",143069.45000000001]
[null,null,null,null,null,null,"BAA-PQA-000068","RELIEF OF WAIORA-DOUGHARTY","REL",74060.240000000005]
[null,null,null,null,null,null,"BAA-PQA-000070","RELIEF OF BEAUCHAMP-HIGH","REL",280.77999999999997]
[null,null,null,null,null,null,"BAA-PQA-000071","RELIEF OF BLENHEIM-WOODS","REL",438096.33]
[null,null,null,null,null,null,"BAA-PQA-000072","YARRA BEND FF ELSPEC G4 EOF PQM RELOC","REL",25]
[null,null,null,null,null,null,"BAA-PQA-000073","RELIEF OF ST LEONARDS-EPSOM","REL",148147.92000000001]
[null,null,null,null,null,null,"BAA-PQA-000074","RELIEF OF O'CONNOR-WHITBY","REL",95837.23]
[null,null,null,null,null,null,"BAA-PQA-000075","RELIEF OF HAWDON-BROWN","REL",5720.73]
[null,null,null,null,null,null,"BAA-PQA-000076","RELIEF OF JOFFRE-KENT","REL",13697.82]
[null,null,null,null,null,null,"BAA-PQA-000077","RELIEF OF CHALLIS-JUBILLEE","REL",5038.8999999999996]
[null,null,null,null,null,null,"BAA-PQA-000083","RELIEF OF WATT-THE AVENUE","REL",256.73]
[null,null,null,null,null,null,"BAA-PQA-000085","RELIEF OF THORPE-WOODS","REL",455.04]
[null,null,null,null,null,"PRA","BAA-PRA-000045","VVC PILOT - FEASIBILITY INVESTIGATION","REL",90302.59]
[null,null,null,null,null,null,"BAA-PRA-000046","GRID STABILITY - MINIMUM DEMAND - PRA","REL",23243.86]
[null,null,null,null,null,null,"BAA-PRA-000047","Comms Network: Expansion & Strengthening","REL",513500.06]
[null,null,null,null,null,null,"BAA-PRA-000050","FLISR ENABLEMENT FOR REFCL SITES","REL",19364.830000000002]
[null,null,null,null,null,null,"BAA-PRA-000051","SSS RTU CONITEL","REL",28865.84]
[null,null,null,null,null,null,"BAA-PRA-000052","VVC ROLLOUT","REL",1078885.1100000001]
[null,null,null,null,null,"PRB","BAA-PRB-000003","FLISR: RCS Roll Out Program","CLSD",934478.29]
[null,null,null,null,null,null,"BAA-PRB-000006","Switch Augmentation Plenty Rd Reservoir","REL",15834.08]
[null,null,null,null,null,null,"BAA-PRB-000007","FLISR: RCS Roll Out Program - Stage 2","REL",1518035.12]
[null,null,null,null,null,"Result",null,null,null,52399469.43]
[null,null,null,"Overall Result",null,null,null,null,null,52399469.43]

{"sheet":"2023-24","index":12,"n_rows":131,"n_cols":12,"rows_kept":131,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[null,null,null,"Select Report from below:"]
[null,null,null,"Period: ","Start","007.2023","End","006.2024"]
[]
[null,null,null,"","","","","","","SCS/ACS Capex Exclude Overheads"]
[null,null,null,"WBS - Regulatory Category C (MAT)",null,"WBS - Mat Code","Work Breakdown Structure Element (WBS Element)",null,"WBS - System Status","AUD"]
[null,null,null,"C44","AUGEX","DOA","BAA-DOA-000022","DC NEXTDC M2 60MVA SUPPLY","CLSD",-12210.25]
[null,null,null,null,null,null,"BAA-DOA-000023","Augment BTS-FF 22kV Loop - Sub Trans","REL",52121.19]
[null,null,null,null,null,null,"BAA-DOA-000024","KTS-BY-ES 66kV loop capacity constraint","TECO",680887.28]
[null,null,null,null,null,null,"BAA-DOA-000026","KTS 66kV SPLIT LOOP - ACCESS RAMP WORKS","REL",-4207]
[null,null,null,null,null,null,"BAA-DOA-000030","ST-CBN-ADC New 66kV Lines","REL",101323.89]
[null,null,null,null,null,null,"BAA-DOA-000032","Twin Circuit KTS-AW","REL",4416]
[null,null,null,null,null,null,"BAA-DOA-000033","New KTS-VDT 66kV line","REL",3387]
[null,null,null,null,null,null,"BAA-DOA-000034","Augment TTS-NH(NEI)-NEL-WT-TTS 66kV loop","REL",9834]
[null,null,null,null,null,null,"BAA-DOA-800015","Augment BTS-NS 22kV loop","REL",10728,null,{"$f":"SUM(J11:J19)","v":846280.11}]
[null,null,null,null,null,"DSH","BAA-DSH-000002","COO & ST Feeder capacity constraint","CLSD",544959.91]
[null,null,null,null,null,null,"BAA-DSH-000006","Install Voltage Regulator – SBY13","REL",18271.41]
[null,null,null,null,null,null,"BAA-DSH-000016","EP Conversion Stage 5","CLSD",171525.86]
[null,null,null,null,null,null,"BAA-DSH-000021","COO & KLO REFCL Feeder Works","REL",3674900.32]
[null,null,null,null,null,null,"BAA-DSH-000022","RECONFIGURE FEEDER - SBY-024","REL",139838.39999999999]
[null,null,null,null,null,null,"BAA-DSH-000023","AUGMENT CS5","REL",882]
[null,null,null,null,null,null,"BAA-DSH-000024","NEW FEEDER FT-012","REL",2328]
[null,null,null,null,null,null,"BAA-DSH-000025","Reconfigure Feeder – YVE21","TECO",1438790.29]
[null,null,null,null,null,null,"BAA-DSH-000026","KLO21 Reconfiguration","REL",17507.349999999999]
[null,null,null,null,null,null,"BAA-DSH-000028","Augment Section of NT11","REL",1470]
[null,null,null,null,null,null,"BAA-DSH-000030","Augment Feeder NS18","REL",2421]
[null,null,null,null,null,null,"BAA-DSH-000031","EP Conversion Stage 7","REL",31304]
[null,null,null,null,null,null,"BAA-DSH-000032","EP Conversion Stage 8","REL",6012]
[null,null,null,null,null,null,"BAA-DSH-000037","COO11 Replace Voltage Regulator","REL",157664]
[null,null,null,null,null,null,"BAA-DSH-000038","Augment feeder FF0-096","REL",3666]
[null,null,null,null,null,null,"BAA-DSH-000039","Augment feeder BD0-008","REL",3504]
[null,null,null,null,null,null,"BAA-DSH-000040","Augment section of FF0-087","REL",2904]
[null,null,null,null,null,null,"BAA-DSH-000041","Augment section of NH0-002","REL",1803]
[null,null,null,null,null,null,"BAA-DSH-000043","Augment feeder EPN-034","REL",2958]
[null,null,null,null,null,null,"BAA-DSH-000045","Augment feeder FT0-011","REL",1011]
[null,null,null,null,null,null,"BAA-DSH-000046","New feeder FT0-025","REL",2004]
[null,null,null,null,null,null,"BAA-DSH-000047","Augment feeder TT0-011","REL",1371]
[null,null,null,null,null,null,"BAA-DSH-000049","New feeder SBY-022","REL",1767]
[null,null,null,null,null,null,"BAA-DSH-000052","New feeder ES0-031","REL",3092]
[null,null,null,null,null,null,"BAA-DSH-000053","New feeder SHM-013","REL",1788]
[null,null,null,null,null,null,"BAA-DSH-000054","New feeder SBY-014","REL",3351]
[null,null,null,null,null,null,"BAA-DSH-000055","New Craigieburn (CBN) ZSS - HV fdr works","REL",3264]
[null,null,null,null,null,null,"BAA-DSH-000058","Augment feeder NH-16","REL",1803]
[null,null,null,null,null,null,"BAA-DSH-000059","Augment feeder NS-17","REL",2586]
[null,null,null,null,null,null,"BAA-DSH-000060","New feeder ES0-033","REL",3416]
[null,null,null,null,null,null,"BAA-DSH-000061","New feeder SBY-031","REL",1911]
[null,null,null,null,null,null,"BAA-DSH-000062","Augment Feeder KLO-23","REL",2508]
[null,null,null,null,null,null,"BAA-DSH-000063","COO Bus 1 Cable Transfers","REL",306]
[null,null,null,null,null,null,"BAA-DSH-000064","COO Bus 2 Feeder Arrangements","REL",2019]
[null,null,null,null,null,null,"BAA-DSH-800079","New Feeder HB21","REL",3453570.68,null,{"$f":"SUM(J20:J54)","v":9708477.2200000007}]
[null,null,null,null,null,"DSI","BAA-DSI-000005","REFCL - Balancing Works","CLSD",18989.55]
[null,null,null,null,null,null,"BAA-DSI-000006","COO11 Fleetwood Dr OH","REL",545672.98]
[null,null,null,null,null,null,"BAA-DSI-000007","COO23 Elphinstone Blvd UG","REL",2270869.77]
[null,null,null,null,null,null,"BAA-DSI-000008","COO23 Mickleham Rd UG","REL",1692224.04,null,{"$f":"SUM(J55:J58)","v":4527756.34}]
[null,null,null,null,null,"DSJ","BAA-DSJ-000196","Relief Of Valley Augustine","CLSD",-6027.29]
[null,null,null,null,null,null,"BAA-DSJ-000200","RELIEF OF BINDI-WIDFORD","CLSD",71432.63]
[null,null,null,null,null,null,"BAA-DSJ-000204","RELIEF OF RATHCOWN-CHEDDAR","CLSD",-8129.07]
[null,null,null,null,null,null,"BAA-DSJ-000219","RELIEF OF WHITE-DUKE","CLSD",66669.41]
[null,null,null,null,null,null,"BAA-DSJ-000227","RELIEF OF VALLEY LAKE – STEELE CREEK","CLSD",-412.01]
[null,null,null,null,null,null,"BAA-DSJ-000233","RELIEF OF LUKE-BANBURY","CLSD",147211.32]
[null,null,null,null,null,null,"BAA-DSJ-000234","RELIEF OF BALMORAL-KENNETH","CLSD",173229.47]
[null,null,null,null,null,null,"BAA-DSJ-000235","HBRA'23 Distribution Substation Augment","REL",2040283.23]
[null,null,null,null,null,null,"BAA-DSJ-000236","2023 MINOR WORKS - DSJ","REL",130650.58]
[null,null,null,null,null,null,"BAA-DSJ-000237","RELIEF OF LEBANON-FENACRE","REL",28359.67]
[null,null,null,null,null,null,"BAA-DSJ-000238","RELIEF OF MARSHALL-INVERMAY","REL",42503.71]
[null,null,null,null,null,null,"BAA-DSJ-000239","RELIEF OF GELLIBRAND-VICTORIA","REL",14831.33]
[null,null,null,null,null,null,"BAA-DSJ-000241","RELIEF OF CARR-NEWLANDS","REL",33724.050000000003]
[null,null,null,null,null,null,"BAA-DSJ-000243","RELIEF OF OAK-CONISTON","REL",17219.04]
[null,null,null,null,null,null,"BAA-DSJ-000246","2024 MINOR WORKS - DSJ","REL",75131.679999999993]
[null,null,null,null,null,null,"BAA-DSJ-800118","Relief of  Dundee - Meade","CLSD",-9748.59,null,{"$f":"SUM(J59:J74)","v":2816929.16}]
[null,null,null,null,null,"DSL","BAA-DSL-000011","RELIEF OF SHAFTSBURY-MORELAND","CLSD",-8309.33]
[null,null,null,null,null,null,"BAA-DSL-000014","RELIEF OF DEAN-SYDNEY","REL",16580.38]
[null,null,null,null,null,null,"BAA-DSL-000015","COMMUNITY BATTERY - FLEMINGTON","REL",61942.95]
[null,null,null,null,null,null,"BAA-DSL-000016","COMMUNITY BATTERY - COBURG","REL",59107.43]
[null,null,null,null,null,null,"BAA-DSL-000017","COMMUNITY BATTERY - BELLFIELD","REL",56124.65]
[null,null,null,null,null,null,"BAA-DSL-000018","COMMUNITY BATTERY - ALPHINGTON","REL",55086.59]
[null,null,null,null,null,null,"BAA-DSL-000020","INTALLATION OF BATTERY AT TULLAMARINE","REL",16282.55]
[null,null,null,null,null,null,"BAA-DSL-000021","RELIEF OF MIDDLE-ASCOT VALE","REL",65788.460000000006]
[null,null,null,null,null,null,"BAA-DSL-000022","Relief Of Centre-Howard","REL",18843.98]
[null,null,null,null,null,null,"BAA-DSL-000023","RELIEF OF MARION-SUSSEX","CLSD",-3240.58]
[null,null,null,null,null,null,"BAA-DSL-000024","RELIEF OF SHEFFIELD-COBURG","REL",10730.13]
[null,null,null,null,null,null,"BAA-DSL-000025","RELIEF OF RENNIE-JOHN","REL",7650.89]
[null,null,null,null,null,null,"BAA-DSL-000026","RELIEF OF GOSFORD-NICHOLAS","REL",27326.23,null,{"$f":"SUM(J75:J87)","v":383914.32999999996}]
[null,null,null,null,null,"DZA","BAA-DZA-000039","EP CONVERSION STAGE 6","REL",3731849.94]
[null,null,null,null,null,null,"BAA-DZA-000044","FF NO.4 6.6KV BUS","REL",1218228.71]
[null,null,null,null,null,null,"BAA-DZA-000045","3rd Transformer and 66kV Works at FT","REL",8376]
[null,null,null,null,null,null,"BAA-DZA-000047","REFCL Works at COO Commissioning","CLSD",681272.23]
[null,null,null,null,null,null,"BAA-DZA-000050","Install 1 x 4MVAr Reactor - COO","REL",1389]
[null,null,null,null,null,null,"BAA-DZA-000051","Install 1 x 4MVAr Reactor - ST","REL",1700]
[null,null,null,null,null,null,"BAA-DZA-000052","Install 2 x 4MVAr Reactors - SHM","REL",1740]
[null,null,null,null,null,null,"BAA-DZA-000053","Install 2 x 4MVAr Reactors - KLO","REL",1965]
[null,null,null,null,null,null,"BAA-DZA-000054","Install 2 x 4MVAr Reactors - SBY","REL",5052]
[null,null,null,null,null,null,"BAA-DZA-000063","New Craigieburn (CBN) ZS SS works","REL",19144.5]
[null,null,null,null,null,null,"BAA-DZA-000067","Grid Stability – UFLS (KTS)","REL",2727]
[null,null,null,null,null,null,"BAA-DZA-000069","DESIGN & CONSTRUCT ADC ZSS","REL",1480859.37]
[null,null,null,null,null,null,"BAA-DZA-000071","Grid Stability – UFLS (TSTS)","REL",813]
[null,null,null,null,null,null,"BAA-DZA-000073","Grid Stability – UFLS (WMTS)","REL",813]
[null,null,null,null,null,null,"BAA-DZA-000075","Grid Stability – UFLS (SMTS)","REL",957]
[null,null,null,null,null,null,"BAA-DZA-000077","Grid Stability – UFLS (TTS)","REL",1101]
[null,null,null,null,null,null,"BAA-DZA-000079","Grid Stability – UFLS (BTS)","REL",957]
[null,null,null,null,null,null,"BAA-DZA-000081","Grid Stability – UFLS (BLTS)","REL",957]
[null,null,null,null,null,null,"BAA-DZA-800028","REFCL Works at COO","TECO",282710.77]
[null,null,null,null,null,null,"BAA-DZA-888888","Capacity Development - DZA","REL",-3207709.06,null,{"$f":"SUM(J88:J107)","v":4234903.4600000009}]
[null,null,null,null,null,"PQA","BAA-PQA-000029","Relief of Napier-Butler","CLSD",-1659.15]
[null,null,null,null,null,null,"BAA-PQA-000033","Relief of Mulberry-Gona","CLSD",-774.26]
[null,null,null,null,null,null,"BAA-PQA-000040","RELIEF OF HOME-TAIT & COLLINGWOOD-HOME","REL",237667.03]
[null,null,null,null,null,null,"BAA-PQA-000049","RELIEF OF MELBOURNE-PASCO","CLSD",110436.13]
[null,null,null,null,null,null,"BAA-PQA-000050","RELIEF OF MELROSE-SOMERS","CLSD",200723.27]
[null,null,null,null,null,null,"BAA-PQA-000051","RELIEF OF FINLAYSON-BRAIDHILL","CLSD",360099.83]
[null,null,null,null,null,null,"BAA-PQA-000052","RELIEF OF SUSSEX-NEWCASTLE","REL",196471.56]
[null,null,null,null,null,null,"BAA-PQA-000053","RELIEF OF KIERNAN_UPP HEIDELBERG","REL",41030.300000000003]
[null,null,null,null,null,null,"BAA-PQA-000054","RELIEF OF WESTGATE-HATTER","REL",120758.15]
[null,null,null,null,null,null,"BAA-PQA-000055","RELIEF OF MCCRAE-ELSEY","REL",36652.36]
[null,null,null,null,null,null,"BAA-PQA-000056","RELIEF OF ERIC-ADA","REL",245404.18]
[null,null,null,null,null,null,"BAA-PQA-000057","RE LOCATE THE PQM METER","TECO",21731.64]
[null,null,null,null,null,null,"BAA-PQA-000061","RELIEF OF KITCHENER-MURRAY","REL",2644.83]
[null,null,null,null,null,null,"BAA-PQA-000062","RELIEF OF PLENTY RESERVOIR COLLEGE","REL",12692.34,null,{"$f":"SUM(J108:J121)","v":1583878.2100000002}]
[null,null,null,null,null,"PRA","BAA-PRA-000042","INSTALLATION OF TRANSFORMER MONITORING S","TECO",33428.06]
[null,null,null,null,null,null,"BAA-PRA-000045","VVC PILOT - FEASIBILITY INVESTIGATION","REL",337494.3]
[null,null,null,null,null,null,"BAA-PRA-000046","GRID STABILITY - MINIMUM DEMAND - PRA","REL",412621.42]
[null,null,null,null,null,null,"BAA-PRA-000047","Comms Network: Expansion & Strengthening","REL",698919.03]
[null,null,null,null,null,null,"BAA-PRA-000050","FLISR ENABLEMENT FOR REFCL SITES","REL",20063.669999999998]
[null,null,null,null,null,null,"BAA-PRA-000051","SSS RTU CONITEL","REL",3710.18]
[null,null,null,null,null,null,"BAA-PRA-000052","VVC ROLLOUT","REL",2525.56,null,{"$f":"SUM(J122:J128)","v":1508762.22}]
[null,null,null,null,null,"PRB","BAA-PRB-000003","FLISR: RCS Roll Out Program","REL",3234916.53,null,{"$f":"J129","v":3234916.53}]
[null,null,null,null,null,"Result",null,null,null,28845817.579999998,null,{"$f":"SUM(L11:L129)","v":28845817.579999998}]
[null,null,null,"Overall Result",null,null,null,null,null,28845817.579999998]

{"sheet":"2022-23","index":13,"n_rows":69,"n_cols":10,"rows_kept":69,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[null,null,null,"Select Report from below:"]
[null,null,null,"Period: ","Start","007.2022","End","006.2023"]
[]
[null,null,null,"","","","","","","SCS/ACS Capex Exclude Overheads"]
[null,null,null,"WBS - Regulatory Category C (MAT)",null,"WBS - Mat Code","Work Breakdown Structure Element (WBS Element)",null,"WBS - System Status","AUD"]
[null,null,null,"C44","AUGEX","DOA","BAA-DOA-000023","Augment BTS-FF 22kV Loop - Sub Trans","REL",3086.55]
[null,null,null,null,null,null,"BAA-DOA-000024","KTS-BY-ES 66kV loop capacity constraint","REL",180979.53]
[null,null,null,null,null,null,"BAA-DOA-000026","KTS 66kV SPLIT LOOP - ACCESS RAMP WORKS","REL",-56140.42]
[null,null,null,null,null,null,"BAA-DOA-800011","Rearr KTS-MAT-AW-PV-KTS 66kV split loop","CLSD",-9898.24]
[null,null,null,null,null,"DSH","BAA-DSH-000002","COO & ST Feeder capacity constraint","REL",3287991.79]
[null,null,null,null,null,null,"BAA-DSH-000016","EP Conversion Stage 5","REL",1738830.11]
[null,null,null,null,null,null,"BAA-DSH-000021","COO & KLO REFCL Feeder Works","REL",15393749.65]
[null,null,null,null,null,null,"BAA-DSH-000025","Reconfigure Feeder – YVE21","REL",91609.74]
[null,null,null,null,null,null,"BAA-DSH-000026","KLO21 Reconfiguration","REL",7330043.9699999997]
[null,null,null,null,null,null,"BAA-DSH-000035","FT26 Feeder Uprate","REL",174405.03]
[null,null,null,null,null,null,"BAA-DSH-800065","Reconfigure feeder - ES23","REL",1997658.3]
[null,null,null,null,null,null,"BAA-DSH-800079","New Feeder HB21","REL",332353.45]
[null,null,null,null,null,"DSI","BAA-DSI-000005","REFCL - Balancing Works","TECO",792261.52]
[null,null,null,null,null,"DSJ","BAA-DSJ-000200","RELIEF OF BINDI-WIDFORD","REL",469517.91]
[null,null,null,null,null,null,"BAA-DSJ-000208","RELIEF OF CUDMORE-MARKET","CLSD",85721.86]
[null,null,null,null,null,null,"BAA-DSJ-000216","RELIEF OF  FLINDERS-THE WALK","CLSD",35910.04]
[null,null,null,null,null,null,"BAA-DSJ-000217","RELIEF OF GOWANBRAE-SEGGAN","CLSD",24716.06]
[null,null,null,null,null,null,"BAA-DSJ-000218","RELIEF OF HALL-BURBANK AND BURBANK-KATRI","CLSD",79896.37]
[null,null,null,null,null,null,"BAA-DSJ-000219","RELIEF OF WHITE-DUKE","TECO",156455.65]
[null,null,null,null,null,null,"BAA-DSJ-000220","RELIEF OF GROSVENOR-FLORENCE","CLSD",16682.09]
[null,null,null,null,null,null,"BAA-DSJ-000222","RELIEF OF CHRISTINA-BARBARA","CLSD",18914.419999999998]
[null,null,null,null,null,null,"BAA-DSJ-000223","RELIEF OF CANNES-CAPRI","CLSD",37569.5]
[null,null,null,null,null,null,"BAA-DSJ-000224","RELIEF OF BONWICK-BASIL","CLSD",163.72]
[null,null,null,null,null,null,"BAA-DSJ-000225","RELIEF OF  GRAHAM-GIBSON","CLSD",12809.64]
[null,null,null,null,null,null,"BAA-DSJ-000226","RELIEF OF HILTON-WEST","CLSD",18517.32]
[null,null,null,null,null,null,"BAA-DSJ-000228","RELIEF OF RENOWN-KERFERED","CLSD",8812.36]
[null,null,null,null,null,null,"BAA-DSJ-000232","2022-Minor Works (DSJ+PQA)","REL",76653.100000000006]
[null,null,null,null,null,null,"BAA-DSJ-000233","RELIEF OF LUKE-BANBURY","REL",10995.74]
[null,null,null,null,null,null,"BAA-DSJ-000234","RELIEF OF BALMORAL-KENNETH","REL",11784.72]
[null,null,null,null,null,null,"BAA-DSJ-000235","HBRA'23 Distribution Substation Augment","REL",169056.84]
[null,null,null,null,null,null,"BAA-DSJ-000236","2023 MINOR WORKS - DSJ","REL",28923.31]
[null,null,null,null,null,null,"BAA-DSJ-000238","RELIEF OF MARSHALL-INVERMAY","REL",211.3]
[null,null,null,null,null,null,"BAA-DSJ-000239","RELIEF OF GELLIBRAND-VICTORIA","REL",281.26]
[null,null,null,null,null,"DSL","BAA-DSL-000011","RELIEF OF SHAFTSBURY-MORELAND","REL",7194.22]
[null,null,null,null,null,null,"BAA-DSL-000012","RELIEF OF BIZANA-FONTEIN","REL",3012.4]
[null,null,null,null,null,null,"BAA-DSL-000013","DCCEEEW COMMUNITY BATTERIES","REL",80493.5]
[null,null,null,null,null,"DZA","BAA-DZA-000039","EP CONVERSION STAGE 6","REL",259623.85]
[null,null,null,null,null,null,"BAA-DZA-000043","YVE, FE, FW, TH NETWORK DEVELOPMENT","REL",2691660.17]
[null,null,null,null,null,null,"BAA-DZA-000044","FF NO.4 6.6KV BUS","REL",474399.48]
[null,null,null,null,null,null,"BAA-DZA-000047","REFCL Works at COO Commissioning","REL",943608.85]
[null,null,null,null,null,null,"BAA-DZA-800028","REFCL Works at COO","REL",4507023.46]
[null,null,null,null,null,null,"BAA-DZA-888888","Capacity Development - DZA","REL",3169466.36]
[null,null,null,null,null,"PQA","BAA-PQA-000040","RELIEF OF HOME-TAIT & COLLINGWOOD-HOME","REL",158804.68]
[null,null,null,null,null,null,"BAA-PQA-000043","RELIEF OF CARROL-ORRONG & CARROL-WHITELA","CLSD",13955.36]
[null,null,null,null,null,null,"BAA-PQA-000049","RELIEF OF MELBOURNE-PASCO","REL",228908.12]
[null,null,null,null,null,null,"BAA-PQA-000050","RELIEF OF MELROSE-SOMERS","REL",12586.6]
[null,null,null,null,null,null,"BAA-PQA-000051","RELIEF OF FINLAYSON-BRAIDHILL","REL",19512.93]
[null,null,null,null,null,null,"BAA-PQA-000052","RELIEF OF SUSSEX-NEWCASTLE","REL",281.26]
[null,null,null,null,null,null,"BAA-PQA-000053","RELIEF OF KIERNAN_UPP HEIDELBERG","REL",211.3]
[null,null,null,null,null,null,"BAA-PQA-000054","RELIEF OF WESTGATE-HATTER","REL",211.3]
[null,null,null,null,null,null,"BAA-PQA-000055","RELIEF OF MCCRAE-ELSEY","REL",211.3]
[null,null,null,null,null,null,"BAA-PQA-000056","RELIEF OF ERIC-ADA","REL",281.26]
[null,null,null,null,null,"PRA","BAA-PRA-000045","VVC PILOT - FEASIBILITY INVESTIGATION","REL",190382.07]
[null,null,null,null,null,null,"BAA-PRA-000046","GRID STABILITY - MINIMUM DEMAND - PRA","REL",51882.76]
[null,null,null,null,null,null,"BAA-PRA-000047","Comms Network: Expansion & Strengthening","REL",14258.76]
[null,null,null,null,null,"PRB","BAA-PRB-000002","R2022> FLISR: RCGS Roll Out Program","CLSD",2329671.69]
[null,null,null,null,null,null,"BAA-PRB-000003","R2023> FLISR: RCGS Roll Out Program","REL",1365487.55]
[null,null,null,null,null,"Result",null,null,null,49043653.420000002]
[null,null,null,"Overall Result",null,null,null,null,null,49043653.420000002]

{"sheet":"2021-22","index":14,"n_rows":61,"n_cols":9,"rows_kept":61,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[null,null,null,"Select Report from below:"]
[null,null,null,"Period: ","Start","007.2021","End","006.2022"]
[]
[null,null,null,"","","","","","SCS/ACS Capex Exclude Overheads"]
[null,null,null,"WBS - Regulatory Category C (MAT)",null,"WBS - Mat Code","Work Breakdown Structure Element (WBS Element)",null,"AUD"]
[null,null,null,"C44","AUGEX","DOA","BAA-DOA-000023","Augment BTS-FF 22kV Loop - Sub Trans",8750]
[null,null,null,null,null,null,"BAA-DOA-000024","KTS-BY-ES 66kV loop capacity constraint",60343.02]
[null,null,null,null,null,null,"BAA-DOA-000026","KTS 66kV SPLIT LOOP - ACCESS RAMP WORKS",131536.17000000001]
[null,null,null,null,null,null,"BAA-DOA-000027","NO GO ZONE BREACH RECTIFICATION WORKS",175775.71]
[null,null,null,null,null,null,"BAA-DOA-800011","Rearr KTS-MAT-AW-PV-KTS 66kV split loop",1263073.57]
[null,null,null,null,null,"DSH","BAA-DSH-000002","COO & ST Feeder capacity constraint",195459.69]
[null,null,null,null,null,null,"BAA-DSH-000008","cj20nversion Stage 6 (HV feeders)",1429.24]
[null,null,null,null,null,null,"BAA-DSH-000016","EP Conversion Stage 5",1147302.82]
[null,null,null,null,null,null,"BAA-DSH-000021","COO & KLO REFCL Feeder Works",9609081.7400000002]
[null,null,null,null,null,null,"BAA-DSH-000025","Reconfigure Feeder – YVE21",7411.82]
[null,null,null,null,null,null,"BAA-DSH-000026","KLO21 Reconfiguration",3516.8]
[null,null,null,null,null,null,"BAA-DSH-000028","Augment Section of NT11",7981.96]
[null,null,null,null,null,null,"BAA-DSH-800065","Reconfigure feeder - ES23",1344275.56]
[null,null,null,null,null,null,"BAA-DSH-800067","Reconfigure feeder - AW3",302817.57]
[null,null,null,null,null,"DSI","BAA-DSI-000005","REFCL - Balancing Works",62733.599999999999]
[null,null,null,null,null,"DSJ","BAA-DSJ-000178","Relief of Wimmera-North",204.18]
[null,null,null,null,null,null,"BAA-DSJ-000200","RELIEF OF BINDI-WIDFORD",21522.7]
[null,null,null,null,null,null,"BAA-DSJ-000208","RELIEF OF CUDMORE-MARKET",134408.91]
[null,null,null,null,null,null,"BAA-DSJ-000210","10KVA DISTRIBUTION SUBSTATION AUGMT 2021",565280.68000000005]
[null,null,null,null,null,null,"BAA-DSJ-000213","RELIEF OF BRUCE-GILBERT",6070.17]
[null,null,null,null,null,null,"BAA-DSJ-000216","RELIEF OF  FLINDERS-THE WALK",123392.78]
[null,null,null,null,null,null,"BAA-DSJ-000217","RELIEF OF GOWANBRAE-SEGGAN",64614.02]
[null,null,null,null,null,null,"BAA-DSJ-000218","RELIEF OF HALL-BURBANK AND BURBANK-KATRI",167560.57999999999]
[null,null,null,null,null,null,"BAA-DSJ-000219","RELIEF OF WHITE-DUKE",104731.06]
[null,null,null,null,null,null,"BAA-DSJ-000220","RELIEF OF GROSVENOR-FLORENCE",63453.84]
[null,null,null,null,null,null,"BAA-DSJ-000221","RELIEF OF EMU RD-P2",42162.79]
[null,null,null,null,null,null,"BAA-DSJ-000222","RELIEF OF CHRISTINA-BARBARA",69855.66]
[null,null,null,null,null,null,"BAA-DSJ-000223","RELIEF OF CANNES-CAPRI",96399.06]
[null,null,null,null,null,null,"BAA-DSJ-000224","RELIEF OF BONWICK-BASIL",237240.14]
[null,null,null,null,null,null,"BAA-DSJ-000225","RELIEF OF  GRAHAM-GIBSON",117966.76]
[null,null,null,null,null,null,"BAA-DSJ-000226","RELIEF OF HILTON-WEST",71499.13]
[null,null,null,null,null,null,"BAA-DSJ-000227","RELIEF OF VALLEY LAKE – STEELE CREEK",-27.14]
[null,null,null,null,null,null,"BAA-DSJ-000228","RELIEF OF RENOWN-KERFERED",78246.7]
[null,null,null,null,null,null,"BAA-DSJ-000230","2021-Minor Works (DSJ+PQA)",77447.7]
[null,null,null,null,null,null,"BAA-DSJ-000232","2022-Minor Works (DSJ+PQA)",51142.91]
[null,null,null,null,null,"DZA","BAA-DZA-000039","EP CONVERSION STAGE 6",300002.81]
[null,null,null,null,null,null,"BAA-DZA-000043","YVE, FE, FW, TH NETWORK DEVELOPMENT",285326.27]
[null,null,null,null,null,null,"BAA-DZA-800028","REFCL Works at COO",12627235.380000001]
[null,null,null,null,null,null,"BAA-DZA-888888","Capacity Development - DZA",195974.49]
[null,null,null,null,null,"PQA","BAA-PQA-000034","Active Voltage Control",35880.559999999998]
[null,null,null,null,null,null,"BAA-PQA-000040","RELIEF OF HOME-TAIT & COLLINGWOOD-HOME",17545.240000000002]
[null,null,null,null,null,null,"BAA-PQA-000042","RELIEF OF FEHON-SOMERVILLE",180686.77]
[null,null,null,null,null,null,"BAA-PQA-000043","RELIEF OF CARROL-ORRONG & CARROL-WHITELA",111152.08]
[null,null,null,null,null,null,"BAA-PQA-000044","RELIEF OF GRAHAM 138-SYLVIA",44433.2]
[null,null,null,null,null,null,"BAA-PQA-000047","RELIEF OF WEBB-QUEENSVILLE",23687.09]
[null,null,null,null,null,null,"BAA-PQA-000049","RELIEF OF MELBOURNE-PASCO",15208.41]
[null,null,null,null,null,"PRA","BAA-PRA-000042","INSTALLATION OF TRANSFORMER MONITORING S",99822]
[null,null,null,null,null,null,"BAA-PRA-000043","RCGS Roll Out - FLISR",-110142.75]
[null,null,null,null,null,"PRB","BAA-PRB-000002","R2022> FLISR: RCGS Roll Out Program",3189911.72]
[null,null,null,null,null,"Result",null,null,33431385.170000002]
[null,null,null,"Overall Result",null,null,null,null,33431385.170000002]

{"sheet":"2020-21","index":15,"n_rows":70,"n_cols":10,"rows_kept":70,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[null,null,null,"Select Report from below:"]
[null,null,null,"Period: ","Start","007.2020","End","006.2021"]
[]
[null,null,null,"","","","","","","SCS/ACS Capex Exclude Overheads"]
[null,null,null,"WBS - Regulatory Category C (MAT)",null,"WBS - Mat Code","Work Breakdown Structure Element (WBS Element)",null,"WBS - System Status","AUD"]
[null,null,null,"C44","AUGEX","DOA","BAA-DOA-000021","P Conversion Stage 6 (subtrans line)","CLSD",-9740.41]
[null,null,null,null,null,null,"BAA-DOA-000024","KTS-BY-ES 66kV loop capacity constraint","CLSD",99145.53]
[null,null,null,null,null,null,"BAA-DOA-000025","TSTS-HB-L-Q capacity constraint","CLSD",-308.48]
[null,null,null,null,null,null,"BAA-DOA-800011","Rearr KTS-MAT-AW-PV-KTS 66kV split loop","CLSD",6553104.6600000001]
[null,null,null,null,null,null,"BAA-DOA-800015","Augment BTS-NS 22kV loop","REL",8256.7099999999991]
[null,null,null,null,null,"DSH","BAA-DSH-000002","COO & ST Feeder capacity constraint","CLSD",30479.34]
[null,null,null,null,null,null,"BAA-DSH-000005","YVE Feeder Capacity Constraint","CLSD",-13003.31]
[null,null,null,null,null,null,"BAA-DSH-000008","cj20nversion Stage 6 (HV feeders)","CLSD",23459.439999999999]
[null,null,null,null,null,null,"BAA-DSH-000016","EP Conversion Stage 5","CLSD",1574016.13]
[null,null,null,null,null,null,"BAA-DSH-000020","Central 11kV feeder capacity constraint","CLSD",-994.93]
[null,null,null,null,null,null,"BAA-DSH-000021","COO & KLO REFCL Feeder Works","CLSD",711223.02]
[null,null,null,null,null,null,"BAA-DSH-000023","AUGMENT CS5","REL",10729.66]
[null,null,null,null,null,null,"BAA-DSH-000025","Reconfigure Feeder – YVE21","CLSD",14624.2]
[null,null,null,null,null,null,"BAA-DSH-800025","PV Thermal Capacity Constraint","CLSD",459347.44]
[null,null,null,null,null,null,"BAA-DSH-800065","Reconfigure feeder - ES23","CLSD",228487.7]
[null,null,null,null,null,null,"BAA-DSH-800067","Reconfigure feeder - AW3","CLSD",365559.74]
[null,null,null,null,null,"DSI","BAA-DSI-800074","Establish Tie Line - SBY13 and SBY23","REL",52073.56]
[null,null,null,null,null,"DSJ","BAA-DSJ-000178","Relief of Wimmera-North","CLSD",162670.13]
[null,null,null,null,null,null,"BAA-DSJ-000198","RELIEF OF FOCH-QUEEN","CLSD",38.01]
[null,null,null,null,null,null,"BAA-DSJ-000199","RELIEF OF MAUDE-MELBOURNE","CLSD",198970.21]
[null,null,null,null,null,null,"BAA-DSJ-000200","RELIEF OF BINDI-WIDFORD","CLSD",35607.65]
[null,null,null,null,null,null,"BAA-DSJ-000201","RELIEF OF DERRY-ABERDEEN","CLSD",34802.81]
[null,null,null,null,null,null,"BAA-DSJ-000202","RELIEF OF HEATHERLEA-STERLING","CLSD",4010.21]
[null,null,null,null,null,null,"BAA-DSJ-000205","2020-Minor Works DSJ & PQA","CLSD",24848.62]
[null,null,null,null,null,null,"BAA-DSJ-000206","Relief Of Steele Creek-Basalt","CLSD",35335.19]
[null,null,null,null,null,null,"BAA-DSJ-000207","Relief Of Stockwell Dr-P7","CLSD",66.900000000000006]
[null,null,null,null,null,null,"BAA-DSJ-000208","RELIEF OF CUDMORE-MARKET","CLSD",10092.379999999999]
[null,null,null,null,null,null,"BAA-DSJ-000210","10KVA DISTRIBUTION SUBSTATION AUGMT 2021","CLSD",462621.45]
[null,null,null,null,null,null,"BAA-DSJ-000212","2020-Minor Works (DSJ+PQA)","CLSD",85787.13]
[null,null,null,null,null,null,"BAA-DSJ-000213","RELIEF OF BRUCE-GILBERT","CLSD",72502.53]
[null,null,null,null,null,null,"BAA-DSJ-000216","RELIEF OF  FLINDERS-THE WALK","CLSD",12052.52]
[null,null,null,null,null,null,"BAA-DSJ-000217","RELIEF OF GOWANBRAE-SEGGAN","CLSD",10605.82]
[null,null,null,null,null,null,"BAA-DSJ-000218","RELIEF OF HALL-BURBANK AND BURBANK-KATRI","CLSD",20592.89]
[null,null,null,null,null,null,"BAA-DSJ-000219","RELIEF OF WHITE-DUKE","CLSD",11547.33]
[null,null,null,null,null,null,"BAA-DSJ-000220","RELIEF OF GROSVENOR-FLORENCE","CLSD",11263.21]
[null,null,null,null,null,null,"BAA-DSJ-000221","RELIEF OF EMU RD-P2","CLSD",4717.1899999999996]
[null,null,null,null,null,null,"BAA-DSJ-000222","RELIEF OF CHRISTINA-BARBARA","CLSD",6035.94]
[null,null,null,null,null,null,"BAA-DSJ-000223","RELIEF OF CANNES-CAPRI","CLSD",7123.45]
[null,null,null,null,null,null,"BAA-DSJ-000224","RELIEF OF BONWICK-BASIL","CLSD",11196.45]
[null,null,null,null,null,null,"BAA-DSJ-000225","RELIEF OF  GRAHAM-GIBSON","CLSD",6223.71]
[null,null,null,null,null,null,"BAA-DSJ-000226","RELIEF OF HILTON-WEST","CLSD",5012.25]
[null,null,null,null,null,null,"BAA-DSJ-000227","RELIEF OF VALLEY LAKE – STEELE CREEK","CLSD",340.39]
[null,null,null,null,null,null,"BAA-DSJ-000228","RELIEF OF RENOWN-KERFERED","CLSD",5959.08]
[null,null,null,null,null,null,"BAA-DSJ-000230","2021-Minor Works (DSJ+PQA)","CLSD",4638.92]
[null,null,null,null,null,null,"BAA-DSJ-800109","Relief of Westward Ho - Spyglass","CLSD",91345.72]
[null,null,null,null,null,"DZA","BAA-DZA-000039","EP CONVERSION STAGE 6","REL",4292.0600000000004]
[null,null,null,null,null,null,"BAA-DZA-800010","P Conversion Stage 6 (PTN)","CLSD",268129.38]
[null,null,null,null,null,null,"BAA-DZA-800026","Redevelop Zone Substation - SBY","CLSD",40501.949999999997]
[null,null,null,null,null,null,"BAA-DZA-800028","REFCL Works at COO","CLSD",1582140.43]
[null,null,null,null,null,null,"BAA-DZA-888888","Capacity Development - DZA","REL",-84927.64]
[null,null,null,null,null,"PQA","BAA-PQA-000034","Active Voltage Control","CLSD",44520.99]
[null,null,null,null,null,null,"BAA-PQA-000039","MINOR PQA WORK","CLSD",19742.14]
[null,null,null,null,null,null,"BAA-PQA-000040","RELIEF OF HOME-TAIT & COLLINGWOOD-HOME","CLSD",5365.06]
[null,null,null,null,null,null,"BAA-PQA-000042","RELIEF OF FEHON-SOMERVILLE","CLSD",111102.62]
[null,null,null,null,null,null,"BAA-PQA-000044","RELIEF OF GRAHAM 138-SYLVIA","CLSD",185295.45]
[null,null,null,null,null,null,"BAA-PQA-000046","RELIEF OF ALOHA-WATT","CLSD",134980.12]
[null,null,null,null,null,null,"BAA-PQA-000047","RELIEF OF WEBB-QUEENSVILLE","CLSD",119774.03]
[null,null,null,null,null,"PRA","BAA-PRA-000043","RCGS Roll Out - FLISR","CLSD",110142.75]
[null,null,null,null,null,"Result",null,null,null,13983527.43]
[null,null,null,"Overall Result",null,null,null,null,null,13983527.43]