## Cover
Powercor
Revised regulatory proposal 2026-31
REFCL reliability
| Model number: | 3.3.12
2025-12-01
15

## Summary
Powercor
REFCL reliability
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Install A-Eberle Fault Passage Indicators |  | -8.1085 | 17.7826 | 9.6741
| Option 3 | Install NOJA ACR's |  | -13.0323 | 17.7826 | 4.7503
| Option 4 | 0
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Install A-Eberle Fault Passage Indicators |  | 9.6741
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 0 | 4.1039 | 4.1039 | 4.1039 | 0 |  | 12.3116
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
Capex and risk ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 9.6741 | 4.7503 |  |  |  | Option 2
| Capex 10% higher |  | 0 | 8.8633 | 3.4471 |  |  |  | Option 2
| Capex 10% lower |  | 0 | 10.485 | 6.0535 |  |  |  | Option 2
| Increasing wind escalation |  | 0 | 12.3415 | 4.8837 |  |  |  | Option 2
|  |  | 0 | 9.6741 | 4.7503 |  |  |  | Option 2
|  |  | 0 | 9.6741 | 4.7503 |  |  |  | Option 2
0
| 0 | [6 empty] | 0
0
0

## Assumptions
Powercor
REFCL reliability
Project
|  | Business: | Powercor
|  | Descripton: | REFCL reliability
|  | Date of cost inputs: | December |  | 2023
|  | Option | Description
|  | Option 1 (base case) | No change to existing practices
|  | Option 2 | Install A-Eberle Fault Passage Indicators
|  | Option 3 | Install NOJA ACR's
Option 4
Option 5
|  | Compliance project | No
|  | Expenditure starts | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  | 3.5% | [real_disc]
|  | VCR date |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  | 20 | [years]\
|  | Output dollars |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  | 2023-06-30
VCR
|  |  | Weighted network average VCR |  |  | 44996.7205 | 2023 VCR ($/MWh)
|  |  | Domestic |  |  | 25335.7556 | 35.87%
|  |  | Commercial |  |  | 52200 | 49.77%
|  |  | Industrial |  |  | 74790 | 11.69%
|  |  | Agricultural |  |  | 44400 | 2.66%
|  |  | Others |  |  | 0 | 0%
Risks
SAFETY
|  | Value of statistical life |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  | 1
|  | Harm to property from bushfire |  |  | 1
|  | Harm to environment |  |  | 1
|  | Safety - Public trespass |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  | 3
|  | Safety from bushfire in HBRA |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  | 10
^ Public or employee
|  | Incident type |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  | 20%
Other benefits
| ENVIRONMENTAL | [7 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  | Value
|  | Reliability in worst-served areas |  |  | 67500 | 2023-12-31 | per MWh
|  | Network resilience |  |  | 24590 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  | 88.3577 | 2023-12-31 | per MWh
|  | Aesthetics |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Communication |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[5 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  | -10% | 0%
| 3 | Increasing wind escalation |  |  | 0% | 15%
| 4 |  |  |  | 0% | 0%
| 5 |  |  |  | 0% | 0%

## Option1 (base case)
Powercor
REFCL reliability
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868
| Energy at risk value | $/MWh | 44996.7205 | 2023-12-31 |  | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357
| Safety consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357 | 38737084.357
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental reliability in worst-served areas | $/MWh | 22503.2795 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (domestic) | $/MWh | 25335.7556 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (commercial) | $/MWh | 52200 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (industrial) | $/customer | 74790 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (agricultural) | $/customer min | 44400 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (others) | $/customer min | 0 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Increasing wind escalation | 0% | 15% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 |  | 0% | 0% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 |  | 0% | 0% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
Powercor
REFCL reliability
OPTION 2 | Install A-Eberle Fault Passage Indicators
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Install A-Eberle Fault Passage Indicators |  | 30 | 2023-12-31 | 0 | 3708212.6667 | 3708212.6667 | 3708212.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 3708212.6667 | 3708212.6667 | 3708212.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 860.8868 | 860.8868 | 851.0601 | 841.2333 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066
| Energy at risk value | $/MWh | 44996.7205 | 2023-12-31 | 38737084.357 | 38737084.357 | 38294913.1074 | 37852741.8579 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 38737084.357 | 38737084.357 | 38294913.1074 | 37852741.8579 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental reliability in worst-served areas | $/MWh | 22503.2795 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (domestic) | $/MWh | 25335.7556 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (commercial) | $/MWh | 52200 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (industrial) | $/customer | 74790 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (agricultural) | $/customer min | 44400 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (others) | $/customer min | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 442171.2496 | 884342.4991 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487
Capital expenditure
| Install A-Eberle Fault Passage Indicators |  |  | 2023-12-31 | 0 | -3708212.6667 | -3708212.6667 | -3708212.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Install A-Eberle Fault Passage Indicators |  |  | 2023-12-31 | 0 | -3708212.6667 | -7416425.3333 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638 | -11124638
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Install A-Eberle Fault Passage Indicators |  |  | 2023-12-31 | 0 | 0 | -201620.4606 | -403240.9211 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | -201620.4606 | -403240.9211 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | -201620.4606 | -403240.9211 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 442171.2496 | 884342.4991 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 240550.789 | 481101.578 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367
| First capex year |  |  | 2
| First year |  |  | 2
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 0 | 240550.789 | 481101.578 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367
| Total annualised capex |  |  |  | 0 | 0 | -201620.4606 | -403240.9211 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817 | -604861.3817
| Total benefits |  |  |  | 0 | 0 | 442171.2496 | 884342.4991 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 0 | 220388.7429 | 440777.4859 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288 | 661166.2288
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 0 | 260712.835 | 521425.6701 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051 | 782138.5051
sens3 | Increasing wind escalation | 0% | 15% | Option 2sens3 | 0 | 0 | 306876.4764 | 613752.9528 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293 | 920629.4293
sens4 |  | 0% | 0% | Option 2sens4 | 0 | 0 | 240550.789 | 481101.578 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367
sens5 |  | 0% | 0% | Option 2sens5 | 0 | 0 | 240550.789 | 481101.578 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 240550.789 | 481101.578 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 240550.789 | 481101.578 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 240550.789 | 481101.578 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367 | 721652.367

## Option3
Powercor
REFCL reliability
OPTION 3 | Install NOJA ACR's
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Install NOJA ACR's |  | 30 | 2023-12-31 | 0 | 5960000 | 5960000 | 5960000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 5960000 | 5960000 | 5960000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 860.8868 | 860.8868 | 851.0601 | 841.2333 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066
| Energy at risk value | $/MWh | 44996.7205 | 2023-12-31 | 38737084.357 | 38737084.357 | 38294913.1074 | 37852741.8579 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 38737084.357 | 38737084.357 | 38294913.1074 | 37852741.8579 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083 | 37410570.6083
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental reliability in worst-served areas | $/MWh | 22503.2795 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (domestic) | $/MWh | 25335.7556 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (commercial) | $/MWh | 52200 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (industrial) | $/customer | 74790 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (agricultural) | $/customer min | 44400 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (others) | $/customer min | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 442171.2496 | 884342.4991 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487
Capital expenditure
| Install NOJA ACR's |  |  | 2023-12-31 | 0 | -5960000 | -5960000 | -5960000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Install NOJA ACR's |  |  | 2023-12-31 | 0 | -5960000 | -11920000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000 | -17880000
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Install NOJA ACR's |  |  | 2023-12-31 | 0 | 0 | -324053.1364 | -648106.2728 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | -324053.1364 | -648106.2728 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | -324053.1364 | -648106.2728 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 442171.2496 | 884342.4991 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 118118.1132 | 236236.2263 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395
| First capex year |  |  | 2
| First year |  |  | 2
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 0 | 118118.1132 | 236236.2263 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395
| Total annualised capex |  |  |  | 0 | 0 | -324053.1364 | -648106.2728 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091 | -972159.4091
| Total benefits |  |  |  | 0 | 0 | 442171.2496 | 884342.4991 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487 | 1326513.7487
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 0 | 85712.7995 | 171425.5991 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986 | 257138.3986
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 0 | 150523.4268 | 301046.8536 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804 | 451570.2804
sens3 | Increasing wind escalation | 0% | 0.75% | Option 3sens3 | 0 | 0 | 121434.3975 | 242868.7951 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926 | 364303.1926
sens4 |  | 0% | 0% | Option 3sens4 | 0 | 0 | 118118.1132 | 236236.2263 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395
sens5 |  | 0% | 0% | Option 3sens5 | 0 | 0 | 118118.1132 | 236236.2263 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 118118.1132 | 236236.2263 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 118118.1132 | 236236.2263 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 118118.1132 | 236236.2263 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395 | 354354.3395

## Option4
Powercor
REFCL reliability
OPTION 4 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 44996.7205 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental reliability in worst-served areas | $/MWh | 22503.2795 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (domestic) | $/MWh | 25335.7556 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (commercial) | $/MWh | 52200 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (industrial) | $/customer | 74790 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (agricultural) | $/customer min | 44400 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (others) | $/customer min | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Increasing wind escalation | 0% | 15% | Option 4sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 |  | 0% | 0% | Option 4sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 |  | 0% | 0% | Option 4sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option5
Powercor
REFCL reliability
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 44996.7205 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental reliability in worst-served areas | $/MWh | 22503.2795 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (domestic) | $/MWh | 25335.7556 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (commercial) | $/MWh | 52200 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (industrial) | $/customer | 74790 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (agricultural) | $/customer min | 44400 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (others) | $/customer min | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Increasing wind escalation | 0% | 15% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 |  | 0% | 0% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 |  | 0% | 0% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
Powercor
REFCL reliability
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 718824258.2871 | 2026-06-30 |  | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 641036984.0053 | 2026-06-30 |  | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104 | 42870192.2104
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 698377931.8786 | 2026-06-30 |  | 42870192.2104 | 42870192.2104 | 42380842.8757 | 41891493.541 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063
Option 2 | Capital expenditure | Option 2Capital expenditure | -11301466.9898 | 2026-06-30 |  | 0 | -4103865.6475 | -4103865.6475 | -4103865.6475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 623254407.0895 | 2026-06-30 |  | 42870192.2104 | 42870192.2104 | 42380842.8757 | 41891493.541 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -8108467.8198 | 2026-06-30 |  | 0 | 0 | -223132.64 | -446265.28 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | -669397.92 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 17782576.9158 | 2026-06-30 |  | 0 | 0 | 489349.3347 | 978698.6694 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 0 | 266216.6947 | 532433.3894 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 9674109.0959 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -8108467.8198 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 17782576.9158 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 698377931.8786 | 2026-06-30 |  | 42870192.2104 | 42870192.2104 | 42380842.8757 | 41891493.541 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063
Option 3 | Capital expenditure | Option 3Capital expenditure | -18164207.2109 | 2026-06-30 |  | 0 | -6595910.6065 | -6595910.6065 | -6595910.6065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 623254407.0895 | 2026-06-30 |  | 42870192.2104 | 42870192.2104 | 42380842.8757 | 41891493.541 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 41402144.2063 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -13032280.6566 | 2026-06-30 |  | 0 | 0 | -358628.4428 | -717256.8857 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | -1075885.3285 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 17782576.9158 | 2026-06-30 |  | 0 | 0 | 489349.3347 | 978698.6694 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 1468048.0041 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 0 | 130720.8919 | 261441.7837 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 4750296.2592 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -13032280.6566 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 17782576.9158 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 0 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | 0 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 0 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0.6694 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702 | 42.8702
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 860.8868 |  |  | Energy at risk energy at risk (weighted) | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868
Option 1 (base case) | Energy at risk value | 38.7371 |  |  | Option 1 (base case) risk cost | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371 | 38.7371

## Sensitivity_calcs
Powercor
REFCL reliability
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE
[7 empty] | 46203 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 798650.0841 | 798650.0841 | 798650.0841 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Increasing wind escalation | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 |  | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 |  | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 9674109.0959 |  | 0 | 0 | 0 | 266216.6947 | 532433.3894 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 8863262.3139 |  | 0 | 0 | 0 | 243903.4307 | 487806.8614 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 731710.2921 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 10484955.8779 |  | 0 | 0 | 0 | 288529.9587 | 577059.9174 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 865589.8761 | 0 | 0 | 0 | 0
Option 2 | sens3 | Increasing wind escalation | Option 2sens3 |  | 12341495.6333 |  | 0 | 0 | 0 | 339619.0949 | 679238.1898 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 1018857.2847 | 0 | 0 | 0 | 0
Option 2 | sens4 |  | Option 2sens4 |  | 9674109.0959 |  | 0 | 0 | 0 | 266216.6947 | 532433.3894 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 0 | 0 | 0 | 0
Option 2 | sens5 |  | Option 2sens5 |  | 9674109.0959 |  | 0 | 0 | 0 | 266216.6947 | 532433.3894 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 9674109.0959 |  | 0 | 0 | 0 | 266216.6947 | 532433.3894 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 9674109.0959 |  | 0 | 0 | 0 | 266216.6947 | 532433.3894 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 9674109.0959 |  | 0 | 0 | 0 | 266216.6947 | 532433.3894 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 798650.0841 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 130720.8919 | 261441.7837 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 4750296.2592 |  | 0 | 0 | 0 | 130720.8919 | 261441.7837 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 3447068.1935 |  | 0 | 0 | 0 | 94858.0476 | 189716.0952 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 284574.1427 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 6053524.3248 |  | 0 | 0 | 0 | 166583.7361 | 333167.4723 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 499751.2084 | 0 | 0 | 0 | 0
Option 3 | sens3 | Increasing wind escalation | Option 3sens3 |  | 4883665.586 |  | 0 | 0 | 0 | 134391.0119 | 268782.0237 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 403173.0356 | 0 | 0 | 0 | 0
Option 3 | sens4 |  | Option 3sens4 |  | 4750296.2592 |  | 0 | 0 | 0 | 130720.8919 | 261441.7837 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 0 | 0 | 0 | 0
Option 3 | sens5 |  | Option 3sens5 |  | 4750296.2592 |  | 0 | 0 | 0 | 130720.8919 | 261441.7837 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 4750296.2592 |  | 0 | 0 | 0 | 130720.8919 | 261441.7837 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 4750296.2592 |  | 0 | 0 | 0 | 130720.8919 | 261441.7837 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 4750296.2592 |  | 0 | 0 | 0 | 130720.8919 | 261441.7837 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 392162.6756 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Increasing wind escalation | Option 4sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 |  | Option 4sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 |  | Option 4sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Increasing wind escalation | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 |  | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 |  | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | FALSE | FALSE | FALSE | TRUE | TRUE | 2028-29: FALSE
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 9.6741 | 4.7503 |  |  | 2026-27: 9.6741; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 8.8633 | 3.4471 |  |  | 2026-27: 8.8633; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 10.485 | 6.0535 |  |  | 2026-27: 10.485; 2028-29: Option 2
sens3 | Increasing wind escalation | 0 | 12.3415 | 4.8837 |  |  | 2026-27: 12.3415; 2028-29: Option 2
sens4 |  | 0 | 9.6741 | 4.7503 |  |  | 2026-27: 9.6741; 2028-29: Option 2
sens5 |  | 0 | 9.6741 | 4.7503 |  |  | 2026-27: 9.6741; 2028-29: Option 2
sens | 0 | [5 empty] | 2026-27: 0
sens | 0 | [5 empty] | 2026-27: 0
sens | 0 | [5 empty] | 2026-27: 0

## Workings_costs
Powercor
REFCL reliability
WORKINGS - COSTS
SCOPE
The introduction of REFCL technology has disrupted the traditional means of maintaining reliability of supply during network earth fault events due to the rapid reduction in fault currents resulting from REFCL operation. Traditional methods utilised the passage of these fault currents and time-based coordination to provide fault indication through remote controlled gas switches.
With the loss of the ability to sense earth faults past remote controlled switches, restoration times for feeder and ACR outages have increased.
This project involves the installation of REFCL compliant earth fault passage indicators adjacent to 149 existing remote controlled switch sites across the REFCL network. This will restore the ability to detect earth faults along the REFCL protected network and allow the use of these indication to sectionalise and restore customers quicker.
NUMBER OF FEEDERS
Location of Remote Controllable Switch of REFCL Protected Feeders
|  | Zone Substation | Total
|  | ART | 4
|  | BAN | 19
|  | BAS | 14
|  | BETS | 10
|  | BGO | 1
|  | CDN | 1
|  | CLC | 21
|  | CMN | 6
|  | CTN | 4
|  | GHP | 8
|  | GSB | 4
|  | HTN | 4
|  | KRT | 4
|  | MRO | 3
|  | TQY | 16
|  | TRG | 4
|  | WIN | 5
|  | WND | 13
|  | WPD | 8
|  | Total | 149
COST
|  |  | Volume | Cost per Unit ($2023) | Indicative Cost
| Option 2 | Install A-Eberele FI's | 149 | 74662 | 11124638
| Option 3 | Install NOJA ACR's | 149 | 120000 | 17880000
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31
|  | % pa | 0% | 33.33% | 33.33% | 33.33% | 0%

## Workings_risks
Powercor
REFCL reliability
WORKINGS - BENEFITS
1. REFCL Feeder Performance
|  | SAIDI saving | SAIFI Saving
|  | 5% | 2.5%
|  | Feeder | Feeder Category | Network SAIDI | Network SAIFI | Network MAIFIe | Energy Not Supplied | Smart ACR Benefit | Updated Energy Not Supplied (Less Smart ACR's) | SAIDI Saving | SAIFI Saving | MAIFIe Saving | CMOS Saving | Sustained Cust Int Saving | Momentary Cust Int Saving | Energy Not Supplied Saved | No Switches
|  | ART031 | Rural Short | 0.050137 | 0.00032275 | 0.0018585 | 1.1051 | 0.89895 | 0.20612 | 0.00046758 | 1.505e-06 | -1.505e-06 | 428.4619 | 1.3791 | -1.3791 | 0.0077454 | 1
|  | ART033 | Rural Long | 0.4205 | 0.0061107 | 0.0054354 | 13.6975 | 1.7979 | 11.8996 | 0.018266 | 0.00013272 | -0.00013272 | 16737.4523 | 121.6127 | -121.6127 | 0.40742 | 3
|  | BAN003 | Rural Long | 2.0148 | 0.032435 | 0.025221 | 69.2024 | 8.9895 | 60.2129 | 0.087652 | 0.00070554 | -0.00070554 | 80318.9229 | 646.5167 | -646.5167 | 2.0282 | 8
|  | BAN005 | Urban | 0.063648 | 0.00041841 | 0.00040949 | 1.3109 | 0 | 1.3109 | 0.0031824 | 1.046e-05 | -1.046e-05 | 2916.1846 | 9.5852 | -9.5852 | 0.054856 | 1
|  | BAN006 | Rural Long | 1.001 | 0.019496 | 0.014511 | 38.4748 | 3.5958 | 34.879 | 0.045374 | 0.00044184 | -0.00044184 | 41578.432 | 404.8765 | -404.8765 | 1.1314 | 2
|  | BAN008 | Rural Long | 0.89078 | 0.023874 | 0.027868 | 43.1656 | 4.4947 | 38.6708 | 0.039901 | 0.00053471 | -0.00053471 | 36563.2767 | 489.9747 | -489.9747 | 1.1504 | 3
|  | BAN009 | Rural Long | 0.6616 | 0.011187 | 0.0061811 | 23.1499 | 2.6968 | 20.4531 | 0.029226 | 0.00024709 | -0.00024709 | 26781.3578 | 226.4216 | -226.4216 | 0.68886 | 2
|  | BAN013 | Urban | 0 | 0 | 0.00024217 | 0.016008 | 0 | 0.016008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
|  | BAN015 | Rural Short | 0.095651 | 0.0057538 | 0.017681 | 7.4376 | 0.89895 | 6.5387 | 0.0042045 | 0.00012646 | -0.00012646 | 3852.7638 | 115.8805 | -115.8805 | 0.15797 | 1
|  | BAS011 | Rural Long | 1.1626 | 0.016719 | 0.012214 | 37.4069 | 6.2926 | 31.1143 | 0.04835 | 0.00034767 | -0.00034767 | 44305.2906 | 318.5826 | -318.5826 | 1.0746 | 4
|  | BAS022 | Rural Long | 1.3043 | 0.021176 | 0.027435 | 46.0334 | 1.7979 | 44.2355 | 0.062668 | 0.00050872 | -0.00050872 | 57425.7274 | 466.1595 | -466.1595 | 1.4546 | 4
|  | BAS032 | Rural Short | 0.23068 | 0.0053914 | 0.012681 | 8.6863 | 0.89895 | 7.7874 | 0.01034 | 0.00012084 | -0.00012084 | 9475.3832 | 110.7277 | -110.7277 | 0.23977 | 1
|  | BAS033 | Rural Long | 0.92738 | 0.019936 | 0.0069652 | 37.2118 | 3.5958 | 33.616 | 0.041888 | 0.00045023 | -0.00045023 | 38384.0398 | 412.5649 | -412.5649 | 1.0895 | 5
|  | BET001 | Rural Long | 0.37055 | 0.0055672 | 0.014 | 13.1331 | 1.7979 | 11.3352 | 0.015991 | 0.00012013 | -0.00012013 | 14653.4674 | 110.076 | -110.076 | 0.36088 | 2
|  | BET002 | Urban | 0 | 0 | 0.0046249 | 0.30572 | 0.89895 | -0.59323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
|  | BET004 | Rural Short | 0.29158 | 0.0044944 | 0.0039046 | 8.1823 | 0.89895 | 7.2833 | 0.012977 | 0.00010002 | -0.00010002 | 11891.4762 | 91.6483 | -91.6483 | 0.26052 | 1
|  | BET005 | Rural Long | 0.8873 | 0.0087221 | 0.0092537 | 23.8742 | 2.6968 | 21.1774 | 0.039353 | 0.00019342 | -0.00019342 | 36061.0957 | 177.2403 | -177.2403 | 0.77939 | 2
|  | BET006 | Rural Long | 0.97773 | 0.022563 | 0.01932 | 42.1262 | 3.5958 | 38.5304 | 0.044714 | 0.00051592 | -0.00051592 | 40973.0346 | 472.7637 | -472.7637 | 1.2006 | 2
|  | BET007 | Rural Long | 0.20724 | 0.0034141 | 0.0059289 | 7.5166 | 3.5958 | 3.9208 | 0.0054051 | 4.4522e-05 | -4.4522e-05 | 4952.928 | 40.7969 | -40.7969 | 0.12615 | 2
|  | BGO022 | Urban | 0.30677 | 0.0035977 | 0.0064467 | 7.9201 | 1.7979 | 6.1222 | 0.011857 | 6.9525e-05 | -6.9525e-05 | 10864.63 | 63.7085 | -63.7085 | 0.2276 | 1
|  | CDN004 | Rural Long | 0.11199 | 0.0019166 | 0.00051101 | 3.8957 | 2.6968 | 1.1988 | 0.0017231 | 1.4745e-05 | -1.4745e-05 | 1578.9802 | 13.5117 | -13.5117 | 0.040802 | 1
|  | CLC002 | Urban | 0.1149 | 0.0007249 | 0.0055702 | 2.6606 | 0 | 2.6606 | 0.005745 | 1.8123e-05 | -1.8123e-05 | 5264.3938 | 16.6065 | -16.6065 | 0.098449 | 1
|  | CLC003 | Rural Long | 2.2121 | 0.023533 | 0.015273 | 60.8669 | 6.2926 | 54.5743 | 0.099172 | 0.0005275 | -0.0005275 | 90875.9192 | 483.3659 | -483.3659 | 2.0067 | 5
|  | CLC004 | Rural Long | 0.26367 | 0.0051405 | 0.001283 | 9.9056 | 2.6968 | 7.2088 | 0.0095944 | 9.3525e-05 | -9.3525e-05 | 8791.7566 | 85.7006 | -85.7006 | 0.23934 | 2
|  | CLC006 | Rural Long | 0.44328 | 0.0043316 | 0.0028018 | 11.7289 | 1.7979 | 9.931 | 0.018767 | 9.169e-05 | -9.169e-05 | 17196.6553 | 84.019 | -84.019 | 0.37109 | 3
|  | CLC013 | Rural Long | 1.1377 | 0.012771 | 0.030375 | 34.159 | 1.7979 | 32.3611 | 0.053892 | 0.00030246 | -0.00030246 | 49383.2358 | 277.1579 | -277.1579 | 1.1073 | 7
|  | CLC014 | Rural Short | 0.57104 | 0.0059713 | 0.0070934 | 13.5806 | 0.89895 | 12.6816 | 0.026662 | 0.0001394 | -0.0001394 | 24431.7466 | 127.7392 | -127.7392 | 0.48357 | 3
|  | CMN001 | Rural Long | 1.3692 | 0.014793 | 0.009111 | 37.9051 | 1.7979 | 36.1072 | 0.065214 | 0.00035228 | -0.00035228 | 59758.6746 | 322.8097 | -322.8097 | 1.3253 | 4
|  | CMN003 | Rural Long | 0.63705 | 0.0097304 | 0.0036218 | 20.8713 | 3.5958 | 17.2755 | 0.026365 | 0.00020135 | -0.00020135 | 24159.2673 | 184.5054 | -184.5054 | 0.59849 | 1
|  | CMN004 | Rural Long | 0.32978 | 0.0044137 | 0.00039379 | 9.9467 | 0.89895 | 9.0478 | 0.014999 | 0.00010037 | -0.00010037 | 13744.1535 | 91.9744 | -91.9744 | 0.3254 | 1
|  | CTN001 | Rural Long | 0.4772 | 0.005242 | 0.0073779 | 13.6992 | 5.3937 | 8.3055 | 0.014466 | 7.9452e-05 | -7.9452e-05 | 13255.7006 | 72.8055 | -72.8055 | 0.29538 | 2
|  | CTN003 | Rural Long | 0.10677 | 0.0010901 | 0.0038669 | 3.1743 | 2.6968 | 0.47745 | 0.00080295 | 4.0989e-06 | -4.0989e-06 | 735.7764 | 3.756 | -3.756 | 0.016064 | 1
|  | CTN004 | Rural Long | 0.098406 | 0.00087496 | 0.0026657 | 2.6926 | 0.89895 | 1.7937 | 0.0032776 | 1.4571e-05 | -1.4571e-05 | 3003.4295 | 13.3522 | -13.3522 | 0.063277 | 1
|  | GHP011 | Rural Long | 0 | 0 | 0.0013789 | 0.12754 | 1.7979 | -1.6704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
|  | GHP012 | Rural Short | 0 | 0 | 0.0008013 | 0.054496 | 0.89895 | -0.84445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
|  | GHP021 | Rural Long | 0 | 0 | 0 | 0 | 2.6968 | -2.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
|  | GHP022 | Rural Long | 0.019054 | 0.0004701 | 0.00046876 | 0.86463 | 0.89895 | -0.034321 | -3.7817e-05 | -4.665e-07 | 4.665e-07 | -34.6536 | -0.42748 | 0.42748 | -0.0010475 | 2
|  | GSB011 | Rural Short | 0.38982 | 0.0050299 | 0.0051908 | 10.1052 | 0.89895 | 9.2062 | 0.017757 | 0.00011456 | -0.00011456 | 16271.6696 | 104.9779 | -104.9779 | 0.33905 | 1
|  | GSB012 | Rural Short | 0.45724 | 0.0084306 | 0.0021034 | 13.7332 | 4.4947 | 9.2385 | 0.015379 | 0.00014178 | -0.00014178 | 14092.799 | 129.9228 | -129.9228 | 0.32694 | 1
|  | GSB013 | Rural Short | 0.23306 | 0.0030219 | 0.0017989 | 5.9652 | 0 | 5.9652 | 0.011653 | 7.5547e-05 | -7.5547e-05 | 10677.9511 | 69.2272 | -69.2272 | 0.22278 | 1
|  | GSB014 | Rural Short | 0.9545 | 0.010418 | 0.0026862 | 22.4477 | 2.6968 | 19.7509 | 0.041992 | 0.00022916 | -0.00022916 | 38478.5798 | 209.9871 | -209.9871 | 0.76911 | 1
|  | HTN012 | Rural Long | 0.14624 | 0.002906 | 0.002962 | 5.7656 | 2.6968 | 3.0688 | 0.003892 | 3.8668e-05 | -3.8668e-05 | 3566.3599 | 35.4331 | -35.4331 | 0.097863 | 1
|  | HTN013 | Rural Long | 0.065191 | 0.0015071 | 0.003993 | 3.0621 | 2.6968 | 0.36524 | 0.0003888 | 4.4941e-06 | -4.4941e-06 | 356.2718 | 4.1182 | -4.1182 | 0.010448 | 1
|  | HTN032 | Rural Long | 0.26042 | 0.0041957 | 0.0090783 | 9.4867 | 0.89895 | 8.5878 | 0.011787 | 9.4953e-05 | -9.4953e-05 | 10800.962 | 87.0091 | -87.0091 | 0.27282 | 1
|  | HTN034 | Rural Long | 0.21039 | 0.0034301 | 0.0063499 | 7.6199 | 6.2926 | 1.3273 | 0.0018324 | 1.4937e-05 | -1.4937e-05 | 1679.0771 | 13.6872 | -13.6872 | 0.042598 | 1
|  | KRT013 | Rural Long | 0.42227 | 0.010535 | 0.0045949 | 18.7608 | 2.6968 | 16.064 | 0.018079 | 0.00022552 | -0.00022552 | 16566.0974 | 206.6495 | -206.6495 | 0.50341 | 3
|  | KRT022 | Rural Short | 0.32659 | 0.0090721 | 0.008421 | 12.8729 | 1.7979 | 11.075 | 0.014049 | 0.00019513 | -0.00019513 | 12873.4029 | 178.8032 | -178.8032 | 0.34996 | 1
|  | MRO005 | Rural Long | 0.38961 | 0.0065462 | 0.0021203 | 13.4441 | 3.5958 | 9.8483 | 0.01427 | 0.00011988 | -0.00011988 | 13076.5222 | 109.8539 | -109.8539 | 0.33553 | 2
|  | MRO007 | Rural Long | 0.50738 | 0.0076068 | 0.0032909 | 16.4953 | 2.6968 | 13.7985 | 0.021222 | 0.00015908 | -0.00015908 | 19446.1916 | 145.771 | -145.771 | 0.47855 | 1
|  | TQY021 | Rural Short | 0.30263 | 0.0048904 | 0.0025775 | 8.5839 | 2.6968 | 5.8871 | 0.010377 | 8.3849e-05 | -8.3849e-05 | 9509.281 | 76.8341 | -76.8341 | 0.21136 | 7
|  | TQY031 | Rural Short | 0.089084 | 0.0015447 | 0.00062991 | 2.6075 | 0.89895 | 1.7085 | 0.0029186 | 2.5304e-05 | -2.5304e-05 | 2674.4112 | 23.1874 | -23.1874 | 0.06079 | 5
|  | TQY032 | Urban | 0.026391 | 0.00094576 | 0 | 1.1704 | 0 | 1.1704 | 0.0013195 | 2.3644e-05 | -2.3644e-05 | 1209.1423 | 21.6659 | -21.6659 | 0.037422 | 4
|  | TRG013 | Rural Long | 0.51496 | 0.0063966 | 0.0050443 | 15.3687 | 5.3937 | 9.9751 | 0.016712 | 0.00010379 | -0.00010379 | 15313.6471 | 95.1098 | -95.1098 | 0.35401 | 2
|  | TRG022 | Rural Long | 0.59392 | 0.0062408 | 0.007777 | 16.5923 | 4.4947 | 12.0976 | 0.021652 | 0.00011376 | -0.00011376 | 19840.2036 | 104.2386 | -104.2386 | 0.43661 | 1
|  | TRG024 | Rural Long | 0.46139 | 0.0052074 | 0.0055652 | 13.2611 | 2.6968 | 10.5643 | 0.018378 | 0.00010371 | -0.00010371 | 16840.6216 | 95.0336 | -95.0336 | 0.37821 | 1
|  | WIN011 | Rural Long | 0.31163 | 0.006497 | 0.012995 | 13.2563 | 0.89895 | 12.3573 | 0.014525 | 0.00015141 | -0.00015141 | 13309.6675 | 138.7435 | -138.7435 | 0.37278 | 3
|  | WIN022 | Rural Long | 0.14223 | 0.0024495 | 0.0041022 | 5.2847 | 0 | 5.2847 | 0.0071114 | 6.1237e-05 | -6.1237e-05 | 6516.4631 | 56.1144 | -56.1144 | 0.1688 | 2
|  | WND012 | Rural Long | 0.58047 | 0.013894 | 0.00808 | 25.2733 | 0.89895 | 24.3743 | 0.027991 | 0.000335 | -0.000335 | 25649.6026 | 306.9777 | -306.9777 | 0.76436 | 2
|  | WND013 | Rural Long | 1.0372 | 0.016425 | 0.0021646 | 34.309 | 1.7979 | 32.5111 | 0.04914 | 0.00038911 | -0.00038911 | 45029.0503 | 356.5559 | -356.5559 | 1.1302 | 5
|  | WND014 | Rural Short | 0.12198 | 0.0034369 | 0.0016412 | 4.7469 | 0.89895 | 3.8479 | 0.0049439 | 6.965e-05 | -6.965e-05 | 4530.2687 | 63.8231 | -63.8231 | 0.12392 | 2
|  | WND023 | Rural Long | 0.053784 | 0.0010454 | 0.0010372 | 2.0886 | 0 | 2.0886 | 0.0026892 | 2.6135e-05 | -2.6135e-05 | 2464.2177 | 23.9484 | -23.9484 | 0.066999 | 2
|  | WND024 | Rural Long | 1.4417 | 0.016763 | 0.0046399 | 40.8262 | 1.7979 | 39.0283 | 0.068912 | 0.00040062 | -0.00040062 | 63147.1597 | 367.1057 | -367.1057 | 1.4307 | 2
|  | WPD022 | Rural Short | 0.42589 | 0.0094488 | 0.0067286 | 14.4729 | 0.89895 | 13.574 | 0.019972 | 0.00022155 | -0.00022155 | 18300.9943 | 203.0128 | -203.0128 | 0.45383 | 3
|  | WPD024 | Rural Short | 0.026926 | 0.001511 | 0.012278 | 2.4978 | 0 | 2.4978 | 0.0013463 | 3.7775e-05 | -3.7775e-05 | 1233.6812 | 34.6151 | -34.6151 | 0.048457 | 1
|  | WPD033 | Rural Short | 0.2813 | 0.0073732 | 0.0016006 | 10.3286 | 1.7979 | 8.5307 | 0.011617 | 0.00015224 | -0.00015224 | 10644.8098 | 139.5072 | -139.5072 | 0.28226 | 4
|  | Total |  | 30.5307 | 0.47895 | 0.44423 | 1006.5166 | 145.6297 | 860.8868 | 1.3144 | 0.010323 | -0.010323 | 1204408.0668 | 9459.3052 | -9459.3052 | 29.4802 | 149 | 831.4066
|  |  | Initial Risk | [9 empty] | Savings
|  |  |  | SAIDI | SAIFI | MAIFIe | [7 empty] | SAIDI | SAIFI | MAIFIe
|  |  | Urban | 0.51171 | 0.0056867 | 0.017293 | [6 empty] | Urban | 0.022103 | 0.00012175 | -0.00012175
|  |  | Rural Short | 4.8481 | 0.086111 | 0.089675 | [6 empty] | Rural Short | 0.20666 | 0.0018348 | -0.0018348
|  |  | Rural Long | 25.1709 | 0.38715 | 0.33726 | [6 empty] | Rural Long | 1.0856 | 0.0083664 | -0.0083664
|  |  |  | CMOS | Sustained Cust Int | Momentary Cust Int | [7 empty] | CMOS | Sustained Cust Int | Momentary Cust Int
|  |  | Urban | 468898.5536 | 5211.0075 | 15846.7069 | [6 empty] | Urban | 20254.3506 | 111.5661 | -111.5661
|  |  | Rural Short | 4442515.2749 | 78907.3042 | 82173.3477 | [6 empty] | Rural Short | 189367.6803 | 1681.2727 | -1681.2727
|  |  | Rural Long | 23065121.8614 | 354763.1543 | 309043.6368 | [6 empty] | Rural Long | 994786.0358 | 7666.4664 | -7666.4664
|  |  |  | 27976535.6899 | 438881.466 | 407063.6913 | [7 empty] | 1204408.0668 | 9459.3052 | -9459.3052
|  |  |  | MWh | [9 empty] | MWh
|  |  | Urban | 13.3838 | [8 empty] | Urban | 0.41832
|  |  | Rural Short | 147.4081 | [8 empty] | Rural Short | 4.338
|  |  | Rural Long | 845.7247 | [8 empty] | Rural Long | 24.7239
|  |  |  | 1006.5166 | [9 empty] | 29.4802

## Workings_benefits
Powercor
REFCL reliability
WORKINGS - BENEFITS
1. MWh Reliability Calulator - Converts Cust Affected and Customer Minutes to Energy Lost
2021-2026 Incentive Rate Calculation
|  |  | Urban | Rural Short | Rural Long
|  | VCR $/MWh | 41210 | 41210 | 41210
|  | CPI | 0.020906 | 0.020906 | 0.020906
|  | w_n | 1.5 | 1.5 | 1.5
|  | Energy Supplied MWh | 4166180.3851 | 4425570.7123 | 2740818.2368
|  | Revenue $ | 650149950.3204 | 650149950.3204 | 650149950.3204
|  | SAIDI | 69.2269 | 104.1416 | 240.9159
|  | SAIFI | 0.82319 | 1.1472 | 2.0249
|  | MAIFI | 1.1996 | 2.5076 | 4.3933
Incentive Rate
|  | ir - SAIDI | 0.030755 | 0.03267 | 0.020233
|  | ir - SAIFI | 1.7242 | 1.9771 | 1.6048
|  | ir - MAIFI (% of SAIFI) | 0.13794 | 0.15817 | 0.12838
8%
Value of Reliability Calulations
|  | 2022-2026 Smoothed Revenue $m | 689.8989 | 689.8989 | 689.8989
$ per Unit
|  | SAIDI | 212176.28 | 225386.5757 | 139585.0789
|  | SAIFI | 11895374.2503 | 13639737.9637 | 11071500.2137
|  | MAIFI | 951629.94 | 1091179.0371 | 885720.0171
|  | Cust | 320111 | 356763 | 212928
$ per Outage Type
|  | SAIDI - $ per CMOS | 0.66282 | 0.63175 | 0.65555
|  | SAIFI - $ per Sustained Cust | 37.1602 | 38.2319 | 51.9965
|  | MAIFI - $ per Momentary Cust | 2.9728 | 3.0586 | 4.1597
MWh by Outage Type
|  |  | Urban | Rural Short | Rural Long
|  | MWh per CMOS | 1.6084e-05 | 1.533e-05 | 1.5908e-05
|  | MWh per Sustained Cust | 0.00090173 | 0.00092773 | 0.0012617
|  | MWh per Momentary Cust Int | 7.2138e-05 | 7.4219e-05 | 0.00010094
2. Project Timing &benefit Summary
|  | Yr 1 | Yr 2 | Yr 3 | Yr 4 | Yr 5 | Yr 6 | Yr 7 | Yr 8 | Yr 9 | Yr 10 | Yr 11 | Yr 12 | Yr 13 | Yr 14 | Yr 15 | Yr 16 | Yr 17 | Yr 18 | Yr 19 | Yr 20 | Yr 21 | Yr 22 | Yr 23 | Yr 24 | Yr 25
| Do Nothing | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868 | 860.8868
| Restore EF Detection Capability | 860.8868 | 860.8868 | 851.0601 | 841.2333 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066 | 831.4066

## Misc_calcs
Powercor
REFCL reliability
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 2.425%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 2.425% | 2.425%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1854 | 1.1997
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.1997
| Conversion from input dollars to output dollars |  | 1.1067
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 2 | TRUE
| Option 3 | 2 | TRUE
| Option 4 | Not used | FALSE
| Option 5 | Not used | FALSE
| First year | 2
!

## Data
Powercor
REFCL reliability
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | TRUE | Not used |  | TRUE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
Powercor
| Reliability in worst-served areas | per MWh | 151432.8174
| Network resilience | per MWh | 24590
| Enabling solar exports | per MWh | 88.3577
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.35181
| Customer value of time - business | per minute customer time | 0.35181
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | FALSE | June | 6 | CY | Not used | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | TRUE | December | 12 | FY |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [5 empty] | 2024 |  | 2024-25
2023
2022
2021
2020