## Cover
Powercor
Revised regulatory proposal 2026-31
Horsham REFCL
| Model number: | 3.3.13
2025-12-01
15
2025-05-09

## Summary
Powercor
Horsham REFCL
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Install Single REFCL at HSM ZSS in 2029-30 |  | -11.6228 | 16.6085 | 4.9857
| Option 3 | Install covered conductor for HSM feeders |  | -148.3137 | 37.7262 | -110.5875
| Option 4 | Install three REFCLs (one per Tx) at HSM ZSS in 2029-30 |  | -14.1743 | 17.6846 | 3.5103
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Install Single REFCL at HSM ZSS in 2029-30 |  | 4.9857
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 0 | 0 | 0 | 9.1149 | 9.1149 |  | 18.2297
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
Capex and risk ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 4.9857 | -110.5875 | 3.5103 |  |  | Option 2
| Capex 10% higher |  | 0 | 3.8234 | -125.4189 | 2.0929 |  |  | Option 2
| Capex 10% lower |  | 0 | 6.148 | -95.7561 | 4.9277 |  |  | Option 2
| Total benefits 10% higher |  | 0 | 6.6466 | -106.8149 | 5.2788 |  |  | Option 2
| Total benefits 10% lower |  | 0 | 3.3248 | -114.3601 | 1.7418 |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 2.1626 | -129.1915 | 0.32441 |  |  | Option 2
0
| 0 | [6 empty] | 0
0
0

## Assumptions
Powercor
Horsham REFCL
Project
|  | Business: | Powercor
|  | Descripton: | Horsham REFCL
|  | Date of cost inputs: | December |  | 2023
|  | Option | Description
|  | Option 1 (base case) | No change to existing practices
|  | Option 2 | Install Single REFCL at HSM ZSS in 2029-30
|  | Option 3 | Install covered conductor for HSM feeders
|  | Option 4 | Install three REFCLs (one per Tx) at HSM ZSS in 2029-30
Option 5
|  | Compliance project | No
|  | Expenditure starts | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  | 3.5% | [real_disc]
|  | VCR date |  |  | 2024-12-31 | [vcr_date]
|  | Analysis period (years) |  |  | 20 | [years]\
|  | Output dollars |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | HSM |  | Horsham | 36496.7249 | 2024 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  | 1
|  | Harm to property from bushfire |  |  | 1
|  | Harm to environment |  |  | 1
|  | Safety - Public trespass |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  | 3
|  | Safety from bushfire in HBRA |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  | 10
^ Public or employee
|  | Incident type |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  | 20%
Other benefits
| ENVIRONMENTAL | [7 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
Sensitivities
[5 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  | 10% | -10%

## Option1 (base case)
Powercor
Horsham REFCL
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| No change to existing practices |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 34455.2362 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 |  | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862
| Unplanned replacements |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bushfire risk |  |  | 2023-12-31 |  | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| No change to existing practices |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| No change to existing practices |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - No change to existing practices |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
Powercor
Horsham REFCL
OPTION 2 | Install Single REFCL at HSM ZSS in 2029-30
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Single REFCL |  | 30 | 2023-12-31 | 2026-27: 0; 2027-28: 0; 2028-29: 0; 2029-30: 8236093.128; 2030-31: 8236093.128
|  |  | 0 | 2023-12-31 | 2026-27: 0; 2027-28: 0; 2028-29: 0; 2029-30: 0; 2030-31: 0
|  |  | 0 | 2023-12-31 | 2026-27: 0; 2027-28: 0; 2028-29: 0; 2029-30: 0; 2030-31: 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 8236093.128 | 8236093.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 34455.2362 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bushfire risk |  |  | 2023-12-31 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108 | 1628482.7108
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545
Capital expenditure
| Single REFCL |  |  | 2023-12-31 | 0 | 0 | 0 | -8236093.128 | -8236093.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Single REFCL |  |  | 2023-12-31 | 0 | 0 | 0 | -8236093.128 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561 | -16472186.2561
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Single REFCL |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -447807.3506 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -447807.3506 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -447807.3506 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -447807.3506 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533
| First capex year |  |  | 4
| First year |  |  | 4
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 0 | 0 | 0 | -447807.3506 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | -447807.3506 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012 | -895614.7012
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545 | 1328310.7545
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 0 | 0 | 0 | -492588.0857 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831 | 343134.5831
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 0 | 0 | 0 | -403026.6156 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234 | 522257.5234
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 0 | 0 | 0 | -447807.3506 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287 | 565527.1287
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 0 | 0 | 0 | -447807.3506 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778 | 299864.9778
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 0 | 0 | 0 | -492588.0857 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077 | 210303.5077
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | 0 | -447807.3506 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | 0 | -447807.3506 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | 0 | -447807.3506 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533 | 432696.0533

## Option3
Powercor
Horsham REFCL
OPTION 3 | Install covered conductor for HSM feeders
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Covered conductor |  | 30 | 2023-12-31 | 2026-27: 0; 2027-28: 0; 2028-29: 0; 2029-30: 105097205; 2030-31: 105097205
|  |  | 0 | 2023-12-31 | 2026-27: 0; 2027-28: 0; 2028-29: 0; 2029-30: 0; 2030-31: 0
|  |  | 0 | 2023-12-31 | 2026-27: 0; 2027-28: 0; 2028-29: 0; 2029-30: 0; 2030-31: 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 105097205 | 105097205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 34455.2362 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 805182.2862 | 805182.2862 | 805182.2862 | 483109.3717 | 322072.9145 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bushfire risk |  |  | 2023-12-31 | 2151611.179 | 2151611.179 | 2151611.179 | 1097321.7013 | 570176.9624 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 2956793.4653 | 2956793.4653 | 2956793.4653 | 1580431.073 | 892249.8769 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808 | 204068.6808
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 1376362.3922 | 2064543.5883 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844
Capital expenditure
| Covered conductor |  |  | 2023-12-31 | 0 | 0 | 0 | -105097205 | -105097205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Covered conductor |  |  | 2023-12-31 | 0 | 0 | 0 | -105097205 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410 | -210194410
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Covered conductor |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -5714274.9841 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -5714274.9841 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -5714274.9841 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 1376362.3922 | 2064543.5883 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 1376362.3922 | -3649731.3957 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837
| First capex year |  |  | 4
| First year |  |  | 4
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 0 | 0 | 1376362.3922 | -3649731.3957 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | -5714274.9841 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681 | -11428549.9681
| Total benefits |  |  |  | 0 | 0 | 0 | 1376362.3922 | 2064543.5883 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844 | 2752724.7844
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 0 | 0 | 1376362.3922 | -4221158.8941 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805 | -9818680.1805
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 0 | 0 | 1376362.3922 | -3078303.8973 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869 | -7532970.1869
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | 0 | 0 | 1513998.6314 | -3443277.0369 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052 | -8400552.7052
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | 0 | 0 | 1238726.153 | -3856185.7546 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621 | -8951097.6621
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | 0 | 0 | 1238726.153 | -4427613.253 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589 | -10093952.6589
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 1376362.3922 | -3649731.3957 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 1376362.3922 | -3649731.3957 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 1376362.3922 | -3649731.3957 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837 | -8675825.1837

## Option4
Powercor
Horsham REFCL
OPTION 4 | Install three REFCLs (one per Tx) at HSM ZSS in 2029-30
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Three REFCLs |  | 30 | 2023-12-31 | 2026-27: 0; 2027-28: 0; 2028-29: 0; 2029-30: 10044122.128; 2030-31: 10044122.128
|  |  | 0 | 2023-12-31 | 2026-27: 0; 2027-28: 0; 2028-29: 0; 2029-30: 0; 2030-31: 0
|  |  | 0 | 2023-12-31 | 2026-27: 0; 2027-28: 0; 2028-29: 0; 2029-30: 0; 2030-31: 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 10044122.128 | 10044122.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 34455.2362 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bushfire risk |  |  | 2023-12-31 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 2956793.4653 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636 | 1542418.2636
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016
Capital expenditure
| Three REFCLs |  |  | 2023-12-31 | 0 | 0 | 0 | -10044122.128 | -10044122.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Three REFCLs |  |  | 2023-12-31 | 0 | 0 | 0 | -10044122.128 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561 | -20088244.2561
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Three REFCLs |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -546112.2949 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -546112.2949 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -546112.2949 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -546112.2949 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118
| First capex year |  |  | 4
| First year |  |  | 4
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | 0 | -546112.2949 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | -546112.2949 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899 | -1092224.5899
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016 | 1414375.2016
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | 0 | -600723.5244 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528 | 212928.1528
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | 0 | -491501.0654 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708 | 431373.0708
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 0 | 0 | 0 | -546112.2949 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132 | 463588.132
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 0 | 0 | 0 | -546112.2949 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916 | 180713.0916
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 0 | 0 | 0 | -600723.5244 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326 | 71490.6326
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | -546112.2949 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | -546112.2949 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | -546112.2949 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118 | 322150.6118

## Option5
Powercor
Horsham REFCL
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 34455.2362 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bushfire risk |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
Powercor
Horsham REFCL
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 52001049.3972 | 2026-06-30 |  | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Capital expenditure | Option 2Capital expenditure | -15888488.7024 | 2026-06-30 |  | 0 | 0 | 0 | -9114854.7012 | -9114854.7012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 35392529.4631 | 2026-06-30 |  | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 1802235.9706 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -11622819.4726 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -495586.7875 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | -991173.575 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 16608519.9341 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 1470036.744 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | -495586.7875 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 0 | 0
Option 2 | NPV | Option 2NPV | 4985700.4615 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -11622819.4726 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 16608519.9341 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Capital expenditure | Option 3Capital expenditure | -202746099.1924 | 2026-06-30 |  | 0 | 0 | 0 | -116310699.5251 | -116310699.5251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 14274823.5326 | 2026-06-30 |  | 3272272.7146 | 3272272.7146 | 3272272.7146 | 1749057.3956 | 987449.7361 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 225842.0766 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -148313748.0118 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -6323967.6134 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | -12647935.2267 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 37726225.8646 | 2026-06-30 |  | 0 | 0 | 0 | 1523215.319 | 2284822.9785 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 3046430.638 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 1523215.319 | -4039144.6349 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | 0 | 0
Option 3 | NPV | Option 3NPV | -110587522.1472 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -148313748.0118 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 37726225.8646 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | -19376410.4504 | 2026-06-30 |  | 0 | 0 | 0 | -11115793.9055 | -11115793.9055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 34316423.5282 | 2026-06-30 |  | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 3272272.7146 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 1706988.7558 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | -14174319.8432 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -604380.5165 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | -1208761.033 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 17684625.869 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 1565283.9587 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | -604380.5165 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 0 | 0
Option 4 | NPV | Option 4NPV | 3510306.0258 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -14174319.8432 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 17684625.869 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0.99117 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723 | 3.2723
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 0 |  |  | Option 1 (base case) risk cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Sensitivity_calcs
Powercor
Horsham REFCL
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE
[7 empty] | 46203 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 4985700.4615 |  | 0 | 0 | 0 | 0 | 0 | -495586.7875 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 3823418.5142 |  | 0 | 0 | 0 | 0 | 0 | -545145.4663 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 379745.8115 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 6147982.4088 |  | 0 | 0 | 0 | 0 | 0 | -446028.1088 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 577980.5265 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 6646552.4549 |  | 0 | 0 | 0 | 0 | 0 | -495586.7875 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 625866.8434 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 3324848.4681 |  | 0 | 0 | 0 | 0 | 0 | -495586.7875 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 331859.4946 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 2162566.5208 |  | 0 | 0 | 0 | 0 | 0 | -545145.4663 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 232742.1371 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 4985700.4615 |  | 0 | 0 | 0 | 0 | 0 | -495586.7875 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 4985700.4615 |  | 0 | 0 | 0 | 0 | 0 | -495586.7875 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 4985700.4615 |  | 0 | 0 | 0 | 0 | 0 | -495586.7875 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 478863.169 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 1523215.319 | -4039144.6349 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | -110587522.1472 |  | 0 | 0 | 0 | 0 | 1523215.319 | -4039144.6349 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | -125418896.9484 |  | 0 | 0 | 0 | 0 | 1523215.319 | -4671541.3962 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | -10866298.1114 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | -95756147.346 |  | 0 | 0 | 0 | 0 | 1523215.319 | -3406747.8735 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | -8336711.0661 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | -106814899.5607 |  | 0 | 0 | 0 | 0 | 1675536.8509 | -3810662.337 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | -9296861.525 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | -114360144.7336 |  | 0 | 0 | 0 | 0 | 1370893.7871 | -4267626.9327 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | -9906147.6526 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | -129191519.5348 |  | 0 | 0 | 0 | 0 | 1370893.7871 | -4900023.6941 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | -11170941.1752 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -110587522.1472 |  | 0 | 0 | 0 | 0 | 1523215.319 | -4039144.6349 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -110587522.1472 |  | 0 | 0 | 0 | 0 | 1523215.319 | -4039144.6349 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -110587522.1472 |  | 0 | 0 | 0 | 0 | 1523215.319 | -4039144.6349 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | -9601504.5888 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 3510306.0258 |  | 0 | 0 | 0 | 0 | 0 | -604380.5165 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 2092874.0415 |  | 0 | 0 | 0 | 0 | 0 | -664818.5682 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 235646.8224 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 4927738.0101 |  | 0 | 0 | 0 | 0 | 0 | -543942.4649 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 477399.029 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 5278768.6127 |  | 0 | 0 | 0 | 0 | 0 | -604380.5165 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 513051.3216 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 1741843.4389 |  | 0 | 0 | 0 | 0 | 0 | -604380.5165 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 199994.5298 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 324411.4546 |  | 0 | 0 | 0 | 0 | 0 | -664818.5682 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 79118.4265 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 3510306.0258 |  | 0 | 0 | 0 | 0 | 0 | -604380.5165 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 3510306.0258 |  | 0 | 0 | 0 | 0 | 0 | -604380.5165 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 3510306.0258 |  | 0 | 0 | 0 | 0 | 0 | -604380.5165 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 356522.9257 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | FALSE | FALSE | FALSE | FALSE | TRUE |  | 2028-29: FALSE
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 4.9857 | -110.5875 | 3.5103 |  |  | 2026-27: 4.9857; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 3.8234 | -125.4189 | 2.0929 |  |  | 2026-27: 3.8234; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 6.148 | -95.7561 | 4.9277 |  |  | 2026-27: 6.148; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 6.6466 | -106.8149 | 5.2788 |  |  | 2026-27: 6.6466; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 3.3248 | -114.3601 | 1.7418 |  |  | 2026-27: 3.3248; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 2.1626 | -129.1915 | 0.32441 |  |  | 2026-27: 2.1626; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: 0
sens | 0 | [6 empty] | 2026-27: 0
sens | 0 | [6 empty] | 2026-27: 0

## Workings_risks
Powercor
Horsham REFCL
WORKINGS - RISKS
| Conversion from June 2022 to December 2023 |  |  | 1.0747
| Risk reduction effectiveness |  |  | 98% |  | ACIL Allen RIS report
| REFCL proportion of year in fire mode |  |  | 32% |  | REFCL safety assessment
Option 1 (base case) - no change to existing practices
Bushfire risk
| Annual bushfire risk |  | 2022-06-30 | 2001968 |  | Sourced from Bushfire Risk Model
| Annual bushfire risk |  | 2023-12-31 | 2151611.179
Safety risk from contact
| Total bare 22kV line length |  | km | 34849
| Average fatal or serious incident HV contacts across total bare 22kV network |  |  | 1.2 |  | Average from September 2015 to September 2025
| Value of statistical life |  | 2023-12-31 | 5607473.5197
| Disproportionate factor for loss of human life |  |  | 3
| Annual safety risk cost |  | $/km | 579.2678
| Length of Horsham bare 22kV overhead feeders |  | km | 1390
| Total safety risk cost for Horsham feeders pa |  | 2023-12-31 | 805182.2862
|  |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
| Bushfire risk |  | 2023-12-31 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179
| Safety risk |  | 2023-12-31 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862
Option 2 - Install Single REFCL at Horsham (HSM) ZSS in 2029-30
Benefits start on completion
| Bushfire risk | Risk reduction after project is completed |  | 805182.2862 2026-27: 50%; 805182.2862 2028-29: 54% per CSIRO model with one REFCL per transformer; reduced to 50% with single REFCL
| Safety risk from contact | Effectiveness of REFCL in reducing safety risk from contact |  | 805182.2862 2026-27: 31.36%; 805182.2862 2028-29: Risk reduction effectiveness x % of the year in Fire mode
|  |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
| Risk reduction profile |  |  | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Residual bushfire risk |  | 2023-12-31 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895 | 1075805.5895
| Residual safety risk |  | 2023-12-31 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213
Option 3 - Install covered conductor for Horsham feeders
Benefits commence during project works
| Bushfire risk | Risk reduction effectiveness |  | 31.36% 2026-27: 98%; Risk reduction effectiveness x % of the year in Fire mode 2028-29: ACIL Allen RIS report
| Safety risk from contact | Effectiveness of covered conductor in reducing safety risk from contact |  | 31.36% 2026-27: 80%; Risk reduction effectiveness x % of the year in Fire mode 2028-29: Paper: "Safety-Related Contact Currents for Humans Touching Medium Voltage Covered Conductor"
|  |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
| Risk reduction profile |  |  | 0% | 0% | 0% | 50% | 75% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Residual bushfire risk |  | 2023-12-31 | 2151611.179 | 2151611.179 | 2151611.179 | 1097321.7013 | 570176.9624 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236 | 43032.2236
| Residual safety risk |  | 2023-12-31 | 805182.2862 | 805182.2862 | 805182.2862 | 483109.3717 | 322072.9145 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572 | 161036.4572
Option 4 - Install Three REFCLs (one per Tx) at HSM ZSS in 2029-30 as per Bushfire Mitigation Regulation performance requirements
Benefits commence on completion
| Bushfire risk | Risk reduction after project is completed |  | 80% 2026-27: 54%; Paper: "Safety-Related Contact Currents for Humans Touching Medium Voltage Covered Conductor" 2028-29: 54% per CSIRO model with one REFCL per transformer; reduced to 50% with single REFCL
| Safety risk from contact | Effectiveness of REFCL in reducing safety risk from contact |  | 80% 2026-27: 31.36%; Paper: "Safety-Related Contact Currents for Humans Touching Medium Voltage Covered Conductor" 2028-29: Risk reduction effectiveness x % of the year in Fire mode
|  |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
| Risk reduction profile |  |  | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Residual bushfire risk |  | 2023-12-31 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 2151611.179 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424 | 989741.1424
| Residual safety risk |  | 2023-12-31 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 805182.2862 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213 | 552677.1213

## Workings_costs
Powercor
Horsham REFCL
WORKINGS - COSTS
Option 1 (base case) - no change to existing practices
| Total capital costs |  | 0
| Total operating costs |  | 0
Option 2 - Install single REFCL at Horsham (HSM) ZSS
| Project duration | years | 2
| ZSS single REFCL costs | 2023-12-31 | 8093913
| Network distribution cost | 2023-12-31 | 8378273.2561
| Total capital cost | 2023-12-31 | 16472186.2561
Assuming project spans across 2 years
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31
| Option 2 capital cost |  |  |  |  | 8236093.128 | 8236093.128
Option 3 - Install covered conductor for Horsham feeders
| Project duration | years | 2
| Covered conductor length for Horsham feeders |  | 1390 | km
| Covered conductor unit cost |  | 151219 | per km | in 2023 $
| Total capital cost |  | 210194410
Assuming project spans across 2 years
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31
| Option 3 capital cost |  |  |  |  | 105097205 | 105097205
Option 4 - Install Three REFCLs (one per Tx) at HSM ZSS in 2029-30 as per Bushfire Mitigation Regulation performance requirements
| Project duration | years | 2
| ZSS 3 REFCL costs | 2023-12-31 | 11709971
| Network distribution cost | 2023-12-31 | 8378273.2561
| Total capital cost | 2023-12-31 | 20088244.2561
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31
| Option 4 capital cost | 2023-12-31 |  |  |  | 10044122.128 | 10044122.128

## Cost_inputs
Powercor
Horsham REFCL
COST INPUTS
Powercor - IR013 - minimising bushfire risk cost estimates
| Category |  | Labour ($2023) | Materials ($2023) | Contract ($2023) | Total ($2023)
| ZSS HSM single REFCL |  | 3868271 | 2906972 | 1318670 | 8093913
| Distribution line works (line hardening and REFCL reliability) |  | 3669047.4826 | 3268130.0393 | 1441095.7342 | 8378273.2561
| Category - ZSS HSM single REFCL Estimated and informed by comparative Tranche 3 projects |  | Labour ($2023) | Materials ($2023) | Contract ($2023) | Total ($2023)
| Primary |  | 2143871 | 2319545 | 1118670 | 5582086
| Secondary |  | 1724400 | 587427 | 200000 | 2511827
| Total |  | 3868271 | 2906972 | 1318670 | 8093913
| Comparative completed tranche 3 single REFCL ZSS works |  | Labour ($2023) | Materials ($2023) | Contract ($2023) | Total ($2023)
| MBN |  | 3221069.2174 | 1981969.6277 | 1448534.6339 | 6651573.479
| ZSS primary costs |  | 1918658.8822 | 1477306.158 | 1190759.4115 | 4586724.4517
| ZSS secondary costs |  | 1302410.3352 | 504663.4697 | 257775.2224 | 2064849.0273
| KRT |  | 3440672.0062 | 2247350.8859 | 1829605.1081 | 7517628.0002
| ZSS primary costs |  | 1938487.1051 | 1828752.1201 | 1417292.3457 | 5184531.571
| ZSS secondary costs |  | 1502184.9011 | 418598.7658 | 412312.7623 | 2333096.4292
| STL |  | 3332336.9117 | 2273063.1832 | 2062963.7022 | 7668363.7971
| ZSS primary costs |  | 1849949.6581 | 1828752.1201 | 1752215.0206 | 5430916.7988
| ZSS secondary costs |  | 1482387.2536 | 444311.0631 | 310748.6816 | 2237446.9983
| Average (MBN, KRT, STL) |  | 3331359.3784 | 2167461.2323 | 1780367.8147 | 7279188.4254
| ZSS primary costs |  | 1902365.2151 | 1711603.4661 | 1453422.2593 | 5067390.9405
| ZSS secondary costs |  | 1428994.1633 | 455857.7662 | 326945.5554 | 2211797.4849
| Category - Distribution Line Works Line hardening and REFCL reliability |  | Labour ($2023) | Materials ($2023) | Contract ($2023) | Total ($2023)
| Project Management, Planning & Design | 1 | 495744 | 0 | 404483.72 | 900227.72
| Hardening - 1ph Sites | 345 | 409590.9 | 124200 | 79350 | 613140.9
| Hardening - 3ph Sites | 880 | 1044753.6 | 502200 | 202400 | 1749353.6
| Balancing - Rephase / Fusing | 30 | 62329.2 | 0 | 6900 | 69229.2
| Balancing - Conductor Work | 1 | 29920.32 | 4833.27 | 2576 | 37329.59
| Balancing - 1ph CBU | 6 | 50439.51 | 124354.01 | 20100 | 194893.52
| Balancing - 3ph CBU | 25 | 243307.75 | 584127.42 | 83750 | 911185.17
| Balancing - Fuse Saver 40A | 15 | 90800.63 | 57209.7 | 27600 | 175610.33
| Balancing - Fuse Saver 100A | 2 | 12106.75 | 7627.96 | 3680 | 23414.71
| Balancing - Fuse Saver 200A | 1 | 6053.38 | 1713.98 | 1840 | 9607.36
| Balancing - Gas Switches | 3 | 34116.81 | 55897.52 | 11040 | 101054.33
| Balancing - Test Site | 7 | 12465.81 | 7577.57 | 3150 | 23193.38
| Compatability - Regulators | 5 | 357083 | 591977.76 | 300000 | 1249060.76
| Compatability - Regulators CL7 Only | 3 | 17171.28 | 41370 | 0 | 58541.28
| Miscellaneous - NVD Blocking | 2 | 18219.52 | 13564 | 0 | 31783.52
| Asset Resilience - Offline Test | 6 | 8180.76 | 0 | 14400 | 22580.76
| Asset Resilience - Online Test | 1 | 14286.34 | 0 | 10200 | 24486.34
| Asset Resilience - Cable Repair | 3 | 18401.91 | 4381.9275 | 3498 | 26281.8375
| Asset Resilience - Cable Replacement | 2 | 27147.86 | 183368.68 | 93803.28 | 304319.82
| Distribution line works (hardening) | Volume | 2952119.33 | 2304403.7975 | 1268771 | 6525294.1275
| ACR Replacements | 11 | 474893.5603 | 395519.3114 | 86620.7651 | 957033.6368
| Switch/Sectionaliser Earth Fault Indication | 12 | 242034.5923 | 568206.9304 | 85703.9692 | 895945.4918
| Distribution line works (REFCL reliability) | Volume | 716928.1526 | 963726.2418 | 172324.7342 | 1852979.1286
| Total |  | 3669047.4826 | 3268130.0393 | 1441095.7342 | 8378273.2561
| Distribution line works - line hardening unit rates Based on Tranche 3 completed works |  | Labour ($2023) | Materials ($2023) | Contract ($2023) | Total ($2023)
| Project Management, Planning & Design |  | 495744 | 0 | 404483.72 | 900227.72
| Hardening - 1ph Sites |  | 1187.22 | 360 | 230 | 1777.22
| Hardening - 3ph Sites |  | 1187.22 | 570.6818 | 230 | 1987.9018
| Balancing - Rephase / Fusing |  | 2077.64 | 0 | 230 | 2307.64
| Balancing - Conductor Work |  | 29920.32 | 4833.27 | 2576 | 37329.59
| Balancing - 1ph CBU |  | 8406.585 | 20725.6683 | 3350 | 32482.2533
| Balancing - 3ph CBU |  | 9732.31 | 23365.0968 | 3350 | 36447.4068
| Balancing - Fuse Saver 40A |  | 6053.3753 | 3813.98 | 1840 | 11707.3553
| Balancing - Fuse Saver 100A |  | 6053.375 | 3813.98 | 1840 | 11707.355
| Balancing - Fuse Saver 200A |  | 6053.38 | 1713.98 | 1840 | 9607.36
| Balancing - Gas Switches |  | 11372.27 | 18632.5067 | 3680 | 33684.7767
| Balancing - Test Site |  | 1780.83 | 1082.51 | 450 | 3313.34
| Compatability - Regulators |  | 71416.6 | 118395.552 | 60000 | 249812.152
| Compatability - Regulators CL7 Only |  | 5723.76 | 13790 | 0 | 19513.76
| Miscellaneous - NVD Blocking |  | 9109.76 | 6782 | 0 | 15891.76
| Asset Resilience - Offline Test |  | 1363.46 | 0 | 2400 | 3763.46
| Asset Resilience - Online Test |  | 14286.34 | 0 | 10200 | 24486.34
| Asset Resilience - Cable Repair |  | 6133.97 | 1460.6425 | 1166 | 8760.6125
| Asset Resilience - Cable Replacement |  | 13573.93 | 91684.34 | 46901.64 | 152159.91
| Distribution line works - REFCL reliability (ACR replacements) Based on completed 2024 projects | Volume | Labour ($2023) | Materials ($2023) | Contract ($2023) | Total ($2023)
| GHP011 REFCL ACR Replacement | 1 | 30261.0935 | 29976.6536 | 4620.1494 | 64857.8965
| GHP021 REFCL ACR Replacement | 2 | 102421.2364 | 76305.8312 | 23386.8935 | 202113.9611
| TQY021 REFCL ACR Replacement | 2 | 96474.1165 | 84469.279 | 18035.2737 | 198978.6692
| WPD022 REFCL ACR Replacement | 1 | 48702.6887 | 37281.3316 | 7983.4198 | 93967.4402
| WPD033 REFCL ACR Replacement | 2 | 76534.7483 | 60311.1554 | 11792.4941 | 148638.3978
| Lyonville P15B REFCL ACR Replacement | 1 | 34155.3931 | 35262.4586 | 5053.3044 | 74471.1562
| Average unit rate | 9 | 43172.1418 | 35956.301 | 7874.615 | 87003.0579
| Distribution line costs - REFCL reliability (switch/sectionaliser) Based on trial 2021 projects | Volume | Labour ($2023) | Materials ($2023) | Contract ($2023) | Total ($2023)
| BAS022 A'Eberle REFCL Project | 3 | 53230.4286 | 128227.4529 | 37191.1183 | 218648.9998
| CLC A'Eberle REFCL Project | 3 | 67786.8675 | 155876.0123 | 5660.8663 | 229323.7461
| Average unit rate | 6 | 20169.5494 | 47350.5775 | 7141.9974 | 74662.1243

## Misc_calcs
Powercor
Horsham REFCL
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 2.425%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 2.425% | 2.425%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1854 | 1.1997
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.1997
| Conversion from input dollars to output dollars |  | 1.1067
| Convert from VCR date | 2024-12-31 | 1.1482
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 0.94406
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 4 | TRUE
| Option 3 | 4 | TRUE
| Option 4 | 4 | TRUE
| Option 5 | Not used | FALSE
| First year | 4

## Data
Powercor
Horsham REFCL
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
Powercor
| Reliability in worst-served areas | per MWh | 151432.8174
| Network resilience | per MWh | 24590
| Enabling solar exports | per MWh | 88.3577
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.35181
| Customer value of time - business | per minute customer time | 0.35181
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | FALSE | June | 6 | CY | Not used | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | TRUE | December | 12 | FY |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [5 empty] | 2024 |  | 2024-25
2023
2022
2021
2020