## Cover
Powercor
Revised proposal 2026-31
Bushfire resilience
| Model number: | 3.5.01
2025-12-01
15
2025-05-15

## Summary
Powercor
Pole bushfire resilience program
SUMMARY
RESULTS
[5 empty] | PV of costs | PV of benefits | NPV |  | Total capital cost
| Option |  |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30 |  | 2026-06-30
| Option 1 (base case) | No change to existing practices |  |  | 0 | 0 | 0 |  | 0
| Option 2 | Replace wood poles with concrete poles |  |  | -14.0082 | 84.0447 | 70.0365 |  | 25.9148
| Option 3 | Wrap wood poles with fire mesh |  |  | -0.97525 | 52.8583 | 51.883 |  | 0.95862
| Option 4 | Combination of replacing wood poles with concrete poles and fire mesh |  |  | -12.4461 | 83.4306 | 70.9845 |  | 22.9237
NPV
| Preferred option: |  | 2026-06-30
| Option 4 | Combination of replacing wood poles with concrete poles and fire mesh | 70.9845
EXPENDITURE
Capital expenditure 2026-31
| 2026-06-30 |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Combination of replacing wood poles with concrete poles and fire mesh |  | 4584.7424 | 4584.7424 | 4584.7424 | 4584.7424 | 4584.7424 |  | 22923.7121
SENSITIVITIES
NPV
2026-06-30
| Option 4 |  | 70.9845
| Capex 10% higher |  | 69.7399
| Capex 10% lower |  | 72.2291
| Total benefits 10% higher |  | 79.3275
| Total benefits 10% lower |  | 62.6414
| Capex 10% higher & Total benefits 10% lower |  | 61.3968
End |  |  | . | . | . | . | . | . | .

## Expenditure
Powercor
Pole bushfire resilience program
|  | Number of poles in segment | Option 4 capex ($ 2023) | PV of option 4 cost ($ 2023) | PV of Option 4 benefits ($ 2023) | Option 4 NPV ($ 2023)
| Selected for replacement | 1093 | 20713640.9514 | -11246205.3302 | 75387084.2251 | 64140878.8948
| Cost of total number of overlapped poles | 67 | -1435403.5044
| Incremental cost of overlapped southern poles | 58 | 283964.5759
| 2026-31 bushfire resilience capex including overlapped pole cost |  | 20713640.9514
| Expenditure per year over 5 years | 2023-12-31 | 4142728.1903 |  |  | 0
| Expenditure per year over 5 years | 2026-06-30 | 4584742.4178

## Assumptions
Powercor
Pole bushfire resilience program
Project
|  | Business: | Powercor
|  | Descripton: | Pole bushfire resilience program
|  | Date of cost inputs: | December |  | 2023
|  | Option | Description
|  | Option 1 (base case) | No change to existing practices
|  | Option 2 | Replace wood poles with concrete poles
|  | Option 3 | Wrap wood poles with fire mesh
|  | Option 4 | Combination of replacing wood poles with concrete poles and fire mesh
Timing & WACC
|  | Input dollars |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  | 3.5% | [real_disc]
|  | VCR date |  |  | 2024-12-31 | [vcr_date]
|  | Model start year |  |  | 2026 | [start]
|  | Analysis period (years) |  |  | 20 | [years]\
|  | Output dollars |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  | 2024-12-31 | [custval_date]
|  | Value of CO2 reductions value date |  |  | 2023-12-31
Costs
| Premium for unplanned bushfire pole replacement |  |  |  | 10%
| 4 year average cost of concrete pole |  |  |  | 21423.9329 | 2023 $ |  |  |  | Roll of 0.9m*15m Genics fire mesh |  |  | 2310 | based on quote from Tengroup
| 4 year average cost of wood pole |  |  |  | 16527.9919 | 2023 $ |  |  |  | Cost of fire mesh material per pole |  |  | 577.5 | assuming 1 roll is sufficient for 4 poles
| Average cost of fire mesh |  |  |  | 792.5 |  |  |  |  | Labour rate ($/h) |  |  | 215
| Asset life (years) |  |  |  | 80 |  |  |  |  | Installation and travel time per pole (h) |  |  | 1
| Fire mesh asset life (years) |  |  |  | 20 |  |  |  |  | Installed fire mesh cost per pole |  |  | 792.5
VCR
[5 empty] | Commercial | Industrial | Agricultural
|  | VCR $/MWh | 2024-12-31 |  | 34390 | 33490 | 22250
|  | 6-12h VCR $/MWh | 2024-12-31 |  | 10120.3463 | 8296.0059 | 8532.601
VNR
Outage hours tiers for VNR
|  | Reduction in CAIDI from situation awareness |  |  | 4%
|  | 12<t<24 |  |  | 12
|  | >24 |  |  | 3.84
|  | >72 |  |  | 0
|  | Average historic bushfire outage duration (hours) |  |  | 29 |  | Based on network CAIDI
|  | Average historic bushfire outage after CAIDI reduction (hours) |  |  | 27.84
Other risks
SAFETY
|  | Value of statistical life |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  | 1
|  | Harm to property from bushfire |  |  | 1
|  | Harm to environment |  |  | 1
|  | Safety - Public trespass |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  | 3
|  | Safety from bushfire in HBRA |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  | 10
^ Public or employee
|  | Incident type |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  | 0 | 0 | 0 | 0
|  | Average to max. demand ratio |  | 50% | 50% | based on ZSS network average
Other benefits
| ENVIRONMENTAL | [7 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  | 2023-12-31 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  | Value
|  | Reliability in worst-served areas |  |  | 151432.8174 | 2024-12-31 | per MWh
|  | Enabling solar exports |  |  | 88.3577 | 2024-12-31 | per MWh
|  | Aesthetics |  |  | 0 | 2024-12-31 | per customer
|  | Customer value of time - residential |  |  | 0.35181 | 2024-12-31 | per customer minute
|  | Customer value of time - business |  |  | 0.35181 | 2024-12-31 | per customer minute
|  | Communication |  |  | 0 | 2024-12-31 | per customer
|  | Information accessibility |  |  | 0 | 2024-12-31 | per customer
Sensitivities
[5 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  | 10% | -10%
Effectiveness
|  | Concrete pole effectiveness against forest fires |  |  |  | 90.32% |  | Assumed pole will not survive if the top 1.5m of the pole burns
|  | Concrete pole effectiveness against grassfires |  |  |  | 100%
|  | Fire mesh effectiveness against forest fires |  |  |  | 9.677% |  | Based on 1.5m height of fire mesh wrap for an average 15.5m pole height
|  | Fire mesh effectiveness against grassfires |  |  |  | 90% |  | This is a conservative assumption as fire mesh is most likely only effective for low intensity grassfires.
|  | Proportion of grassfires of all bushfires |  |  |  | 63.7% |  | Based on vegetated HV spans
|  | Concrete pole effectiveness against all bushfires |  |  |  | 96.49%
|  | Fire mesh effectiveness against all bushfires |  |  |  | 60.84%

## LOS_data
Powercor
Pole bushfire resilience program
|  |  |  | Climate time period: E1986-2005 |  | Clilmate time period: E2020-2039 |  | Climate time period: E2040-2059
|  |  |  | Mid-point: | 1995 | Mid-point: | 2030 | Mid-point: | 2050 |  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 |  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
| segment | Customers |  | Annual average occurrence of loss |  | Annual average occurrence of loss |  | Annual average occurrence of loss |  | Gradient LOS0_per_year |  | 2026: LOS0_per_year | Gradient LOS1_per_year |  | LOS1_per_year
|  | segment & downstream | Segment only | segment loss only | segment & downstream loss | segment loss only | segment & downstream loss | segment loss only | segment & downstream loss | 1986-2005 to 2020-2039 | 2020-2039 to 2040-2059 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 1986-2005 to 2020-2039 | 2020-2039 to 2040-2059 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
|  | CUST0 | CUST1 | LOS0_per_year | LOS1_per_year | LOS0_per_year | LOS1_per_year | LOS0_per_year | LOS1_per_year
| AC024-200218081 | 1 | 1 | 0.00014613 | 0 | 0.00023544 | 0 | 0.0002165 | 0 | 2.5515e-06 | -9.4715e-07 | 0.00022523 | 0.00022778 | 0.00023033 | 0.00023289 | 0.00023544 | 0.00023449 | 0.00023354 | 0.0002326 | 0.00023165 | 0.0002307 | 0.00022976 | 0.00022881 | 0.00022786 | 0.00022691 | 0.00022597 | 0.00022502 | 0.00022407 | 0.00022313 | 0.00022218 | 0.00022123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AC024-200218767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AC024-200218825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AC025-200218004 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AC026-200217919 | 0 | 0 | 0.030341 | 0 | 0.035357 | 0 | 0.03535 | 0 | 0.00014332 | -3.69e-07 | 0.034784 | 0.034927 | 0.035071 | 0.035214 | 0.035357 | 0.035357 | 0.035357 | 0.035356 | 0.035356 | 0.035355 | 0.035355 | 0.035355 | 0.035354 | 0.035354 | 0.035354 | 0.035353 | 0.035353 | 0.035353 | 0.035352 | 0.035352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AC031-200217854 | 9 | 9 | 0.0050434 | 0 | 0.0061662 | 0 | 0.006099 | 0 | 3.208e-05 | -3.3569e-06 | 0.0060378 | 0.0060699 | 0.006102 | 0.0061341 | 0.0061662 | 0.0061628 | 0.0061594 | 0.0061561 | 0.0061527 | 0.0061494 | 0.006146 | 0.0061427 | 0.0061393 | 0.0061359 | 0.0061326 | 0.0061292 | 0.0061259 | 0.0061225 | 0.0061192 | 0.0061158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AC032-200217768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL002-15404158 | 317 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL002-200779408 | 315 | 315 | 0.0011692 | 0 | 0.0018635 | 0 | 0.001736 | 0 | 1.9836e-05 | -6.3775e-06 | 0.0017842 | 0.001804 | 0.0018238 | 0.0018437 | 0.0018635 | 0.0018571 | 0.0018508 | 0.0018444 | 0.001838 | 0.0018316 | 0.0018253 | 0.0018189 | 0.0018125 | 0.0018061 | 0.0017997 | 0.0017934 | 0.001787 | 0.0017806 | 0.0017742 | 0.0017679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL006-200403372 | 2034 | 2034 | 0.0047574 | 0 | 0.0065232 | 0 | 0.0061258 | 0 | 5.0452e-05 | -1.9872e-05 | 0.0063214 | 0.0063719 | 0.0064223 | 0.0064728 | 0.0065232 | 0.0065034 | 0.0064835 | 0.0064636 | 0.0064437 | 0.0064239 | 0.006404 | 0.0063841 | 0.0063642 | 0.0063444 | 0.0063245 | 0.0063046 | 0.0062848 | 0.0062649 | 0.006245 | 0.0062251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL007-200403464 | 1019 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL007-200403526 | 1010 | 1010 | 4.43e-06 | 0 | 6.55e-06 | 0 | 5.93e-06 | 0 | 6.0571e-08 | -3.1e-08 | 6.3077e-06 | 6.3683e-06 | 6.4289e-06 | 6.4894e-06 | 6.55e-06 | 6.519e-06 | 6.488e-06 | 6.457e-06 | 6.426e-06 | 6.395e-06 | 6.364e-06 | 6.333e-06 | 6.302e-06 | 6.271e-06 | 6.24e-06 | 6.209e-06 | 6.178e-06 | 6.147e-06 | 6.116e-06 | 6.085e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL011-200635544 | 131 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL012-200635470 | 1780 | 1780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL014-200635260 | 2091 | 2091 | 0.0053629 | 0 | 0.0069384 | 0 | 0.0067186 | 0 | 4.5015e-05 | -1.0989e-05 | 0.0067584 | 0.0068034 | 0.0068484 | 0.0068934 | 0.0069384 | 0.0069274 | 0.0069164 | 0.0069055 | 0.0068945 | 0.0068835 | 0.0068725 | 0.0068615 | 0.0068505 | 0.0068395 | 0.0068285 | 0.0068175 | 0.0068065 | 0.0067956 | 0.0067846 | 0.0067736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART023-15411707 | 1034 | 638 | 0.012805 | 0.0045488 | 0.017478 | 0.0063626 | 0.017775 | 0.0064761 | 0.00013353 | 1.4826e-05 | 0.016944 | 0.017078 | 0.017211 | 0.017345 | 0.017478 | 0.017493 | 0.017508 | 0.017523 | 0.017538 | 0.017552 | 0.017567 | 0.017582 | 0.017597 | 0.017612 | 0.017627 | 0.017641 | 0.017656 | 0.017671 | 0.017686 | 0.017701 | 5.1825e-05 | 5.6711e-06 | 0.0061553 | 0.0062072 | 0.006259 | 0.0063108 | 0.0063626 | 0.0063683 | 0.006374 | 0.0063797 | 0.0063853 | 0.006391 | 0.0063967 | 0.0064023 | 0.006408 | 0.0064137 | 0.0064194 | 0.006425 | 0.0064307 | 0.0064364 | 0.006442 | 0.0064477
| ART023-15411718 | 1035 | 1 | 0 | 4.46e-07 | 0 | 7.91e-07 | 0 | 8.25e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8571e-09 | 1.7e-09 | 7.5157e-07 | 7.6143e-07 | 7.7129e-07 | 7.8114e-07 | 7.91e-07 | 7.927e-07 | 7.944e-07 | 7.961e-07 | 7.978e-07 | 7.995e-07 | 8.012e-07 | 8.029e-07 | 8.046e-07 | 8.063e-07 | 8.08e-07 | 8.097e-07 | 8.114e-07 | 8.131e-07 | 8.148e-07 | 8.165e-07
| ART023-154832740 | 8 | 8 | 0.00063355 | 0 | 0.00092238 | 0 | 0.00092584 | 0 | 8.2524e-06 | 1.726e-07 | 0.00088937 | 0.00089763 | 0.00090588 | 0.00091413 | 0.00092238 | 0.00092256 | 0.00092273 | 0.0009229 | 0.00092307 | 0.00092325 | 0.00092342 | 0.00092359 | 0.00092376 | 0.00092394 | 0.00092411 | 0.00092428 | 0.00092446 | 0.00092463 | 0.0009248 | 0.00092497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART023-154832902 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART023-24601770 | 273 | 249 | 0.0073157 | 0.00039181 | 0.010602 | 0.00057739 | 0.010676 | 0.00058185 | 9.3897e-05 | 3.7021e-06 | 0.010226 | 0.01032 | 0.010414 | 0.010508 | 0.010602 | 0.010606 | 0.010609 | 0.010613 | 0.010617 | 0.010621 | 0.010624 | 0.010628 | 0.010632 | 0.010635 | 0.010639 | 0.010643 | 0.010646 | 0.01065 | 0.010654 | 0.010658 | 5.3022e-06 | 2.232e-07 | 0.00055618 | 0.00056148 | 0.00056678 | 0.00057209 | 0.00057739 | 0.00057761 | 0.00057784 | 0.00057806 | 0.00057828 | 0.00057851 | 0.00057873 | 0.00057895 | 0.00057917 | 0.0005794 | 0.00057962 | 0.00057984 | 0.00058007 | 0.00058029 | 0.00058051 | 0.00058074
| ART023-63832300 | 396 | 42 | 0.0082006 | 0.0021034 | 0.010915 | 0.0032385 | 0.010944 | 0.0032702 | 7.7568e-05 | 1.4424e-06 | 0.010605 | 0.010683 | 0.01076 | 0.010838 | 0.010915 | 0.010917 | 0.010918 | 0.01092 | 0.010921 | 0.010923 | 0.010924 | 0.010926 | 0.010927 | 0.010928 | 0.01093 | 0.010931 | 0.010933 | 0.010934 | 0.010936 | 0.010937 | 3.2432e-05 | 1.5823e-06 | 0.0031088 | 0.0031412 | 0.0031737 | 0.0032061 | 0.0032385 | 0.0032401 | 0.0032417 | 0.0032433 | 0.0032449 | 0.0032464 | 0.003248 | 0.0032496 | 0.0032512 | 0.0032528 | 0.0032544 | 0.0032559 | 0.0032575 | 0.0032591 | 0.0032607 | 0.0032623
| ART023-76359967 | 81 | 81 | 0.0070143 | 0 | 0.010065 | 0 | 0.0098956 | 0 | 8.716e-05 | -8.4652e-06 | 0.0097163 | 0.0098034 | 0.0098906 | 0.0099778 | 0.010065 | 0.010056 | 0.010048 | 0.01004 | 0.010031 | 0.010023 | 0.010014 | 0.010006 | 0.0099972 | 0.0099887 | 0.0099803 | 0.0099718 | 0.0099633 | 0.0099549 | 0.0099464 | 0.0099379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART031-140150600 | 36 | 36 | 0.0051508 | 0 | 0.0067453 | 0 | 0.0066632 | 0 | 4.5558e-05 | -4.1053e-06 | 0.006563 | 0.0066086 | 0.0066542 | 0.0066997 | 0.0067453 | 0.0067412 | 0.0067371 | 0.006733 | 0.0067289 | 0.0067247 | 0.0067206 | 0.0067165 | 0.0067124 | 0.0067083 | 0.0067042 | 0.0067001 | 0.006696 | 0.0066919 | 0.0066878 | 0.0066837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART031-15411744 | 1453 | 991 | 0.00727 | 0.0029246 | 0.0089299 | 0.0048779 | 0.009034 | 0.0050599 | 4.7425e-05 | 5.2038e-06 | 0.0087402 | 0.0087876 | 0.008835 | 0.0088825 | 0.0089299 | 0.0089351 | 0.0089403 | 0.0089455 | 0.0089507 | 0.0089559 | 0.0089611 | 0.0089663 | 0.0089715 | 0.0089767 | 0.0089819 | 0.0089871 | 0.0089923 | 0.0089975 | 0.0090027 | 0.0090079 | 5.5808e-05 | 9.1039e-06 | 0.0046546 | 0.0047104 | 0.0047663 | 0.0048221 | 0.0048779 | 0.004887 | 0.0048961 | 0.0049052 | 0.0049143 | 0.0049234 | 0.0049325 | 0.0049416 | 0.0049507 | 0.0049598 | 0.0049689 | 0.004978 | 0.0049871 | 0.0049962 | 0.0050053 | 0.0050144
| ART031-155164001 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART031-155164103 | 6 | 6 | 2.78e-05 | 0 | 4.43e-05 | 0 | 4.51e-05 | 0 | 4.7143e-07 | 4e-08 | 4.2414e-05 | 4.2886e-05 | 4.3357e-05 | 4.3829e-05 | 4.43e-05 | 4.434e-05 | 4.438e-05 | 4.442e-05 | 4.446e-05 | 4.45e-05 | 4.454e-05 | 4.458e-05 | 4.462e-05 | 4.466e-05 | 4.47e-05 | 4.474e-05 | 4.478e-05 | 4.482e-05 | 4.486e-05 | 4.49e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART031-76359985 | 41 | 41 | 0.0012831 | 0 | 0.0018365 | 0 | 0.0018676 | 0 | 1.5813e-05 | 1.5551e-06 | 0.0017733 | 0.0017891 | 0.0018049 | 0.0018207 | 0.0018365 | 0.0018381 | 0.0018396 | 0.0018412 | 0.0018427 | 0.0018443 | 0.0018458 | 0.0018474 | 0.001849 | 0.0018505 | 0.0018521 | 0.0018536 | 0.0018552 | 0.0018567 | 0.0018583 | 0.0018598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART031-76433910 | 462 | 346 | 0.01096 | 0.0062524 | 0.014373 | 0.0081981 | 0.014403 | 0.0081929 | 9.7517e-05 | 1.4964e-06 | 0.013983 | 0.01408 | 0.014178 | 0.014275 | 0.014373 | 0.014374 | 0.014376 | 0.014377 | 0.014379 | 0.01438 | 0.014382 | 0.014383 | 0.014385 | 0.014386 | 0.014388 | 0.014389 | 0.014391 | 0.014392 | 0.014394 | 0.014395 | 5.5591e-05 | -2.5915e-07 | 0.0079757 | 0.0080313 | 0.0080869 | 0.0081425 | 0.0081981 | 0.0081978 | 0.0081975 | 0.0081973 | 0.008197 | 0.0081968 | 0.0081965 | 0.0081962 | 0.008196 | 0.0081957 | 0.0081955 | 0.0081952 | 0.0081949 | 0.0081947 | 0.0081944 | 0.0081942
| ART031-78747678 | 30 | 30 | 0.0026783 | 0 | 0.0035516 | 0 | 0.0036462 | 0 | 2.4951e-05 | 4.7308e-06 | 0.0034517 | 0.0034767 | 0.0035016 | 0.0035266 | 0.0035516 | 0.0035563 | 0.003561 | 0.0035657 | 0.0035705 | 0.0035752 | 0.0035799 | 0.0035847 | 0.0035894 | 0.0035941 | 0.0035989 | 0.0036036 | 0.0036083 | 0.0036131 | 0.0036178 | 0.0036225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART031-78747795 | 0 | 0 | 0.0034261 | 0 | 0.0048398 | 0 | 0.0048865 | 0 | 4.0389e-05 | 2.3387e-06 | 0.0046782 | 0.0047186 | 0.004759 | 0.0047994 | 0.0048398 | 0.0048421 | 0.0048444 | 0.0048468 | 0.0048491 | 0.0048515 | 0.0048538 | 0.0048561 | 0.0048585 | 0.0048608 | 0.0048631 | 0.0048655 | 0.0048678 | 0.0048702 | 0.0048725 | 0.0048748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-15411794 | 1901 | 462 | 0.01355 | 0.0043571 | 0.017678 | 0.0057923 | 0.016848 | 0.0055076 | 0.00011794 | -4.152e-05 | 0.017207 | 0.017325 | 0.017442 | 0.01756 | 0.017678 | 0.017637 | 0.017595 | 0.017554 | 0.017512 | 0.017471 | 0.017429 | 0.017388 | 0.017346 | 0.017305 | 0.017263 | 0.017222 | 0.01718 | 0.017139 | 0.017097 | 0.017056 | 4.1006e-05 | -1.4239e-05 | 0.0056283 | 0.0056693 | 0.0057103 | 0.0057513 | 0.0057923 | 0.0057781 | 0.0057639 | 0.0057496 | 0.0057354 | 0.0057211 | 0.0057069 | 0.0056927 | 0.0056784 | 0.0056642 | 0.0056499 | 0.0056357 | 0.0056215 | 0.0056072 | 0.005593 | 0.0055788
| ART033-154972245 | 36 | 36 | 0.00098687 | 0 | 0.0013351 | 0 | 0.0013643 | 0 | 9.9507e-06 | 1.4562e-06 | 0.0012953 | 0.0013053 | 0.0013152 | 0.0013252 | 0.0013351 | 0.0013366 | 0.0013381 | 0.0013395 | 0.001341 | 0.0013424 | 0.0013439 | 0.0013453 | 0.0013468 | 0.0013483 | 0.0013497 | 0.0013512 | 0.0013526 | 0.0013541 | 0.0013555 | 0.001357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-154972416 | 16 | 16 | 0.0010784 | 0 | 0.0015464 | 0 | 0.0014821 | 0 | 1.3373e-05 | -3.2179e-06 | 0.0014929 | 0.0015063 | 0.0015197 | 0.0015331 | 0.0015464 | 0.0015432 | 0.00154 | 0.0015368 | 0.0015336 | 0.0015303 | 0.0015271 | 0.0015239 | 0.0015207 | 0.0015175 | 0.0015142 | 0.001511 | 0.0015078 | 0.0015046 | 0.0015014 | 0.0014982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-154972520 | 12 | 12 | 0.0005566 | 0 | 0.0008369 | 0 | 0.00085455 | 0 | 8.0084e-06 | 8.8245e-07 | 0.00080486 | 0.00081287 | 0.00082088 | 0.00082889 | 0.0008369 | 0.00083778 | 0.00083866 | 0.00083954 | 0.00084043 | 0.00084131 | 0.00084219 | 0.00084307 | 0.00084396 | 0.00084484 | 0.00084572 | 0.0008466 | 0.00084749 | 0.00084837 | 0.00084925 | 0.00085013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-154972637 | 20 | 20 | 5.53e-06 | 0 | 8.8e-06 | 0 | 7.88e-06 | 0 | 9.3429e-08 | -4.6e-08 | 8.4263e-06 | 8.5197e-06 | 8.6131e-06 | 8.7066e-06 | 8.8e-06 | 8.754e-06 | 8.708e-06 | 8.662e-06 | 8.616e-06 | 8.57e-06 | 8.524e-06 | 8.478e-06 | 8.432e-06 | 8.386e-06 | 8.34e-06 | 8.294e-06 | 8.248e-06 | 8.202e-06 | 8.156e-06 | 8.11e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155019358 | 44 | 44 | 0.00016591 | 0 | 0.00024924 | 0 | 0.00023394 | 0 | 2.3809e-06 | -7.651e-07 | 0.00023972 | 0.0002421 | 0.00024448 | 0.00024686 | 0.00024924 | 0.00024848 | 0.00024771 | 0.00024695 | 0.00024618 | 0.00024542 | 0.00024465 | 0.00024389 | 0.00024312 | 0.00024236 | 0.00024159 | 0.00024083 | 0.00024006 | 0.0002393 | 0.00023853 | 0.00023777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155019455 | 0 | 0 | 1.36e-07 | 0 | 1.92e-07 | 0 | 1.85e-07 | 0 | 1.6e-09 | -3.5e-10 | 1.856e-07 | 1.872e-07 | 1.888e-07 | 1.904e-07 | 1.92e-07 | 1.9165e-07 | 1.913e-07 | 1.9095e-07 | 1.906e-07 | 1.9025e-07 | 1.899e-07 | 1.8955e-07 | 1.892e-07 | 1.8885e-07 | 1.885e-07 | 1.8815e-07 | 1.878e-07 | 1.8745e-07 | 1.871e-07 | 1.8675e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155019644 | 61 | 61 | 0.0011867 | 0 | 0.0016334 | 0 | 0.0017373 | 0 | 1.2764e-05 | 5.1948e-06 | 0.0015824 | 0.0015951 | 0.0016079 | 0.0016207 | 0.0016334 | 0.0016386 | 0.0016438 | 0.001649 | 0.0016542 | 0.0016594 | 0.0016646 | 0.0016698 | 0.001675 | 0.0016802 | 0.0016854 | 0.0016906 | 0.0016958 | 0.001701 | 0.0017062 | 0.0017114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155019780 | 2 | 2 | 0.0012273 | 0 | 0.0016164 | 0 | 0.0015693 | 0 | 1.1117e-05 | -2.3529e-06 | 0.0015719 | 0.001583 | 0.0015941 | 0.0016053 | 0.0016164 | 0.001614 | 0.0016117 | 0.0016093 | 0.001607 | 0.0016046 | 0.0016023 | 0.0015999 | 0.0015976 | 0.0015952 | 0.0015928 | 0.0015905 | 0.0015881 | 0.0015858 | 0.0015834 | 0.0015811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155019881 | 9 | 9 | 0.0011621 | 0 | 0.001418 | 0 | 0.0013564 | 0 | 7.3104e-06 | -3.0799e-06 | 0.0013887 | 0.0013961 | 0.0014034 | 0.0014107 | 0.001418 | 0.0014149 | 0.0014118 | 0.0014087 | 0.0014057 | 0.0014026 | 0.0013995 | 0.0013964 | 0.0013933 | 0.0013903 | 0.0013872 | 0.0013841 | 0.001381 | 0.0013779 | 0.0013749 | 0.0013718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155025562 | 54 | 54 | 0.00042973 | 0 | 0.00063908 | 0 | 0.00057798 | 0 | 5.9813e-06 | -3.0548e-06 | 0.00061515 | 0.00062113 | 0.00062711 | 0.0006331 | 0.00063908 | 0.00063602 | 0.00063297 | 0.00062991 | 0.00062686 | 0.0006238 | 0.00062075 | 0.00061769 | 0.00061464 | 0.00061158 | 0.00060853 | 0.00060547 | 0.00060242 | 0.00059937 | 0.00059631 | 0.00059326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155025764 | 4 | 4 | 9.76e-06 | 0 | 1.69e-05 | 0 | 1.78e-05 | 0 | 2.04e-07 | 4.5e-08 | 1.6084e-05 | 1.6288e-05 | 1.6492e-05 | 1.6696e-05 | 1.69e-05 | 1.6945e-05 | 1.699e-05 | 1.7035e-05 | 1.708e-05 | 1.7125e-05 | 1.717e-05 | 1.7215e-05 | 1.726e-05 | 1.7305e-05 | 1.735e-05 | 1.7395e-05 | 1.744e-05 | 1.7485e-05 | 1.753e-05 | 1.7575e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155025850 | 38 | 38 | 9.3e-06 | 0 | 1.57e-05 | 0 | 1.65e-05 | 0 | 1.8286e-07 | 4e-08 | 1.4969e-05 | 1.5151e-05 | 1.5334e-05 | 1.5517e-05 | 1.57e-05 | 1.574e-05 | 1.578e-05 | 1.582e-05 | 1.586e-05 | 1.59e-05 | 1.594e-05 | 1.598e-05 | 1.602e-05 | 1.606e-05 | 1.61e-05 | 1.614e-05 | 1.618e-05 | 1.622e-05 | 1.626e-05 | 1.63e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155026277 | 46 | 46 | 6.2e-05 | 0 | 9.42e-05 | 0 | 9.45e-05 | 0 | 9.2e-07 | 1.5e-08 | 9.052e-05 | 9.144e-05 | 9.236e-05 | 9.328e-05 | 9.42e-05 | 9.4215e-05 | 9.423e-05 | 9.4245e-05 | 9.426e-05 | 9.4275e-05 | 9.429e-05 | 9.4305e-05 | 9.432e-05 | 9.4335e-05 | 9.435e-05 | 9.4365e-05 | 9.438e-05 | 9.4395e-05 | 9.441e-05 | 9.4425e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155052342 | 37 | 37 | 0.0057339 | 0 | 0.0079399 | 0 | 0.0080569 | 0 | 6.3027e-05 | 5.8503e-06 | 0.0076878 | 0.0077508 | 0.0078138 | 0.0078769 | 0.0079399 | 0.0079457 | 0.0079516 | 0.0079574 | 0.0079633 | 0.0079691 | 0.007975 | 0.0079808 | 0.0079867 | 0.0079925 | 0.0079984 | 0.0080042 | 0.0080101 | 0.0080159 | 0.0080218 | 0.0080276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155052479 | 20 | 20 | 0.00010059 | 0 | 0.00014548 | 0 | 0.00013852 | 0 | 1.2826e-06 | -3.48e-07 | 0.00014035 | 0.00014163 | 0.00014291 | 0.0001442 | 0.00014548 | 0.00014513 | 0.00014478 | 0.00014443 | 0.00014409 | 0.00014374 | 0.00014339 | 0.00014304 | 0.00014269 | 0.00014235 | 0.000142 | 0.00014165 | 0.0001413 | 0.00014095 | 0.00014061 | 0.00014026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155052606 | 5 | 5 | 2.67e-06 | 0 | 5.52e-06 | 0 | 4.71e-06 | 0 | 8.1429e-08 | -4.05e-08 | 5.1943e-06 | 5.2757e-06 | 5.3571e-06 | 5.4386e-06 | 5.52e-06 | 5.4795e-06 | 5.439e-06 | 5.3985e-06 | 5.358e-06 | 5.3175e-06 | 5.277e-06 | 5.2365e-06 | 5.196e-06 | 5.1555e-06 | 5.115e-06 | 5.0745e-06 | 5.034e-06 | 4.9935e-06 | 4.953e-06 | 4.9125e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155052720 | 6 | 6 | 2.32e-06 | 0 | 4.09e-06 | 0 | 3.78e-06 | 0 | 5.0571e-08 | -1.55e-08 | 3.8877e-06 | 3.9383e-06 | 3.9889e-06 | 4.0394e-06 | 4.09e-06 | 4.0745e-06 | 4.059e-06 | 4.0435e-06 | 4.028e-06 | 4.0125e-06 | 3.997e-06 | 3.9815e-06 | 3.966e-06 | 3.9505e-06 | 3.935e-06 | 3.9195e-06 | 3.904e-06 | 3.8885e-06 | 3.873e-06 | 3.8575e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155062161 | 6 | 6 | 1.95e-06 | 0 | 3.65e-06 | 0 | 3.37e-06 | 0 | 4.8571e-08 | -1.4e-08 | 3.4557e-06 | 3.5043e-06 | 3.5529e-06 | 3.6014e-06 | 3.65e-06 | 3.636e-06 | 3.622e-06 | 3.608e-06 | 3.594e-06 | 3.58e-06 | 3.566e-06 | 3.552e-06 | 3.538e-06 | 3.524e-06 | 3.51e-06 | 3.496e-06 | 3.482e-06 | 3.468e-06 | 3.454e-06 | 3.44e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155062324 | 3 | 3 | 4.26e-07 | 0 | 7.95e-07 | 0 | 7.17e-07 | 0 | 1.0543e-08 | -3.9e-09 | 7.5283e-07 | 7.6337e-07 | 7.7391e-07 | 7.8446e-07 | 7.95e-07 | 7.911e-07 | 7.872e-07 | 7.833e-07 | 7.794e-07 | 7.755e-07 | 7.716e-07 | 7.677e-07 | 7.638e-07 | 7.599e-07 | 7.56e-07 | 7.521e-07 | 7.482e-07 | 7.443e-07 | 7.404e-07 | 7.365e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155062418 | 38 | 38 | 0.00066881 | 0 | 0.0010235 | 0 | 0.00091249 | 0 | 1.0134e-05 | -5.5503e-06 | 0.00098296 | 0.00099309 | 0.0010032 | 0.0010134 | 0.0010235 | 0.0010179 | 0.0010124 | 0.0010068 | 0.0010013 | 0.00099574 | 0.00099019 | 0.00098464 | 0.00097909 | 0.00097354 | 0.00096799 | 0.00096244 | 0.00095689 | 0.00095134 | 0.00094579 | 0.00094024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155079125 | 23 | 23 | 0.00043213 | 0 | 0.00059856 | 0 | 0.00054529 | 0 | 4.7549e-06 | -2.6634e-06 | 0.00057954 | 0.00058429 | 0.00058905 | 0.0005938 | 0.00059856 | 0.00059589 | 0.00059323 | 0.00059057 | 0.0005879 | 0.00058524 | 0.00058258 | 0.00057991 | 0.00057725 | 0.00057459 | 0.00057192 | 0.00056926 | 0.0005666 | 0.00056393 | 0.00056127 | 0.00055861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155091128 | 33 | 33 | 0.00073768 | 0 | 0.00092297 | 0 | 0.00087115 | 0 | 5.2939e-06 | -2.591e-06 | 0.00090179 | 0.00090709 | 0.00091238 | 0.00091767 | 0.00092297 | 0.00092038 | 0.00091778 | 0.00091519 | 0.0009126 | 0.00091001 | 0.00090742 | 0.00090483 | 0.00090224 | 0.00089965 | 0.00089706 | 0.00089447 | 0.00089187 | 0.00088928 | 0.00088669 | 0.0008841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155155386 | 5 | 5 | 0.00048952 | 0 | 0.00064081 | 0 | 0.00061776 | 0 | 4.3226e-06 | -1.1525e-06 | 0.00062352 | 0.00062784 | 0.00063216 | 0.00063649 | 0.00064081 | 0.00063966 | 0.00063851 | 0.00063735 | 0.0006362 | 0.00063505 | 0.0006339 | 0.00063274 | 0.00063159 | 0.00063044 | 0.00062929 | 0.00062813 | 0.00062698 | 0.00062583 | 0.00062468 | 0.00062352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-162913151 | 392 | 333 | 0.0025649 | 0.00023914 | 0.0034489 | 0.00034205 | 0.0032512 | 0.00032186 | 2.5258e-05 | -9.8872e-06 | 0.0033479 | 0.0033732 | 0.0033984 | 0.0034237 | 0.0034489 | 0.0034391 | 0.0034292 | 0.0034193 | 0.0034094 | 0.0033995 | 0.0033896 | 0.0033797 | 0.0033699 | 0.00336 | 0.0033501 | 0.0033402 | 0.0033303 | 0.0033204 | 0.0033105 | 0.0033006 | 2.9404e-06 | -1.0098e-06 | 0.00033029 | 0.00033323 | 0.00033617 | 0.00033911 | 0.00034205 | 0.00034104 | 0.00034003 | 0.00033902 | 0.00033801 | 0.000337 | 0.000336 | 0.00033499 | 0.00033398 | 0.00033297 | 0.00033196 | 0.00033095 | 0.00032994 | 0.00032893 | 0.00032792 | 0.00032691
| ART033-183308941 | 6 | 6 | 6.38e-07 | 0 | 1.11e-06 | 0 | 9.97e-07 | 0 | 1.3486e-08 | -5.65e-09 | 1.0561e-06 | 1.0695e-06 | 1.083e-06 | 1.0965e-06 | 1.11e-06 | 1.1044e-06 | 1.0987e-06 | 1.0931e-06 | 1.0874e-06 | 1.0817e-06 | 1.0761e-06 | 1.0704e-06 | 1.0648e-06 | 1.0591e-06 | 1.0535e-06 | 1.0478e-06 | 1.0422e-06 | 1.0365e-06 | 1.0309e-06 | 1.0252e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-24601322 | 743 | 528 | 0.0036623 | 0.00031756 | 0.0052427 | 0.00047976 | 0.0049994 | 0.00045714 | 4.5154e-05 | -1.2162e-05 | 0.0050621 | 0.0051072 | 0.0051524 | 0.0051975 | 0.0052427 | 0.0052305 | 0.0052183 | 0.0052062 | 0.005194 | 0.0051819 | 0.0051697 | 0.0051575 | 0.0051454 | 0.0051332 | 0.005121 | 0.0051089 | 0.0050967 | 0.0050846 | 0.0050724 | 0.0050602 | 4.6343e-06 | -1.1309e-06 | 0.00046122 | 0.00046586 | 0.00047049 | 0.00047512 | 0.00047976 | 0.00047863 | 0.0004775 | 0.00047637 | 0.00047524 | 0.0004741 | 0.00047297 | 0.00047184 | 0.00047071 | 0.00046958 | 0.00046845 | 0.00046732 | 0.00046619 | 0.00046506 | 0.00046393 | 0.0004628
| ART033-80719107 | 35 | 35 | 0.0013495 | 0 | 0.0018879 | 0 | 0.0018964 | 0 | 1.5381e-05 | 4.252e-07 | 0.0018263 | 0.0018417 | 0.0018571 | 0.0018725 | 0.0018879 | 0.0018883 | 0.0018887 | 0.0018891 | 0.0018896 | 0.00189 | 0.0018904 | 0.0018908 | 0.0018913 | 0.0018917 | 0.0018921 | 0.0018925 | 0.001893 | 0.0018934 | 0.0018938 | 0.0018942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART034-15411844 | 2427 | 2427 | 0.019329 | 0 | 0.027067 | 0 | 0.027511 | 0 | 0.0002211 | 2.2165e-05 | 0.026183 | 0.026404 | 0.026625 | 0.026846 | 0.027067 | 0.02709 | 0.027112 | 0.027134 | 0.027156 | 0.027178 | 0.0272 | 0.027223 | 0.027245 | 0.027267 | 0.027289 | 0.027311 | 0.027333 | 0.027356 | 0.027378 | 0.0274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART034-15411868 | 2432 | 5 | 0 | 4.46e-07 | 0 | 7.91e-07 | 0 | 8.25e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8571e-09 | 1.7e-09 | 7.5157e-07 | 7.6143e-07 | 7.7129e-07 | 7.8114e-07 | 7.91e-07 | 7.927e-07 | 7.944e-07 | 7.961e-07 | 7.978e-07 | 7.995e-07 | 8.012e-07 | 8.029e-07 | 8.046e-07 | 8.063e-07 | 8.08e-07 | 8.097e-07 | 8.114e-07 | 8.131e-07 | 8.148e-07 | 8.165e-07
| BAN001-15414753 | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN001-15414766 | 488 | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN002-15414829 | 1544 | 1544 | 0.0090681 | 0 | 0.011869 | 0 | 0.012368 | 0 | 8.004e-05 | 2.4943e-05 | 0.011549 | 0.011629 | 0.011709 | 0.011789 | 0.011869 | 0.011894 | 0.011919 | 0.011944 | 0.011969 | 0.011994 | 0.012019 | 0.012044 | 0.012069 | 0.012094 | 0.012119 | 0.012144 | 0.012169 | 0.012194 | 0.012219 | 0.012244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-141839634 | 24 | 24 | 0.0012097 | 0 | 0.0017015 | 0 | 0.0018389 | 0 | 1.405e-05 | 6.8743e-06 | 0.0016453 | 0.0016593 | 0.0016734 | 0.0016874 | 0.0017015 | 0.0017083 | 0.0017152 | 0.0017221 | 0.001729 | 0.0017358 | 0.0017427 | 0.0017496 | 0.0017564 | 0.0017633 | 0.0017702 | 0.0017771 | 0.0017839 | 0.0017908 | 0.0017977 | 0.0018046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-141839757 | 53 | 53 | 0.0066049 | 0 | 0.0081044 | 0 | 0.0084499 | 0 | 4.2844e-05 | 1.7277e-05 | 0.007933 | 0.0079759 | 0.0080187 | 0.0080616 | 0.0081044 | 0.0081217 | 0.008139 | 0.0081562 | 0.0081735 | 0.0081908 | 0.0082081 | 0.0082253 | 0.0082426 | 0.0082599 | 0.0082772 | 0.0082945 | 0.0083117 | 0.008329 | 0.0083463 | 0.0083636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-141839920 | 11 | 11 | 0.0016332 | 0 | 0.0021734 | 0 | 0.0023281 | 0 | 1.5435e-05 | 7.7319e-06 | 0.0021117 | 0.0021271 | 0.0021426 | 0.002158 | 0.0021734 | 0.0021812 | 0.0021889 | 0.0021966 | 0.0022044 | 0.0022121 | 0.0022198 | 0.0022276 | 0.0022353 | 0.002243 | 0.0022508 | 0.0022585 | 0.0022662 | 0.002274 | 0.0022817 | 0.0022894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-141840240 | 47 | 47 | 0.012519 | 0 | 0.016076 | 0 | 0.017619 | 0 | 0.00010162 | 7.7151e-05 | 0.015669 | 0.015771 | 0.015873 | 0.015974 | 0.016076 | 0.016153 | 0.01623 | 0.016307 | 0.016384 | 0.016462 | 0.016539 | 0.016616 | 0.016693 | 0.01677 | 0.016847 | 0.016924 | 0.017002 | 0.017079 | 0.017156 | 0.017233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-154067153 | 4483 | 3394 | 0.022378 | 0.00556 | 0.025943 | 0.0075086 | 0.028113 | 0.0090313 | 0.00010188 | 0.00010848 | 0.025536 | 0.025638 | 0.02574 | 0.025842 | 0.025943 | 0.026052 | 0.02616 | 0.026269 | 0.026377 | 0.026486 | 0.026594 | 0.026703 | 0.026811 | 0.02692 | 0.027028 | 0.027137 | 0.027245 | 0.027354 | 0.027462 | 0.027571 | 5.5675e-05 | 7.6135e-05 | 0.0072859 | 0.0073416 | 0.0073973 | 0.0074529 | 0.0075086 | 0.0075847 | 0.0076609 | 0.007737 | 0.0078131 | 0.0078893 | 0.0079654 | 0.0080415 | 0.0081177 | 0.0081938 | 0.00827 | 0.0083461 | 0.0084222 | 0.0084984 | 0.0085745 | 0.0086506
| BAN003-15414742 | 6457 | 0 | 0.048373 | 0.0055873 | 0.049809 | 0.0056833 | 0.049101 | 0.0056362 | 4.1028e-05 | -3.5358e-05 | 0.049645 | 0.049686 | 0.049727 | 0.049768 | 0.049809 | 0.049773 | 0.049738 | 0.049703 | 0.049667 | 0.049632 | 0.049596 | 0.049561 | 0.049526 | 0.04949 | 0.049455 | 0.04942 | 0.049384 | 0.049349 | 0.049314 | 0.049278 | 2.743e-06 | -2.3544e-06 | 0.0056723 | 0.0056751 | 0.0056778 | 0.0056806 | 0.0056833 | 0.005681 | 0.0056786 | 0.0056762 | 0.0056739 | 0.0056715 | 0.0056692 | 0.0056668 | 0.0056645 | 0.0056621 | 0.0056598 | 0.0056574 | 0.0056551 | 0.0056527 | 0.0056503 | 0.005648
| BAN003-159380665 | 37 | 37 | 0.0068245 | 0 | 0.010277 | 0 | 0.011094 | 0 | 9.8629e-05 | 4.086e-05 | 0.009882 | 0.0099807 | 0.010079 | 0.010178 | 0.010277 | 0.010317 | 0.010358 | 0.010399 | 0.01044 | 0.010481 | 0.010522 | 0.010563 | 0.010603 | 0.010644 | 0.010685 | 0.010726 | 0.010767 | 0.010808 | 0.010849 | 0.010889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-159380816 | 80 | 80 | 0.0076933 | 0 | 0.010032 | 0 | 0.010579 | 0 | 6.6825e-05 | 2.7351e-05 | 0.0097649 | 0.0098317 | 0.0098986 | 0.0099654 | 0.010032 | 0.01006 | 0.010087 | 0.010114 | 0.010142 | 0.010169 | 0.010196 | 0.010224 | 0.010251 | 0.010278 | 0.010306 | 0.010333 | 0.01036 | 0.010388 | 0.010415 | 0.010442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-163842570 | 22 | 22 | 0.002096 | 0 | 0.0029519 | 0 | 0.0034831 | 0 | 2.4454e-05 | 2.6558e-05 | 0.0028541 | 0.0028786 | 0.002903 | 0.0029275 | 0.0029519 | 0.0029785 | 0.003005 | 0.0030316 | 0.0030581 | 0.0030847 | 0.0031113 | 0.0031378 | 0.0031644 | 0.0031909 | 0.0032175 | 0.0032441 | 0.0032706 | 0.0032972 | 0.0033237 | 0.0033503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-164488210 | 18 | 18 | 0.0026076 | 0 | 0.003757 | 0 | 0.0043546 | 0 | 3.2841e-05 | 2.9882e-05 | 0.0036256 | 0.0036585 | 0.0036913 | 0.0037242 | 0.003757 | 0.0037869 | 0.0038168 | 0.0038466 | 0.0038765 | 0.0039064 | 0.0039363 | 0.0039662 | 0.0039961 | 0.0040259 | 0.0040558 | 0.0040857 | 0.0041156 | 0.0041455 | 0.0041753 | 0.0042052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-171330864 | 38 | 38 | 0.0057594 | 0 | 0.0079782 | 0 | 0.0090182 | 0 | 6.3394e-05 | 5.2e-05 | 0.0077246 | 0.007788 | 0.0078514 | 0.0079148 | 0.0079782 | 0.0080302 | 0.0080822 | 0.0081342 | 0.0081862 | 0.0082382 | 0.0082902 | 0.0083422 | 0.0083942 | 0.0084462 | 0.0084982 | 0.0085502 | 0.0086022 | 0.0086542 | 0.0087062 | 0.0087582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-193118819 | 4954 | 393 | 0.023044 | 0.0082847 | 0.027544 | 0.010166 | 0.030912 | 0.011596 | 0.00012857 | 0.00016838 | 0.02703 | 0.027159 | 0.027287 | 0.027416 | 0.027544 | 0.027713 | 0.027881 | 0.028049 | 0.028218 | 0.028386 | 0.028554 | 0.028723 | 0.028891 | 0.02906 | 0.029228 | 0.029396 | 0.029565 | 0.029733 | 0.029902 | 0.03007 | 5.3757e-05 | 7.1502e-05 | 0.0099511 | 0.010005 | 0.010059 | 0.010112 | 0.010166 | 0.010238 | 0.010309 | 0.010381 | 0.010452 | 0.010524 | 0.010595 | 0.010667 | 0.010738 | 0.01081 | 0.010881 | 0.010953 | 0.011024 | 0.011096 | 0.011167 | 0.011239
| BAN003-193396210 | 652 | 297 | 0.0025343 | 0.0057499 | 0.0032329 | 0.0077227 | 0.0036472 | 0.0092198 | 1.9961e-05 | 2.0716e-05 | 0.0031531 | 0.003173 | 0.003193 | 0.003213 | 0.0032329 | 0.0032536 | 0.0032744 | 0.0032951 | 0.0033158 | 0.0033365 | 0.0033572 | 0.0033779 | 0.0033986 | 0.0034194 | 0.0034401 | 0.0034608 | 0.0034815 | 0.0035022 | 0.0035229 | 0.0035437 | 5.6363e-05 | 7.4857e-05 | 0.0074972 | 0.0075536 | 0.0076099 | 0.0076663 | 0.0077227 | 0.0077975 | 0.0078724 | 0.0079472 | 0.0080221 | 0.0080969 | 0.0081718 | 0.0082466 | 0.0083215 | 0.0083964 | 0.0084712 | 0.0085461 | 0.0086209 | 0.0086958 | 0.0087706 | 0.0088455
| BAN003-193396225 | 437 | 336 | 0.014538 | 0.0071716 | 0.019038 | 0.010351 | 0.020915 | 0.011951 | 0.00012858 | 9.3807e-05 | 0.018524 | 0.018653 | 0.018781 | 0.01891 | 0.019038 | 0.019132 | 0.019226 | 0.01932 | 0.019414 | 0.019507 | 0.019601 | 0.019695 | 0.019789 | 0.019883 | 0.019977 | 0.02007 | 0.020164 | 0.020258 | 0.020352 | 0.020446 | 9.0828e-05 | 7.9997e-05 | 0.0099873 | 0.010078 | 0.010169 | 0.01026 | 0.010351 | 0.010431 | 0.010511 | 0.010591 | 0.010671 | 0.010751 | 0.010831 | 0.010911 | 0.010991 | 0.011071 | 0.011151 | 0.011231 | 0.011311 | 0.011391 | 0.011471 | 0.011551
| BAN003-193396423 | 1250 | 654 | 0.029441 | 0.010164 | 0.034682 | 0.012693 | 0.037433 | 0.014275 | 0.00014976 | 0.00013757 | 0.034083 | 0.034233 | 0.034383 | 0.034532 | 0.034682 | 0.03482 | 0.034957 | 0.035095 | 0.035232 | 0.03537 | 0.035507 | 0.035645 | 0.035783 | 0.03592 | 0.036058 | 0.036195 | 0.036333 | 0.03647 | 0.036608 | 0.036746 | 7.2247e-05 | 7.9095e-05 | 0.012404 | 0.012476 | 0.012549 | 0.012621 | 0.012693 | 0.012772 | 0.012851 | 0.01293 | 0.013009 | 0.013088 | 0.013168 | 0.013247 | 0.013326 | 0.013405 | 0.013484 | 0.013563 | 0.013642 | 0.013721 | 0.0138 | 0.013879
| BAN003-24598678 | 63 | 63 | 0.00046612 | 0 | 0.00065818 | 0 | 0.00072917 | 0 | 5.4874e-06 | 3.5497e-06 | 0.00063623 | 0.00064172 | 0.0006472 | 0.00065269 | 0.00065818 | 0.00066173 | 0.00066528 | 0.00066883 | 0.00067238 | 0.00067593 | 0.00067948 | 0.00068303 | 0.00068658 | 0.00069013 | 0.00069368 | 0.00069723 | 0.00070077 | 0.00070432 | 0.00070787 | 0.00071142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-24598720 | 190 | 110 | 0.0054174 | 0.0015866 | 0.0055394 | 0.0016223 | 0.0054818 | 0.0016063 | 3.4853e-06 | -2.8831e-06 | 0.0055255 | 0.005529 | 0.0055325 | 0.0055359 | 0.0055394 | 0.0055365 | 0.0055337 | 0.0055308 | 0.0055279 | 0.005525 | 0.0055221 | 0.0055192 | 0.0055164 | 0.0055135 | 0.0055106 | 0.0055077 | 0.0055048 | 0.0055019 | 0.0054991 | 0.0054962 | 1.0205e-06 | -8.0175e-07 | 0.0016182 | 0.0016192 | 0.0016202 | 0.0016213 | 0.0016223 | 0.0016215 | 0.0016207 | 0.0016199 | 0.0016191 | 0.0016183 | 0.0016175 | 0.0016167 | 0.0016159 | 0.0016151 | 0.0016143 | 0.0016135 | 0.0016127 | 0.0016119 | 0.0016111 | 0.0016103
| BAN003-24598790 | 520 | 432 | 0.023736 | 0.0021833 | 0.028126 | 0.0027396 | 0.029304 | 0.0030659 | 0.00012542 | 5.8908e-05 | 0.027624 | 0.02775 | 0.027875 | 0.028001 | 0.028126 | 0.028185 | 0.028244 | 0.028303 | 0.028362 | 0.028421 | 0.028479 | 0.028538 | 0.028597 | 0.028656 | 0.028715 | 0.028774 | 0.028833 | 0.028892 | 0.028951 | 0.02901 | 1.5896e-05 | 1.6315e-05 | 0.0026761 | 0.002692 | 0.0027079 | 0.0027237 | 0.0027396 | 0.002756 | 0.0027723 | 0.0027886 | 0.0028049 | 0.0028212 | 0.0028375 | 0.0028539 | 0.0028702 | 0.0028865 | 0.0029028 | 0.0029191 | 0.0029354 | 0.0029517 | 0.0029681 | 0.0029844
| BAN003-24610965 | 31 | 31 | 0.0025769 | 0 | 0.0034232 | 0 | 0.0043471 | 0 | 2.4181e-05 | 4.6193e-05 | 0.0033265 | 0.0033507 | 0.0033749 | 0.003399 | 0.0034232 | 0.0034694 | 0.0035156 | 0.0035618 | 0.003608 | 0.0036542 | 0.0037004 | 0.0037466 | 0.0037928 | 0.003839 | 0.0038851 | 0.0039313 | 0.0039775 | 0.0040237 | 0.0040699 | 0.0041161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-79423703 | 23 | 23 | 0.0022447 | 0 | 0.0029594 | 0 | 0.0032646 | 0 | 2.0422e-05 | 1.5259e-05 | 0.0028778 | 0.0028982 | 0.0029186 | 0.002939 | 0.0029594 | 0.0029747 | 0.00299 | 0.0030052 | 0.0030205 | 0.0030357 | 0.003051 | 0.0030663 | 0.0030815 | 0.0030968 | 0.003112 | 0.0031273 | 0.0031426 | 0.0031578 | 0.0031731 | 0.0031883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-79424004 | 76 | 76 | 0.0041328 | 0 | 0.005393 | 0 | 0.0059999 | 0 | 3.6006e-05 | 3.0343e-05 | 0.005249 | 0.005285 | 0.005321 | 0.005357 | 0.005393 | 0.0054234 | 0.0054537 | 0.0054841 | 0.0055144 | 0.0055447 | 0.0055751 | 0.0056054 | 0.0056358 | 0.0056661 | 0.0056965 | 0.0057268 | 0.0057571 | 0.0057875 | 0.0058178 | 0.0058482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-79424224 | 47 | 47 | 0.0062987 | 0 | 0.0085035 | 0 | 0.0095167 | 0 | 6.2995e-05 | 5.0658e-05 | 0.0082515 | 0.0083145 | 0.0083775 | 0.0084405 | 0.0085035 | 0.0085542 | 0.0086048 | 0.0086555 | 0.0087061 | 0.0087568 | 0.0088075 | 0.0088581 | 0.0089088 | 0.0089594 | 0.0090101 | 0.0090607 | 0.0091114 | 0.0091621 | 0.0092127 | 0.0092634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-79424313 | 58 | 58 | 0.0032187 | 0 | 0.0047039 | 0 | 0.005256 | 0 | 4.2435e-05 | 2.7602e-05 | 0.0045342 | 0.0045766 | 0.0046191 | 0.0046615 | 0.0047039 | 0.0047315 | 0.0047591 | 0.0047867 | 0.0048143 | 0.0048419 | 0.0048695 | 0.0048971 | 0.0049247 | 0.0049523 | 0.0049799 | 0.0050075 | 0.0050352 | 0.0050628 | 0.0050904 | 0.005118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-79424384 | 94 | 94 | 0.0066528 | 0 | 0.0089187 | 0 | 0.0098943 | 0 | 6.4739e-05 | 4.8782e-05 | 0.0086598 | 0.0087245 | 0.0087892 | 0.008854 | 0.0089187 | 0.0089675 | 0.0090163 | 0.0090651 | 0.0091138 | 0.0091626 | 0.0092114 | 0.0092602 | 0.009309 | 0.0093577 | 0.0094065 | 0.0094553 | 0.0095041 | 0.0095529 | 0.0096016 | 0.0096504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-79424629 | 80 | 80 | 0.0051498 | 0 | 0.0065571 | 0 | 0.0073905 | 0 | 4.0208e-05 | 4.1673e-05 | 0.0063962 | 0.0064364 | 0.0064766 | 0.0065168 | 0.0065571 | 0.0065987 | 0.0066404 | 0.0066821 | 0.0067237 | 0.0067654 | 0.0068071 | 0.0068488 | 0.0068904 | 0.0069321 | 0.0069738 | 0.0070155 | 0.0070571 | 0.0070988 | 0.0071405 | 0.0071821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN003-79424820 | 39 | 39 | 0.0031724 | 0 | 0.0048 | 0 | 0.0052026 | 0 | 4.6502e-05 | 2.0129e-05 | 0.004614 | 0.0046605 | 0.004707 | 0.0047535 | 0.0048 | 0.0048201 | 0.0048403 | 0.0048604 | 0.0048805 | 0.0049006 | 0.0049208 | 0.0049409 | 0.004961 | 0.0049812 | 0.0050013 | 0.0050214 | 0.0050415 | 0.0050617 | 0.0050818 | 0.0051019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN004-15414853 | 1329 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN004-15414866 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN004-15414892 | 1324 | 1314 | 0.0016639 | 0 | 0.0023169 | 0 | 0.0024869 | 0 | 1.8657e-05 | 8.5005e-06 | 0.0022423 | 0.0022609 | 0.0022796 | 0.0022983 | 0.0023169 | 0.0023254 | 0.0023339 | 0.0023424 | 0.0023509 | 0.0023594 | 0.0023679 | 0.0023764 | 0.0023849 | 0.0023934 | 0.0024019 | 0.0024104 | 0.0024189 | 0.0024274 | 0.0024359 | 0.0024444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN005-15414666 | 1445 | 1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN006-15414916 | 5480 | 3248 | 0.0040532 | 0.00054961 | 0.0055264 | 0.00082475 | 0.0060183 | 0.00091766 | 4.2089e-05 | 2.4599e-05 | 0.005358 | 0.0054001 | 0.0054422 | 0.0054843 | 0.0055264 | 0.005551 | 0.0055756 | 0.0056002 | 0.0056248 | 0.0056494 | 0.005674 | 0.0056986 | 0.0057231 | 0.0057477 | 0.0057723 | 0.0057969 | 0.0058215 | 0.0058461 | 0.0058707 | 0.0058953 | 7.8609e-06 | 4.6457e-06 | 0.0007933 | 0.00080116 | 0.00080903 | 0.00081689 | 0.00082475 | 0.00082939 | 0.00083404 | 0.00083868 | 0.00084333 | 0.00084798 | 0.00085262 | 0.00085727 | 0.00086191 | 0.00086656 | 0.0008712 | 0.00087585 | 0.0008805 | 0.00088514 | 0.00088979 | 0.00089443
| BAN006-157281583 | 6 | 6 | 0.0002904 | 0 | 0.00042774 | 0 | 0.00043655 | 0 | 3.924e-06 | 4.4065e-07 | 0.00041204 | 0.00041597 | 0.00041989 | 0.00042381 | 0.00042774 | 0.00042818 | 0.00042862 | 0.00042906 | 0.0004295 | 0.00042994 | 0.00043038 | 0.00043082 | 0.00043126 | 0.0004317 | 0.00043214 | 0.00043259 | 0.00043303 | 0.00043347 | 0.00043391 | 0.00043435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN006-161068079 | 22 | 22 | 0.00034156 | 0 | 0.00048147 | 0 | 0.00049943 | 0 | 3.9975e-06 | 8.9765e-07 | 0.00046548 | 0.00046948 | 0.00047348 | 0.00047748 | 0.00048147 | 0.00048237 | 0.00048327 | 0.00048417 | 0.00048506 | 0.00048596 | 0.00048686 | 0.00048776 | 0.00048865 | 0.00048955 | 0.00049045 | 0.00049135 | 0.00049224 | 0.00049314 | 0.00049404 | 0.00049494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN006-193339101 | 2232 | 424 | 0.0012339 | 0.0023261 | 0.0015481 | 0.0030645 | 0.0016193 | 0.0032825 | 8.9767e-06 | 3.5563e-06 | 0.0015122 | 0.0015212 | 0.0015302 | 0.0015392 | 0.0015481 | 0.0015517 | 0.0015552 | 0.0015588 | 0.0015624 | 0.0015659 | 0.0015695 | 0.001573 | 0.0015766 | 0.0015801 | 0.0015837 | 0.0015872 | 0.0015908 | 0.0015944 | 0.0015979 | 0.0016015 | 2.1097e-05 | 1.0901e-05 | 0.0029801 | 0.0030012 | 0.0030223 | 0.0030434 | 0.0030645 | 0.0030754 | 0.0030863 | 0.0030972 | 0.0031081 | 0.003119 | 0.0031299 | 0.0031408 | 0.0031517 | 0.0031626 | 0.0031735 | 0.0031844 | 0.0031953 | 0.0032062 | 0.0032171 | 0.003228
| BAN006-193339124 | 576 | 435 | 0.016715 | 0.0018902 | 0.01948 | 0.002484 | 0.019496 | 0.0024632 | 7.8984e-05 | 8.0525e-07 | 0.019164 | 0.019243 | 0.019322 | 0.019401 | 0.01948 | 0.019481 | 0.019482 | 0.019482 | 0.019483 | 0.019484 | 0.019485 | 0.019486 | 0.019486 | 0.019487 | 0.019488 | 0.019489 | 0.01949 | 0.01949 | 0.019491 | 0.019492 | 1.6966e-05 | -1.0402e-06 | 0.0024161 | 0.0024331 | 0.00245 | 0.002467 | 0.002484 | 0.0024829 | 0.0024819 | 0.0024808 | 0.0024798 | 0.0024788 | 0.0024777 | 0.0024767 | 0.0024756 | 0.0024746 | 0.0024736 | 0.0024725 | 0.0024715 | 0.0024704 | 0.0024694 | 0.0024684
| BAN006-193339156 | 532 | 532 | 0.007572 | 0 | 0.01118 | 0 | 0.01155 | 0 | 0.0001031 | 1.8469e-05 | 0.010768 | 0.010871 | 0.010974 | 0.011077 | 0.01118 | 0.011199 | 0.011217 | 0.011236 | 0.011254 | 0.011273 | 0.011291 | 0.01131 | 0.011328 | 0.011347 | 0.011365 | 0.011383 | 0.011402 | 0.01142 | 0.011439 | 0.011457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN006-193339179 | 1232 | 605 | 0.013136 | 0.0031412 | 0.014059 | 0.0041188 | 0.014746 | 0.0047813 | 2.6351e-05 | 3.4352e-05 | 0.013953 | 0.01398 | 0.014006 | 0.014032 | 0.014059 | 0.014093 | 0.014127 | 0.014162 | 0.014196 | 0.01423 | 0.014265 | 0.014299 | 0.014333 | 0.014368 | 0.014402 | 0.014437 | 0.014471 | 0.014505 | 0.01454 | 0.014574 | 2.7931e-05 | 3.3127e-05 | 0.0040071 | 0.004035 | 0.0040629 | 0.0040909 | 0.0041188 | 0.0041519 | 0.004185 | 0.0042182 | 0.0042513 | 0.0042844 | 0.0043176 | 0.0043507 | 0.0043838 | 0.0044169 | 0.0044501 | 0.0044832 | 0.0045163 | 0.0045494 | 0.0045826 | 0.0046157
| BAN006-72501199 | 58 | 58 | 0.0028188 | 0 | 0.0035541 | 0 | 0.0035148 | 0 | 2.1007e-05 | -1.9645e-06 | 0.00347 | 0.003491 | 0.003512 | 0.0035331 | 0.0035541 | 0.0035521 | 0.0035501 | 0.0035482 | 0.0035462 | 0.0035442 | 0.0035423 | 0.0035403 | 0.0035383 | 0.0035364 | 0.0035344 | 0.0035325 | 0.0035305 | 0.0035285 | 0.0035266 | 0.0035246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN006-72501281 | 61 | 61 | 0.0047421 | 0 | 0.0064514 | 0 | 0.0069214 | 0 | 4.8836e-05 | 2.3504e-05 | 0.006256 | 0.0063049 | 0.0063537 | 0.0064025 | 0.0064514 | 0.0064749 | 0.0064984 | 0.0065219 | 0.0065454 | 0.0065689 | 0.0065924 | 0.0066159 | 0.0066394 | 0.0066629 | 0.0066864 | 0.0067099 | 0.0067334 | 0.0067569 | 0.0067804 | 0.0068039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN006-84647249 | 55 | 55 | 0.0015642 | 0 | 0.0022473 | 0 | 0.0022778 | 0 | 1.9517e-05 | 1.5268e-06 | 0.0021692 | 0.0021887 | 0.0022083 | 0.0022278 | 0.0022473 | 0.0022488 | 0.0022503 | 0.0022519 | 0.0022534 | 0.0022549 | 0.0022565 | 0.002258 | 0.0022595 | 0.002261 | 0.0022626 | 0.0022641 | 0.0022656 | 0.0022671 | 0.0022687 | 0.0022702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN006-85222599 | 34 | 34 | 0.0022426 | 0 | 0.0032525 | 0 | 0.0034521 | 0 | 2.8855e-05 | 9.9796e-06 | 0.0031371 | 0.003166 | 0.0031948 | 0.0032237 | 0.0032525 | 0.0032625 | 0.0032725 | 0.0032825 | 0.0032925 | 0.0033024 | 0.0033124 | 0.0033224 | 0.0033324 | 0.0033424 | 0.0033523 | 0.0033623 | 0.0033723 | 0.0033823 | 0.0033923 | 0.0034022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN007-15414603 | 4790 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN007-156954231 | 214 | 214 | 0.033172 | 0 | 0.042061 | 0 | 0.044715 | 0 | 0.00025396 | 0.00013274 | 0.041045 | 0.041299 | 0.041553 | 0.041807 | 0.042061 | 0.042193 | 0.042326 | 0.042459 | 0.042592 | 0.042724 | 0.042857 | 0.04299 | 0.043123 | 0.043255 | 0.043388 | 0.043521 | 0.043654 | 0.043786 | 0.043919 | 0.044052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN007-24598874 | 3879 | 3879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN007-24598888 | 746 | 532 | 0.001691 | 0 | 0.001818 | 0 | 0.00184 | 0 | 3.6287e-06 | 1.0961e-06 | 0.0018035 | 0.0018072 | 0.0018108 | 0.0018144 | 0.001818 | 0.0018191 | 0.0018202 | 0.0018213 | 0.0018224 | 0.0018235 | 0.0018246 | 0.0018257 | 0.0018268 | 0.0018279 | 0.001829 | 0.0018301 | 0.0018312 | 0.0018323 | 0.0018334 | 0.0018345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN008-15414979 | 4081 | 0 | 0.016339 | 0.003807 | 0.020126 | 0.0050853 | 0.021162 | 0.0054653 | 0.00010819 | 5.1824e-05 | 0.019693 | 0.019801 | 0.01991 | 0.020018 | 0.020126 | 0.020178 | 0.02023 | 0.020281 | 0.020333 | 0.020385 | 0.020437 | 0.020489 | 0.020541 | 0.020592 | 0.020644 | 0.020696 | 0.020748 | 0.0208 | 0.020852 | 0.020903 | 3.6521e-05 | 1.9004e-05 | 0.0049392 | 0.0049757 | 0.0050122 | 0.0050487 | 0.0050853 | 0.0051043 | 0.0051233 | 0.0051423 | 0.0051613 | 0.0051803 | 0.0051993 | 0.0052183 | 0.0052373 | 0.0052563 | 0.0052753 | 0.0052943 | 0.0053133 | 0.0053323 | 0.0053513 | 0.0053703
| BAN008-193386449 | 3968 | 0 | 0.0042677 | 0.0019715 | 0.005808 | 0.0028301 | 0.0064572 | 0.0032387 | 4.4006e-05 | 3.2464e-05 | 0.0056319 | 0.0056759 | 0.0057199 | 0.005764 | 0.005808 | 0.0058404 | 0.0058729 | 0.0059054 | 0.0059378 | 0.0059703 | 0.0060027 | 0.0060352 | 0.0060677 | 0.0061001 | 0.0061326 | 0.0061651 | 0.0061975 | 0.00623 | 0.0062625 | 0.0062949 | 2.4533e-05 | 2.0431e-05 | 0.002732 | 0.0027565 | 0.0027811 | 0.0028056 | 0.0028301 | 0.0028506 | 0.002871 | 0.0028914 | 0.0029119 | 0.0029323 | 0.0029527 | 0.0029731 | 0.0029936 | 0.003014 | 0.0030344 | 0.0030549 | 0.0030753 | 0.0030957 | 0.0031162 | 0.0031366
| BAN008-193386491 | 3968 | 0 | 0.050551 | 0.0039826 | 0.060364 | 0.0054865 | 0.065524 | 0.0064018 | 0.00028038 | 0.00025801 | 0.059243 | 0.059523 | 0.059803 | 0.060084 | 0.060364 | 0.060622 | 0.06088 | 0.061138 | 0.061396 | 0.061654 | 0.061912 | 0.06217 | 0.062428 | 0.062686 | 0.062944 | 0.063202 | 0.06346 | 0.063718 | 0.063976 | 0.064234 | 4.2968e-05 | 4.5764e-05 | 0.0053146 | 0.0053576 | 0.0054006 | 0.0054435 | 0.0054865 | 0.0055323 | 0.005578 | 0.0056238 | 0.0056695 | 0.0057153 | 0.0057611 | 0.0058068 | 0.0058526 | 0.0058984 | 0.0059441 | 0.0059899 | 0.0060357 | 0.0060814 | 0.0061272 | 0.0061729
| BAN008-193386514 | 1077 | 1077 | 0.035768 | 0 | 0.043866 | 0 | 0.047614 | 0 | 0.00023134 | 0.00018743 | 0.04294 | 0.043171 | 0.043403 | 0.043634 | 0.043866 | 0.044053 | 0.04424 | 0.044428 | 0.044615 | 0.044803 | 0.04499 | 0.045178 | 0.045365 | 0.045552 | 0.04574 | 0.045927 | 0.046115 | 0.046302 | 0.04649 | 0.046677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN008-193386533 | 113 | 113 | 0.0053999 | 0 | 0.0071643 | 0 | 0.0078734 | 0 | 5.041e-05 | 3.5456e-05 | 0.0069626 | 0.007013 | 0.0070634 | 0.0071138 | 0.0071643 | 0.0071997 | 0.0072352 | 0.0072706 | 0.0073061 | 0.0073415 | 0.007377 | 0.0074124 | 0.0074479 | 0.0074834 | 0.0075188 | 0.0075543 | 0.0075897 | 0.0076252 | 0.0076606 | 0.0076961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN009-15414553 | 3364 | 618 | 0.026005 | 0.0058307 | 0.033005 | 0.0078643 | 0.035136 | 0.0086198 | 0.00019999 | 0.00010654 | 0.032205 | 0.032405 | 0.032605 | 0.032805 | 0.033005 | 0.033111 | 0.033218 | 0.033325 | 0.033431 | 0.033538 | 0.033644 | 0.033751 | 0.033857 | 0.033964 | 0.03407 | 0.034177 | 0.034283 | 0.03439 | 0.034497 | 0.034603 | 5.8102e-05 | 3.7779e-05 | 0.0076319 | 0.00769 | 0.0077481 | 0.0078062 | 0.0078643 | 0.007902 | 0.0079398 | 0.0079776 | 0.0080154 | 0.0080532 | 0.0080909 | 0.0081287 | 0.0081665 | 0.0082043 | 0.0082421 | 0.0082798 | 0.0083176 | 0.0083554 | 0.0083932 | 0.008431
| BAN009-199768607 | 2746 | 1702 | 0.010498 | 0.0046201 | 0.013372 | 0.006503 | 0.015115 | 0.0078209 | 8.2094e-05 | 8.7173e-05 | 0.013043 | 0.013125 | 0.013207 | 0.01329 | 0.013372 | 0.013459 | 0.013546 | 0.013633 | 0.01372 | 0.013808 | 0.013895 | 0.013982 | 0.014069 | 0.014156 | 0.014243 | 0.014331 | 0.014418 | 0.014505 | 0.014592 | 0.014679 | 5.3796e-05 | 6.5897e-05 | 0.0062878 | 0.0063416 | 0.0063954 | 0.0064492 | 0.006503 | 0.0065689 | 0.0066348 | 0.0067007 | 0.0067666 | 0.0068325 | 0.0068984 | 0.0069643 | 0.0070302 | 0.0070961 | 0.007162 | 0.0072279 | 0.0072938 | 0.0073597 | 0.0074256 | 0.0074914
| BAN009-201078585 | 995 | 899 | 0.015335 | 0.0031099 | 0.020656 | 0.0044917 | 0.022345 | 0.0049716 | 0.00015203 | 8.4485e-05 | 0.020048 | 0.0202 | 0.020352 | 0.020504 | 0.020656 | 0.02074 | 0.020825 | 0.020909 | 0.020994 | 0.021078 | 0.021163 | 0.021247 | 0.021332 | 0.021416 | 0.021501 | 0.021585 | 0.02167 | 0.021754 | 0.021839 | 0.021923 | 3.9478e-05 | 2.3999e-05 | 0.0043337 | 0.0043732 | 0.0044127 | 0.0044522 | 0.0044917 | 0.0045157 | 0.0045396 | 0.0045636 | 0.0045876 | 0.0046116 | 0.0046356 | 0.0046596 | 0.0046836 | 0.0047076 | 0.0047316 | 0.0047556 | 0.0047796 | 0.0048036 | 0.0048276 | 0.0048516
| BAN009-77240394 | 49 | 49 | 0.030107 | 0 | 0.037896 | 0 | 0.041902 | 0 | 0.00022256 | 0.0002003 | 0.037006 | 0.037229 | 0.037451 | 0.037674 | 0.037896 | 0.038097 | 0.038297 | 0.038497 | 0.038697 | 0.038898 | 0.039098 | 0.039298 | 0.039499 | 0.039699 | 0.039899 | 0.0401 | 0.0403 | 0.0405 | 0.0407 | 0.040901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN009-77240588 | 41 | 41 | 0.0043834 | 0 | 0.0059838 | 0 | 0.006752 | 0 | 4.5728e-05 | 3.8408e-05 | 0.0058009 | 0.0058466 | 0.0058924 | 0.0059381 | 0.0059838 | 0.0060222 | 0.0060606 | 0.006099 | 0.0061375 | 0.0061759 | 0.0062143 | 0.0062527 | 0.0062911 | 0.0063295 | 0.0063679 | 0.0064063 | 0.0064447 | 0.0064831 | 0.0065215 | 0.0065599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN009-78742110 | 19 | 19 | 0.0023899 | 0 | 0.0034485 | 0 | 0.0036375 | 0 | 3.0248e-05 | 9.446e-06 | 0.0033276 | 0.0033578 | 0.0033881 | 0.0034183 | 0.0034485 | 0.003458 | 0.0034674 | 0.0034769 | 0.0034863 | 0.0034958 | 0.0035052 | 0.0035147 | 0.0035241 | 0.0035336 | 0.003543 | 0.0035525 | 0.0035619 | 0.0035713 | 0.0035808 | 0.0035902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN009-78742394 | 36 | 36 | 0.00041321 | 0 | 0.00061419 | 0 | 0.00072323 | 0 | 5.7423e-06 | 5.4523e-06 | 0.00059122 | 0.00059696 | 0.0006027 | 0.00060845 | 0.00061419 | 0.00061964 | 0.00062509 | 0.00063055 | 0.000636 | 0.00064145 | 0.0006469 | 0.00065235 | 0.00065781 | 0.00066326 | 0.00066871 | 0.00067416 | 0.00067962 | 0.00068507 | 0.00069052 | 0.00069597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN011-15414529 | 561 | 561 | 0.011879 | 0 | 0.014162 | 0 | 0.014225 | 0 | 6.5217e-05 | 3.1714e-06 | 0.013901 | 0.013966 | 0.014031 | 0.014096 | 0.014162 | 0.014165 | 0.014168 | 0.014171 | 0.014174 | 0.014178 | 0.014181 | 0.014184 | 0.014187 | 0.01419 | 0.014193 | 0.014197 | 0.0142 | 0.014203 | 0.014206 | 0.014209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN011-171348706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN013-15414453 | 2713 | 2713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN015-15414416 | 5402 | 2356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN015-24611936 | 3046 | 3046 | 0.021331 | 0 | 0.025318 | 0 | 0.026985 | 0 | 0.0001139 | 8.3384e-05 | 0.024862 | 0.024976 | 0.02509 | 0.025204 | 0.025318 | 0.025401 | 0.025484 | 0.025568 | 0.025651 | 0.025734 | 0.025818 | 0.025901 | 0.025985 | 0.026068 | 0.026151 | 0.026235 | 0.026318 | 0.026402 | 0.026485 | 0.026568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-111131839 | 391 | 391 | 1.48e-05 | 0 | 1.99e-05 | 0 | 2.19e-05 | 0 | 1.4571e-07 | 1e-07 | 1.9317e-05 | 1.9463e-05 | 1.9609e-05 | 1.9754e-05 | 1.99e-05 | 2e-05 | 2.01e-05 | 2.02e-05 | 2.03e-05 | 2.04e-05 | 2.05e-05 | 2.06e-05 | 2.07e-05 | 2.08e-05 | 2.09e-05 | 2.1e-05 | 2.11e-05 | 2.12e-05 | 2.13e-05 | 2.14e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-134530801 | 26 | 26 | 0.0033159 | 0 | 0.0039714 | 0 | 0.0041321 | 0 | 1.873e-05 | 8.0358e-06 | 0.0038965 | 0.0039152 | 0.0039339 | 0.0039527 | 0.0039714 | 0.0039794 | 0.0039875 | 0.0039955 | 0.0040035 | 0.0040116 | 0.0040196 | 0.0040276 | 0.0040357 | 0.0040437 | 0.0040517 | 0.0040598 | 0.0040678 | 0.0040759 | 0.0040839 | 0.0040919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-140236715 | 40 | 40 | 0.00078669 | 0 | 0.00095897 | 0 | 0.00090123 | 0 | 4.9221e-06 | -2.8871e-06 | 0.00093928 | 0.0009442 | 0.00094912 | 0.00095405 | 0.00095897 | 0.00095608 | 0.00095319 | 0.00095031 | 0.00094742 | 0.00094453 | 0.00094165 | 0.00093876 | 0.00093587 | 0.00093298 | 0.0009301 | 0.00092721 | 0.00092432 | 0.00092144 | 0.00091855 | 0.00091566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-140237055 | 33 | 33 | 0.00050478 | 0 | 0.00069289 | 0 | 0.00064942 | 0 | 5.3747e-06 | -2.1737e-06 | 0.00067139 | 0.00067677 | 0.00068214 | 0.00068752 | 0.00069289 | 0.00069072 | 0.00068855 | 0.00068637 | 0.0006842 | 0.00068202 | 0.00067985 | 0.00067768 | 0.0006755 | 0.00067333 | 0.00067116 | 0.00066898 | 0.00066681 | 0.00066463 | 0.00066246 | 0.00066029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-15414096 | 6024 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-15414109 | 6020 | 2803 | 0.0080348 | 0.0010508 | 0.0097338 | 0.0013598 | 0.010066 | 0.0014945 | 4.8544e-05 | 1.6594e-05 | 0.0095396 | 0.0095882 | 0.0096367 | 0.0096852 | 0.0097338 | 0.0097504 | 0.009767 | 0.0097836 | 0.0098002 | 0.0098168 | 0.0098333 | 0.0098499 | 0.0098665 | 0.0098831 | 0.0098997 | 0.0099163 | 0.0099329 | 0.0099495 | 0.0099661 | 0.0099827 | 8.8275e-06 | 6.7369e-06 | 0.0013245 | 0.0013333 | 0.0013421 | 0.0013509 | 0.0013598 | 0.0013665 | 0.0013732 | 0.00138 | 0.0013867 | 0.0013935 | 0.0014002 | 0.0014069 | 0.0014137 | 0.0014204 | 0.0014271 | 0.0014339 | 0.0014406 | 0.0014473 | 0.0014541 | 0.0014608
| BAS011-158128939 | 13 | 13 | 0.0046588 | 0 | 0.0064831 | 0 | 0.0068237 | 0 | 5.2123e-05 | 1.7032e-05 | 0.0062746 | 0.0063267 | 0.0063788 | 0.006431 | 0.0064831 | 0.0065001 | 0.0065171 | 0.0065342 | 0.0065512 | 0.0065682 | 0.0065853 | 0.0066023 | 0.0066193 | 0.0066364 | 0.0066534 | 0.0066704 | 0.0066875 | 0.0067045 | 0.0067215 | 0.0067386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-158493706 | 15 | 15 | 0.00067542 | 0 | 0.00089571 | 0 | 0.00098297 | 0 | 6.2939e-06 | 4.3631e-06 | 0.00087053 | 0.00087683 | 0.00088312 | 0.00088941 | 0.00089571 | 0.00090007 | 0.00090443 | 0.0009088 | 0.00091316 | 0.00091752 | 0.00092189 | 0.00092625 | 0.00093061 | 0.00093497 | 0.00093934 | 0.0009437 | 0.00094806 | 0.00095243 | 0.00095679 | 0.00096115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-158493822 | 9 | 9 | 1.33e-06 | 0 | 2.3e-06 | 0 | 2.28e-06 | 0 | 2.7714e-08 | -1e-09 | 2.1891e-06 | 2.2169e-06 | 2.2446e-06 | 2.2723e-06 | 2.3e-06 | 2.299e-06 | 2.298e-06 | 2.297e-06 | 2.296e-06 | 2.295e-06 | 2.294e-06 | 2.293e-06 | 2.292e-06 | 2.291e-06 | 2.29e-06 | 2.289e-06 | 2.288e-06 | 2.287e-06 | 2.286e-06 | 2.285e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-163842929 | 12 | 12 | 0.002348 | 0 | 0.0030058 | 0 | 0.003238 | 0 | 1.8794e-05 | 1.161e-05 | 0.0029306 | 0.0029494 | 0.0029682 | 0.002987 | 0.0030058 | 0.0030174 | 0.003029 | 0.0030406 | 0.0030523 | 0.0030639 | 0.0030755 | 0.0030871 | 0.0030987 | 0.0031103 | 0.0031219 | 0.0031335 | 0.0031451 | 0.0031567 | 0.0031684 | 0.00318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-163930345 | 15 | 15 | 0.00016692 | 0 | 0.0002282 | 0 | 0.00021248 | 0 | 1.7507e-06 | -7.856e-07 | 0.00022119 | 0.00022294 | 0.00022469 | 0.00022645 | 0.0002282 | 0.00022741 | 0.00022662 | 0.00022584 | 0.00022505 | 0.00022427 | 0.00022348 | 0.0002227 | 0.00022191 | 0.00022113 | 0.00022034 | 0.00021955 | 0.00021877 | 0.00021798 | 0.0002172 | 0.00021641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-163930441 | 8 | 8 | 7.06e-07 | 0 | 1.17e-06 | 0 | 1.08e-06 | 0 | 1.3257e-08 | -4.5e-09 | 1.117e-06 | 1.1302e-06 | 1.1435e-06 | 1.1567e-06 | 1.17e-06 | 1.1655e-06 | 1.161e-06 | 1.1565e-06 | 1.152e-06 | 1.1475e-06 | 1.143e-06 | 1.1385e-06 | 1.134e-06 | 1.1295e-06 | 1.125e-06 | 1.1205e-06 | 1.116e-06 | 1.1115e-06 | 1.107e-06 | 1.1025e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-164206932 | 2088 | 189 | 0.0029732 | 0.00074529 | 0.0038963 | 0.00097803 | 0.0041294 | 0.001035 | 2.6374e-05 | 1.1656e-05 | 0.0037908 | 0.0038172 | 0.0038435 | 0.0038699 | 0.0038963 | 0.0039079 | 0.0039196 | 0.0039312 | 0.0039429 | 0.0039546 | 0.0039662 | 0.0039779 | 0.0039895 | 0.0040012 | 0.0040128 | 0.0040245 | 0.0040361 | 0.0040478 | 0.0040595 | 0.0040711 | 6.6496e-06 | 2.8467e-06 | 0.00095143 | 0.00095808 | 0.00096473 | 0.00097138 | 0.00097803 | 0.00098088 | 0.00098372 | 0.00098657 | 0.00098942 | 0.00099226 | 0.00099511 | 0.00099796 | 0.0010008 | 0.0010036 | 0.0010065 | 0.0010093 | 0.0010122 | 0.001015 | 0.0010179 | 0.0010207
| BAS011-164206954 | 1862 | 276 | 0.0087661 | 0.0053446 | 0.01179 | 0.0074518 | 0.012294 | 0.0078329 | 8.6387e-05 | 2.5238e-05 | 0.011444 | 0.01153 | 0.011617 | 0.011703 | 0.01179 | 0.011815 | 0.01184 | 0.011865 | 0.011891 | 0.011916 | 0.011941 | 0.011966 | 0.011992 | 0.012017 | 0.012042 | 0.012067 | 0.012092 | 0.012118 | 0.012143 | 0.012168 | 6.0206e-05 | 1.9058e-05 | 0.007211 | 0.0072712 | 0.0073314 | 0.0073916 | 0.0074518 | 0.0074708 | 0.0074899 | 0.007509 | 0.007528 | 0.0075471 | 0.0075661 | 0.0075852 | 0.0076042 | 0.0076233 | 0.0076424 | 0.0076614 | 0.0076805 | 0.0076995 | 0.0077186 | 0.0077377
| BAS011-164206976 | 464 | 189 | 0.025629 | 0.0033262 | 0.032988 | 0.0046787 | 0.03374 | 0.004932 | 0.00021026 | 3.7594e-05 | 0.032147 | 0.032358 | 0.032568 | 0.032778 | 0.032988 | 0.033026 | 0.033064 | 0.033101 | 0.033139 | 0.033176 | 0.033214 | 0.033252 | 0.033289 | 0.033327 | 0.033364 | 0.033402 | 0.033439 | 0.033477 | 0.033515 | 0.033552 | 3.8643e-05 | 1.2665e-05 | 0.0045241 | 0.0045627 | 0.0046014 | 0.00464 | 0.0046787 | 0.0046913 | 0.004704 | 0.0047166 | 0.0047293 | 0.004742 | 0.0047546 | 0.0047673 | 0.00478 | 0.0047926 | 0.0048053 | 0.004818 | 0.0048306 | 0.0048433 | 0.004856 | 0.0048686
| BAS011-164287379 | 1436 | 772 | 0.00011698 | 0.00016204 | 0.00017268 | 0.00022331 | 0.00018481 | 0.00023382 | 1.5914e-06 | 6.0665e-07 | 0.00016632 | 0.00016791 | 0.0001695 | 0.00017109 | 0.00017268 | 0.00017329 | 0.00017389 | 0.0001745 | 0.00017511 | 0.00017571 | 0.00017632 | 0.00017693 | 0.00017753 | 0.00017814 | 0.00017875 | 0.00017935 | 0.00017996 | 0.00018057 | 0.00018117 | 0.00018178 | 1.7507e-06 | 5.2545e-07 | 0.00021631 | 0.00021806 | 0.00021981 | 0.00022156 | 0.00022331 | 0.00022384 | 0.00022436 | 0.00022489 | 0.00022541 | 0.00022594 | 0.00022647 | 0.00022699 | 0.00022752 | 0.00022804 | 0.00022857 | 0.00022909 | 0.00022962 | 0.00023014 | 0.00023067 | 0.00023119
| BAS011-172348924 | 68 | 68 | 0.0060198 | 0 | 0.0072781 | 0 | 0.0074427 | 0 | 3.5953e-05 | 8.2273e-06 | 0.0071343 | 0.0071702 | 0.0072062 | 0.0072422 | 0.0072781 | 0.0072863 | 0.0072946 | 0.0073028 | 0.007311 | 0.0073192 | 0.0073275 | 0.0073357 | 0.0073439 | 0.0073522 | 0.0073604 | 0.0073686 | 0.0073768 | 0.0073851 | 0.0073933 | 0.0074015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-182896771 | 26 | 8 | 0.00017622 | 0.00012537 | 0.00025466 | 0.00017706 | 0.00025632 | 0.00017737 | 2.2412e-06 | 8.285e-08 | 0.00024569 | 0.00024794 | 0.00025018 | 0.00025242 | 0.00025466 | 0.00025474 | 0.00025482 | 0.00025491 | 0.00025499 | 0.00025507 | 0.00025516 | 0.00025524 | 0.00025532 | 0.0002554 | 0.00025549 | 0.00025557 | 0.00025565 | 0.00025574 | 0.00025582 | 0.0002559 | 1.4768e-06 | 1.57e-08 | 0.00017115 | 0.00017263 | 0.00017411 | 0.00017558 | 0.00017706 | 0.00017708 | 0.00017709 | 0.00017711 | 0.00017712 | 0.00017714 | 0.00017715 | 0.00017717 | 0.00017719 | 0.0001772 | 0.00017722 | 0.00017723 | 0.00017725 | 0.00017726 | 0.00017728 | 0.0001773
| BAS011-24598608 | 703 | 298 | 0.0033832 | 0.0031217 | 0.0042622 | 0.0039658 | 0.0044711 | 0.0041666 | 2.5114e-05 | 1.0445e-05 | 0.0041617 | 0.0041868 | 0.004212 | 0.0042371 | 0.0042622 | 0.0042726 | 0.0042831 | 0.0042935 | 0.004304 | 0.0043144 | 0.0043249 | 0.0043353 | 0.0043457 | 0.0043562 | 0.0043666 | 0.0043771 | 0.0043875 | 0.004398 | 0.0044084 | 0.0044189 | 2.4118e-05 | 1.004e-05 | 0.0038693 | 0.0038934 | 0.0039175 | 0.0039417 | 0.0039658 | 0.0039758 | 0.0039859 | 0.0039959 | 0.0040059 | 0.004016 | 0.004026 | 0.0040361 | 0.0040461 | 0.0040561 | 0.0040662 | 0.0040762 | 0.0040863 | 0.0040963 | 0.0041063 | 0.0041164
| BAS011-24602396 | 200 | 55 | 3.25e-05 | 0.0011437 | 3.7e-05 | 0.0012613 | 3.64e-05 | 0.0012451 | 1.2857e-07 | -3e-08 | 3.6486e-05 | 3.6614e-05 | 3.6743e-05 | 3.6871e-05 | 3.7e-05 | 3.697e-05 | 3.694e-05 | 3.691e-05 | 3.688e-05 | 3.685e-05 | 3.682e-05 | 3.679e-05 | 3.676e-05 | 3.673e-05 | 3.67e-05 | 3.667e-05 | 3.664e-05 | 3.661e-05 | 3.658e-05 | 3.655e-05 | 3.3617e-06 | -8.0965e-07 | 0.0012479 | 0.0012512 | 0.0012546 | 0.001258 | 0.0012613 | 0.0012605 | 0.0012597 | 0.0012589 | 0.0012581 | 0.0012573 | 0.0012565 | 0.0012556 | 0.0012548 | 0.001254 | 0.0012532 | 0.0012524 | 0.0012516 | 0.0012508 | 0.00125 | 0.0012492
| BAS011-24608723 | 37 | 37 | 0.0003001 | 0 | 0.00037992 | 0 | 0.00041451 | 0 | 2.2806e-06 | 1.7292e-06 | 0.0003708 | 0.00037308 | 0.00037536 | 0.00037764 | 0.00037992 | 0.00038165 | 0.00038338 | 0.00038511 | 0.00038684 | 0.00038857 | 0.0003903 | 0.00039203 | 0.00039376 | 0.00039549 | 0.00039722 | 0.00039895 | 0.00040068 | 0.0004024 | 0.00040413 | 0.00040586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-76148984 | 23 | 23 | 0.00014392 | 0 | 0.00019193 | 0 | 0.00019459 | 0 | 1.3719e-06 | 1.3305e-07 | 0.00018644 | 0.00018782 | 0.00018919 | 0.00019056 | 0.00019193 | 0.00019207 | 0.0001922 | 0.00019233 | 0.00019246 | 0.0001926 | 0.00019273 | 0.00019286 | 0.000193 | 0.00019313 | 0.00019326 | 0.0001934 | 0.00019353 | 0.00019366 | 0.00019379 | 0.00019393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-76149624 | 18 | 18 | 0.00070022 | 0 | 0.00091668 | 0 | 0.00092995 | 0 | 6.1843e-06 | 6.6385e-07 | 0.00089194 | 0.00089812 | 0.00090431 | 0.00091049 | 0.00091668 | 0.00091734 | 0.000918 | 0.00091867 | 0.00091933 | 0.00092 | 0.00092066 | 0.00092132 | 0.00092199 | 0.00092265 | 0.00092331 | 0.00092398 | 0.00092464 | 0.00092531 | 0.00092597 | 0.00092663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-76150176 | 40 | 40 | 0.0011807 | 0 | 0.0016596 | 0 | 0.0016833 | 0 | 1.3684e-05 | 1.1816e-06 | 0.0016049 | 0.0016186 | 0.0016323 | 0.001646 | 0.0016596 | 0.0016608 | 0.001662 | 0.0016632 | 0.0016644 | 0.0016655 | 0.0016667 | 0.0016679 | 0.0016691 | 0.0016703 | 0.0016715 | 0.0016726 | 0.0016738 | 0.001675 | 0.0016762 | 0.0016774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-76150520 | 26 | 26 | 0.0024532 | 0 | 0.0033122 | 0 | 0.0032969 | 0 | 2.4541e-05 | -7.6325e-07 | 0.003214 | 0.0032385 | 0.0032631 | 0.0032876 | 0.0033122 | 0.0033114 | 0.0033106 | 0.0033099 | 0.0033091 | 0.0033084 | 0.0033076 | 0.0033068 | 0.0033061 | 0.0033053 | 0.0033045 | 0.0033038 | 0.003303 | 0.0033022 | 0.0033015 | 0.0033007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-76150666 | 23 | 23 | 0.0050394 | 0 | 0.0068647 | 0 | 0.0070929 | 0 | 5.2151e-05 | 1.1409e-05 | 0.0066561 | 0.0067082 | 0.0067604 | 0.0068125 | 0.0068647 | 0.0068761 | 0.0068875 | 0.0068989 | 0.0069103 | 0.0069217 | 0.0069331 | 0.0069446 | 0.006956 | 0.0069674 | 0.0069788 | 0.0069902 | 0.0070016 | 0.007013 | 0.0070244 | 0.0070358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-79244341 | 27 | 27 | 0.00062809 | 0 | 0.00083113 | 0 | 0.00092061 | 0 | 5.8011e-06 | 4.4743e-06 | 0.00080792 | 0.00081372 | 0.00081952 | 0.00082532 | 0.00083113 | 0.0008356 | 0.00084007 | 0.00084455 | 0.00084902 | 0.0008535 | 0.00085797 | 0.00086245 | 0.00086692 | 0.00087139 | 0.00087587 | 0.00088034 | 0.00088482 | 0.00088929 | 0.00089377 | 0.00089824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-79244394 | 18 | 18 | 0.0026958 | 0 | 0.0036967 | 0 | 0.0039118 | 0 | 2.8596e-05 | 1.0757e-05 | 0.0035823 | 0.0036109 | 0.0036395 | 0.0036681 | 0.0036967 | 0.0037074 | 0.0037182 | 0.0037289 | 0.0037397 | 0.0037505 | 0.0037612 | 0.003772 | 0.0037827 | 0.0037935 | 0.0038042 | 0.003815 | 0.0038258 | 0.0038365 | 0.0038473 | 0.003858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-79244446 | 52 | 52 | 0.013507 | 0 | 0.017509 | 0 | 0.017947 | 0 | 0.00011434 | 2.1914e-05 | 0.017052 | 0.017166 | 0.01728 | 0.017395 | 0.017509 | 0.017531 | 0.017553 | 0.017575 | 0.017597 | 0.017619 | 0.01764 | 0.017662 | 0.017684 | 0.017706 | 0.017728 | 0.01775 | 0.017772 | 0.017794 | 0.017816 | 0.017838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-79244508 | 12 | 12 | 8.53e-05 | 0 | 0.0001181 | 0 | 0.00012494 | 0 | 9.3726e-07 | 3.4185e-07 | 0.00011435 | 0.00011529 | 0.00011623 | 0.00011717 | 0.0001181 | 0.00011845 | 0.00011879 | 0.00011913 | 0.00011947 | 0.00011981 | 0.00012016 | 0.0001205 | 0.00012084 | 0.00012118 | 0.00012152 | 0.00012186 | 0.00012221 | 0.00012255 | 0.00012289 | 0.00012323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-79244589 | 13 | 13 | 0.0017834 | 0 | 0.0026426 | 0 | 0.0026746 | 0 | 2.4548e-05 | 1.6005e-06 | 0.0025444 | 0.002569 | 0.0025935 | 0.0026181 | 0.0026426 | 0.0026442 | 0.0026458 | 0.0026474 | 0.002649 | 0.0026506 | 0.0026522 | 0.0026538 | 0.0026554 | 0.002657 | 0.0026586 | 0.0026602 | 0.0026618 | 0.0026634 | 0.002665 | 0.0026666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-79245218 | 35 | 35 | 5.83e-05 | 0 | 6.35e-05 | 0 | 6.28e-05 | 0 | 1.4857e-07 | -3.5e-08 | 6.2906e-05 | 6.3054e-05 | 6.3203e-05 | 6.3351e-05 | 6.35e-05 | 6.3465e-05 | 6.343e-05 | 6.3395e-05 | 6.336e-05 | 6.3325e-05 | 6.329e-05 | 6.3255e-05 | 6.322e-05 | 6.3185e-05 | 6.315e-05 | 6.3115e-05 | 6.308e-05 | 6.3045e-05 | 6.301e-05 | 6.2975e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-84427318 | 52 | 52 | 0.0006893 | 0 | 0.00096708 | 0 | 0.0010032 | 0 | 7.9366e-06 | 1.8066e-06 | 0.00093533 | 0.00094327 | 0.00095121 | 0.00095914 | 0.00096708 | 0.00096889 | 0.00097069 | 0.0009725 | 0.00097431 | 0.00097611 | 0.00097792 | 0.00097973 | 0.00098153 | 0.00098334 | 0.00098515 | 0.00098695 | 0.00098876 | 0.00099057 | 0.00099237 | 0.00099418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-84621962 | 59 | 59 | 0.010764 | 0 | 0.013015 | 0 | 0.013353 | 0 | 6.4325e-05 | 1.6889e-05 | 0.012758 | 0.012822 | 0.012886 | 0.012951 | 0.013015 | 0.013032 | 0.013049 | 0.013066 | 0.013082 | 0.013099 | 0.013116 | 0.013133 | 0.01315 | 0.013167 | 0.013184 | 0.013201 | 0.013218 | 0.013234 | 0.013251 | 0.013268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-84622282 | 56 | 56 | 0.003157 | 0 | 0.0039756 | 0 | 0.0042435 | 0 | 2.3386e-05 | 1.3395e-05 | 0.003882 | 0.0039054 | 0.0039288 | 0.0039522 | 0.0039756 | 0.0039889 | 0.0040023 | 0.0040157 | 0.0040291 | 0.0040425 | 0.0040559 | 0.0040693 | 0.0040827 | 0.0040961 | 0.0041095 | 0.0041229 | 0.0041363 | 0.0041497 | 0.0041631 | 0.0041765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-84732066 | 27 | 27 | 1.21e-05 | 0 | 1.91e-05 | 0 | 2.08e-05 | 0 | 2e-07 | 8.5e-08 | 1.83e-05 | 1.85e-05 | 1.87e-05 | 1.89e-05 | 1.91e-05 | 1.9185e-05 | 1.927e-05 | 1.9355e-05 | 1.944e-05 | 1.9525e-05 | 1.961e-05 | 1.9695e-05 | 1.978e-05 | 1.9865e-05 | 1.995e-05 | 2.0035e-05 | 2.012e-05 | 2.0205e-05 | 2.029e-05 | 2.0375e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-85028212 | 42 | 42 | 0.0028923 | 0 | 0.0036687 | 0 | 0.003665 | 0 | 2.2183e-05 | -1.832e-07 | 0.00358 | 0.0036021 | 0.0036243 | 0.0036465 | 0.0036687 | 0.0036685 | 0.0036683 | 0.0036681 | 0.003668 | 0.0036678 | 0.0036676 | 0.0036674 | 0.0036672 | 0.003667 | 0.0036669 | 0.0036667 | 0.0036665 | 0.0036663 | 0.0036661 | 0.0036659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-85028323 | 8 | 8 | 1.79e-06 | 0 | 2.36e-06 | 0 | 2.78e-06 | 0 | 1.6286e-08 | 2.1e-08 | 2.2949e-06 | 2.3111e-06 | 2.3274e-06 | 2.3437e-06 | 2.36e-06 | 2.381e-06 | 2.402e-06 | 2.423e-06 | 2.444e-06 | 2.465e-06 | 2.486e-06 | 2.507e-06 | 2.528e-06 | 2.549e-06 | 2.57e-06 | 2.591e-06 | 2.612e-06 | 2.633e-06 | 2.654e-06 | 2.675e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-85029671 | 34 | 34 | 0.00079889 | 0 | 0.0010648 | 0 | 0.0011385 | 0 | 7.5985e-06 | 3.6831e-06 | 0.0010344 | 0.001042 | 0.0010496 | 0.0010572 | 0.0010648 | 0.0010685 | 0.0010722 | 0.0010759 | 0.0010796 | 0.0010833 | 0.0010869 | 0.0010906 | 0.0010943 | 0.001098 | 0.0011017 | 0.0011054 | 0.001109 | 0.0011127 | 0.0011164 | 0.0011201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-85030316 | 33 | 33 | 0.00041543 | 0 | 0.00055685 | 0 | 0.00059026 | 0 | 4.0405e-06 | 1.6706e-06 | 0.00054068 | 0.00054472 | 0.00054877 | 0.00055281 | 0.00055685 | 0.00055852 | 0.00056019 | 0.00056186 | 0.00056353 | 0.0005652 | 0.00056687 | 0.00056854 | 0.00057021 | 0.00057188 | 0.00057355 | 0.00057522 | 0.00057689 | 0.00057856 | 0.00058023 | 0.00058191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-85421065 | 24 | 24 | 0.0029155 | 0 | 0.00363 | 0 | 0.0037059 | 0 | 2.0415e-05 | 3.7972e-06 | 0.0035483 | 0.0035688 | 0.0035892 | 0.0036096 | 0.00363 | 0.0036338 | 0.0036376 | 0.0036414 | 0.0036452 | 0.003649 | 0.0036528 | 0.0036566 | 0.0036604 | 0.0036642 | 0.003668 | 0.0036718 | 0.0036756 | 0.0036794 | 0.0036832 | 0.003687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-85421256 | 20 | 20 | 0.0013935 | 0 | 0.001896 | 0 | 0.0020167 | 0 | 1.4356e-05 | 6.0371e-06 | 0.0018385 | 0.0018529 | 0.0018672 | 0.0018816 | 0.001896 | 0.001902 | 0.001908 | 0.0019141 | 0.0019201 | 0.0019261 | 0.0019322 | 0.0019382 | 0.0019442 | 0.0019503 | 0.0019563 | 0.0019624 | 0.0019684 | 0.0019744 | 0.0019805 | 0.0019865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-85724039 | 57 | 57 | 0.0059937 | 0 | 0.0075262 | 0 | 0.0078638 | 0 | 4.3785e-05 | 1.6881e-05 | 0.0073511 | 0.0073949 | 0.0074386 | 0.0074824 | 0.0075262 | 0.0075431 | 0.00756 | 0.0075769 | 0.0075937 | 0.0076106 | 0.0076275 | 0.0076444 | 0.0076613 | 0.0076781 | 0.007695 | 0.0077119 | 0.0077288 | 0.0077457 | 0.0077625 | 0.0077794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-89021568 | 51 | 51 | 0.0017433 | 0 | 0.0022602 | 0 | 0.0023376 | 0 | 1.4767e-05 | 3.8692e-06 | 0.0022011 | 0.0022159 | 0.0022306 | 0.0022454 | 0.0022602 | 0.002264 | 0.0022679 | 0.0022718 | 0.0022756 | 0.0022795 | 0.0022834 | 0.0022873 | 0.0022911 | 0.002295 | 0.0022989 | 0.0023027 | 0.0023066 | 0.0023105 | 0.0023143 | 0.0023182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-99529198 | 13 | 13 | 0.00046732 | 0 | 0.00068433 | 0 | 0.00075966 | 0 | 6.2002e-06 | 3.7668e-06 | 0.00065953 | 0.00066573 | 0.00067193 | 0.00067813 | 0.00068433 | 0.00068809 | 0.00069186 | 0.00069563 | 0.00069939 | 0.00070316 | 0.00070693 | 0.00071069 | 0.00071446 | 0.00071823 | 0.00072199 | 0.00072576 | 0.00072953 | 0.00073329 | 0.00073706 | 0.00074083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS012-15414133 | 2346 | 1369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS012-187042122 | 977 | 977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS013-15414170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS014-15414207 | 2708 | 1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS014-74639994 | 1483 | 1483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS021-15414366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-130430211 | 48 | 48 | 0.0014233 | 0 | 0.0018444 | 0 | 0.0018905 | 0 | 1.2033e-05 | 2.3031e-06 | 0.0017963 | 0.0018083 | 0.0018203 | 0.0018324 | 0.0018444 | 0.0018467 | 0.001849 | 0.0018513 | 0.0018536 | 0.0018559 | 0.0018582 | 0.0018605 | 0.0018628 | 0.0018651 | 0.0018674 | 0.0018697 | 0.001872 | 0.0018744 | 0.0018767 | 0.001879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-131562724 | 815 | 413 | 0.033881 | 0.010316 | 0.040843 | 0.012823 | 0.044545 | 0.014217 | 0.00019893 | 0.00018507 | 0.040048 | 0.040247 | 0.040446 | 0.040644 | 0.040843 | 0.041028 | 0.041214 | 0.041399 | 0.041584 | 0.041769 | 0.041954 | 0.042139 | 0.042324 | 0.042509 | 0.042694 | 0.042879 | 0.043064 | 0.043249 | 0.043434 | 0.043619 | 7.1644e-05 | 6.9661e-05 | 0.012537 | 0.012609 | 0.01268 | 0.012752 | 0.012823 | 0.012893 | 0.012963 | 0.013032 | 0.013102 | 0.013172 | 0.013241 | 0.013311 | 0.013381 | 0.01345 | 0.01352 | 0.01359 | 0.013659 | 0.013729 | 0.013799 | 0.013868
| BAS022-139345117 | 71 | 71 | 0.0056938 | 0 | 0.0070419 | 0 | 0.0068943 | 0 | 3.8517e-05 | -7.3782e-06 | 0.0068878 | 0.0069263 | 0.0069648 | 0.0070034 | 0.0070419 | 0.0070345 | 0.0070271 | 0.0070197 | 0.0070124 | 0.007005 | 0.0069976 | 0.0069902 | 0.0069828 | 0.0069755 | 0.0069681 | 0.0069607 | 0.0069533 | 0.006946 | 0.0069386 | 0.0069312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-139345255 | 75 | 75 | 0.0050115 | 0 | 0.0052565 | 0 | 0.0050417 | 0 | 7.0017e-06 | -1.0745e-05 | 0.0052285 | 0.0052355 | 0.0052425 | 0.0052495 | 0.0052565 | 0.0052458 | 0.0052351 | 0.0052243 | 0.0052136 | 0.0052028 | 0.0051921 | 0.0051813 | 0.0051706 | 0.0051598 | 0.0051491 | 0.0051384 | 0.0051276 | 0.0051169 | 0.0051061 | 0.0050954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-139345594 | 79 | 79 | 0.0024175 | 0 | 0.0030366 | 0 | 0.0032032 | 0 | 1.7691e-05 | 8.3286e-06 | 0.0029659 | 0.0029836 | 0.0030013 | 0.0030189 | 0.0030366 | 0.003045 | 0.0030533 | 0.0030616 | 0.0030699 | 0.0030783 | 0.0030866 | 0.0030949 | 0.0031033 | 0.0031116 | 0.0031199 | 0.0031282 | 0.0031366 | 0.0031449 | 0.0031532 | 0.0031616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-142437045 | 78 | 78 | 0.013369 | 0 | 0.016444 | 0 | 0.016526 | 0 | 8.7873e-05 | 4.1151e-06 | 0.016093 | 0.01618 | 0.016268 | 0.016356 | 0.016444 | 0.016448 | 0.016452 | 0.016456 | 0.016461 | 0.016465 | 0.016469 | 0.016473 | 0.016477 | 0.016481 | 0.016485 | 0.016489 | 0.016493 | 0.016498 | 0.016502 | 0.016506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-142437276 | 22 | 22 | 0.0012177 | 0 | 0.0015112 | 0 | 0.0015206 | 0 | 8.3861e-06 | 4.688e-07 | 0.0014776 | 0.001486 | 0.0014944 | 0.0015028 | 0.0015112 | 0.0015117 | 0.0015121 | 0.0015126 | 0.0015131 | 0.0015135 | 0.001514 | 0.0015145 | 0.0015149 | 0.0015154 | 0.0015159 | 0.0015163 | 0.0015168 | 0.0015173 | 0.0015178 | 0.0015182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-142437414 | 45 | 45 | 0.0063899 | 0 | 0.0078206 | 0 | 0.0079378 | 0 | 4.0879e-05 | 5.8554e-06 | 0.0076571 | 0.007698 | 0.0077389 | 0.0077798 | 0.0078206 | 0.0078265 | 0.0078324 | 0.0078382 | 0.0078441 | 0.0078499 | 0.0078558 | 0.0078616 | 0.0078675 | 0.0078733 | 0.0078792 | 0.0078851 | 0.0078909 | 0.0078968 | 0.0079026 | 0.0079085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-144337084 | 42 | 42 | 0.0048181 | 0 | 0.0059024 | 0 | 0.0063423 | 0 | 3.098e-05 | 2.1994e-05 | 0.0057785 | 0.0058095 | 0.0058404 | 0.0058714 | 0.0059024 | 0.0059244 | 0.0059464 | 0.0059684 | 0.0059904 | 0.0060124 | 0.0060344 | 0.0060564 | 0.0060784 | 0.0061004 | 0.0061223 | 0.0061443 | 0.0061663 | 0.0061883 | 0.0062103 | 0.0062323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-15416117 | 6237 | 1935 | 0.0054921 | 0.0078013 | 0.0065647 | 0.0094931 | 0.0069784 | 0.010186 | 3.0645e-05 | 2.0686e-05 | 0.0064421 | 0.0064727 | 0.0065034 | 0.006534 | 0.0065647 | 0.0065853 | 0.006606 | 0.0066267 | 0.0066474 | 0.0066681 | 0.0066888 | 0.0067095 | 0.0067301 | 0.0067508 | 0.0067715 | 0.0067922 | 0.0068129 | 0.0068336 | 0.0068543 | 0.006875 | 4.8337e-05 | 3.4655e-05 | 0.0092998 | 0.0093481 | 0.0093964 | 0.0094448 | 0.0094931 | 0.0095278 | 0.0095624 | 0.0095971 | 0.0096317 | 0.0096664 | 0.009701 | 0.0097357 | 0.0097703 | 0.009805 | 0.0098397 | 0.0098743 | 0.009909 | 0.0099436 | 0.0099783 | 0.010013
| BAS022-155392787 | 39 | 39 | 0.0038925 | 0 | 0.0044099 | 0 | 0.0046141 | 0 | 1.4781e-05 | 1.0212e-05 | 0.0043508 | 0.0043655 | 0.0043803 | 0.0043951 | 0.0044099 | 0.0044201 | 0.0044303 | 0.0044405 | 0.0044507 | 0.0044609 | 0.0044712 | 0.0044814 | 0.0044916 | 0.0045018 | 0.004512 | 0.0045222 | 0.0045324 | 0.0045426 | 0.0045528 | 0.0045631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-155392904 | 22 | 22 | 0.0015382 | 0 | 0.0019507 | 0 | 0.0020725 | 0 | 1.1784e-05 | 6.0894e-06 | 0.0019035 | 0.0019153 | 0.0019271 | 0.0019389 | 0.0019507 | 0.0019568 | 0.0019629 | 0.001969 | 0.001975 | 0.0019811 | 0.0019872 | 0.0019933 | 0.0019994 | 0.0020055 | 0.0020116 | 0.0020177 | 0.0020238 | 0.0020298 | 0.0020359 | 0.002042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-155393076 | 48 | 48 | 0.0024097 | 0 | 0.0032027 | 0 | 0.0033982 | 0 | 2.2658e-05 | 9.7745e-06 | 0.0031121 | 0.0031348 | 0.0031574 | 0.0031801 | 0.0032027 | 0.0032125 | 0.0032223 | 0.0032321 | 0.0032418 | 0.0032516 | 0.0032614 | 0.0032712 | 0.0032809 | 0.0032907 | 0.0033005 | 0.0033103 | 0.00332 | 0.0033298 | 0.0033396 | 0.0033494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-163916141 | 25 | 25 | 0.0072231 | 0 | 0.0091093 | 0 | 0.009581 | 0 | 5.3891e-05 | 2.3585e-05 | 0.0088938 | 0.0089476 | 0.0090015 | 0.0090554 | 0.0091093 | 0.0091329 | 0.0091565 | 0.0091801 | 0.0092037 | 0.0092272 | 0.0092508 | 0.0092744 | 0.009298 | 0.0093216 | 0.0093452 | 0.0093688 | 0.0093923 | 0.0094159 | 0.0094395 | 0.0094631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-164206998 | 671 | 598 | 0.025491 | 0.0080564 | 0.029762 | 0.0097081 | 0.030772 | 0.010147 | 0.00012203 | 5.048e-05 | 0.029274 | 0.029396 | 0.029518 | 0.02964 | 0.029762 | 0.029813 | 0.029863 | 0.029913 | 0.029964 | 0.030014 | 0.030065 | 0.030115 | 0.030166 | 0.030216 | 0.030267 | 0.030317 | 0.030368 | 0.030418 | 0.030469 | 0.030519 | 4.7191e-05 | 2.1956e-05 | 0.0095194 | 0.0095666 | 0.0096138 | 0.0096609 | 0.0097081 | 0.0097301 | 0.0097521 | 0.009774 | 0.009796 | 0.0098179 | 0.0098399 | 0.0098618 | 0.0098838 | 0.0099057 | 0.0099277 | 0.0099497 | 0.0099716 | 0.0099936 | 0.010016 | 0.010037
| BAS022-171331284 | 31 | 31 | 0.010679 | 0 | 0.012844 | 0 | 0.013462 | 0 | 6.1862e-05 | 3.0853e-05 | 0.012597 | 0.012659 | 0.012721 | 0.012783 | 0.012844 | 0.012875 | 0.012906 | 0.012937 | 0.012968 | 0.012999 | 0.01303 | 0.01306 | 0.013091 | 0.013122 | 0.013153 | 0.013184 | 0.013215 | 0.013246 | 0.013276 | 0.013307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-172349144 | 3 | 3 | 3.13e-05 | 0 | 3.89e-05 | 0 | 4.3e-05 | 0 | 2.1714e-07 | 2.05e-07 | 3.8031e-05 | 3.8249e-05 | 3.8466e-05 | 3.8683e-05 | 3.89e-05 | 3.9105e-05 | 3.931e-05 | 3.9515e-05 | 3.972e-05 | 3.9925e-05 | 4.013e-05 | 4.0335e-05 | 4.054e-05 | 4.0745e-05 | 4.095e-05 | 4.1155e-05 | 4.136e-05 | 4.1565e-05 | 4.177e-05 | 4.1975e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-193385657 | 715 | 715 | 0.011238 | 0 | 0.012616 | 0 | 0.012859 | 0 | 3.9393e-05 | 1.2126e-05 | 0.012459 | 0.012498 | 0.012538 | 0.012577 | 0.012616 | 0.012628 | 0.012641 | 0.012653 | 0.012665 | 0.012677 | 0.012689 | 0.012701 | 0.012713 | 0.012725 | 0.012738 | 0.01275 | 0.012762 | 0.012774 | 0.012786 | 0.012798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-193385775 | 3628 | 1520 | 0.049809 | 0.021422 | 0.059121 | 0.026602 | 0.061234 | 0.027898 | 0.00026607 | 0.00010563 | 0.058057 | 0.058323 | 0.058589 | 0.058855 | 0.059121 | 0.059227 | 0.059332 | 0.059438 | 0.059544 | 0.059649 | 0.059755 | 0.059861 | 0.059966 | 0.060072 | 0.060177 | 0.060283 | 0.060389 | 0.060494 | 0.0606 | 0.060706 | 0.00014799 | 6.4791e-05 | 0.02601 | 0.026158 | 0.026306 | 0.026454 | 0.026602 | 0.026667 | 0.026731 | 0.026796 | 0.026861 | 0.026926 | 0.026991 | 0.027055 | 0.02712 | 0.027185 | 0.02725 | 0.027315 | 0.027379 | 0.027444 | 0.027509 | 0.027574
| BAS022-24598930 | 578 | 282 | 0.013419 | 0.0033276 | 0.01634 | 0.0041606 | 0.017181 | 0.0043725 | 8.3455e-05 | 4.2072e-05 | 0.016006 | 0.016089 | 0.016173 | 0.016256 | 0.01634 | 0.016382 | 0.016424 | 0.016466 | 0.016508 | 0.01655 | 0.016592 | 0.016634 | 0.016676 | 0.016718 | 0.016761 | 0.016803 | 0.016845 | 0.016887 | 0.016929 | 0.016971 | 2.3802e-05 | 1.0594e-05 | 0.0040654 | 0.0040892 | 0.004113 | 0.0041368 | 0.0041606 | 0.0041712 | 0.0041818 | 0.0041924 | 0.004203 | 0.0042136 | 0.0042242 | 0.0042348 | 0.0042454 | 0.004256 | 0.0042666 | 0.0042772 | 0.0042878 | 0.0042984 | 0.0043089 | 0.0043195
| BAS022-72697775 | 13 | 13 | 0.0017537 | 0 | 0.00221 | 0 | 0.0022772 | 0 | 1.3037e-05 | 3.361e-06 | 0.0021578 | 0.0021709 | 0.0021839 | 0.002197 | 0.00221 | 0.0022134 | 0.0022167 | 0.0022201 | 0.0022234 | 0.0022268 | 0.0022302 | 0.0022335 | 0.0022369 | 0.0022402 | 0.0022436 | 0.002247 | 0.0022503 | 0.0022537 | 0.0022571 | 0.0022604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-72698236 | 25 | 25 | 0.0020373 | 0 | 0.0025598 | 0 | 0.0027278 | 0 | 1.4928e-05 | 8.4041e-06 | 0.0025 | 0.002515 | 0.0025299 | 0.0025448 | 0.0025598 | 0.0025682 | 0.0025766 | 0.002585 | 0.0025934 | 0.0026018 | 0.0026102 | 0.0026186 | 0.002627 | 0.0026354 | 0.0026438 | 0.0026522 | 0.0026606 | 0.002669 | 0.0026774 | 0.0026858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-72698508 | 18 | 18 | 0.0016446 | 0 | 0.0019898 | 0 | 0.0020809 | 0 | 9.8621e-06 | 4.5542e-06 | 0.0019503 | 0.0019602 | 0.0019701 | 0.0019799 | 0.0019898 | 0.0019943 | 0.0019989 | 0.0020034 | 0.002008 | 0.0020125 | 0.0020171 | 0.0020217 | 0.0020262 | 0.0020308 | 0.0020353 | 0.0020399 | 0.0020444 | 0.002049 | 0.0020535 | 0.0020581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-88324187 | 44 | 44 | 0.0050156 | 0 | 0.0061843 | 0 | 0.0065891 | 0 | 3.3392e-05 | 2.0242e-05 | 0.0060507 | 0.0060841 | 0.0061175 | 0.0061509 | 0.0061843 | 0.0062046 | 0.0062248 | 0.006245 | 0.0062653 | 0.0062855 | 0.0063058 | 0.006326 | 0.0063462 | 0.0063665 | 0.0063867 | 0.006407 | 0.0064272 | 0.0064475 | 0.0064677 | 0.0064879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-88324452 | 46 | 46 | 0.004944 | 0 | 0.0062773 | 0 | 0.0065353 | 0 | 3.8094e-05 | 1.29e-05 | 0.0061249 | 0.006163 | 0.0062011 | 0.0062392 | 0.0062773 | 0.0062902 | 0.0063031 | 0.006316 | 0.0063289 | 0.0063418 | 0.0063547 | 0.0063676 | 0.0063805 | 0.0063934 | 0.0064063 | 0.0064192 | 0.0064321 | 0.006445 | 0.0064579 | 0.0064708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS023-141849160 | 30 | 30 | 0.0091968 | 0 | 0.011278 | 0 | 0.01171 | 0 | 5.9466e-05 | 2.1579e-05 | 0.01104 | 0.0111 | 0.011159 | 0.011219 | 0.011278 | 0.0113 | 0.011321 | 0.011343 | 0.011364 | 0.011386 | 0.011408 | 0.011429 | 0.011451 | 0.011472 | 0.011494 | 0.011515 | 0.011537 | 0.011559 | 0.01158 | 0.011602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS023-141849179 | 19 | 19 | 0.0016964 | 0 | 0.0022189 | 0 | 0.0024218 | 0 | 1.4929e-05 | 1.0141e-05 | 0.0021592 | 0.0021741 | 0.0021891 | 0.002204 | 0.0022189 | 0.0022291 | 0.0022392 | 0.0022494 | 0.0022595 | 0.0022696 | 0.0022798 | 0.0022899 | 0.0023001 | 0.0023102 | 0.0023203 | 0.0023305 | 0.0023406 | 0.0023508 | 0.0023609 | 0.002371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS023-15416141 | 4514 | 1770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS023-155325011 | 45 | 45 | 0.0076156 | 0 | 0.0095159 | 0 | 0.0099265 | 0 | 5.4294e-05 | 2.0527e-05 | 0.0092987 | 0.009353 | 0.0094073 | 0.0094616 | 0.0095159 | 0.0095364 | 0.009557 | 0.0095775 | 0.009598 | 0.0096186 | 0.0096391 | 0.0096596 | 0.0096801 | 0.0097007 | 0.0097212 | 0.0097417 | 0.0097622 | 0.0097828 | 0.0098033 | 0.0098238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS023-24612761 | 2744 | 2219 | 0.024783 | 0.0018887 | 0.028967 | 0.0024095 | 0.0296 | 0.002705 | 0.00011953 | 3.1637e-05 | 0.028489 | 0.028608 | 0.028728 | 0.028847 | 0.028967 | 0.028999 | 0.02903 | 0.029062 | 0.029094 | 0.029125 | 0.029157 | 0.029188 | 0.02922 | 0.029252 | 0.029283 | 0.029315 | 0.029347 | 0.029378 | 0.02941 | 0.029442 | 1.4882e-05 | 1.4776e-05 | 0.00235 | 0.0023649 | 0.0023798 | 0.0023946 | 0.0024095 | 0.0024243 | 0.0024391 | 0.0024539 | 0.0024686 | 0.0024834 | 0.0024982 | 0.002513 | 0.0025277 | 0.0025425 | 0.0025573 | 0.0025721 | 0.0025868 | 0.0026016 | 0.0026164 | 0.0026312
| BAS023-41628847 | 525 | 431 | 0.0098767 | 0.007656 | 0.01248 | 0.0097648 | 0.013347 | 0.010307 | 7.4391e-05 | 4.3311e-05 | 0.012183 | 0.012257 | 0.012332 | 0.012406 | 0.01248 | 0.012524 | 0.012567 | 0.01261 | 0.012654 | 0.012697 | 0.01274 | 0.012784 | 0.012827 | 0.01287 | 0.012913 | 0.012957 | 0.013 | 0.013043 | 0.013087 | 0.01313 | 6.0251e-05 | 2.7097e-05 | 0.0095238 | 0.0095841 | 0.0096443 | 0.0097046 | 0.0097648 | 0.0097919 | 0.009819 | 0.0098461 | 0.0098732 | 0.0099003 | 0.0099274 | 0.0099545 | 0.0099816 | 0.010009 | 0.010036 | 0.010063 | 0.01009 | 0.010117 | 0.010144 | 0.010171
| BAS024-15416191 | 5306 | 5306 | 0.00027023 | 0 | 0.00035501 | 0 | 0.0003948 | 0 | 2.4223e-06 | 1.9895e-06 | 0.00034532 | 0.00034774 | 0.00035016 | 0.00035259 | 0.00035501 | 0.000357 | 0.00035899 | 0.00036098 | 0.00036297 | 0.00036496 | 0.00036695 | 0.00036894 | 0.00037092 | 0.00037291 | 0.0003749 | 0.00037689 | 0.00037888 | 0.00038087 | 0.00038286 | 0.00038485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS032-155216556 | 2452 | 2452 | 0.043218 | 0 | 0.049005 | 0 | 0.050068 | 0 | 0.00016536 | 5.3139e-05 | 0.048344 | 0.048509 | 0.048675 | 0.04884 | 0.049005 | 0.049059 | 0.049112 | 0.049165 | 0.049218 | 0.049271 | 0.049324 | 0.049377 | 0.04943 | 0.049484 | 0.049537 | 0.04959 | 0.049643 | 0.049696 | 0.049749 | 0.049802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS032-177751012 | 4743 | 2291 | 0.010333 | 0.00081112 | 0.011445 | 0.0010363 | 0.011707 | 0.0011399 | 3.1768e-05 | 1.312e-05 | 0.011318 | 0.011349 | 0.011381 | 0.011413 | 0.011445 | 0.011458 | 0.011471 | 0.011484 | 0.011497 | 0.01151 | 0.011523 | 0.011537 | 0.01155 | 0.011563 | 0.011576 | 0.011589 | 0.011602 | 0.011615 | 0.011628 | 0.011642 | 6.4348e-06 | 5.1781e-06 | 0.0010106 | 0.001017 | 0.0010235 | 0.0010299 | 0.0010363 | 0.0010415 | 0.0010467 | 0.0010519 | 0.001057 | 0.0010622 | 0.0010674 | 0.0010726 | 0.0010778 | 0.0010829 | 0.0010881 | 0.0010933 | 0.0010985 | 0.0011036 | 0.0011088 | 0.001114
| BAS033-139662053 | 72 | 72 | 0.011743 | 0 | 0.015455 | 0 | 0.014815 | 0 | 0.00010607 | -3.1999e-05 | 0.015031 | 0.015137 | 0.015243 | 0.015349 | 0.015455 | 0.015423 | 0.015391 | 0.015359 | 0.015327 | 0.015295 | 0.015263 | 0.015231 | 0.015199 | 0.015167 | 0.015135 | 0.015103 | 0.015071 | 0.015039 | 0.015007 | 0.014975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-139662229 | 55 | 55 | 0.023414 | 0 | 0.030155 | 0 | 0.030262 | 0 | 0.0001926 | 5.3558e-06 | 0.029385 | 0.029577 | 0.02977 | 0.029962 | 0.030155 | 0.03016 | 0.030166 | 0.030171 | 0.030176 | 0.030182 | 0.030187 | 0.030192 | 0.030198 | 0.030203 | 0.030209 | 0.030214 | 0.030219 | 0.030225 | 0.03023 | 0.030235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-140150122 | 29 | 29 | 0.0026344 | 0 | 0.0035406 | 0 | 0.0033903 | 0 | 2.5892e-05 | -7.5169e-06 | 0.0034371 | 0.003463 | 0.0034889 | 0.0035148 | 0.0035406 | 0.0035331 | 0.0035256 | 0.0035181 | 0.0035106 | 0.0035031 | 0.0034955 | 0.003488 | 0.0034805 | 0.003473 | 0.0034655 | 0.003458 | 0.0034504 | 0.0034429 | 0.0034354 | 0.0034279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-142953276 | 56 | 56 | 0.010719 | 0 | 0.012571 | 0 | 0.013593 | 0 | 5.2933e-05 | 5.1091e-05 | 0.01236 | 0.012412 | 0.012465 | 0.012518 | 0.012571 | 0.012622 | 0.012673 | 0.012725 | 0.012776 | 0.012827 | 0.012878 | 0.012929 | 0.01298 | 0.013031 | 0.013082 | 0.013133 | 0.013184 | 0.013235 | 0.013287 | 0.013338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-155164312 | 36 | 36 | 4.36e-05 | 0 | 6.32e-05 | 0 | 6.24e-05 | 0 | 5.6e-07 | -4e-08 | 6.096e-05 | 6.152e-05 | 6.208e-05 | 6.264e-05 | 6.32e-05 | 6.316e-05 | 6.312e-05 | 6.308e-05 | 6.304e-05 | 6.3e-05 | 6.296e-05 | 6.292e-05 | 6.288e-05 | 6.284e-05 | 6.28e-05 | 6.276e-05 | 6.272e-05 | 6.268e-05 | 6.264e-05 | 6.26e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-155176923 | 59 | 59 | 0.0097966 | 0 | 0.013034 | 0 | 0.012571 | 0 | 9.251e-05 | -2.3196e-05 | 0.012664 | 0.012757 | 0.012849 | 0.012942 | 0.013034 | 0.013011 | 0.012988 | 0.012965 | 0.012942 | 0.012918 | 0.012895 | 0.012872 | 0.012849 | 0.012826 | 0.012802 | 0.012779 | 0.012756 | 0.012733 | 0.01271 | 0.012686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-155190238 | 41 | 41 | 0.0013533 | 0 | 0.0017926 | 0 | 0.0016153 | 0 | 1.2554e-05 | -8.8647e-06 | 0.0017424 | 0.001755 | 0.0017675 | 0.0017801 | 0.0017926 | 0.0017838 | 0.0017749 | 0.001766 | 0.0017572 | 0.0017483 | 0.0017394 | 0.0017306 | 0.0017217 | 0.0017129 | 0.001704 | 0.0016951 | 0.0016863 | 0.0016774 | 0.0016685 | 0.0016597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-155190444 | 20 | 20 | 0.00039757 | 0 | 0.00056596 | 0 | 0.00055636 | 0 | 4.8112e-06 | -4.801e-07 | 0.00054672 | 0.00055153 | 0.00055634 | 0.00056115 | 0.00056596 | 0.00056548 | 0.000565 | 0.00056452 | 0.00056404 | 0.00056356 | 0.00056308 | 0.0005626 | 0.00056212 | 0.00056164 | 0.00056116 | 0.00056068 | 0.0005602 | 0.00055972 | 0.00055924 | 0.00055876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-155190566 | 15 | 15 | 0.001014 | 0 | 0.00148 | 0 | 0.0014015 | 0 | 1.3314e-05 | -3.9242e-06 | 0.0014268 | 0.0014401 | 0.0014534 | 0.0014667 | 0.00148 | 0.0014761 | 0.0014722 | 0.0014683 | 0.0014643 | 0.0014604 | 0.0014565 | 0.0014526 | 0.0014486 | 0.0014447 | 0.0014408 | 0.0014369 | 0.0014329 | 0.001429 | 0.0014251 | 0.0014212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-155190689 | 10 | 10 | 0.00012258 | 0 | 0.00016959 | 0 | 0.00016572 | 0 | 1.3431e-06 | -1.932e-07 | 0.00016421 | 0.00016556 | 0.0001669 | 0.00016824 | 0.00016959 | 0.00016939 | 0.0001692 | 0.00016901 | 0.00016881 | 0.00016862 | 0.00016843 | 0.00016823 | 0.00016804 | 0.00016785 | 0.00016765 | 0.00016746 | 0.00016727 | 0.00016707 | 0.00016688 | 0.00016669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-155190801 | 6 | 6 | 2.09e-05 | 0 | 3.09e-05 | 0 | 2.96e-05 | 0 | 2.8571e-07 | -6.5e-08 | 2.9757e-05 | 3.0043e-05 | 3.0329e-05 | 3.0614e-05 | 3.09e-05 | 3.0835e-05 | 3.077e-05 | 3.0705e-05 | 3.064e-05 | 3.0575e-05 | 3.051e-05 | 3.0445e-05 | 3.038e-05 | 3.0315e-05 | 3.025e-05 | 3.0185e-05 | 3.012e-05 | 3.0055e-05 | 2.999e-05 | 2.9925e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-155250207 | 35 | 35 | 0.0011512 | 0 | 0.0016042 | 0 | 0.001537 | 0 | 1.2943e-05 | -3.3591e-06 | 0.0015524 | 0.0015653 | 0.0015783 | 0.0015912 | 0.0016042 | 0.0016008 | 0.0015974 | 0.0015941 | 0.0015907 | 0.0015874 | 0.001584 | 0.0015806 | 0.0015773 | 0.0015739 | 0.0015706 | 0.0015672 | 0.0015638 | 0.0015605 | 0.0015571 | 0.0015538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-155250324 | 6 | 6 | 4.85e-06 | 0 | 7.38e-06 | 0 | 7.31e-06 | 0 | 7.2286e-08 | -3.5e-09 | 7.0909e-06 | 7.1631e-06 | 7.2354e-06 | 7.3077e-06 | 7.38e-06 | 7.3765e-06 | 7.373e-06 | 7.3695e-06 | 7.366e-06 | 7.3625e-06 | 7.359e-06 | 7.3555e-06 | 7.352e-06 | 7.3485e-06 | 7.345e-06 | 7.3415e-06 | 7.338e-06 | 7.3345e-06 | 7.331e-06 | 7.3275e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-177750890 | 6639 | 2952 | 0.0027696 | 0.0053459 | 0.0032603 | 0.006376 | 0.0033744 | 0.0066251 | 1.4019e-05 | 5.7068e-06 | 0.0032042 | 0.0032182 | 0.0032322 | 0.0032462 | 0.0032603 | 0.003266 | 0.0032717 | 0.0032774 | 0.0032831 | 0.0032888 | 0.0032945 | 0.0033002 | 0.0033059 | 0.0033116 | 0.0033173 | 0.003323 | 0.0033287 | 0.0033345 | 0.0033402 | 0.0033459 | 2.943e-05 | 1.2457e-05 | 0.0062582 | 0.0062877 | 0.0063171 | 0.0063465 | 0.006376 | 0.0063884 | 0.0064009 | 0.0064133 | 0.0064258 | 0.0064383 | 0.0064507 | 0.0064632 | 0.0064756 | 0.0064881 | 0.0065005 | 0.006513 | 0.0065255 | 0.0065379 | 0.0065504 | 0.0065628
| BAS033-193428051 | 2317 | 1333 | 0.11461 | 0.012233 | 0.13691 | 0.016153 | 0.13956 | 0.016996 | 0.00063709 | 0.00013242 | 0.13436 | 0.135 | 0.13564 | 0.13627 | 0.13691 | 0.13704 | 0.13718 | 0.13731 | 0.13744 | 0.13757 | 0.13771 | 0.13784 | 0.13797 | 0.1381 | 0.13823 | 0.13837 | 0.1385 | 0.13863 | 0.13876 | 0.1389 | 0.00011199 | 4.2166e-05 | 0.015705 | 0.015817 | 0.015929 | 0.016041 | 0.016153 | 0.016195 | 0.016237 | 0.016279 | 0.016322 | 0.016364 | 0.016406 | 0.016448 | 0.01649 | 0.016532 | 0.016575 | 0.016617 | 0.016659 | 0.016701 | 0.016743 | 0.016785
| BAS033-193428083 | 378 | 79 | 0.0048087 | 0.0035093 | 0.0063661 | 0.0048213 | 0.0059689 | 0.0044833 | 4.4499e-05 | -1.9862e-05 | 0.0061881 | 0.0062326 | 0.0062771 | 0.0063216 | 0.0063661 | 0.0063463 | 0.0063264 | 0.0063066 | 0.0062867 | 0.0062668 | 0.006247 | 0.0062271 | 0.0062072 | 0.0061874 | 0.0061675 | 0.0061477 | 0.0061278 | 0.0061079 | 0.0060881 | 0.0060682 | 3.7486e-05 | -1.6895e-05 | 0.0046713 | 0.0047088 | 0.0047463 | 0.0047838 | 0.0048213 | 0.0048044 | 0.0047875 | 0.0047706 | 0.0047537 | 0.0047368 | 0.0047199 | 0.004703 | 0.0046861 | 0.0046692 | 0.0046523 | 0.0046354 | 0.0046185 | 0.0046016 | 0.0045847 | 0.0045678
| BAS033-193428108 | 479 | 454 | 0.0086449 | 0.00045648 | 0.011961 | 0.00061216 | 0.011733 | 0.00059605 | 9.4748e-05 | -1.1389e-05 | 0.011582 | 0.011677 | 0.011772 | 0.011866 | 0.011961 | 0.01195 | 0.011938 | 0.011927 | 0.011916 | 0.011904 | 0.011893 | 0.011881 | 0.01187 | 0.011859 | 0.011847 | 0.011836 | 0.011824 | 0.011813 | 0.011802 | 0.01179 | 4.448e-06 | -8.059e-07 | 0.00059437 | 0.00059882 | 0.00060327 | 0.00060771 | 0.00061216 | 0.00061136 | 0.00061055 | 0.00060975 | 0.00060894 | 0.00060813 | 0.00060733 | 0.00060652 | 0.00060572 | 0.00060491 | 0.0006041 | 0.0006033 | 0.00060249 | 0.00060169 | 0.00060088 | 0.00060007
| BAS033-193428622 | 3673 | 1183 | 0.039607 | 0.018389 | 0.04753 | 0.022375 | 0.049132 | 0.023316 | 0.00022636 | 8.01e-05 | 0.046625 | 0.046851 | 0.047077 | 0.047304 | 0.04753 | 0.04761 | 0.04769 | 0.04777 | 0.04785 | 0.04793 | 0.048011 | 0.048091 | 0.048171 | 0.048251 | 0.048331 | 0.048411 | 0.048491 | 0.048571 | 0.048651 | 0.048731 | 0.00011388 | 4.7084e-05 | 0.021919 | 0.022033 | 0.022147 | 0.022261 | 0.022375 | 0.022422 | 0.022469 | 0.022516 | 0.022563 | 0.02261 | 0.022657 | 0.022704 | 0.022751 | 0.022798 | 0.022845 | 0.022893 | 0.02294 | 0.022987 | 0.023034 | 0.023081
| BAS033-78747898 | 14 | 14 | 5.45e-05 | 0 | 6.79e-05 | 0 | 7.51e-05 | 0 | 3.8286e-07 | 3.6e-07 | 6.6369e-05 | 6.6751e-05 | 6.7134e-05 | 6.7517e-05 | 6.79e-05 | 6.826e-05 | 6.862e-05 | 6.898e-05 | 6.934e-05 | 6.97e-05 | 7.006e-05 | 7.042e-05 | 7.078e-05 | 7.114e-05 | 7.15e-05 | 7.186e-05 | 7.222e-05 | 7.258e-05 | 7.294e-05 | 7.33e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-78747960 | 6 | 6 | 0.00043304 | 0 | 0.00052466 | 0 | 0.00055981 | 0 | 2.6177e-06 | 1.7574e-06 | 0.00051419 | 0.00051681 | 0.00051942 | 0.00052204 | 0.00052466 | 0.00052642 | 0.00052817 | 0.00052993 | 0.00053169 | 0.00053345 | 0.0005352 | 0.00053696 | 0.00053872 | 0.00054048 | 0.00054223 | 0.00054399 | 0.00054575 | 0.00054751 | 0.00054926 | 0.00055102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-78748025 | 83 | 83 | 0.014987 | 0 | 0.017503 | 0 | 0.018082 | 0 | 7.1907e-05 | 2.8952e-05 | 0.017216 | 0.017288 | 0.01736 | 0.017432 | 0.017503 | 0.017532 | 0.017561 | 0.01759 | 0.017619 | 0.017648 | 0.017677 | 0.017706 | 0.017735 | 0.017764 | 0.017793 | 0.017822 | 0.017851 | 0.01788 | 0.017909 | 0.017938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-78748089 | 28 | 28 | 0.0049736 | 0 | 0.006009 | 0 | 0.0063059 | 0 | 2.9582e-05 | 1.4847e-05 | 0.0058907 | 0.0059202 | 0.0059498 | 0.0059794 | 0.006009 | 0.0060238 | 0.0060387 | 0.0060535 | 0.0060684 | 0.0060832 | 0.0060981 | 0.0061129 | 0.0061278 | 0.0061426 | 0.0061575 | 0.0061723 | 0.0061871 | 0.006202 | 0.0062168 | 0.0062317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-95730010 | 5 | 5 | 0.0011074 | 0 | 0.0014704 | 0 | 0.0013718 | 0 | 1.0372e-05 | -4.9284e-06 | 0.0014289 | 0.0014393 | 0.0014497 | 0.00146 | 0.0014704 | 0.0014655 | 0.0014605 | 0.0014556 | 0.0014507 | 0.0014458 | 0.0014408 | 0.0014359 | 0.001431 | 0.001426 | 0.0014211 | 0.0014162 | 0.0014113 | 0.0014063 | 0.0014014 | 0.0013965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS033-96330036 | 62 | 62 | 0.0041757 | 0 | 0.005729 | 0 | 0.0054843 | 0 | 4.4381e-05 | -1.2234e-05 | 0.0055515 | 0.0055959 | 0.0056403 | 0.0056846 | 0.005729 | 0.0057168 | 0.0057046 | 0.0056923 | 0.0056801 | 0.0056679 | 0.0056556 | 0.0056434 | 0.0056312 | 0.0056189 | 0.0056067 | 0.0055945 | 0.0055822 | 0.00557 | 0.0055577 | 0.0055455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS034-15416250 | 5438 | 5438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS034-199849971 | 0 | 0 | 0.0069547 | 0 | 0.0080846 | 0 | 0.0083134 | 0 | 3.2286e-05 | 1.144e-05 | 0.0079555 | 0.0079878 | 0.0080201 | 0.0080524 | 0.0080846 | 0.0080961 | 0.0081075 | 0.008119 | 0.0081304 | 0.0081418 | 0.0081533 | 0.0081647 | 0.0081762 | 0.0081876 | 0.008199 | 0.0082105 | 0.0082219 | 0.0082334 | 0.0082448 | 0.0082562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BBD013-15437974 | 145 | 56 | 0.0082331 | 0.0013224 | 0.011969 | 0.0019371 | 0.011648 | 0.0018887 | 0.00010673 | -1.6043e-05 | 0.011542 | 0.011648 | 0.011755 | 0.011862 | 0.011969 | 0.011953 | 0.011937 | 0.011921 | 0.011904 | 0.011888 | 0.011872 | 0.011856 | 0.01184 | 0.011824 | 0.011808 | 0.011792 | 0.011776 | 0.01176 | 0.011744 | 0.011728 | 1.7563e-05 | -2.4188e-06 | 0.0018668 | 0.0018844 | 0.001902 | 0.0019195 | 0.0019371 | 0.0019347 | 0.0019322 | 0.0019298 | 0.0019274 | 0.001925 | 0.0019226 | 0.0019202 | 0.0019177 | 0.0019153 | 0.0019129 | 0.0019105 | 0.0019081 | 0.0019056 | 0.0019032 | 0.0019008
| BBD013-24614080 | 89 | 89 | 0.0054939 | 0 | 0.0074496 | 0 | 0.0074218 | 0 | 5.5877e-05 | -1.3893e-06 | 0.0072261 | 0.007282 | 0.0073379 | 0.0073938 | 0.0074496 | 0.0074482 | 0.0074469 | 0.0074455 | 0.0074441 | 0.0074427 | 0.0074413 | 0.0074399 | 0.0074385 | 0.0074371 | 0.0074357 | 0.0074344 | 0.007433 | 0.0074316 | 0.0074302 | 0.0074288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BBD014-15437952 | 124 | 16 | 0.00076216 | 6.81e-05 | 0.0011313 | 0.00010101 | 0.0011039 | 9.86e-05 | 1.0546e-05 | -1.3671e-06 | 0.0010891 | 0.0010996 | 0.0011102 | 0.0011207 | 0.0011313 | 0.0011299 | 0.0011285 | 0.0011272 | 0.0011258 | 0.0011244 | 0.0011231 | 0.0011217 | 0.0011203 | 0.001119 | 0.0011176 | 0.0011162 | 0.0011149 | 0.0011135 | 0.0011121 | 0.0011108 | 9.4031e-07 | -1.2055e-07 | 9.725e-05 | 9.819e-05 | 9.913e-05 | 0.00010007 | 0.00010101 | 0.00010089 | 0.00010077 | 0.00010065 | 0.00010053 | 0.00010041 | 0.00010029 | 0.00010017 | 0.00010005 | 9.9926e-05 | 9.9805e-05 | 9.9685e-05 | 9.9564e-05 | 9.9444e-05 | 9.9323e-05 | 9.9203e-05
| BBD014-160682204 | 10 | 10 | 0.00013978 | 0 | 0.00014103 | 0 | 0.00014047 | 0 | 3.5914e-08 | -2.82e-08 | 0.00014089 | 0.00014093 | 0.00014096 | 0.000141 | 0.00014103 | 0.00014101 | 0.00014098 | 0.00014095 | 0.00014092 | 0.00014089 | 0.00014086 | 0.00014084 | 0.00014081 | 0.00014078 | 0.00014075 | 0.00014072 | 0.0001407 | 0.00014067 | 0.00014064 | 0.00014061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BBD014-162435599 | 0 | 0 | 0.0011229 | 0 | 0.0015965 | 0 | 0.0016408 | 0 | 1.3532e-05 | 2.2153e-06 | 0.0015424 | 0.0015559 | 0.0015694 | 0.001583 | 0.0015965 | 0.0015987 | 0.0016009 | 0.0016031 | 0.0016054 | 0.0016076 | 0.0016098 | 0.001612 | 0.0016142 | 0.0016164 | 0.0016187 | 0.0016209 | 0.0016231 | 0.0016253 | 0.0016275 | 0.0016297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BBD014-96325732 | 108 | 8 | 0.0015237 | 2.55e-05 | 0.0023753 | 4.02e-05 | 0.0021894 | 3.7e-05 | 2.433e-05 | -9.2912e-06 | 0.0022779 | 0.0023023 | 0.0023266 | 0.0023509 | 0.0023753 | 0.002366 | 0.0023567 | 0.0023474 | 0.0023381 | 0.0023288 | 0.0023195 | 0.0023102 | 0.0023009 | 0.0022916 | 0.0022824 | 0.0022731 | 0.0022638 | 0.0022545 | 0.0022452 | 0.0022359 | 4.2e-07 | -1.6e-07 | 3.852e-05 | 3.894e-05 | 3.936e-05 | 3.978e-05 | 4.02e-05 | 4.004e-05 | 3.988e-05 | 3.972e-05 | 3.956e-05 | 3.94e-05 | 3.924e-05 | 3.908e-05 | 3.892e-05 | 3.876e-05 | 3.86e-05 | 3.844e-05 | 3.828e-05 | 3.812e-05 | 3.796e-05 | 3.78e-05
| BBD014-96325958 | 100 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BBD014-97325263 | 92 | 82 | 0.012958 | 0.00041517 | 0.01875 | 0.00061624 | 0.018141 | 0.00059859 | 0.0001655 | -3.0467e-05 | 0.018088 | 0.018254 | 0.018419 | 0.018585 | 0.01875 | 0.01872 | 0.018689 | 0.018659 | 0.018628 | 0.018598 | 0.018567 | 0.018537 | 0.018506 | 0.018476 | 0.018445 | 0.018415 | 0.018384 | 0.018354 | 0.018324 | 0.018293 | 5.7449e-06 | -8.825e-07 | 0.00059326 | 0.00059901 | 0.00060475 | 0.0006105 | 0.00061624 | 0.00061536 | 0.00061448 | 0.00061359 | 0.00061271 | 0.00061183 | 0.00061095 | 0.00061006 | 0.00060918 | 0.0006083 | 0.00060742 | 0.00060653 | 0.00060565 | 0.00060477 | 0.00060389 | 0.000603
| BBD021-15437930 | 204 | 5 | 4.6e-07 | 0.00019625 | 6.83e-07 | 0.00029129 | 6.67e-07 | 0.00028425 | 6.3714e-09 | -8e-10 | 6.5751e-07 | 6.6389e-07 | 6.7026e-07 | 6.7663e-07 | 6.83e-07 | 6.822e-07 | 6.814e-07 | 6.806e-07 | 6.798e-07 | 6.79e-07 | 6.782e-07 | 6.774e-07 | 6.766e-07 | 6.758e-07 | 6.75e-07 | 6.742e-07 | 6.734e-07 | 6.726e-07 | 6.718e-07 | 6.71e-07 | 2.7155e-06 | -3.52e-07 | 0.00028043 | 0.00028314 | 0.00028586 | 0.00028857 | 0.00029129 | 0.00029093 | 0.00029058 | 0.00029023 | 0.00028988 | 0.00028953 | 0.00028917 | 0.00028882 | 0.00028847 | 0.00028812 | 0.00028777 | 0.00028741 | 0.00028706 | 0.00028671 | 0.00028636 | 0.00028601
| BBD021-24611491 | 70 | 29 | 0.011878 | 0.0019433 | 0.017181 | 0.0029828 | 0.016549 | 0.0028951 | 0.00015152 | -3.1617e-05 | 0.016575 | 0.016727 | 0.016878 | 0.01703 | 0.017181 | 0.01715 | 0.017118 | 0.017086 | 0.017055 | 0.017023 | 0.016992 | 0.01696 | 0.016928 | 0.016897 | 0.016865 | 0.016834 | 0.016802 | 0.01677 | 0.016739 | 0.016707 | 2.97e-05 | -4.3839e-06 | 0.002864 | 0.0028937 | 0.0029234 | 0.0029531 | 0.0029828 | 0.0029784 | 0.0029741 | 0.0029697 | 0.0029653 | 0.0029609 | 0.0029565 | 0.0029521 | 0.0029478 | 0.0029434 | 0.002939 | 0.0029346 | 0.0029302 | 0.0029258 | 0.0029215 | 0.0029171
| BBD021-24613487 | 199 | 129 | 0.026005 | 0.00048858 | 0.035968 | 0.00072222 | 0.034429 | 0.00069545 | 0.00028466 | -7.6939e-05 | 0.034829 | 0.035114 | 0.035398 | 0.035683 | 0.035968 | 0.035891 | 0.035814 | 0.035737 | 0.03566 | 0.035583 | 0.035506 | 0.035429 | 0.035352 | 0.035275 | 0.035198 | 0.035121 | 0.035045 | 0.034968 | 0.034891 | 0.034814 | 6.6756e-06 | -1.3387e-06 | 0.00069552 | 0.0007022 | 0.00070887 | 0.00071555 | 0.00072222 | 0.00072088 | 0.00071954 | 0.00071821 | 0.00071687 | 0.00071553 | 0.00071419 | 0.00071285 | 0.00071151 | 0.00071017 | 0.00070883 | 0.0007075 | 0.00070616 | 0.00070482 | 0.00070348 | 0.00070214
| BBD021-40480035 | 41 | 41 | 0.030335 | 0 | 0.041392 | 0 | 0.039541 | 0 | 0.00031594 | -9.2558e-05 | 0.040129 | 0.040445 | 0.04076 | 0.041076 | 0.041392 | 0.0413 | 0.041207 | 0.041115 | 0.041022 | 0.04093 | 0.040837 | 0.040744 | 0.040652 | 0.040559 | 0.040467 | 0.040374 | 0.040282 | 0.040189 | 0.040097 | 0.040004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BBD022-15437908 | 5 | 5 | 0.0070562 | 0 | 0.01036 | 0 | 0.009891 | 0 | 9.4389e-05 | -2.344e-05 | 0.0099822 | 0.010077 | 0.010171 | 0.010265 | 0.01036 | 0.010336 | 0.010313 | 0.010289 | 0.010266 | 0.010243 | 0.010219 | 0.010196 | 0.010172 | 0.010149 | 0.010125 | 0.010102 | 0.010079 | 0.010055 | 0.010032 | 0.010008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET001-143534818 | 31 | 31 | 0.0050588 | 0 | 0.0065209 | 0 | 0.0067161 | 0 | 4.1776e-05 | 9.7578e-06 | 0.0063538 | 0.0063956 | 0.0064374 | 0.0064792 | 0.0065209 | 0.0065307 | 0.0065405 | 0.0065502 | 0.00656 | 0.0065697 | 0.0065795 | 0.0065892 | 0.006599 | 0.0066088 | 0.0066185 | 0.0066283 | 0.006638 | 0.0066478 | 0.0066575 | 0.0066673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET001-15424260 | 5587 | 5206 | 0.0067216 | 0.013212 | 0.0086986 | 0.017205 | 0.009192 | 0.018208 | 5.6484e-05 | 2.467e-05 | 0.0084726 | 0.0085291 | 0.0085856 | 0.0086421 | 0.0086986 | 0.0087233 | 0.0087479 | 0.0087726 | 0.0087973 | 0.0088219 | 0.0088466 | 0.0088713 | 0.0088959 | 0.0089206 | 0.0089453 | 0.00897 | 0.0089946 | 0.0090193 | 0.009044 | 0.0090686 | 0.0001141 | 5.0136e-05 | 0.016749 | 0.016863 | 0.016977 | 0.017091 | 0.017205 | 0.017255 | 0.017306 | 0.017356 | 0.017406 | 0.017456 | 0.017506 | 0.017556 | 0.017606 | 0.017657 | 0.017707 | 0.017757 | 0.017807 | 0.017857 | 0.017907 | 0.017957
| BET001-163510183 | 129 | 101 | 0.024013 | 0.0085277 | 0.03044 | 0.010847 | 0.032018 | 0.01141 | 0.00018362 | 7.8943e-05 | 0.029705 | 0.029889 | 0.030072 | 0.030256 | 0.03044 | 0.030518 | 0.030597 | 0.030676 | 0.030755 | 0.030834 | 0.030913 | 0.030992 | 0.031071 | 0.03115 | 0.031229 | 0.031308 | 0.031387 | 0.031466 | 0.031545 | 0.031624 | 6.6265e-05 | 2.8126e-05 | 0.010582 | 0.010648 | 0.010714 | 0.010781 | 0.010847 | 0.010875 | 0.010903 | 0.010931 | 0.01096 | 0.010988 | 0.011016 | 0.011044 | 0.011072 | 0.0111 | 0.011128 | 0.011156 | 0.011185 | 0.011213 | 0.011241 | 0.011269
| BET001-163510254 | 252 | 221 | 0.018271 | 0.0031252 | 0.024635 | 0.0040601 | 0.026328 | 0.0042942 | 0.00018182 | 8.463e-05 | 0.023908 | 0.02409 | 0.024272 | 0.024453 | 0.024635 | 0.02472 | 0.024804 | 0.024889 | 0.024974 | 0.025058 | 0.025143 | 0.025228 | 0.025312 | 0.025397 | 0.025481 | 0.025566 | 0.025651 | 0.025735 | 0.02582 | 0.025905 | 2.6713e-05 | 1.1705e-05 | 0.0039533 | 0.00398 | 0.0040067 | 0.0040334 | 0.0040601 | 0.0040718 | 0.0040835 | 0.0040953 | 0.004107 | 0.0041187 | 0.0041304 | 0.0041421 | 0.0041538 | 0.0041655 | 0.0041772 | 0.0041889 | 0.0042006 | 0.0042123 | 0.004224 | 0.0042357
| BET001-163979859 | 28 | 28 | 0.010123 | 0 | 0.013655 | 0 | 0.014363 | 0 | 0.00010091 | 3.5415e-05 | 0.013251 | 0.013352 | 0.013453 | 0.013554 | 0.013655 | 0.01369 | 0.013726 | 0.013761 | 0.013797 | 0.013832 | 0.013867 | 0.013903 | 0.013938 | 0.013974 | 0.014009 | 0.014044 | 0.01408 | 0.014115 | 0.014151 | 0.014186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET002-147836095 | 2312 | 2312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET002-15424310 | 3156 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET003-15424094 | 331 | 331 | 0.0019431 | 0 | 0.0023698 | 0 | 0.0024504 | 0 | 1.2192e-05 | 4.0287e-06 | 0.002321 | 0.0023332 | 0.0023454 | 0.0023576 | 0.0023698 | 0.0023738 | 0.0023779 | 0.0023819 | 0.0023859 | 0.00239 | 0.002394 | 0.002398 | 0.002402 | 0.0024061 | 0.0024101 | 0.0024141 | 0.0024182 | 0.0024222 | 0.0024262 | 0.0024302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET004-112026510 | 36 | 36 | 0.013258 | 0 | 0.017475 | 0 | 0.01849 | 0 | 0.0001205 | 5.075e-05 | 0.016993 | 0.017114 | 0.017234 | 0.017355 | 0.017475 | 0.017526 | 0.017577 | 0.017628 | 0.017678 | 0.017729 | 0.01778 | 0.017831 | 0.017881 | 0.017932 | 0.017983 | 0.018034 | 0.018084 | 0.018135 | 0.018186 | 0.018237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET004-15424334 | 3419 | 2482 | 0.010794 | 0.0069899 | 0.013377 | 0.0087688 | 0.014668 | 0.0096556 | 7.3803e-05 | 6.4537e-05 | 0.013082 | 0.013156 | 0.01323 | 0.013303 | 0.013377 | 0.013442 | 0.013506 | 0.013571 | 0.013635 | 0.0137 | 0.013764 | 0.013829 | 0.013893 | 0.013958 | 0.014023 | 0.014087 | 0.014152 | 0.014216 | 0.014281 | 0.014345 | 5.0826e-05 | 4.4341e-05 | 0.0085655 | 0.0086163 | 0.0086672 | 0.008718 | 0.0087688 | 0.0088131 | 0.0088575 | 0.0089018 | 0.0089462 | 0.0089905 | 0.0090349 | 0.0090792 | 0.0091235 | 0.0091679 | 0.0092122 | 0.0092566 | 0.0093009 | 0.0093452 | 0.0093896 | 0.0094339
| BET004-163616866 | 32 | 32 | 0.0085427 | 0 | 0.011295 | 0 | 0.01184 | 0 | 7.8648e-05 | 2.7238e-05 | 0.010981 | 0.011059 | 0.011138 | 0.011217 | 0.011295 | 0.011323 | 0.01135 | 0.011377 | 0.011404 | 0.011432 | 0.011459 | 0.011486 | 0.011513 | 0.011541 | 0.011568 | 0.011595 | 0.011622 | 0.011649 | 0.011677 | 0.011704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET004-164487583 | 5 | 5 | 0.0058305 | 0 | 0.0072807 | 0 | 0.0075523 | 0 | 4.1433e-05 | 1.3582e-05 | 0.0071149 | 0.0071564 | 0.0071978 | 0.0072392 | 0.0072807 | 0.0072942 | 0.0073078 | 0.0073214 | 0.007335 | 0.0073486 | 0.0073622 | 0.0073757 | 0.0073893 | 0.0074029 | 0.0074165 | 0.0074301 | 0.0074436 | 0.0074572 | 0.0074708 | 0.0074844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET004-164487758 | 8 | 8 | 0.0045575 | 0 | 0.0060316 | 0 | 0.006324 | 0 | 4.2115e-05 | 1.4622e-05 | 0.0058631 | 0.0059052 | 0.0059473 | 0.0059895 | 0.0060316 | 0.0060462 | 0.0060608 | 0.0060754 | 0.0060901 | 0.0061047 | 0.0061193 | 0.0061339 | 0.0061485 | 0.0061632 | 0.0061778 | 0.0061924 | 0.006207 | 0.0062217 | 0.0062363 | 0.0062509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET004-24611449 | 937 | 578 | 0.022022 | 0.031858 | 0.027454 | 0.039212 | 0.028272 | 0.040316 | 0.00015519 | 4.091e-05 | 0.026833 | 0.026988 | 0.027143 | 0.027299 | 0.027454 | 0.027495 | 0.027536 | 0.027576 | 0.027617 | 0.027658 | 0.027699 | 0.02774 | 0.027781 | 0.027822 | 0.027863 | 0.027904 | 0.027945 | 0.027986 | 0.028026 | 0.028067 | 0.00021011 | 5.5221e-05 | 0.038371 | 0.038581 | 0.038792 | 0.039002 | 0.039212 | 0.039267 | 0.039322 | 0.039377 | 0.039433 | 0.039488 | 0.039543 | 0.039598 | 0.039654 | 0.039709 | 0.039764 | 0.039819 | 0.039874 | 0.03993 | 0.039985 | 0.04004
| BET004-72499638 | 48 | 48 | 0.014868 | 0 | 0.018902 | 0 | 0.019431 | 0 | 0.00011527 | 2.6462e-05 | 0.018441 | 0.018556 | 0.018671 | 0.018787 | 0.018902 | 0.018928 | 0.018955 | 0.018981 | 0.019008 | 0.019034 | 0.019061 | 0.019087 | 0.019114 | 0.01914 | 0.019166 | 0.019193 | 0.019219 | 0.019246 | 0.019272 | 0.019299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET004-72499720 | 27 | 27 | 0.0040478 | 0 | 0.0051985 | 0 | 0.0054597 | 0 | 3.2879e-05 | 1.3059e-05 | 0.005067 | 0.0050999 | 0.0051328 | 0.0051657 | 0.0051985 | 0.0052116 | 0.0052247 | 0.0052377 | 0.0052508 | 0.0052638 | 0.0052769 | 0.0052899 | 0.005303 | 0.0053161 | 0.0053291 | 0.0053422 | 0.0053552 | 0.0053683 | 0.0053814 | 0.0053944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET004-72499790 | 37 | 37 | 0.0021343 | 0 | 0.0029443 | 0 | 0.0031436 | 0 | 2.3145e-05 | 9.965e-06 | 0.0028517 | 0.0028749 | 0.002898 | 0.0029212 | 0.0029443 | 0.0029543 | 0.0029643 | 0.0029742 | 0.0029842 | 0.0029941 | 0.0030041 | 0.0030141 | 0.003024 | 0.003034 | 0.003044 | 0.0030539 | 0.0030639 | 0.0030739 | 0.0030838 | 0.0030938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET004-72500100 | 54 | 54 | 0.0074393 | 0 | 0.0092552 | 0 | 0.0096657 | 0 | 5.1881e-05 | 2.0523e-05 | 0.0090477 | 0.0090995 | 0.0091514 | 0.0092033 | 0.0092552 | 0.0092757 | 0.0092962 | 0.0093168 | 0.0093373 | 0.0093578 | 0.0093783 | 0.0093989 | 0.0094194 | 0.0094399 | 0.0094604 | 0.0094809 | 0.0095015 | 0.009522 | 0.0095425 | 0.009563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET004-72500230 | 37 | 37 | 0.0022477 | 0 | 0.0029264 | 0 | 0.0030224 | 0 | 1.939e-05 | 4.7984e-06 | 0.0028488 | 0.0028682 | 0.0028876 | 0.002907 | 0.0029264 | 0.0029312 | 0.002936 | 0.0029408 | 0.0029456 | 0.0029504 | 0.0029552 | 0.00296 | 0.0029648 | 0.0029696 | 0.0029744 | 0.0029792 | 0.002984 | 0.0029888 | 0.0029936 | 0.0029984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET004-72500251 | 47 | 47 | 0.0094065 | 0 | 0.012933 | 0 | 0.013647 | 0 | 0.00010075 | 3.5718e-05 | 0.01253 | 0.01263 | 0.012731 | 0.012832 | 0.012933 | 0.012968 | 0.013004 | 0.01304 | 0.013075 | 0.013111 | 0.013147 | 0.013183 | 0.013218 | 0.013254 | 0.01329 | 0.013325 | 0.013361 | 0.013397 | 0.013433 | 0.013468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET004-72500469 | 28 | 28 | 0.012722 | 0 | 0.014858 | 0 | 0.015232 | 0 | 6.1026e-05 | 1.8696e-05 | 0.014614 | 0.014675 | 0.014736 | 0.014797 | 0.014858 | 0.014877 | 0.014895 | 0.014914 | 0.014933 | 0.014951 | 0.01497 | 0.014989 | 0.015008 | 0.015026 | 0.015045 | 0.015064 | 0.015082 | 0.015101 | 0.01512 | 0.015138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET005-110828671 | 64 | 64 | 0.010559 | 0 | 0.013672 | 0 | 0.014201 | 0 | 8.8929e-05 | 2.647e-05 | 0.013316 | 0.013405 | 0.013494 | 0.013583 | 0.013672 | 0.013698 | 0.013725 | 0.013751 | 0.013778 | 0.013804 | 0.013831 | 0.013857 | 0.013884 | 0.01391 | 0.013937 | 0.013963 | 0.01399 | 0.014016 | 0.014043 | 0.014069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET005-117327746 | 9 | 9 | 0.0052091 | 0 | 0.007343 | 0 | 0.0080772 | 0 | 6.0971e-05 | 3.6709e-05 | 0.0070992 | 0.0071601 | 0.0072211 | 0.0072821 | 0.007343 | 0.0073798 | 0.0074165 | 0.0074532 | 0.0074899 | 0.0075266 | 0.0075633 | 0.0076 | 0.0076367 | 0.0076734 | 0.0077101 | 0.0077468 | 0.0077835 | 0.0078203 | 0.007857 | 0.0078937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET005-142631975 | 5 | 5 | 0.00066924 | 0 | 0.00093341 | 0 | 0.0010097 | 0 | 7.5477e-06 | 3.8139e-06 | 0.00090322 | 0.00091076 | 0.00091831 | 0.00092586 | 0.00093341 | 0.00093722 | 0.00094103 | 0.00094485 | 0.00094866 | 0.00095248 | 0.00095629 | 0.0009601 | 0.00096392 | 0.00096773 | 0.00097155 | 0.00097536 | 0.00097917 | 0.00098299 | 0.0009868 | 0.00099061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET005-142632215 | 23 | 23 | 0.0039335 | 0 | 0.005353 | 0 | 0.005708 | 0 | 4.0557e-05 | 1.7746e-05 | 0.0051908 | 0.0052314 | 0.0052719 | 0.0053125 | 0.005353 | 0.0053708 | 0.0053885 | 0.0054063 | 0.005424 | 0.0054418 | 0.0054595 | 0.0054773 | 0.005495 | 0.0055128 | 0.0055305 | 0.0055482 | 0.005566 | 0.0055837 | 0.0056015 | 0.0056192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET005-143035133 | 47 | 47 | 0.0035489 | 0 | 0.0047791 | 0 | 0.0049777 | 0 | 3.515e-05 | 9.9279e-06 | 0.0046385 | 0.0046737 | 0.0047088 | 0.004744 | 0.0047791 | 0.004789 | 0.004799 | 0.0048089 | 0.0048188 | 0.0048288 | 0.0048387 | 0.0048486 | 0.0048585 | 0.0048685 | 0.0048784 | 0.0048883 | 0.0048983 | 0.0049082 | 0.0049181 | 0.004928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET005-143035406 | 42 | 42 | 0.010443 | 0 | 0.013433 | 0 | 0.013939 | 0 | 8.5427e-05 | 2.5303e-05 | 0.013091 | 0.013177 | 0.013262 | 0.013348 | 0.013433 | 0.013458 | 0.013484 | 0.013509 | 0.013534 | 0.013559 | 0.013585 | 0.01361 | 0.013635 | 0.013661 | 0.013686 | 0.013711 | 0.013737 | 0.013762 | 0.013787 | 0.013813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET005-143035691 | 9 | 9 | 0.0072233 | 0 | 0.009442 | 0 | 0.010035 | 0 | 6.3392e-05 | 2.9674e-05 | 0.0091884 | 0.0092518 | 0.0093152 | 0.0093786 | 0.009442 | 0.0094717 | 0.0095014 | 0.009531 | 0.0095607 | 0.0095904 | 0.0096201 | 0.0096497 | 0.0096794 | 0.0097091 | 0.0097387 | 0.0097684 | 0.0097981 | 0.0098278 | 0.0098574 | 0.0098871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET005-15436909 | 3687 | 2212 | 0.014597 | 0.015131 | 0.016571 | 0.017514 | 0.016911 | 0.017944 | 5.6378e-05 | 1.7026e-05 | 0.016345 | 0.016402 | 0.016458 | 0.016514 | 0.016571 | 0.016588 | 0.016605 | 0.016622 | 0.016639 | 0.016656 | 0.016673 | 0.01669 | 0.016707 | 0.016724 | 0.016741 | 0.016758 | 0.016775 | 0.016792 | 0.016809 | 0.016826 | 6.8078e-05 | 2.1494e-05 | 0.017242 | 0.01731 | 0.017378 | 0.017446 | 0.017514 | 0.017536 | 0.017557 | 0.017579 | 0.0176 | 0.017622 | 0.017643 | 0.017665 | 0.017686 | 0.017708 | 0.017729 | 0.017751 | 0.017772 | 0.017794 | 0.017815 | 0.017837
| BET005-162764936 | 10 | 10 | 0.0013098 | 0 | 0.0017248 | 0 | 0.001801 | 0 | 1.1857e-05 | 3.8088e-06 | 0.0016774 | 0.0016892 | 0.0017011 | 0.0017129 | 0.0017248 | 0.0017286 | 0.0017324 | 0.0017362 | 0.00174 | 0.0017438 | 0.0017476 | 0.0017514 | 0.0017553 | 0.0017591 | 0.0017629 | 0.0017667 | 0.0017705 | 0.0017743 | 0.0017781 | 0.0017819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET005-24614354 | 1475 | 909 | 0.032089 | 0.017614 | 0.038767 | 0.022799 | 0.040401 | 0.024161 | 0.00019082 | 8.1707e-05 | 0.038004 | 0.038195 | 0.038386 | 0.038576 | 0.038767 | 0.038849 | 0.038931 | 0.039012 | 0.039094 | 0.039176 | 0.039258 | 0.039339 | 0.039421 | 0.039503 | 0.039584 | 0.039666 | 0.039748 | 0.039829 | 0.039911 | 0.039993 | 0.00014815 | 6.8099e-05 | 0.022207 | 0.022355 | 0.022503 | 0.022651 | 0.022799 | 0.022867 | 0.022935 | 0.023003 | 0.023072 | 0.02314 | 0.023208 | 0.023276 | 0.023344 | 0.023412 | 0.02348 | 0.023548 | 0.023616 | 0.023684 | 0.023753 | 0.023821
| BET005-54520179 | 408 | 234 | 0.042499 | 0.0062047 | 0.057118 | 0.0089468 | 0.061437 | 0.0098776 | 0.00041771 | 0.00021591 | 0.055448 | 0.055865 | 0.056283 | 0.056701 | 0.057118 | 0.057334 | 0.05755 | 0.057766 | 0.057982 | 0.058198 | 0.058414 | 0.05863 | 0.058846 | 0.059062 | 0.059278 | 0.059493 | 0.059709 | 0.059925 | 0.060141 | 0.060357 | 7.8346e-05 | 4.6541e-05 | 0.0086334 | 0.0087118 | 0.0087901 | 0.0088685 | 0.0089468 | 0.0089933 | 0.0090399 | 0.0090864 | 0.009133 | 0.0091795 | 0.009226 | 0.0092726 | 0.0093191 | 0.0093657 | 0.0094122 | 0.0094587 | 0.0095053 | 0.0095518 | 0.0095984 | 0.0096449
| BET005-76446461 | 59 | 59 | 0.0049583 | 0 | 0.0068211 | 0 | 0.0072553 | 0 | 5.3222e-05 | 2.171e-05 | 0.0066082 | 0.0066614 | 0.0067146 | 0.0067678 | 0.0068211 | 0.0068428 | 0.0068645 | 0.0068862 | 0.0069079 | 0.0069296 | 0.0069513 | 0.006973 | 0.0069947 | 0.0070165 | 0.0070382 | 0.0070599 | 0.0070816 | 0.0071033 | 0.007125 | 0.0071467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET005-76446537 | 31 | 31 | 0.0048714 | 0 | 0.0068577 | 0 | 0.0073264 | 0 | 5.675e-05 | 2.3438e-05 | 0.0066307 | 0.0066874 | 0.0067442 | 0.0068009 | 0.0068577 | 0.0068811 | 0.0069045 | 0.006928 | 0.0069514 | 0.0069748 | 0.0069983 | 0.0070217 | 0.0070452 | 0.0070686 | 0.007092 | 0.0071155 | 0.0071389 | 0.0071623 | 0.0071858 | 0.0072092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET006-122234049 | 31 | 31 | 0.0032786 | 0 | 0.0041349 | 0 | 0.0043259 | 0 | 2.4464e-05 | 9.5514e-06 | 0.004037 | 0.0040615 | 0.0040859 | 0.0041104 | 0.0041349 | 0.0041444 | 0.004154 | 0.0041635 | 0.0041731 | 0.0041826 | 0.0041922 | 0.0042017 | 0.0042113 | 0.0042208 | 0.0042304 | 0.0042399 | 0.0042495 | 0.004259 | 0.0042686 | 0.0042781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET006-123629680 | 88 | 88 | 0.012121 | 0 | 0.015695 | 0 | 0.016151 | 0 | 0.00010213 | 2.281e-05 | 0.015287 | 0.015389 | 0.015491 | 0.015593 | 0.015695 | 0.015718 | 0.015741 | 0.015764 | 0.015786 | 0.015809 | 0.015832 | 0.015855 | 0.015878 | 0.0159 | 0.015923 | 0.015946 | 0.015969 | 0.015992 | 0.016014 | 0.016037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET006-130742783 | 26 | 26 | 0.0092639 | 0 | 0.011828 | 0 | 0.012356 | 0 | 7.3275e-05 | 2.6368e-05 | 0.011535 | 0.011609 | 0.011682 | 0.011755 | 0.011828 | 0.011855 | 0.011881 | 0.011908 | 0.011934 | 0.01196 | 0.011987 | 0.012013 | 0.012039 | 0.012066 | 0.012092 | 0.012119 | 0.012145 | 0.012171 | 0.012198 | 0.012224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET006-143535036 | 30 | 30 | 0.002294 | 0 | 0.0030293 | 0 | 0.0031543 | 0 | 2.1006e-05 | 6.2536e-06 | 0.0029452 | 0.0029663 | 0.0029873 | 0.0030083 | 0.0030293 | 0.0030355 | 0.0030418 | 0.003048 | 0.0030543 | 0.0030605 | 0.0030668 | 0.0030731 | 0.0030793 | 0.0030856 | 0.0030918 | 0.0030981 | 0.0031043 | 0.0031106 | 0.0031168 | 0.0031231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET006-143535310 | 38 | 38 | 0.0024336 | 0 | 0.0031625 | 0 | 0.0034357 | 0 | 2.0828e-05 | 1.3659e-05 | 0.0030792 | 0.0031 | 0.0031209 | 0.0031417 | 0.0031625 | 0.0031762 | 0.0031899 | 0.0032035 | 0.0032172 | 0.0032308 | 0.0032445 | 0.0032581 | 0.0032718 | 0.0032855 | 0.0032991 | 0.0033128 | 0.0033264 | 0.0033401 | 0.0033538 | 0.0033674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET006-143535450 | 50 | 50 | 0.0072307 | 0 | 0.0098215 | 0 | 0.010333 | 0 | 7.4022e-05 | 2.5588e-05 | 0.0095254 | 0.0095994 | 0.0096735 | 0.0097475 | 0.0098215 | 0.0098471 | 0.0098727 | 0.0098983 | 0.0099238 | 0.0099494 | 0.009975 | 0.010001 | 0.010026 | 0.010052 | 0.010077 | 0.010103 | 0.010129 | 0.010154 | 0.01018 | 0.010205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET006-15436859 | 5544 | 2754 | 0.016072 | 0.020848 | 0.016835 | 0.021665 | 0.016945 | 0.021785 | 2.1798e-05 | 5.5019e-06 | 0.016748 | 0.01677 | 0.016792 | 0.016814 | 0.016835 | 0.016841 | 0.016846 | 0.016852 | 0.016857 | 0.016863 | 0.016868 | 0.016874 | 0.016879 | 0.016885 | 0.01689 | 0.016896 | 0.016901 | 0.016907 | 0.016912 | 0.016918 | 2.3335e-05 | 5.9903e-06 | 0.021572 | 0.021595 | 0.021618 | 0.021642 | 0.021665 | 0.021671 | 0.021677 | 0.021683 | 0.021689 | 0.021695 | 0.021701 | 0.021707 | 0.021713 | 0.021719 | 0.021725 | 0.021731 | 0.021737 | 0.021743 | 0.021749 | 0.021755
| BET006-160813078 | 49 | 49 | 0.0056566 | 0 | 0.0076148 | 0 | 0.0082165 | 0 | 5.5948e-05 | 3.0087e-05 | 0.007391 | 0.0074469 | 0.0075029 | 0.0075588 | 0.0076148 | 0.0076449 | 0.0076749 | 0.007705 | 0.0077351 | 0.0077652 | 0.0077953 | 0.0078254 | 0.0078555 | 0.0078856 | 0.0079156 | 0.0079457 | 0.0079758 | 0.0080059 | 0.008036 | 0.0080661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET006-163864001 | 22 | 22 | 0.024305 | 0 | 0.030626 | 0 | 0.032155 | 0 | 0.00018058 | 7.6473e-05 | 0.029903 | 0.030084 | 0.030265 | 0.030445 | 0.030626 | 0.030702 | 0.030779 | 0.030855 | 0.030932 | 0.031008 | 0.031085 | 0.031161 | 0.031238 | 0.031314 | 0.03139 | 0.031467 | 0.031543 | 0.03162 | 0.031696 | 0.031773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET006-195895491 | 0 | 0 | 0.060129 | 0 | 0.078016 | 0 | 0.081549 | 0 | 0.00051104 | 0.00017667 | 0.075972 | 0.076483 | 0.076994 | 0.077505 | 0.078016 | 0.078192 | 0.078369 | 0.078546 | 0.078722 | 0.078899 | 0.079076 | 0.079252 | 0.079429 | 0.079606 | 0.079782 | 0.079959 | 0.080136 | 0.080312 | 0.080489 | 0.080666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET006-195895635 | 1246 | 263 | 0.0073279 | 0.011355 | 0.0093484 | 0.0148 | 0.0098657 | 0.015691 | 5.7728e-05 | 2.5869e-05 | 0.0091174 | 0.0091752 | 0.0092329 | 0.0092906 | 0.0093484 | 0.0093742 | 0.0094001 | 0.009426 | 0.0094518 | 0.0094777 | 0.0095036 | 0.0095294 | 0.0095553 | 0.0095812 | 0.0096071 | 0.0096329 | 0.0096588 | 0.0096847 | 0.0097105 | 0.0097364 | 9.8415e-05 | 4.4536e-05 | 0.014406 | 0.014505 | 0.014603 | 0.014701 | 0.0148 | 0.014844 | 0.014889 | 0.014933 | 0.014978 | 0.015023 | 0.015067 | 0.015112 | 0.015156 | 0.015201 | 0.015245 | 0.01529 | 0.015334 | 0.015379 | 0.015423 | 0.015468
| BET006-195895661 | 680 | 566 | 0.045854 | 0.0038265 | 0.052437 | 0.0051746 | 0.054312 | 0.0056559 | 0.00018808 | 9.3757e-05 | 0.051684 | 0.051872 | 0.05206 | 0.052249 | 0.052437 | 0.05253 | 0.052624 | 0.052718 | 0.052812 | 0.052905 | 0.052999 | 0.053093 | 0.053187 | 0.05328 | 0.053374 | 0.053468 | 0.053562 | 0.053655 | 0.053749 | 0.053843 | 3.8516e-05 | 2.4065e-05 | 0.0050205 | 0.0050591 | 0.0050976 | 0.0051361 | 0.0051746 | 0.0051987 | 0.0052227 | 0.0052468 | 0.0052709 | 0.0052949 | 0.005319 | 0.0053431 | 0.0053671 | 0.0053912 | 0.0054153 | 0.0054393 | 0.0054634 | 0.0054875 | 0.0055115 | 0.0055356
| BET006-195895699 | 2768 | 1522 | 0.027824 | 0.0066283 | 0.036347 | 0.008763 | 0.037587 | 0.0090742 | 0.0002435 | 6.2006e-05 | 0.035373 | 0.035616 | 0.03586 | 0.036103 | 0.036347 | 0.036409 | 0.036471 | 0.036533 | 0.036595 | 0.036657 | 0.036719 | 0.036781 | 0.036843 | 0.036905 | 0.036967 | 0.037029 | 0.037091 | 0.037153 | 0.037215 | 0.037277 | 6.0993e-05 | 1.5559e-05 | 0.0085191 | 0.0085801 | 0.008641 | 0.008702 | 0.008763 | 0.0087786 | 0.0087941 | 0.0088097 | 0.0088253 | 0.0088408 | 0.0088564 | 0.0088719 | 0.0088875 | 0.0089031 | 0.0089186 | 0.0089342 | 0.0089497 | 0.0089653 | 0.0089809 | 0.0089964
| BET006-74053669 | 49 | 49 | 0.0017381 | 0 | 0.0023391 | 0 | 0.0024646 | 0 | 1.7173e-05 | 6.2712e-06 | 0.0022705 | 0.0022876 | 0.0023048 | 0.002322 | 0.0023391 | 0.0023454 | 0.0023517 | 0.002358 | 0.0023642 | 0.0023705 | 0.0023768 | 0.002383 | 0.0023893 | 0.0023956 | 0.0024019 | 0.0024081 | 0.0024144 | 0.0024207 | 0.0024269 | 0.0024332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET006-74053924 | 27 | 27 | 0.0093258 | 0 | 0.012274 | 0 | 0.01297 | 0 | 8.4229e-05 | 3.4826e-05 | 0.011937 | 0.012021 | 0.012105 | 0.01219 | 0.012274 | 0.012309 | 0.012343 | 0.012378 | 0.012413 | 0.012448 | 0.012483 | 0.012518 | 0.012552 | 0.012587 | 0.012622 | 0.012657 | 0.012692 | 0.012727 | 0.012761 | 0.012796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET007-110330821 | 47 | 47 | 0.0063213 | 0 | 0.0072266 | 0 | 0.0075867 | 0 | 2.5866e-05 | 1.8007e-05 | 0.0071231 | 0.007149 | 0.0071748 | 0.0072007 | 0.0072266 | 0.0072446 | 0.0072626 | 0.0072806 | 0.0072986 | 0.0073166 | 0.0073346 | 0.0073526 | 0.0073706 | 0.0073886 | 0.0074066 | 0.0074246 | 0.0074426 | 0.0074606 | 0.0074787 | 0.0074967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET007-129159691 | 31 | 31 | 0.0018538 | 0 | 0.0023406 | 0 | 0.0024911 | 0 | 1.3906e-05 | 7.5257e-06 | 0.0022849 | 0.0022988 | 0.0023128 | 0.0023267 | 0.0023406 | 0.0023481 | 0.0023556 | 0.0023631 | 0.0023707 | 0.0023782 | 0.0023857 | 0.0023932 | 0.0024008 | 0.0024083 | 0.0024158 | 0.0024233 | 0.0024309 | 0.0024384 | 0.0024459 | 0.0024535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET007-132469306 | 38 | 38 | 0.054712 | 0 | 0.063409 | 0 | 0.06718 | 0 | 0.00024851 | 0.00018851 | 0.062415 | 0.062664 | 0.062912 | 0.063161 | 0.063409 | 0.063598 | 0.063786 | 0.063975 | 0.064163 | 0.064352 | 0.06454 | 0.064729 | 0.064917 | 0.065106 | 0.065295 | 0.065483 | 0.065672 | 0.06586 | 0.066049 | 0.066237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET007-132750977 | 45 | 45 | 0.0046865 | 0 | 0.0056497 | 0 | 0.0061157 | 0 | 2.7519e-05 | 2.33e-05 | 0.0055396 | 0.0055671 | 0.0055946 | 0.0056221 | 0.0056497 | 0.005673 | 0.0056963 | 0.0057196 | 0.0057429 | 0.0057662 | 0.0057895 | 0.0058128 | 0.0058361 | 0.0058594 | 0.0058827 | 0.005906 | 0.0059293 | 0.0059526 | 0.0059759 | 0.0059992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET007-132751049 | 16 | 16 | 0.0010255 | 0 | 0.0012541 | 0 | 0.0013741 | 0 | 6.531e-06 | 6.0016e-06 | 0.001228 | 0.0012345 | 0.001241 | 0.0012476 | 0.0012541 | 0.0012601 | 0.0012661 | 0.0012721 | 0.0012781 | 0.0012841 | 0.0012901 | 0.0012961 | 0.0013021 | 0.0013081 | 0.0013141 | 0.0013201 | 0.0013261 | 0.0013321 | 0.0013381 | 0.0013441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET007-134953366 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET007-154907496 | 33 | 33 | 0.0051562 | 0 | 0.0063571 | 0 | 0.0069023 | 0 | 3.4311e-05 | 2.7258e-05 | 0.0062199 | 0.0062542 | 0.0062885 | 0.0063228 | 0.0063571 | 0.0063844 | 0.0064116 | 0.0064389 | 0.0064661 | 0.0064934 | 0.0065207 | 0.0065479 | 0.0065752 | 0.0066024 | 0.0066297 | 0.0066569 | 0.0066842 | 0.0067115 | 0.0067387 | 0.006766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET007-154907629 | 16 | 16 | 0.00815 | 0 | 0.0098574 | 0 | 0.010617 | 0 | 4.8784e-05 | 3.7957e-05 | 0.0096623 | 0.009711 | 0.0097598 | 0.0098086 | 0.0098574 | 0.0098954 | 0.0099333 | 0.0099713 | 0.010009 | 0.010047 | 0.010085 | 0.010123 | 0.010161 | 0.010199 | 0.010237 | 0.010275 | 0.010313 | 0.010351 | 0.010389 | 0.010427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET007-154907735 | 18 | 18 | 0.0056858 | 0 | 0.0074336 | 0 | 0.0078209 | 0 | 4.9937e-05 | 1.936e-05 | 0.0072339 | 0.0072838 | 0.0073338 | 0.0073837 | 0.0074336 | 0.007453 | 0.0074724 | 0.0074917 | 0.0075111 | 0.0075304 | 0.0075498 | 0.0075692 | 0.0075885 | 0.0076079 | 0.0076273 | 0.0076466 | 0.007666 | 0.0076853 | 0.0077047 | 0.0077241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET007-154907875 | 34 | 34 | 0.0023291 | 0 | 0.0029787 | 0 | 0.003119 | 0 | 1.856e-05 | 7.0192e-06 | 0.0029044 | 0.002923 | 0.0029415 | 0.0029601 | 0.0029787 | 0.0029857 | 0.0029927 | 0.0029997 | 0.0030067 | 0.0030138 | 0.0030208 | 0.0030278 | 0.0030348 | 0.0030418 | 0.0030488 | 0.0030559 | 0.0030629 | 0.0030699 | 0.0030769 | 0.0030839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET007-155326877 | 2687 | 1971 | 0.048823 | 0.015518 | 0.056996 | 0.018844 | 0.058355 | 0.019419 | 0.0002335 | 6.7941e-05 | 0.056062 | 0.056295 | 0.056529 | 0.056762 | 0.056996 | 0.057064 | 0.057132 | 0.0572 | 0.057268 | 0.057336 | 0.057403 | 0.057471 | 0.057539 | 0.057607 | 0.057675 | 0.057743 | 0.057811 | 0.057879 | 0.057947 | 0.058015 | 9.5035e-05 | 2.8706e-05 | 0.018464 | 0.018559 | 0.018654 | 0.018749 | 0.018844 | 0.018873 | 0.018902 | 0.018931 | 0.018959 | 0.018988 | 0.019017 | 0.019045 | 0.019074 | 0.019103 | 0.019132 | 0.01916 | 0.019189 | 0.019218 | 0.019246 | 0.019275
| BET007-159943710 | 274 | 189 | 0.02116 | 0.0036672 | 0.025704 | 0.004554 | 0.027602 | 0.0049435 | 0.00012983 | 9.4876e-05 | 0.025185 | 0.025315 | 0.025445 | 0.025574 | 0.025704 | 0.025799 | 0.025894 | 0.025989 | 0.026084 | 0.026179 | 0.026273 | 0.026368 | 0.026463 | 0.026558 | 0.026653 | 0.026748 | 0.026843 | 0.026938 | 0.027032 | 0.027127 | 2.5338e-05 | 1.9478e-05 | 0.0044526 | 0.004478 | 0.0045033 | 0.0045286 | 0.004554 | 0.0045735 | 0.0045929 | 0.0046124 | 0.0046319 | 0.0046514 | 0.0046708 | 0.0046903 | 0.0047098 | 0.0047293 | 0.0047488 | 0.0047682 | 0.0047877 | 0.0048072 | 0.0048267 | 0.0048461
| BET007-162663688 | 324 | 225 | 0.0087902 | 0.0081111 | 0.011184 | 0.010129 | 0.0117 | 0.010551 | 6.8388e-05 | 2.5807e-05 | 0.01091 | 0.010979 | 0.011047 | 0.011115 | 0.011184 | 0.01121 | 0.011235 | 0.011261 | 0.011287 | 0.011313 | 0.011339 | 0.011364 | 0.01139 | 0.011416 | 0.011442 | 0.011468 | 0.011493 | 0.011519 | 0.011545 | 0.011571 | 5.7645e-05 | 2.1135e-05 | 0.0098981 | 0.0099557 | 0.010013 | 0.010071 | 0.010129 | 0.01015 | 0.010171 | 0.010192 | 0.010213 | 0.010234 | 0.010255 | 0.010277 | 0.010298 | 0.010319 | 0.01034 | 0.010361 | 0.010382 | 0.010403 | 0.010425 | 0.010446
| BET007-24613316 | 4498 | 1811 | 0.0043666 | 0.002012 | 0.0055166 | 0.0024944 | 0.0057464 | 0.0025889 | 3.2855e-05 | 1.1493e-05 | 0.0053852 | 0.005418 | 0.0054509 | 0.0054837 | 0.0055166 | 0.0055281 | 0.0055396 | 0.0055511 | 0.0055626 | 0.0055741 | 0.0055855 | 0.005597 | 0.0056085 | 0.00562 | 0.0056315 | 0.005643 | 0.0056545 | 0.005666 | 0.0056775 | 0.005689 | 1.3783e-05 | 4.7279e-06 | 0.0024393 | 0.002453 | 0.0024668 | 0.0024806 | 0.0024944 | 0.0024991 | 0.0025038 | 0.0025086 | 0.0025133 | 0.002518 | 0.0025228 | 0.0025275 | 0.0025322 | 0.0025369 | 0.0025417 | 0.0025464 | 0.0025511 | 0.0025559 | 0.0025606 | 0.0025653
| BET007-63637518 | 5439 | 941 | 0.0023213 | 0.0013152 | 0.0027535 | 0.0017174 | 0.0028315 | 0.0017994 | 1.2347e-05 | 3.9034e-06 | 0.0027041 | 0.0027164 | 0.0027288 | 0.0027411 | 0.0027535 | 0.0027574 | 0.0027613 | 0.0027652 | 0.0027691 | 0.002773 | 0.0027769 | 0.0027808 | 0.0027847 | 0.0027886 | 0.0027925 | 0.0027964 | 0.0028003 | 0.0028042 | 0.0028081 | 0.002812 | 1.1491e-05 | 4.0977e-06 | 0.0016715 | 0.0016829 | 0.0016944 | 0.0017059 | 0.0017174 | 0.0017215 | 0.0017256 | 0.0017297 | 0.0017338 | 0.0017379 | 0.001742 | 0.0017461 | 0.0017502 | 0.0017543 | 0.0017584 | 0.0017625 | 0.0017666 | 0.0017707 | 0.0017748 | 0.0017789
| BET008-94648877 | 2928 | 2928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO011-197684068 | 445 | 445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO012-197683994 | 2579 | 2579 | 0.007554 | 0 | 0.0090324 | 0 | 0.0092992 | 0 | 4.2241e-05 | 1.3339e-05 | 0.0088635 | 0.0089057 | 0.008948 | 0.0089902 | 0.0090324 | 0.0090458 | 0.0090591 | 0.0090725 | 0.0090858 | 0.0090991 | 0.0091125 | 0.0091258 | 0.0091391 | 0.0091525 | 0.0091658 | 0.0091792 | 0.0091925 | 0.0092058 | 0.0092192 | 0.0092325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO013-163795489 | 153 | 153 | 0.022201 | 0 | 0.028087 | 0 | 0.029133 | 0 | 0.00016816 | 5.2298e-05 | 0.027414 | 0.027582 | 0.02775 | 0.027918 | 0.028087 | 0.028139 | 0.028191 | 0.028244 | 0.028296 | 0.028348 | 0.0284 | 0.028453 | 0.028505 | 0.028557 | 0.02861 | 0.028662 | 0.028714 | 0.028767 | 0.028819 | 0.028871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO013-197650863 | 2705 | 2242 | 0.01522 | 0.0075942 | 0.018516 | 0.0092816 | 0.020015 | 0.0099808 | 9.4167e-05 | 7.4974e-05 | 0.018139 | 0.018233 | 0.018327 | 0.018422 | 0.018516 | 0.018591 | 0.018666 | 0.018741 | 0.018816 | 0.018891 | 0.018966 | 0.019041 | 0.019116 | 0.019191 | 0.019265 | 0.01934 | 0.019415 | 0.01949 | 0.019565 | 0.01964 | 4.8211e-05 | 3.496e-05 | 0.0090888 | 0.009137 | 0.0091852 | 0.0092334 | 0.0092816 | 0.0093166 | 0.0093515 | 0.0093865 | 0.0094214 | 0.0094564 | 0.0094914 | 0.0095263 | 0.0095613 | 0.0095962 | 0.0096312 | 0.0096662 | 0.0097011 | 0.0097361 | 0.009771 | 0.009806
| BGO013-24606216 | 463 | 310 | 0.015639 | 0.014959 | 0.020023 | 0.018633 | 0.021277 | 0.019614 | 0.00012527 | 6.2684e-05 | 0.019522 | 0.019647 | 0.019773 | 0.019898 | 0.020023 | 0.020086 | 0.020148 | 0.020211 | 0.020274 | 0.020337 | 0.020399 | 0.020462 | 0.020525 | 0.020587 | 0.02065 | 0.020713 | 0.020775 | 0.020838 | 0.020901 | 0.020963 | 0.00010495 | 4.9081e-05 | 0.018213 | 0.018318 | 0.018423 | 0.018528 | 0.018633 | 0.018682 | 0.018731 | 0.01878 | 0.018829 | 0.018878 | 0.018927 | 0.018976 | 0.019025 | 0.019074 | 0.019123 | 0.019172 | 0.019222 | 0.019271 | 0.01932 | 0.019369
| BGO014-197650786 | 526 | 526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO022-164367964 | 1352 | 1352 | 0.0025168 | 0 | 0.0032799 | 0 | 0.0035103 | 0 | 2.1802e-05 | 1.1521e-05 | 0.0031927 | 0.0032145 | 0.0032363 | 0.0032581 | 0.0032799 | 0.0032914 | 0.0033029 | 0.0033144 | 0.003326 | 0.0033375 | 0.003349 | 0.0033605 | 0.003372 | 0.0033836 | 0.0033951 | 0.0034066 | 0.0034181 | 0.0034297 | 0.0034412 | 0.0034527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO022-164368050 | 2207 | 2207 | 0.0010924 | 0 | 0.0012764 | 0 | 0.001316 | 0 | 5.258e-06 | 1.9799e-06 | 0.0012554 | 0.0012606 | 0.0012659 | 0.0012711 | 0.0012764 | 0.0012784 | 0.0012804 | 0.0012823 | 0.0012843 | 0.0012863 | 0.0012883 | 0.0012903 | 0.0012922 | 0.0012942 | 0.0012962 | 0.0012982 | 0.0013002 | 0.0013021 | 0.0013041 | 0.0013061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO022-197683907 | 4586 | 1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-143335276 | 42 | 42 | 0.051523 | 0 | 0.065351 | 0 | 0.072785 | 0 | 0.0003951 | 0.0003717 | 0.063771 | 0.064166 | 0.064561 | 0.064956 | 0.065351 | 0.065723 | 0.066095 | 0.066467 | 0.066838 | 0.06721 | 0.067582 | 0.067953 | 0.068325 | 0.068697 | 0.069068 | 0.06944 | 0.069812 | 0.070184 | 0.070555 | 0.070927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-143335516 | 49 | 49 | 0.0021364 | 0 | 0.0029024 | 0 | 0.0031551 | 0 | 2.1883e-05 | 1.2637e-05 | 0.0028148 | 0.0028367 | 0.0028586 | 0.0028805 | 0.0029024 | 0.002915 | 0.0029276 | 0.0029403 | 0.0029529 | 0.0029655 | 0.0029782 | 0.0029908 | 0.0030035 | 0.0030161 | 0.0030287 | 0.0030414 | 0.003054 | 0.0030666 | 0.0030793 | 0.0030919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-154908179 | 28 | 28 | 0.0021491 | 0 | 0.0028833 | 0 | 0.0030774 | 0 | 2.0977e-05 | 9.7074e-06 | 0.0027994 | 0.0028204 | 0.0028413 | 0.0028623 | 0.0028833 | 0.002893 | 0.0029027 | 0.0029124 | 0.0029221 | 0.0029318 | 0.0029415 | 0.0029512 | 0.002961 | 0.0029707 | 0.0029804 | 0.0029901 | 0.0029998 | 0.0030095 | 0.0030192 | 0.0030289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-154971813 | 9 | 9 | 0.0023132 | 0 | 0.0032268 | 0 | 0.0035324 | 0 | 2.6103e-05 | 1.528e-05 | 0.0031224 | 0.0031485 | 0.0031746 | 0.0032007 | 0.0032268 | 0.0032421 | 0.0032574 | 0.0032726 | 0.0032879 | 0.0033032 | 0.0033185 | 0.0033338 | 0.003349 | 0.0033643 | 0.0033796 | 0.0033949 | 0.0034102 | 0.0034254 | 0.0034407 | 0.003456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-154971917 | 9 | 9 | 0.0031565 | 0 | 0.0041714 | 0 | 0.0045548 | 0 | 2.8997e-05 | 1.9169e-05 | 0.0040554 | 0.0040844 | 0.0041134 | 0.0041424 | 0.0041714 | 0.0041906 | 0.0042097 | 0.0042289 | 0.0042481 | 0.0042672 | 0.0042864 | 0.0043056 | 0.0043247 | 0.0043439 | 0.0043631 | 0.0043822 | 0.0044014 | 0.0044206 | 0.0044398 | 0.0044589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-154972040 | 11 | 11 | 0.0020984 | 0 | 0.0028953 | 0 | 0.0032376 | 0 | 2.2769e-05 | 1.7116e-05 | 0.0028042 | 0.002827 | 0.0028498 | 0.0028725 | 0.0028953 | 0.0029124 | 0.0029295 | 0.0029467 | 0.0029638 | 0.0029809 | 0.002998 | 0.0030151 | 0.0030322 | 0.0030494 | 0.0030665 | 0.0030836 | 0.0031007 | 0.0031178 | 0.0031349 | 0.0031521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-155521549 | 19 | 19 | 0.0082214 | 0 | 0.010543 | 0 | 0.012484 | 0 | 6.6341e-05 | 9.702e-05 | 0.010278 | 0.010344 | 0.010411 | 0.010477 | 0.010543 | 0.01064 | 0.010737 | 0.010834 | 0.010931 | 0.011028 | 0.011125 | 0.011222 | 0.011319 | 0.011416 | 0.011513 | 0.011611 | 0.011708 | 0.011805 | 0.011902 | 0.011999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-159428721 | 2362 | 1424 | 0.039583 | 0.016434 | 0.045494 | 0.021392 | 0.047523 | 0.023231 | 0.00016888 | 0.00010149 | 0.044818 | 0.044987 | 0.045156 | 0.045325 | 0.045494 | 0.045595 | 0.045697 | 0.045798 | 0.045899 | 0.046001 | 0.046102 | 0.046204 | 0.046305 | 0.046407 | 0.046508 | 0.04661 | 0.046711 | 0.046813 | 0.046914 | 0.047016 | 0.00014167 | 9.1959e-05 | 0.020826 | 0.020967 | 0.021109 | 0.021251 | 0.021392 | 0.021484 | 0.021576 | 0.021668 | 0.02176 | 0.021852 | 0.021944 | 0.022036 | 0.022128 | 0.02222 | 0.022312 | 0.022404 | 0.022496 | 0.022588 | 0.02268 | 0.022772
| BGO023-159428755 | 2757 | 289 | 0.0061652 | 0.0099726 | 0.0080427 | 0.013239 | 0.0087751 | 0.014646 | 5.3642e-05 | 3.6619e-05 | 0.0078281 | 0.0078818 | 0.0079354 | 0.0079891 | 0.0080427 | 0.0080793 | 0.0081159 | 0.0081526 | 0.0081892 | 0.0082258 | 0.0082624 | 0.008299 | 0.0083357 | 0.0083723 | 0.0084089 | 0.0084455 | 0.0084821 | 0.0085188 | 0.0085554 | 0.008592 | 9.3336e-05 | 7.035e-05 | 0.012866 | 0.012959 | 0.013053 | 0.013146 | 0.013239 | 0.01331 | 0.01338 | 0.01345 | 0.013521 | 0.013591 | 0.013661 | 0.013732 | 0.013802 | 0.013873 | 0.013943 | 0.014013 | 0.014084 | 0.014154 | 0.014224 | 0.014295
| BGO023-197650699 | 2975 | 218 | 0.028042 | 0.0030805 | 0.032992 | 0.0041827 | 0.03416 | 0.0044966 | 0.00014143 | 5.8398e-05 | 0.032426 | 0.032567 | 0.032709 | 0.03285 | 0.032992 | 0.03305 | 0.033109 | 0.033167 | 0.033225 | 0.033284 | 0.033342 | 0.033401 | 0.033459 | 0.033517 | 0.033576 | 0.033634 | 0.033692 | 0.033751 | 0.033809 | 0.033868 | 3.1494e-05 | 1.5693e-05 | 0.0040568 | 0.0040883 | 0.0041198 | 0.0041513 | 0.0041827 | 0.0041984 | 0.0042141 | 0.0042298 | 0.0042455 | 0.0042612 | 0.0042769 | 0.0042926 | 0.0043083 | 0.004324 | 0.0043397 | 0.0043554 | 0.0043711 | 0.0043868 | 0.0044024 | 0.0044181
| BGO023-24604124 | 575 | 508 | 0.020661 | 0.017119 | 0.026137 | 0.021846 | 0.029815 | 0.025132 | 0.00015645 | 0.00018387 | 0.025511 | 0.025668 | 0.025824 | 0.025981 | 0.026137 | 0.026321 | 0.026505 | 0.026689 | 0.026873 | 0.027056 | 0.02724 | 0.027424 | 0.027608 | 0.027792 | 0.027976 | 0.02816 | 0.028344 | 0.028527 | 0.028711 | 0.028895 | 0.00013507 | 0.00016428 | 0.021306 | 0.021441 | 0.021576 | 0.021711 | 0.021846 | 0.022011 | 0.022175 | 0.022339 | 0.022503 | 0.022668 | 0.022832 | 0.022996 | 0.023161 | 0.023325 | 0.023489 | 0.023653 | 0.023818 | 0.023982 | 0.024146 | 0.02431
| BGO023-24614382 | 291 | 172 | 0.019457 | 0.0043705 | 0.024529 | 0.006024 | 0.027658 | 0.0072517 | 0.00014491 | 0.00015645 | 0.023949 | 0.024094 | 0.024239 | 0.024384 | 0.024529 | 0.024685 | 0.024842 | 0.024998 | 0.025155 | 0.025311 | 0.025468 | 0.025624 | 0.02578 | 0.025937 | 0.026093 | 0.02625 | 0.026406 | 0.026563 | 0.026719 | 0.026876 | 4.7243e-05 | 6.1382e-05 | 0.0058351 | 0.0058823 | 0.0059295 | 0.0059768 | 0.006024 | 0.0060854 | 0.0061468 | 0.0062082 | 0.0062696 | 0.0063309 | 0.0063923 | 0.0064537 | 0.0065151 | 0.0065765 | 0.0066379 | 0.0066992 | 0.0067606 | 0.006822 | 0.0068834 | 0.0069448
| BGO023-76446934 | 37 | 37 | 0.0049328 | 0 | 0.0070065 | 0 | 0.0075156 | 0 | 5.9249e-05 | 2.5454e-05 | 0.0067695 | 0.0068288 | 0.006888 | 0.0069473 | 0.0070065 | 0.007032 | 0.0070574 | 0.0070829 | 0.0071083 | 0.0071338 | 0.0071592 | 0.0071847 | 0.0072101 | 0.0072356 | 0.007261 | 0.0072865 | 0.007312 | 0.0073374 | 0.0073629 | 0.0073883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-76447847 | 40 | 40 | 0.0033343 | 0 | 0.0048349 | 0 | 0.0054925 | 0 | 4.2874e-05 | 3.2881e-05 | 0.0046634 | 0.0047063 | 0.0047492 | 0.004792 | 0.0048349 | 0.0048678 | 0.0049007 | 0.0049336 | 0.0049664 | 0.0049993 | 0.0050322 | 0.0050651 | 0.005098 | 0.0051308 | 0.0051637 | 0.0051966 | 0.0052295 | 0.0052624 | 0.0052952 | 0.0053281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-76448158 | 35 | 35 | 0.0043656 | 0 | 0.0061374 | 0 | 0.0070982 | 0 | 5.0624e-05 | 4.804e-05 | 0.005935 | 0.0059856 | 0.0060362 | 0.0060868 | 0.0061374 | 0.0061855 | 0.0062335 | 0.0062816 | 0.0063296 | 0.0063776 | 0.0064257 | 0.0064737 | 0.0065218 | 0.0065698 | 0.0066178 | 0.0066659 | 0.0067139 | 0.006762 | 0.00681 | 0.006858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-76448224 | 44 | 44 | 0.0064465 | 0 | 0.0078944 | 0 | 0.008711 | 0 | 4.1367e-05 | 4.0833e-05 | 0.0077289 | 0.0077703 | 0.0078116 | 0.007853 | 0.0078944 | 0.0079352 | 0.007976 | 0.0080169 | 0.0080577 | 0.0080985 | 0.0081394 | 0.0081802 | 0.008221 | 0.0082619 | 0.0083027 | 0.0083435 | 0.0083844 | 0.0084252 | 0.008466 | 0.0085069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-95132601 | 35 | 35 | 0.0026107 | 0 | 0.003651 | 0 | 0.0039043 | 0 | 2.9722e-05 | 1.2666e-05 | 0.0035321 | 0.0035618 | 0.0035915 | 0.0036212 | 0.003651 | 0.0036636 | 0.0036763 | 0.003689 | 0.0037016 | 0.0037143 | 0.0037269 | 0.0037396 | 0.0037523 | 0.0037649 | 0.0037776 | 0.0037903 | 0.0038029 | 0.0038156 | 0.0038283 | 0.0038409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-95621561 | 6 | 6 | 0.00074243 | 0 | 0.0009986 | 0 | 0.0011817 | 0 | 7.319e-06 | 9.1567e-06 | 0.00096932 | 0.00097664 | 0.00098396 | 0.00099128 | 0.0009986 | 0.0010078 | 0.0010169 | 0.0010261 | 0.0010352 | 0.0010444 | 0.0010535 | 0.0010627 | 0.0010719 | 0.001081 | 0.0010902 | 0.0010993 | 0.0011085 | 0.0011176 | 0.0011268 | 0.0011359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT016-15429893 | 671 | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT017-15429856 | 2067 | 2067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT019-15429808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT020-15429758 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT021-15429734 | 1142 | 1142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT022-15429547 | 1636 | 960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT022-164443534 | 676 | 676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT030-15429658 | 2408 | 2408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT031-15429682 | 368 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH003-137632826 | 46 | 46 | 0.0045623 | 0 | 0.0057148 | 0 | 0.0060934 | 0 | 3.2928e-05 | 1.8931e-05 | 0.0055831 | 0.005616 | 0.0056489 | 0.0056818 | 0.0057148 | 0.0057337 | 0.0057526 | 0.0057716 | 0.0057905 | 0.0058094 | 0.0058284 | 0.0058473 | 0.0058662 | 0.0058851 | 0.0059041 | 0.005923 | 0.0059419 | 0.0059609 | 0.0059798 | 0.0059987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH003-137632841 | 43 | 43 | 0.0011106 | 0 | 0.001566 | 0 | 0.0017419 | 0 | 1.3011e-05 | 8.7955e-06 | 0.0015139 | 0.0015269 | 0.00154 | 0.001553 | 0.001566 | 0.0015748 | 0.0015836 | 0.0015924 | 0.0016012 | 0.00161 | 0.0016188 | 0.0016275 | 0.0016363 | 0.0016451 | 0.0016539 | 0.0016627 | 0.0016715 | 0.0016803 | 0.0016891 | 0.0016979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH003-137632864 | 25 | 25 | 0.0010552 | 0 | 0.0013945 | 0 | 0.0015054 | 0 | 9.6947e-06 | 5.546e-06 | 0.0013557 | 0.0013654 | 0.0013751 | 0.0013848 | 0.0013945 | 0.0014001 | 0.0014056 | 0.0014112 | 0.0014167 | 0.0014223 | 0.0014278 | 0.0014333 | 0.0014389 | 0.0014444 | 0.00145 | 0.0014555 | 0.0014611 | 0.0014666 | 0.0014722 | 0.0014777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH003-137632887 | 15 | 15 | 0.0013615 | 0 | 0.0016861 | 0 | 0.0018261 | 0 | 9.274e-06 | 7.0025e-06 | 0.001649 | 0.0016582 | 0.0016675 | 0.0016768 | 0.0016861 | 0.0016931 | 0.0017001 | 0.0017071 | 0.0017141 | 0.0017211 | 0.0017281 | 0.0017351 | 0.0017421 | 0.0017491 | 0.0017561 | 0.0017631 | 0.0017701 | 0.0017771 | 0.0017841 | 0.0017911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH003-140036206 | 1793 | 1510 | 0.0093896 | 0.0011999 | 0.012016 | 0.0016776 | 0.012612 | 0.001854 | 7.5039e-05 | 2.982e-05 | 0.011716 | 0.011791 | 0.011866 | 0.011941 | 0.012016 | 0.012046 | 0.012076 | 0.012105 | 0.012135 | 0.012165 | 0.012195 | 0.012225 | 0.012255 | 0.012284 | 0.012314 | 0.012344 | 0.012374 | 0.012404 | 0.012433 | 0.012463 | 1.365e-05 | 8.8172e-06 | 0.001623 | 0.0016367 | 0.0016503 | 0.001664 | 0.0016776 | 0.0016864 | 0.0016953 | 0.0017041 | 0.0017129 | 0.0017217 | 0.0017305 | 0.0017393 | 0.0017482 | 0.001757 | 0.0017658 | 0.0017746 | 0.0017834 | 0.0017922 | 0.0018011 | 0.0018099
| BMH003-15408256 | 3676 | 1020 | 0.00027969 | 0.00017795 | 0.00029063 | 0.00018115 | 0.00028106 | 0.00017835 | 3.1243e-07 | -4.7825e-07 | 0.00028938 | 0.00028969 | 0.00029 | 0.00029031 | 0.00029063 | 0.00029015 | 0.00028967 | 0.00028919 | 0.00028871 | 0.00028824 | 0.00028776 | 0.00028728 | 0.0002868 | 0.00028632 | 0.00028584 | 0.00028537 | 0.00028489 | 0.00028441 | 0.00028393 | 0.00028345 | 9.1371e-08 | -1.3985e-07 | 0.00018078 | 0.00018087 | 0.00018097 | 0.00018106 | 0.00018115 | 0.00018101 | 0.00018087 | 0.00018073 | 0.00018059 | 0.00018045 | 0.00018031 | 0.00018017 | 0.00018003 | 0.00017989 | 0.00017975 | 0.00017961 | 0.00017947 | 0.00017933 | 0.00017919 | 0.00017905
| BMH003-155324907 | 26 | 26 | 0.034755 | 0 | 0.046825 | 0 | 0.049868 | 0 | 0.00034484 | 0.00015217 | 0.045445 | 0.04579 | 0.046135 | 0.04648 | 0.046825 | 0.046977 | 0.047129 | 0.047281 | 0.047434 | 0.047586 | 0.047738 | 0.04789 | 0.048042 | 0.048194 | 0.048347 | 0.048499 | 0.048651 | 0.048803 | 0.048955 | 0.049107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH003-24599924 | 19 | 19 | 0.00029466 | 0 | 0.00043096 | 0 | 0.00048875 | 0 | 3.8941e-06 | 2.8896e-06 | 0.00041538 | 0.00041928 | 0.00042317 | 0.00042706 | 0.00043096 | 0.00043385 | 0.00043674 | 0.00043963 | 0.00044252 | 0.00044541 | 0.0004483 | 0.00045119 | 0.00045407 | 0.00045696 | 0.00045985 | 0.00046274 | 0.00046563 | 0.00046852 | 0.00047141 | 0.0004743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH003-24599938 | 2656 | 791 | 0.003904 | 0.0048803 | 0.0059605 | 0.0077258 | 0.0061408 | 0.00802 | 5.8756e-05 | 9.0184e-06 | 0.0057254 | 0.0057842 | 0.0058429 | 0.0059017 | 0.0059605 | 0.0059695 | 0.0059785 | 0.0059875 | 0.0059965 | 0.0060055 | 0.0060146 | 0.0060236 | 0.0060326 | 0.0060416 | 0.0060506 | 0.0060597 | 0.0060687 | 0.0060777 | 0.0060867 | 0.0060957 | 8.1301e-05 | 1.4709e-05 | 0.0074006 | 0.0074819 | 0.0075632 | 0.0076445 | 0.0077258 | 0.0077405 | 0.0077552 | 0.0077699 | 0.0077846 | 0.0077993 | 0.007814 | 0.0078288 | 0.0078435 | 0.0078582 | 0.0078729 | 0.0078876 | 0.0079023 | 0.007917 | 0.0079317 | 0.0079464
| BMH003-54311761 | 261 | 87 | 0.0037248 | 0.0015531 | 0.0048653 | 0.0020488 | 0.0051635 | 0.0021728 | 3.2586e-05 | 1.4906e-05 | 0.004735 | 0.0047676 | 0.0048002 | 0.0048328 | 0.0048653 | 0.0048803 | 0.0048952 | 0.0049101 | 0.004925 | 0.0049399 | 0.0049548 | 0.0049697 | 0.0049846 | 0.0049995 | 0.0050144 | 0.0050293 | 0.0050442 | 0.0050591 | 0.005074 | 0.0050889 | 1.4164e-05 | 6.199e-06 | 0.0019922 | 0.0020063 | 0.0020205 | 0.0020347 | 0.0020488 | 0.002055 | 0.0020612 | 0.0020674 | 0.0020736 | 0.0020798 | 0.002086 | 0.0020922 | 0.0020984 | 0.0021046 | 0.0021108 | 0.002117 | 0.0021232 | 0.0021294 | 0.0021356 | 0.0021418
| BMH003-84023922 | 38 | 38 | 0.00016255 | 0 | 0.00022675 | 0 | 0.00024892 | 0 | 1.8342e-06 | 1.1088e-06 | 0.00021941 | 0.00022124 | 0.00022308 | 0.00022491 | 0.00022675 | 0.00022785 | 0.00022896 | 0.00023007 | 0.00023118 | 0.00023229 | 0.0002334 | 0.00023451 | 0.00023562 | 0.00023673 | 0.00023783 | 0.00023894 | 0.00024005 | 0.00024116 | 0.00024227 | 0.00024338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH003-84426167 | 22 | 22 | 0.0020917 | 0 | 0.0030101 | 0 | 0.0034886 | 0 | 2.6239e-05 | 2.3926e-05 | 0.0029052 | 0.0029314 | 0.0029576 | 0.0029839 | 0.0030101 | 0.003034 | 0.003058 | 0.0030819 | 0.0031058 | 0.0031298 | 0.0031537 | 0.0031776 | 0.0032015 | 0.0032255 | 0.0032494 | 0.0032733 | 0.0032972 | 0.0033212 | 0.0033451 | 0.003369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH004-15408343 | 3727 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH004-15408369 | 3715 | 3715 | 0.014617 | 0 | 0.021583 | 0 | 0.021908 | 0 | 0.00019901 | 1.6262e-05 | 0.020787 | 0.020986 | 0.021185 | 0.021384 | 0.021583 | 0.021599 | 0.021615 | 0.021631 | 0.021648 | 0.021664 | 0.02168 | 0.021696 | 0.021713 | 0.021729 | 0.021745 | 0.021761 | 0.021778 | 0.021794 | 0.02181 | 0.021826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH005-15408219 | 4108 | 1722 | 0.01102 | 0.0017622 | 0.015429 | 0.0027574 | 0.015134 | 0.0027982 | 0.00012597 | -1.4751e-05 | 0.014925 | 0.015051 | 0.015177 | 0.015303 | 0.015429 | 0.015415 | 0.0154 | 0.015385 | 0.01537 | 0.015356 | 0.015341 | 0.015326 | 0.015311 | 0.015297 | 0.015282 | 0.015267 | 0.015252 | 0.015238 | 0.015223 | 0.015208 | 2.8435e-05 | 2.0387e-06 | 0.0026437 | 0.0026721 | 0.0027005 | 0.002729 | 0.0027574 | 0.0027594 | 0.0027615 | 0.0027635 | 0.0027656 | 0.0027676 | 0.0027696 | 0.0027717 | 0.0027737 | 0.0027758 | 0.0027778 | 0.0027798 | 0.0027819 | 0.0027839 | 0.002786 | 0.002788
| BMH005-15408230 | 90 | 90 | 0.0032135 | 0 | 0.0046301 | 0 | 0.0048246 | 0 | 4.0473e-05 | 9.7247e-06 | 0.0044682 | 0.0045087 | 0.0045492 | 0.0045896 | 0.0046301 | 0.0046398 | 0.0046496 | 0.0046593 | 0.004669 | 0.0046787 | 0.0046885 | 0.0046982 | 0.0047079 | 0.0047176 | 0.0047274 | 0.0047371 | 0.0047468 | 0.0047565 | 0.0047663 | 0.004776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH005-65434147 | 2296 | 2296 | 0.002325 | 0 | 0.0038776 | 0 | 0.0040369 | 0 | 4.436e-05 | 7.9679e-06 | 0.0037001 | 0.0037445 | 0.0037888 | 0.0038332 | 0.0038776 | 0.0038855 | 0.0038935 | 0.0039015 | 0.0039094 | 0.0039174 | 0.0039254 | 0.0039333 | 0.0039413 | 0.0039493 | 0.0039572 | 0.0039652 | 0.0039732 | 0.0039811 | 0.0039891 | 0.0039971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH006-15408306 | 929 | 686 | 0.0062446 | 0.0033939 | 0.0083347 | 0.0047173 | 0.0088225 | 0.0050281 | 5.9718e-05 | 2.4392e-05 | 0.0080958 | 0.0081555 | 0.0082153 | 0.008275 | 0.0083347 | 0.0083591 | 0.0083835 | 0.0084079 | 0.0084323 | 0.0084567 | 0.0084811 | 0.0085054 | 0.0085298 | 0.0085542 | 0.0085786 | 0.008603 | 0.0086274 | 0.0086518 | 0.0086762 | 0.0087006 | 3.781e-05 | 1.5541e-05 | 0.004566 | 0.0046038 | 0.0046416 | 0.0046794 | 0.0047173 | 0.0047328 | 0.0047483 | 0.0047639 | 0.0047794 | 0.004795 | 0.0048105 | 0.004826 | 0.0048416 | 0.0048571 | 0.0048727 | 0.0048882 | 0.0049038 | 0.0049193 | 0.0049348 | 0.0049504
| BMH006-201878277 | 228 | 170 | 0.0064862 | 0.0027566 | 0.0088255 | 0.0037173 | 0.0093967 | 0.0039597 | 6.6837e-05 | 2.856e-05 | 0.0085582 | 0.008625 | 0.0086918 | 0.0087587 | 0.0088255 | 0.0088541 | 0.0088826 | 0.0089112 | 0.0089398 | 0.0089683 | 0.0089969 | 0.0090254 | 0.009054 | 0.0090826 | 0.0091111 | 0.0091397 | 0.0091682 | 0.0091968 | 0.0092254 | 0.0092539 | 2.745e-05 | 1.2121e-05 | 0.0036075 | 0.003635 | 0.0036624 | 0.0036899 | 0.0037173 | 0.0037294 | 0.0037416 | 0.0037537 | 0.0037658 | 0.0037779 | 0.00379 | 0.0038022 | 0.0038143 | 0.0038264 | 0.0038385 | 0.0038506 | 0.0038628 | 0.0038749 | 0.003887 | 0.0038991
| BMH006-24602242 | 3 | 3 | 0.0008285 | 0 | 0.0011941 | 0 | 0.0012494 | 0 | 1.0446e-05 | 2.7634e-06 | 0.0011523 | 0.0011628 | 0.0011732 | 0.0011837 | 0.0011941 | 0.0011969 | 0.0011996 | 0.0012024 | 0.0012052 | 0.0012079 | 0.0012107 | 0.0012134 | 0.0012162 | 0.001219 | 0.0012217 | 0.0012245 | 0.0012273 | 0.00123 | 0.0012328 | 0.0012355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH006-74239819 | 15 | 15 | 0.0010213 | 0 | 0.0014289 | 0 | 0.0015232 | 0 | 1.1646e-05 | 4.7135e-06 | 0.0013823 | 0.001394 | 0.0014056 | 0.0014173 | 0.0014289 | 0.0014336 | 0.0014383 | 0.0014431 | 0.0014478 | 0.0014525 | 0.0014572 | 0.0014619 | 0.0014666 | 0.0014713 | 0.001476 | 0.0014808 | 0.0014855 | 0.0014902 | 0.0014949 | 0.0014996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH006-84024816 | 12 | 12 | 0.0014407 | 0 | 0.0020429 | 0 | 0.002188 | 0 | 1.7206e-05 | 7.2543e-06 | 0.0019741 | 0.0019913 | 0.0020085 | 0.0020257 | 0.0020429 | 0.0020502 | 0.0020574 | 0.0020647 | 0.0020719 | 0.0020792 | 0.0020864 | 0.0020937 | 0.0021009 | 0.0021082 | 0.0021154 | 0.0021227 | 0.0021299 | 0.0021372 | 0.0021445 | 0.0021517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH006-85029171 | 25 | 25 | 0.0014663 | 0 | 0.0020576 | 0 | 0.0021487 | 0 | 1.6893e-05 | 4.5588e-06 | 0.00199 | 0.0020069 | 0.0020238 | 0.0020407 | 0.0020576 | 0.0020621 | 0.0020667 | 0.0020712 | 0.0020758 | 0.0020804 | 0.0020849 | 0.0020895 | 0.002094 | 0.0020986 | 0.0021032 | 0.0021077 | 0.0021123 | 0.0021168 | 0.0021214 | 0.002126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH006-85031037 | 18 | 18 | 0.00082891 | 0 | 0.0011626 | 0 | 0.0012082 | 0 | 9.5352e-06 | 2.2786e-06 | 0.0011245 | 0.001134 | 0.0011436 | 0.0011531 | 0.0011626 | 0.0011649 | 0.0011672 | 0.0011695 | 0.0011718 | 0.001174 | 0.0011763 | 0.0011786 | 0.0011809 | 0.0011832 | 0.0011854 | 0.0011877 | 0.00119 | 0.0011923 | 0.0011945 | 0.0011968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-144336613 | 10 | 10 | 0.00043535 | 0 | 0.00045763 | 0 | 0.00044435 | 0 | 6.3651e-07 | -6.642e-07 | 0.00045509 | 0.00045572 | 0.00045636 | 0.000457 | 0.00045763 | 0.00045697 | 0.0004563 | 0.00045564 | 0.00045498 | 0.00045431 | 0.00045365 | 0.00045298 | 0.00045232 | 0.00045165 | 0.00045099 | 0.00045033 | 0.00044966 | 0.000449 | 0.00044833 | 0.00044767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-147732702 | 8 | 8 | 0.00024132 | 0 | 0.00040607 | 0 | 0.00023951 | 0 | 4.7073e-06 | -8.3283e-06 | 0.00038724 | 0.00039195 | 0.00039666 | 0.00040136 | 0.00040607 | 0.00039774 | 0.00038942 | 0.00038109 | 0.00037276 | 0.00036443 | 0.0003561 | 0.00034777 | 0.00033945 | 0.00033112 | 0.00032279 | 0.00031446 | 0.00030613 | 0.0002978 | 0.00028948 | 0.00028115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-147732747 | 8 | 8 | 0.0005331 | 0 | 0.00080817 | 0 | 0.00061205 | 0 | 7.859e-06 | -9.8061e-06 | 0.00077673 | 0.00078459 | 0.00079245 | 0.00080031 | 0.00080817 | 0.00079836 | 0.00078856 | 0.00077875 | 0.00076894 | 0.00075914 | 0.00074933 | 0.00073953 | 0.00072972 | 0.00071991 | 0.00071011 | 0.0007003 | 0.0006905 | 0.00068069 | 0.00067088 | 0.00066108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-15400083 | 1681 | 1051 | 0.0024842 | 0.00093286 | 0.0035074 | 0.0013342 | 0.0028245 | 0.0010665 | 2.9235e-05 | -3.4149e-05 | 0.0033905 | 0.0034197 | 0.003449 | 0.0034782 | 0.0035074 | 0.0034733 | 0.0034391 | 0.003405 | 0.0033709 | 0.0033367 | 0.0033026 | 0.0032684 | 0.0032343 | 0.0032001 | 0.003166 | 0.0031318 | 0.0030977 | 0.0030635 | 0.0030294 | 0.0029952 | 1.1468e-05 | -1.3388e-05 | 0.0012884 | 0.0012998 | 0.0013113 | 0.0013228 | 0.0013342 | 0.0013208 | 0.0013074 | 0.0012941 | 0.0012807 | 0.0012673 | 0.0012539 | 0.0012405 | 0.0012271 | 0.0012137 | 0.0012003 | 0.001187 | 0.0011736 | 0.0011602 | 0.0011468 | 0.0011334
| CDN001-15400094 | 1682 | 1 | 0.00019724 | 9.97e-05 | 0.00030679 | 0.00015 | 0.00023215 | 0.00011594 | 3.13e-06 | -3.7318e-06 | 0.00029427 | 0.0002974 | 0.00030053 | 0.00030366 | 0.00030679 | 0.00030306 | 0.00029933 | 0.00029559 | 0.00029186 | 0.00028813 | 0.0002844 | 0.00028067 | 0.00027693 | 0.0002732 | 0.00026947 | 0.00026574 | 0.00026201 | 0.00025828 | 0.00025454 | 0.00025081 | 1.4371e-06 | -1.7029e-06 | 0.00014425 | 0.00014569 | 0.00014712 | 0.00014856 | 0.00015 | 0.00014829 | 0.00014659 | 0.00014489 | 0.00014319 | 0.00014148 | 0.00013978 | 0.00013808 | 0.00013637 | 0.00013467 | 0.00013297 | 0.00013126 | 0.00012956 | 0.00012786 | 0.00012616 | 0.00012445
| CDN001-154719434 | 17 | 17 | 0.00011459 | 0 | 0.000175 | 0 | 0.00012933 | 0 | 1.7263e-06 | -2.2837e-06 | 0.0001681 | 0.00016983 | 0.00017155 | 0.00017328 | 0.00017501 | 0.00017272 | 0.00017044 | 0.00016815 | 0.00016587 | 0.00016359 | 0.0001613 | 0.00015902 | 0.00015674 | 0.00015445 | 0.00015217 | 0.00014988 | 0.0001476 | 0.00014532 | 0.00014303 | 0.00014075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-156321963 | 611 | 239 | 0.0011157 | 0.0011659 | 0.0017344 | 0.0018537 | 0.0012822 | 0.0013494 | 1.7677e-05 | -2.2608e-05 | 0.0016637 | 0.0016814 | 0.001699 | 0.0017167 | 0.0017344 | 0.0017118 | 0.0016892 | 0.0016666 | 0.001644 | 0.0016213 | 0.0015987 | 0.0015761 | 0.0015535 | 0.0015309 | 0.0015083 | 0.0014857 | 0.0014631 | 0.0014405 | 0.0014179 | 0.0013953 | 1.9653e-05 | -2.5215e-05 | 0.0017751 | 0.0017948 | 0.0018144 | 0.0018341 | 0.0018537 | 0.0018285 | 0.0018033 | 0.0017781 | 0.0017529 | 0.0017277 | 0.0017024 | 0.0016772 | 0.001652 | 0.0016268 | 0.0016016 | 0.0015764 | 0.0015511 | 0.0015259 | 0.0015007 | 0.0014755
| CDN001-158379454 | 23 | 23 | 0.00081128 | 0 | 0.00085729 | 0 | 0.00082986 | 0 | 1.3145e-06 | -1.3716e-06 | 0.00085203 | 0.00085334 | 0.00085466 | 0.00085597 | 0.00085729 | 0.00085592 | 0.00085454 | 0.00085317 | 0.0008518 | 0.00085043 | 0.00084906 | 0.00084769 | 0.00084632 | 0.00084494 | 0.00084357 | 0.0008422 | 0.00084083 | 0.00083946 | 0.00083809 | 0.00083671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-160252941 | 19 | 19 | 3.15e-05 | 0 | 5.31e-05 | 0 | 3.84e-05 | 0 | 6.1714e-07 | -7.35e-07 | 5.0631e-05 | 5.1249e-05 | 5.1866e-05 | 5.2483e-05 | 5.31e-05 | 5.2365e-05 | 5.163e-05 | 5.0895e-05 | 5.016e-05 | 4.9425e-05 | 4.869e-05 | 4.7955e-05 | 4.722e-05 | 4.6485e-05 | 4.575e-05 | 4.5015e-05 | 4.428e-05 | 4.3545e-05 | 4.281e-05 | 4.2075e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-162435420 | 17 | 17 | 1.68e-05 | 0 | 3.32e-05 | 0 | 2e-05 | 0 | 4.6857e-07 | -6.6e-07 | 3.1326e-05 | 3.1794e-05 | 3.2263e-05 | 3.2731e-05 | 3.32e-05 | 3.254e-05 | 3.188e-05 | 3.122e-05 | 3.056e-05 | 2.99e-05 | 2.924e-05 | 2.858e-05 | 2.792e-05 | 2.726e-05 | 2.66e-05 | 2.594e-05 | 2.528e-05 | 2.462e-05 | 2.396e-05 | 2.33e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-162435922 | 9 | 9 | 0.00038044 | 0 | 0.00056109 | 0 | 0.00042993 | 0 | 5.1616e-06 | -6.5581e-06 | 0.00054045 | 0.00054561 | 0.00055077 | 0.00055593 | 0.00056109 | 0.00055454 | 0.00054798 | 0.00054142 | 0.00053486 | 0.0005283 | 0.00052175 | 0.00051519 | 0.00050863 | 0.00050207 | 0.00049551 | 0.00048896 | 0.0004824 | 0.00047584 | 0.00046928 | 0.00046272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-164044162 | 0 | 0 | 0.00033137 | 0 | 0.00035985 | 0 | 0.00032498 | 0 | 8.1374e-07 | -1.7435e-06 | 0.00035659 | 0.00035741 | 0.00035822 | 0.00035903 | 0.00035985 | 0.0003581 | 0.00035636 | 0.00035462 | 0.00035287 | 0.00035113 | 0.00034939 | 0.00034764 | 0.0003459 | 0.00034416 | 0.00034241 | 0.00034067 | 0.00033893 | 0.00033718 | 0.00033544 | 0.0003337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-164044516 | 61 | 41 | 0.00040615 | 0.00043051 | 0.00052189 | 0.00064589 | 0.00040129 | 0.00042306 | 3.3069e-06 | -6.0301e-06 | 0.00050866 | 0.00051197 | 0.00051528 | 0.00051858 | 0.00052189 | 0.00051586 | 0.00050983 | 0.0005038 | 0.00049777 | 0.00049174 | 0.00048571 | 0.00047968 | 0.00047365 | 0.00046762 | 0.00046159 | 0.00045556 | 0.00044953 | 0.0004435 | 0.00043747 | 0.00043144 | 6.1537e-06 | -1.1141e-05 | 0.00062127 | 0.00062742 | 0.00063358 | 0.00063973 | 0.00064588 | 0.00063474 | 0.0006236 | 0.00061246 | 0.00060132 | 0.00059018 | 0.00057904 | 0.0005679 | 0.00055675 | 0.00054561 | 0.00053447 | 0.00052333 | 0.00051219 | 0.00050105 | 0.00048991 | 0.00047876
| CDN001-171348505 | 4 | 4 | 0.00055406 | 0 | 0.0006865 | 0 | 0.00055119 | 0 | 3.7842e-06 | -6.7655e-06 | 0.00067137 | 0.00067515 | 0.00067893 | 0.00068272 | 0.0006865 | 0.00067974 | 0.00067297 | 0.00066621 | 0.00065944 | 0.00065267 | 0.00064591 | 0.00063914 | 0.00063238 | 0.00062561 | 0.00061885 | 0.00061208 | 0.00060532 | 0.00059855 | 0.00059178 | 0.00058502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-177002783 | 10 | 10 | 0.00074318 | 0 | 0.0011713 | 0 | 0.00085695 | 0 | 1.2231e-05 | -1.5717e-05 | 0.0011224 | 0.0011346 | 0.0011468 | 0.001159 | 0.0011713 | 0.0011556 | 0.0011398 | 0.0011241 | 0.0011084 | 0.0010927 | 0.001077 | 0.0010613 | 0.0010455 | 0.0010298 | 0.0010141 | 0.0009984 | 0.00098268 | 0.00096696 | 0.00095125 | 0.00093553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-178141597 | 177 | 82 | 0 | 5.11e-08 | 0 | 5.11e-08 | 0 | 5.11e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08 | 5.11e-08
| CDN001-202076817 | 320 | 143 | 0.00087552 | 0.00019443 | 0.001268 | 0.00030466 | 0.00093607 | 0.00020927 | 1.1214e-05 | -1.6597e-05 | 0.0012231 | 0.0012344 | 0.0012456 | 0.0012568 | 0.001268 | 0.0012514 | 0.0012348 | 0.0012182 | 0.0012016 | 0.001185 | 0.0011684 | 0.0011518 | 0.0011352 | 0.0011186 | 0.001102 | 0.0010854 | 0.0010688 | 0.0010522 | 0.0010356 | 0.0010191 | 3.1496e-06 | -4.7694e-06 | 0.00029206 | 0.00029521 | 0.00029836 | 0.00030151 | 0.00030466 | 0.00029989 | 0.00029512 | 0.00029035 | 0.00028558 | 0.00028081 | 0.00027605 | 0.00027128 | 0.00026651 | 0.00026174 | 0.00025697 | 0.0002522 | 0.00024743 | 0.00024266 | 0.00023789 | 0.00023312
| CDN002-15400020 | 510 | 365 | 0.0022829 | 0.0022006 | 0.0033644 | 0.0033648 | 0.0027295 | 0.002692 | 3.0901e-05 | -3.1745e-05 | 0.0032408 | 0.0032717 | 0.0033026 | 0.0033335 | 0.0033644 | 0.0033327 | 0.003301 | 0.0032692 | 0.0032375 | 0.0032057 | 0.003174 | 0.0031422 | 0.0031105 | 0.0030787 | 0.003047 | 0.0030152 | 0.0029835 | 0.0029518 | 0.00292 | 0.0028883 | 3.3262e-05 | -3.3638e-05 | 0.0032318 | 0.003265 | 0.0032983 | 0.0033315 | 0.0033648 | 0.0033312 | 0.0032975 | 0.0032639 | 0.0032302 | 0.0031966 | 0.003163 | 0.0031293 | 0.0030957 | 0.0030621 | 0.0030284 | 0.0029948 | 0.0029611 | 0.0029275 | 0.0028939 | 0.0028602
| CDN002-15400044 | 510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN002-162961049 | 14 | 14 | 0.00014538 | 0 | 0.00024802 | 0 | 0.00017779 | 0 | 2.9326e-06 | -3.5114e-06 | 0.00023629 | 0.00023922 | 0.00024215 | 0.00024508 | 0.00024802 | 0.00024451 | 0.00024099 | 0.00023748 | 0.00023397 | 0.00023046 | 0.00022695 | 0.00022344 | 0.00021993 | 0.00021641 | 0.0002129 | 0.00020939 | 0.00020588 | 0.00020237 | 0.00019886 | 0.00019535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN002-162961261 | 6 | 6 | 1.43e-05 | 0 | 2.56e-05 | 0 | 2.05e-05 | 0 | 3.2286e-07 | -2.55e-07 | 2.4309e-05 | 2.4631e-05 | 2.4954e-05 | 2.5277e-05 | 2.56e-05 | 2.5345e-05 | 2.509e-05 | 2.4835e-05 | 2.458e-05 | 2.4325e-05 | 2.407e-05 | 2.3815e-05 | 2.356e-05 | 2.3305e-05 | 2.305e-05 | 2.2795e-05 | 2.254e-05 | 2.2285e-05 | 2.203e-05 | 2.1775e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN002-162961458 | 2 | 2 | 0.00028248 | 0 | 0.00047952 | 0 | 0.00038799 | 0 | 5.6298e-06 | -4.5766e-06 | 0.000457 | 0.00046263 | 0.00046826 | 0.00047389 | 0.00047952 | 0.00047494 | 0.00047037 | 0.00046579 | 0.00046121 | 0.00045664 | 0.00045206 | 0.00044748 | 0.00044291 | 0.00043833 | 0.00043375 | 0.00042918 | 0.0004246 | 0.00042002 | 0.00041545 | 0.00041087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN002-163179235 | 12 | 12 | 0.0010823 | 0 | 0.0015419 | 0 | 0.0012043 | 0 | 1.3131e-05 | -1.688e-05 | 0.0014894 | 0.0015025 | 0.0015157 | 0.0015288 | 0.0015419 | 0.001525 | 0.0015082 | 0.0014913 | 0.0014744 | 0.0014575 | 0.0014406 | 0.0014238 | 0.0014069 | 0.00139 | 0.0013731 | 0.0013562 | 0.0013394 | 0.0013225 | 0.0013056 | 0.0012887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN002-163194789 | 1 | 1 | 1.06e-05 | 0 | 1.84e-05 | 0 | 1.31e-05 | 0 | 2.2286e-07 | -2.65e-07 | 1.7509e-05 | 1.7731e-05 | 1.7954e-05 | 1.8177e-05 | 1.84e-05 | 1.8135e-05 | 1.787e-05 | 1.7605e-05 | 1.734e-05 | 1.7075e-05 | 1.681e-05 | 1.6545e-05 | 1.628e-05 | 1.6015e-05 | 1.575e-05 | 1.5485e-05 | 1.522e-05 | 1.4955e-05 | 1.469e-05 | 1.4425e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN002-163309826 | 5 | 5 | 0.0022307 | 0 | 0.0037729 | 0 | 0.0029738 | 0 | 4.4065e-05 | -3.9955e-05 | 0.0035967 | 0.0036407 | 0.0036848 | 0.0037289 | 0.0037729 | 0.003733 | 0.003693 | 0.0036531 | 0.0036131 | 0.0035732 | 0.0035332 | 0.0034932 | 0.0034533 | 0.0034133 | 0.0033734 | 0.0033334 | 0.0032935 | 0.0032535 | 0.0032136 | 0.0031736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN002-85030215 | 128 | 105 | 0.0016938 | 0.00033279 | 0.0027882 | 0.00061086 | 0.0020638 | 0.00043045 | 3.1269e-05 | -3.6217e-05 | 0.0026631 | 0.0026944 | 0.0027256 | 0.0027569 | 0.0027882 | 0.002752 | 0.0027157 | 0.0026795 | 0.0026433 | 0.0026071 | 0.0025709 | 0.0025347 | 0.0024984 | 0.0024622 | 0.002426 | 0.0023898 | 0.0023536 | 0.0023173 | 0.0022811 | 0.0022449 | 7.9447e-06 | -9.0203e-06 | 0.00057908 | 0.00058702 | 0.00059497 | 0.00060291 | 0.00061086 | 0.00060184 | 0.00059282 | 0.0005838 | 0.00057478 | 0.00056576 | 0.00055674 | 0.00054772 | 0.0005387 | 0.00052968 | 0.00052066 | 0.00051164 | 0.00050261 | 0.00049359 | 0.00048457 | 0.00047555
| CDN003-15400133 | 1722 | 1722 | 0.00052533 | 0 | 0.00070549 | 0 | 0.00057624 | 0 | 5.1475e-06 | -6.4626e-06 | 0.0006849 | 0.00069005 | 0.00069519 | 0.00070034 | 0.00070549 | 0.00069903 | 0.00069256 | 0.0006861 | 0.00067964 | 0.00067318 | 0.00066671 | 0.00066025 | 0.00065379 | 0.00064733 | 0.00064086 | 0.0006344 | 0.00062794 | 0.00062147 | 0.00061501 | 0.00060855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN004-139244393 | 16 | 16 | 7.5e-05 | 0 | 0.00013083 | 0 | 0.00012838 | 0 | 1.5951e-06 | -1.222e-07 | 0.00012445 | 0.00012604 | 0.00012764 | 0.00012923 | 0.00013083 | 0.0001307 | 0.00013058 | 0.00013046 | 0.00013034 | 0.00013022 | 0.00013009 | 0.00012997 | 0.00012985 | 0.00012973 | 0.0001296 | 0.00012948 | 0.00012936 | 0.00012924 | 0.00012912 | 0.00012899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN004-139244670 | 61 | 61 | 0.0011101 | 0 | 0.0017062 | 0 | 0.0015031 | 0 | 1.7033e-05 | -1.0156e-05 | 0.0016381 | 0.0016551 | 0.0016722 | 0.0016892 | 0.0017062 | 0.0016961 | 0.0016859 | 0.0016758 | 0.0016656 | 0.0016555 | 0.0016453 | 0.0016351 | 0.001625 | 0.0016148 | 0.0016047 | 0.0015945 | 0.0015844 | 0.0015742 | 0.0015641 | 0.0015539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN004-139351301 | 9 | 9 | 0.00022678 | 0 | 0.00036223 | 0 | 0.00032734 | 0 | 3.87e-06 | -1.7445e-06 | 0.00034675 | 0.00035062 | 0.00035449 | 0.00035836 | 0.00036223 | 0.00036049 | 0.00035874 | 0.000357 | 0.00035525 | 0.00035351 | 0.00035176 | 0.00035002 | 0.00034827 | 0.00034653 | 0.00034479 | 0.00034304 | 0.0003413 | 0.00033955 | 0.00033781 | 0.00033606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN004-142953493 | 16 | 16 | 0.00042596 | 0 | 0.00061058 | 0 | 0.00051993 | 0 | 5.2749e-06 | -4.5324e-06 | 0.00058948 | 0.00059475 | 0.00060003 | 0.0006053 | 0.00061058 | 0.00060604 | 0.00060151 | 0.00059698 | 0.00059245 | 0.00058791 | 0.00058338 | 0.00057885 | 0.00057432 | 0.00056979 | 0.00056525 | 0.00056072 | 0.00055619 | 0.00055166 | 0.00054712 | 0.00054259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN004-15399970 | 787 | 118 | 0.0019188 | 0.00018711 | 0.002635 | 0.00026046 | 0.0020906 | 0.0002044 | 2.0465e-05 | -2.7221e-05 | 0.0025532 | 0.0025736 | 0.0025941 | 0.0026146 | 0.002635 | 0.0026078 | 0.0025806 | 0.0025534 | 0.0025262 | 0.0024989 | 0.0024717 | 0.0024445 | 0.0024173 | 0.0023901 | 0.0023628 | 0.0023356 | 0.0023084 | 0.0022812 | 0.002254 | 0.0022267 | 2.0957e-06 | -2.8027e-06 | 0.00025207 | 0.00025417 | 0.00025627 | 0.00025836 | 0.00026046 | 0.00025765 | 0.00025485 | 0.00025205 | 0.00024925 | 0.00024644 | 0.00024364 | 0.00024084 | 0.00023804 | 0.00023523 | 0.00023243 | 0.00022963 | 0.00022683 | 0.00022402 | 0.00022122 | 0.00021842
| CDN004-159428859 | 5 | 5 | 0.00025703 | 0 | 0.0003653 | 0 | 0.00033698 | 0 | 3.0933e-06 | -1.4158e-06 | 0.00035292 | 0.00035602 | 0.00035911 | 0.0003622 | 0.0003653 | 0.00036388 | 0.00036247 | 0.00036105 | 0.00035963 | 0.00035822 | 0.0003568 | 0.00035539 | 0.00035397 | 0.00035256 | 0.00035114 | 0.00034972 | 0.00034831 | 0.00034689 | 0.00034548 | 0.00034406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN004-159428956 | 26 | 26 | 0.0001898 | 0 | 0.00026918 | 0 | 0.00024352 | 0 | 2.268e-06 | -1.2829e-06 | 0.0002601 | 0.00026237 | 0.00026464 | 0.00026691 | 0.00026918 | 0.00026789 | 0.00026661 | 0.00026533 | 0.00026404 | 0.00026276 | 0.00026148 | 0.0002602 | 0.00025891 | 0.00025763 | 0.00025635 | 0.00025506 | 0.00025378 | 0.0002525 | 0.00025121 | 0.00024993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN004-159429052 | 8 | 8 | 6.81e-05 | 0 | 6.91e-05 | 0 | 6.85e-05 | 0 | 2.8571e-08 | -3e-08 | 6.8986e-05 | 6.9014e-05 | 6.9043e-05 | 6.9071e-05 | 6.91e-05 | 6.907e-05 | 6.904e-05 | 6.901e-05 | 6.898e-05 | 6.895e-05 | 6.892e-05 | 6.889e-05 | 6.886e-05 | 6.883e-05 | 6.88e-05 | 6.877e-05 | 6.874e-05 | 6.871e-05 | 6.868e-05 | 6.865e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN004-162436765 | 35 | 35 | 7.76e-05 | 0 | 0.00011882 | 0 | 0.00010552 | 0 | 1.1777e-06 | -6.6485e-07 | 0.00011411 | 0.00011529 | 0.00011647 | 0.00011764 | 0.00011882 | 0.00011816 | 0.00011749 | 0.00011683 | 0.00011616 | 0.0001155 | 0.00011483 | 0.00011417 | 0.0001135 | 0.00011284 | 0.00011217 | 0.00011151 | 0.00011084 | 0.00011018 | 0.00010951 | 0.00010885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN004-202037935 | 608 | 63 | 0.00062826 | 0.0004804 | 0.00080709 | 0.00063947 | 0.00082959 | 0.00065519 | 5.1096e-06 | 1.1246e-06 | 0.00078666 | 0.00079177 | 0.00079687 | 0.00080198 | 0.00080709 | 0.00080822 | 0.00080934 | 0.00081047 | 0.00081159 | 0.00081272 | 0.00081384 | 0.00081497 | 0.00081609 | 0.00081722 | 0.00081834 | 0.00081946 | 0.00082059 | 0.00082171 | 0.00082284 | 0.00082396 | 4.5449e-06 | 7.861e-07 | 0.00062129 | 0.00062584 | 0.00063038 | 0.00063493 | 0.00063947 | 0.00064026 | 0.00064104 | 0.00064183 | 0.00064261 | 0.0006434 | 0.00064419 | 0.00064497 | 0.00064576 | 0.00064654 | 0.00064733 | 0.00064812 | 0.0006489 | 0.00064969 | 0.00065048 | 0.00065126
| CDN004-202768387 | 496 | 430 | 0.0021366 | 0.00029058 | 0.0030822 | 0.00044745 | 0.0028769 | 0.00041598 | 2.7017e-05 | -1.0264e-05 | 0.0029741 | 0.0030012 | 0.0030282 | 0.0030552 | 0.0030822 | 0.003072 | 0.0030617 | 0.0030514 | 0.0030412 | 0.0030309 | 0.0030206 | 0.0030104 | 0.0030001 | 0.0029898 | 0.0029796 | 0.0029693 | 0.0029591 | 0.0029488 | 0.0029385 | 0.0029283 | 4.4819e-06 | -1.5732e-06 | 0.00042952 | 0.000434 | 0.00043848 | 0.00044297 | 0.00044745 | 0.00044587 | 0.0004443 | 0.00044273 | 0.00044115 | 0.00043958 | 0.00043801 | 0.00043643 | 0.00043486 | 0.00043329 | 0.00043171 | 0.00043014 | 0.00042857 | 0.000427 | 0.00042542 | 0.00042385
| CDN006-143338433 | 29 | 29 | 0.00046825 | 0 | 0.00066836 | 0 | 0.00062415 | 0 | 5.7175e-06 | -2.2105e-06 | 0.00064549 | 0.00065121 | 0.00065692 | 0.00066264 | 0.00066836 | 0.00066615 | 0.00066394 | 0.00066173 | 0.00065952 | 0.00065731 | 0.0006551 | 0.00065288 | 0.00065067 | 0.00064846 | 0.00064625 | 0.00064404 | 0.00064183 | 0.00063962 | 0.00063741 | 0.0006352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-143338709 | 46 | 46 | 5.97e-05 | 0 | 8.86e-05 | 0 | 8.33e-05 | 0 | 8.2571e-07 | -2.65e-07 | 8.5297e-05 | 8.6123e-05 | 8.6949e-05 | 8.7774e-05 | 8.86e-05 | 8.8335e-05 | 8.807e-05 | 8.7805e-05 | 8.754e-05 | 8.7275e-05 | 8.701e-05 | 8.6745e-05 | 8.648e-05 | 8.6215e-05 | 8.595e-05 | 8.5685e-05 | 8.542e-05 | 8.5155e-05 | 8.489e-05 | 8.4625e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-143338924 | 12 | 12 | 1.57e-05 | 0 | 2.43e-05 | 0 | 2.19e-05 | 0 | 2.4571e-07 | -1.2e-07 | 2.3317e-05 | 2.3563e-05 | 2.3809e-05 | 2.4054e-05 | 2.43e-05 | 2.418e-05 | 2.406e-05 | 2.394e-05 | 2.382e-05 | 2.37e-05 | 2.358e-05 | 2.346e-05 | 2.334e-05 | 2.322e-05 | 2.31e-05 | 2.298e-05 | 2.286e-05 | 2.274e-05 | 2.262e-05 | 2.25e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-143339149 | 7 | 7 | 0.00050747 | 0 | 0.00066911 | 0 | 0.00058408 | 0 | 4.6184e-06 | -4.2515e-06 | 0.00065064 | 0.00065525 | 0.00065987 | 0.00066449 | 0.00066911 | 0.00066486 | 0.00066061 | 0.00065635 | 0.0006521 | 0.00064785 | 0.0006436 | 0.00063935 | 0.0006351 | 0.00063085 | 0.00062659 | 0.00062234 | 0.00061809 | 0.00061384 | 0.00060959 | 0.00060534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-15399920 | 987 | 261 | 0.0011166 | 0.00062809 | 0.0015998 | 0.00091859 | 0.0012272 | 0.00069431 | 1.3806e-05 | -1.8627e-05 | 0.0015446 | 0.0015584 | 0.0015722 | 0.001586 | 0.0015998 | 0.0015812 | 0.0015625 | 0.0015439 | 0.0015253 | 0.0015067 | 0.001488 | 0.0014694 | 0.0014508 | 0.0014321 | 0.0014135 | 0.0013949 | 0.0013763 | 0.0013576 | 0.001339 | 0.0013204 | 8.3001e-06 | -1.1214e-05 | 0.00088539 | 0.00089369 | 0.00090199 | 0.00091029 | 0.00091859 | 0.00090738 | 0.00089616 | 0.00088495 | 0.00087374 | 0.00086252 | 0.00085131 | 0.00084009 | 0.00082888 | 0.00081767 | 0.00080645 | 0.00079524 | 0.00078402 | 0.00077281 | 0.0007616 | 0.00075038
| CDN006-158379713 | 35 | 35 | 0.00030815 | 0 | 0.00045667 | 0 | 0.0004276 | 0 | 4.2434e-06 | -1.4536e-06 | 0.00043969 | 0.00044394 | 0.00044818 | 0.00045242 | 0.00045667 | 0.00045521 | 0.00045376 | 0.00045231 | 0.00045085 | 0.0004494 | 0.00044795 | 0.00044649 | 0.00044504 | 0.00044359 | 0.00044213 | 0.00044068 | 0.00043923 | 0.00043777 | 0.00043632 | 0.00043486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-158379840 | 14 | 14 | 0.00020078 | 0 | 0.00031316 | 0 | 0.00029124 | 0 | 3.2107e-06 | -1.096e-06 | 0.00030031 | 0.00030352 | 0.00030674 | 0.00030995 | 0.00031316 | 0.00031206 | 0.00031096 | 0.00030987 | 0.00030877 | 0.00030768 | 0.00030658 | 0.00030548 | 0.00030439 | 0.00030329 | 0.0003022 | 0.0003011 | 0.0003 | 0.00029891 | 0.00029781 | 0.00029672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-160451043 | 27 | 27 | 0.0003439 | 0 | 0.00053357 | 0 | 0.00049964 | 0 | 5.4191e-06 | -1.6968e-06 | 0.0005119 | 0.00051731 | 0.00052273 | 0.00052815 | 0.00053357 | 0.00053188 | 0.00053018 | 0.00052848 | 0.00052678 | 0.00052509 | 0.00052339 | 0.00052169 | 0.00052 | 0.0005183 | 0.0005166 | 0.00051491 | 0.00051321 | 0.00051151 | 0.00050982 | 0.00050812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-162450281 | 6 | 6 | 1.86e-06 | 0 | 3.47e-06 | 0 | 3.26e-06 | 0 | 4.6e-08 | -1.05e-08 | 3.286e-06 | 3.332e-06 | 3.378e-06 | 3.424e-06 | 3.47e-06 | 3.4595e-06 | 3.449e-06 | 3.4385e-06 | 3.428e-06 | 3.4175e-06 | 3.407e-06 | 3.3965e-06 | 3.386e-06 | 3.3755e-06 | 3.365e-06 | 3.3545e-06 | 3.344e-06 | 3.3335e-06 | 3.323e-06 | 3.3125e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-162451240 | 3 | 3 | 0.00014932 | 0 | 0.00021765 | 0 | 0.00018868 | 0 | 1.9521e-06 | -1.4483e-06 | 0.00020984 | 0.00021179 | 0.00021374 | 0.00021569 | 0.00021765 | 0.0002162 | 0.00021475 | 0.0002133 | 0.00021185 | 0.0002104 | 0.00020896 | 0.00020751 | 0.00020606 | 0.00020461 | 0.00020316 | 0.00020171 | 0.00020027 | 0.00019882 | 0.00019737 | 0.00019592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-162572514 | 2 | 2 | 3.44e-05 | 0 | 3.44e-05 | 0 | 3.44e-05 | 0 | 0 | 0 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 3.44e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-162572817 | 4 | 4 | 8.97e-06 | 0 | 1.54e-05 | 0 | 1.13e-05 | 0 | 1.8371e-07 | -2.05e-07 | 1.4665e-05 | 1.4849e-05 | 1.5033e-05 | 1.5216e-05 | 1.54e-05 | 1.5195e-05 | 1.499e-05 | 1.4785e-05 | 1.458e-05 | 1.4375e-05 | 1.417e-05 | 1.3965e-05 | 1.376e-05 | 1.3555e-05 | 1.335e-05 | 1.3145e-05 | 1.294e-05 | 1.2735e-05 | 1.253e-05 | 1.2325e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-162588679 | 7 | 7 | 0.00033448 | 0 | 0.00053357 | 0 | 0.000375 | 0 | 5.6884e-06 | -7.9286e-06 | 0.00051082 | 0.00051651 | 0.0005222 | 0.00052788 | 0.00053357 | 0.00052564 | 0.00051771 | 0.00050979 | 0.00050186 | 0.00049393 | 0.000486 | 0.00047807 | 0.00047014 | 0.00046221 | 0.00045429 | 0.00044636 | 0.00043843 | 0.0004305 | 0.00042257 | 0.00041464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-162675220 | 10 | 10 | 1.05e-06 | 0 | 1.63e-06 | 0 | 1.32e-06 | 0 | 1.6571e-08 | -1.55e-08 | 1.5637e-06 | 1.5803e-06 | 1.5969e-06 | 1.6134e-06 | 1.63e-06 | 1.6145e-06 | 1.599e-06 | 1.5835e-06 | 1.568e-06 | 1.5525e-06 | 1.537e-06 | 1.5215e-06 | 1.506e-06 | 1.4905e-06 | 1.475e-06 | 1.4595e-06 | 1.444e-06 | 1.4285e-06 | 1.413e-06 | 1.3975e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-162675596 | 2 | 2 | 1.31e-06 | 0 | 2.36e-06 | 0 | 2.17e-06 | 0 | 3e-08 | -9.5e-09 | 2.24e-06 | 2.27e-06 | 2.3e-06 | 2.33e-06 | 2.36e-06 | 2.3505e-06 | 2.341e-06 | 2.3315e-06 | 2.322e-06 | 2.3125e-06 | 2.303e-06 | 2.2935e-06 | 2.284e-06 | 2.2745e-06 | 2.265e-06 | 2.2555e-06 | 2.246e-06 | 2.2365e-06 | 2.227e-06 | 2.2175e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-183157401 | 8 | 8 | 1.27e-05 | 0 | 2.23e-05 | 0 | 1.49e-05 | 0 | 2.7429e-07 | -3.7e-07 | 2.1203e-05 | 2.1477e-05 | 2.1751e-05 | 2.2026e-05 | 2.23e-05 | 2.193e-05 | 2.156e-05 | 2.119e-05 | 2.082e-05 | 2.045e-05 | 2.008e-05 | 1.971e-05 | 1.934e-05 | 1.897e-05 | 1.86e-05 | 1.823e-05 | 1.786e-05 | 1.749e-05 | 1.712e-05 | 1.675e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN006-202038054 | 555 | 391 | 0.0013867 | 0.00035385 | 0.0018301 | 0.00049709 | 0.001731 | 0.00046531 | 1.2669e-05 | -4.9559e-06 | 0.0017794 | 0.0017921 | 0.0018048 | 0.0018175 | 0.0018301 | 0.0018252 | 0.0018202 | 0.0018153 | 0.0018103 | 0.0018053 | 0.0018004 | 0.0017954 | 0.0017905 | 0.0017855 | 0.0017806 | 0.0017756 | 0.0017707 | 0.0017657 | 0.0017607 | 0.0017558 | 4.0926e-06 | -1.5893e-06 | 0.00048072 | 0.00048481 | 0.00048891 | 0.000493 | 0.00049709 | 0.0004955 | 0.00049391 | 0.00049232 | 0.00049073 | 0.00048915 | 0.00048756 | 0.00048597 | 0.00048438 | 0.00048279 | 0.0004812 | 0.00047961 | 0.00047802 | 0.00047643 | 0.00047484 | 0.00047325
| CDN006-202248649 | 707 | 123 | 0.0013532 | 0.00043916 | 0.0019192 | 0.00061907 | 0.0017213 | 0.00055457 | 1.6171e-05 | -9.895e-06 | 0.0018545 | 0.0018707 | 0.0018868 | 0.001903 | 0.0019192 | 0.0019093 | 0.0018994 | 0.0018895 | 0.0018796 | 0.0018697 | 0.0018598 | 0.0018499 | 0.00184 | 0.0018301 | 0.0018202 | 0.0018103 | 0.0018004 | 0.0017905 | 0.0017807 | 0.0017708 | 5.1403e-06 | -3.2252e-06 | 0.00059851 | 0.00060365 | 0.00060879 | 0.00061393 | 0.00061907 | 0.00061585 | 0.00061262 | 0.0006094 | 0.00060617 | 0.00060295 | 0.00059972 | 0.00059649 | 0.00059327 | 0.00059004 | 0.00058682 | 0.00058359 | 0.00058037 | 0.00057714 | 0.00057392 | 0.00057069
| CHA003-15429144 | 1208 | 976 | 0.0017842 | 0.00061692 | 0.0023906 | 0.00084393 | 0.0028677 | 0.0010367 | 1.7326e-05 | 2.3853e-05 | 0.0023213 | 0.0023387 | 0.002356 | 0.0023733 | 0.0023906 | 0.0024145 | 0.0024383 | 0.0024622 | 0.002486 | 0.0025099 | 0.0025338 | 0.0025576 | 0.0025815 | 0.0026053 | 0.0026292 | 0.002653 | 0.0026769 | 0.0027007 | 0.0027246 | 0.0027484 | 6.486e-06 | 9.6366e-06 | 0.00081798 | 0.00082447 | 0.00083095 | 0.00083744 | 0.00084393 | 0.00085356 | 0.0008632 | 0.00087284 | 0.00088247 | 0.00089211 | 0.00090175 | 0.00091138 | 0.00092102 | 0.00093065 | 0.00094029 | 0.00094993 | 0.00095956 | 0.0009692 | 0.00097884 | 0.00098847
| CHA003-155052833 | 8 | 8 | 2.69e-05 | 0 | 3.7e-05 | 0 | 4.59e-05 | 0 | 2.8857e-07 | 4.45e-07 | 3.5846e-05 | 3.6134e-05 | 3.6423e-05 | 3.6711e-05 | 3.7e-05 | 3.7445e-05 | 3.789e-05 | 3.8335e-05 | 3.878e-05 | 3.9225e-05 | 3.967e-05 | 4.0115e-05 | 4.056e-05 | 4.1005e-05 | 4.145e-05 | 4.1895e-05 | 4.234e-05 | 4.2785e-05 | 4.323e-05 | 4.3675e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA003-155052965 | 1 | 1 | 0.00067057 | 0 | 0.00090461 | 0 | 0.0011261 | 0 | 6.687e-06 | 1.1075e-05 | 0.00087787 | 0.00088455 | 0.00089124 | 0.00089793 | 0.00090461 | 0.00091569 | 0.00092676 | 0.00093784 | 0.00094891 | 0.00095999 | 0.00097106 | 0.00098214 | 0.00099321 | 0.0010043 | 0.0010154 | 0.0010264 | 0.0010375 | 0.0010486 | 0.0010597 | 0.0010707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA003-24606706 | 224 | 223 | 0.008875 | 0.0003282 | 0.01117 | 0.00045204 | 0.012907 | 0.00056063 | 6.5579e-05 | 8.6832e-05 | 0.010908 | 0.010974 | 0.011039 | 0.011105 | 0.01117 | 0.011257 | 0.011344 | 0.011431 | 0.011518 | 0.011604 | 0.011691 | 0.011778 | 0.011865 | 0.011952 | 0.012039 | 0.012125 | 0.012212 | 0.012299 | 0.012386 | 0.012473 | 3.5385e-06 | 5.4295e-06 | 0.00043789 | 0.00044143 | 0.00044497 | 0.00044851 | 0.00045204 | 0.00045747 | 0.0004629 | 0.00046833 | 0.00047376 | 0.00047919 | 0.00048462 | 0.00049005 | 0.00049548 | 0.00050091 | 0.00050634 | 0.00051177 | 0.0005172 | 0.00052263 | 0.00052806 | 0.00053349
| CHA005-15429107 | 1341 | 332 | 0.0025924 | 0.0036857 | 0.0034188 | 0.0050287 | 0.0040268 | 0.0062212 | 2.3613e-05 | 3.0399e-05 | 0.0033244 | 0.003348 | 0.0033716 | 0.0033952 | 0.0034188 | 0.0034492 | 0.0034796 | 0.00351 | 0.0035404 | 0.0035708 | 0.0036012 | 0.0036316 | 0.003662 | 0.0036924 | 0.0037228 | 0.0037532 | 0.0037836 | 0.003814 | 0.0038444 | 0.0038748 | 3.8373e-05 | 5.9626e-05 | 0.0048752 | 0.0049136 | 0.004952 | 0.0049903 | 0.0050287 | 0.0050883 | 0.005148 | 0.0052076 | 0.0052672 | 0.0053269 | 0.0053865 | 0.0054461 | 0.0055057 | 0.0055654 | 0.005625 | 0.0056846 | 0.0057442 | 0.0058039 | 0.0058635 | 0.0059231
| CHA005-155053189 | 9 | 9 | 2.92e-05 | 0 | 4.06e-05 | 0 | 5.08e-05 | 0 | 3.2571e-07 | 5.1e-07 | 3.9297e-05 | 3.9623e-05 | 3.9949e-05 | 4.0274e-05 | 4.06e-05 | 4.111e-05 | 4.162e-05 | 4.213e-05 | 4.264e-05 | 4.315e-05 | 4.366e-05 | 4.417e-05 | 4.468e-05 | 4.519e-05 | 4.57e-05 | 4.621e-05 | 4.672e-05 | 4.723e-05 | 4.774e-05 | 4.825e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA005-24606076 | 903 | 428 | 0.024089 | 0.0040734 | 0.030294 | 0.0050564 | 0.034101 | 0.0054978 | 0.00017728 | 0.00019034 | 0.029585 | 0.029762 | 0.02994 | 0.030117 | 0.030294 | 0.030484 | 0.030675 | 0.030865 | 0.031055 | 0.031246 | 0.031436 | 0.031626 | 0.031817 | 0.032007 | 0.032198 | 0.032388 | 0.032578 | 0.032769 | 0.032959 | 0.033149 | 2.8085e-05 | 2.2071e-05 | 0.0049441 | 0.0049721 | 0.0050002 | 0.0050283 | 0.0050564 | 0.0050785 | 0.0051005 | 0.0051226 | 0.0051447 | 0.0051668 | 0.0051888 | 0.0052109 | 0.005233 | 0.005255 | 0.0052771 | 0.0052992 | 0.0053213 | 0.0053433 | 0.0053654 | 0.0053875
| CHA005-24606160 | 101 | 101 | 0.0066263 | 0 | 0.0086461 | 0 | 0.0099663 | 0 | 5.7709e-05 | 6.6008e-05 | 0.0084153 | 0.008473 | 0.0085307 | 0.0085884 | 0.0086461 | 0.0087121 | 0.0087781 | 0.0088441 | 0.0089101 | 0.0089761 | 0.0090422 | 0.0091082 | 0.0091742 | 0.0092402 | 0.0093062 | 0.0093722 | 0.0094382 | 0.0095042 | 0.0095702 | 0.0096362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA005-53118475 | 66 | 66 | 0.0083524 | 0 | 0.010661 | 0 | 0.011973 | 0 | 6.5968e-05 | 6.5575e-05 | 0.010397 | 0.010463 | 0.010529 | 0.010595 | 0.010661 | 0.010727 | 0.010792 | 0.010858 | 0.010924 | 0.010989 | 0.011055 | 0.01112 | 0.011186 | 0.011251 | 0.011317 | 0.011383 | 0.011448 | 0.011514 | 0.011579 | 0.011645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA005-56709738 | 97 | 97 | 0.0012431 | 0 | 0.0017213 | 0 | 0.0020588 | 0 | 1.3664e-05 | 1.6876e-05 | 0.0016667 | 0.0016803 | 0.001694 | 0.0017077 | 0.0017213 | 0.0017382 | 0.0017551 | 0.001772 | 0.0017888 | 0.0018057 | 0.0018226 | 0.0018395 | 0.0018563 | 0.0018732 | 0.0018901 | 0.001907 | 0.0019238 | 0.0019407 | 0.0019576 | 0.0019745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA005-56710238 | 308 | 308 | 0.048241 | 0 | 0.061041 | 0 | 0.067021 | 0 | 0.00036571 | 0.000299 | 0.059579 | 0.059944 | 0.06031 | 0.060676 | 0.061041 | 0.06134 | 0.061639 | 0.061938 | 0.062237 | 0.062536 | 0.062835 | 0.063134 | 0.063433 | 0.063732 | 0.064031 | 0.06433 | 0.064629 | 0.064928 | 0.065227 | 0.065526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-120251163 | 48 | 48 | 0.0018658 | 0 | 0.0023799 | 0 | 0.0027071 | 0 | 1.4688e-05 | 1.636e-05 | 0.0023211 | 0.0023358 | 0.0023505 | 0.0023652 | 0.0023799 | 0.0023962 | 0.0024126 | 0.0024289 | 0.0024453 | 0.0024617 | 0.002478 | 0.0024944 | 0.0025107 | 0.0025271 | 0.0025435 | 0.0025598 | 0.0025762 | 0.0025925 | 0.0026089 | 0.0026253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-130745345 | 19 | 19 | 2.27e-05 | 0 | 2.92e-05 | 0 | 3.5e-05 | 0 | 1.8571e-07 | 2.9e-07 | 2.8457e-05 | 2.8643e-05 | 2.8829e-05 | 2.9014e-05 | 2.92e-05 | 2.949e-05 | 2.978e-05 | 3.007e-05 | 3.036e-05 | 3.065e-05 | 3.094e-05 | 3.123e-05 | 3.152e-05 | 3.181e-05 | 3.21e-05 | 3.239e-05 | 3.268e-05 | 3.297e-05 | 3.326e-05 | 3.355e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-138134893 | 19 | 19 | 8.13e-06 | 0 | 1.16e-05 | 0 | 1.29e-05 | 0 | 9.9143e-08 | 6.5e-08 | 1.1203e-05 | 1.1303e-05 | 1.1402e-05 | 1.1501e-05 | 1.16e-05 | 1.1665e-05 | 1.173e-05 | 1.1795e-05 | 1.186e-05 | 1.1925e-05 | 1.199e-05 | 1.2055e-05 | 1.212e-05 | 1.2185e-05 | 1.225e-05 | 1.2315e-05 | 1.238e-05 | 1.2445e-05 | 1.251e-05 | 1.2575e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-15429283 | 1854 | 480 | 0.003122 | 0.0024039 | 0.0040104 | 0.003281 | 0.0046408 | 0.004018 | 2.5382e-05 | 3.1521e-05 | 0.0039088 | 0.0039342 | 0.0039596 | 0.003985 | 0.0040104 | 0.0040419 | 0.0040734 | 0.0041049 | 0.0041365 | 0.004168 | 0.0041995 | 0.004231 | 0.0042625 | 0.0042941 | 0.0043256 | 0.0043571 | 0.0043886 | 0.0044201 | 0.0044517 | 0.0044832 | 2.506e-05 | 3.6847e-05 | 0.0031808 | 0.0032059 | 0.0032309 | 0.003256 | 0.003281 | 0.0033179 | 0.0033547 | 0.0033916 | 0.0034284 | 0.0034653 | 0.0035021 | 0.003539 | 0.0035758 | 0.0036127 | 0.0036495 | 0.0036863 | 0.0037232 | 0.00376 | 0.0037969 | 0.0038337
| CHA006-155505830 | 31 | 31 | 0.00020197 | 0 | 0.00027356 | 0 | 0.00030173 | 0 | 2.0455e-06 | 1.4086e-06 | 0.00026538 | 0.00026742 | 0.00026947 | 0.00027151 | 0.00027356 | 0.00027497 | 0.00027638 | 0.00027779 | 0.00027919 | 0.0002806 | 0.00028201 | 0.00028342 | 0.00028483 | 0.00028624 | 0.00028765 | 0.00028905 | 0.00029046 | 0.00029187 | 0.00029328 | 0.00029469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155506079 | 40 | 40 | 0.0021026 | 0 | 0.0025322 | 0 | 0.0027053 | 0 | 1.2276e-05 | 8.6538e-06 | 0.0024831 | 0.0024954 | 0.0025077 | 0.0025199 | 0.0025322 | 0.0025409 | 0.0025495 | 0.0025582 | 0.0025668 | 0.0025755 | 0.0025841 | 0.0025928 | 0.0026015 | 0.0026101 | 0.0026188 | 0.0026274 | 0.0026361 | 0.0026447 | 0.0026534 | 0.002662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155506186 | 32 | 32 | 0.00024994 | 0 | 0.00031497 | 0 | 0.00033783 | 0 | 1.8582e-06 | 1.1428e-06 | 0.00030754 | 0.0003094 | 0.00031125 | 0.00031311 | 0.00031497 | 0.00031611 | 0.00031726 | 0.0003184 | 0.00031954 | 0.00032068 | 0.00032183 | 0.00032297 | 0.00032411 | 0.00032526 | 0.0003264 | 0.00032754 | 0.00032868 | 0.00032983 | 0.00033097 | 0.00033211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155506347 | 29 | 29 | 0.0003396 | 0 | 0.00042191 | 0 | 0.00045324 | 0 | 2.3517e-06 | 1.5668e-06 | 0.0004125 | 0.00041485 | 0.0004172 | 0.00041955 | 0.00042191 | 0.00042347 | 0.00042504 | 0.00042661 | 0.00042817 | 0.00042974 | 0.00043131 | 0.00043287 | 0.00043444 | 0.00043601 | 0.00043757 | 0.00043914 | 0.00044071 | 0.00044227 | 0.00044384 | 0.00044541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155506472 | 10 | 10 | 0.0016379 | 0 | 0.0019768 | 0 | 0.0021053 | 0 | 9.6826e-06 | 6.4233e-06 | 0.0019381 | 0.0019478 | 0.0019575 | 0.0019671 | 0.0019768 | 0.0019832 | 0.0019897 | 0.0019961 | 0.0020025 | 0.0020089 | 0.0020154 | 0.0020218 | 0.0020282 | 0.0020346 | 0.002041 | 0.0020475 | 0.0020539 | 0.0020603 | 0.0020667 | 0.0020732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155506614 | 5 | 5 | 2.32e-05 | 0 | 3.38e-05 | 0 | 3.86e-05 | 0 | 3.0286e-07 | 2.4e-07 | 3.2589e-05 | 3.2891e-05 | 3.3194e-05 | 3.3497e-05 | 3.38e-05 | 3.404e-05 | 3.428e-05 | 3.452e-05 | 3.476e-05 | 3.5e-05 | 3.524e-05 | 3.548e-05 | 3.572e-05 | 3.596e-05 | 3.62e-05 | 3.644e-05 | 3.668e-05 | 3.692e-05 | 3.716e-05 | 3.74e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155618024 | 14 | 14 | 2.46e-05 | 0 | 3.34e-05 | 0 | 3.99e-05 | 0 | 2.5143e-07 | 3.25e-07 | 3.2394e-05 | 3.2646e-05 | 3.2897e-05 | 3.3149e-05 | 3.34e-05 | 3.3725e-05 | 3.405e-05 | 3.4375e-05 | 3.47e-05 | 3.5025e-05 | 3.535e-05 | 3.5675e-05 | 3.6e-05 | 3.6325e-05 | 3.665e-05 | 3.6975e-05 | 3.73e-05 | 3.7625e-05 | 3.795e-05 | 3.8275e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155618140 | 18 | 18 | 0.0061997 | 0 | 0.0063401 | 0 | 0.0062778 | 0 | 4.0098e-06 | -3.1137e-06 | 0.006324 | 0.0063281 | 0.0063321 | 0.0063361 | 0.0063401 | 0.006337 | 0.0063339 | 0.0063307 | 0.0063276 | 0.0063245 | 0.0063214 | 0.0063183 | 0.0063152 | 0.0063121 | 0.0063089 | 0.0063058 | 0.0063027 | 0.0062996 | 0.0062965 | 0.0062934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155618314 | 22 | 22 | 0.00078963 | 0 | 0.00094097 | 0 | 0.001007 | 0 | 4.3241e-06 | 3.3018e-06 | 0.00092367 | 0.000928 | 0.00093232 | 0.00093665 | 0.00094097 | 0.00094427 | 0.00094757 | 0.00095088 | 0.00095418 | 0.00095748 | 0.00096078 | 0.00096408 | 0.00096739 | 0.00097069 | 0.00097399 | 0.00097729 | 0.00098059 | 0.00098389 | 0.0009872 | 0.0009905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155621164 | 11 | 11 | 0.0035463 | 0 | 0.0042266 | 0 | 0.0043906 | 0 | 1.9438e-05 | 8.1988e-06 | 0.0041489 | 0.0041683 | 0.0041878 | 0.0042072 | 0.0042266 | 0.0042348 | 0.004243 | 0.0042512 | 0.0042594 | 0.0042676 | 0.0042758 | 0.004284 | 0.0042922 | 0.0043004 | 0.0043086 | 0.0043168 | 0.004325 | 0.0043332 | 0.0043414 | 0.0043496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155668372 | 8 | 8 | 0.00024733 | 0 | 0.00034687 | 0 | 0.00041907 | 0 | 2.8438e-06 | 3.6101e-06 | 0.00033549 | 0.00033833 | 0.00034118 | 0.00034402 | 0.00034687 | 0.00035048 | 0.00035409 | 0.0003577 | 0.00036131 | 0.00036492 | 0.00036853 | 0.00037214 | 0.00037575 | 0.00037936 | 0.00038297 | 0.00038658 | 0.00039019 | 0.0003938 | 0.00039741 | 0.00040102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155668704 | 9 | 9 | 0.00026151 | 0 | 0.00035511 | 0 | 0.0004293 | 0 | 2.6742e-06 | 3.7097e-06 | 0.00034441 | 0.00034709 | 0.00034976 | 0.00035243 | 0.00035511 | 0.00035882 | 0.00036253 | 0.00036624 | 0.00036995 | 0.00037366 | 0.00037737 | 0.00038108 | 0.00038479 | 0.0003885 | 0.0003922 | 0.00039591 | 0.00039962 | 0.00040333 | 0.00040704 | 0.00041075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155668831 | 27 | 27 | 0.00048776 | 0 | 0.00066638 | 0 | 0.00076298 | 0 | 5.1035e-06 | 4.83e-06 | 0.00064597 | 0.00065107 | 0.00065617 | 0.00066128 | 0.00066638 | 0.00067121 | 0.00067604 | 0.00068087 | 0.0006857 | 0.00069053 | 0.00069536 | 0.00070019 | 0.00070502 | 0.00070985 | 0.00071468 | 0.00071951 | 0.00072434 | 0.00072917 | 0.000734 | 0.00073883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155727138 | 10 | 10 | 0.0001507 | 0 | 0.000204 | 0 | 0.00025086 | 0 | 1.5228e-06 | 2.3432e-06 | 0.00019791 | 0.00019943 | 0.00020095 | 0.00020248 | 0.000204 | 0.00020634 | 0.00020869 | 0.00021103 | 0.00021337 | 0.00021572 | 0.00021806 | 0.0002204 | 0.00022274 | 0.00022509 | 0.00022743 | 0.00022977 | 0.00023212 | 0.00023446 | 0.0002368 | 0.00023915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-155747849 | 19 | 19 | 0.0050265 | 0 | 0.0063014 | 0 | 0.0066794 | 0 | 3.6426e-05 | 1.8898e-05 | 0.0061557 | 0.0061921 | 0.0062286 | 0.006265 | 0.0063014 | 0.0063203 | 0.0063392 | 0.0063581 | 0.006377 | 0.0063959 | 0.0064148 | 0.0064337 | 0.0064526 | 0.0064715 | 0.0064904 | 0.0065093 | 0.0065282 | 0.0065471 | 0.006566 | 0.0065849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-156354256 | 23 | 23 | 0.00013314 | 0 | 0.00017213 | 0 | 0.0002191 | 0 | 1.1141e-06 | 2.3484e-06 | 0.00016767 | 0.00016879 | 0.0001699 | 0.00017102 | 0.00017213 | 0.00017448 | 0.00017683 | 0.00017918 | 0.00018152 | 0.00018387 | 0.00018622 | 0.00018857 | 0.00019092 | 0.00019327 | 0.00019561 | 0.00019796 | 0.00020031 | 0.00020266 | 0.00020501 | 0.00020736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-164004018 | 12 | 12 | 0.0011713 | 0 | 0.0016084 | 0 | 0.0019523 | 0 | 1.2489e-05 | 1.7196e-05 | 0.0015584 | 0.0015709 | 0.0015834 | 0.0015959 | 0.0016084 | 0.0016256 | 0.0016428 | 0.00166 | 0.0016772 | 0.0016944 | 0.0017116 | 0.0017288 | 0.001746 | 0.0017632 | 0.0017804 | 0.0017975 | 0.0018147 | 0.0018319 | 0.0018491 | 0.0018663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-164004212 | 10 | 10 | 0.00012236 | 0 | 0.00016564 | 0 | 0.00020369 | 0 | 1.2364e-06 | 1.9026e-06 | 0.00016069 | 0.00016193 | 0.00016316 | 0.0001644 | 0.00016564 | 0.00016754 | 0.00016944 | 0.00017134 | 0.00017325 | 0.00017515 | 0.00017705 | 0.00017896 | 0.00018086 | 0.00018276 | 0.00018466 | 0.00018657 | 0.00018847 | 0.00019037 | 0.00019227 | 0.00019418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-164004465 | 8 | 8 | 5.54e-05 | 0 | 7.42e-05 | 0 | 9.52e-05 | 0 | 5.3714e-07 | 1.05e-06 | 7.2051e-05 | 7.2589e-05 | 7.3126e-05 | 7.3663e-05 | 7.42e-05 | 7.525e-05 | 7.63e-05 | 7.735e-05 | 7.84e-05 | 7.945e-05 | 8.05e-05 | 8.155e-05 | 8.26e-05 | 8.365e-05 | 8.47e-05 | 8.575e-05 | 8.68e-05 | 8.785e-05 | 8.89e-05 | 8.995e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-164281123 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-181783097 | 162 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-185820630 | 1028 | 375 | 0.002058 | 0.0010636 | 0.0024897 | 0.0013475 | 0.002627 | 0.0014892 | 1.2334e-05 | 6.8651e-06 | 0.0024404 | 0.0024527 | 0.002465 | 0.0024774 | 0.0024897 | 0.0024966 | 0.0025034 | 0.0025103 | 0.0025172 | 0.002524 | 0.0025309 | 0.0025377 | 0.0025446 | 0.0025515 | 0.0025583 | 0.0025652 | 0.0025721 | 0.0025789 | 0.0025858 | 0.0025927 | 8.1132e-06 | 7.0844e-06 | 0.0013151 | 0.0013232 | 0.0013313 | 0.0013394 | 0.0013475 | 0.0013546 | 0.0013617 | 0.0013688 | 0.0013759 | 0.001383 | 0.00139 | 0.0013971 | 0.0014042 | 0.0014113 | 0.0014184 | 0.0014255 | 0.0014326 | 0.0014396 | 0.0014467 | 0.0014538
| CHA006-202038162 | 176 | 138 | 0.0088338 | 2.39e-05 | 0.010793 | 3.27e-05 | 0.011506 | 3.71e-05 | 5.5971e-05 | 3.5686e-05 | 0.010569 | 0.010625 | 0.010681 | 0.010737 | 0.010793 | 0.010828 | 0.010864 | 0.0109 | 0.010935 | 0.010971 | 0.011007 | 0.011043 | 0.011078 | 0.011114 | 0.01115 | 0.011185 | 0.011221 | 0.011257 | 0.011292 | 0.011328 | 2.5143e-07 | 2.2e-07 | 3.1694e-05 | 3.1946e-05 | 3.2197e-05 | 3.2449e-05 | 3.27e-05 | 3.292e-05 | 3.314e-05 | 3.336e-05 | 3.358e-05 | 3.38e-05 | 3.402e-05 | 3.424e-05 | 3.446e-05 | 3.468e-05 | 3.49e-05 | 3.512e-05 | 3.534e-05 | 3.556e-05 | 3.578e-05 | 3.6e-05
| CHA006-24606426 | 375 | 135 | 0.0095872 | 0.003006 | 0.010406 | 0.0036685 | 0.010722 | 0.0039336 | 2.3393e-05 | 1.5823e-05 | 0.010312 | 0.010336 | 0.010359 | 0.010383 | 0.010406 | 0.010422 | 0.010438 | 0.010453 | 0.010469 | 0.010485 | 0.010501 | 0.010517 | 0.010533 | 0.010548 | 0.010564 | 0.01058 | 0.010596 | 0.010612 | 0.010628 | 0.010643 | 1.893e-05 | 1.3252e-05 | 0.0035928 | 0.0036117 | 0.0036307 | 0.0036496 | 0.0036685 | 0.0036818 | 0.003695 | 0.0037083 | 0.0037215 | 0.0037348 | 0.003748 | 0.0037613 | 0.0037745 | 0.0037878 | 0.003801 | 0.0038143 | 0.0038276 | 0.0038408 | 0.0038541 | 0.0038673
| CHA006-56709766 | 124 | 102 | 6.52e-05 | 9.29e-05 | 8.74e-05 | 0.00012441 | 0.00011203 | 0.00015953 | 6.3429e-07 | 1.2314e-06 | 8.4863e-05 | 8.5497e-05 | 8.6131e-05 | 8.6766e-05 | 8.74e-05 | 8.8631e-05 | 8.9863e-05 | 9.1094e-05 | 9.2326e-05 | 9.3557e-05 | 9.4788e-05 | 9.602e-05 | 9.7251e-05 | 9.8483e-05 | 9.9714e-05 | 0.00010095 | 0.00010218 | 0.00010341 | 0.00010464 | 0.00010587 | 9.002e-07 | 1.756e-06 | 0.00012081 | 0.00012171 | 0.00012261 | 0.00012351 | 0.00012441 | 0.00012616 | 0.00012792 | 0.00012967 | 0.00013143 | 0.00013319 | 0.00013494 | 0.0001367 | 0.00013845 | 0.00014021 | 0.00014197 | 0.00014372 | 0.00014548 | 0.00014723 | 0.00014899 | 0.00015075
| CHA006-95436119 | 168 | 150 | 0.016327 | 0.0017256 | 0.020805 | 0.0022589 | 0.024783 | 0.0027854 | 0.00012794 | 0.0001989 | 0.020293 | 0.020421 | 0.020549 | 0.020677 | 0.020805 | 0.021004 | 0.021203 | 0.021402 | 0.021601 | 0.0218 | 0.021998 | 0.022197 | 0.022396 | 0.022595 | 0.022794 | 0.022993 | 0.023192 | 0.023391 | 0.02359 | 0.023789 | 1.5239e-05 | 2.6322e-05 | 0.002198 | 0.0022132 | 0.0022284 | 0.0022437 | 0.0022589 | 0.0022852 | 0.0023116 | 0.0023379 | 0.0023642 | 0.0023905 | 0.0024168 | 0.0024432 | 0.0024695 | 0.0024958 | 0.0025221 | 0.0025485 | 0.0025748 | 0.0026011 | 0.0026274 | 0.0026537
| CHA007-162618256 | 1 | 1 | 1.1e-05 | 0 | 1.49e-05 | 0 | 1.87e-05 | 0 | 1.1143e-07 | 1.9e-07 | 1.4454e-05 | 1.4566e-05 | 1.4677e-05 | 1.4789e-05 | 1.49e-05 | 1.509e-05 | 1.528e-05 | 1.547e-05 | 1.566e-05 | 1.585e-05 | 1.604e-05 | 1.623e-05 | 1.642e-05 | 1.661e-05 | 1.68e-05 | 1.699e-05 | 1.718e-05 | 1.737e-05 | 1.756e-05 | 1.775e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA008-162618131 | 1 | 1 | 8.87e-06 | 0 | 1.2e-05 | 0 | 1.5e-05 | 0 | 8.9429e-08 | 1.5e-07 | 1.1642e-05 | 1.1732e-05 | 1.1821e-05 | 1.1911e-05 | 1.2e-05 | 1.215e-05 | 1.23e-05 | 1.245e-05 | 1.26e-05 | 1.275e-05 | 1.29e-05 | 1.305e-05 | 1.32e-05 | 1.335e-05 | 1.35e-05 | 1.365e-05 | 1.38e-05 | 1.395e-05 | 1.41e-05 | 1.425e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-15436218 | 1540 | 3 | 0 | 2.04e-06 | 0 | 2.64e-06 | 0 | 2.6e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7143e-08 | -2e-09 | 2.5714e-06 | 2.5886e-06 | 2.6057e-06 | 2.6229e-06 | 2.64e-06 | 2.638e-06 | 2.636e-06 | 2.634e-06 | 2.632e-06 | 2.63e-06 | 2.628e-06 | 2.626e-06 | 2.624e-06 | 2.622e-06 | 2.62e-06 | 2.618e-06 | 2.616e-06 | 2.614e-06 | 2.612e-06 | 2.61e-06
| CHM011-159371854 | 14 | 14 | 0.0020805 | 0 | 0.0026192 | 0 | 0.0022985 | 0 | 1.5393e-05 | -1.6037e-05 | 0.0025576 | 0.002573 | 0.0025884 | 0.0026038 | 0.0026192 | 0.0026032 | 0.0025871 | 0.0025711 | 0.0025551 | 0.002539 | 0.002523 | 0.0025069 | 0.0024909 | 0.0024749 | 0.0024588 | 0.0024428 | 0.0024268 | 0.0024107 | 0.0023947 | 0.0023787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-159371937 | 13 | 13 | 0.00030193 | 0 | 0.00039064 | 0 | 0.00034029 | 0 | 2.5345e-06 | -2.5172e-06 | 0.0003805 | 0.00038303 | 0.00038557 | 0.0003881 | 0.00039064 | 0.00038812 | 0.0003856 | 0.00038309 | 0.00038057 | 0.00037805 | 0.00037553 | 0.00037302 | 0.0003705 | 0.00036798 | 0.00036547 | 0.00036295 | 0.00036043 | 0.00035791 | 0.0003554 | 0.00035288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-159372020 | 27 | 27 | 0.00336 | 0 | 0.0041747 | 0 | 0.0036837 | 0 | 2.3275e-05 | -2.4551e-05 | 0.0040816 | 0.0041048 | 0.0041281 | 0.0041514 | 0.0041747 | 0.0041501 | 0.0041256 | 0.004101 | 0.0040765 | 0.0040519 | 0.0040274 | 0.0040028 | 0.0039783 | 0.0039537 | 0.0039292 | 0.0039046 | 0.0038801 | 0.0038555 | 0.003831 | 0.0038064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-159372116 | 14 | 14 | 0.00067579 | 0 | 0.00085631 | 0 | 0.00074962 | 0 | 5.1577e-06 | -5.3346e-06 | 0.00083568 | 0.00084084 | 0.000846 | 0.00085116 | 0.00085631 | 0.00085098 | 0.00084564 | 0.00084031 | 0.00083497 | 0.00082964 | 0.00082431 | 0.00081897 | 0.00081364 | 0.0008083 | 0.00080297 | 0.00079763 | 0.0007923 | 0.00078696 | 0.00078163 | 0.00077629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-159372219 | 42 | 42 | 0.0017772 | 0 | 0.0021592 | 0 | 0.0019233 | 0 | 1.0915e-05 | -1.1797e-05 | 0.0021156 | 0.0021265 | 0.0021374 | 0.0021483 | 0.0021592 | 0.0021474 | 0.0021357 | 0.0021239 | 0.0021121 | 0.0021003 | 0.0020885 | 0.0020767 | 0.0020649 | 0.0020531 | 0.0020413 | 0.0020295 | 0.0020177 | 0.0020059 | 0.0019941 | 0.0019823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-159372384 | 35 | 35 | 0.00029634 | 0 | 0.00036757 | 0 | 0.00033224 | 0 | 2.0351e-06 | -1.7668e-06 | 0.00035943 | 0.00036147 | 0.0003635 | 0.00036554 | 0.00036757 | 0.00036581 | 0.00036404 | 0.00036227 | 0.00036051 | 0.00035874 | 0.00035697 | 0.0003552 | 0.00035344 | 0.00035167 | 0.0003499 | 0.00034814 | 0.00034637 | 0.0003446 | 0.00034284 | 0.00034107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-159372472 | 12 | 12 | 0.00027372 | 0 | 0.00033078 | 0 | 0.00029751 | 0 | 1.6303e-06 | -1.6634e-06 | 0.00032426 | 0.00032589 | 0.00032752 | 0.00032915 | 0.00033078 | 0.00032911 | 0.00032745 | 0.00032579 | 0.00032412 | 0.00032246 | 0.0003208 | 0.00031913 | 0.00031747 | 0.00031581 | 0.00031414 | 0.00031248 | 0.00031082 | 0.00030915 | 0.00030749 | 0.00030583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-159372576 | 6 | 6 | 0.004129 | 0 | 0.0051503 | 0 | 0.0045373 | 0 | 2.9177e-05 | -3.065e-05 | 0.0050335 | 0.0050627 | 0.0050919 | 0.0051211 | 0.0051503 | 0.0051196 | 0.005089 | 0.0050583 | 0.0050277 | 0.004997 | 0.0049664 | 0.0049357 | 0.0049051 | 0.0048744 | 0.0048438 | 0.0048131 | 0.0047825 | 0.0047518 | 0.0047212 | 0.0046905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-159372815 | 11 | 11 | 2.37e-05 | 0 | 3.14e-05 | 0 | 2.66e-05 | 0 | 2.2e-07 | -2.4e-07 | 3.052e-05 | 3.074e-05 | 3.096e-05 | 3.118e-05 | 3.14e-05 | 3.116e-05 | 3.092e-05 | 3.068e-05 | 3.044e-05 | 3.02e-05 | 2.996e-05 | 2.972e-05 | 2.948e-05 | 2.924e-05 | 2.9e-05 | 2.876e-05 | 2.852e-05 | 2.828e-05 | 2.804e-05 | 2.78e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-159372981 | 14 | 14 | 0.0010267 | 0 | 0.0012397 | 0 | 0.0010907 | 0 | 6.0861e-06 | -7.4479e-06 | 0.0012153 | 0.0012214 | 0.0012275 | 0.0012336 | 0.0012397 | 0.0012322 | 0.0012248 | 0.0012173 | 0.0012099 | 0.0012024 | 0.001195 | 0.0011875 | 0.0011801 | 0.0011726 | 0.0011652 | 0.0011577 | 0.0011503 | 0.0011428 | 0.0011354 | 0.001128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-159373200 | 38 | 38 | 0.0016495 | 0 | 0.0020508 | 0 | 0.0017827 | 0 | 1.1465e-05 | -1.3402e-05 | 0.0020049 | 0.0020164 | 0.0020278 | 0.0020393 | 0.0020508 | 0.0020374 | 0.002024 | 0.0020106 | 0.0019972 | 0.0019838 | 0.0019704 | 0.001957 | 0.0019436 | 0.0019302 | 0.0019168 | 0.0019033 | 0.0018899 | 0.0018765 | 0.0018631 | 0.0018497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-159373315 | 13 | 13 | 0.00026862 | 0 | 0.00032778 | 0 | 0.00028614 | 0 | 1.6902e-06 | -2.0822e-06 | 0.00032102 | 0.00032271 | 0.0003244 | 0.00032609 | 0.00032778 | 0.0003257 | 0.00032362 | 0.00032154 | 0.00031945 | 0.00031737 | 0.00031529 | 0.00031321 | 0.00031113 | 0.00030904 | 0.00030696 | 0.00030488 | 0.0003028 | 0.00030071 | 0.00029863 | 0.00029655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-159373411 | 11 | 11 | 0.00049869 | 0 | 0.0006266 | 0 | 0.00056085 | 0 | 3.6546e-06 | -3.2872e-06 | 0.00061198 | 0.00061563 | 0.00061929 | 0.00062294 | 0.0006266 | 0.00062331 | 0.00062002 | 0.00061674 | 0.00061345 | 0.00061016 | 0.00060687 | 0.00060359 | 0.0006003 | 0.00059701 | 0.00059373 | 0.00059044 | 0.00058715 | 0.00058386 | 0.00058058 | 0.00057729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-160317885 | 24 | 24 | 0.0011591 | 0 | 0.0014099 | 0 | 0.0012671 | 0 | 7.1673e-06 | -7.1407e-06 | 0.0013813 | 0.0013884 | 0.0013956 | 0.0014028 | 0.0014099 | 0.0014028 | 0.0013957 | 0.0013885 | 0.0013814 | 0.0013742 | 0.0013671 | 0.00136 | 0.0013528 | 0.0013457 | 0.0013385 | 0.0013314 | 0.0013242 | 0.0013171 | 0.00131 | 0.0013028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-160318163 | 17 | 17 | 5.8e-06 | 0 | 7.65e-06 | 0 | 6.62e-06 | 0 | 5.2857e-08 | -5.15e-08 | 7.4386e-06 | 7.4914e-06 | 7.5443e-06 | 7.5971e-06 | 7.65e-06 | 7.5985e-06 | 7.547e-06 | 7.4955e-06 | 7.444e-06 | 7.3925e-06 | 7.341e-06 | 7.2895e-06 | 7.238e-06 | 7.1865e-06 | 7.135e-06 | 7.0835e-06 | 7.032e-06 | 6.9805e-06 | 6.929e-06 | 6.8775e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-160318338 | 18 | 18 | 0.00012368 | 0 | 0.00015786 | 0 | 0.00013629 | 0 | 9.7663e-07 | -1.0786e-06 | 0.00015395 | 0.00015493 | 0.00015591 | 0.00015688 | 0.00015786 | 0.00015678 | 0.0001557 | 0.00015462 | 0.00015355 | 0.00015247 | 0.00015139 | 0.00015031 | 0.00014923 | 0.00014815 | 0.00014707 | 0.000146 | 0.00014492 | 0.00014384 | 0.00014276 | 0.00014168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-160677964 | 31 | 31 | 0.0012239 | 0 | 0.0015447 | 0 | 0.0013802 | 0 | 9.1655e-06 | -8.2228e-06 | 0.001508 | 0.0015172 | 0.0015263 | 0.0015355 | 0.0015447 | 0.0015365 | 0.0015282 | 0.00152 | 0.0015118 | 0.0015036 | 0.0014953 | 0.0014871 | 0.0014789 | 0.0014707 | 0.0014625 | 0.0014542 | 0.001446 | 0.0014378 | 0.0014296 | 0.0014213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-160678238 | 15 | 15 | 0.0023131 | 0 | 0.0028149 | 0 | 0.002497 | 0 | 1.4337e-05 | -1.5896e-05 | 0.0027575 | 0.0027719 | 0.0027862 | 0.0028006 | 0.0028149 | 0.002799 | 0.0027831 | 0.0027672 | 0.0027513 | 0.0027354 | 0.0027195 | 0.0027036 | 0.0026877 | 0.0026718 | 0.0026559 | 0.00264 | 0.0026242 | 0.0026083 | 0.0025924 | 0.0025765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-160721783 | 13 | 13 | 1.42e-05 | 0 | 1.85e-05 | 0 | 1.6e-05 | 0 | 1.2286e-07 | -1.25e-07 | 1.8009e-05 | 1.8131e-05 | 1.8254e-05 | 1.8377e-05 | 1.85e-05 | 1.8375e-05 | 1.825e-05 | 1.8125e-05 | 1.8e-05 | 1.7875e-05 | 1.775e-05 | 1.7625e-05 | 1.75e-05 | 1.7375e-05 | 1.725e-05 | 1.7125e-05 | 1.7e-05 | 1.6875e-05 | 1.675e-05 | 1.6625e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-163177271 | 10 | 10 | 0.00049734 | 0 | 0.0006647 | 0 | 0.00055914 | 0 | 4.7816e-06 | -5.2779e-06 | 0.00064558 | 0.00065036 | 0.00065514 | 0.00065992 | 0.0006647 | 0.00065942 | 0.00065415 | 0.00064887 | 0.00064359 | 0.00063831 | 0.00063303 | 0.00062776 | 0.00062248 | 0.0006172 | 0.00061192 | 0.00060664 | 0.00060137 | 0.00059609 | 0.00059081 | 0.00058553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-163198394 | 17 | 17 | 0.00092329 | 0 | 0.0011292 | 0 | 0.00096893 | 0 | 5.884e-06 | -8.0148e-06 | 0.0011057 | 0.0011116 | 0.0011175 | 0.0011233 | 0.0011292 | 0.0011212 | 0.0011132 | 0.0011052 | 0.0010972 | 0.0010892 | 0.0010811 | 0.0010731 | 0.0010651 | 0.0010571 | 0.0010491 | 0.0010411 | 0.0010331 | 0.001025 | 0.001017 | 0.001009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-163198509 | 46 | 46 | 0.0053224 | 0 | 0.006647 | 0 | 0.0059353 | 0 | 3.7847e-05 | -3.5587e-05 | 0.0064957 | 0.0065335 | 0.0065713 | 0.0066092 | 0.006647 | 0.0066115 | 0.0065759 | 0.0065403 | 0.0065047 | 0.0064691 | 0.0064335 | 0.0063979 | 0.0063623 | 0.0063268 | 0.0062912 | 0.0062556 | 0.00622 | 0.0061844 | 0.0061488 | 0.0061132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-163310655 | 9 | 9 | 0.012638 | 0 | 0.016135 | 0 | 0.014011 | 0 | 9.9911e-05 | -0.00010619 | 0.015735 | 0.015835 | 0.015935 | 0.016035 | 0.016135 | 0.016029 | 0.015923 | 0.015817 | 0.01571 | 0.015604 | 0.015498 | 0.015392 | 0.015286 | 0.015179 | 0.015073 | 0.014967 | 0.014861 | 0.014755 | 0.014649 | 0.014542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-164238923 | 10 | 10 | 1.75e-05 | 0 | 2.28e-05 | 0 | 1.91e-05 | 0 | 1.5143e-07 | -1.85e-07 | 2.2194e-05 | 2.2346e-05 | 2.2497e-05 | 2.2649e-05 | 2.28e-05 | 2.2615e-05 | 2.243e-05 | 2.2245e-05 | 2.206e-05 | 2.1875e-05 | 2.169e-05 | 2.1505e-05 | 2.132e-05 | 2.1135e-05 | 2.095e-05 | 2.0765e-05 | 2.058e-05 | 2.0395e-05 | 2.021e-05 | 2.0025e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-164366730 | 5 | 5 | 0.0013776 | 0 | 0.0017197 | 0 | 0.0015123 | 0 | 9.775e-06 | -1.0371e-05 | 0.0016806 | 0.0016904 | 0.0017002 | 0.0017099 | 0.0017197 | 0.0017093 | 0.001699 | 0.0016886 | 0.0016782 | 0.0016679 | 0.0016575 | 0.0016471 | 0.0016367 | 0.0016264 | 0.001616 | 0.0016056 | 0.0015953 | 0.0015849 | 0.0015745 | 0.0015642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-187119686 | 1537 | 602 | 0.01047 | 0.002865 | 0.012614 | 0.0034882 | 0.011417 | 0.0031578 | 6.1259e-05 | -5.9809e-05 | 0.012369 | 0.01243 | 0.012491 | 0.012552 | 0.012614 | 0.012554 | 0.012494 | 0.012434 | 0.012374 | 0.012315 | 0.012255 | 0.012195 | 0.012135 | 0.012075 | 0.012016 | 0.011956 | 0.011896 | 0.011836 | 0.011776 | 0.011716 | 1.7804e-05 | -1.652e-05 | 0.003417 | 0.0034348 | 0.0034526 | 0.0034704 | 0.0034882 | 0.0034717 | 0.0034551 | 0.0034386 | 0.0034221 | 0.0034056 | 0.0033891 | 0.0033725 | 0.003356 | 0.0033395 | 0.003323 | 0.0033065 | 0.0032899 | 0.0032734 | 0.0032569 | 0.0032404
| CHM011-24600428 | 229 | 107 | 0.0043279 | 0.0030011 | 0.0052232 | 0.0036132 | 0.0046747 | 0.0032331 | 2.5578e-05 | -2.7425e-05 | 0.0051208 | 0.0051464 | 0.005172 | 0.0051976 | 0.0052232 | 0.0051957 | 0.0051683 | 0.0051409 | 0.0051135 | 0.005086 | 0.0050586 | 0.0050312 | 0.0050038 | 0.0049763 | 0.0049489 | 0.0049215 | 0.0048941 | 0.0048666 | 0.0048392 | 0.0048118 | 1.7489e-05 | -1.9002e-05 | 0.0035432 | 0.0035607 | 0.0035782 | 0.0035957 | 0.0036132 | 0.0035942 | 0.0035752 | 0.0035562 | 0.0035372 | 0.0035182 | 0.0034992 | 0.0034802 | 0.0034612 | 0.0034422 | 0.0034232 | 0.0034042 | 0.0033852 | 0.0033662 | 0.0033472 | 0.0033282
| CHM011-24600540 | 583 | 363 | 0.0041884 | 0.0029153 | 0.0052112 | 0.0036339 | 0.0046407 | 0.0032245 | 2.9223e-05 | -2.8525e-05 | 0.0050943 | 0.0051235 | 0.0051528 | 0.005182 | 0.0052112 | 0.0051827 | 0.0051542 | 0.0051256 | 0.0050971 | 0.0050686 | 0.0050401 | 0.0050115 | 0.004983 | 0.0049545 | 0.004926 | 0.0048974 | 0.0048689 | 0.0048404 | 0.0048119 | 0.0047833 | 2.053e-05 | -2.0471e-05 | 0.0035518 | 0.0035723 | 0.0035928 | 0.0036134 | 0.0036339 | 0.0036134 | 0.003593 | 0.0035725 | 0.003552 | 0.0035315 | 0.0035111 | 0.0034906 | 0.0034701 | 0.0034497 | 0.0034292 | 0.0034087 | 0.0033882 | 0.0033678 | 0.0033473 | 0.0033268
| CLC001-15400682 | 1690 | 1681 | 0.00054912 | 0 | 0.00057887 | 0 | 0.0005571 | 0 | 8.5006e-07 | -1.0885e-06 | 0.00057547 | 0.00057632 | 0.00057717 | 0.00057802 | 0.00057887 | 0.00057778 | 0.00057669 | 0.00057561 | 0.00057452 | 0.00057343 | 0.00057234 | 0.00057125 | 0.00057016 | 0.00056907 | 0.00056799 | 0.0005669 | 0.00056581 | 0.00056472 | 0.00056363 | 0.00056254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC001-15400693 | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC002-15400645 | 2992 | 2992 | 0.0022842 | 0 | 0.0023756 | 0 | 0.0022925 | 0 | 2.6133e-06 | -4.1564e-06 | 0.0023652 | 0.0023678 | 0.0023704 | 0.002373 | 0.0023756 | 0.0023715 | 0.0023673 | 0.0023632 | 0.002359 | 0.0023549 | 0.0023507 | 0.0023466 | 0.0023424 | 0.0023382 | 0.0023341 | 0.0023299 | 0.0023258 | 0.0023216 | 0.0023175 | 0.0023133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-119149948 | 35 | 35 | 8.12e-05 | 0 | 0.00014083 | 0 | 9.61e-05 | 0 | 1.7036e-06 | -2.2363e-06 | 0.00013401 | 0.00013572 | 0.00013742 | 0.00013912 | 0.00014083 | 0.00013859 | 0.00013635 | 0.00013412 | 0.00013188 | 0.00012965 | 0.00012741 | 0.00012517 | 0.00012294 | 0.0001207 | 0.00011846 | 0.00011623 | 0.00011399 | 0.00011175 | 0.00010952 | 0.00010728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-123633044 | 14 | 14 | 0.00073733 | 0 | 0.0010303 | 0 | 0.00079107 | 0 | 8.3694e-06 | -1.196e-05 | 0.00099679 | 0.0010052 | 0.0010135 | 0.0010219 | 0.0010303 | 0.0010183 | 0.0010063 | 0.00099438 | 0.00098242 | 0.00097046 | 0.00095851 | 0.00094655 | 0.00093459 | 0.00092263 | 0.00091067 | 0.00089871 | 0.00088675 | 0.00087479 | 0.00086283 | 0.00085087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-130014430 | 4 | 4 | 2.01e-05 | 0 | 3.87e-05 | 0 | 2.94e-05 | 0 | 5.3143e-07 | -4.65e-07 | 3.6574e-05 | 3.7106e-05 | 3.7637e-05 | 3.8169e-05 | 3.87e-05 | 3.8235e-05 | 3.777e-05 | 3.7305e-05 | 3.684e-05 | 3.6375e-05 | 3.591e-05 | 3.5445e-05 | 3.498e-05 | 3.4515e-05 | 3.405e-05 | 3.3585e-05 | 3.312e-05 | 3.2655e-05 | 3.219e-05 | 3.1725e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-130014725 | 19 | 19 | 2.6e-05 | 0 | 6.8e-05 | 0 | 3.72e-05 | 0 | 1.2e-06 | -1.54e-06 | 6.32e-05 | 6.44e-05 | 6.56e-05 | 6.68e-05 | 6.8e-05 | 6.646e-05 | 6.492e-05 | 6.338e-05 | 6.184e-05 | 6.03e-05 | 5.876e-05 | 5.722e-05 | 5.568e-05 | 5.414e-05 | 5.26e-05 | 5.106e-05 | 4.952e-05 | 4.798e-05 | 4.644e-05 | 4.49e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-130014949 | 3 | 3 | 0.00072351 | 0 | 0.0013116 | 0 | 0.0010126 | 0 | 1.6804e-05 | -1.4951e-05 | 0.0012444 | 0.0012612 | 0.001278 | 0.0012948 | 0.0013116 | 0.0012967 | 0.0012817 | 0.0012668 | 0.0012518 | 0.0012369 | 0.0012219 | 0.001207 | 0.001192 | 0.0011771 | 0.0011621 | 0.0011472 | 0.0011322 | 0.0011173 | 0.0011023 | 0.0010874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-130747301 | 24 | 24 | 0.00013391 | 0 | 0.00025647 | 0 | 0.00019417 | 0 | 3.5017e-06 | -3.115e-06 | 0.00024246 | 0.00024596 | 0.00024947 | 0.00025297 | 0.00025647 | 0.00025336 | 0.00025024 | 0.00024713 | 0.00024401 | 0.0002409 | 0.00023778 | 0.00023467 | 0.00023155 | 0.00022843 | 0.00022532 | 0.0002222 | 0.00021909 | 0.00021597 | 0.00021286 | 0.00020974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-130748256 | 15 | 15 | 0.00028444 | 0 | 0.00043549 | 0 | 0.00032757 | 0 | 4.3157e-06 | -5.3957e-06 | 0.00041822 | 0.00042254 | 0.00042685 | 0.00043117 | 0.00043549 | 0.00043009 | 0.00042469 | 0.0004193 | 0.0004139 | 0.00040851 | 0.00040311 | 0.00039772 | 0.00039232 | 0.00038693 | 0.00038153 | 0.00037613 | 0.00037074 | 0.00036534 | 0.00035995 | 0.00035455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-152030196 | 16 | 16 | 0.0013858 | 0 | 0.0015315 | 0 | 0.0013532 | 0 | 4.1637e-06 | -8.9148e-06 | 0.0015149 | 0.001519 | 0.0015232 | 0.0015273 | 0.0015315 | 0.0015226 | 0.0015137 | 0.0015048 | 0.0014958 | 0.0014869 | 0.001478 | 0.0014691 | 0.0014602 | 0.0014513 | 0.0014424 | 0.0014334 | 0.0014245 | 0.0014156 | 0.0014067 | 0.0013978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-15400758 | 2795 | 1238 | 0.0083649 | 0.00095427 | 0.010754 | 0.0015529 | 0.0091229 | 0.001217 | 6.8256e-05 | -8.1548e-05 | 0.010481 | 0.010549 | 0.010617 | 0.010686 | 0.010754 | 0.010672 | 0.010591 | 0.010509 | 0.010428 | 0.010346 | 0.010265 | 0.010183 | 0.010102 | 0.01002 | 0.0099384 | 0.0098569 | 0.0097753 | 0.0096938 | 0.0096122 | 0.0095307 | 1.7105e-05 | -1.6796e-05 | 0.0014845 | 0.0015016 | 0.0015187 | 0.0015358 | 0.0015529 | 0.0015361 | 0.0015193 | 0.0015026 | 0.0014858 | 0.001469 | 0.0014522 | 0.0014354 | 0.0014186 | 0.0014018 | 0.001385 | 0.0013682 | 0.0013514 | 0.0013346 | 0.0013178 | 0.001301
| CLC003-154876479 | 6 | 6 | 0.0002503 | 0 | 0.00032669 | 0 | 0.00030761 | 0 | 2.1825e-06 | -9.5415e-07 | 0.00031796 | 0.00032014 | 0.00032233 | 0.00032451 | 0.00032669 | 0.00032574 | 0.00032478 | 0.00032383 | 0.00032287 | 0.00032192 | 0.00032097 | 0.00032001 | 0.00031906 | 0.0003181 | 0.00031715 | 0.00031619 | 0.00031524 | 0.00031429 | 0.00031333 | 0.00031238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-154908324 | 55 | 55 | 0.001175 | 0 | 0.001286 | 0 | 0.0011494 | 0 | 3.1698e-06 | -6.8291e-06 | 0.0012733 | 0.0012765 | 0.0012796 | 0.0012828 | 0.001286 | 0.0012792 | 0.0012723 | 0.0012655 | 0.0012587 | 0.0012518 | 0.001245 | 0.0012382 | 0.0012314 | 0.0012245 | 0.0012177 | 0.0012109 | 0.001204 | 0.0011972 | 0.0011904 | 0.0011836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-154908634 | 8 | 8 | 4.68e-05 | 0 | 6.81e-05 | 0 | 6.47e-05 | 0 | 6.0857e-07 | -1.7e-07 | 6.5666e-05 | 6.6274e-05 | 6.6883e-05 | 6.7491e-05 | 6.81e-05 | 6.793e-05 | 6.776e-05 | 6.759e-05 | 6.742e-05 | 6.725e-05 | 6.708e-05 | 6.691e-05 | 6.674e-05 | 6.657e-05 | 6.64e-05 | 6.623e-05 | 6.606e-05 | 6.589e-05 | 6.572e-05 | 6.555e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-154908755 | 7 | 7 | 2.11e-05 | 0 | 3.52e-05 | 0 | 2.6e-05 | 0 | 4.0286e-07 | -4.6e-07 | 3.3589e-05 | 3.3991e-05 | 3.4394e-05 | 3.4797e-05 | 3.52e-05 | 3.474e-05 | 3.428e-05 | 3.382e-05 | 3.336e-05 | 3.29e-05 | 3.244e-05 | 3.198e-05 | 3.152e-05 | 3.106e-05 | 3.06e-05 | 3.014e-05 | 2.968e-05 | 2.922e-05 | 2.876e-05 | 2.83e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-154908853 | 16 | 16 | 7.59e-05 | 0 | 0.00010799 | 0 | 9.61e-05 | 0 | 9.1677e-07 | -5.9435e-07 | 0.00010432 | 0.00010524 | 0.00010615 | 0.00010707 | 0.00010799 | 0.00010739 | 0.0001068 | 0.0001062 | 0.00010561 | 0.00010502 | 0.00010442 | 0.00010383 | 0.00010323 | 0.00010264 | 0.00010204 | 0.00010145 | 0.00010085 | 0.00010026 | 9.9666e-05 | 9.9072e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-154908977 | 21 | 21 | 0.0015063 | 0 | 0.0021091 | 0 | 0.0018256 | 0 | 1.7225e-05 | -1.4179e-05 | 0.0020402 | 0.0020575 | 0.0020747 | 0.0020919 | 0.0021091 | 0.002095 | 0.0020808 | 0.0020666 | 0.0020524 | 0.0020382 | 0.0020241 | 0.0020099 | 0.0019957 | 0.0019815 | 0.0019674 | 0.0019532 | 0.001939 | 0.0019248 | 0.0019106 | 0.0018965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-193886326 | 113 | 47 | 0.0023445 | 0.00027284 | 0.0035959 | 0.00046526 | 0.0026627 | 0.00033049 | 3.5755e-05 | -4.6659e-05 | 0.0034529 | 0.0034886 | 0.0035244 | 0.0035602 | 0.0035959 | 0.0035492 | 0.0035026 | 0.0034559 | 0.0034093 | 0.0033626 | 0.003316 | 0.0032693 | 0.0032226 | 0.003176 | 0.0031293 | 0.0030827 | 0.003036 | 0.0029893 | 0.0029427 | 0.002896 | 5.4976e-06 | -6.7384e-06 | 0.00044327 | 0.00044877 | 0.00045426 | 0.00045976 | 0.00046526 | 0.00045852 | 0.00045178 | 0.00044504 | 0.00043831 | 0.00043157 | 0.00042483 | 0.00041809 | 0.00041135 | 0.00040461 | 0.00039788 | 0.00039114 | 0.0003844 | 0.00037766 | 0.00037092 | 0.00036418
| CLC003-198593463 | 136 | 62 | 0.0013023 | 6.91e-05 | 0.0017672 | 0.00011331 | 0.001282 | 6.87e-05 | 1.3282e-05 | -2.4261e-05 | 0.001714 | 0.0017273 | 0.0017406 | 0.0017539 | 0.0017672 | 0.0017429 | 0.0017186 | 0.0016944 | 0.0016701 | 0.0016459 | 0.0016216 | 0.0015973 | 0.0015731 | 0.0015488 | 0.0015246 | 0.0015003 | 0.001476 | 0.0014518 | 0.0014275 | 0.0014033 | 1.2632e-06 | -2.2305e-06 | 0.00010826 | 0.00010952 | 0.00011078 | 0.00011205 | 0.00011331 | 0.00011108 | 0.00010885 | 0.00010662 | 0.00010439 | 0.00010216 | 9.9928e-05 | 9.7697e-05 | 9.5467e-05 | 9.3236e-05 | 9.1006e-05 | 8.8775e-05 | 8.6544e-05 | 8.4314e-05 | 8.2083e-05 | 7.9853e-05
| CLC003-24597492 | 956 | 0 | 0.0027709 | 8.52e-05 | 0.0040665 | 0.00015781 | 0.0029631 | 0.00010129 | 3.7016e-05 | -5.5171e-05 | 0.0039184 | 0.0039554 | 0.0039924 | 0.0040295 | 0.0040665 | 0.0040113 | 0.0039561 | 0.003901 | 0.0038458 | 0.0037906 | 0.0037354 | 0.0036803 | 0.0036251 | 0.0035699 | 0.0035148 | 0.0034596 | 0.0034044 | 0.0033493 | 0.0032941 | 0.0032389 | 2.0744e-06 | -2.8259e-06 | 0.00014951 | 0.00015158 | 0.00015366 | 0.00015573 | 0.00015781 | 0.00015498 | 0.00015215 | 0.00014933 | 0.0001465 | 0.00014368 | 0.00014085 | 0.00013802 | 0.0001352 | 0.00013237 | 0.00012955 | 0.00012672 | 0.00012389 | 0.00012107 | 0.00011824 | 0.00011542
| CLC003-24597520 | 383 | 131 | 0.0017504 | 4.59e-05 | 0.0022998 | 7.93e-05 | 0.0017048 | 4.59e-05 | 1.5698e-05 | -2.9754e-05 | 0.002237 | 0.0022527 | 0.0022684 | 0.0022841 | 0.0022998 | 0.0022701 | 0.0022403 | 0.0022106 | 0.0021808 | 0.0021511 | 0.0021213 | 0.0020916 | 0.0020618 | 0.0020321 | 0.0020023 | 0.0019725 | 0.0019428 | 0.001913 | 0.0018833 | 0.0018535 | 9.5429e-07 | -1.67e-06 | 7.5483e-05 | 7.6437e-05 | 7.7391e-05 | 7.8346e-05 | 7.93e-05 | 7.763e-05 | 7.596e-05 | 7.429e-05 | 7.262e-05 | 7.095e-05 | 6.928e-05 | 6.761e-05 | 6.594e-05 | 6.427e-05 | 6.26e-05 | 6.093e-05 | 5.926e-05 | 5.759e-05 | 5.592e-05 | 5.425e-05
| CLC003-24597576 | 573 | 0 | 0.0014652 | 0.00061777 | 0.0023001 | 0.00094903 | 0.0015838 | 0.00066287 | 2.3855e-05 | -3.5814e-05 | 0.0022047 | 0.0022286 | 0.0022524 | 0.0022763 | 0.0023001 | 0.0022643 | 0.0022285 | 0.0021927 | 0.0021569 | 0.002121 | 0.0020852 | 0.0020494 | 0.0020136 | 0.0019778 | 0.001942 | 0.0019062 | 0.0018703 | 0.0018345 | 0.0017987 | 0.0017629 | 9.4644e-06 | -1.4308e-05 | 0.00091117 | 0.00092063 | 0.0009301 | 0.00093956 | 0.00094903 | 0.00093472 | 0.00092041 | 0.0009061 | 0.00089179 | 0.00087749 | 0.00086318 | 0.00084887 | 0.00083456 | 0.00082026 | 0.00080595 | 0.00079164 | 0.00077733 | 0.00076302 | 0.00074872 | 0.00073441
| CLC003-24607110 | 573 | 573 | 0.0059115 | 0 | 0.0064996 | 0 | 0.0057761 | 0 | 1.6804e-05 | -3.6176e-05 | 0.0064324 | 0.0064492 | 0.006466 | 0.0064828 | 0.0064996 | 0.0064634 | 0.0064273 | 0.0063911 | 0.0063549 | 0.0063187 | 0.0062826 | 0.0062464 | 0.0062102 | 0.006174 | 0.0061379 | 0.0061017 | 0.0060655 | 0.0060293 | 0.0059932 | 0.005957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-24607264 | 381 | 319 | 0.0015877 | 0.001437 | 0.0024373 | 0.0022101 | 0.0018594 | 0.001682 | 2.4273e-05 | -2.8894e-05 | 0.0023402 | 0.0023645 | 0.0023887 | 0.002413 | 0.0024373 | 0.0024084 | 0.0023795 | 0.0023506 | 0.0023217 | 0.0022928 | 0.0022639 | 0.002235 | 0.0022061 | 0.0021772 | 0.0021483 | 0.0021194 | 0.0020905 | 0.0020616 | 0.0020328 | 0.0020039 | 2.2087e-05 | -2.6403e-05 | 0.0021217 | 0.0021438 | 0.0021659 | 0.002188 | 0.0022101 | 0.0021837 | 0.0021573 | 0.0021309 | 0.0021045 | 0.0020781 | 0.0020516 | 0.0020252 | 0.0019988 | 0.0019724 | 0.001946 | 0.0019196 | 0.0018932 | 0.0018668 | 0.0018404 | 0.001814
| CLC003-24613704 | 100 | 100 | 0.0017807 | 0 | 0.0025273 | 0 | 0.0019397 | 0 | 2.1332e-05 | -2.9382e-05 | 0.002442 | 0.0024633 | 0.0024846 | 0.002506 | 0.0025273 | 0.0024979 | 0.0024685 | 0.0024391 | 0.0024098 | 0.0023804 | 0.002351 | 0.0023216 | 0.0022922 | 0.0022629 | 0.0022335 | 0.0022041 | 0.0021747 | 0.0021453 | 0.0021159 | 0.0020866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-78545961 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-80120806 | 6 | 6 | 0.001058 | 0 | 0.0015239 | 0 | 0.0012789 | 0 | 1.3312e-05 | -1.225e-05 | 0.0014706 | 0.0014839 | 0.0014972 | 0.0015106 | 0.0015239 | 0.0015116 | 0.0014994 | 0.0014871 | 0.0014749 | 0.0014626 | 0.0014504 | 0.0014381 | 0.0014259 | 0.0014136 | 0.0014014 | 0.0013891 | 0.0013769 | 0.0013646 | 0.0013524 | 0.0013401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-80121007 | 7 | 7 | 2.93e-05 | 0 | 4.65e-05 | 0 | 3.9e-05 | 0 | 4.9143e-07 | -3.75e-07 | 4.4534e-05 | 4.5026e-05 | 4.5517e-05 | 4.6009e-05 | 4.65e-05 | 4.6125e-05 | 4.575e-05 | 4.5375e-05 | 4.5e-05 | 4.4625e-05 | 4.425e-05 | 4.3875e-05 | 4.35e-05 | 4.3125e-05 | 4.275e-05 | 4.2375e-05 | 4.2e-05 | 4.1625e-05 | 4.125e-05 | 4.0875e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-80919181 | 67 | 67 | 0.0028477 | 0 | 0.0043163 | 0 | 0.0034885 | 0 | 4.1959e-05 | -4.1389e-05 | 0.0041485 | 0.0041904 | 0.0042324 | 0.0042743 | 0.0043163 | 0.0042749 | 0.0042335 | 0.0041921 | 0.0041507 | 0.0041093 | 0.004068 | 0.0040266 | 0.0039852 | 0.0039438 | 0.0039024 | 0.003861 | 0.0038196 | 0.0037782 | 0.0037368 | 0.0036955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC004-15400582 | 2439 | 1672 | 0.0038368 | 0.0018734 | 0.0049793 | 0.0027942 | 0.0045733 | 0.0025071 | 3.2644e-05 | -2.0298e-05 | 0.0048487 | 0.0048814 | 0.004914 | 0.0049467 | 0.0049793 | 0.004959 | 0.0049387 | 0.0049184 | 0.0048981 | 0.0048778 | 0.0048575 | 0.0048372 | 0.0048169 | 0.0047966 | 0.0047763 | 0.004756 | 0.0047357 | 0.0047154 | 0.0046951 | 0.0046748 | 2.6309e-05 | -1.4352e-05 | 0.0026889 | 0.0027152 | 0.0027415 | 0.0027679 | 0.0027942 | 0.0027798 | 0.0027655 | 0.0027511 | 0.0027368 | 0.0027224 | 0.002708 | 0.0026937 | 0.0026793 | 0.002665 | 0.0026506 | 0.0026363 | 0.0026219 | 0.0026076 | 0.0025932 | 0.0025789
| CLC004-176886107 | 27 | 27 | 2.6e-05 | 0 | 3.9e-05 | 0 | 3.71e-05 | 0 | 3.7143e-07 | -9.5e-08 | 3.7514e-05 | 3.7886e-05 | 3.8257e-05 | 3.8629e-05 | 3.9e-05 | 3.8905e-05 | 3.881e-05 | 3.8715e-05 | 3.862e-05 | 3.8525e-05 | 3.843e-05 | 3.8335e-05 | 3.824e-05 | 3.8145e-05 | 3.805e-05 | 3.7955e-05 | 3.786e-05 | 3.7765e-05 | 3.767e-05 | 3.7575e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC004-201015049 | 227 | 200 | 0.0040823 | 2.06e-05 | 0.0057284 | 3.14e-05 | 0.0050891 | 2.77e-05 | 4.7032e-05 | -3.1963e-05 | 0.0055402 | 0.0055873 | 0.0056343 | 0.0056813 | 0.0057284 | 0.0056964 | 0.0056644 | 0.0056325 | 0.0056005 | 0.0055685 | 0.0055366 | 0.0055046 | 0.0054727 | 0.0054407 | 0.0054087 | 0.0053768 | 0.0053448 | 0.0053128 | 0.0052809 | 0.0052489 | 3.0857e-07 | -1.85e-07 | 3.0166e-05 | 3.0474e-05 | 3.0783e-05 | 3.1091e-05 | 3.14e-05 | 3.1215e-05 | 3.103e-05 | 3.0845e-05 | 3.066e-05 | 3.0475e-05 | 3.029e-05 | 3.0105e-05 | 2.992e-05 | 2.9735e-05 | 2.955e-05 | 2.9365e-05 | 2.918e-05 | 2.8995e-05 | 2.881e-05 | 2.8625e-05
| CLC004-24597506 | 540 | 540 | 0.0054799 | 0 | 0.0070405 | 0 | 0.006377 | 0 | 4.459e-05 | -3.3178e-05 | 0.0068622 | 0.0069068 | 0.0069513 | 0.0069959 | 0.0070405 | 0.0070073 | 0.0069742 | 0.006941 | 0.0069078 | 0.0068746 | 0.0068415 | 0.0068083 | 0.0067751 | 0.0067419 | 0.0067087 | 0.0066756 | 0.0066424 | 0.0066092 | 0.006576 | 0.0065429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-142438034 | 18 | 18 | 9.6e-05 | 0 | 0.00016557 | 0 | 0.00016556 | 0 | 1.9878e-06 | -6e-10 | 0.00015762 | 0.00015961 | 0.0001616 | 0.00016358 | 0.00016557 | 0.00016557 | 0.00016557 | 0.00016557 | 0.00016557 | 0.00016557 | 0.00016557 | 0.00016557 | 0.00016557 | 0.00016557 | 0.00016557 | 0.00016557 | 0.00016556 | 0.00016556 | 0.00016556 | 0.00016556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-142438492 | 17 | 17 | 0.0014919 | 0 | 0.0018477 | 0 | 0.001796 | 0 | 1.0166e-05 | -2.584e-06 | 0.001807 | 0.0018172 | 0.0018274 | 0.0018375 | 0.0018477 | 0.0018451 | 0.0018425 | 0.0018399 | 0.0018374 | 0.0018348 | 0.0018322 | 0.0018296 | 0.001827 | 0.0018244 | 0.0018218 | 0.0018193 | 0.0018167 | 0.0018141 | 0.0018115 | 0.0018089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-144337956 | 28 | 28 | 0.001802 | 0 | 0.0025251 | 0 | 0.002278 | 0 | 2.0659e-05 | -1.2352e-05 | 0.0024424 | 0.0024631 | 0.0024838 | 0.0025044 | 0.0025251 | 0.0025127 | 0.0025004 | 0.002488 | 0.0024757 | 0.0024633 | 0.002451 | 0.0024386 | 0.0024263 | 0.0024139 | 0.0024015 | 0.0023892 | 0.0023768 | 0.0023645 | 0.0023521 | 0.0023398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-144337978 | 12 | 12 | 0.0010897 | 0 | 0.0014953 | 0 | 0.0014463 | 0 | 1.159e-05 | -2.4482e-06 | 0.0014489 | 0.0014605 | 0.0014721 | 0.0014837 | 0.0014953 | 0.0014928 | 0.0014904 | 0.001488 | 0.0014855 | 0.0014831 | 0.0014806 | 0.0014782 | 0.0014757 | 0.0014733 | 0.0014708 | 0.0014684 | 0.0014659 | 0.0014635 | 0.001461 | 0.0014586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-15400532 | 1565 | 587 | 0.006085 | 0.0011785 | 0.0067515 | 0.0018233 | 0.0063996 | 0.0016488 | 1.9044e-05 | -1.7595e-05 | 0.0066753 | 0.0066944 | 0.0067134 | 0.0067325 | 0.0067515 | 0.0067339 | 0.0067163 | 0.0066987 | 0.0066811 | 0.0066635 | 0.0066459 | 0.0066284 | 0.0066108 | 0.0065932 | 0.0065756 | 0.006558 | 0.0065404 | 0.0065228 | 0.0065052 | 0.0064876 | 1.8421e-05 | -8.7246e-06 | 0.0017496 | 0.001768 | 0.0017864 | 0.0018048 | 0.0018232 | 0.0018145 | 0.0018058 | 0.0017971 | 0.0017884 | 0.0017796 | 0.0017709 | 0.0017622 | 0.0017535 | 0.0017447 | 0.001736 | 0.0017273 | 0.0017186 | 0.0017098 | 0.0017011 | 0.0016924
| CLC006-154827505 | 12 | 12 | 1.73e-05 | 0 | 3.01e-05 | 0 | 2.98e-05 | 0 | 3.6571e-07 | -1.5e-08 | 2.8637e-05 | 2.9003e-05 | 2.9369e-05 | 2.9734e-05 | 3.01e-05 | 3.0085e-05 | 3.007e-05 | 3.0055e-05 | 3.004e-05 | 3.0025e-05 | 3.001e-05 | 2.9995e-05 | 2.998e-05 | 2.9965e-05 | 2.995e-05 | 2.9935e-05 | 2.992e-05 | 2.9905e-05 | 2.989e-05 | 2.9875e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-154827674 | 21 | 21 | 0.00075736 | 0 | 0.0011299 | 0 | 0.00099947 | 0 | 1.0645e-05 | -6.5224e-06 | 0.0010873 | 0.001098 | 0.0011086 | 0.0011193 | 0.0011299 | 0.0011234 | 0.0011169 | 0.0011103 | 0.0011038 | 0.0010973 | 0.0010908 | 0.0010843 | 0.0010777 | 0.0010712 | 0.0010647 | 0.0010582 | 0.0010516 | 0.0010451 | 0.0010386 | 0.0010321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-154827847 | 5 | 5 | 0.00099915 | 0 | 0.0010028 | 0 | 0.00099809 | 0 | 1.0554e-07 | -2.3795e-07 | 0.0010024 | 0.0010025 | 0.0010026 | 0.0010027 | 0.0010028 | 0.0010026 | 0.0010024 | 0.0010021 | 0.0010019 | 0.0010017 | 0.0010014 | 0.0010012 | 0.0010009 | 0.0010007 | 0.0010005 | 0.0010002 | 0.00099999 | 0.00099975 | 0.00099951 | 0.00099928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-154828072 | 35 | 35 | 0.00076064 | 0 | 0.0010964 | 0 | 0.0010071 | 0 | 9.5936e-06 | -4.4658e-06 | 0.001058 | 0.0010676 | 0.0010772 | 0.0010868 | 0.0010964 | 0.0010919 | 0.0010875 | 0.001083 | 0.0010786 | 0.0010741 | 0.0010696 | 0.0010652 | 0.0010607 | 0.0010562 | 0.0010518 | 0.0010473 | 0.0010428 | 0.0010384 | 0.0010339 | 0.0010294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-154828287 | 21 | 21 | 0.00082855 | 0 | 0.0014249 | 0 | 0.0013109 | 0 | 1.7038e-05 | -5.6997e-06 | 0.0013567 | 0.0013738 | 0.0013908 | 0.0014078 | 0.0014249 | 0.0014192 | 0.0014135 | 0.0014078 | 0.0014021 | 0.0013964 | 0.0013907 | 0.001385 | 0.0013793 | 0.0013736 | 0.0013679 | 0.0013622 | 0.0013565 | 0.0013508 | 0.0013451 | 0.0013394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-154828396 | 32 | 32 | 0.0019115 | 0 | 0.0032348 | 0 | 0.0029844 | 0 | 3.781e-05 | -1.2523e-05 | 0.0030836 | 0.0031214 | 0.0031592 | 0.003197 | 0.0032348 | 0.0032223 | 0.0032098 | 0.0031973 | 0.0031848 | 0.0031722 | 0.0031597 | 0.0031472 | 0.0031347 | 0.0031221 | 0.0031096 | 0.0030971 | 0.0030846 | 0.003072 | 0.0030595 | 0.003047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-154907356 | 10 | 10 | 0.00054676 | 0 | 0.0008459 | 0 | 0.00080266 | 0 | 8.5469e-06 | -2.1622e-06 | 0.00081171 | 0.00082026 | 0.00082881 | 0.00083736 | 0.0008459 | 0.00084374 | 0.00084158 | 0.00083942 | 0.00083725 | 0.00083509 | 0.00083293 | 0.00083077 | 0.0008286 | 0.00082644 | 0.00082428 | 0.00082212 | 0.00081996 | 0.00081779 | 0.00081563 | 0.00081347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-156831394 | 604 | 366 | 0.0034178 | 0.0021142 | 0.0052141 | 0.0033423 | 0.0049732 | 0.0031733 | 5.1324e-05 | -1.2042e-05 | 0.0050088 | 0.0050601 | 0.0051114 | 0.0051628 | 0.0052141 | 0.005202 | 0.00519 | 0.005178 | 0.0051659 | 0.0051539 | 0.0051418 | 0.0051298 | 0.0051177 | 0.0051057 | 0.0050937 | 0.0050816 | 0.0050696 | 0.0050575 | 0.0050455 | 0.0050335 | 3.5088e-05 | -8.4535e-06 | 0.003202 | 0.0032371 | 0.0032722 | 0.0033072 | 0.0033423 | 0.0033339 | 0.0033254 | 0.003317 | 0.0033085 | 0.0033001 | 0.0032916 | 0.0032832 | 0.0032747 | 0.0032662 | 0.0032578 | 0.0032493 | 0.0032409 | 0.0032324 | 0.003224 | 0.0032155
| CLC006-44811375 | 295 | 295 | 0.0034744 | 0 | 0.005202 | 0 | 0.0049303 | 0 | 4.9362e-05 | -1.3584e-05 | 0.0050046 | 0.0050539 | 0.0051033 | 0.0051527 | 0.005202 | 0.0051884 | 0.0051749 | 0.0051613 | 0.0051477 | 0.0051341 | 0.0051205 | 0.0051069 | 0.0050933 | 0.0050798 | 0.0050662 | 0.0050526 | 0.005039 | 0.0050254 | 0.0050118 | 0.0049983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-80819775 | 58 | 58 | 0.0019992 | 0 | 0.0032098 | 0 | 0.0029816 | 0 | 3.459e-05 | -1.141e-05 | 0.0030715 | 0.0031061 | 0.0031407 | 0.0031753 | 0.0032098 | 0.0031984 | 0.003187 | 0.0031756 | 0.0031642 | 0.0031528 | 0.0031414 | 0.00313 | 0.0031186 | 0.0031072 | 0.0030957 | 0.0030843 | 0.0030729 | 0.0030615 | 0.0030501 | 0.0030387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC006-80819849 | 48 | 48 | 0.0004918 | 0 | 0.0008901 | 0 | 0.00081922 | 0 | 1.138e-05 | -3.5441e-06 | 0.00084458 | 0.00085596 | 0.00086734 | 0.00087872 | 0.00089011 | 0.00088656 | 0.00088302 | 0.00087947 | 0.00087593 | 0.00087238 | 0.00086884 | 0.0008653 | 0.00086175 | 0.00085821 | 0.00085466 | 0.00085112 | 0.00084758 | 0.00084403 | 0.00084049 | 0.00083694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013-120141536 | 31 | 31 | 0.0014331 | 0 | 0.0022457 | 0 | 0.0017787 | 0 | 2.3217e-05 | -2.3348e-05 | 0.0021528 | 0.002176 | 0.0021992 | 0.0022225 | 0.0022457 | 0.0022223 | 0.002199 | 0.0021756 | 0.0021523 | 0.0021289 | 0.0021056 | 0.0020822 | 0.0020589 | 0.0020355 | 0.0020122 | 0.0019888 | 0.0019655 | 0.0019422 | 0.0019188 | 0.0018955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013-155048935 | 9 | 9 | 7.95e-05 | 0 | 0.00010937 | 0 | 0.0001038 | 0 | 8.5349e-07 | -2.7855e-07 | 0.00010596 | 0.00010681 | 0.00010767 | 0.00010852 | 0.00010937 | 0.00010909 | 0.00010881 | 0.00010854 | 0.00010826 | 0.00010798 | 0.0001077 | 0.00010742 | 0.00010714 | 0.00010687 | 0.00010659 | 0.00010631 | 0.00010603 | 0.00010575 | 0.00010547 | 0.00010519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013-155049125 | 24 | 24 | 0.003618 | 0 | 0.0045996 | 0 | 0.0042155 | 0 | 2.8045e-05 | -1.9206e-05 | 0.0044874 | 0.0045154 | 0.0045435 | 0.0045715 | 0.0045996 | 0.0045804 | 0.0045612 | 0.004542 | 0.0045228 | 0.0045036 | 0.0044843 | 0.0044651 | 0.0044459 | 0.0044267 | 0.0044075 | 0.0043883 | 0.0043691 | 0.0043499 | 0.0043307 | 0.0043115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013-155049446 | 15 | 15 | 0.0015107 | 0 | 0.002357 | 0 | 0.0020167 | 0 | 2.418e-05 | -1.7015e-05 | 0.0022603 | 0.0022845 | 0.0023086 | 0.0023328 | 0.002357 | 0.00234 | 0.002323 | 0.002306 | 0.0022889 | 0.0022719 | 0.0022549 | 0.0022379 | 0.0022209 | 0.0022039 | 0.0021869 | 0.0021698 | 0.0021528 | 0.0021358 | 0.0021188 | 0.0021018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013-155049582 | 25 | 25 | 0.00024139 | 0 | 0.0005466 | 0 | 0.00030562 | 0 | 8.7203e-06 | -1.2049e-05 | 0.00051172 | 0.00052044 | 0.00052916 | 0.00053788 | 0.0005466 | 0.00053455 | 0.0005225 | 0.00051046 | 0.00049841 | 0.00048636 | 0.00047431 | 0.00046226 | 0.00045021 | 0.00043816 | 0.00042611 | 0.00041406 | 0.00040201 | 0.00038996 | 0.00037792 | 0.00036587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013-155079387 | 7 | 7 | 0.0002869 | 0 | 0.00046768 | 0 | 0.00033708 | 0 | 5.1653e-06 | -6.5301e-06 | 0.00044702 | 0.00045219 | 0.00045735 | 0.00046252 | 0.00046768 | 0.00046115 | 0.00045462 | 0.00044809 | 0.00044156 | 0.00043503 | 0.0004285 | 0.00042197 | 0.00041544 | 0.00040891 | 0.00040238 | 0.00039585 | 0.00038932 | 0.00038279 | 0.00037626 | 0.00036973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013-155079659 | 10 | 10 | 0.0020776 | 0 | 0.0031058 | 0 | 0.0027387 | 0 | 2.9378e-05 | -1.8356e-05 | 0.0029883 | 0.0030177 | 0.0030471 | 0.0030765 | 0.0031058 | 0.0030875 | 0.0030691 | 0.0030508 | 0.0030324 | 0.0030141 | 0.0029957 | 0.0029774 | 0.002959 | 0.0029406 | 0.0029223 | 0.0029039 | 0.0028856 | 0.0028672 | 0.0028489 | 0.0028305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013-161744857 | 4416 | 0 | 0.0065693 | 0.0033898 | 0.008283 | 0.0052138 | 0.007452 | 0.0044724 | 4.8962e-05 | -4.155e-05 | 0.0080871 | 0.0081361 | 0.0081851 | 0.008234 | 0.008283 | 0.0082414 | 0.0081999 | 0.0081583 | 0.0081168 | 0.0080752 | 0.0080337 | 0.0079921 | 0.0079506 | 0.007909 | 0.0078675 | 0.0078259 | 0.0077844 | 0.0077428 | 0.0077013 | 0.0076597 | 5.2114e-05 | -3.7066e-05 | 0.0050053 | 0.0050574 | 0.0051095 | 0.0051617 | 0.0052138 | 0.0051767 | 0.0051396 | 0.0051026 | 0.0050655 | 0.0050284 | 0.0049914 | 0.0049543 | 0.0049172 | 0.0048802 | 0.0048431 | 0.004806 | 0.004769 | 0.0047319 | 0.0046948 | 0.0046578
| CLC013-24598538 | 53 | 53 | 0.0011665 | 0 | 0.0016351 | 0 | 0.0014463 | 0 | 1.3386e-05 | -9.4367e-06 | 0.0015815 | 0.0015949 | 0.0016083 | 0.0016217 | 0.0016351 | 0.0016256 | 0.0016162 | 0.0016067 | 0.0015973 | 0.0015879 | 0.0015784 | 0.001569 | 0.0015596 | 0.0015501 | 0.0015407 | 0.0015313 | 0.0015218 | 0.0015124 | 0.0015029 | 0.0014935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013-24598566 | 48 | 48 | 0.0029856 | 0 | 0.0037918 | 0 | 0.0034635 | 0 | 2.3033e-05 | -1.6414e-05 | 0.0036996 | 0.0037227 | 0.0037457 | 0.0037687 | 0.0037918 | 0.0037753 | 0.0037589 | 0.0037425 | 0.0037261 | 0.0037097 | 0.0036933 | 0.0036769 | 0.0036604 | 0.003644 | 0.0036276 | 0.0036112 | 0.0035948 | 0.0035784 | 0.003562 | 0.0035455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013-24602770 | 3116 | 1533 | 0.0011432 | 7.76e-05 | 0.0018927 | 0.00014723 | 0.0013157 | 9.41e-05 | 2.1415e-05 | -2.8851e-05 | 0.0018071 | 0.0018285 | 0.0018499 | 0.0018713 | 0.0018927 | 0.0018639 | 0.001835 | 0.0018062 | 0.0017773 | 0.0017485 | 0.0017196 | 0.0016908 | 0.0016619 | 0.0016331 | 0.0016042 | 0.0015754 | 0.0015465 | 0.0015177 | 0.0014888 | 0.00146 | 1.9893e-06 | -2.6563e-06 | 0.00013927 | 0.00014126 | 0.00014325 | 0.00014524 | 0.00014723 | 0.00014457 | 0.00014191 | 0.00013926 | 0.0001366 | 0.00013394 | 0.00013129 | 0.00012863 | 0.00012598 | 0.00012332 | 0.00012066 | 0.00011801 | 0.00011535 | 0.00011269 | 0.00011004 | 0.00010738
| CLC013-24602784 | 631 | 631 | 0.007356 | 0 | 0.010766 | 0 | 0.0079749 | 0 | 9.7429e-05 | -0.00013955 | 0.010376 | 0.010474 | 0.010571 | 0.010669 | 0.010766 | 0.010626 | 0.010487 | 0.010347 | 0.010208 | 0.010068 | 0.0099287 | 0.0097891 | 0.0096495 | 0.00951 | 0.0093704 | 0.0092309 | 0.0090913 | 0.0089518 | 0.0088122 | 0.0086727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013-40996443 | 4281 | 455 | 0.0030725 | 0.00063119 | 0.0033314 | 0.00064997 | 0.0030145 | 0.00062685 | 7.3957e-06 | -1.5846e-05 | 0.0033018 | 0.0033092 | 0.0033166 | 0.003324 | 0.0033314 | 0.0033155 | 0.0032997 | 0.0032838 | 0.003268 | 0.0032522 | 0.0032363 | 0.0032205 | 0.0032046 | 0.0031888 | 0.0031729 | 0.0031571 | 0.0031412 | 0.0031254 | 0.0031095 | 0.0030937 | 5.3646e-07 | -1.1557e-06 | 0.00064782 | 0.00064836 | 0.0006489 | 0.00064943 | 0.00064997 | 0.00064881 | 0.00064766 | 0.0006465 | 0.00064535 | 0.00064419 | 0.00064303 | 0.00064188 | 0.00064072 | 0.00063957 | 0.00063841 | 0.00063726 | 0.0006361 | 0.00063494 | 0.00063379 | 0.00063263
| CLC013-77737876 | 14 | 14 | 0.00010635 | 0 | 0.0001273 | 0 | 0.00011898 | 0 | 5.9863e-07 | -4.1625e-07 | 0.00012491 | 0.00012551 | 0.0001261 | 0.0001267 | 0.0001273 | 0.00012688 | 0.00012647 | 0.00012605 | 0.00012564 | 0.00012522 | 0.0001248 | 0.00012439 | 0.00012397 | 0.00012355 | 0.00012314 | 0.00012272 | 0.00012231 | 0.00012189 | 0.00012147 | 0.00012106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013-77738225 | 3 | 3 | 4.65e-05 | 0 | 4.65e-05 | 0 | 4.65e-05 | 0 | 0 | 0 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 4.65e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC014-119350337 | 572 | 572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC014-161744928 | 1497 | 925 | 0.010915 | 0 | 0.014906 | 0 | 0.013283 | 0 | 0.00011402 | -8.1124e-05 | 0.01445 | 0.014564 | 0.014678 | 0.014792 | 0.014906 | 0.014825 | 0.014744 | 0.014662 | 0.014581 | 0.0145 | 0.014419 | 0.014338 | 0.014257 | 0.014176 | 0.014095 | 0.014013 | 0.013932 | 0.013851 | 0.01377 | 0.013689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME014-15423823 | 3712 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME014-15423849 | 3710 | 1459 | 0.038559 | 0 | 0.046704 | 0 | 0.0508 | 0 | 0.0002327 | 0.00020482 | 0.045773 | 0.046006 | 0.046239 | 0.046471 | 0.046704 | 0.046909 | 0.047114 | 0.047319 | 0.047523 | 0.047728 | 0.047933 | 0.048138 | 0.048343 | 0.048547 | 0.048752 | 0.048957 | 0.049162 | 0.049367 | 0.049572 | 0.049776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME014-24612269 | 2251 | 2251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME015-15423773 | 1238 | 298 | 0.0029928 | 0.00090584 | 0.0039898 | 0.0012215 | 0.0044592 | 0.0013767 | 2.8487e-05 | 2.3468e-05 | 0.0038759 | 0.0039044 | 0.0039328 | 0.0039613 | 0.0039898 | 0.0040133 | 0.0040368 | 0.0040602 | 0.0040837 | 0.0041072 | 0.0041306 | 0.0041541 | 0.0041776 | 0.004201 | 0.0042245 | 0.004248 | 0.0042714 | 0.0042949 | 0.0043184 | 0.0043418 | 9.0187e-06 | 7.7576e-06 | 0.0011854 | 0.0011944 | 0.0012035 | 0.0012125 | 0.0012215 | 0.0012293 | 0.001237 | 0.0012448 | 0.0012525 | 0.0012603 | 0.001268 | 0.0012758 | 0.0012836 | 0.0012913 | 0.0012991 | 0.0013068 | 0.0013146 | 0.0013223 | 0.0013301 | 0.0013379
| CME015-182988165 | 940 | 940 | 0.0084208 | 0 | 0.01065 | 0 | 0.011759 | 0 | 6.3693e-05 | 5.5435e-05 | 0.010395 | 0.010459 | 0.010523 | 0.010586 | 0.01065 | 0.010705 | 0.010761 | 0.010816 | 0.010872 | 0.010927 | 0.010983 | 0.011038 | 0.011094 | 0.011149 | 0.011204 | 0.01126 | 0.011315 | 0.011371 | 0.011426 | 0.011482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME016-142932211 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME016-142932557 | 26 | 26 | 0.0015821 | 0 | 0.002001 | 0 | 0.0023061 | 0 | 1.1969e-05 | 1.5254e-05 | 0.0019531 | 0.0019651 | 0.0019771 | 0.001989 | 0.002001 | 0.0020162 | 0.0020315 | 0.0020468 | 0.002062 | 0.0020773 | 0.0020925 | 0.0021078 | 0.002123 | 0.0021383 | 0.0021535 | 0.0021688 | 0.002184 | 0.0021993 | 0.0022146 | 0.0022298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME016-142932825 | 28 | 28 | 0.00099816 | 0 | 0.0012898 | 0 | 0.0014227 | 0 | 8.3316e-06 | 6.6452e-06 | 0.0012564 | 0.0012648 | 0.0012731 | 0.0012814 | 0.0012898 | 0.0012964 | 0.0013031 | 0.0013097 | 0.0013163 | 0.001323 | 0.0013296 | 0.0013363 | 0.0013429 | 0.0013496 | 0.0013562 | 0.0013629 | 0.0013695 | 0.0013762 | 0.0013828 | 0.0013894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME016-142933135 | 35 | 35 | 0.0019863 | 0 | 0.0024858 | 0 | 0.0029449 | 0 | 1.4272e-05 | 2.2957e-05 | 0.0024287 | 0.002443 | 0.0024573 | 0.0024715 | 0.0024858 | 0.0025088 | 0.0025317 | 0.0025547 | 0.0025776 | 0.0026006 | 0.0026235 | 0.0026465 | 0.0026695 | 0.0026924 | 0.0027154 | 0.0027383 | 0.0027613 | 0.0027842 | 0.0028072 | 0.0028302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME016-154143626 | 603 | 568 | 0.0038774 | 0.00070585 | 0.0045756 | 0.00083285 | 0.0055711 | 0.0010216 | 1.9949e-05 | 4.977e-05 | 0.0044959 | 0.0045158 | 0.0045358 | 0.0045557 | 0.0045756 | 0.0046254 | 0.0046752 | 0.004725 | 0.0047747 | 0.0048245 | 0.0048743 | 0.004924 | 0.0049738 | 0.0050236 | 0.0050734 | 0.0051231 | 0.0051729 | 0.0052227 | 0.0052724 | 0.0053222 | 3.6285e-06 | 9.4358e-06 | 0.00081834 | 0.00082196 | 0.00082559 | 0.00082922 | 0.00083285 | 0.00084229 | 0.00085172 | 0.00086116 | 0.00087059 | 0.00088003 | 0.00088946 | 0.0008989 | 0.00090834 | 0.00091777 | 0.00092721 | 0.00093664 | 0.00094608 | 0.00095551 | 0.00096495 | 0.00097439
| CME016-15423749 | 2680 | 241 | 0.03866 | 0.00096143 | 0.046646 | 0.0012508 | 0.050348 | 0.0014744 | 0.00022817 | 0.0001851 | 0.045733 | 0.045961 | 0.046189 | 0.046418 | 0.046646 | 0.046831 | 0.047016 | 0.047201 | 0.047386 | 0.047571 | 0.047756 | 0.047941 | 0.048127 | 0.048312 | 0.048497 | 0.048682 | 0.048867 | 0.049052 | 0.049237 | 0.049422 | 8.2672e-06 | 1.1183e-05 | 0.0012177 | 0.001226 | 0.0012342 | 0.0012425 | 0.0012508 | 0.001262 | 0.0012731 | 0.0012843 | 0.0012955 | 0.0013067 | 0.0013179 | 0.0013291 | 0.0013402 | 0.0013514 | 0.0013626 | 0.0013738 | 0.001385 | 0.0013962 | 0.0014073 | 0.0014185
| CME016-163066872 | 48 | 48 | 1.88e-05 | 0 | 2.68e-05 | 0 | 3.37e-05 | 0 | 2.2857e-07 | 3.45e-07 | 2.5886e-05 | 2.6114e-05 | 2.6343e-05 | 2.6571e-05 | 2.68e-05 | 2.7145e-05 | 2.749e-05 | 2.7835e-05 | 2.818e-05 | 2.8525e-05 | 2.887e-05 | 2.9215e-05 | 2.956e-05 | 2.9905e-05 | 3.025e-05 | 3.0595e-05 | 3.094e-05 | 3.1285e-05 | 3.163e-05 | 3.1975e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME016-171344649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME016-24605950 | 1769 | 1118 | 1.27e-05 | 1.91e-05 | 1.65e-05 | 2.48e-05 | 1.95e-05 | 2.93e-05 | 1.0857e-07 | 1.5e-07 | 1.6066e-05 | 1.6174e-05 | 1.6283e-05 | 1.6391e-05 | 1.65e-05 | 1.665e-05 | 1.68e-05 | 1.695e-05 | 1.71e-05 | 1.725e-05 | 1.74e-05 | 1.755e-05 | 1.77e-05 | 1.785e-05 | 1.8e-05 | 1.815e-05 | 1.83e-05 | 1.845e-05 | 1.86e-05 | 1.875e-05 | 1.6286e-07 | 2.25e-07 | 2.4149e-05 | 2.4311e-05 | 2.4474e-05 | 2.4637e-05 | 2.48e-05 | 2.5025e-05 | 2.525e-05 | 2.5475e-05 | 2.57e-05 | 2.5925e-05 | 2.615e-05 | 2.6375e-05 | 2.66e-05 | 2.6825e-05 | 2.705e-05 | 2.7275e-05 | 2.75e-05 | 2.7725e-05 | 2.795e-05 | 2.8175e-05
| CME016-68675557 | 2389 | 592 | 0.00022056 | 0.00014697 | 0.0002824 | 0.00018933 | 0.00033523 | 0.00022607 | 1.7667e-06 | 2.6415e-06 | 0.00027533 | 0.0002771 | 0.00027886 | 0.00028063 | 0.0002824 | 0.00028504 | 0.00028768 | 0.00029032 | 0.00029296 | 0.00029561 | 0.00029825 | 0.00030089 | 0.00030353 | 0.00030617 | 0.00030881 | 0.00031146 | 0.0003141 | 0.00031674 | 0.00031938 | 0.00032202 | 1.2102e-06 | 1.8372e-06 | 0.00018449 | 0.0001857 | 0.00018691 | 0.00018812 | 0.00018933 | 0.00019116 | 0.000193 | 0.00019484 | 0.00019667 | 0.00019851 | 0.00020035 | 0.00020219 | 0.00020402 | 0.00020586 | 0.0002077 | 0.00020954 | 0.00021137 | 0.00021321 | 0.00021505 | 0.00021688
| CME021-15423551 | 2092 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME021-15423564 | 2087 | 923 | 0.0035791 | 0.00091388 | 0.0042911 | 0.0011867 | 0.0044749 | 0.0013379 | 2.0345e-05 | 9.1856e-06 | 0.0042098 | 0.0042301 | 0.0042505 | 0.0042708 | 0.0042911 | 0.0043003 | 0.0043095 | 0.0043187 | 0.0043279 | 0.0043371 | 0.0043463 | 0.0043554 | 0.0043646 | 0.0043738 | 0.004383 | 0.0043922 | 0.0044014 | 0.0044106 | 0.0044197 | 0.0044289 | 7.7959e-06 | 7.5567e-06 | 0.0011556 | 0.0011634 | 0.0011711 | 0.0011789 | 0.0011867 | 0.0011943 | 0.0012019 | 0.0012094 | 0.001217 | 0.0012245 | 0.0012321 | 0.0012396 | 0.0012472 | 0.0012548 | 0.0012623 | 0.0012699 | 0.0012774 | 0.001285 | 0.0012925 | 0.0013001
| CME021-184455628 | 1164 | 1164 | 0.0052243 | 0 | 0.0067101 | 0 | 0.0075144 | 0 | 4.2449e-05 | 4.0216e-05 | 0.0065403 | 0.0065827 | 0.0066252 | 0.0066676 | 0.0067101 | 0.0067503 | 0.0067905 | 0.0068307 | 0.0068709 | 0.0069111 | 0.0069513 | 0.0069916 | 0.0070318 | 0.007072 | 0.0071122 | 0.0071524 | 0.0071926 | 0.0072329 | 0.0072731 | 0.0073133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME022-15423527 | 450 | 450 | 9.71e-05 | 0 | 0.00013352 | 0 | 0.00015941 | 0 | 1.0406e-06 | 1.2947e-06 | 0.00012936 | 0.0001304 | 0.00013144 | 0.00013248 | 0.00013352 | 0.00013481 | 0.00013611 | 0.0001374 | 0.0001387 | 0.00013999 | 0.00014129 | 0.00014258 | 0.00014388 | 0.00014517 | 0.00014647 | 0.00014776 | 0.00014906 | 0.00015035 | 0.00015165 | 0.00015294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN001-124828418 | 1054 | 970 | 0.038719 | 0.0070182 | 0.05232 | 0.0096854 | 0.055119 | 0.010234 | 0.00038859 | 0.00013998 | 0.050765 | 0.051154 | 0.051543 | 0.051931 | 0.05232 | 0.05246 | 0.0526 | 0.05274 | 0.05288 | 0.05302 | 0.05316 | 0.0533 | 0.05344 | 0.05358 | 0.05372 | 0.05386 | 0.054 | 0.054139 | 0.054279 | 0.054419 | 7.6206e-05 | 2.7435e-05 | 0.0093806 | 0.0094568 | 0.009533 | 0.0096092 | 0.0096854 | 0.0097129 | 0.0097403 | 0.0097677 | 0.0097952 | 0.0098226 | 0.0098501 | 0.0098775 | 0.0099049 | 0.0099324 | 0.0099598 | 0.0099872 | 0.010015 | 0.010042 | 0.01007 | 0.010097
| CMN001-132430534 | 1388 | 948 | 0.011842 | 0.003452 | 0.015291 | 0.0045039 | 0.016038 | 0.00474 | 9.8531e-05 | 3.7339e-05 | 0.014897 | 0.014995 | 0.015094 | 0.015192 | 0.015291 | 0.015328 | 0.015366 | 0.015403 | 0.01544 | 0.015478 | 0.015515 | 0.015552 | 0.01559 | 0.015627 | 0.015664 | 0.015702 | 0.015739 | 0.015776 | 0.015814 | 0.015851 | 3.0054e-05 | 1.1809e-05 | 0.0043836 | 0.0044137 | 0.0044438 | 0.0044738 | 0.0045039 | 0.0045157 | 0.0045275 | 0.0045393 | 0.0045511 | 0.0045629 | 0.0045747 | 0.0045865 | 0.0045983 | 0.0046101 | 0.0046219 | 0.0046338 | 0.0046456 | 0.0046574 | 0.0046692 | 0.004681
| CMN001-15420462 | 4990 | 1490 | 0.021655 | 0.017707 | 0.025414 | 0.022912 | 0.025757 | 0.024016 | 0.00010737 | 1.7187e-05 | 0.024984 | 0.025091 | 0.025199 | 0.025306 | 0.025414 | 0.025431 | 0.025448 | 0.025465 | 0.025482 | 0.025499 | 0.025517 | 0.025534 | 0.025551 | 0.025568 | 0.025585 | 0.025603 | 0.02562 | 0.025637 | 0.025654 | 0.025671 | 0.00014871 | 5.5209e-05 | 0.022317 | 0.022466 | 0.022615 | 0.022764 | 0.022912 | 0.022967 | 0.023023 | 0.023078 | 0.023133 | 0.023188 | 0.023244 | 0.023299 | 0.023354 | 0.023409 | 0.023464 | 0.02352 | 0.023575 | 0.02363 | 0.023685 | 0.02374
| CMN001-156820944 | 2010 | 932 | 0.050522 | 0.019688 | 0.060745 | 0.02468 | 0.063783 | 0.026676 | 0.00029208 | 0.00015191 | 0.059576 | 0.059868 | 0.06016 | 0.060452 | 0.060745 | 0.060896 | 0.061048 | 0.0612 | 0.061352 | 0.061504 | 0.061656 | 0.061808 | 0.06196 | 0.062112 | 0.062264 | 0.062416 | 0.062567 | 0.062719 | 0.062871 | 0.063023 | 0.00014263 | 9.9763e-05 | 0.02411 | 0.024252 | 0.024395 | 0.024538 | 0.02468 | 0.02478 | 0.02488 | 0.02498 | 0.025079 | 0.025179 | 0.025279 | 0.025379 | 0.025478 | 0.025578 | 0.025678 | 0.025778 | 0.025877 | 0.025977 | 0.026077 | 0.026177
| CMN001-163864096 | 24 | 24 | 0.0083322 | 0 | 0.010636 | 0 | 0.011106 | 0 | 6.5827e-05 | 2.347e-05 | 0.010373 | 0.010439 | 0.010504 | 0.01057 | 0.010636 | 0.01066 | 0.010683 | 0.010707 | 0.01073 | 0.010753 | 0.010777 | 0.0108 | 0.010824 | 0.010847 | 0.010871 | 0.010894 | 0.010918 | 0.010941 | 0.010965 | 0.010988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN001-182014538 | 416 | 351 | 0.0090145 | 0.0041175 | 0.012686 | 0.0058983 | 0.012675 | 0.0058965 | 0.00010489 | -5.3015e-07 | 0.012266 | 0.012371 | 0.012476 | 0.012581 | 0.012686 | 0.012685 | 0.012685 | 0.012684 | 0.012684 | 0.012683 | 0.012683 | 0.012682 | 0.012682 | 0.012681 | 0.01268 | 0.01268 | 0.012679 | 0.012679 | 0.012678 | 0.012678 | 5.088e-05 | -9.355e-08 | 0.0056948 | 0.0057457 | 0.0057966 | 0.0058474 | 0.0058983 | 0.0058982 | 0.0058981 | 0.005898 | 0.005898 | 0.0058979 | 0.0058978 | 0.0058977 | 0.0058976 | 0.0058975 | 0.0058974 | 0.0058973 | 0.0058972 | 0.0058971 | 0.005897 | 0.0058969
| CMN001-73767965 | 43 | 43 | 0.0027174 | 0 | 0.0037821 | 0 | 0.0038418 | 0 | 3.0419e-05 | 2.9872e-06 | 0.0036604 | 0.0036908 | 0.0037212 | 0.0037516 | 0.0037821 | 0.0037851 | 0.003788 | 0.003791 | 0.003794 | 0.003797 | 0.0038 | 0.003803 | 0.003806 | 0.003809 | 0.0038119 | 0.0038149 | 0.0038179 | 0.0038209 | 0.0038239 | 0.0038269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN001-73948224 | 27 | 27 | 0.0070336 | 0 | 0.0093091 | 0 | 0.0099465 | 0 | 6.5014e-05 | 3.187e-05 | 0.009049 | 0.0091141 | 0.0091791 | 0.0092441 | 0.0093091 | 0.009341 | 0.0093728 | 0.0094047 | 0.0094366 | 0.0094685 | 0.0095003 | 0.0095322 | 0.0095641 | 0.0095959 | 0.0096278 | 0.0096597 | 0.0096915 | 0.0097234 | 0.0097553 | 0.0097872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN001-73948442 | 14 | 14 | 0.00090001 | 0 | 0.0014008 | 0 | 0.0016247 | 0 | 1.4308e-05 | 1.1198e-05 | 0.0013435 | 0.0013579 | 0.0013722 | 0.0013865 | 0.0014008 | 0.001412 | 0.0014232 | 0.0014344 | 0.0014456 | 0.0014568 | 0.001468 | 0.0014792 | 0.0014904 | 0.0015016 | 0.0015128 | 0.001524 | 0.0015351 | 0.0015463 | 0.0015575 | 0.0015687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN001-74644085 | 65 | 65 | 0.0082481 | 0 | 0.011233 | 0 | 0.012181 | 0 | 8.5294e-05 | 4.7396e-05 | 0.010892 | 0.010977 | 0.011063 | 0.011148 | 0.011233 | 0.011281 | 0.011328 | 0.011376 | 0.011423 | 0.01147 | 0.011518 | 0.011565 | 0.011613 | 0.01166 | 0.011707 | 0.011755 | 0.011802 | 0.01185 | 0.011897 | 0.011944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN001-74644167 | 35 | 35 | 0.011169 | 0 | 0.014946 | 0 | 0.015272 | 0 | 0.0001079 | 1.6314e-05 | 0.014514 | 0.014622 | 0.01473 | 0.014838 | 0.014946 | 0.014962 | 0.014978 | 0.014995 | 0.015011 | 0.015027 | 0.015044 | 0.01506 | 0.015076 | 0.015093 | 0.015109 | 0.015125 | 0.015142 | 0.015158 | 0.015174 | 0.01519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN001-74644242 | 67 | 67 | 0.010147 | 0 | 0.014034 | 0 | 0.014427 | 0 | 0.00011107 | 1.9621e-05 | 0.01359 | 0.013701 | 0.013812 | 0.013923 | 0.014034 | 0.014054 | 0.014073 | 0.014093 | 0.014113 | 0.014132 | 0.014152 | 0.014171 | 0.014191 | 0.014211 | 0.01423 | 0.01425 | 0.01427 | 0.014289 | 0.014309 | 0.014328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN001-74644428 | 24 | 24 | 0.001852 | 0 | 0.0025311 | 0 | 0.0026622 | 0 | 1.9402e-05 | 6.5589e-06 | 0.0024535 | 0.0024729 | 0.0024923 | 0.0025117 | 0.0025311 | 0.0025376 | 0.0025442 | 0.0025507 | 0.0025573 | 0.0025639 | 0.0025704 | 0.002577 | 0.0025835 | 0.0025901 | 0.0025967 | 0.0026032 | 0.0026098 | 0.0026163 | 0.0026229 | 0.0026295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN002-138133472 | 19 | 19 | 0.0026391 | 0 | 0.0034102 | 0 | 0.0035549 | 0 | 2.2032e-05 | 7.2363e-06 | 0.0033221 | 0.0033441 | 0.0033662 | 0.0033882 | 0.0034102 | 0.0034175 | 0.0034247 | 0.0034319 | 0.0034392 | 0.0034464 | 0.0034536 | 0.0034609 | 0.0034681 | 0.0034753 | 0.0034826 | 0.0034898 | 0.0034971 | 0.0035043 | 0.0035115 | 0.0035188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN002-15420512 | 1563 | 1409 | 0.059779 | 0.0065048 | 0.071858 | 0.0084974 | 0.075994 | 0.0092265 | 0.00034511 | 0.00020682 | 0.070477 | 0.070823 | 0.071168 | 0.071513 | 0.071858 | 0.072065 | 0.072272 | 0.072478 | 0.072685 | 0.072892 | 0.073099 | 0.073306 | 0.073512 | 0.073719 | 0.073926 | 0.074133 | 0.07434 | 0.074547 | 0.074753 | 0.07496 | 5.693e-05 | 3.6457e-05 | 0.0082697 | 0.0083266 | 0.0083835 | 0.0084405 | 0.0084974 | 0.0085339 | 0.0085703 | 0.0086068 | 0.0086432 | 0.0086797 | 0.0087161 | 0.0087526 | 0.008789 | 0.0088255 | 0.008862 | 0.0088984 | 0.0089349 | 0.0089713 | 0.0090078 | 0.0090442
| CMN002-15420523 | 1564 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN002-78928402 | 24 | 24 | 0.002774 | 0 | 0.0036111 | 0 | 0.003746 | 0 | 2.3917e-05 | 6.7438e-06 | 0.0035154 | 0.0035394 | 0.0035633 | 0.0035872 | 0.0036111 | 0.0036179 | 0.0036246 | 0.0036313 | 0.0036381 | 0.0036448 | 0.0036516 | 0.0036583 | 0.0036651 | 0.0036718 | 0.0036785 | 0.0036853 | 0.003692 | 0.0036988 | 0.0037055 | 0.0037123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN002-78928472 | 22 | 22 | 0.0083059 | 0 | 0.01043 | 0 | 0.010758 | 0 | 6.0694e-05 | 1.6367e-05 | 0.010187 | 0.010248 | 0.010309 | 0.01037 | 0.01043 | 0.010447 | 0.010463 | 0.010479 | 0.010496 | 0.010512 | 0.010528 | 0.010545 | 0.010561 | 0.010578 | 0.010594 | 0.01061 | 0.010627 | 0.010643 | 0.010659 | 0.010676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN002-87920200 | 26 | 26 | 0.0019716 | 0 | 0.0026226 | 0 | 0.0028691 | 0 | 1.8601e-05 | 1.2324e-05 | 0.0025482 | 0.0025668 | 0.0025854 | 0.002604 | 0.0026226 | 0.0026349 | 0.0026473 | 0.0026596 | 0.0026719 | 0.0026842 | 0.0026966 | 0.0027089 | 0.0027212 | 0.0027335 | 0.0027458 | 0.0027582 | 0.0027705 | 0.0027828 | 0.0027951 | 0.0028075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN003-123737154 | 1243 | 663 | 0.04253 | 0.011012 | 0.05314 | 0.014579 | 0.054414 | 0.015115 | 0.00030314 | 6.3708e-05 | 0.051928 | 0.052231 | 0.052534 | 0.052837 | 0.05314 | 0.053204 | 0.053268 | 0.053331 | 0.053395 | 0.053459 | 0.053522 | 0.053586 | 0.05365 | 0.053714 | 0.053777 | 0.053841 | 0.053905 | 0.053968 | 0.054032 | 0.054096 | 0.00010192 | 2.6756e-05 | 0.014172 | 0.014274 | 0.014376 | 0.014478 | 0.014579 | 0.014606 | 0.014633 | 0.01466 | 0.014687 | 0.014713 | 0.01474 | 0.014767 | 0.014794 | 0.01482 | 0.014847 | 0.014874 | 0.014901 | 0.014927 | 0.014954 | 0.014981
| CMN003-15420636 | 3016 | 7 | 2.01e-06 | 0 | 2.65e-06 | 0 | 2.8e-06 | 0 | 1.8286e-08 | 7.5e-09 | 2.5769e-06 | 2.5951e-06 | 2.6134e-06 | 2.6317e-06 | 2.65e-06 | 2.6575e-06 | 2.665e-06 | 2.6725e-06 | 2.68e-06 | 2.6875e-06 | 2.695e-06 | 2.7025e-06 | 2.71e-06 | 2.7175e-06 | 2.725e-06 | 2.7325e-06 | 2.74e-06 | 2.7475e-06 | 2.755e-06 | 2.7625e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN003-15420649 | 3009 | 1766 | 0.016457 | 0.01646 | 0.020119 | 0.021269 | 0.020682 | 0.022313 | 0.00010461 | 2.8156e-05 | 0.0197 | 0.019805 | 0.019909 | 0.020014 | 0.020119 | 0.020147 | 0.020175 | 0.020203 | 0.020231 | 0.020259 | 0.020287 | 0.020316 | 0.020344 | 0.020372 | 0.0204 | 0.020428 | 0.020456 | 0.020485 | 0.020513 | 0.020541 | 0.00013739 | 5.2204e-05 | 0.020719 | 0.020857 | 0.020994 | 0.021131 | 0.021269 | 0.021321 | 0.021373 | 0.021425 | 0.021478 | 0.02153 | 0.021582 | 0.021634 | 0.021686 | 0.021739 | 0.021791 | 0.021843 | 0.021895 | 0.021947 | 0.022 | 0.022052
| CMN003-164373106 | 371 | 309 | 0.023516 | 0.0034817 | 0.029229 | 0.004572 | 0.029766 | 0.0047366 | 0.00016324 | 2.6835e-05 | 0.028576 | 0.028739 | 0.028903 | 0.029066 | 0.029229 | 0.029256 | 0.029283 | 0.02931 | 0.029337 | 0.029363 | 0.02939 | 0.029417 | 0.029444 | 0.029471 | 0.029498 | 0.029524 | 0.029551 | 0.029578 | 0.029605 | 0.029632 | 3.1152e-05 | 8.2307e-06 | 0.0044474 | 0.0044785 | 0.0045097 | 0.0045408 | 0.004572 | 0.0045802 | 0.0045884 | 0.0045967 | 0.0046049 | 0.0046131 | 0.0046214 | 0.0046296 | 0.0046378 | 0.0046461 | 0.0046543 | 0.0046625 | 0.0046708 | 0.004679 | 0.0046872 | 0.0046954
| CMN003-164373173 | 168 | 168 | 0.0053464 | 0 | 0.006768 | 0 | 0.0073419 | 0 | 4.0616e-05 | 2.8698e-05 | 0.0066055 | 0.0066461 | 0.0066867 | 0.0067274 | 0.006768 | 0.0067967 | 0.0068254 | 0.0068541 | 0.0068828 | 0.0069115 | 0.0069402 | 0.0069689 | 0.0069976 | 0.0070262 | 0.0070549 | 0.0070836 | 0.0071123 | 0.007141 | 0.0071697 | 0.0071984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN003-75645317 | 10 | 10 | 0.001184 | 0 | 0.0014332 | 0 | 0.0015784 | 0 | 7.118e-06 | 7.2626e-06 | 0.0014047 | 0.0014118 | 0.0014189 | 0.0014261 | 0.0014332 | 0.0014404 | 0.0014477 | 0.001455 | 0.0014622 | 0.0014695 | 0.0014768 | 0.001484 | 0.0014913 | 0.0014985 | 0.0015058 | 0.0015131 | 0.0015203 | 0.0015276 | 0.0015349 | 0.0015421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN003-75645537 | 15 | 15 | 0.00095523 | 0 | 0.0012609 | 0 | 0.0013651 | 0 | 8.7348e-06 | 5.2059e-06 | 0.001226 | 0.0012347 | 0.0012435 | 0.0012522 | 0.0012609 | 0.0012662 | 0.0012714 | 0.0012766 | 0.0012818 | 0.001287 | 0.0012922 | 0.0012974 | 0.0013026 | 0.0013078 | 0.001313 | 0.0013182 | 0.0013234 | 0.0013286 | 0.0013338 | 0.001339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN003-76447191 | 15 | 15 | 0.0058938 | 0 | 0.0081974 | 0 | 0.0082822 | 0 | 6.5819e-05 | 4.2397e-06 | 0.0079341 | 0.008 | 0.0080658 | 0.0081316 | 0.0081974 | 0.0082017 | 0.0082059 | 0.0082101 | 0.0082144 | 0.0082186 | 0.0082229 | 0.0082271 | 0.0082313 | 0.0082356 | 0.0082398 | 0.008244 | 0.0082483 | 0.0082525 | 0.0082568 | 0.008261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN003-76447226 | 16 | 16 | 0.0013332 | 0 | 0.0017331 | 0 | 0.0018458 | 0 | 1.1424e-05 | 5.6389e-06 | 0.0016874 | 0.0016988 | 0.0017102 | 0.0017216 | 0.0017331 | 0.0017387 | 0.0017443 | 0.00175 | 0.0017556 | 0.0017613 | 0.0017669 | 0.0017725 | 0.0017782 | 0.0017838 | 0.0017895 | 0.0017951 | 0.0018007 | 0.0018064 | 0.001812 | 0.0018176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN004-15420549 | 1752 | 1329 | 0.028879 | 0.010739 | 0.03803 | 0.01475 | 0.038557 | 0.014995 | 0.00026147 | 2.6339e-05 | 0.036984 | 0.037246 | 0.037507 | 0.037769 | 0.03803 | 0.038056 | 0.038083 | 0.038109 | 0.038135 | 0.038162 | 0.038188 | 0.038214 | 0.038241 | 0.038267 | 0.038293 | 0.03832 | 0.038346 | 0.038372 | 0.038399 | 0.038425 | 0.00011461 | 1.2236e-05 | 0.014292 | 0.014406 | 0.014521 | 0.014635 | 0.01475 | 0.014762 | 0.014775 | 0.014787 | 0.014799 | 0.014811 | 0.014824 | 0.014836 | 0.014848 | 0.01486 | 0.014872 | 0.014885 | 0.014897 | 0.014909 | 0.014921 | 0.014934
| CMN004-24614626 | 384 | 384 | 0.018474 | 0.0042314 | 0.025252 | 0.0058925 | 0.025661 | 0.0059997 | 0.00019364 | 2.0478e-05 | 0.024477 | 0.024671 | 0.024864 | 0.025058 | 0.025252 | 0.025272 | 0.025293 | 0.025313 | 0.025334 | 0.025354 | 0.025375 | 0.025395 | 0.025415 | 0.025436 | 0.025456 | 0.025477 | 0.025497 | 0.025518 | 0.025538 | 0.025559 | 4.746e-05 | 5.3588e-06 | 0.0057027 | 0.0057501 | 0.0057976 | 0.005845 | 0.0058925 | 0.0058979 | 0.0059032 | 0.0059086 | 0.0059139 | 0.0059193 | 0.0059247 | 0.00593 | 0.0059354 | 0.0059407 | 0.0059461 | 0.0059514 | 0.0059568 | 0.0059622 | 0.0059675 | 0.0059729
| CMN004-74052344 | 18 | 18 | 0.0073273 | 0 | 0.0091424 | 0 | 0.0094583 | 0 | 5.186e-05 | 1.5796e-05 | 0.008935 | 0.0089868 | 0.0090387 | 0.0090905 | 0.0091424 | 0.0091582 | 0.009174 | 0.0091898 | 0.0092056 | 0.0092214 | 0.0092372 | 0.009253 | 0.0092688 | 0.0092846 | 0.0093004 | 0.0093162 | 0.0093319 | 0.0093477 | 0.0093635 | 0.0093793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN004-76446391 | 21 | 21 | 0.0029143 | 0 | 0.0041575 | 0 | 0.004238 | 0 | 3.5521e-05 | 4.0263e-06 | 0.0040154 | 0.004051 | 0.0040865 | 0.004122 | 0.0041575 | 0.0041615 | 0.0041656 | 0.0041696 | 0.0041736 | 0.0041777 | 0.0041817 | 0.0041857 | 0.0041897 | 0.0041938 | 0.0041978 | 0.0042018 | 0.0042058 | 0.0042099 | 0.0042139 | 0.0042179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN004-76547682 | 0 | 0 | 0.0094515 | 0 | 0.013701 | 0 | 0.013515 | 0 | 0.00012141 | -9.3048e-06 | 0.013215 | 0.013337 | 0.013458 | 0.01358 | 0.013701 | 0.013692 | 0.013682 | 0.013673 | 0.013664 | 0.013654 | 0.013645 | 0.013636 | 0.013627 | 0.013617 | 0.013608 | 0.013599 | 0.013589 | 0.01358 | 0.013571 | 0.013561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN005-15420597 | 1063 | 1063 | 0.030904 | 0 | 0.039204 | 0 | 0.040879 | 0 | 0.00023713 | 8.3753e-05 | 0.038255 | 0.038492 | 0.03873 | 0.038967 | 0.039204 | 0.039288 | 0.039371 | 0.039455 | 0.039539 | 0.039623 | 0.039706 | 0.03979 | 0.039874 | 0.039958 | 0.040041 | 0.040125 | 0.040209 | 0.040293 | 0.040376 | 0.04046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-15431802 | 830 | 1 | 5.29e-08 | 5.16e-06 | 8.52e-08 | 8.32e-06 | 6.32e-08 | 6.17e-06 | 9.2286e-10 | -1.1e-09 | 8.1509e-08 | 8.2431e-08 | 8.3354e-08 | 8.4277e-08 | 8.52e-08 | 8.41e-08 | 8.3e-08 | 8.19e-08 | 8.08e-08 | 7.97e-08 | 7.86e-08 | 7.75e-08 | 7.64e-08 | 7.53e-08 | 7.42e-08 | 7.31e-08 | 7.2e-08 | 7.09e-08 | 6.98e-08 | 6.87e-08 | 9.0286e-08 | -1.075e-07 | 7.9589e-06 | 8.0491e-06 | 8.1394e-06 | 8.2297e-06 | 8.32e-06 | 8.2125e-06 | 8.105e-06 | 7.9975e-06 | 7.89e-06 | 7.7825e-06 | 7.675e-06 | 7.5675e-06 | 7.46e-06 | 7.3525e-06 | 7.245e-06 | 7.1375e-06 | 7.03e-06 | 6.9225e-06 | 6.815e-06 | 6.7075e-06
| COB011-15431815 | 829 | 435 | 0.0028072 | 0.0009184 | 0.0036174 | 0.0013525 | 0.0030711 | 0.0010526 | 2.315e-05 | -2.7317e-05 | 0.0035248 | 0.003548 | 0.0035711 | 0.0035943 | 0.0036174 | 0.0035901 | 0.0035628 | 0.0035354 | 0.0035081 | 0.0034808 | 0.0034535 | 0.0034262 | 0.0033989 | 0.0033715 | 0.0033442 | 0.0033169 | 0.0032896 | 0.0032623 | 0.003235 | 0.0032076 | 1.2402e-05 | -1.4996e-05 | 0.0013029 | 0.0013153 | 0.0013277 | 0.0013401 | 0.0013525 | 0.0013375 | 0.0013225 | 0.0013075 | 0.0012925 | 0.0012775 | 0.0012625 | 0.0012475 | 0.0012325 | 0.0012175 | 0.0012025 | 0.0011875 | 0.0011725 | 0.0011575 | 0.0011425 | 0.0011275
| COB011-162571445 | 6 | 6 | 3.57e-06 | 0 | 6.66e-06 | 0 | 4.6e-06 | 0 | 8.8286e-08 | -1.03e-07 | 6.3069e-06 | 6.3951e-06 | 6.4834e-06 | 6.5717e-06 | 6.66e-06 | 6.557e-06 | 6.454e-06 | 6.351e-06 | 6.248e-06 | 6.145e-06 | 6.042e-06 | 5.939e-06 | 5.836e-06 | 5.733e-06 | 5.63e-06 | 5.527e-06 | 5.424e-06 | 5.321e-06 | 5.218e-06 | 5.115e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-162571831 | 1 | 1 | 5.39e-07 | 0 | 9.53e-07 | 0 | 6.42e-07 | 0 | 1.1829e-08 | -1.555e-08 | 9.0569e-07 | 9.1751e-07 | 9.2934e-07 | 9.4117e-07 | 9.53e-07 | 9.3745e-07 | 9.219e-07 | 9.0635e-07 | 8.908e-07 | 8.7525e-07 | 8.597e-07 | 8.4415e-07 | 8.286e-07 | 8.1305e-07 | 7.975e-07 | 7.8195e-07 | 7.664e-07 | 7.5085e-07 | 7.353e-07 | 7.1975e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-162572039 | 4 | 4 | 0.00018475 | 0 | 0.00026426 | 0 | 0.00021211 | 0 | 2.2716e-06 | -2.6073e-06 | 0.00025517 | 0.00025744 | 0.00025971 | 0.00026198 | 0.00026426 | 0.00026165 | 0.00025904 | 0.00025643 | 0.00025383 | 0.00025122 | 0.00024861 | 0.000246 | 0.0002434 | 0.00024079 | 0.00023818 | 0.00023558 | 0.00023297 | 0.00023036 | 0.00022775 | 0.00022515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-162572240 | 10 | 10 | 5.59e-05 | 0 | 9.22e-05 | 0 | 6.35e-05 | 0 | 1.0371e-06 | -1.435e-06 | 8.8051e-05 | 8.9089e-05 | 9.0126e-05 | 9.1163e-05 | 9.22e-05 | 9.0765e-05 | 8.933e-05 | 8.7895e-05 | 8.646e-05 | 8.5025e-05 | 8.359e-05 | 8.2155e-05 | 8.072e-05 | 7.9285e-05 | 7.785e-05 | 7.6415e-05 | 7.498e-05 | 7.3545e-05 | 7.211e-05 | 7.0675e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-162572975 | 9 | 9 | 6.65e-07 | 0 | 1.62e-06 | 0 | 9.56e-07 | 0 | 2.7286e-08 | -3.32e-08 | 1.5109e-06 | 1.5381e-06 | 1.5654e-06 | 1.5927e-06 | 1.62e-06 | 1.5868e-06 | 1.5536e-06 | 1.5204e-06 | 1.4872e-06 | 1.454e-06 | 1.4208e-06 | 1.3876e-06 | 1.3544e-06 | 1.3212e-06 | 1.288e-06 | 1.2548e-06 | 1.2216e-06 | 1.1884e-06 | 1.1552e-06 | 1.122e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-162661437 | 10 | 10 | 4.21e-05 | 0 | 6.93e-05 | 0 | 4.84e-05 | 0 | 7.7714e-07 | -1.045e-06 | 6.6191e-05 | 6.6969e-05 | 6.7746e-05 | 6.8523e-05 | 6.93e-05 | 6.8255e-05 | 6.721e-05 | 6.6165e-05 | 6.512e-05 | 6.4075e-05 | 6.303e-05 | 6.1985e-05 | 6.094e-05 | 5.9895e-05 | 5.885e-05 | 5.7805e-05 | 5.676e-05 | 5.5715e-05 | 5.467e-05 | 5.3625e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-162661589 | 23 | 23 | 0.00064322 | 0 | 0.00098424 | 0 | 0.00069035 | 0 | 9.7435e-06 | -1.4695e-05 | 0.00094527 | 0.00095501 | 0.00096476 | 0.0009745 | 0.00098424 | 0.00096955 | 0.00095486 | 0.00094016 | 0.00092547 | 0.00091077 | 0.00089608 | 0.00088138 | 0.00086669 | 0.00085199 | 0.0008373 | 0.0008226 | 0.00080791 | 0.00079321 | 0.00077852 | 0.00076382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-162661811 | 21 | 21 | 1.62e-06 | 0 | 4.5e-06 | 0 | 2.7e-06 | 0 | 8.2286e-08 | -9e-08 | 4.1709e-06 | 4.2531e-06 | 4.3354e-06 | 4.4177e-06 | 4.5e-06 | 4.41e-06 | 4.32e-06 | 4.23e-06 | 4.14e-06 | 4.05e-06 | 3.96e-06 | 3.87e-06 | 3.78e-06 | 3.69e-06 | 3.6e-06 | 3.51e-06 | 3.42e-06 | 3.33e-06 | 3.24e-06 | 3.15e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-162798633 | 5 | 5 | 0.00051071 | 0 | 0.00068695 | 0 | 0.00052955 | 0 | 5.0355e-06 | -7.87e-06 | 0.00066681 | 0.00067184 | 0.00067688 | 0.00068192 | 0.00068695 | 0.00067908 | 0.00067121 | 0.00066334 | 0.00065547 | 0.0006476 | 0.00063973 | 0.00063186 | 0.00062399 | 0.00061612 | 0.00060825 | 0.00060038 | 0.00059251 | 0.00058464 | 0.00057677 | 0.0005689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-163103340 | 15 | 15 | 0.00024368 | 0 | 0.00042264 | 0 | 0.00030012 | 0 | 5.1131e-06 | -6.1258e-06 | 0.00040219 | 0.0004073 | 0.00041241 | 0.00041752 | 0.00042264 | 0.00041651 | 0.00041039 | 0.00040426 | 0.00039813 | 0.00039201 | 0.00038588 | 0.00037976 | 0.00037363 | 0.00036751 | 0.00036138 | 0.00035525 | 0.00034913 | 0.000343 | 0.00033688 | 0.00033075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-164044294 | 0 | 0 | 1.01e-06 | 0 | 1.01e-06 | 0 | 1.01e-06 | 0 | 0 | 0 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 1.01e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-201141604 | 374 | 55 | 0.00050167 | 0.00020718 | 0.00064942 | 0.00032683 | 0.00052266 | 0.00022414 | 4.2215e-06 | -6.3382e-06 | 0.00063254 | 0.00063676 | 0.00064098 | 0.0006452 | 0.00064942 | 0.00064308 | 0.00063675 | 0.00063041 | 0.00062407 | 0.00061773 | 0.00061139 | 0.00060505 | 0.00059872 | 0.00059238 | 0.00058604 | 0.0005797 | 0.00057336 | 0.00056702 | 0.00056069 | 0.00055435 | 3.4187e-06 | -5.1346e-06 | 0.00031315 | 0.00031657 | 0.00031999 | 0.00032341 | 0.00032683 | 0.00032169 | 0.00031656 | 0.00031143 | 0.00030629 | 0.00030116 | 0.00029602 | 0.00029089 | 0.00028575 | 0.00028062 | 0.00027548 | 0.00027035 | 0.00026521 | 0.00026008 | 0.00025494 | 0.00024981
| COB011-202349052 | 319 | 235 | 0.0016116 | 0.00068997 | 0.0020031 | 0.0010176 | 0.0016501 | 0.00073587 | 1.1188e-05 | -1.7653e-05 | 0.0019584 | 0.0019696 | 0.0019808 | 0.001992 | 0.0020031 | 0.0019855 | 0.0019678 | 0.0019502 | 0.0019325 | 0.0019149 | 0.0018972 | 0.0018796 | 0.0018619 | 0.0018443 | 0.0018266 | 0.001809 | 0.0017913 | 0.0017737 | 0.001756 | 0.0017383 | 9.36e-06 | -1.4085e-05 | 0.00098013 | 0.00098949 | 0.00099885 | 0.0010082 | 0.0010176 | 0.0010035 | 0.0009894 | 0.00097531 | 0.00096123 | 0.00094714 | 0.00093306 | 0.00091897 | 0.00090489 | 0.0008908 | 0.00087672 | 0.00086263 | 0.00084855 | 0.00083446 | 0.00082038 | 0.00080629
| COB012-15431852 | 33 | 33 | 0.00052105 | 0 | 0.00073463 | 0 | 0.00059253 | 0 | 6.1023e-06 | -7.1052e-06 | 0.00071022 | 0.00071633 | 0.00072243 | 0.00072853 | 0.00073463 | 0.00072753 | 0.00072042 | 0.00071332 | 0.00070621 | 0.00069911 | 0.000692 | 0.0006849 | 0.00067779 | 0.00067069 | 0.00066358 | 0.00065648 | 0.00064937 | 0.00064227 | 0.00063516 | 0.00062806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB021-15436290 | 14 | 14 | 0.0015192 | 8.21e-07 | 0.0021211 | 1.48e-06 | 0.0017121 | 1.01e-06 | 1.7196e-05 | -2.0447e-05 | 0.0020523 | 0.0020695 | 0.0020867 | 0.0021039 | 0.0021211 | 0.0021006 | 0.0020802 | 0.0020597 | 0.0020393 | 0.0020188 | 0.0019984 | 0.001978 | 0.0019575 | 0.0019371 | 0.0019166 | 0.0018962 | 0.0018757 | 0.0018553 | 0.0018348 | 0.0018144 | 1.8829e-08 | -2.35e-08 | 1.4047e-06 | 1.4235e-06 | 1.4423e-06 | 1.4612e-06 | 1.48e-06 | 1.4565e-06 | 1.433e-06 | 1.4095e-06 | 1.386e-06 | 1.3625e-06 | 1.339e-06 | 1.3155e-06 | 1.292e-06 | 1.2685e-06 | 1.245e-06 | 1.2215e-06 | 1.198e-06 | 1.1745e-06 | 1.151e-06 | 1.1275e-06
| COB021-24613718 | 0 | 0 | 2.07e-07 | 0 | 5.18e-07 | 0 | 3.11e-07 | 0 | 8.8857e-09 | -1.035e-08 | 4.8246e-07 | 4.9134e-07 | 5.0023e-07 | 5.0911e-07 | 5.18e-07 | 5.0765e-07 | 4.973e-07 | 4.8695e-07 | 4.766e-07 | 4.6625e-07 | 4.559e-07 | 4.4555e-07 | 4.352e-07 | 4.2485e-07 | 4.145e-07 | 4.0415e-07 | 3.938e-07 | 3.8345e-07 | 3.731e-07 | 3.6275e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB022-160576265 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO013-15404871 | 3531 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO013-15404884 | 3516 | 3516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO014-15404821 | 37 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO021-153844129 | 252 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO021-15404447 | 865 | 613 | 0.00043714 | 0 | 0.00051962 | 0 | 0.00051441 | 0 | 2.3566e-06 | -2.604e-07 | 0.0005102 | 0.00051255 | 0.00051491 | 0.00051727 | 0.00051962 | 0.00051936 | 0.0005191 | 0.00051884 | 0.00051858 | 0.00051832 | 0.00051806 | 0.0005178 | 0.00051754 | 0.00051728 | 0.00051702 | 0.00051676 | 0.0005165 | 0.00051624 | 0.00051598 | 0.00051572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO022-15404471 | 3058 | 2663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO022-24612421 | 395 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO023-15404521 | 299 | 299 | 1.14e-05 | 0 | 1.62e-05 | 0 | 1.75e-05 | 0 | 1.3714e-07 | 6.5e-08 | 1.5651e-05 | 1.5789e-05 | 1.5926e-05 | 1.6063e-05 | 1.62e-05 | 1.6265e-05 | 1.633e-05 | 1.6395e-05 | 1.646e-05 | 1.6525e-05 | 1.659e-05 | 1.6655e-05 | 1.672e-05 | 1.6785e-05 | 1.685e-05 | 1.6915e-05 | 1.698e-05 | 1.7045e-05 | 1.711e-05 | 1.7175e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO031-15404634 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO031-15404660 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO032-15404697 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO033-15404721 | 16 | 16 | 0.0015858 | 0 | 0.0022147 | 0 | 0.0023718 | 0 | 1.797e-05 | 7.8526e-06 | 0.0021428 | 0.0021608 | 0.0021788 | 0.0021967 | 0.0022147 | 0.0022226 | 0.0022304 | 0.0022383 | 0.0022461 | 0.002254 | 0.0022618 | 0.0022697 | 0.0022775 | 0.0022854 | 0.0022932 | 0.0023011 | 0.002309 | 0.0023168 | 0.0023247 | 0.0023325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO034-15404810 | 1360 | 1360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-129145544 | 530 | 521 | 0.0072357 | 7.55e-06 | 0.0087941 | 1.02e-05 | 0.0089488 | 1.08e-05 | 4.4526e-05 | 7.7344e-06 | 0.008616 | 0.0086605 | 0.0087051 | 0.0087496 | 0.0087941 | 0.0088019 | 0.0088096 | 0.0088173 | 0.0088251 | 0.0088328 | 0.0088405 | 0.0088483 | 0.008856 | 0.0088637 | 0.0088715 | 0.0088792 | 0.0088869 | 0.0088947 | 0.0089024 | 0.0089101 | 7.5714e-08 | 3e-08 | 9.8971e-06 | 9.9729e-06 | 1.0049e-05 | 1.0124e-05 | 1.02e-05 | 1.023e-05 | 1.026e-05 | 1.029e-05 | 1.032e-05 | 1.035e-05 | 1.038e-05 | 1.041e-05 | 1.044e-05 | 1.047e-05 | 1.05e-05 | 1.053e-05 | 1.056e-05 | 1.059e-05 | 1.062e-05 | 1.065e-05
| CTN001-15418475 | 1633 | 0 | 0.0020177 | 0.0012249 | 0.002301 | 0.0016317 | 0.0022821 | 0.0016724 | 8.094e-06 | -9.452e-07 | 0.0022686 | 0.0022767 | 0.0022848 | 0.0022929 | 0.002301 | 0.0023 | 0.0022991 | 0.0022981 | 0.0022972 | 0.0022962 | 0.0022953 | 0.0022944 | 0.0022934 | 0.0022925 | 0.0022915 | 0.0022906 | 0.0022896 | 0.0022887 | 0.0022877 | 0.0022868 | 1.1623e-05 | 2.0371e-06 | 0.0015852 | 0.0015968 | 0.0016084 | 0.0016201 | 0.0016317 | 0.0016337 | 0.0016358 | 0.0016378 | 0.0016398 | 0.0016419 | 0.0016439 | 0.0016459 | 0.001648 | 0.00165 | 0.001652 | 0.0016541 | 0.0016561 | 0.0016582 | 0.0016602 | 0.0016622
| CTN001-155143379 | 21 | 21 | 0.0027727 | 0 | 0.0040869 | 0 | 0.0040108 | 0 | 3.7547e-05 | -3.8029e-06 | 0.0039367 | 0.0039742 | 0.0040118 | 0.0040493 | 0.0040869 | 0.0040831 | 0.0040793 | 0.0040755 | 0.0040717 | 0.0040679 | 0.0040641 | 0.0040603 | 0.0040564 | 0.0040526 | 0.0040488 | 0.004045 | 0.0040412 | 0.0040374 | 0.0040336 | 0.0040298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155143591 | 27 | 27 | 0.0039636 | 0 | 0.0061293 | 0 | 0.0057841 | 0 | 6.1875e-05 | -1.7259e-05 | 0.0058818 | 0.0059436 | 0.0060055 | 0.0060674 | 0.0061293 | 0.006112 | 0.0060947 | 0.0060775 | 0.0060602 | 0.006043 | 0.0060257 | 0.0060084 | 0.0059912 | 0.0059739 | 0.0059567 | 0.0059394 | 0.0059222 | 0.0059049 | 0.0058876 | 0.0058704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155143776 | 32 | 32 | 0.0034451 | 0 | 0.0046383 | 0 | 0.004832 | 0 | 3.4091e-05 | 9.6839e-06 | 0.0045019 | 0.004536 | 0.0045701 | 0.0046042 | 0.0046383 | 0.004648 | 0.0046577 | 0.0046673 | 0.004677 | 0.0046867 | 0.0046964 | 0.0047061 | 0.0047158 | 0.0047254 | 0.0047351 | 0.0047448 | 0.0047545 | 0.0047642 | 0.0047739 | 0.0047836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155143905 | 37 | 37 | 1.02e-05 | 0 | 1.58e-05 | 0 | 1.65e-05 | 0 | 1.6e-07 | 3.5e-08 | 1.516e-05 | 1.532e-05 | 1.548e-05 | 1.564e-05 | 1.58e-05 | 1.5835e-05 | 1.587e-05 | 1.5905e-05 | 1.594e-05 | 1.5975e-05 | 1.601e-05 | 1.6045e-05 | 1.608e-05 | 1.6115e-05 | 1.615e-05 | 1.6185e-05 | 1.622e-05 | 1.6255e-05 | 1.629e-05 | 1.6325e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155145203 | 4 | 4 | 0.0011545 | 0 | 0.0018214 | 0 | 0.0017701 | 0 | 1.9054e-05 | -2.5638e-06 | 0.0017452 | 0.0017642 | 0.0017833 | 0.0018024 | 0.0018214 | 0.0018188 | 0.0018163 | 0.0018137 | 0.0018112 | 0.0018086 | 0.001806 | 0.0018035 | 0.0018009 | 0.0017983 | 0.0017958 | 0.0017932 | 0.0017906 | 0.0017881 | 0.0017855 | 0.001783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155179699 | 7 | 7 | 0.00061299 | 0 | 0.0010367 | 0 | 0.0010031 | 0 | 1.2105e-05 | -1.679e-06 | 0.00098825 | 0.0010004 | 0.0010125 | 0.0010246 | 0.0010367 | 0.001035 | 0.0010333 | 0.0010316 | 0.00103 | 0.0010283 | 0.0010266 | 0.0010249 | 0.0010232 | 0.0010216 | 0.0010199 | 0.0010182 | 0.0010165 | 0.0010148 | 0.0010132 | 0.0010115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155179789 | 11 | 11 | 0.00079831 | 0 | 0.0013629 | 0 | 0.0013098 | 0 | 1.6132e-05 | -2.6573e-06 | 0.0012984 | 0.0013145 | 0.0013307 | 0.0013468 | 0.0013629 | 0.0013603 | 0.0013576 | 0.001355 | 0.0013523 | 0.0013496 | 0.001347 | 0.0013443 | 0.0013417 | 0.001339 | 0.0013364 | 0.0013337 | 0.001331 | 0.0013284 | 0.0013257 | 0.0013231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155190934 | 3 | 3 | 0.00030189 | 0 | 0.00046653 | 0 | 0.00044847 | 0 | 4.7037e-06 | -9.0275e-07 | 0.00044771 | 0.00045241 | 0.00045712 | 0.00046182 | 0.00046653 | 0.00046562 | 0.00046472 | 0.00046382 | 0.00046291 | 0.00046201 | 0.00046111 | 0.00046021 | 0.0004593 | 0.0004584 | 0.0004575 | 0.00045659 | 0.00045569 | 0.00045479 | 0.00045389 | 0.00045298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155191080 | 2 | 2 | 2.55e-06 | 0 | 4.12e-06 | 0 | 4.29e-06 | 0 | 4.4857e-08 | 8.5e-09 | 3.9406e-06 | 3.9854e-06 | 4.0303e-06 | 4.0751e-06 | 4.12e-06 | 4.1285e-06 | 4.137e-06 | 4.1455e-06 | 4.154e-06 | 4.1625e-06 | 4.171e-06 | 4.1795e-06 | 4.188e-06 | 4.1965e-06 | 4.205e-06 | 4.2135e-06 | 4.222e-06 | 4.2305e-06 | 4.239e-06 | 4.2475e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155191213 | 5 | 5 | 0.0011849 | 0 | 0.0019666 | 0 | 0.0018624 | 0 | 2.2335e-05 | -5.2103e-06 | 0.0018773 | 0.0018996 | 0.0019219 | 0.0019443 | 0.0019666 | 0.0019614 | 0.0019562 | 0.001951 | 0.0019458 | 0.0019405 | 0.0019353 | 0.0019301 | 0.0019249 | 0.0019197 | 0.0019145 | 0.0019093 | 0.0019041 | 0.0018989 | 0.0018937 | 0.0018884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155191322 | 29 | 29 | 0.0054606 | 0 | 0.0086183 | 0 | 0.0084242 | 0 | 9.0218e-05 | -9.7026e-06 | 0.0082574 | 0.0083476 | 0.0084378 | 0.008528 | 0.0086183 | 0.0086085 | 0.0085988 | 0.0085891 | 0.0085794 | 0.0085697 | 0.00856 | 0.0085503 | 0.0085406 | 0.0085309 | 0.0085212 | 0.0085115 | 0.0085018 | 0.0084921 | 0.0084824 | 0.0084727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155250725 | 9 | 9 | 3.3e-06 | 0 | 3.3e-06 | 0 | 3.3e-06 | 0 | 0 | 0 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 3.3e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155250997 | 26 | 26 | 0.010115 | 0 | 0.013634 | 0 | 0.014014 | 0 | 0.00010054 | 1.8985e-05 | 0.013232 | 0.013333 | 0.013433 | 0.013534 | 0.013634 | 0.013653 | 0.013672 | 0.013691 | 0.01371 | 0.013729 | 0.013748 | 0.013767 | 0.013786 | 0.013805 | 0.013824 | 0.013843 | 0.013862 | 0.013881 | 0.0139 | 0.013919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155668176 | 15 | 15 | 0.0024839 | 0 | 0.0040135 | 0 | 0.0039178 | 0 | 4.3701e-05 | -4.7849e-06 | 0.0038387 | 0.0038824 | 0.0039261 | 0.0039698 | 0.0040135 | 0.0040087 | 0.0040039 | 0.0039991 | 0.0039943 | 0.0039896 | 0.0039848 | 0.00398 | 0.0039752 | 0.0039704 | 0.0039656 | 0.0039609 | 0.0039561 | 0.0039513 | 0.0039465 | 0.0039417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155668272 | 7 | 7 | 0.0013534 | 0 | 0.0022175 | 0 | 0.0021933 | 0 | 2.4687e-05 | -1.2096e-06 | 0.0021187 | 0.0021434 | 0.0021681 | 0.0021928 | 0.0022175 | 0.0022162 | 0.002215 | 0.0022138 | 0.0022126 | 0.0022114 | 0.0022102 | 0.002209 | 0.0022078 | 0.0022066 | 0.0022054 | 0.0022041 | 0.0022029 | 0.0022017 | 0.0022005 | 0.0021993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155821745 | 18 | 18 | 0.0030578 | 0 | 0.0049108 | 0 | 0.0047407 | 0 | 5.2943e-05 | -8.505e-06 | 0.0046991 | 0.004752 | 0.004805 | 0.0048579 | 0.0049108 | 0.0049023 | 0.0048938 | 0.0048853 | 0.0048768 | 0.0048683 | 0.0048598 | 0.0048513 | 0.0048428 | 0.0048343 | 0.0048258 | 0.0048173 | 0.0048088 | 0.0048003 | 0.0047918 | 0.0047833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155821947 | 29 | 11 | 0.00052283 | 0.00041175 | 0.00052903 | 0.00041635 | 0.00052568 | 0.00041388 | 1.772e-07 | -1.679e-07 | 0.00052833 | 0.0005285 | 0.00052868 | 0.00052886 | 0.00052903 | 0.00052887 | 0.0005287 | 0.00052853 | 0.00052836 | 0.00052819 | 0.00052803 | 0.00052786 | 0.00052769 | 0.00052752 | 0.00052735 | 0.00052719 | 0.00052702 | 0.00052685 | 0.00052668 | 0.00052652 | 1.3143e-07 | -1.236e-07 | 0.00041582 | 0.00041596 | 0.00041609 | 0.00041622 | 0.00041635 | 0.00041623 | 0.0004161 | 0.00041598 | 0.00041586 | 0.00041573 | 0.00041561 | 0.00041548 | 0.00041536 | 0.00041524 | 0.00041511 | 0.00041499 | 0.00041487 | 0.00041474 | 0.00041462 | 0.0004145
| CTN001-155822474 | 7 | 7 | 0.001851 | 0 | 0.0029391 | 0 | 0.0029117 | 0 | 3.1089e-05 | -1.3725e-06 | 0.0028148 | 0.0028459 | 0.002877 | 0.002908 | 0.0029391 | 0.0029378 | 0.0029364 | 0.002935 | 0.0029336 | 0.0029323 | 0.0029309 | 0.0029295 | 0.0029281 | 0.0029268 | 0.0029254 | 0.002924 | 0.0029227 | 0.0029213 | 0.0029199 | 0.0029185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-155822565 | 16 | 16 | 0.0032756 | 0 | 0.0051239 | 0 | 0.0051235 | 0 | 5.2808e-05 | -2.195e-08 | 0.0049127 | 0.0049655 | 0.0050183 | 0.0050711 | 0.0051239 | 0.0051239 | 0.0051239 | 0.0051239 | 0.0051238 | 0.0051238 | 0.0051238 | 0.0051238 | 0.0051238 | 0.0051237 | 0.0051237 | 0.0051237 | 0.0051237 | 0.0051236 | 0.0051236 | 0.0051236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-156780450 | 28 | 28 | 0.00215 | 0 | 0.002817 | 0 | 0.00295 | 0 | 1.9058e-05 | 6.6465e-06 | 0.0027408 | 0.0027599 | 0.0027789 | 0.002798 | 0.002817 | 0.0028237 | 0.0028303 | 0.002837 | 0.0028436 | 0.0028503 | 0.0028569 | 0.0028636 | 0.0028702 | 0.0028768 | 0.0028835 | 0.0028901 | 0.0028968 | 0.0029034 | 0.0029101 | 0.0029167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-158006395 | 671 | 32 | 0 | 2.07e-08 | 0 | 2.07e-08 | 0 | 2.07e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08 | 2.07e-08
| CTN001-161785823 | 21 | 21 | 0.0046173 | 0 | 0.0061991 | 0 | 0.0063619 | 0 | 4.5194e-05 | 8.1396e-06 | 0.0060184 | 0.0060635 | 0.0061087 | 0.0061539 | 0.0061991 | 0.0062073 | 0.0062154 | 0.0062235 | 0.0062317 | 0.0062398 | 0.006248 | 0.0062561 | 0.0062642 | 0.0062724 | 0.0062805 | 0.0062887 | 0.0062968 | 0.0063049 | 0.0063131 | 0.0063212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-163126863 | 28 | 28 | 0.00023966 | 0 | 0.00030774 | 0 | 0.00031329 | 0 | 1.9453e-06 | 2.774e-07 | 0.00029996 | 0.00030191 | 0.00030385 | 0.0003058 | 0.00030774 | 0.00030802 | 0.0003083 | 0.00030857 | 0.00030885 | 0.00030913 | 0.00030941 | 0.00030968 | 0.00030996 | 0.00031024 | 0.00031052 | 0.00031079 | 0.00031107 | 0.00031135 | 0.00031163 | 0.0003119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-163266702 | 3 | 3 | 0.0016669 | 0 | 0.002683 | 0 | 0.0027093 | 0 | 2.9031e-05 | 1.3142e-06 | 0.0025668 | 0.0025959 | 0.0026249 | 0.0026539 | 0.002683 | 0.0026843 | 0.0026856 | 0.0026869 | 0.0026882 | 0.0026895 | 0.0026909 | 0.0026922 | 0.0026935 | 0.0026948 | 0.0026961 | 0.0026974 | 0.0026987 | 0.0027001 | 0.0027014 | 0.0027027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-24604306 | 798 | 497 | 0.010018 | 0.002743 | 0.014401 | 0.0043343 | 0.013963 | 0.004188 | 0.00012523 | -2.1891e-05 | 0.0139 | 0.014025 | 0.01415 | 0.014276 | 0.014401 | 0.014379 | 0.014357 | 0.014335 | 0.014313 | 0.014291 | 0.014269 | 0.014248 | 0.014226 | 0.014204 | 0.014182 | 0.01416 | 0.014138 | 0.014116 | 0.014094 | 0.014072 | 4.5466e-05 | -7.316e-06 | 0.0041525 | 0.0041979 | 0.0042434 | 0.0042889 | 0.0043343 | 0.004327 | 0.0043197 | 0.0043124 | 0.0043051 | 0.0042977 | 0.0042904 | 0.0042831 | 0.0042758 | 0.0042685 | 0.0042612 | 0.0042538 | 0.0042465 | 0.0042392 | 0.0042319 | 0.0042246
| CTN001-24604862 | 89 | 14 | 0.0042722 | 0.003955 | 0.0044044 | 0.0040088 | 0.0043129 | 0.0039719 | 3.7781e-06 | -4.5755e-06 | 0.0043893 | 0.0043931 | 0.0043969 | 0.0044007 | 0.0044044 | 0.0043999 | 0.0043953 | 0.0043907 | 0.0043861 | 0.0043816 | 0.004377 | 0.0043724 | 0.0043678 | 0.0043633 | 0.0043587 | 0.0043541 | 0.0043495 | 0.004345 | 0.0043404 | 0.0043358 | 1.5377e-06 | -1.8453e-06 | 0.0040027 | 0.0040042 | 0.0040058 | 0.0040073 | 0.0040088 | 0.004007 | 0.0040052 | 0.0040033 | 0.0040015 | 0.0039996 | 0.0039978 | 0.0039959 | 0.0039941 | 0.0039922 | 0.0039904 | 0.0039886 | 0.0039867 | 0.0039849 | 0.003983 | 0.0039812
| CTN001-24611782 | 962 | 99 | 0.00083548 | 0.0013378 | 0.0011156 | 0.0019698 | 0.0011244 | 0.0020124 | 8.0045e-06 | 4.373e-07 | 0.0010836 | 0.0010916 | 0.0010996 | 0.0011076 | 0.0011156 | 0.0011161 | 0.0011165 | 0.0011169 | 0.0011174 | 0.0011178 | 0.0011183 | 0.0011187 | 0.0011191 | 0.0011196 | 0.00112 | 0.0011204 | 0.0011209 | 0.0011213 | 0.0011218 | 0.0011222 | 1.8057e-05 | 2.1305e-06 | 0.0018976 | 0.0019156 | 0.0019337 | 0.0019517 | 0.0019698 | 0.0019719 | 0.001974 | 0.0019762 | 0.0019783 | 0.0019804 | 0.0019826 | 0.0019847 | 0.0019868 | 0.001989 | 0.0019911 | 0.0019932 | 0.0019953 | 0.0019975 | 0.0019996 | 0.0020017
| CTN001-24611950 | 159 | 93 | 0.0022782 | 0.00071097 | 0.0031709 | 0.0010739 | 0.0030652 | 0.0010334 | 2.5506e-05 | -5.2872e-06 | 0.0030689 | 0.0030944 | 0.0031199 | 0.0031454 | 0.0031709 | 0.0031656 | 0.0031603 | 0.003155 | 0.0031498 | 0.0031445 | 0.0031392 | 0.0031339 | 0.0031286 | 0.0031233 | 0.003118 | 0.0031127 | 0.0031075 | 0.0031022 | 0.0030969 | 0.0030916 | 1.0369e-05 | -2.023e-06 | 0.0010324 | 0.0010428 | 0.0010531 | 0.0010635 | 0.0010739 | 0.0010719 | 0.0010698 | 0.0010678 | 0.0010658 | 0.0010638 | 0.0010617 | 0.0010597 | 0.0010577 | 0.0010557 | 0.0010537 | 0.0010516 | 0.0010496 | 0.0010476 | 0.0010456 | 0.0010435
| CTN002-15418512 | 1154 | 631 | 0.044811 | 0.0044612 | 0.05429 | 0.0056718 | 0.055035 | 0.0058117 | 0.00027083 | 3.7254e-05 | 0.053207 | 0.053477 | 0.053748 | 0.054019 | 0.05429 | 0.054327 | 0.054364 | 0.054402 | 0.054439 | 0.054476 | 0.054513 | 0.054551 | 0.054588 | 0.054625 | 0.054662 | 0.0547 | 0.054737 | 0.054774 | 0.054811 | 0.054849 | 3.459e-05 | 6.9973e-06 | 0.0055334 | 0.005568 | 0.0056026 | 0.0056372 | 0.0056718 | 0.0056788 | 0.0056858 | 0.0056928 | 0.0056998 | 0.0057068 | 0.0057138 | 0.0057208 | 0.0057278 | 0.0057348 | 0.0057418 | 0.0057488 | 0.0057558 | 0.0057628 | 0.0057698 | 0.0057768
| CTN002-154876793 | 29 | 29 | 0.0051182 | 0 | 0.0065773 | 0 | 0.0067613 | 0 | 4.169e-05 | 9.1995e-06 | 0.0064106 | 0.0064523 | 0.006494 | 0.0065356 | 0.0065773 | 0.0065865 | 0.0065957 | 0.0066049 | 0.0066141 | 0.0066233 | 0.0066325 | 0.0066417 | 0.0066509 | 0.0066601 | 0.0066693 | 0.0066785 | 0.0066877 | 0.0066969 | 0.0067061 | 0.0067153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN002-154876923 | 40 | 40 | 0.0055323 | 0 | 0.0072117 | 0 | 0.0081871 | 0 | 4.7984e-05 | 4.8767e-05 | 0.0070198 | 0.0070678 | 0.0071157 | 0.0071637 | 0.0072117 | 0.0072605 | 0.0073092 | 0.007358 | 0.0074068 | 0.0074555 | 0.0075043 | 0.0075531 | 0.0076019 | 0.0076506 | 0.0076994 | 0.0077482 | 0.0077969 | 0.0078457 | 0.0078945 | 0.0079432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN002-154877191 | 41 | 41 | 0.0029766 | 0 | 0.0037457 | 0 | 0.0038593 | 0 | 2.1975e-05 | 5.6821e-06 | 0.0036578 | 0.0036798 | 0.0037018 | 0.0037237 | 0.0037457 | 0.0037514 | 0.0037571 | 0.0037627 | 0.0037684 | 0.0037741 | 0.0037798 | 0.0037855 | 0.0037912 | 0.0037968 | 0.0038025 | 0.0038082 | 0.0038139 | 0.0038196 | 0.0038252 | 0.0038309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN002-154877287 | 22 | 22 | 0.00048546 | 0 | 0.00051452 | 0 | 0.00050907 | 0 | 8.302e-07 | -2.721e-07 | 0.00051119 | 0.00051202 | 0.00051285 | 0.00051368 | 0.00051452 | 0.00051424 | 0.00051397 | 0.0005137 | 0.00051343 | 0.00051315 | 0.00051288 | 0.00051261 | 0.00051234 | 0.00051207 | 0.00051179 | 0.00051152 | 0.00051125 | 0.00051098 | 0.00051071 | 0.00051043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN002-154877444 | 20 | 20 | 2.41e-05 | 0 | 3.77e-05 | 0 | 4.09e-05 | 0 | 3.8857e-07 | 1.6e-07 | 3.6146e-05 | 3.6534e-05 | 3.6923e-05 | 3.7311e-05 | 3.77e-05 | 3.786e-05 | 3.802e-05 | 3.818e-05 | 3.834e-05 | 3.85e-05 | 3.866e-05 | 3.882e-05 | 3.898e-05 | 3.914e-05 | 3.93e-05 | 3.946e-05 | 3.962e-05 | 3.978e-05 | 3.994e-05 | 4.01e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN002-155259126 | 19 | 19 | 0.0025223 | 0 | 0.0031993 | 0 | 0.0033424 | 0 | 1.9343e-05 | 7.153e-06 | 0.003122 | 0.0031413 | 0.0031607 | 0.00318 | 0.0031993 | 0.0032065 | 0.0032136 | 0.0032208 | 0.0032279 | 0.0032351 | 0.0032423 | 0.0032494 | 0.0032566 | 0.0032637 | 0.0032709 | 0.003278 | 0.0032852 | 0.0032923 | 0.0032995 | 0.0033066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN002-155504946 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN002-155616870 | 6 | 6 | 0.001503 | 0 | 0.0020214 | 0 | 0.0021177 | 0 | 1.4812e-05 | 4.8127e-06 | 0.0019622 | 0.001977 | 0.0019918 | 0.0020066 | 0.0020214 | 0.0020262 | 0.0020311 | 0.0020359 | 0.0020407 | 0.0020455 | 0.0020503 | 0.0020551 | 0.0020599 | 0.0020648 | 0.0020696 | 0.0020744 | 0.0020792 | 0.002084 | 0.0020888 | 0.0020936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN002-155622465 | 15 | 15 | 0.00033479 | 0 | 0.00045907 | 0 | 0.00048041 | 0 | 3.5508e-06 | 1.0673e-06 | 0.00044486 | 0.00044841 | 0.00045197 | 0.00045552 | 0.00045907 | 0.00046013 | 0.0004612 | 0.00046227 | 0.00046334 | 0.0004644 | 0.00046547 | 0.00046654 | 0.00046761 | 0.00046867 | 0.00046974 | 0.00047081 | 0.00047187 | 0.00047294 | 0.00047401 | 0.00047508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN002-155683683 | 38 | 21 | 0.0019437 | 0.00037901 | 0.0024978 | 0.00052478 | 0.0027092 | 0.00059681 | 1.583e-05 | 1.0573e-05 | 0.0024345 | 0.0024503 | 0.0024661 | 0.0024819 | 0.0024978 | 0.0025083 | 0.0025189 | 0.0025295 | 0.0025401 | 0.0025506 | 0.0025612 | 0.0025718 | 0.0025824 | 0.0025929 | 0.0026035 | 0.0026141 | 0.0026246 | 0.0026352 | 0.0026458 | 0.0026564 | 4.1647e-06 | 3.6019e-06 | 0.00050812 | 0.00051228 | 0.00051645 | 0.00052061 | 0.00052478 | 0.00052838 | 0.00053198 | 0.00053558 | 0.00053918 | 0.00054278 | 0.00054639 | 0.00054999 | 0.00055359 | 0.00055719 | 0.00056079 | 0.0005644 | 0.000568 | 0.0005716 | 0.0005752 | 0.0005788
| CTN002-155683893 | 17 | 17 | 0.0022665 | 0 | 0.0031479 | 0 | 0.0033723 | 0 | 2.5181e-05 | 1.1224e-05 | 0.0030471 | 0.0030723 | 0.0030975 | 0.0031227 | 0.0031479 | 0.0031591 | 0.0031703 | 0.0031815 | 0.0031928 | 0.003204 | 0.0032152 | 0.0032264 | 0.0032376 | 0.0032489 | 0.0032601 | 0.0032713 | 0.0032825 | 0.0032938 | 0.003305 | 0.0033162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN002-158379241 | 131 | 34 | 0.0019752 | 0.00099561 | 0.0023784 | 0.0012994 | 0.0024134 | 0.0013449 | 1.152e-05 | 1.7531e-06 | 0.0023323 | 0.0023438 | 0.0023553 | 0.0023668 | 0.0023784 | 0.0023801 | 0.0023819 | 0.0023836 | 0.0023854 | 0.0023871 | 0.0023889 | 0.0023906 | 0.0023924 | 0.0023941 | 0.0023959 | 0.0023976 | 0.0023994 | 0.0024011 | 0.0024029 | 0.0024047 | 8.6794e-06 | 2.2761e-06 | 0.0012647 | 0.0012734 | 0.001282 | 0.0012907 | 0.0012994 | 0.0013017 | 0.0013039 | 0.0013062 | 0.0013085 | 0.0013108 | 0.001313 | 0.0013153 | 0.0013176 | 0.0013199 | 0.0013222 | 0.0013244 | 0.0013267 | 0.001329 | 0.0013313 | 0.0013335
| CTN002-182897070 | 2 | 2 | 2.03e-06 | 0 | 3.2e-06 | 0 | 3.4e-06 | 0 | 3.3429e-08 | 1e-08 | 3.0663e-06 | 3.0997e-06 | 3.1331e-06 | 3.1666e-06 | 3.2e-06 | 3.21e-06 | 3.22e-06 | 3.23e-06 | 3.24e-06 | 3.25e-06 | 3.26e-06 | 3.27e-06 | 3.28e-06 | 3.29e-06 | 3.3e-06 | 3.31e-06 | 3.32e-06 | 3.33e-06 | 3.34e-06 | 3.35e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN002-24605474 | 470 | 255 | 0.015432 | 0.002421 | 0.018392 | 0.0030943 | 0.018518 | 0.0031775 | 8.4592e-05 | 6.2606e-06 | 0.018054 | 0.018139 | 0.018223 | 0.018308 | 0.018392 | 0.018399 | 0.018405 | 0.018411 | 0.018417 | 0.018424 | 0.01843 | 0.018436 | 0.018442 | 0.018449 | 0.018455 | 0.018461 | 0.018467 | 0.018474 | 0.01848 | 0.018486 | 1.9236e-05 | 4.1627e-06 | 0.0030173 | 0.0030366 | 0.0030558 | 0.0030751 | 0.0030943 | 0.0030985 | 0.0031026 | 0.0031068 | 0.0031109 | 0.0031151 | 0.0031193 | 0.0031234 | 0.0031276 | 0.0031318 | 0.0031359 | 0.0031401 | 0.0031442 | 0.0031484 | 0.0031526 | 0.0031567
| CTN003-15418451 | 1199 | 382 | 0.011571 | 0.0015029 | 0.014617 | 0.0021399 | 0.014784 | 0.0022102 | 8.7024e-05 | 8.3901e-06 | 0.014268 | 0.014356 | 0.014443 | 0.01453 | 0.014617 | 0.014625 | 0.014633 | 0.014642 | 0.01465 | 0.014659 | 0.014667 | 0.014675 | 0.014684 | 0.014692 | 0.0147 | 0.014709 | 0.014717 | 0.014726 | 0.014734 | 0.014742 | 1.82e-05 | 3.5153e-06 | 0.0020671 | 0.0020853 | 0.0021035 | 0.0021217 | 0.0021399 | 0.0021434 | 0.002147 | 0.0021505 | 0.002154 | 0.0021575 | 0.002161 | 0.0021645 | 0.002168 | 0.0021716 | 0.0021751 | 0.0021786 | 0.0021821 | 0.0021856 | 0.0021891 | 0.0021927
| CTN003-155024326 | 10 | 10 | 0.0014376 | 0 | 0.0022244 | 0 | 0.0023124 | 0 | 2.248e-05 | 4.4026e-06 | 0.0021345 | 0.002157 | 0.0021794 | 0.0022019 | 0.0022244 | 0.0022288 | 0.0022332 | 0.0022376 | 0.002242 | 0.0022464 | 0.0022508 | 0.0022552 | 0.0022596 | 0.002264 | 0.0022684 | 0.0022728 | 0.0022772 | 0.0022816 | 0.002286 | 0.0022904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155024531 | 13 | 13 | 0.001743 | 0 | 0.0026565 | 0 | 0.0027339 | 0 | 2.6103e-05 | 3.868e-06 | 0.0025521 | 0.0025782 | 0.0026043 | 0.0026304 | 0.0026565 | 0.0026604 | 0.0026643 | 0.0026682 | 0.002672 | 0.0026759 | 0.0026798 | 0.0026836 | 0.0026875 | 0.0026914 | 0.0026952 | 0.0026991 | 0.002703 | 0.0027068 | 0.0027107 | 0.0027146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155024643 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155024758 | 15 | 15 | 0.0041969 | 0 | 0.0063032 | 0 | 0.0066365 | 0 | 6.0181e-05 | 1.6662e-05 | 0.0060625 | 0.0061227 | 0.0061829 | 0.0062431 | 0.0063032 | 0.0063199 | 0.0063366 | 0.0063532 | 0.0063699 | 0.0063866 | 0.0064032 | 0.0064199 | 0.0064365 | 0.0064532 | 0.0064699 | 0.0064865 | 0.0065032 | 0.0065199 | 0.0065365 | 0.0065532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155024899 | 19 | 19 | 0.0037511 | 0 | 0.0051937 | 0 | 0.0056308 | 0 | 4.1215e-05 | 2.1854e-05 | 0.0050288 | 0.00507 | 0.0051112 | 0.0051525 | 0.0051937 | 0.0052155 | 0.0052374 | 0.0052592 | 0.0052811 | 0.0053029 | 0.0053248 | 0.0053467 | 0.0053685 | 0.0053904 | 0.0054122 | 0.0054341 | 0.0054559 | 0.0054778 | 0.0054996 | 0.0055215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155024988 | 12 | 12 | 0.0017662 | 0 | 0.0024281 | 0 | 0.0027378 | 0 | 1.8911e-05 | 1.5484e-05 | 0.0023524 | 0.0023714 | 0.0023903 | 0.0024092 | 0.0024281 | 0.0024436 | 0.0024591 | 0.0024745 | 0.00249 | 0.0025055 | 0.002521 | 0.0025365 | 0.002552 | 0.0025674 | 0.0025829 | 0.0025984 | 0.0026139 | 0.0026294 | 0.0026449 | 0.0026603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155025108 | 5 | 5 | 0.0013325 | 0 | 0.0018978 | 0 | 0.0020371 | 0 | 1.6152e-05 | 6.9641e-06 | 0.0018332 | 0.0018494 | 0.0018655 | 0.0018817 | 0.0018978 | 0.0019048 | 0.0019117 | 0.0019187 | 0.0019257 | 0.0019326 | 0.0019396 | 0.0019466 | 0.0019535 | 0.0019605 | 0.0019675 | 0.0019744 | 0.0019814 | 0.0019883 | 0.0019953 | 0.0020023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155025214 | 6 | 6 | 0.0021888 | 0 | 0.0032816 | 0 | 0.0034039 | 0 | 3.1223e-05 | 6.116e-06 | 0.0031567 | 0.0031879 | 0.0032191 | 0.0032504 | 0.0032816 | 0.0032877 | 0.0032938 | 0.0032999 | 0.003306 | 0.0033122 | 0.0033183 | 0.0033244 | 0.0033305 | 0.0033366 | 0.0033427 | 0.0033489 | 0.003355 | 0.0033611 | 0.0033672 | 0.0033733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155025401 | 30 | 30 | 0.0034278 | 0 | 0.0047827 | 0 | 0.0047209 | 0 | 3.8712e-05 | -3.0891e-06 | 0.0046279 | 0.0046666 | 0.0047053 | 0.004744 | 0.0047827 | 0.0047796 | 0.0047765 | 0.0047734 | 0.0047703 | 0.0047673 | 0.0047642 | 0.0047611 | 0.004758 | 0.0047549 | 0.0047518 | 0.0047487 | 0.0047456 | 0.0047425 | 0.0047395 | 0.0047364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155052230 | 8 | 8 | 0.0026724 | 0 | 0.0040728 | 0 | 0.0042377 | 0 | 4.0014e-05 | 8.2406e-06 | 0.0039128 | 0.0039528 | 0.0039928 | 0.0040328 | 0.0040728 | 0.0040811 | 0.0040893 | 0.0040976 | 0.0041058 | 0.004114 | 0.0041223 | 0.0041305 | 0.0041388 | 0.004147 | 0.0041553 | 0.0041635 | 0.0041717 | 0.00418 | 0.0041882 | 0.0041965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155063034 | 16 | 16 | 0.0031608 | 0 | 0.004803 | 0 | 0.0050241 | 0 | 4.692e-05 | 1.1052e-05 | 0.0046153 | 0.0046623 | 0.0047092 | 0.0047561 | 0.004803 | 0.0048141 | 0.0048251 | 0.0048362 | 0.0048472 | 0.0048583 | 0.0048693 | 0.0048804 | 0.0048914 | 0.0049025 | 0.0049135 | 0.0049246 | 0.0049357 | 0.0049467 | 0.0049578 | 0.0049688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155063181 | 8 | 8 | 0.00035951 | 0 | 0.00055689 | 0 | 0.00058678 | 0 | 5.6396e-06 | 1.4944e-06 | 0.00053433 | 0.00053997 | 0.00054561 | 0.00055125 | 0.00055689 | 0.00055839 | 0.00055988 | 0.00056137 | 0.00056287 | 0.00056436 | 0.00056586 | 0.00056735 | 0.00056885 | 0.00057034 | 0.00057184 | 0.00057333 | 0.00057482 | 0.00057632 | 0.00057781 | 0.00057931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155063369 | 9 | 9 | 0.0019027 | 0 | 0.0027506 | 0 | 0.0030106 | 0 | 2.4225e-05 | 1.3002e-05 | 0.0026537 | 0.0026779 | 0.0027021 | 0.0027263 | 0.0027506 | 0.0027636 | 0.0027766 | 0.0027896 | 0.0028026 | 0.0028156 | 0.0028286 | 0.0028416 | 0.0028546 | 0.0028676 | 0.0028806 | 0.0028936 | 0.0029066 | 0.0029196 | 0.0029326 | 0.0029456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155063514 | 4 | 4 | 0.00045373 | 0 | 0.00063525 | 0 | 0.0006892 | 0 | 5.1862e-06 | 2.6974e-06 | 0.0006145 | 0.00061969 | 0.00062488 | 0.00063006 | 0.00063525 | 0.00063795 | 0.00064064 | 0.00064334 | 0.00064604 | 0.00064874 | 0.00065143 | 0.00065413 | 0.00065683 | 0.00065953 | 0.00066222 | 0.00066492 | 0.00066762 | 0.00067032 | 0.00067301 | 0.00067571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155063645 | 2 | 2 | 0.0015288 | 0 | 0.0022363 | 0 | 0.0023908 | 0 | 2.0215e-05 | 7.7252e-06 | 0.0021554 | 0.0021756 | 0.0021959 | 0.0022161 | 0.0022363 | 0.002244 | 0.0022517 | 0.0022595 | 0.0022672 | 0.0022749 | 0.0022826 | 0.0022904 | 0.0022981 | 0.0023058 | 0.0023135 | 0.0023213 | 0.002329 | 0.0023367 | 0.0023444 | 0.0023522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155063885 | 22 | 22 | 0.007221 | 0 | 0.010926 | 0 | 0.011755 | 0 | 0.00010586 | 4.1445e-05 | 0.010503 | 0.010608 | 0.010714 | 0.01082 | 0.010926 | 0.010967 | 0.011009 | 0.01105 | 0.011092 | 0.011133 | 0.011175 | 0.011216 | 0.011258 | 0.011299 | 0.011341 | 0.011382 | 0.011423 | 0.011465 | 0.011506 | 0.011548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155155512 | 27 | 27 | 0.0017627 | 0 | 0.0023585 | 0 | 0.0025702 | 0 | 1.7022e-05 | 1.0586e-05 | 0.0022904 | 0.0023074 | 0.0023244 | 0.0023415 | 0.0023585 | 0.0023691 | 0.0023797 | 0.0023902 | 0.0024008 | 0.0024114 | 0.002422 | 0.0024326 | 0.0024432 | 0.0024538 | 0.0024643 | 0.0024749 | 0.0024855 | 0.0024961 | 0.0025067 | 0.0025173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155155602 | 3 | 3 | 4.9e-06 | 0 | 7.06e-06 | 0 | 7.87e-06 | 0 | 6.1714e-08 | 4.05e-08 | 6.8131e-06 | 6.8749e-06 | 6.9366e-06 | 6.9983e-06 | 7.06e-06 | 7.1005e-06 | 7.141e-06 | 7.1815e-06 | 7.222e-06 | 7.2625e-06 | 7.303e-06 | 7.3435e-06 | 7.384e-06 | 7.4245e-06 | 7.465e-06 | 7.5055e-06 | 7.546e-06 | 7.5865e-06 | 7.627e-06 | 7.6675e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155176630 | 16 | 16 | 0.0017744 | 0 | 0.0026157 | 0 | 0.0026716 | 0 | 2.4037e-05 | 2.7939e-06 | 0.0025196 | 0.0025436 | 0.0025676 | 0.0025917 | 0.0026157 | 0.0026185 | 0.0026213 | 0.0026241 | 0.0026269 | 0.0026297 | 0.0026325 | 0.0026353 | 0.0026381 | 0.0026409 | 0.0026437 | 0.0026465 | 0.0026492 | 0.002652 | 0.0026548 | 0.0026576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155177865 | 5 | 5 | 0.00038243 | 0 | 0.00057702 | 0 | 0.0005936 | 0 | 5.5599e-06 | 8.289e-07 | 0.00055479 | 0.00056035 | 0.00056591 | 0.00057147 | 0.00057703 | 0.00057785 | 0.00057868 | 0.00057951 | 0.00058034 | 0.00058117 | 0.000582 | 0.00058283 | 0.00058366 | 0.00058449 | 0.00058531 | 0.00058614 | 0.00058697 | 0.0005878 | 0.00058863 | 0.00058946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155392598 | 7 | 7 | 0.0013318 | 0 | 0.002095 | 0 | 0.0020835 | 0 | 2.1805e-05 | -5.7485e-07 | 0.0020078 | 0.0020296 | 0.0020514 | 0.0020732 | 0.002095 | 0.0020944 | 0.0020939 | 0.0020933 | 0.0020927 | 0.0020921 | 0.0020916 | 0.002091 | 0.0020904 | 0.0020898 | 0.0020893 | 0.0020887 | 0.0020881 | 0.0020875 | 0.002087 | 0.0020864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155422079 | 25 | 18 | 0.0029334 | 0.00018892 | 0.0043334 | 0.00029688 | 0.0045813 | 0.00031815 | 4e-05 | 1.2394e-05 | 0.0041734 | 0.0042134 | 0.0042534 | 0.0042934 | 0.0043334 | 0.0043458 | 0.0043582 | 0.0043706 | 0.004383 | 0.0043954 | 0.0044078 | 0.0044202 | 0.0044326 | 0.004445 | 0.0044574 | 0.0044698 | 0.0044821 | 0.0044945 | 0.0045069 | 0.0045193 | 3.0847e-06 | 1.0635e-06 | 0.00028454 | 0.00028763 | 0.00029071 | 0.0002938 | 0.00029688 | 0.00029794 | 0.00029901 | 0.00030007 | 0.00030114 | 0.0003022 | 0.00030326 | 0.00030433 | 0.00030539 | 0.00030645 | 0.00030752 | 0.00030858 | 0.00030964 | 0.00031071 | 0.00031177 | 0.00031283
| CTN003-158006357 | 782 | 19 | 0.00079654 | 0.00073011 | 0.0012405 | 0.0011498 | 0.0012916 | 0.0011991 | 1.2684e-05 | 2.5538e-06 | 0.0011898 | 0.0012024 | 0.0012151 | 0.0012278 | 0.0012405 | 0.001243 | 0.0012456 | 0.0012481 | 0.0012507 | 0.0012533 | 0.0012558 | 0.0012584 | 0.0012609 | 0.0012635 | 0.001266 | 0.0012686 | 0.0012711 | 0.0012737 | 0.0012762 | 0.0012788 | 1.199e-05 | 2.4665e-06 | 0.0011018 | 0.0011138 | 0.0011258 | 0.0011378 | 0.0011498 | 0.0011522 | 0.0011547 | 0.0011572 | 0.0011596 | 0.0011621 | 0.0011646 | 0.001167 | 0.0011695 | 0.001172 | 0.0011744 | 0.0011769 | 0.0011794 | 0.0011818 | 0.0011843 | 0.0011868
| CTN003-182897268 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-24603160 | 339 | 257 | 0.012472 | 0.00096796 | 0.015639 | 0.0014606 | 0.015661 | 0.0014996 | 9.0467e-05 | 1.1175e-06 | 0.015277 | 0.015367 | 0.015458 | 0.015548 | 0.015639 | 0.01564 | 0.015641 | 0.015642 | 0.015643 | 0.015644 | 0.015645 | 0.015646 | 0.015648 | 0.015649 | 0.01565 | 0.015651 | 0.015652 | 0.015653 | 0.015654 | 0.015655 | 1.4077e-05 | 1.9495e-06 | 0.0014043 | 0.0014184 | 0.0014325 | 0.0014466 | 0.0014606 | 0.0014626 | 0.0014645 | 0.0014665 | 0.0014684 | 0.0014704 | 0.0014723 | 0.0014743 | 0.0014762 | 0.0014782 | 0.0014801 | 0.0014821 | 0.001484 | 0.001486 | 0.0014879 | 0.0014899
| CTN003-47810169 | 418 | 261 | 0.010303 | 0.0033948 | 0.013943 | 0.0050825 | 0.014397 | 0.0053357 | 0.00010401 | 2.2698e-05 | 0.013527 | 0.013631 | 0.013735 | 0.013839 | 0.013943 | 0.013966 | 0.013989 | 0.014012 | 0.014034 | 0.014057 | 0.01408 | 0.014102 | 0.014125 | 0.014148 | 0.01417 | 0.014193 | 0.014216 | 0.014239 | 0.014261 | 0.014284 | 4.8219e-05 | 1.2662e-05 | 0.0048896 | 0.0049378 | 0.004986 | 0.0050343 | 0.0050825 | 0.0050951 | 0.0051078 | 0.0051205 | 0.0051331 | 0.0051458 | 0.0051585 | 0.0051711 | 0.0051838 | 0.0051964 | 0.0052091 | 0.0052218 | 0.0052344 | 0.0052471 | 0.0052597 | 0.0052724
| CTN003-88138723 | 18 | 18 | 0.0021369 | 0 | 0.0032087 | 0 | 0.0033973 | 0 | 3.0623e-05 | 9.4301e-06 | 0.0030862 | 0.0031168 | 0.0031475 | 0.0031781 | 0.0032087 | 0.0032181 | 0.0032276 | 0.003237 | 0.0032464 | 0.0032559 | 0.0032653 | 0.0032747 | 0.0032841 | 0.0032936 | 0.003303 | 0.0033124 | 0.0033219 | 0.0033313 | 0.0033407 | 0.0033502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN004-134372186 | 40 | 40 | 0.0030933 | 0 | 0.0042402 | 0 | 0.0043631 | 0 | 3.2767e-05 | 6.1475e-06 | 0.0041091 | 0.0041419 | 0.0041746 | 0.0042074 | 0.0042402 | 0.0042463 | 0.0042525 | 0.0042586 | 0.0042648 | 0.0042709 | 0.004277 | 0.0042832 | 0.0042893 | 0.0042955 | 0.0043016 | 0.0043078 | 0.0043139 | 0.0043201 | 0.0043262 | 0.0043324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN004-134372435 | 24 | 24 | 0.0032561 | 0 | 0.004528 | 0 | 0.004611 | 0 | 3.634e-05 | 4.1468e-06 | 0.0043827 | 0.004419 | 0.0044554 | 0.0044917 | 0.004528 | 0.0045322 | 0.0045363 | 0.0045405 | 0.0045446 | 0.0045488 | 0.0045529 | 0.0045571 | 0.0045612 | 0.0045654 | 0.0045695 | 0.0045736 | 0.0045778 | 0.0045819 | 0.0045861 | 0.0045902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN004-15418536 | 1261 | 1126 | 0.040513 | 0.0062093 | 0.050199 | 0.0084655 | 0.050825 | 0.0087302 | 0.00027674 | 3.1332e-05 | 0.049092 | 0.049369 | 0.049645 | 0.049922 | 0.050199 | 0.05023 | 0.050261 | 0.050293 | 0.050324 | 0.050355 | 0.050387 | 0.050418 | 0.050449 | 0.050481 | 0.050512 | 0.050543 | 0.050575 | 0.050606 | 0.050637 | 0.050669 | 6.4463e-05 | 1.3236e-05 | 0.0082076 | 0.0082721 | 0.0083366 | 0.008401 | 0.0084655 | 0.0084787 | 0.008492 | 0.0085052 | 0.0085184 | 0.0085317 | 0.0085449 | 0.0085581 | 0.0085714 | 0.0085846 | 0.0085978 | 0.0086111 | 0.0086243 | 0.0086376 | 0.0086508 | 0.008664
| CTN004-15418547 | 1262 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN004-155091767 | 12 | 12 | 0.0023309 | 0 | 0.0031271 | 0 | 0.0032509 | 0 | 2.2747e-05 | 6.1899e-06 | 0.0030361 | 0.0030588 | 0.0030816 | 0.0031043 | 0.0031271 | 0.0031333 | 0.0031395 | 0.0031456 | 0.0031518 | 0.003158 | 0.0031642 | 0.0031704 | 0.0031766 | 0.0031828 | 0.003189 | 0.0031952 | 0.0032014 | 0.0032075 | 0.0032137 | 0.0032199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN004-155091935 | 23 | 23 | 0.0019128 | 0 | 0.0026803 | 0 | 0.0027412 | 0 | 2.1928e-05 | 3.0459e-06 | 0.0025925 | 0.0026145 | 0.0026364 | 0.0026583 | 0.0026803 | 0.0026833 | 0.0026864 | 0.0026894 | 0.0026924 | 0.0026955 | 0.0026985 | 0.0027016 | 0.0027046 | 0.0027077 | 0.0027107 | 0.0027138 | 0.0027168 | 0.0027199 | 0.0027229 | 0.0027259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN004-155092023 | 9 | 9 | 0.0030798 | 0 | 0.004211 | 0 | 0.0043258 | 0 | 3.232e-05 | 5.7421e-06 | 0.0040817 | 0.004114 | 0.0041463 | 0.0041787 | 0.004211 | 0.0042167 | 0.0042225 | 0.0042282 | 0.0042339 | 0.0042397 | 0.0042454 | 0.0042512 | 0.0042569 | 0.0042627 | 0.0042684 | 0.0042741 | 0.0042799 | 0.0042856 | 0.0042914 | 0.0042971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN004-155092123 | 25 | 25 | 0.0056605 | 0 | 0.0074944 | 0 | 0.0074991 | 0 | 5.2398e-05 | 2.3495e-07 | 0.0072848 | 0.0073372 | 0.0073896 | 0.007442 | 0.0074944 | 0.0074946 | 0.0074949 | 0.0074951 | 0.0074953 | 0.0074956 | 0.0074958 | 0.0074961 | 0.0074963 | 0.0074965 | 0.0074968 | 0.007497 | 0.0074972 | 0.0074975 | 0.0074977 | 0.0074979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN004-160370806 | 0 | 0 | 1.11e-06 | 0 | 1.82e-06 | 0 | 1.87e-06 | 0 | 2.0286e-08 | 2.5e-09 | 1.7389e-06 | 1.7591e-06 | 1.7794e-06 | 1.7997e-06 | 1.82e-06 | 1.8225e-06 | 1.825e-06 | 1.8275e-06 | 1.83e-06 | 1.8325e-06 | 1.835e-06 | 1.8375e-06 | 1.84e-06 | 1.8425e-06 | 1.845e-06 | 1.8475e-06 | 1.85e-06 | 1.8525e-06 | 1.855e-06 | 1.8575e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN005-15418323 | 648 | 648 | 0.0059125 | 0 | 0.0071674 | 0 | 0.007233 | 0 | 3.5854e-05 | 3.2818e-06 | 0.0070239 | 0.0070598 | 0.0070957 | 0.0071315 | 0.0071674 | 0.0071706 | 0.0071739 | 0.0071772 | 0.0071805 | 0.0071838 | 0.0071871 | 0.0071903 | 0.0071936 | 0.0071969 | 0.0072002 | 0.0072035 | 0.0072067 | 0.00721 | 0.0072133 | 0.0072166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-100525030 | 40 | 40 | 0.002241 | 0 | 0.0029011 | 0 | 0.0029104 | 0 | 1.8858e-05 | 4.68e-07 | 0.0028256 | 0.0028445 | 0.0028633 | 0.0028822 | 0.0029011 | 0.0029015 | 0.002902 | 0.0029025 | 0.0029029 | 0.0029034 | 0.0029039 | 0.0029043 | 0.0029048 | 0.0029053 | 0.0029057 | 0.0029062 | 0.0029067 | 0.0029071 | 0.0029076 | 0.0029081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-123737136 | 276 | 10 | 0.00048647 | 0.0004499 | 0.00062199 | 0.00064041 | 0.00062623 | 0.00065795 | 3.8718e-06 | 2.1205e-07 | 0.0006065 | 0.00061037 | 0.00061424 | 0.00061812 | 0.00062199 | 0.0006222 | 0.00062241 | 0.00062262 | 0.00062284 | 0.00062305 | 0.00062326 | 0.00062347 | 0.00062368 | 0.0006239 | 0.00062411 | 0.00062432 | 0.00062453 | 0.00062474 | 0.00062496 | 0.00062517 | 5.4431e-06 | 8.7685e-07 | 0.00061864 | 0.00062408 | 0.00062952 | 0.00063497 | 0.00064041 | 0.00064129 | 0.00064216 | 0.00064304 | 0.00064392 | 0.00064479 | 0.00064567 | 0.00064655 | 0.00064742 | 0.0006483 | 0.00064918 | 0.00065005 | 0.00065093 | 0.00065181 | 0.00065268 | 0.00065356
| CTN006-138230928 | 21 | 21 | 0.0030681 | 0 | 0.0041225 | 0 | 0.004213 | 0 | 3.0128e-05 | 4.5212e-06 | 0.004002 | 0.0040322 | 0.0040623 | 0.0040924 | 0.0041225 | 0.0041271 | 0.0041316 | 0.0041361 | 0.0041406 | 0.0041452 | 0.0041497 | 0.0041542 | 0.0041587 | 0.0041632 | 0.0041678 | 0.0041723 | 0.0041768 | 0.0041813 | 0.0041858 | 0.0041904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-15418599 | 1975 | 0 | 4.31e-07 | 1.18e-05 | 6.69e-07 | 1.83e-05 | 7.1e-07 | 1.94e-05 | 6.8e-09 | 2.05e-09 | 6.418e-07 | 6.486e-07 | 6.554e-07 | 6.622e-07 | 6.69e-07 | 6.7105e-07 | 6.731e-07 | 6.7515e-07 | 6.772e-07 | 6.7925e-07 | 6.813e-07 | 6.8335e-07 | 6.854e-07 | 6.8745e-07 | 6.895e-07 | 6.9155e-07 | 6.936e-07 | 6.9565e-07 | 6.977e-07 | 6.9975e-07 | 1.8571e-07 | 5.5e-08 | 1.7557e-05 | 1.7743e-05 | 1.7929e-05 | 1.8114e-05 | 1.83e-05 | 1.8355e-05 | 1.841e-05 | 1.8465e-05 | 1.852e-05 | 1.8575e-05 | 1.863e-05 | 1.8685e-05 | 1.874e-05 | 1.8795e-05 | 1.885e-05 | 1.8905e-05 | 1.896e-05 | 1.9015e-05 | 1.907e-05 | 1.9125e-05
| CTN006-154972740 | 24 | 24 | 0.001607 | 0 | 0.0022104 | 0 | 0.0021919 | 0 | 1.724e-05 | -9.2395e-07 | 0.0021414 | 0.0021587 | 0.0021759 | 0.0021932 | 0.0022104 | 0.0022095 | 0.0022086 | 0.0022076 | 0.0022067 | 0.0022058 | 0.0022049 | 0.0022039 | 0.002203 | 0.0022021 | 0.0022012 | 0.0022002 | 0.0021993 | 0.0021984 | 0.0021975 | 0.0021966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-154972844 | 4 | 4 | 1.82e-06 | 0 | 2.9e-06 | 0 | 2.96e-06 | 0 | 3.0857e-08 | 3e-09 | 2.7766e-06 | 2.8074e-06 | 2.8383e-06 | 2.8691e-06 | 2.9e-06 | 2.903e-06 | 2.906e-06 | 2.909e-06 | 2.912e-06 | 2.915e-06 | 2.918e-06 | 2.921e-06 | 2.924e-06 | 2.927e-06 | 2.93e-06 | 2.933e-06 | 2.936e-06 | 2.939e-06 | 2.942e-06 | 2.945e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-154972931 | 24 | 24 | 0.0039495 | 0 | 0.0057753 | 0 | 0.0058832 | 0 | 5.2167e-05 | 5.3939e-06 | 0.0055666 | 0.0056188 | 0.005671 | 0.0057232 | 0.0057753 | 0.0057807 | 0.0057861 | 0.0057915 | 0.0057969 | 0.0058023 | 0.0058077 | 0.0058131 | 0.0058185 | 0.0058239 | 0.0058293 | 0.0058347 | 0.00584 | 0.0058454 | 0.0058508 | 0.0058562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-154973045 | 9 | 9 | 0.0031355 | 0 | 0.004911 | 0 | 0.0048955 | 0 | 5.0728e-05 | -7.747e-07 | 0.0047081 | 0.0047588 | 0.0048095 | 0.0048602 | 0.004911 | 0.0049102 | 0.0049094 | 0.0049086 | 0.0049079 | 0.0049071 | 0.0049063 | 0.0049055 | 0.0049048 | 0.004904 | 0.0049032 | 0.0049024 | 0.0049017 | 0.0049009 | 0.0049001 | 0.0048994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155015964 | 22 | 22 | 0.00088214 | 0 | 0.0011576 | 0 | 0.0011682 | 0 | 7.8702e-06 | 5.3005e-07 | 0.0011261 | 0.001134 | 0.0011419 | 0.0011497 | 0.0011576 | 0.0011581 | 0.0011587 | 0.0011592 | 0.0011597 | 0.0011602 | 0.0011608 | 0.0011613 | 0.0011618 | 0.0011624 | 0.0011629 | 0.0011634 | 0.001164 | 0.0011645 | 0.001165 | 0.0011655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155016184 | 7 | 7 | 9.92e-05 | 0 | 0.00010719 | 0 | 0.00010567 | 0 | 2.2817e-07 | -7.555e-08 | 0.00010627 | 0.0001065 | 0.00010673 | 0.00010696 | 0.00010719 | 0.00010711 | 0.00010703 | 0.00010696 | 0.00010688 | 0.00010681 | 0.00010673 | 0.00010666 | 0.00010658 | 0.00010651 | 0.00010643 | 0.00010635 | 0.00010628 | 0.0001062 | 0.00010613 | 0.00010605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155016351 | 8 | 8 | 9.34e-06 | 0 | 1.45e-05 | 0 | 1.54e-05 | 0 | 1.4743e-07 | 4.5e-08 | 1.391e-05 | 1.4058e-05 | 1.4205e-05 | 1.4353e-05 | 1.45e-05 | 1.4545e-05 | 1.459e-05 | 1.4635e-05 | 1.468e-05 | 1.4725e-05 | 1.477e-05 | 1.4815e-05 | 1.486e-05 | 1.4905e-05 | 1.495e-05 | 1.4995e-05 | 1.504e-05 | 1.5085e-05 | 1.513e-05 | 1.5175e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155016482 | 36 | 36 | 0.0048848 | 0 | 0.0068336 | 0 | 0.0069133 | 0 | 5.5682e-05 | 3.985e-06 | 0.0066109 | 0.0066666 | 0.0067223 | 0.006778 | 0.0068336 | 0.0068376 | 0.0068416 | 0.0068456 | 0.0068496 | 0.0068536 | 0.0068576 | 0.0068615 | 0.0068655 | 0.0068695 | 0.0068735 | 0.0068775 | 0.0068815 | 0.0068855 | 0.0068894 | 0.0068934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155018538 | 12 | 12 | 0.0032038 | 0 | 0.0045462 | 0 | 0.0047139 | 0 | 3.8354e-05 | 8.382e-06 | 0.0043928 | 0.0044311 | 0.0044695 | 0.0045079 | 0.0045462 | 0.0045546 | 0.004563 | 0.0045714 | 0.0045797 | 0.0045881 | 0.0045965 | 0.0046049 | 0.0046133 | 0.0046216 | 0.00463 | 0.0046384 | 0.0046468 | 0.0046552 | 0.0046636 | 0.0046719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155018674 | 13 | 13 | 0.0036785 | 0 | 0.0047141 | 0 | 0.0047528 | 0 | 2.9588e-05 | 1.9366e-06 | 0.0045957 | 0.0046253 | 0.0046549 | 0.0046845 | 0.0047141 | 0.004716 | 0.004718 | 0.0047199 | 0.0047218 | 0.0047238 | 0.0047257 | 0.0047276 | 0.0047296 | 0.0047315 | 0.0047335 | 0.0047354 | 0.0047373 | 0.0047393 | 0.0047412 | 0.0047431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155018773 | 23 | 23 | 0.0021783 | 0 | 0.0031447 | 0 | 0.0031672 | 0 | 2.7613e-05 | 1.1207e-06 | 0.0030343 | 0.0030619 | 0.0030895 | 0.0031171 | 0.0031447 | 0.0031459 | 0.003147 | 0.0031481 | 0.0031492 | 0.0031504 | 0.0031515 | 0.0031526 | 0.0031537 | 0.0031548 | 0.003156 | 0.0031571 | 0.0031582 | 0.0031593 | 0.0031604 | 0.0031616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155018968 | 7 | 7 | 1.19e-05 | 0 | 1.99e-05 | 0 | 2.03e-05 | 0 | 2.2857e-07 | 2e-08 | 1.8986e-05 | 1.9214e-05 | 1.9443e-05 | 1.9671e-05 | 1.99e-05 | 1.992e-05 | 1.994e-05 | 1.996e-05 | 1.998e-05 | 2e-05 | 2.002e-05 | 2.004e-05 | 2.006e-05 | 2.008e-05 | 2.01e-05 | 2.012e-05 | 2.014e-05 | 2.016e-05 | 2.018e-05 | 2.02e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155019123 | 19 | 19 | 0.0027092 | 0 | 0.0036733 | 0 | 0.0037446 | 0 | 2.7546e-05 | 3.5677e-06 | 0.0035631 | 0.0035906 | 0.0036182 | 0.0036457 | 0.0036733 | 0.0036768 | 0.0036804 | 0.003684 | 0.0036875 | 0.0036911 | 0.0036947 | 0.0036983 | 0.0037018 | 0.0037054 | 0.003709 | 0.0037125 | 0.0037161 | 0.0037197 | 0.0037232 | 0.0037268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155062010 | 26 | 26 | 0.0013541 | 0 | 0.0019474 | 0 | 0.0019687 | 0 | 1.6951e-05 | 1.0668e-06 | 0.0018796 | 0.0018965 | 0.0019135 | 0.0019304 | 0.0019474 | 0.0019485 | 0.0019495 | 0.0019506 | 0.0019517 | 0.0019527 | 0.0019538 | 0.0019549 | 0.0019559 | 0.001957 | 0.0019581 | 0.0019591 | 0.0019602 | 0.0019613 | 0.0019623 | 0.0019634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155062651 | 38 | 38 | 0.0030799 | 0 | 0.004393 | 0 | 0.0043979 | 0 | 3.7517e-05 | 2.446e-07 | 0.0042429 | 0.0042805 | 0.004318 | 0.0043555 | 0.004393 | 0.0043933 | 0.0043935 | 0.0043937 | 0.004394 | 0.0043942 | 0.0043945 | 0.0043947 | 0.004395 | 0.0043952 | 0.0043955 | 0.0043957 | 0.0043959 | 0.0043962 | 0.0043964 | 0.0043967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155077957 | 26 | 26 | 0.002653 | 0 | 0.0036807 | 0 | 0.003798 | 0 | 2.9363e-05 | 5.8629e-06 | 0.0035633 | 0.0035926 | 0.003622 | 0.0036514 | 0.0036807 | 0.0036866 | 0.0036925 | 0.0036983 | 0.0037042 | 0.00371 | 0.0037159 | 0.0037218 | 0.0037276 | 0.0037335 | 0.0037394 | 0.0037452 | 0.0037511 | 0.003757 | 0.0037628 | 0.0037687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155078265 | 11 | 11 | 1.95e-05 | 0 | 3.24e-05 | 0 | 3.26e-05 | 0 | 3.6857e-07 | 1e-08 | 3.0926e-05 | 3.1294e-05 | 3.1663e-05 | 3.2031e-05 | 3.24e-05 | 3.241e-05 | 3.242e-05 | 3.243e-05 | 3.244e-05 | 3.245e-05 | 3.246e-05 | 3.247e-05 | 3.248e-05 | 3.249e-05 | 3.25e-05 | 3.251e-05 | 3.252e-05 | 3.253e-05 | 3.254e-05 | 3.255e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155078364 | 13 | 13 | 0.003136 | 0 | 0.0048943 | 0 | 0.0049544 | 0 | 5.0238e-05 | 3.003e-06 | 0.0046934 | 0.0047436 | 0.0047938 | 0.0048441 | 0.0048943 | 0.0048973 | 0.0049003 | 0.0049033 | 0.0049063 | 0.0049093 | 0.0049123 | 0.0049153 | 0.0049183 | 0.0049213 | 0.0049244 | 0.0049274 | 0.0049304 | 0.0049334 | 0.0049364 | 0.0049394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155078558 | 20 | 20 | 0.002962 | 0 | 0.004247 | 0 | 0.0042482 | 0 | 3.6713e-05 | 6.04e-08 | 0.0041001 | 0.0041368 | 0.0041736 | 0.0042103 | 0.004247 | 0.004247 | 0.0042471 | 0.0042472 | 0.0042472 | 0.0042473 | 0.0042473 | 0.0042474 | 0.0042475 | 0.0042475 | 0.0042476 | 0.0042477 | 0.0042477 | 0.0042478 | 0.0042478 | 0.0042479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155078784 | 5 | 5 | 6.54e-05 | 0 | 9.42e-05 | 0 | 9.68e-05 | 0 | 8.2286e-07 | 1.3e-07 | 9.0909e-05 | 9.1731e-05 | 9.2554e-05 | 9.3377e-05 | 9.42e-05 | 9.433e-05 | 9.446e-05 | 9.459e-05 | 9.472e-05 | 9.485e-05 | 9.498e-05 | 9.511e-05 | 9.524e-05 | 9.537e-05 | 9.55e-05 | 9.563e-05 | 9.576e-05 | 9.589e-05 | 9.602e-05 | 9.615e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155078876 | 8 | 8 | 3.71e-06 | 0 | 6e-06 | 0 | 6e-06 | 0 | 6.5429e-08 | 0 | 5.7383e-06 | 5.8037e-06 | 5.8691e-06 | 5.9346e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 6e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-155392437 | 17 | 17 | 0.0021124 | 0 | 0.0030489 | 0 | 0.0030789 | 0 | 2.6755e-05 | 1.5025e-06 | 0.0029418 | 0.0029686 | 0.0029954 | 0.0030221 | 0.0030489 | 0.0030504 | 0.0030519 | 0.0030534 | 0.0030549 | 0.0030564 | 0.0030579 | 0.0030594 | 0.0030609 | 0.0030624 | 0.0030639 | 0.0030654 | 0.0030669 | 0.0030684 | 0.0030699 | 0.0030714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-157466480 | 143 | 45 | 0.00094079 | 0.00030402 | 0.0012221 | 0.00041339 | 0.00126 | 0.00042834 | 8.0374e-06 | 1.8955e-06 | 0.00119 | 0.001198 | 0.001206 | 0.0012141 | 0.0012221 | 0.001224 | 0.0012259 | 0.0012278 | 0.0012297 | 0.0012316 | 0.0012335 | 0.0012354 | 0.0012373 | 0.0012392 | 0.0012411 | 0.001243 | 0.0012448 | 0.0012467 | 0.0012486 | 0.0012505 | 3.1248e-06 | 7.4755e-07 | 0.00040089 | 0.00040401 | 0.00040714 | 0.00041026 | 0.00041338 | 0.00041413 | 0.00041488 | 0.00041563 | 0.00041638 | 0.00041712 | 0.00041787 | 0.00041862 | 0.00041937 | 0.00042011 | 0.00042086 | 0.00042161 | 0.00042236 | 0.0004231 | 0.00042385 | 0.0004246
| CTN006-157466735 | 110 | 42 | 0.0016913 | 0.00053149 | 0.0022153 | 0.00073335 | 0.0022399 | 0.00074856 | 1.4969e-05 | 1.2331e-06 | 0.0021554 | 0.0021703 | 0.0021853 | 0.0022003 | 0.0022153 | 0.0022165 | 0.0022177 | 0.0022189 | 0.0022202 | 0.0022214 | 0.0022226 | 0.0022239 | 0.0022251 | 0.0022263 | 0.0022276 | 0.0022288 | 0.00223 | 0.0022313 | 0.0022325 | 0.0022337 | 5.7675e-06 | 7.6025e-07 | 0.00071028 | 0.00071605 | 0.00072182 | 0.00072758 | 0.00073335 | 0.00073411 | 0.00073487 | 0.00073563 | 0.00073639 | 0.00073715 | 0.00073791 | 0.00073867 | 0.00073943 | 0.00074019 | 0.00074095 | 0.00074171 | 0.00074248 | 0.00074324 | 0.000744 | 0.00074476
| CTN006-157466858 | 1034 | 901 | 0.0042097 | 0.0027764 | 0.0052956 | 0.004106 | 0.0053675 | 0.0042924 | 3.1024e-05 | 3.5966e-06 | 0.0051715 | 0.0052025 | 0.0052335 | 0.0052645 | 0.0052956 | 0.0052992 | 0.0053028 | 0.0053064 | 0.00531 | 0.0053136 | 0.0053172 | 0.0053207 | 0.0053243 | 0.0053279 | 0.0053315 | 0.0053351 | 0.0053387 | 0.0053423 | 0.0053459 | 0.0053495 | 3.7989e-05 | 9.3183e-06 | 0.0039541 | 0.0039921 | 0.00403 | 0.004068 | 0.004106 | 0.0041153 | 0.0041247 | 0.004134 | 0.0041433 | 0.0041526 | 0.0041619 | 0.0041712 | 0.0041806 | 0.0041899 | 0.0041992 | 0.0042085 | 0.0042178 | 0.0042272 | 0.0042365 | 0.0042458
| CTN006-158006328 | 1165 | 35 | 0.0042108 | 0.0024397 | 0.0055538 | 0.0034907 | 0.0055448 | 0.0035116 | 3.8371e-05 | -4.49e-07 | 0.0054003 | 0.0054387 | 0.005477 | 0.0055154 | 0.0055538 | 0.0055533 | 0.0055529 | 0.0055524 | 0.005552 | 0.0055515 | 0.0055511 | 0.0055506 | 0.0055502 | 0.0055497 | 0.0055493 | 0.0055488 | 0.0055484 | 0.0055479 | 0.0055475 | 0.005547 | 3.0028e-05 | 1.0479e-06 | 0.0033706 | 0.0034006 | 0.0034306 | 0.0034606 | 0.0034907 | 0.0034917 | 0.0034928 | 0.0034938 | 0.0034949 | 0.0034959 | 0.003497 | 0.003498 | 0.003499 | 0.0035001 | 0.0035011 | 0.0035022 | 0.0035032 | 0.0035043 | 0.0035053 | 0.0035064
| CTN006-163924253 | 18 | 18 | 0.0026451 | 0 | 0.0033161 | 0 | 0.0033445 | 0 | 1.9172e-05 | 1.4177e-06 | 0.0032395 | 0.0032586 | 0.0032778 | 0.003297 | 0.0033161 | 0.0033176 | 0.003319 | 0.0033204 | 0.0033218 | 0.0033232 | 0.0033246 | 0.0033261 | 0.0033275 | 0.0033289 | 0.0033303 | 0.0033317 | 0.0033332 | 0.0033346 | 0.003336 | 0.0033374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-24603272 | 810 | 37 | 0.0035399 | 0.0029527 | 0.0045497 | 0.0038795 | 0.0046062 | 0.0039434 | 2.8853e-05 | 2.8206e-06 | 0.0044343 | 0.0044632 | 0.004492 | 0.0045209 | 0.0045497 | 0.0045526 | 0.0045554 | 0.0045582 | 0.004561 | 0.0045638 | 0.0045667 | 0.0045695 | 0.0045723 | 0.0045751 | 0.0045779 | 0.0045808 | 0.0045836 | 0.0045864 | 0.0045892 | 0.0045921 | 2.648e-05 | 3.1957e-06 | 0.0037736 | 0.0038 | 0.0038265 | 0.003853 | 0.0038795 | 0.0038827 | 0.0038859 | 0.0038891 | 0.0038923 | 0.0038955 | 0.0038986 | 0.0039018 | 0.003905 | 0.0039082 | 0.0039114 | 0.0039146 | 0.0039178 | 0.003921 | 0.0039242 | 0.0039274
| CTN006-24605098 | 95 | 34 | 0.0031001 | 0.0011248 | 0.0044006 | 0.0016793 | 0.0045054 | 0.001731 | 3.7157e-05 | 5.2385e-06 | 0.004252 | 0.0042892 | 0.0043263 | 0.0043635 | 0.0044006 | 0.0044059 | 0.0044111 | 0.0044163 | 0.0044216 | 0.0044268 | 0.0044321 | 0.0044373 | 0.0044425 | 0.0044478 | 0.004453 | 0.0044583 | 0.0044635 | 0.0044687 | 0.004474 | 0.0044792 | 1.5844e-05 | 2.5823e-06 | 0.0016159 | 0.0016318 | 0.0016476 | 0.0016635 | 0.0016793 | 0.0016819 | 0.0016845 | 0.0016871 | 0.0016897 | 0.0016922 | 0.0016948 | 0.0016974 | 0.0017 | 0.0017026 | 0.0017051 | 0.0017077 | 0.0017103 | 0.0017129 | 0.0017155 | 0.0017181
| CTN006-24605334 | 410 | 410 | 0.01608 | 0 | 0.020118 | 0 | 0.020346 | 0 | 0.00011539 | 1.14e-05 | 0.019656 | 0.019772 | 0.019887 | 0.020003 | 0.020118 | 0.020129 | 0.020141 | 0.020152 | 0.020164 | 0.020175 | 0.020186 | 0.020198 | 0.020209 | 0.020221 | 0.020232 | 0.020243 | 0.020255 | 0.020266 | 0.020278 | 0.020289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN006-88333121 | 4 | 4 | 0.0020747 | 0 | 0.0029369 | 0 | 0.0030126 | 0 | 2.4633e-05 | 3.7869e-06 | 0.0028383 | 0.002863 | 0.0028876 | 0.0029122 | 0.0029369 | 0.0029407 | 0.0029445 | 0.0029482 | 0.002952 | 0.0029558 | 0.0029596 | 0.0029634 | 0.0029672 | 0.002971 | 0.0029747 | 0.0029785 | 0.0029823 | 0.0029861 | 0.0029899 | 0.0029937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL011-193014102 | 5060 | 3214 | 0.0066585 | 1.22e-06 | 0.0070504 | 1.35e-06 | 0.0065649 | 1.19e-06 | 1.1198e-05 | -2.4277e-05 | 0.0070056 | 0.0070168 | 0.007028 | 0.0070392 | 0.0070504 | 0.0070261 | 0.0070019 | 0.0069776 | 0.0069533 | 0.006929 | 0.0069048 | 0.0068805 | 0.0068562 | 0.0068319 | 0.0068076 | 0.0067834 | 0.0067591 | 0.0067348 | 0.0067105 | 0.0066863 | 3.7143e-09 | -8e-09 | 1.3351e-06 | 1.3389e-06 | 1.3426e-06 | 1.3463e-06 | 1.35e-06 | 1.342e-06 | 1.334e-06 | 1.326e-06 | 1.318e-06 | 1.31e-06 | 1.302e-06 | 1.294e-06 | 1.286e-06 | 1.278e-06 | 1.27e-06 | 1.262e-06 | 1.254e-06 | 1.246e-06 | 1.238e-06 | 1.23e-06
| DDL011-24612671 | 1846 | 1846 | 0.00054852 | 0 | 0.00058005 | 0 | 0.00054093 | 0 | 9.0069e-07 | -1.9559e-06 | 0.00057644 | 0.00057734 | 0.00057824 | 0.00057915 | 0.00058005 | 0.00057809 | 0.00057613 | 0.00057418 | 0.00057222 | 0.00057027 | 0.00056831 | 0.00056635 | 0.0005644 | 0.00056244 | 0.00056049 | 0.00055853 | 0.00055658 | 0.00055462 | 0.00055266 | 0.00055071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL012-193014212 | 4313 | 547 | 0.002879 | 0.00016954 | 0.0036059 | 0.0002101 | 0.00409 | 0.00022869 | 2.0767e-05 | 2.4205e-05 | 0.0035228 | 0.0035436 | 0.0035643 | 0.0035851 | 0.0036059 | 0.0036301 | 0.0036543 | 0.0036785 | 0.0037027 | 0.0037269 | 0.0037511 | 0.0037753 | 0.0037995 | 0.0038237 | 0.0038479 | 0.0038721 | 0.0038963 | 0.0039205 | 0.0039447 | 0.0039689 | 1.1588e-06 | 9.2925e-07 | 0.00020546 | 0.00020662 | 0.00020778 | 0.00020894 | 0.0002101 | 0.00021103 | 0.00021196 | 0.00021289 | 0.00021382 | 0.00021475 | 0.00021568 | 0.0002166 | 0.00021753 | 0.00021846 | 0.00021939 | 0.00022032 | 0.00022125 | 0.00022218 | 0.00022311 | 0.00022404
| DDL012-24612381 | 2683 | 2683 | 0.00031985 | 0 | 0.00034236 | 0 | 0.00031479 | 0 | 6.4317e-07 | -1.3786e-06 | 0.00033979 | 0.00034043 | 0.00034108 | 0.00034172 | 0.00034236 | 0.00034098 | 0.00033961 | 0.00033823 | 0.00033685 | 0.00033547 | 0.00033409 | 0.00033271 | 0.00033133 | 0.00032996 | 0.00032858 | 0.0003272 | 0.00032582 | 0.00032444 | 0.00032306 | 0.00032168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL012-24612395 | 1083 | 1083 | 0.001171 | 0 | 0.00127 | 0 | 0.00115 | 0 | 2.826e-06 | -5.9984e-06 | 0.0012586 | 0.0012615 | 0.0012643 | 0.0012671 | 0.00127 | 0.001264 | 0.001258 | 0.001252 | 0.001246 | 0.00124 | 0.001234 | 0.001228 | 0.001222 | 0.001216 | 0.00121 | 0.001204 | 0.001198 | 0.001192 | 0.001186 | 0.00118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL013-197602097 | 5863 | 1892 | 0.0024689 | 0.00031859 | 0.0025228 | 0.00033969 | 0.0024798 | 0.00032499 | 1.5405e-06 | -2.1477e-06 | 0.0025166 | 0.0025182 | 0.0025197 | 0.0025212 | 0.0025228 | 0.0025206 | 0.0025185 | 0.0025163 | 0.0025142 | 0.002512 | 0.0025099 | 0.0025077 | 0.0025056 | 0.0025034 | 0.0025013 | 0.0024992 | 0.002497 | 0.0024949 | 0.0024927 | 0.0024906 | 6.0291e-07 | -7.348e-07 | 0.00033728 | 0.00033788 | 0.00033848 | 0.00033909 | 0.00033969 | 0.00033896 | 0.00033822 | 0.00033749 | 0.00033675 | 0.00033602 | 0.00033528 | 0.00033455 | 0.00033381 | 0.00033308 | 0.00033234 | 0.00033161 | 0.00033087 | 0.00033014 | 0.0003294 | 0.00032867
| DDL013-24612353 | 2054 | 2054 | 0.0037497 | 0 | 0.0038676 | 0 | 0.003779 | 0 | 3.3692e-06 | -4.4279e-06 | 0.0038541 | 0.0038575 | 0.0038609 | 0.0038642 | 0.0038676 | 0.0038632 | 0.0038587 | 0.0038543 | 0.0038499 | 0.0038455 | 0.003841 | 0.0038366 | 0.0038322 | 0.0038277 | 0.0038233 | 0.0038189 | 0.0038145 | 0.00381 | 0.0038056 | 0.0038012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL013-24612367 | 1917 | 1917 | 0.00019977 | 0 | 0.00021475 | 0 | 0.0002044 | 0 | 4.2817e-07 | -5.1755e-07 | 0.00021304 | 0.00021347 | 0.0002139 | 0.00021433 | 0.00021475 | 0.00021424 | 0.00021372 | 0.0002132 | 0.00021268 | 0.00021217 | 0.00021165 | 0.00021113 | 0.00021061 | 0.0002101 | 0.00020958 | 0.00020906 | 0.00020854 | 0.00020803 | 0.00020751 | 0.00020699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL014-197602155 | 5029 | 5029 | 0.0093516 | 0 | 0.0097084 | 0 | 0.0092729 | 0 | 1.0194e-05 | -2.1775e-05 | 0.0096676 | 0.0096778 | 0.009688 | 0.0096982 | 0.0097084 | 0.0096866 | 0.0096648 | 0.0096431 | 0.0096213 | 0.0095995 | 0.0095777 | 0.009556 | 0.0095342 | 0.0095124 | 0.0094906 | 0.0094689 | 0.0094471 | 0.0094253 | 0.0094035 | 0.0093818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL021-193014245 | 3802 | 1078 | 0.0038141 | 0.0007496 | 0.0041093 | 0.00082518 | 0.0037496 | 0.00073425 | 8.4357e-06 | -1.7986e-05 | 0.0040756 | 0.004084 | 0.0040925 | 0.0041009 | 0.0041093 | 0.0040914 | 0.0040734 | 0.0040554 | 0.0040374 | 0.0040194 | 0.0040014 | 0.0039834 | 0.0039655 | 0.0039475 | 0.0039295 | 0.0039115 | 0.0038935 | 0.0038755 | 0.0038575 | 0.0038396 | 2.1594e-06 | -4.5469e-06 | 0.00081654 | 0.0008187 | 0.00082086 | 0.00082302 | 0.00082518 | 0.00082064 | 0.00081609 | 0.00081154 | 0.00080699 | 0.00080245 | 0.0007979 | 0.00079335 | 0.00078881 | 0.00078426 | 0.00077971 | 0.00077517 | 0.00077062 | 0.00076607 | 0.00076153 | 0.00075698
| DDL021-24613592 | 2724 | 2724 | 0.0036977 | 0 | 0.0038069 | 0 | 0.0037242 | 0 | 3.1222e-06 | -4.1398e-06 | 0.0037945 | 0.0037976 | 0.0038007 | 0.0038038 | 0.0038069 | 0.0038028 | 0.0037987 | 0.0037945 | 0.0037904 | 0.0037863 | 0.0037821 | 0.003778 | 0.0037738 | 0.0037697 | 0.0037656 | 0.0037614 | 0.0037573 | 0.0037531 | 0.003749 | 0.0037449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL022-197602273 | 5025 | 2907 | 0.0039265 | 1.24e-05 | 0.0040631 | 1.4e-05 | 0.0038858 | 1.21e-05 | 3.9026e-06 | -8.8652e-06 | 0.0040474 | 0.0040514 | 0.0040553 | 0.0040592 | 0.0040631 | 0.0040542 | 0.0040453 | 0.0040365 | 0.0040276 | 0.0040187 | 0.0040099 | 0.004001 | 0.0039921 | 0.0039833 | 0.0039744 | 0.0039655 | 0.0039567 | 0.0039478 | 0.0039389 | 0.0039301 | 4.5714e-08 | -9.5e-08 | 1.3817e-05 | 1.3863e-05 | 1.3909e-05 | 1.3954e-05 | 1.4e-05 | 1.3905e-05 | 1.381e-05 | 1.3715e-05 | 1.362e-05 | 1.3525e-05 | 1.343e-05 | 1.3335e-05 | 1.324e-05 | 1.3145e-05 | 1.305e-05 | 1.2955e-05 | 1.286e-05 | 1.2765e-05 | 1.267e-05 | 1.2575e-05
| DDL022-24596878 | 2118 | 2118 | 0.00057379 | 0 | 0.00057139 | 0 | 0.00057107 | 0 | -6.8514e-08 | -1.615e-08 | 0.00057166 | 0.0005716 | 0.00057153 | 0.00057146 | 0.00057139 | 0.00057137 | 0.00057136 | 0.00057134 | 0.00057133 | 0.00057131 | 0.00057129 | 0.00057128 | 0.00057126 | 0.00057124 | 0.00057123 | 0.00057121 | 0.0005712 | 0.00057118 | 0.00057116 | 0.00057115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL023-197602323 | 3294 | 1733 | 0.0046441 | 0 | 0.0049428 | 0 | 0.004575 | 0 | 8.5333e-06 | -1.8392e-05 | 0.0049087 | 0.0049172 | 0.0049257 | 0.0049343 | 0.0049428 | 0.0049244 | 0.004906 | 0.0048876 | 0.0048692 | 0.0048508 | 0.0048325 | 0.0048141 | 0.0047957 | 0.0047773 | 0.0047589 | 0.0047405 | 0.0047221 | 0.0047037 | 0.0046853 | 0.0046669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL023-24612657 | 1561 | 159 | 0.00051058 | 0 | 0.0005573 | 0 | 0.00050085 | 0 | 1.3349e-06 | -2.8227e-06 | 0.00055196 | 0.0005533 | 0.00055463 | 0.00055597 | 0.0005573 | 0.00055448 | 0.00055166 | 0.00054883 | 0.00054601 | 0.00054319 | 0.00054036 | 0.00053754 | 0.00053472 | 0.0005319 | 0.00052907 | 0.00052625 | 0.00052343 | 0.00052061 | 0.00051778 | 0.00051496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL023-72495872 | 1402 | 1402 | 0.00077883 | 0 | 0.00088286 | 0 | 0.00072779 | 0 | 2.9721e-06 | -7.7533e-06 | 0.00087097 | 0.00087394 | 0.00087691 | 0.00087988 | 0.00088286 | 0.0008751 | 0.00086735 | 0.0008596 | 0.00085184 | 0.00084409 | 0.00083634 | 0.00082858 | 0.00082083 | 0.00081308 | 0.00080532 | 0.00079757 | 0.00078982 | 0.00078206 | 0.00077431 | 0.00076656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL024-203514186 | 3738 | 1666 | 0.0092561 | 0.00099878 | 0.0096163 | 0.0010599 | 0.0091748 | 0.00098619 | 1.0292e-05 | -2.2076e-05 | 0.0095752 | 0.0095854 | 0.0095957 | 0.009606 | 0.0096163 | 0.0095942 | 0.0095722 | 0.0095501 | 0.009528 | 0.0095059 | 0.0094839 | 0.0094618 | 0.0094397 | 0.0094176 | 0.0093956 | 0.0093735 | 0.0093514 | 0.0093293 | 0.0093073 | 0.0092852 | 1.7466e-06 | -3.686e-06 | 0.0010529 | 0.0010547 | 0.0010564 | 0.0010582 | 0.0010599 | 0.0010562 | 0.0010525 | 0.0010489 | 0.0010452 | 0.0010415 | 0.0010378 | 0.0010341 | 0.0010304 | 0.0010267 | 0.0010231 | 0.0010194 | 0.0010157 | 0.001012 | 0.0010083 | 0.0010046
| DDL024-73759432 | 2072 | 2072 | 0.0009072 | 0 | 0.00096635 | 0 | 0.00089357 | 0 | 1.6901e-06 | -3.6394e-06 | 0.00095959 | 0.00096128 | 0.00096297 | 0.00096466 | 0.00096635 | 0.00096271 | 0.00095908 | 0.00095544 | 0.0009518 | 0.00094816 | 0.00094452 | 0.00094088 | 0.00093724 | 0.0009336 | 0.00092996 | 0.00092632 | 0.00092268 | 0.00091904 | 0.0009154 | 0.00091176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA001-15422792 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA001-15422805 | 2272 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA001-15422818 | 2270 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA001-24613400 | 1340 | 1340 | 0.038115 | 0 | 0.047489 | 0 | 0.051712 | 0 | 0.00026783 | 0.00021115 | 0.046418 | 0.046686 | 0.046953 | 0.047221 | 0.047489 | 0.0477 | 0.047911 | 0.048122 | 0.048334 | 0.048545 | 0.048756 | 0.048967 | 0.049178 | 0.049389 | 0.049601 | 0.049812 | 0.050023 | 0.050234 | 0.050445 | 0.050656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA001-24613414 | 818 | 818 | 0.0024104 | 0 | 0.0028054 | 0 | 0.002914 | 0 | 1.1286e-05 | 5.4288e-06 | 0.0027603 | 0.0027716 | 0.0027828 | 0.0027941 | 0.0028054 | 0.0028108 | 0.0028163 | 0.0028217 | 0.0028271 | 0.0028326 | 0.002838 | 0.0028434 | 0.0028488 | 0.0028543 | 0.0028597 | 0.0028651 | 0.0028706 | 0.002876 | 0.0028814 | 0.0028868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA003-15422755 | 2496 | 2496 | 0.040499 | 0 | 0.048887 | 0 | 0.053595 | 0 | 0.00023965 | 0.00023539 | 0.047929 | 0.048168 | 0.048408 | 0.048648 | 0.048887 | 0.049123 | 0.049358 | 0.049593 | 0.049829 | 0.050064 | 0.050299 | 0.050535 | 0.05077 | 0.051006 | 0.051241 | 0.051476 | 0.051712 | 0.051947 | 0.052183 | 0.052418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA005-15422679 | 886 | 288 | 0.0043941 | 0.00059871 | 0.0048566 | 0.00069232 | 0.0048638 | 0.00069684 | 1.3215e-05 | 3.587e-07 | 0.0048037 | 0.004817 | 0.0048302 | 0.0048434 | 0.0048566 | 0.004857 | 0.0048573 | 0.0048577 | 0.004858 | 0.0048584 | 0.0048587 | 0.0048591 | 0.0048595 | 0.0048598 | 0.0048602 | 0.0048605 | 0.0048609 | 0.0048613 | 0.0048616 | 0.004862 | 2.6745e-06 | 2.26e-07 | 0.00068162 | 0.0006843 | 0.00068697 | 0.00068965 | 0.00069232 | 0.00069255 | 0.00069277 | 0.000693 | 0.00069322 | 0.00069345 | 0.00069368 | 0.0006939 | 0.00069413 | 0.00069435 | 0.00069458 | 0.00069481 | 0.00069503 | 0.00069526 | 0.00069548 | 0.00069571
| ECA005-24596794 | 161 | 161 | 2.37e-05 | 0 | 3.16e-05 | 0 | 3.93e-05 | 0 | 2.2571e-07 | 3.85e-07 | 3.0697e-05 | 3.0923e-05 | 3.1149e-05 | 3.1374e-05 | 3.16e-05 | 3.1985e-05 | 3.237e-05 | 3.2755e-05 | 3.314e-05 | 3.3525e-05 | 3.391e-05 | 3.4295e-05 | 3.468e-05 | 3.5065e-05 | 3.545e-05 | 3.5835e-05 | 3.622e-05 | 3.6605e-05 | 3.699e-05 | 3.7375e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA005-88419875 | 598 | 437 | 0.0063014 | 2.14e-05 | 0.0079259 | 2.79e-05 | 0.0089436 | 3.32e-05 | 4.6414e-05 | 5.0885e-05 | 0.0077402 | 0.0077866 | 0.0078331 | 0.0078795 | 0.0079259 | 0.0079768 | 0.0080276 | 0.0080785 | 0.0081294 | 0.0081803 | 0.0082312 | 0.0082821 | 0.008333 | 0.0083838 | 0.0084347 | 0.0084856 | 0.0085365 | 0.0085874 | 0.0086383 | 0.0086891 | 1.8571e-07 | 2.65e-07 | 2.7157e-05 | 2.7343e-05 | 2.7529e-05 | 2.7714e-05 | 2.79e-05 | 2.8165e-05 | 2.843e-05 | 2.8695e-05 | 2.896e-05 | 2.9225e-05 | 2.949e-05 | 2.9755e-05 | 3.002e-05 | 3.0285e-05 | 3.055e-05 | 3.0815e-05 | 3.108e-05 | 3.1345e-05 | 3.161e-05 | 3.1875e-05
| ECA007-111138070 | 731 | 585 | 0.011596 | 0.0023757 | 0.014345 | 0.0031404 | 0.015015 | 0.0033358 | 7.8538e-05 | 3.3492e-05 | 0.014031 | 0.014109 | 0.014188 | 0.014266 | 0.014345 | 0.014378 | 0.014412 | 0.014445 | 0.014479 | 0.014512 | 0.014546 | 0.014579 | 0.014613 | 0.014646 | 0.01468 | 0.014713 | 0.014747 | 0.01478 | 0.014814 | 0.014847 | 2.1848e-05 | 9.7736e-06 | 0.003053 | 0.0030748 | 0.0030967 | 0.0031185 | 0.0031404 | 0.0031501 | 0.0031599 | 0.0031697 | 0.0031795 | 0.0031892 | 0.003199 | 0.0032088 | 0.0032186 | 0.0032283 | 0.0032381 | 0.0032479 | 0.0032576 | 0.0032674 | 0.0032772 | 0.003287
| ECA007-139030671 | 13 | 13 | 0.00047628 | 0 | 0.00063355 | 0 | 0.00069699 | 0 | 4.4933e-06 | 3.1722e-06 | 0.00061557 | 0.00062007 | 0.00062456 | 0.00062905 | 0.00063355 | 0.00063672 | 0.00063989 | 0.00064306 | 0.00064624 | 0.00064941 | 0.00065258 | 0.00065575 | 0.00065892 | 0.0006621 | 0.00066527 | 0.00066844 | 0.00067161 | 0.00067479 | 0.00067796 | 0.00068113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA007-139030700 | 49 | 49 | 0.001939 | 0 | 0.0025784 | 0 | 0.0027783 | 0 | 1.8267e-05 | 9.9996e-06 | 0.0025053 | 0.0025236 | 0.0025418 | 0.0025601 | 0.0025784 | 0.0025884 | 0.0025984 | 0.0026084 | 0.0026184 | 0.0026284 | 0.0026384 | 0.0026484 | 0.0026584 | 0.0026684 | 0.0026784 | 0.0026884 | 0.0026984 | 0.0027084 | 0.0027184 | 0.0027284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA007-15422655 | 1173 | 386 | 0.0083886 | 0.00027829 | 0.010113 | 0.00035397 | 0.01175 | 0.00043033 | 4.9263e-05 | 8.1839e-05 | 0.0099158 | 0.009965 | 0.010014 | 0.010064 | 0.010113 | 0.010195 | 0.010277 | 0.010358 | 0.01044 | 0.010522 | 0.010604 | 0.010686 | 0.010768 | 0.010849 | 0.010931 | 0.011013 | 0.011095 | 0.011177 | 0.011259 | 0.01134 | 2.1625e-06 | 3.8177e-06 | 0.00034532 | 0.00034749 | 0.00034965 | 0.00035181 | 0.00035397 | 0.00035779 | 0.00036161 | 0.00036543 | 0.00036924 | 0.00037306 | 0.00037688 | 0.0003807 | 0.00038452 | 0.00038833 | 0.00039215 | 0.00039597 | 0.00039979 | 0.0004036 | 0.00040742 | 0.00041124
| ECA007-155422337 | 36 | 36 | 0.0016399 | 0 | 0.0020839 | 0 | 0.00239 | 0 | 1.2686e-05 | 1.5305e-05 | 0.0020332 | 0.0020459 | 0.0020585 | 0.0020712 | 0.0020839 | 0.0020992 | 0.0021145 | 0.0021298 | 0.0021451 | 0.0021604 | 0.0021757 | 0.0021911 | 0.0022064 | 0.0022217 | 0.002237 | 0.0022523 | 0.0022676 | 0.0022829 | 0.0022982 | 0.0023135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA007-155422427 | 7 | 7 | 0.0012908 | 0 | 0.0016436 | 0 | 0.0018918 | 0 | 1.008e-05 | 1.2411e-05 | 0.0016033 | 0.0016133 | 0.0016234 | 0.0016335 | 0.0016436 | 0.001656 | 0.0016684 | 0.0016808 | 0.0016932 | 0.0017056 | 0.001718 | 0.0017304 | 0.0017429 | 0.0017553 | 0.0017677 | 0.0017801 | 0.0017925 | 0.0018049 | 0.0018173 | 0.0018297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA007-155422573 | 24 | 24 | 0.0022219 | 0 | 0.0030281 | 0 | 0.0034302 | 0 | 2.3033e-05 | 2.0108e-05 | 0.002936 | 0.002959 | 0.002982 | 0.0030051 | 0.0030281 | 0.0030482 | 0.0030683 | 0.0030884 | 0.0031085 | 0.0031286 | 0.0031487 | 0.0031688 | 0.003189 | 0.0032091 | 0.0032292 | 0.0032493 | 0.0032694 | 0.0032895 | 0.0033096 | 0.0033297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA007-175612541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA007-24611056 | 787 | 56 | 0.0044489 | 0.0014529 | 0.0053621 | 0.0017957 | 0.0061152 | 0.0021342 | 2.6093e-05 | 3.7652e-05 | 0.0052577 | 0.0052838 | 0.0053099 | 0.005336 | 0.0053621 | 0.0053998 | 0.0054374 | 0.0054751 | 0.0055127 | 0.0055504 | 0.005588 | 0.0056257 | 0.0056633 | 0.005701 | 0.0057386 | 0.0057763 | 0.0058139 | 0.0058516 | 0.0058892 | 0.0059269 | 9.7962e-06 | 1.6925e-05 | 0.0017566 | 0.0017663 | 0.0017761 | 0.0017859 | 0.0017957 | 0.0018127 | 0.0018296 | 0.0018465 | 0.0018634 | 0.0018804 | 0.0018973 | 0.0019142 | 0.0019311 | 0.0019481 | 0.001965 | 0.0019819 | 0.0019988 | 0.0020158 | 0.0020327 | 0.0020496
| ECA010-15423016 | 2260 | 2260 | 0.035941 | 0 | 0.046271 | 0 | 0.05128 | 0 | 0.00029512 | 0.00025047 | 0.04509 | 0.045385 | 0.04568 | 0.045976 | 0.046271 | 0.046521 | 0.046772 | 0.047022 | 0.047273 | 0.047523 | 0.047774 | 0.048024 | 0.048274 | 0.048525 | 0.048775 | 0.049026 | 0.049276 | 0.049527 | 0.049777 | 0.050028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA012-15423053 | 2000 | 1199 | 0.0086478 | 0.0031495 | 0.011109 | 0.0040768 | 0.012499 | 0.0046108 | 7.032e-05 | 6.9483e-05 | 0.010828 | 0.010898 | 0.010968 | 0.011039 | 0.011109 | 0.011178 | 0.011248 | 0.011317 | 0.011387 | 0.011456 | 0.011526 | 0.011595 | 0.011665 | 0.011734 | 0.011804 | 0.011873 | 0.011943 | 0.012012 | 0.012082 | 0.012151 | 2.6492e-05 | 2.6701e-05 | 0.0039708 | 0.0039973 | 0.0040238 | 0.0040503 | 0.0040768 | 0.0041035 | 0.0041302 | 0.0041569 | 0.0041836 | 0.0042103 | 0.004237 | 0.0042637 | 0.0042904 | 0.0043171 | 0.0043438 | 0.0043705 | 0.0043972 | 0.0044239 | 0.0044506 | 0.0044773
| ECA012-160768254 | 20 | 20 | 0.0015376 | 0 | 0.0019898 | 0 | 0.0022536 | 0 | 1.292e-05 | 1.319e-05 | 0.0019381 | 0.001951 | 0.0019639 | 0.0019769 | 0.0019898 | 0.002003 | 0.0020162 | 0.0020293 | 0.0020425 | 0.0020557 | 0.0020689 | 0.0020821 | 0.0020953 | 0.0021085 | 0.0021217 | 0.0021349 | 0.0021481 | 0.0021612 | 0.0021744 | 0.0021876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA012-164487948 | 6 | 6 | 0.00030019 | 0 | 0.00037885 | 0 | 0.00044259 | 0 | 2.2474e-06 | 3.1871e-06 | 0.00036986 | 0.00037211 | 0.00037436 | 0.0003766 | 0.00037885 | 0.00038204 | 0.00038523 | 0.00038841 | 0.0003916 | 0.00039479 | 0.00039797 | 0.00040116 | 0.00040435 | 0.00040754 | 0.00041072 | 0.00041391 | 0.0004171 | 0.00042028 | 0.00042347 | 0.00042666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA012-202230762 | 801 | 775 | 0.0055724 | 0.00042452 | 0.0062514 | 0.00046729 | 0.0062809 | 0.00046947 | 1.94e-05 | 1.474e-06 | 0.0061738 | 0.0061932 | 0.0062126 | 0.006232 | 0.0062514 | 0.0062529 | 0.0062544 | 0.0062559 | 0.0062573 | 0.0062588 | 0.0062603 | 0.0062618 | 0.0062632 | 0.0062647 | 0.0062662 | 0.0062677 | 0.0062691 | 0.0062706 | 0.0062721 | 0.0062735 | 1.222e-06 | 1.09e-07 | 0.0004624 | 0.00046362 | 0.00046484 | 0.00046606 | 0.00046728 | 0.00046739 | 0.0004675 | 0.00046761 | 0.00046772 | 0.00046783 | 0.00046794 | 0.00046805 | 0.00046816 | 0.00046827 | 0.00046837 | 0.00046848 | 0.00046859 | 0.0004687 | 0.00046881 | 0.00046892
| EHK021-15417698 | 367 | 367 | 0.0053635 | 0 | 0.0065241 | 0 | 0.0067444 | 0 | 3.3159e-05 | 1.1016e-05 | 0.0063914 | 0.0064246 | 0.0064578 | 0.0064909 | 0.0065241 | 0.0065351 | 0.0065461 | 0.0065571 | 0.0065681 | 0.0065792 | 0.0065902 | 0.0066012 | 0.0066122 | 0.0066232 | 0.0066342 | 0.0066453 | 0.0066563 | 0.0066673 | 0.0066783 | 0.0066893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK022-15417761 | 1370 | 1370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK023-15417824 | 4251 | 4251 | 0.084297 | 0 | 0.1058 | 0 | 0.10994 | 0 | 0.00061432 | 0.00020684 | 0.10334 | 0.10396 | 0.10457 | 0.10518 | 0.1058 | 0.10601 | 0.10621 | 0.10642 | 0.10663 | 0.10683 | 0.10704 | 0.10725 | 0.10745 | 0.10766 | 0.10787 | 0.10807 | 0.10828 | 0.10849 | 0.10869 | 0.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-109924737 | 16 | 16 | 0.00019847 | 0 | 0.00027328 | 0 | 0.00030204 | 0 | 2.1374e-06 | 1.438e-06 | 0.00026473 | 0.00026687 | 0.00026901 | 0.00027114 | 0.00027328 | 0.00027472 | 0.00027616 | 0.0002776 | 0.00027903 | 0.00028047 | 0.00028191 | 0.00028335 | 0.00028479 | 0.00028622 | 0.00028766 | 0.0002891 | 0.00029054 | 0.00029198 | 0.00029341 | 0.00029485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-119636484 | 296 | 255 | 0.011813 | 0 | 0.012833 | 0 | 0.012639 | 0 | 2.9161e-05 | -9.741e-06 | 0.012717 | 0.012746 | 0.012775 | 0.012804 | 0.012833 | 0.012824 | 0.012814 | 0.012804 | 0.012794 | 0.012785 | 0.012775 | 0.012765 | 0.012755 | 0.012746 | 0.012736 | 0.012726 | 0.012716 | 0.012707 | 0.012697 | 0.012687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-130742429 | 30 | 30 | 0.011035 | 0 | 0.014511 | 0 | 0.015912 | 0 | 9.9315e-05 | 7.0021e-05 | 0.014114 | 0.014214 | 0.014313 | 0.014412 | 0.014511 | 0.014582 | 0.014652 | 0.014722 | 0.014792 | 0.014862 | 0.014932 | 0.015002 | 0.015072 | 0.015142 | 0.015212 | 0.015282 | 0.015352 | 0.015422 | 0.015492 | 0.015562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-15417874 | 2181 | 708 | 0.02275 | 0.012275 | 0.029122 | 0.016469 | 0.03005 | 0.01708 | 0.00018208 | 4.6378e-05 | 0.028394 | 0.028576 | 0.028758 | 0.02894 | 0.029122 | 0.029169 | 0.029215 | 0.029261 | 0.029308 | 0.029354 | 0.029401 | 0.029447 | 0.029493 | 0.02954 | 0.029586 | 0.029632 | 0.029679 | 0.029725 | 0.029772 | 0.029818 | 0.00011985 | 3.0543e-05 | 0.01599 | 0.01611 | 0.01623 | 0.01635 | 0.016469 | 0.0165 | 0.01653 | 0.016561 | 0.016592 | 0.016622 | 0.016653 | 0.016683 | 0.016714 | 0.016744 | 0.016775 | 0.016805 | 0.016836 | 0.016866 | 0.016897 | 0.016928
| EHK024-155053117 | 25 | 25 | 0.0011821 | 0 | 0.0015451 | 0 | 0.0017081 | 0 | 1.0373e-05 | 8.1497e-06 | 0.0015037 | 0.001514 | 0.0015244 | 0.0015348 | 0.0015451 | 0.0015533 | 0.0015614 | 0.0015696 | 0.0015777 | 0.0015859 | 0.001594 | 0.0016022 | 0.0016103 | 0.0016185 | 0.0016266 | 0.0016348 | 0.0016429 | 0.0016511 | 0.0016592 | 0.0016674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-155155262 | 9 | 9 | 0.00035156 | 0 | 0.00049027 | 0 | 0.0005163 | 0 | 3.9632e-06 | 1.3018e-06 | 0.00047442 | 0.00047838 | 0.00048234 | 0.00048631 | 0.00049027 | 0.00049157 | 0.00049287 | 0.00049417 | 0.00049548 | 0.00049678 | 0.00049808 | 0.00049938 | 0.00050068 | 0.00050199 | 0.00050329 | 0.00050459 | 0.00050589 | 0.00050719 | 0.00050849 | 0.0005098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-155423299 | 23 | 23 | 0.0016081 | 0 | 0.0021073 | 0 | 0.0023424 | 0 | 1.4262e-05 | 1.1755e-05 | 0.0020503 | 0.0020645 | 0.0020788 | 0.002093 | 0.0021073 | 0.0021191 | 0.0021308 | 0.0021426 | 0.0021543 | 0.0021661 | 0.0021778 | 0.0021896 | 0.0022013 | 0.0022131 | 0.0022249 | 0.0022366 | 0.0022484 | 0.0022601 | 0.0022719 | 0.0022836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-155616704 | 13 | 13 | 0.00039285 | 0 | 0.0004312 | 0 | 0.0004369 | 0 | 1.0958e-06 | 2.848e-07 | 0.00042682 | 0.00042791 | 0.00042901 | 0.0004301 | 0.0004312 | 0.00043148 | 0.00043177 | 0.00043205 | 0.00043234 | 0.00043262 | 0.00043291 | 0.00043319 | 0.00043348 | 0.00043376 | 0.00043405 | 0.00043433 | 0.00043462 | 0.0004349 | 0.00043519 | 0.00043547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-155621039 | 45 | 45 | 0.0020849 | 0 | 0.0027072 | 0 | 0.0028612 | 0 | 1.7779e-05 | 7.6989e-06 | 0.0026361 | 0.0026538 | 0.0026716 | 0.0026894 | 0.0027072 | 0.0027149 | 0.0027226 | 0.0027303 | 0.002738 | 0.0027457 | 0.0027534 | 0.0027611 | 0.0027688 | 0.0027765 | 0.0027842 | 0.0027919 | 0.0027996 | 0.0028073 | 0.002815 | 0.0028227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-161138740 | 705 | 372 | 0.013851 | 0.0033291 | 0.016371 | 0.0041946 | 0.01732 | 0.0045772 | 7.1984e-05 | 4.7446e-05 | 0.016083 | 0.016155 | 0.016227 | 0.016299 | 0.016371 | 0.016418 | 0.016466 | 0.016513 | 0.016561 | 0.016608 | 0.016656 | 0.016703 | 0.01675 | 0.016798 | 0.016845 | 0.016893 | 0.01694 | 0.016988 | 0.017035 | 0.017083 | 2.473e-05 | 1.9133e-05 | 0.0040957 | 0.0041204 | 0.0041451 | 0.0041699 | 0.0041946 | 0.0042137 | 0.0042329 | 0.004252 | 0.0042711 | 0.0042903 | 0.0043094 | 0.0043285 | 0.0043476 | 0.0043668 | 0.0043859 | 0.004405 | 0.0044242 | 0.0044433 | 0.0044624 | 0.0044816
| EHK024-162768321 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-162802004 | 6 | 6 | 1.83e-05 | 0 | 2.66e-05 | 0 | 2.97e-05 | 0 | 2.3714e-07 | 1.55e-07 | 2.5651e-05 | 2.5889e-05 | 2.6126e-05 | 2.6363e-05 | 2.66e-05 | 2.6755e-05 | 2.691e-05 | 2.7065e-05 | 2.722e-05 | 2.7375e-05 | 2.753e-05 | 2.7685e-05 | 2.784e-05 | 2.7995e-05 | 2.815e-05 | 2.8305e-05 | 2.846e-05 | 2.8615e-05 | 2.877e-05 | 2.8925e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-162802163 | 8 | 8 | 1.97e-05 | 0 | 2.77e-05 | 0 | 3.05e-05 | 0 | 2.2857e-07 | 1.4e-07 | 2.6786e-05 | 2.7014e-05 | 2.7243e-05 | 2.7471e-05 | 2.77e-05 | 2.784e-05 | 2.798e-05 | 2.812e-05 | 2.826e-05 | 2.84e-05 | 2.854e-05 | 2.868e-05 | 2.882e-05 | 2.896e-05 | 2.91e-05 | 2.924e-05 | 2.938e-05 | 2.952e-05 | 2.966e-05 | 2.98e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-171210602 | 6 | 6 | 7.5e-06 | 0 | 1.02e-05 | 0 | 1.17e-05 | 0 | 7.7143e-08 | 7.5e-08 | 9.8914e-06 | 9.9686e-06 | 1.0046e-05 | 1.0123e-05 | 1.02e-05 | 1.0275e-05 | 1.035e-05 | 1.0425e-05 | 1.05e-05 | 1.0575e-05 | 1.065e-05 | 1.0725e-05 | 1.08e-05 | 1.0875e-05 | 1.095e-05 | 1.1025e-05 | 1.11e-05 | 1.1175e-05 | 1.125e-05 | 1.1325e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-63048145 | 255 | 226 | 0.0050729 | 0.00050123 | 0.0065473 | 0.00067772 | 0.0071609 | 0.00075873 | 4.2127e-05 | 3.0678e-05 | 0.0063788 | 0.0064209 | 0.0064631 | 0.0065052 | 0.0065473 | 0.006578 | 0.0066087 | 0.0066394 | 0.00667 | 0.0067007 | 0.0067314 | 0.0067621 | 0.0067927 | 0.0068234 | 0.0068541 | 0.0068848 | 0.0069155 | 0.0069461 | 0.0069768 | 0.0070075 | 5.0427e-06 | 4.0501e-06 | 0.00065755 | 0.0006626 | 0.00066764 | 0.00067268 | 0.00067772 | 0.00068177 | 0.00068582 | 0.00068987 | 0.00069392 | 0.00069797 | 0.00070202 | 0.00070607 | 0.00071012 | 0.00071417 | 0.00071823 | 0.00072228 | 0.00072633 | 0.00073038 | 0.00073443 | 0.00073848
| EHK024-63048164 | 697 | 327 | 0.0091962 | 0.0033787 | 0.011557 | 0.0042889 | 0.012189 | 0.0045318 | 6.7458e-05 | 3.1573e-05 | 0.011287 | 0.011355 | 0.011422 | 0.01149 | 0.011557 | 0.011589 | 0.01162 | 0.011652 | 0.011683 | 0.011715 | 0.011747 | 0.011778 | 0.01181 | 0.011841 | 0.011873 | 0.011905 | 0.011936 | 0.011968 | 0.011999 | 0.012031 | 2.6006e-05 | 1.2143e-05 | 0.0041849 | 0.0042109 | 0.0042369 | 0.0042629 | 0.0042889 | 0.0043011 | 0.0043132 | 0.0043254 | 0.0043375 | 0.0043497 | 0.0043618 | 0.0043739 | 0.0043861 | 0.0043982 | 0.0044104 | 0.0044225 | 0.0044347 | 0.0044468 | 0.0044589 | 0.0044711
| EHK024-73766693 | 41 | 41 | 0.0062992 | 0 | 0.0082752 | 0 | 0.0086434 | 0 | 5.6456e-05 | 1.841e-05 | 0.0080494 | 0.0081059 | 0.0081623 | 0.0082188 | 0.0082752 | 0.0082936 | 0.008312 | 0.0083305 | 0.0083489 | 0.0083673 | 0.0083857 | 0.0084041 | 0.0084225 | 0.0084409 | 0.0084593 | 0.0084777 | 0.0084961 | 0.0085146 | 0.008533 | 0.0085514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-73766943 | 24 | 24 | 0.0023104 | 0 | 0.0028493 | 0 | 0.003094 | 0 | 1.5399e-05 | 1.2236e-05 | 0.0027877 | 0.0028031 | 0.0028185 | 0.0028339 | 0.0028493 | 0.0028615 | 0.0028738 | 0.002886 | 0.0028983 | 0.0029105 | 0.0029227 | 0.002935 | 0.0029472 | 0.0029594 | 0.0029717 | 0.0029839 | 0.0029961 | 0.0030084 | 0.0030206 | 0.0030329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK031-134953753 | 38 | 38 | 0.011414 | 0 | 0.014527 | 0 | 0.015116 | 0 | 8.8947e-05 | 2.9459e-05 | 0.014171 | 0.01426 | 0.014349 | 0.014438 | 0.014527 | 0.014556 | 0.014586 | 0.014615 | 0.014645 | 0.014674 | 0.014704 | 0.014733 | 0.014763 | 0.014792 | 0.014821 | 0.014851 | 0.01488 | 0.01491 | 0.014939 | 0.014969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK031-134953882 | 40 | 40 | 0.004122 | 0 | 0.0054475 | 0 | 0.0055972 | 0 | 3.7871e-05 | 7.4812e-06 | 0.005296 | 0.0053339 | 0.0053718 | 0.0054097 | 0.0054475 | 0.005455 | 0.0054625 | 0.00547 | 0.0054775 | 0.0054849 | 0.0054924 | 0.0054999 | 0.0055074 | 0.0055149 | 0.0055223 | 0.0055298 | 0.0055373 | 0.0055448 | 0.0055523 | 0.0055597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK031-134954057 | 27 | 27 | 0.0024394 | 0 | 0.0031945 | 0 | 0.0033502 | 0 | 2.1575e-05 | 7.783e-06 | 0.0031082 | 0.0031298 | 0.0031514 | 0.0031729 | 0.0031945 | 0.0032023 | 0.0032101 | 0.0032179 | 0.0032256 | 0.0032334 | 0.0032412 | 0.003249 | 0.0032568 | 0.0032646 | 0.0032723 | 0.0032801 | 0.0032879 | 0.0032957 | 0.0033035 | 0.0033113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK031-15417885 | 2347 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK031-15417924 | 2345 | 1815 | 0.052399 | 0.013279 | 0.066888 | 0.017469 | 0.069706 | 0.018294 | 0.00041397 | 0.00014092 | 0.065232 | 0.065646 | 0.06606 | 0.066474 | 0.066888 | 0.067029 | 0.067169 | 0.06731 | 0.067451 | 0.067592 | 0.067733 | 0.067874 | 0.068015 | 0.068156 | 0.068297 | 0.068438 | 0.068579 | 0.06872 | 0.068861 | 0.069001 | 0.00011971 | 4.1219e-05 | 0.01699 | 0.01711 | 0.01723 | 0.017349 | 0.017469 | 0.01751 | 0.017552 | 0.017593 | 0.017634 | 0.017675 | 0.017716 | 0.017758 | 0.017799 | 0.01784 | 0.017881 | 0.017923 | 0.017964 | 0.018005 | 0.018046 | 0.018087
| EHK031-156804503 | 219 | 219 | 0.010182 | 0 | 0.012442 | 0 | 0.012485 | 0 | 6.4587e-05 | 2.1581e-06 | 0.012184 | 0.012248 | 0.012313 | 0.012378 | 0.012442 | 0.012444 | 0.012447 | 0.012449 | 0.012451 | 0.012453 | 0.012455 | 0.012457 | 0.012459 | 0.012462 | 0.012464 | 0.012466 | 0.012468 | 0.01247 | 0.012472 | 0.012475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK031-156804528 | 233 | 206 | 0.008578 | 0.00091847 | 0.010914 | 0.0012269 | 0.011328 | 0.0012825 | 6.6756e-05 | 2.07e-05 | 0.010647 | 0.010714 | 0.010781 | 0.010848 | 0.010914 | 0.010935 | 0.010956 | 0.010977 | 0.010997 | 0.011018 | 0.011039 | 0.011059 | 0.01108 | 0.011101 | 0.011121 | 0.011142 | 0.011163 | 0.011184 | 0.011204 | 0.011225 | 8.8128e-06 | 2.7802e-06 | 0.0011917 | 0.0012005 | 0.0012093 | 0.0012181 | 0.0012269 | 0.0012297 | 0.0012325 | 0.0012353 | 0.001238 | 0.0012408 | 0.0012436 | 0.0012464 | 0.0012492 | 0.0012519 | 0.0012547 | 0.0012575 | 0.0012603 | 0.0012631 | 0.0012658 | 0.0012686
| EHK032-15417935 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK032-15417948 | 142 | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK033-15418024 | 5478 | 5478 | 0.11562 | 0 | 0.14249 | 0 | 0.14561 | 0 | 0.00076761 | 0.0001561 | 0.13942 | 0.14018 | 0.14095 | 0.14172 | 0.14249 | 0.14264 | 0.1428 | 0.14295 | 0.14311 | 0.14327 | 0.14342 | 0.14358 | 0.14373 | 0.14389 | 0.14405 | 0.1442 | 0.14436 | 0.14451 | 0.14467 | 0.14483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK034-15431419 | 888 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FNS011-15405543 | 2052 | 1812 | 0.019157 | 0.0038509 | 0.023856 | 0.0050581 | 0.025955 | 0.0056123 | 0.00013428 | 0.00010492 | 0.023319 | 0.023453 | 0.023588 | 0.023722 | 0.023856 | 0.023961 | 0.024066 | 0.024171 | 0.024276 | 0.024381 | 0.024486 | 0.024591 | 0.024696 | 0.024801 | 0.024906 | 0.02501 | 0.025115 | 0.02522 | 0.025325 | 0.02543 | 3.449e-05 | 2.7712e-05 | 0.0049201 | 0.0049546 | 0.0049891 | 0.0050236 | 0.0050581 | 0.0050858 | 0.0051135 | 0.0051412 | 0.0051689 | 0.0051966 | 0.0052243 | 0.005252 | 0.0052798 | 0.0053075 | 0.0053352 | 0.0053629 | 0.0053906 | 0.0054183 | 0.005446 | 0.0054737
| FNS011-24604152 | 240 | 240 | 0.0046994 | 0 | 0.0061295 | 0 | 0.0067725 | 0 | 4.0859e-05 | 3.2151e-05 | 0.0059661 | 0.0060069 | 0.0060478 | 0.0060886 | 0.0061295 | 0.0061617 | 0.0061938 | 0.006226 | 0.0062581 | 0.0062903 | 0.0063224 | 0.0063546 | 0.0063867 | 0.0064189 | 0.006451 | 0.0064832 | 0.0065153 | 0.0065475 | 0.0065796 | 0.0066118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FNS012-15405393 | 3051 | 1462 | 0.013578 | 0.0024322 | 0.0188 | 0.0034127 | 0.02019 | 0.0036845 | 0.00014921 | 6.9461e-05 | 0.018204 | 0.018353 | 0.018502 | 0.018651 | 0.0188 | 0.01887 | 0.018939 | 0.019009 | 0.019078 | 0.019148 | 0.019217 | 0.019287 | 0.019356 | 0.019426 | 0.019495 | 0.019564 | 0.019634 | 0.019703 | 0.019773 | 0.019842 | 2.8015e-05 | 1.359e-05 | 0.0033007 | 0.0033287 | 0.0033567 | 0.0033847 | 0.0034127 | 0.0034263 | 0.0034399 | 0.0034535 | 0.0034671 | 0.0034807 | 0.0034943 | 0.0035078 | 0.0035214 | 0.003535 | 0.0035486 | 0.0035622 | 0.0035758 | 0.0035894 | 0.003603 | 0.0036166
| FNS012-76065032 | 1589 | 1589 | 0.0027434 | 0 | 0.003673 | 0 | 0.0041265 | 0 | 2.6558e-05 | 2.2676e-05 | 0.0035668 | 0.0035933 | 0.0036199 | 0.0036464 | 0.003673 | 0.0036957 | 0.0037183 | 0.003741 | 0.0037637 | 0.0037864 | 0.003809 | 0.0038317 | 0.0038544 | 0.0038771 | 0.0038997 | 0.0039224 | 0.0039451 | 0.0039678 | 0.0039905 | 0.0040131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FNS013-15405406 | 3989 | 3892 | 0.0090721 | 0.0044788 | 0.012562 | 0.0063923 | 0.012037 | 0.0061128 | 9.9716e-05 | -2.6275e-05 | 0.012163 | 0.012263 | 0.012363 | 0.012462 | 0.012562 | 0.012536 | 0.01251 | 0.012483 | 0.012457 | 0.012431 | 0.012405 | 0.012378 | 0.012352 | 0.012326 | 0.012299 | 0.012273 | 0.012247 | 0.012221 | 0.012194 | 0.012168 | 5.4673e-05 | -1.3976e-05 | 0.0061736 | 0.0062283 | 0.006283 | 0.0063377 | 0.0063923 | 0.0063784 | 0.0063644 | 0.0063504 | 0.0063364 | 0.0063225 | 0.0063085 | 0.0062945 | 0.0062805 | 0.0062665 | 0.0062526 | 0.0062386 | 0.0062246 | 0.0062106 | 0.0061967 | 0.0061827
| FNS013-73561266 | 97 | 97 | 0.012904 | 0 | 0.017126 | 0 | 0.018379 | 0 | 0.00012063 | 6.2649e-05 | 0.016644 | 0.016764 | 0.016885 | 0.017006 | 0.017126 | 0.017189 | 0.017251 | 0.017314 | 0.017377 | 0.017439 | 0.017502 | 0.017565 | 0.017627 | 0.01769 | 0.017753 | 0.017815 | 0.017878 | 0.017941 | 0.018003 | 0.018066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FNS021-15405600 | 1994 | 1340 | 0.023543 | 0.0015585 | 0.027062 | 0.002177 | 0.027774 | 0.002346 | 0.00010052 | 3.5611e-05 | 0.026659 | 0.02676 | 0.026861 | 0.026961 | 0.027062 | 0.027097 | 0.027133 | 0.027168 | 0.027204 | 0.02724 | 0.027275 | 0.027311 | 0.027346 | 0.027382 | 0.027418 | 0.027453 | 0.027489 | 0.027525 | 0.02756 | 0.027596 | 1.7674e-05 | 8.4477e-06 | 0.0021063 | 0.002124 | 0.0021417 | 0.0021594 | 0.002177 | 0.0021855 | 0.0021939 | 0.0022024 | 0.0022108 | 0.0022193 | 0.0022277 | 0.0022362 | 0.0022446 | 0.0022531 | 0.0022615 | 0.00227 | 0.0022784 | 0.0022869 | 0.0022953 | 0.0023037
| FNS021-24604138 | 654 | 654 | 0.0032919 | 0 | 0.0044455 | 0 | 0.0050132 | 0 | 3.2959e-05 | 2.8387e-05 | 0.0043136 | 0.0043466 | 0.0043795 | 0.0044125 | 0.0044455 | 0.0044738 | 0.0045022 | 0.0045306 | 0.004559 | 0.0045874 | 0.0046158 | 0.0046442 | 0.0046726 | 0.0047009 | 0.0047293 | 0.0047577 | 0.0047861 | 0.0048145 | 0.0048429 | 0.0048713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FNS022-15405419 | 973 | 398 | 0.042357 | 0.009131 | 0.05404 | 0.013141 | 0.053372 | 0.013054 | 0.00033378 | -3.339e-05 | 0.052705 | 0.053038 | 0.053372 | 0.053706 | 0.05404 | 0.054006 | 0.053973 | 0.053939 | 0.053906 | 0.053873 | 0.053839 | 0.053806 | 0.053773 | 0.053739 | 0.053706 | 0.053672 | 0.053639 | 0.053606 | 0.053572 | 0.053539 | 0.00011458 | -4.3757e-06 | 0.012683 | 0.012797 | 0.012912 | 0.013027 | 0.013141 | 0.013137 | 0.013132 | 0.013128 | 0.013124 | 0.013119 | 0.013115 | 0.013111 | 0.013106 | 0.013102 | 0.013097 | 0.013093 | 0.013089 | 0.013084 | 0.01308 | 0.013075
| FNS022-24604096 | 575 | 575 | 0.017537 | 0 | 0.024403 | 0 | 0.025433 | 0 | 0.00019617 | 5.1464e-05 | 0.023619 | 0.023815 | 0.024011 | 0.024207 | 0.024403 | 0.024455 | 0.024506 | 0.024558 | 0.024609 | 0.024661 | 0.024712 | 0.024764 | 0.024815 | 0.024866 | 0.024918 | 0.024969 | 0.025021 | 0.025072 | 0.025124 | 0.025175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FNS032-15405445 | 224 | 89 | 0.014219 | 1.68e-05 | 0.018382 | 2.39e-05 | 0.018744 | 2.59e-05 | 0.00011896 | 1.8082e-05 | 0.017906 | 0.018025 | 0.018144 | 0.018263 | 0.018382 | 0.0184 | 0.018418 | 0.018436 | 0.018454 | 0.018473 | 0.018491 | 0.018509 | 0.018527 | 0.018545 | 0.018563 | 0.018581 | 0.018599 | 0.018617 | 0.018635 | 0.018653 | 2.0286e-07 | 1e-07 | 2.3089e-05 | 2.3291e-05 | 2.3494e-05 | 2.3697e-05 | 2.39e-05 | 2.4e-05 | 2.41e-05 | 2.42e-05 | 2.43e-05 | 2.44e-05 | 2.45e-05 | 2.46e-05 | 2.47e-05 | 2.48e-05 | 2.49e-05 | 2.5e-05 | 2.51e-05 | 2.52e-05 | 2.53e-05 | 2.54e-05
| FNS032-156356596 | 10 | 10 | 2.02e-05 | 0 | 3.13e-05 | 0 | 3.13e-05 | 0 | 3.1714e-07 | 0 | 3.0031e-05 | 3.0349e-05 | 3.0666e-05 | 3.0983e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 3.13e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FNS032-24606816 | 135 | 125 | 0.012453 | 2.03e-05 | 0.015772 | 3.05e-05 | 0.015185 | 2.92e-05 | 9.4823e-05 | -2.9338e-05 | 0.015392 | 0.015487 | 0.015582 | 0.015677 | 0.015772 | 0.015742 | 0.015713 | 0.015684 | 0.015654 | 0.015625 | 0.015596 | 0.015566 | 0.015537 | 0.015508 | 0.015478 | 0.015449 | 0.01542 | 0.01539 | 0.015361 | 0.015331 | 2.9143e-07 | -6.5e-08 | 2.9334e-05 | 2.9626e-05 | 2.9917e-05 | 3.0209e-05 | 3.05e-05 | 3.0435e-05 | 3.037e-05 | 3.0305e-05 | 3.024e-05 | 3.0175e-05 | 3.011e-05 | 3.0045e-05 | 2.998e-05 | 2.9915e-05 | 2.985e-05 | 2.9785e-05 | 2.972e-05 | 2.9655e-05 | 2.959e-05 | 2.9525e-05
| GB011-15403523 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GB011-15403536 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GB012-15403573 | 27 | 27 | 0.017047 | 0 | 0.018474 | 0 | 0.016754 | 0 | 4.0791e-05 | -8.6029e-05 | 0.018311 | 0.018352 | 0.018393 | 0.018434 | 0.018474 | 0.018388 | 0.018302 | 0.018216 | 0.01813 | 0.018044 | 0.017958 | 0.017872 | 0.017786 | 0.0177 | 0.017614 | 0.017528 | 0.017442 | 0.017356 | 0.01727 | 0.017184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GB014-15403449 | 546 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GB014-15403475 | 539 | 539 | 1.22e-05 | 0 | 1.38e-05 | 0 | 1.32e-05 | 0 | 4.5714e-08 | -3e-08 | 1.3617e-05 | 1.3663e-05 | 1.3709e-05 | 1.3754e-05 | 1.38e-05 | 1.377e-05 | 1.374e-05 | 1.371e-05 | 1.368e-05 | 1.365e-05 | 1.362e-05 | 1.359e-05 | 1.356e-05 | 1.353e-05 | 1.35e-05 | 1.347e-05 | 1.344e-05 | 1.341e-05 | 1.338e-05 | 1.335e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GB031-15403499 | 632 | 632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GB032-15403425 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GB032-15403438 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY011-153967160 | 1961 | 1961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY011-15403919 | 4414 | 2453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY012-15403889 | 893 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY013-15403874 | 346 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY014-116530590 | 3616 | 3616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY014-15403904 | 3888 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY022-15403949 | 523 | 523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY024-15403979 | 2453 | 879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY024-77737752 | 1574 | 1574 | 9.75e-05 | 0 | 0.00011497 | 0 | 0.00011044 | 0 | 4.9917e-07 | -2.267e-07 | 0.00011297 | 0.00011347 | 0.00011397 | 0.00011447 | 0.00011497 | 0.00011474 | 0.00011452 | 0.00011429 | 0.00011406 | 0.00011384 | 0.00011361 | 0.00011338 | 0.00011316 | 0.00011293 | 0.0001127 | 0.00011248 | 0.00011225 | 0.00011202 | 0.0001118 | 0.00011157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP011-123128913 | 8 | 8 | 1.29e-05 | 0 | 2.02e-05 | 0 | 2.09e-05 | 0 | 2.0857e-07 | 3.5e-08 | 1.9366e-05 | 1.9574e-05 | 1.9783e-05 | 1.9991e-05 | 2.02e-05 | 2.0235e-05 | 2.027e-05 | 2.0305e-05 | 2.034e-05 | 2.0375e-05 | 2.041e-05 | 2.0445e-05 | 2.048e-05 | 2.0515e-05 | 2.055e-05 | 2.0585e-05 | 2.062e-05 | 2.0655e-05 | 2.069e-05 | 2.0725e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP011-124927621 | 18 | 18 | 0.0021799 | 0 | 0.0030568 | 0 | 0.0030076 | 0 | 2.5054e-05 | -2.461e-06 | 0.0029566 | 0.0029816 | 0.0030067 | 0.0030317 | 0.0030568 | 0.0030543 | 0.0030519 | 0.0030494 | 0.0030469 | 0.0030445 | 0.003042 | 0.0030396 | 0.0030371 | 0.0030346 | 0.0030322 | 0.0030297 | 0.0030273 | 0.0030248 | 0.0030223 | 0.0030199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP011-144337307 | 14 | 14 | 0.0026982 | 0 | 0.0037039 | 0 | 0.0040343 | 0 | 2.8735e-05 | 1.6522e-05 | 0.0035889 | 0.0036177 | 0.0036464 | 0.0036751 | 0.0037039 | 0.0037204 | 0.0037369 | 0.0037534 | 0.00377 | 0.0037865 | 0.003803 | 0.0038195 | 0.0038361 | 0.0038526 | 0.0038691 | 0.0038856 | 0.0039021 | 0.0039187 | 0.0039352 | 0.0039517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP011-144337672 | 21 | 21 | 0.0024146 | 0 | 0.0030838 | 0 | 0.0032507 | 0 | 1.912e-05 | 8.3482e-06 | 0.0030073 | 0.0030264 | 0.0030455 | 0.0030646 | 0.0030838 | 0.0030921 | 0.0031005 | 0.0031088 | 0.0031171 | 0.0031255 | 0.0031338 | 0.0031422 | 0.0031505 | 0.0031589 | 0.0031672 | 0.0031756 | 0.0031839 | 0.0031923 | 0.0032006 | 0.003209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP011-187048453 | 1131 | 631 | 0.015384 | 0.0034877 | 0.020538 | 0.0048192 | 0.021184 | 0.0050059 | 0.00014725 | 3.2279e-05 | 0.019949 | 0.020097 | 0.020244 | 0.020391 | 0.020538 | 0.020571 | 0.020603 | 0.020635 | 0.020667 | 0.0207 | 0.020732 | 0.020764 | 0.020797 | 0.020829 | 0.020861 | 0.020893 | 0.020926 | 0.020958 | 0.02099 | 0.021022 | 3.8043e-05 | 9.3385e-06 | 0.004667 | 0.004705 | 0.0047431 | 0.0047811 | 0.0048192 | 0.0048285 | 0.0048378 | 0.0048472 | 0.0048565 | 0.0048659 | 0.0048752 | 0.0048845 | 0.0048939 | 0.0049032 | 0.0049126 | 0.0049219 | 0.0049312 | 0.0049406 | 0.0049499 | 0.0049592
| GHP011-190579532 | 1131 | 0 | 0.0031064 | 0.0027648 | 0.0042989 | 0.0036475 | 0.0042744 | 0.0035776 | 3.4071e-05 | -1.2243e-06 | 0.0041626 | 0.0041967 | 0.0042308 | 0.0042649 | 0.0042989 | 0.0042977 | 0.0042965 | 0.0042952 | 0.004294 | 0.0042928 | 0.0042916 | 0.0042904 | 0.0042891 | 0.0042879 | 0.0042867 | 0.0042855 | 0.0042842 | 0.004283 | 0.0042818 | 0.0042806 | 2.522e-05 | -3.4984e-06 | 0.0035467 | 0.0035719 | 0.0035971 | 0.0036223 | 0.0036476 | 0.0036441 | 0.0036406 | 0.0036371 | 0.0036336 | 0.0036301 | 0.0036266 | 0.0036231 | 0.0036196 | 0.0036161 | 0.0036126 | 0.0036091 | 0.0036056 | 0.0036021 | 0.0035986 | 0.0035951
| GHP011-62939475 | 500 | 369 | 0.0055444 | 0.0030561 | 0.0070679 | 0.0038127 | 0.0076134 | 0.0040128 | 4.3528e-05 | 2.7278e-05 | 0.0068938 | 0.0069373 | 0.0069808 | 0.0070243 | 0.0070679 | 0.0070951 | 0.0071224 | 0.0071497 | 0.007177 | 0.0072043 | 0.0072315 | 0.0072588 | 0.0072861 | 0.0073134 | 0.0073406 | 0.0073679 | 0.0073952 | 0.0074225 | 0.0074498 | 0.007477 | 2.1617e-05 | 1.0002e-05 | 0.0037263 | 0.0037479 | 0.0037695 | 0.0037911 | 0.0038127 | 0.0038228 | 0.0038328 | 0.0038428 | 0.0038528 | 0.0038628 | 0.0038728 | 0.0038828 | 0.0038928 | 0.0039028 | 0.0039128 | 0.0039228 | 0.0039328 | 0.0039428 | 0.0039528 | 0.0039628
| GHP011-72503866 | 70 | 70 | 0.0011987 | 0 | 0.0017034 | 0 | 0.001677 | 0 | 1.442e-05 | -1.3211e-06 | 0.0016457 | 0.0016602 | 0.0016746 | 0.001689 | 0.0017034 | 0.0017021 | 0.0017008 | 0.0016994 | 0.0016981 | 0.0016968 | 0.0016955 | 0.0016942 | 0.0016928 | 0.0016915 | 0.0016902 | 0.0016889 | 0.0016876 | 0.0016862 | 0.0016849 | 0.0016836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP012-190579518 | 1925 | 0 | 0.012558 | 0 | 0.01656 | 0 | 0.017641 | 0 | 0.00011436 | 5.4038e-05 | 0.016103 | 0.016217 | 0.016332 | 0.016446 | 0.01656 | 0.016614 | 0.016669 | 0.016723 | 0.016777 | 0.016831 | 0.016885 | 0.016939 | 0.016993 | 0.017047 | 0.017101 | 0.017155 | 0.017209 | 0.017263 | 0.017317 | 0.017371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP012-77546539 | 1925 | 1925 | 0.0030266 | 0 | 0.0036849 | 0 | 0.0036872 | 0 | 1.8809e-05 | 1.145e-07 | 0.0036097 | 0.0036285 | 0.0036473 | 0.0036661 | 0.0036849 | 0.003685 | 0.0036851 | 0.0036853 | 0.0036854 | 0.0036855 | 0.0036856 | 0.0036857 | 0.0036858 | 0.0036859 | 0.0036861 | 0.0036862 | 0.0036863 | 0.0036864 | 0.0036865 | 0.0036866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP021-130746528 | 1624 | 555 | 0.0041984 | 0.0016824 | 0.0057321 | 0.0022001 | 0.0064269 | 0.002372 | 4.3819e-05 | 3.4739e-05 | 0.0055568 | 0.0056006 | 0.0056445 | 0.0056883 | 0.0057321 | 0.0057668 | 0.0058016 | 0.0058363 | 0.0058711 | 0.0059058 | 0.0059405 | 0.0059753 | 0.00601 | 0.0060448 | 0.0060795 | 0.0061142 | 0.006149 | 0.0061837 | 0.0062184 | 0.0062532 | 1.4792e-05 | 8.5953e-06 | 0.002141 | 0.0021558 | 0.0021705 | 0.0021853 | 0.0022001 | 0.0022087 | 0.0022173 | 0.0022259 | 0.0022345 | 0.0022431 | 0.0022517 | 0.0022603 | 0.0022689 | 0.0022775 | 0.0022861 | 0.0022947 | 0.0023033 | 0.0023119 | 0.0023205 | 0.0023291
| GHP021-140732642 | 33 | 33 | 0.0011432 | 0 | 0.0014636 | 0 | 0.0014979 | 0 | 9.1524e-06 | 1.7152e-06 | 0.001427 | 0.0014361 | 0.0014453 | 0.0014544 | 0.0014636 | 0.0014653 | 0.001467 | 0.0014687 | 0.0014704 | 0.0014721 | 0.0014739 | 0.0014756 | 0.0014773 | 0.001479 | 0.0014807 | 0.0014824 | 0.0014842 | 0.0014859 | 0.0014876 | 0.0014893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP021-141034135 | 50 | 50 | 0.00036734 | 0 | 0.00047524 | 0 | 0.00047097 | 0 | 3.0827e-06 | -2.1365e-07 | 0.00046291 | 0.00046599 | 0.00046908 | 0.00047216 | 0.00047524 | 0.00047503 | 0.00047481 | 0.0004746 | 0.00047439 | 0.00047417 | 0.00047396 | 0.00047375 | 0.00047353 | 0.00047332 | 0.0004731 | 0.00047289 | 0.00047268 | 0.00047246 | 0.00047225 | 0.00047204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP021-187048221 | 1069 | 986 | 0.015015 | 0.00016436 | 0.019279 | 0.0002389 | 0.019173 | 0.00024287 | 0.00012183 | -5.2807e-06 | 0.018791 | 0.018913 | 0.019035 | 0.019157 | 0.019279 | 0.019273 | 0.019268 | 0.019263 | 0.019258 | 0.019252 | 0.019247 | 0.019242 | 0.019236 | 0.019231 | 0.019226 | 0.019221 | 0.019215 | 0.01921 | 0.019205 | 0.019199 | 2.1296e-06 | 1.9855e-07 | 0.00023038 | 0.00023251 | 0.00023464 | 0.00023677 | 0.0002389 | 0.0002391 | 0.0002393 | 0.0002395 | 0.0002397 | 0.00023989 | 0.00024009 | 0.00024029 | 0.00024049 | 0.00024069 | 0.00024089 | 0.00024109 | 0.00024128 | 0.00024148 | 0.00024168 | 0.00024188
| GHP021-190579468 | 2376 | 0 | 0.0022774 | 0.0055971 | 0.0031518 | 0.0078462 | 0.0032449 | 0.0081179 | 2.4985e-05 | 4.6503e-06 | 0.0030519 | 0.0030769 | 0.0031019 | 0.0031269 | 0.0031518 | 0.0031565 | 0.0031612 | 0.0031658 | 0.0031705 | 0.0031751 | 0.0031798 | 0.0031844 | 0.0031891 | 0.0031937 | 0.0031984 | 0.003203 | 0.0032077 | 0.0032123 | 0.003217 | 0.0032216 | 6.426e-05 | 1.3585e-05 | 0.0075892 | 0.0076534 | 0.0077177 | 0.0077819 | 0.0078462 | 0.0078598 | 0.0078734 | 0.0078869 | 0.0079005 | 0.0079141 | 0.0079277 | 0.0079413 | 0.0079549 | 0.0079685 | 0.007982 | 0.0079956 | 0.0080092 | 0.0080228 | 0.0080364 | 0.00805
| GHP021-24614163 | 752 | 752 | 0.0067761 | 0 | 0.0070364 | 0 | 0.0067173 | 0 | 7.4365e-06 | -1.5953e-05 | 0.0070066 | 0.007014 | 0.0070215 | 0.0070289 | 0.0070364 | 0.0070204 | 0.0070044 | 0.0069885 | 0.0069725 | 0.0069566 | 0.0069406 | 0.0069247 | 0.0069087 | 0.0068928 | 0.0068768 | 0.0068609 | 0.0068449 | 0.006829 | 0.006813 | 0.0067971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP022-141431252 | 26 | 26 | 0.0024107 | 0 | 0.0034 | 0 | 0.0036272 | 0 | 2.8267e-05 | 1.1359e-05 | 0.003287 | 0.0033152 | 0.0033435 | 0.0033718 | 0.0034 | 0.0034114 | 0.0034228 | 0.0034341 | 0.0034455 | 0.0034568 | 0.0034682 | 0.0034796 | 0.0034909 | 0.0035023 | 0.0035136 | 0.003525 | 0.0035363 | 0.0035477 | 0.0035591 | 0.0035704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP022-141431280 | 11 | 11 | 0.00094994 | 0 | 0.0012615 | 0 | 0.0012845 | 0 | 8.9014e-06 | 1.1525e-06 | 0.0012259 | 0.0012348 | 0.0012437 | 0.0012526 | 0.0012615 | 0.0012626 | 0.0012638 | 0.0012649 | 0.0012661 | 0.0012673 | 0.0012684 | 0.0012696 | 0.0012707 | 0.0012719 | 0.001273 | 0.0012742 | 0.0012753 | 0.0012765 | 0.0012776 | 0.0012788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GHP022-188587433 | 475 | 395 | 0.015666 | 0.0026611 | 0.019526 | 0.0036663 | 0.020558 | 0.0039764 | 0.00011031 | 5.1595e-05 | 0.019085 | 0.019195 | 0.019306 | 0.019416 | 0.019526 | 0.019578 | 0.019629 | 0.019681 | 0.019733 | 0.019784 | 0.019836 | 0.019887 | 0.019939 | 0.019991 | 0.020042 | 0.020094 | 0.020145 | 0.020197 | 0.020249 | 0.0203 | 2.8719e-05 | 1.5502e-05 | 0.0035514 | 0.0035801 | 0.0036089 | 0.0036376 | 0.0036663 | 0.0036818 | 0.0036973 | 0.0037128 | 0.0037283 | 0.0037438 | 0.0037593 | 0.0037748 | 0.0037903 | 0.0038058 | 0.0038213 | 0.0038368 | 0.0038523 | 0.0038678 | 0.0038833 | 0.0038988
| GHP022-190579440 | 475 | 0 | 0.0082356 | 0.00063855 | 0.011031 | 0.00082073 | 0.011879 | 0.0008427 | 7.9878e-05 | 4.2373e-05 | 0.010712 | 0.010792 | 0.010872 | 0.010951 | 0.011031 | 0.011074 | 0.011116 | 0.011158 | 0.011201 | 0.011243 | 0.011286 | 0.011328 | 0.01137 | 0.011413 | 0.011455 | 0.011497 | 0.01154 | 0.011582 | 0.011625 | 0.011667 | 5.2053e-06 | 1.0985e-06 | 0.00079991 | 0.00080511 | 0.00081032 | 0.00081552 | 0.00082073 | 0.00082183 | 0.00082293 | 0.00082403 | 0.00082512 | 0.00082622 | 0.00082732 | 0.00082842 | 0.00082952 | 0.00083062 | 0.00083171 | 0.00083281 | 0.00083391 | 0.00083501 | 0.00083611 | 0.00083721
| GHP022-72503462 | 43 | 43 | 0.0030016 | 0 | 0.0043095 | 0 | 0.0045913 | 0 | 3.737e-05 | 1.4089e-05 | 0.0041601 | 0.0041974 | 0.0042348 | 0.0042722 | 0.0043095 | 0.0043236 | 0.0043377 | 0.0043518 | 0.0043659 | 0.00438 | 0.0043941 | 0.0044082 | 0.0044223 | 0.0044363 | 0.0044504 | 0.0044645 | 0.0044786 | 0.0044927 | 0.0045068 | 0.0045209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL011-15402625 | 1109 | 1109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL012-15402649 | 2855 | 2855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL013-15402686 | 2203 | 2203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL014-15402723 | 2959 | 2959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL015-15402771 | 3591 | 3591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL021-15402795 | 3384 | 2196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL021-24612685 | 1188 | 1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL022-15402832 | 3776 | 804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL022-24612699 | 2972 | 2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL023-15402869 | 2121 | 2121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL024-15402919 | 1768 | 1768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE011-15406891 | 359 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE012-15406954 | 4727 | 3531 | 1.41e-05 | 0 | 2.14e-05 | 0 | 2.24e-05 | 0 | 2.0857e-07 | 5e-08 | 2.0566e-05 | 2.0774e-05 | 2.0983e-05 | 2.1191e-05 | 2.14e-05 | 2.145e-05 | 2.15e-05 | 2.155e-05 | 2.16e-05 | 2.165e-05 | 2.17e-05 | 2.175e-05 | 2.18e-05 | 2.185e-05 | 2.19e-05 | 2.195e-05 | 2.2e-05 | 2.205e-05 | 2.21e-05 | 2.215e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE012-77546340 | 1196 | 1196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE013-15407017 | 6632 | 6632 | 0.011586 | 0 | 0.01568 | 0 | 0.01589 | 0 | 0.00011699 | 1.0461e-05 | 0.015212 | 0.015329 | 0.015446 | 0.015563 | 0.01568 | 0.015691 | 0.015701 | 0.015712 | 0.015722 | 0.015733 | 0.015743 | 0.015754 | 0.015764 | 0.015774 | 0.015785 | 0.015795 | 0.015806 | 0.015816 | 0.015827 | 0.015837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE021-15407054 | 603 | 603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE023-15407104 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE024-15407167 | 4884 | 3522 | 0.0048328 | 0.00080109 | 0.0049199 | 0.00084973 | 0.0047951 | 0.0007896 | 2.4897e-06 | -6.2419e-06 | 0.00491 | 0.0049125 | 0.0049149 | 0.0049174 | 0.0049199 | 0.0049137 | 0.0049074 | 0.0049012 | 0.004895 | 0.0048887 | 0.0048825 | 0.0048762 | 0.00487 | 0.0048637 | 0.0048575 | 0.0048513 | 0.004845 | 0.0048388 | 0.0048325 | 0.0048263 | 1.3898e-06 | -3.0066e-06 | 0.00084417 | 0.00084556 | 0.00084695 | 0.00084834 | 0.00084973 | 0.00084673 | 0.00084372 | 0.00084071 | 0.00083771 | 0.0008347 | 0.00083169 | 0.00082869 | 0.00082568 | 0.00082267 | 0.00081967 | 0.00081666 | 0.00081365 | 0.00081065 | 0.00080764 | 0.00080463
| GLE024-24612325 | 1362 | 1362 | 0.0021867 | 0 | 0.0023365 | 0 | 0.0021527 | 0 | 4.2806e-06 | -9.1898e-06 | 0.0023194 | 0.0023237 | 0.002328 | 0.0023322 | 0.0023365 | 0.0023273 | 0.0023182 | 0.002309 | 0.0022998 | 0.0022906 | 0.0022814 | 0.0022722 | 0.002263 | 0.0022538 | 0.0022446 | 0.0022354 | 0.0022263 | 0.0022171 | 0.0022079 | 0.0021987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE031-15407178 | 3592 | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE031-24612339 | 1555 | 1555 | 0.0013349 | 0 | 0.0014327 | 0 | 0.0013132 | 0 | 2.7927e-06 | -5.9724e-06 | 0.0014215 | 0.0014243 | 0.0014271 | 0.0014299 | 0.0014327 | 0.0014267 | 0.0014207 | 0.0014147 | 0.0014088 | 0.0014028 | 0.0013968 | 0.0013909 | 0.0013849 | 0.0013789 | 0.0013729 | 0.001367 | 0.001361 | 0.001355 | 0.0013491 | 0.0013431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE032-15407241 | 2766 | 1168 | 0.00071453 | 0 | 0.00080661 | 0 | 0.00079175 | 0 | 2.6308e-06 | -7.426e-07 | 0.00079608 | 0.00079871 | 0.00080135 | 0.00080398 | 0.00080661 | 0.00080586 | 0.00080512 | 0.00080438 | 0.00080364 | 0.00080289 | 0.00080215 | 0.00080141 | 0.00080067 | 0.00079992 | 0.00079918 | 0.00079844 | 0.0007977 | 0.00079695 | 0.00079621 | 0.00079547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE032-24612713 | 1598 | 1598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE033-15407304 | 574 | 574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB011-24597032 | 264 | 264 | 0.048198 | 0 | 0.064407 | 0 | 0.073019 | 0 | 0.0004631 | 0.00043061 | 0.062555 | 0.063018 | 0.063481 | 0.063944 | 0.064407 | 0.064838 | 0.065268 | 0.065699 | 0.066129 | 0.06656 | 0.066991 | 0.067421 | 0.067852 | 0.068282 | 0.068713 | 0.069144 | 0.069574 | 0.070005 | 0.070435 | 0.070866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB011-24613746 | 1640 | 1640 | 0.018602 | 0 | 0.0267 | 0 | 0.03122 | 0 | 0.00023135 | 0.00022603 | 0.025774 | 0.026006 | 0.026237 | 0.026468 | 0.0267 | 0.026926 | 0.027152 | 0.027378 | 0.027604 | 0.02783 | 0.028056 | 0.028282 | 0.028508 | 0.028734 | 0.02896 | 0.029186 | 0.029412 | 0.029638 | 0.029864 | 0.03009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB011-74623144 | 2553 | 4 | 0.0047805 | 0.0010063 | 0.0058634 | 0.0014291 | 0.0063877 | 0.0016634 | 3.0941e-05 | 2.6214e-05 | 0.0057397 | 0.0057706 | 0.0058015 | 0.0058325 | 0.0058634 | 0.0058896 | 0.0059158 | 0.0059421 | 0.0059683 | 0.0059945 | 0.0060207 | 0.0060469 | 0.0060731 | 0.0060993 | 0.0061256 | 0.0061518 | 0.006178 | 0.0062042 | 0.0062304 | 0.0062566 | 1.2081e-05 | 1.1713e-05 | 0.0013808 | 0.0013929 | 0.001405 | 0.0014171 | 0.0014291 | 0.0014409 | 0.0014526 | 0.0014643 | 0.001476 | 0.0014877 | 0.0014994 | 0.0015111 | 0.0015228 | 0.0015346 | 0.0015463 | 0.001558 | 0.0015697 | 0.0015814 | 0.0015931 | 0.0016048
| GSB011-74623154 | 2549 | 645 | 0.011776 | 0.0093967 | 0.016531 | 0.014016 | 0.019293 | 0.016692 | 0.00013586 | 0.00013807 | 0.015988 | 0.016124 | 0.01626 | 0.016396 | 0.016531 | 0.016669 | 0.016808 | 0.016946 | 0.017084 | 0.017222 | 0.01736 | 0.017498 | 0.017636 | 0.017774 | 0.017912 | 0.01805 | 0.018188 | 0.018326 | 0.018464 | 0.018603 | 0.00013198 | 0.00013379 | 0.013488 | 0.01362 | 0.013752 | 0.013884 | 0.014016 | 0.01415 | 0.014283 | 0.014417 | 0.014551 | 0.014685 | 0.014819 | 0.014952 | 0.015086 | 0.01522 | 0.015354 | 0.015487 | 0.015621 | 0.015755 | 0.015889 | 0.016023
| GSB012-181419068 | 0 | 0 | 0.002133 | 0 | 0.0029787 | 0 | 0.0034692 | 0 | 2.4162e-05 | 2.4523e-05 | 0.0028821 | 0.0029062 | 0.0029304 | 0.0029545 | 0.0029787 | 0.0030032 | 0.0030278 | 0.0030523 | 0.0030768 | 0.0031013 | 0.0031258 | 0.0031504 | 0.0031749 | 0.0031994 | 0.0032239 | 0.0032485 | 0.003273 | 0.0032975 | 0.003322 | 0.0033466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB012-24607348 | 2031 | 1711 | 0.072789 | 0.012354 | 0.093629 | 0.018297 | 0.095419 | 0.01873 | 0.00059542 | 8.9487e-05 | 0.091247 | 0.091843 | 0.092438 | 0.093034 | 0.093629 | 0.093718 | 0.093808 | 0.093897 | 0.093987 | 0.094076 | 0.094166 | 0.094255 | 0.094345 | 0.094434 | 0.094524 | 0.094613 | 0.094703 | 0.094792 | 0.094882 | 0.094971 | 0.00016978 | 2.1682e-05 | 0.017618 | 0.017787 | 0.017957 | 0.018127 | 0.018297 | 0.018319 | 0.01834 | 0.018362 | 0.018384 | 0.018405 | 0.018427 | 0.018449 | 0.01847 | 0.018492 | 0.018514 | 0.018535 | 0.018557 | 0.018579 | 0.0186 | 0.018622
| GSB012-24607362 | 288 | 197 | 0.0038902 | 0.003729 | 0.005546 | 0.0053127 | 0.0055211 | 0.0052916 | 4.7309e-05 | -1.2484e-06 | 0.0053568 | 0.0054041 | 0.0054514 | 0.0054987 | 0.005546 | 0.0055448 | 0.0055435 | 0.0055423 | 0.005541 | 0.0055398 | 0.0055385 | 0.0055373 | 0.005536 | 0.0055348 | 0.0055335 | 0.0055323 | 0.005531 | 0.0055298 | 0.0055285 | 0.0055273 | 4.5248e-05 | -1.0554e-06 | 0.0051317 | 0.0051769 | 0.0052222 | 0.0052674 | 0.0053127 | 0.0053116 | 0.0053105 | 0.0053095 | 0.0053084 | 0.0053074 | 0.0053063 | 0.0053053 | 0.0053042 | 0.0053032 | 0.0053021 | 0.0053011 | 0.0053 | 0.0052989 | 0.0052979 | 0.0052968
| GSB012-72499030 | 13 | 13 | 0.0034387 | 0 | 0.0049873 | 0 | 0.005376 | 0 | 4.4245e-05 | 1.9435e-05 | 0.0048104 | 0.0048546 | 0.0048988 | 0.0049431 | 0.0049873 | 0.0050068 | 0.0050262 | 0.0050456 | 0.0050651 | 0.0050845 | 0.0051039 | 0.0051234 | 0.0051428 | 0.0051622 | 0.0051817 | 0.0052011 | 0.0052206 | 0.00524 | 0.0052594 | 0.0052789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB012-72499395 | 24 | 24 | 0.00423 | 0 | 0.0060974 | 0 | 0.0060692 | 0 | 5.3353e-05 | -1.4075e-06 | 0.005884 | 0.0059373 | 0.0059907 | 0.006044 | 0.0060974 | 0.006096 | 0.0060946 | 0.0060932 | 0.0060918 | 0.0060904 | 0.006089 | 0.0060875 | 0.0060861 | 0.0060847 | 0.0060833 | 0.0060819 | 0.0060805 | 0.0060791 | 0.0060777 | 0.0060763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB012-74623277 | 2218 | 187 | 0.035722 | 0.0084849 | 0.046192 | 0.012169 | 0.048912 | 0.013239 | 0.00029913 | 0.000136 | 0.044995 | 0.045294 | 0.045593 | 0.045893 | 0.046192 | 0.046328 | 0.046464 | 0.0466 | 0.046736 | 0.046872 | 0.047008 | 0.047144 | 0.04728 | 0.047416 | 0.047552 | 0.047688 | 0.047824 | 0.04796 | 0.048096 | 0.048232 | 0.00010525 | 5.3503e-05 | 0.011748 | 0.011853 | 0.011958 | 0.012063 | 0.012169 | 0.012222 | 0.012276 | 0.012329 | 0.012383 | 0.012436 | 0.01249 | 0.012543 | 0.012597 | 0.01265 | 0.012704 | 0.012757 | 0.012811 | 0.012864 | 0.012918 | 0.012971
| GSB012-77736949 | 32 | 32 | 0.0078567 | 0 | 0.010687 | 0 | 0.012344 | 0 | 8.088e-05 | 8.2833e-05 | 0.010364 | 0.010445 | 0.010526 | 0.010607 | 0.010687 | 0.01077 | 0.010853 | 0.010936 | 0.011019 | 0.011102 | 0.011184 | 0.011267 | 0.01135 | 0.011433 | 0.011516 | 0.011599 | 0.011681 | 0.011764 | 0.011847 | 0.01193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB012-85320967 | 13 | 13 | 6.2e-05 | 0 | 9.79e-05 | 0 | 0.00010533 | 0 | 1.0257e-06 | 3.717e-07 | 9.3797e-05 | 9.4823e-05 | 9.5849e-05 | 9.6874e-05 | 9.79e-05 | 9.8272e-05 | 9.8643e-05 | 9.9015e-05 | 9.9387e-05 | 9.9758e-05 | 0.00010013 | 0.0001005 | 0.00010087 | 0.00010125 | 0.00010162 | 0.00010199 | 0.00010236 | 0.00010273 | 0.0001031 | 0.00010348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB013-74623435 | 2830 | 2830 | 0.052948 | 0 | 0.069772 | 0 | 0.074255 | 0 | 0.00048067 | 0.00022413 | 0.067849 | 0.06833 | 0.068811 | 0.069291 | 0.069772 | 0.069996 | 0.07022 | 0.070444 | 0.070668 | 0.070893 | 0.071117 | 0.071341 | 0.071565 | 0.071789 | 0.072013 | 0.072237 | 0.072461 | 0.072686 | 0.07291 | 0.073134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB014-163179564 | 4 | 4 | 0.00062421 | 0 | 0.00099756 | 0 | 0.0011202 | 0 | 1.0667e-05 | 6.1327e-06 | 0.00095489 | 0.00096556 | 0.00097623 | 0.00098689 | 0.00099756 | 0.0010037 | 0.0010098 | 0.001016 | 0.0010221 | 0.0010282 | 0.0010344 | 0.0010405 | 0.0010466 | 0.0010528 | 0.0010589 | 0.001065 | 0.0010712 | 0.0010773 | 0.0010834 | 0.0010896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB014-194965507 | 833 | 833 | 0.065348 | 0 | 0.087957 | 0 | 0.10123 | 0 | 0.00064598 | 0.00066374 | 0.085373 | 0.086019 | 0.086665 | 0.087311 | 0.087957 | 0.088621 | 0.089285 | 0.089948 | 0.090612 | 0.091276 | 0.09194 | 0.092603 | 0.093267 | 0.093931 | 0.094595 | 0.095258 | 0.095922 | 0.096586 | 0.09725 | 0.097913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB014-194965541 | 1240 | 546 | 0.024524 | 0.0054794 | 0.030551 | 0.0078918 | 0.033179 | 0.009354 | 0.0001722 | 0.00013137 | 0.029863 | 0.030035 | 0.030207 | 0.030379 | 0.030551 | 0.030683 | 0.030814 | 0.030946 | 0.031077 | 0.031208 | 0.03134 | 0.031471 | 0.031602 | 0.031734 | 0.031865 | 0.031997 | 0.032128 | 0.032259 | 0.032391 | 0.032522 | 6.8924e-05 | 7.3109e-05 | 0.0076161 | 0.007685 | 0.0077539 | 0.0078229 | 0.0078918 | 0.0079649 | 0.008038 | 0.0081111 | 0.0081842 | 0.0082573 | 0.0083304 | 0.0084035 | 0.0084767 | 0.0085498 | 0.0086229 | 0.008696 | 0.0087691 | 0.0088422 | 0.0089153 | 0.0089884
| GSB014-194965599 | 694 | 663 | 0.017525 | 0.0027075 | 0.023828 | 0.0041882 | 0.027451 | 0.0051448 | 0.00018006 | 0.00018115 | 0.023107 | 0.023287 | 0.023467 | 0.023647 | 0.023828 | 0.024009 | 0.02419 | 0.024371 | 0.024552 | 0.024733 | 0.024914 | 0.025096 | 0.025277 | 0.025458 | 0.025639 | 0.02582 | 0.026001 | 0.026183 | 0.026364 | 0.026545 | 4.2306e-05 | 4.783e-05 | 0.004019 | 0.0040613 | 0.0041036 | 0.0041459 | 0.0041882 | 0.0042361 | 0.0042839 | 0.0043317 | 0.0043796 | 0.0044274 | 0.0044752 | 0.0045231 | 0.0045709 | 0.0046187 | 0.0046665 | 0.0047144 | 0.0047622 | 0.00481 | 0.0048579 | 0.0049057
| GSB014-73768594 | 27 | 27 | 0.0053159 | 0 | 0.0083502 | 0 | 0.0092752 | 0 | 8.6696e-05 | 4.6249e-05 | 0.0080035 | 0.0080901 | 0.0081768 | 0.0082635 | 0.0083502 | 0.0083965 | 0.0084427 | 0.008489 | 0.0085352 | 0.0085815 | 0.0086277 | 0.008674 | 0.0087202 | 0.0087665 | 0.0088127 | 0.008859 | 0.0089052 | 0.0089515 | 0.0089977 | 0.009044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB014-74623507 | 2109 | 36 | 0.00873 | 0.029321 | 0.011119 | 0.037104 | 0.012166 | 0.040893 | 6.8245e-05 | 5.2347e-05 | 0.010846 | 0.010914 | 0.010982 | 0.01105 | 0.011119 | 0.011171 | 0.011223 | 0.011276 | 0.011328 | 0.01138 | 0.011433 | 0.011485 | 0.011537 | 0.01159 | 0.011642 | 0.011694 | 0.011747 | 0.011799 | 0.011851 | 0.011904 | 0.00022237 | 0.00018945 | 0.036215 | 0.036437 | 0.036659 | 0.036882 | 0.037104 | 0.037294 | 0.037483 | 0.037673 | 0.037862 | 0.038051 | 0.038241 | 0.03843 | 0.03862 | 0.038809 | 0.038999 | 0.039188 | 0.039378 | 0.039567 | 0.039757 | 0.039946
| HSM001-108341890 | 53 | 53 | 0.0046501 | 0 | 0.0060134 | 0 | 0.006109 | 0 | 3.8951e-05 | 4.7787e-06 | 0.0058576 | 0.0058966 | 0.0059355 | 0.0059745 | 0.0060134 | 0.0060182 | 0.006023 | 0.0060277 | 0.0060325 | 0.0060373 | 0.0060421 | 0.0060469 | 0.0060516 | 0.0060564 | 0.0060612 | 0.006066 | 0.0060708 | 0.0060755 | 0.0060803 | 0.0060851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-15416529 | 1135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-15416542 | 1135 | 127 | 0.016842 | 0.0052619 | 0.01826 | 0.0053989 | 0.017774 | 0.0053527 | 4.0516e-05 | -2.4332e-05 | 0.018098 | 0.018139 | 0.018179 | 0.01822 | 0.01826 | 0.018236 | 0.018212 | 0.018187 | 0.018163 | 0.018139 | 0.018114 | 0.01809 | 0.018066 | 0.018041 | 0.018017 | 0.017993 | 0.017968 | 0.017944 | 0.01792 | 0.017895 | 3.914e-06 | -2.3066e-06 | 0.0053832 | 0.0053871 | 0.0053911 | 0.005395 | 0.0053989 | 0.0053966 | 0.0053943 | 0.005392 | 0.0053897 | 0.0053873 | 0.005385 | 0.0053827 | 0.0053804 | 0.0053781 | 0.0053758 | 0.0053735 | 0.0053712 | 0.0053689 | 0.0053666 | 0.0053643
| HSM001-157535060 | 27 | 27 | 0.0047845 | 0 | 0.0071498 | 0 | 0.0073194 | 0 | 6.7581e-05 | 8.4787e-06 | 0.0068795 | 0.0069471 | 0.0070147 | 0.0070822 | 0.0071498 | 0.0071583 | 0.0071668 | 0.0071753 | 0.0071837 | 0.0071922 | 0.0072007 | 0.0072092 | 0.0072176 | 0.0072261 | 0.0072346 | 0.0072431 | 0.0072516 | 0.00726 | 0.0072685 | 0.007277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-157535228 | 26 | 26 | 0.0062389 | 0 | 0.0086371 | 0 | 0.0090569 | 0 | 6.8519e-05 | 2.0987e-05 | 0.008363 | 0.0084316 | 0.0085001 | 0.0085686 | 0.0086371 | 0.0086581 | 0.0086791 | 0.0087001 | 0.0087211 | 0.0087421 | 0.008763 | 0.008784 | 0.008805 | 0.008826 | 0.008847 | 0.008868 | 0.008889 | 0.00891 | 0.0089309 | 0.0089519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-157577413 | 45 | 45 | 0.0022652 | 0 | 0.0030389 | 0 | 0.0031453 | 0 | 2.2107e-05 | 5.318e-06 | 0.0029505 | 0.0029726 | 0.0029947 | 0.0030168 | 0.0030389 | 0.0030442 | 0.0030495 | 0.0030549 | 0.0030602 | 0.0030655 | 0.0030708 | 0.0030761 | 0.0030815 | 0.0030868 | 0.0030921 | 0.0030974 | 0.0031027 | 0.003108 | 0.0031134 | 0.0031187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-157577658 | 20 | 20 | 0.0067198 | 0 | 0.0088691 | 0 | 0.0088718 | 0 | 6.1408e-05 | 1.3825e-07 | 0.0086234 | 0.0086848 | 0.0087462 | 0.0088076 | 0.0088691 | 0.0088692 | 0.0088693 | 0.0088695 | 0.0088696 | 0.0088697 | 0.0088699 | 0.00887 | 0.0088702 | 0.0088703 | 0.0088704 | 0.0088706 | 0.0088707 | 0.0088709 | 0.008871 | 0.0088711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-157598665 | 12 | 12 | 0.0021507 | 0 | 0.0032299 | 0 | 0.0032872 | 0 | 3.0833e-05 | 2.8685e-06 | 0.0031065 | 0.0031374 | 0.0031682 | 0.003199 | 0.0032299 | 0.0032327 | 0.0032356 | 0.0032385 | 0.0032413 | 0.0032442 | 0.0032471 | 0.0032499 | 0.0032528 | 0.0032557 | 0.0032585 | 0.0032614 | 0.0032643 | 0.0032671 | 0.00327 | 0.0032729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-157598865 | 16 | 16 | 0.0022989 | 0 | 0.0035346 | 0 | 0.0035108 | 0 | 3.5305e-05 | -1.1919e-06 | 0.0033934 | 0.0034287 | 0.003464 | 0.0034993 | 0.0035346 | 0.0035334 | 0.0035322 | 0.0035311 | 0.0035299 | 0.0035287 | 0.0035275 | 0.0035263 | 0.0035251 | 0.0035239 | 0.0035227 | 0.0035215 | 0.0035203 | 0.0035191 | 0.0035179 | 0.0035168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-157598965 | 18 | 18 | 0.0053744 | 0 | 0.0078358 | 0 | 0.0079989 | 0 | 7.0326e-05 | 8.1545e-06 | 0.0075545 | 0.0076248 | 0.0076952 | 0.0077655 | 0.0078358 | 0.007844 | 0.0078521 | 0.0078603 | 0.0078684 | 0.0078766 | 0.0078848 | 0.0078929 | 0.0079011 | 0.0079092 | 0.0079174 | 0.0079255 | 0.0079337 | 0.0079418 | 0.00795 | 0.0079581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-163581806 | 8 | 8 | 0.00032941 | 0 | 0.00046569 | 0 | 0.00049184 | 0 | 3.8935e-06 | 1.3075e-06 | 0.00045011 | 0.00045401 | 0.0004579 | 0.00046179 | 0.00046569 | 0.00046699 | 0.0004683 | 0.00046961 | 0.00047092 | 0.00047222 | 0.00047353 | 0.00047484 | 0.00047615 | 0.00047745 | 0.00047876 | 0.00048007 | 0.00048138 | 0.00048269 | 0.00048399 | 0.0004853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-163582048 | 6 | 6 | 0.0014495 | 0 | 0.0020537 | 0 | 0.0021148 | 0 | 1.7263e-05 | 3.054e-06 | 0.0019847 | 0.0020019 | 0.0020192 | 0.0020364 | 0.0020537 | 0.0020568 | 0.0020598 | 0.0020629 | 0.0020659 | 0.002069 | 0.002072 | 0.0020751 | 0.0020781 | 0.0020812 | 0.0020842 | 0.0020873 | 0.0020904 | 0.0020934 | 0.0020965 | 0.0020995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-167869770 | 24 | 24 | 0.0016298 | 0 | 0.0021265 | 0 | 0.0022674 | 0 | 1.4192e-05 | 7.0456e-06 | 0.0020697 | 0.0020839 | 0.0020981 | 0.0021123 | 0.0021265 | 0.0021335 | 0.0021406 | 0.0021476 | 0.0021547 | 0.0021617 | 0.0021687 | 0.0021758 | 0.0021828 | 0.0021899 | 0.0021969 | 0.002204 | 0.002211 | 0.0022181 | 0.0022251 | 0.0022322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-167869862 | 20 | 20 | 0.0036956 | 0 | 0.0050937 | 0 | 0.0051235 | 0 | 3.9945e-05 | 1.4889e-06 | 0.0049339 | 0.0049739 | 0.0050138 | 0.0050538 | 0.0050937 | 0.0050952 | 0.0050967 | 0.0050982 | 0.0050997 | 0.0051012 | 0.0051026 | 0.0051041 | 0.0051056 | 0.0051071 | 0.0051086 | 0.0051101 | 0.0051116 | 0.0051131 | 0.0051146 | 0.005116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-192496053 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-24613473 | 356 | 175 | 0.0097942 | 0.0066199 | 0.013977 | 0.0097313 | 0.014041 | 0.0098281 | 0.0001195 | 3.2295e-06 | 0.013499 | 0.013618 | 0.013738 | 0.013857 | 0.013977 | 0.01398 | 0.013983 | 0.013986 | 0.01399 | 0.013993 | 0.013996 | 0.013999 | 0.014002 | 0.014006 | 0.014009 | 0.014012 | 0.014015 | 0.014019 | 0.014022 | 0.014025 | 8.8899e-05 | 4.8416e-06 | 0.0093757 | 0.0094646 | 0.0095535 | 0.0096424 | 0.0097313 | 0.0097361 | 0.009741 | 0.0097458 | 0.0097507 | 0.0097555 | 0.0097604 | 0.0097652 | 0.00977 | 0.0097749 | 0.0097797 | 0.0097846 | 0.0097894 | 0.0097942 | 0.0097991 | 0.0098039
| HSM001-41021978 | 605 | 520 | 0.010007 | 0.0040689 | 0.01371 | 0.0060505 | 0.013852 | 0.0061832 | 0.0001058 | 7.1059e-06 | 0.013287 | 0.013392 | 0.013498 | 0.013604 | 0.01371 | 0.013717 | 0.013724 | 0.013731 | 0.013738 | 0.013745 | 0.013752 | 0.01376 | 0.013767 | 0.013774 | 0.013781 | 0.013788 | 0.013795 | 0.013802 | 0.013809 | 0.013816 | 5.6617e-05 | 6.6378e-06 | 0.005824 | 0.0058806 | 0.0059372 | 0.0059939 | 0.0060505 | 0.0060571 | 0.0060638 | 0.0060704 | 0.006077 | 0.0060837 | 0.0060903 | 0.0060969 | 0.0061036 | 0.0061102 | 0.0061169 | 0.0061235 | 0.0061301 | 0.0061368 | 0.0061434 | 0.00615
| HSM002-15416605 | 1394 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-15416618 | 1392 | 368 | 0.026116 | 0.010152 | 0.032555 | 0.013129 | 0.031709 | 0.012996 | 0.00018395 | -4.2311e-05 | 0.031819 | 0.032003 | 0.032187 | 0.032371 | 0.032555 | 0.032512 | 0.03247 | 0.032428 | 0.032386 | 0.032343 | 0.032301 | 0.032259 | 0.032216 | 0.032174 | 0.032132 | 0.032089 | 0.032047 | 0.032005 | 0.031962 | 0.03192 | 8.506e-05 | -6.6372e-06 | 0.012788 | 0.012873 | 0.012958 | 0.013044 | 0.013129 | 0.013122 | 0.013115 | 0.013109 | 0.013102 | 0.013095 | 0.013089 | 0.013082 | 0.013075 | 0.013069 | 0.013062 | 0.013056 | 0.013049 | 0.013042 | 0.013036 | 0.013029
| HSM002-155422817 | 9 | 9 | 0.0057798 | 0 | 0.0070609 | 0 | 0.0062478 | 0 | 3.6602e-05 | -4.0656e-05 | 0.0069145 | 0.0069511 | 0.0069877 | 0.0070243 | 0.0070609 | 0.0070202 | 0.0069796 | 0.0069389 | 0.0068983 | 0.0068576 | 0.006817 | 0.0067763 | 0.0067356 | 0.006695 | 0.0066543 | 0.0066137 | 0.006573 | 0.0065324 | 0.0064917 | 0.0064511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-157400246 | 8 | 8 | 0.00065269 | 0 | 0.0008489 | 0 | 0.0008484 | 0 | 5.6061e-06 | -2.515e-08 | 0.00082648 | 0.00083209 | 0.00083769 | 0.0008433 | 0.0008489 | 0.00084888 | 0.00084885 | 0.00084883 | 0.0008488 | 0.00084878 | 0.00084875 | 0.00084873 | 0.0008487 | 0.00084868 | 0.00084865 | 0.00084863 | 0.0008486 | 0.00084858 | 0.00084855 | 0.00084853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-157400607 | 7 | 7 | 0.00089166 | 0 | 0.0010719 | 0 | 0.0010472 | 0 | 5.1502e-06 | -1.2378e-06 | 0.0010513 | 0.0010565 | 0.0010616 | 0.0010668 | 0.0010719 | 0.0010707 | 0.0010694 | 0.0010682 | 0.001067 | 0.0010657 | 0.0010645 | 0.0010633 | 0.001062 | 0.0010608 | 0.0010595 | 0.0010583 | 0.0010571 | 0.0010558 | 0.0010546 | 0.0010534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-157400755 | 26 | 26 | 0.0024601 | 0 | 0.0033095 | 0 | 0.0032191 | 0 | 2.4269e-05 | -4.5185e-06 | 0.0032124 | 0.0032367 | 0.0032609 | 0.0032852 | 0.0033095 | 0.003305 | 0.0033004 | 0.0032959 | 0.0032914 | 0.0032869 | 0.0032824 | 0.0032779 | 0.0032733 | 0.0032688 | 0.0032643 | 0.0032598 | 0.0032553 | 0.0032507 | 0.0032462 | 0.0032417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-157998943 | 19 | 19 | 0.00020349 | 0 | 0.00024659 | 0 | 0.00022 | 0 | 1.2312e-06 | -1.3292e-06 | 0.00024166 | 0.00024289 | 0.00024412 | 0.00024535 | 0.00024659 | 0.00024526 | 0.00024393 | 0.0002426 | 0.00024127 | 0.00023994 | 0.00023861 | 0.00023728 | 0.00023595 | 0.00023462 | 0.00023329 | 0.00023196 | 0.00023064 | 0.00022931 | 0.00022798 | 0.00022665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-157999372 | 28 | 28 | 0.00073147 | 0 | 0.0009183 | 0 | 0.00087482 | 0 | 5.3382e-06 | -2.1743e-06 | 0.00089695 | 0.00090229 | 0.00090763 | 0.00091297 | 0.0009183 | 0.00091613 | 0.00091396 | 0.00091178 | 0.00090961 | 0.00090743 | 0.00090526 | 0.00090308 | 0.00090091 | 0.00089874 | 0.00089656 | 0.00089439 | 0.00089221 | 0.00089004 | 0.00088786 | 0.00088569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-157999534 | 12 | 12 | 0.00019458 | 0 | 0.00024426 | 0 | 0.00023888 | 0 | 1.4194e-06 | -2.691e-07 | 0.00023858 | 0.00024 | 0.00024142 | 0.00024284 | 0.00024426 | 0.00024399 | 0.00024372 | 0.00024345 | 0.00024318 | 0.00024291 | 0.00024265 | 0.00024238 | 0.00024211 | 0.00024184 | 0.00024157 | 0.0002413 | 0.00024103 | 0.00024076 | 0.00024049 | 0.00024022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-158058496 | 46 | 46 | 2.06e-05 | 0 | 2.24e-05 | 0 | 2.12e-05 | 0 | 5.1429e-08 | -6e-08 | 2.2194e-05 | 2.2246e-05 | 2.2297e-05 | 2.2349e-05 | 2.24e-05 | 2.234e-05 | 2.228e-05 | 2.222e-05 | 2.216e-05 | 2.21e-05 | 2.204e-05 | 2.198e-05 | 2.192e-05 | 2.186e-05 | 2.18e-05 | 2.174e-05 | 2.168e-05 | 2.162e-05 | 2.156e-05 | 2.15e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-158058597 | 22 | 22 | 0.00030545 | 0 | 0.00036943 | 0 | 0.00035155 | 0 | 1.8281e-06 | -8.9425e-07 | 0.00036212 | 0.00036395 | 0.00036578 | 0.00036761 | 0.00036943 | 0.00036854 | 0.00036765 | 0.00036675 | 0.00036586 | 0.00036496 | 0.00036407 | 0.00036317 | 0.00036228 | 0.00036139 | 0.00036049 | 0.0003596 | 0.0003587 | 0.00035781 | 0.00035691 | 0.00035602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-158110114 | 11 | 11 | 0.0019508 | 0 | 0.0023829 | 0 | 0.0021683 | 0 | 1.2346e-05 | -1.0731e-05 | 0.0023335 | 0.0023459 | 0.0023582 | 0.0023706 | 0.0023829 | 0.0023722 | 0.0023615 | 0.0023507 | 0.00234 | 0.0023293 | 0.0023185 | 0.0023078 | 0.0022971 | 0.0022863 | 0.0022756 | 0.0022649 | 0.0022541 | 0.0022434 | 0.0022327 | 0.0022219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-158110202 | 5 | 5 | 0.00038904 | 0 | 0.0004719 | 0 | 0.00042518 | 0 | 2.3674e-06 | -2.3359e-06 | 0.00046243 | 0.0004648 | 0.00046717 | 0.00046953 | 0.0004719 | 0.00046957 | 0.00046723 | 0.00046489 | 0.00046256 | 0.00046022 | 0.00045789 | 0.00045555 | 0.00045321 | 0.00045088 | 0.00044854 | 0.00044621 | 0.00044387 | 0.00044153 | 0.0004392 | 0.00043686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-158110374 | 5 | 5 | 0.001777 | 0 | 0.0021715 | 0 | 0.0019428 | 0 | 1.1273e-05 | -1.1437e-05 | 0.0021264 | 0.0021377 | 0.002149 | 0.0021603 | 0.0021715 | 0.0021601 | 0.0021487 | 0.0021372 | 0.0021258 | 0.0021144 | 0.0021029 | 0.0020915 | 0.00208 | 0.0020686 | 0.0020572 | 0.0020457 | 0.0020343 | 0.0020229 | 0.0020114 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-158110591 | 9 | 9 | 0.00043973 | 0 | 0.00054626 | 0 | 0.00048755 | 0 | 3.0439e-06 | -2.9354e-06 | 0.00053409 | 0.00053713 | 0.00054017 | 0.00054322 | 0.00054626 | 0.00054333 | 0.00054039 | 0.00053745 | 0.00053452 | 0.00053158 | 0.00052865 | 0.00052571 | 0.00052278 | 0.00051984 | 0.00051691 | 0.00051397 | 0.00051104 | 0.0005081 | 0.00050517 | 0.00050223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-158110691 | 36 | 36 | 0.0040301 | 0 | 0.0049666 | 0 | 0.0049748 | 0 | 2.6759e-05 | 4.086e-07 | 0.0048596 | 0.0048863 | 0.0049131 | 0.0049399 | 0.0049666 | 0.004967 | 0.0049674 | 0.0049678 | 0.0049683 | 0.0049687 | 0.0049691 | 0.0049695 | 0.0049699 | 0.0049703 | 0.0049707 | 0.0049711 | 0.0049715 | 0.0049719 | 0.0049723 | 0.0049728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-158126654 | 11 | 11 | 0.0025346 | 0 | 0.0033336 | 0 | 0.0033362 | 0 | 2.2827e-05 | 1.335e-07 | 0.0032423 | 0.0032651 | 0.0032879 | 0.0033107 | 0.0033336 | 0.0033337 | 0.0033338 | 0.003334 | 0.0033341 | 0.0033342 | 0.0033344 | 0.0033345 | 0.0033346 | 0.0033348 | 0.0033349 | 0.003335 | 0.0033352 | 0.0033353 | 0.0033354 | 0.0033356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-158165458 | 30 | 30 | 0.018341 | 0 | 0.021687 | 0 | 0.021322 | 0 | 9.5622e-05 | -1.8282e-05 | 0.021305 | 0.0214 | 0.021496 | 0.021592 | 0.021687 | 0.021669 | 0.021651 | 0.021632 | 0.021614 | 0.021596 | 0.021578 | 0.021559 | 0.021541 | 0.021523 | 0.021504 | 0.021486 | 0.021468 | 0.02145 | 0.021431 | 0.021413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-158165593 | 16 | 16 | 7.21e-06 | 0 | 9.31e-06 | 0 | 9.31e-06 | 0 | 6e-08 | 0 | 9.07e-06 | 9.13e-06 | 9.19e-06 | 9.25e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 9.31e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-163503065 | 23 | 23 | 0.00016053 | 0 | 0.00019959 | 0 | 0.0001836 | 0 | 1.1161e-06 | -7.9955e-07 | 0.00019513 | 0.00019624 | 0.00019736 | 0.00019847 | 0.00019959 | 0.00019879 | 0.00019799 | 0.00019719 | 0.00019639 | 0.00019559 | 0.00019479 | 0.00019399 | 0.00019319 | 0.00019239 | 0.00019159 | 0.00019079 | 0.00019 | 0.0001892 | 0.0001884 | 0.0001876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-163560034 | 63 | 63 | 0.0036186 | 0 | 0.0044044 | 0 | 0.0039543 | 0 | 2.2453e-05 | -2.2508e-05 | 0.0043146 | 0.0043371 | 0.0043595 | 0.004382 | 0.0044044 | 0.0043819 | 0.0043594 | 0.0043369 | 0.0043144 | 0.0042919 | 0.0042694 | 0.0042469 | 0.0042244 | 0.0042019 | 0.0041794 | 0.0041569 | 0.0041343 | 0.0041118 | 0.0040893 | 0.0040668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-24600694 | 531 | 319 | 0.011965 | 0.0044393 | 0.014557 | 0.0054005 | 0.013903 | 0.0050336 | 7.4056e-05 | -3.2735e-05 | 0.014261 | 0.014335 | 0.014409 | 0.014483 | 0.014557 | 0.014525 | 0.014492 | 0.014459 | 0.014426 | 0.014394 | 0.014361 | 0.014328 | 0.014296 | 0.014263 | 0.01423 | 0.014197 | 0.014165 | 0.014132 | 0.014099 | 0.014066 | 2.7463e-05 | -1.8346e-05 | 0.0052907 | 0.0053181 | 0.0053456 | 0.0053731 | 0.0054005 | 0.0053822 | 0.0053638 | 0.0053455 | 0.0053271 | 0.0053088 | 0.0052905 | 0.0052721 | 0.0052538 | 0.0052354 | 0.0052171 | 0.0051987 | 0.0051804 | 0.005162 | 0.0051437 | 0.0051253
| HSM002-24601420 | 1024 | 319 | 0.013844 | 0.0029485 | 0.016486 | 0.0035461 | 0.016142 | 0.0034856 | 7.5484e-05 | -1.7198e-05 | 0.016184 | 0.016259 | 0.016335 | 0.01641 | 0.016486 | 0.016468 | 0.016451 | 0.016434 | 0.016417 | 0.0164 | 0.016382 | 0.016365 | 0.016348 | 0.016331 | 0.016314 | 0.016296 | 0.016279 | 0.016262 | 0.016245 | 0.016228 | 1.7076e-05 | -3.0282e-06 | 0.0034778 | 0.0034949 | 0.003512 | 0.003529 | 0.0035461 | 0.0035431 | 0.0035401 | 0.003537 | 0.003534 | 0.003531 | 0.0035279 | 0.0035249 | 0.0035219 | 0.0035189 | 0.0035158 | 0.0035128 | 0.0035098 | 0.0035068 | 0.0035037 | 0.0035007
| HSM003-15416492 | 1602 | 153 | 0.018973 | 1.45e-05 | 0.026645 | 2.16e-05 | 0.02758 | 2.28e-05 | 0.0002192 | 4.6739e-05 | 0.025768 | 0.025987 | 0.026206 | 0.026426 | 0.026645 | 0.026692 | 0.026738 | 0.026785 | 0.026832 | 0.026878 | 0.026925 | 0.026972 | 0.027019 | 0.027065 | 0.027112 | 0.027159 | 0.027206 | 0.027252 | 0.027299 | 0.027346 | 2.0286e-07 | 6e-08 | 2.0789e-05 | 2.0991e-05 | 2.1194e-05 | 2.1397e-05 | 2.16e-05 | 2.166e-05 | 2.172e-05 | 2.178e-05 | 2.184e-05 | 2.19e-05 | 2.196e-05 | 2.202e-05 | 2.208e-05 | 2.214e-05 | 2.22e-05 | 2.226e-05 | 2.232e-05 | 2.238e-05 | 2.244e-05 | 2.25e-05
| HSM003-160653285 | 29 | 29 | 0.0047363 | 0 | 0.0069449 | 0 | 0.0065407 | 0 | 6.3105e-05 | -2.0212e-05 | 0.0066925 | 0.0067556 | 0.0068187 | 0.0068818 | 0.0069449 | 0.0069247 | 0.0069045 | 0.0068843 | 0.0068641 | 0.0068439 | 0.0068237 | 0.0068035 | 0.0067833 | 0.006763 | 0.0067428 | 0.0067226 | 0.0067024 | 0.0066822 | 0.006662 | 0.0066418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-160653643 | 22 | 22 | 0.003319 | 0 | 0.0048414 | 0 | 0.0046172 | 0 | 4.3496e-05 | -1.1208e-05 | 0.0046674 | 0.0047109 | 0.0047544 | 0.0047979 | 0.0048414 | 0.0048302 | 0.004819 | 0.0048078 | 0.0047965 | 0.0047853 | 0.0047741 | 0.0047629 | 0.0047517 | 0.0047405 | 0.0047293 | 0.0047181 | 0.0047069 | 0.0046957 | 0.0046845 | 0.0046733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-160677450 | 21 | 21 | 0.0055774 | 0 | 0.0085007 | 0 | 0.0078911 | 0 | 8.3521e-05 | -3.0477e-05 | 0.0081666 | 0.0082501 | 0.0083336 | 0.0084171 | 0.0085007 | 0.0084702 | 0.0084397 | 0.0084092 | 0.0083788 | 0.0083483 | 0.0083178 | 0.0082873 | 0.0082568 | 0.0082264 | 0.0081959 | 0.0081654 | 0.0081349 | 0.0081045 | 0.008074 | 0.0080435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-160677580 | 23 | 23 | 0.0020058 | 0 | 0.0034147 | 0 | 0.0032503 | 0 | 4.0255e-05 | -8.222e-06 | 0.0032537 | 0.0032939 | 0.0033342 | 0.0033745 | 0.0034147 | 0.0034065 | 0.0033983 | 0.00339 | 0.0033818 | 0.0033736 | 0.0033654 | 0.0033572 | 0.0033489 | 0.0033407 | 0.0033325 | 0.0033243 | 0.003316 | 0.0033078 | 0.0032996 | 0.0032914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-160677831 | 36 | 36 | 0.0022986 | 0 | 0.0034513 | 0 | 0.0034937 | 0 | 3.2932e-05 | 2.1228e-06 | 0.0033195 | 0.0033525 | 0.0033854 | 0.0034183 | 0.0034513 | 0.0034534 | 0.0034555 | 0.0034576 | 0.0034597 | 0.0034619 | 0.003464 | 0.0034661 | 0.0034682 | 0.0034704 | 0.0034725 | 0.0034746 | 0.0034767 | 0.0034789 | 0.003481 | 0.0034831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-160683184 | 19 | 19 | 0.0037143 | 0 | 0.0058303 | 0 | 0.0053687 | 0 | 6.0458e-05 | -2.3079e-05 | 0.0055885 | 0.0056489 | 0.0057094 | 0.0057698 | 0.0058303 | 0.0058072 | 0.0057841 | 0.0057611 | 0.005738 | 0.0057149 | 0.0056918 | 0.0056688 | 0.0056457 | 0.0056226 | 0.0055995 | 0.0055764 | 0.0055534 | 0.0055303 | 0.0055072 | 0.0054841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-160683337 | 26 | 26 | 0.0031446 | 0 | 0.0046144 | 0 | 0.0044427 | 0 | 4.1996e-05 | -8.5848e-06 | 0.0044465 | 0.0044884 | 0.0045304 | 0.0045724 | 0.0046144 | 0.0046058 | 0.0045973 | 0.0045887 | 0.0045801 | 0.0045715 | 0.0045629 | 0.0045543 | 0.0045458 | 0.0045372 | 0.0045286 | 0.00452 | 0.0045114 | 0.0045028 | 0.0044942 | 0.0044857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-160683747 | 33 | 33 | 0.0034478 | 0 | 0.0054651 | 0 | 0.0051366 | 0 | 5.7637e-05 | -1.6428e-05 | 0.0052346 | 0.0052922 | 0.0053498 | 0.0054075 | 0.0054651 | 0.0054487 | 0.0054322 | 0.0054158 | 0.0053994 | 0.005383 | 0.0053665 | 0.0053501 | 0.0053337 | 0.0053173 | 0.0053008 | 0.0052844 | 0.005268 | 0.0052515 | 0.0052351 | 0.0052187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-160720939 | 33 | 33 | 0.0050402 | 0 | 0.0071136 | 0 | 0.0068008 | 0 | 5.924e-05 | -1.5641e-05 | 0.0068766 | 0.0069359 | 0.0069951 | 0.0070543 | 0.0071136 | 0.0070979 | 0.0070823 | 0.0070667 | 0.007051 | 0.0070354 | 0.0070197 | 0.0070041 | 0.0069885 | 0.0069728 | 0.0069572 | 0.0069415 | 0.0069259 | 0.0069103 | 0.0068946 | 0.006879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-160721106 | 21 | 21 | 0.0035809 | 0 | 0.0053812 | 0 | 0.0050293 | 0 | 5.1438e-05 | -1.7594e-05 | 0.0051754 | 0.0052269 | 0.0052783 | 0.0053297 | 0.0053812 | 0.0053636 | 0.005346 | 0.0053284 | 0.0053108 | 0.0052932 | 0.0052756 | 0.005258 | 0.0052404 | 0.0052228 | 0.0052052 | 0.0051876 | 0.0051701 | 0.0051525 | 0.0051349 | 0.0051173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-160828901 | 9 | 9 | 0.0023618 | 0 | 0.0038717 | 0 | 0.00371 | 0 | 4.314e-05 | -8.0825e-06 | 0.0036991 | 0.0037423 | 0.0037854 | 0.0038285 | 0.0038717 | 0.0038636 | 0.0038555 | 0.0038474 | 0.0038394 | 0.0038313 | 0.0038232 | 0.0038151 | 0.003807 | 0.0037989 | 0.0037909 | 0.0037828 | 0.0037747 | 0.0037666 | 0.0037585 | 0.0037505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-160875785 | 25 | 25 | 0.0029156 | 0 | 0.0040066 | 0 | 0.0039985 | 0 | 3.1173e-05 | -4.073e-07 | 0.003882 | 0.0039131 | 0.0039443 | 0.0039755 | 0.0040066 | 0.0040062 | 0.0040058 | 0.0040054 | 0.004005 | 0.0040046 | 0.0040042 | 0.0040038 | 0.0040034 | 0.004003 | 0.0040026 | 0.0040022 | 0.0040018 | 0.0040013 | 0.0040009 | 0.0040005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-160931238 | 24 | 24 | 0.0046756 | 0 | 0.0073628 | 0 | 0.0068151 | 0 | 7.6778e-05 | -2.7387e-05 | 0.0070557 | 0.0071325 | 0.0072092 | 0.007286 | 0.0073628 | 0.0073354 | 0.007308 | 0.0072806 | 0.0072533 | 0.0072259 | 0.0071985 | 0.0071711 | 0.0071437 | 0.0071163 | 0.0070889 | 0.0070615 | 0.0070342 | 0.0070068 | 0.0069794 | 0.006952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-161008360 | 32 | 32 | 0.0033721 | 0 | 0.0048889 | 0 | 0.0047955 | 0 | 4.334e-05 | -4.6711e-06 | 0.0047156 | 0.0047589 | 0.0048023 | 0.0048456 | 0.0048889 | 0.0048843 | 0.0048796 | 0.0048749 | 0.0048703 | 0.0048656 | 0.0048609 | 0.0048562 | 0.0048516 | 0.0048469 | 0.0048422 | 0.0048376 | 0.0048329 | 0.0048282 | 0.0048236 | 0.0048189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-161008735 | 24 | 24 | 0.0017712 | 0 | 0.003025 | 0 | 0.0028807 | 0 | 3.5821e-05 | -7.2138e-06 | 0.0028817 | 0.0029175 | 0.0029533 | 0.0029892 | 0.003025 | 0.0030178 | 0.0030106 | 0.0030033 | 0.0029961 | 0.0029889 | 0.0029817 | 0.0029745 | 0.0029673 | 0.0029601 | 0.0029528 | 0.0029456 | 0.0029384 | 0.0029312 | 0.002924 | 0.0029168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-161094121 | 3 | 3 | 6.74e-06 | 0 | 1.09e-05 | 0 | 1.03e-05 | 0 | 1.1886e-07 | -3e-08 | 1.0425e-05 | 1.0543e-05 | 1.0662e-05 | 1.0781e-05 | 1.09e-05 | 1.087e-05 | 1.084e-05 | 1.081e-05 | 1.078e-05 | 1.075e-05 | 1.072e-05 | 1.069e-05 | 1.066e-05 | 1.063e-05 | 1.06e-05 | 1.057e-05 | 1.054e-05 | 1.051e-05 | 1.048e-05 | 1.045e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-161094233 | 6 | 6 | 0.0020433 | 0 | 0.0031207 | 0 | 0.0029167 | 0 | 3.0784e-05 | -1.0199e-05 | 0.0029976 | 0.0030283 | 0.0030591 | 0.0030899 | 0.0031207 | 0.0031105 | 0.0031003 | 0.0030901 | 0.0030799 | 0.0030697 | 0.0030595 | 0.0030493 | 0.0030391 | 0.0030289 | 0.0030187 | 0.0030085 | 0.0029983 | 0.0029881 | 0.0029779 | 0.0029677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-163378469 | 23 | 23 | 0.0033071 | 0 | 0.0055308 | 0 | 0.0053007 | 0 | 6.3534e-05 | -1.1505e-05 | 0.0052766 | 0.0053402 | 0.0054037 | 0.0054672 | 0.0055308 | 0.0055193 | 0.0055078 | 0.0054963 | 0.0054848 | 0.0054732 | 0.0054617 | 0.0054502 | 0.0054387 | 0.0054272 | 0.0054157 | 0.0054042 | 0.0053927 | 0.0053812 | 0.0053697 | 0.0053582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-163378579 | 14 | 14 | 0.0031042 | 0 | 0.0048391 | 0 | 0.0046866 | 0 | 4.957e-05 | -7.6236e-06 | 0.0046408 | 0.0046904 | 0.00474 | 0.0047895 | 0.0048391 | 0.0048315 | 0.0048239 | 0.0048162 | 0.0048086 | 0.004801 | 0.0047934 | 0.0047857 | 0.0047781 | 0.0047705 | 0.0047629 | 0.0047552 | 0.0047476 | 0.00474 | 0.0047324 | 0.0047247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-164469812 | 6 | 6 | 0.00081342 | 0 | 0.0012725 | 0 | 0.0012018 | 0 | 1.3117e-05 | -3.5348e-06 | 0.0012201 | 0.0012332 | 0.0012463 | 0.0012594 | 0.0012725 | 0.001269 | 0.0012655 | 0.0012619 | 0.0012584 | 0.0012549 | 0.0012513 | 0.0012478 | 0.0012442 | 0.0012407 | 0.0012372 | 0.0012336 | 0.0012301 | 0.0012266 | 0.001223 | 0.0012195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-164470113 | 5 | 5 | 0.00069273 | 0 | 0.0010699 | 0 | 0.00098872 | 0 | 1.0778e-05 | -4.0612e-06 | 0.0010268 | 0.0010376 | 0.0010484 | 0.0010592 | 0.0010699 | 0.0010659 | 0.0010618 | 0.0010578 | 0.0010537 | 0.0010496 | 0.0010456 | 0.0010415 | 0.0010375 | 0.0010334 | 0.0010293 | 0.0010253 | 0.0010212 | 0.0010172 | 0.0010131 | 0.001009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM003-24600316 | 587 | 418 | 0.0037266 | 0.0030638 | 0.0052232 | 0.0044529 | 0.0050662 | 0.0043732 | 4.276e-05 | -7.8484e-06 | 0.0050522 | 0.0050949 | 0.0051377 | 0.0051805 | 0.0052232 | 0.0052154 | 0.0052075 | 0.0051997 | 0.0051918 | 0.005184 | 0.0051761 | 0.0051683 | 0.0051604 | 0.0051526 | 0.0051447 | 0.0051369 | 0.005129 | 0.0051212 | 0.0051133 | 0.0051055 | 3.9689e-05 | -3.9869e-06 | 0.0042941 | 0.0043338 | 0.0043735 | 0.0044132 | 0.0044529 | 0.0044489 | 0.0044449 | 0.0044409 | 0.004437 | 0.004433 | 0.004429 | 0.004425 | 0.004421 | 0.004417 | 0.004413 | 0.004409 | 0.0044051 | 0.0044011 | 0.0043971 | 0.0043931
| HSM003-24601084 | 1003 | 260 | 0.015327 | 0.006433 | 0.020363 | 0.0098202 | 0.019005 | 0.0091634 | 0.0001439 | -6.7913e-05 | 0.019788 | 0.019932 | 0.020076 | 0.020219 | 0.020363 | 0.020295 | 0.020228 | 0.02016 | 0.020092 | 0.020024 | 0.019956 | 0.019888 | 0.01982 | 0.019752 | 0.019684 | 0.019616 | 0.019548 | 0.01948 | 0.019413 | 0.019345 | 9.6776e-05 | -3.2838e-05 | 0.0094331 | 0.0095298 | 0.0096266 | 0.0097234 | 0.0098202 | 0.0097873 | 0.0097545 | 0.0097216 | 0.0096888 | 0.009656 | 0.0096231 | 0.0095903 | 0.0095575 | 0.0095246 | 0.0094918 | 0.0094589 | 0.0094261 | 0.0093933 | 0.0093604 | 0.0093276
| HSM003-24601658 | 132 | 21 | 0.0030956 | 0.0031627 | 0.0045429 | 0.0048511 | 0.0042206 | 0.0045083 | 4.1351e-05 | -1.6113e-05 | 0.0043775 | 0.0044188 | 0.0044602 | 0.0045015 | 0.0045429 | 0.0045268 | 0.0045107 | 0.0044946 | 0.0044784 | 0.0044623 | 0.0044462 | 0.0044301 | 0.004414 | 0.0043979 | 0.0043818 | 0.0043657 | 0.0043495 | 0.0043334 | 0.0043173 | 0.0043012 | 4.8242e-05 | -1.7143e-05 | 0.0046582 | 0.0047064 | 0.0047546 | 0.0048029 | 0.0048511 | 0.004834 | 0.0048168 | 0.0047997 | 0.0047825 | 0.0047654 | 0.0047483 | 0.0047311 | 0.004714 | 0.0046968 | 0.0046797 | 0.0046625 | 0.0046454 | 0.0046283 | 0.0046111 | 0.004594
| HSM003-24601840 | 1438 | 270 | 0.0016794 | 0.002566 | 0.0022101 | 0.0037932 | 0.0020431 | 0.0035163 | 1.5164e-05 | -8.3505e-06 | 0.0021495 | 0.0021646 | 0.0021798 | 0.002195 | 0.0022101 | 0.0022018 | 0.0021934 | 0.0021851 | 0.0021767 | 0.0021684 | 0.00216 | 0.0021517 | 0.0021433 | 0.002135 | 0.0021266 | 0.0021183 | 0.0021099 | 0.0021016 | 0.0020932 | 0.0020849 | 3.5063e-05 | -1.3848e-05 | 0.003653 | 0.003688 | 0.0037231 | 0.0037581 | 0.0037932 | 0.0037794 | 0.0037655 | 0.0037517 | 0.0037378 | 0.003724 | 0.0037101 | 0.0036963 | 0.0036824 | 0.0036686 | 0.0036547 | 0.0036409 | 0.003627 | 0.0036132 | 0.0035993 | 0.0035855
| HSM004-15416655 | 2063 | 442 | 0.022949 | 0.014066 | 0.031359 | 0.019427 | 0.030561 | 0.018992 | 0.0002403 | -3.9899e-05 | 0.030398 | 0.030638 | 0.030879 | 0.031119 | 0.031359 | 0.031319 | 0.03128 | 0.03124 | 0.0312 | 0.03116 | 0.03112 | 0.03108 | 0.03104 | 0.031 | 0.03096 | 0.03092 | 0.030881 | 0.030841 | 0.030801 | 0.030761 | 0.00015319 | -2.1771e-05 | 0.018815 | 0.018968 | 0.019121 | 0.019274 | 0.019427 | 0.019406 | 0.019384 | 0.019362 | 0.01934 | 0.019319 | 0.019297 | 0.019275 | 0.019253 | 0.019231 | 0.01921 | 0.019188 | 0.019166 | 0.019144 | 0.019123 | 0.019101
| HSM004-155422230 | 21 | 21 | 0.00030786 | 0 | 0.00038277 | 0 | 0.00033799 | 0 | 2.1402e-06 | -2.2389e-06 | 0.00037421 | 0.00037635 | 0.00037849 | 0.00038063 | 0.00038277 | 0.00038053 | 0.00037829 | 0.00037605 | 0.00037382 | 0.00037158 | 0.00036934 | 0.0003671 | 0.00036486 | 0.00036262 | 0.00036038 | 0.00035814 | 0.0003559 | 0.00035367 | 0.00035143 | 0.00034919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-159429141 | 33 | 33 | 0.0022424 | 0 | 0.0030237 | 0 | 0.0031014 | 0 | 2.2321e-05 | 3.8849e-06 | 0.0029344 | 0.0029567 | 0.002979 | 0.0030014 | 0.0030237 | 0.0030276 | 0.0030315 | 0.0030353 | 0.0030392 | 0.0030431 | 0.003047 | 0.0030509 | 0.0030548 | 0.0030586 | 0.0030625 | 0.0030664 | 0.0030703 | 0.0030742 | 0.0030781 | 0.003082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-159429252 | 33 | 33 | 0.0031794 | 0 | 0.0038761 | 0 | 0.0035684 | 0 | 1.9907e-05 | -1.5388e-05 | 0.0037965 | 0.0038164 | 0.0038363 | 0.0038562 | 0.0038761 | 0.0038608 | 0.0038454 | 0.00383 | 0.0038146 | 0.0037992 | 0.0037838 | 0.0037684 | 0.003753 | 0.0037376 | 0.0037223 | 0.0037069 | 0.0036915 | 0.0036761 | 0.0036607 | 0.0036453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-159452345 | 29 | 29 | 0.006188 | 0 | 0.0078693 | 0 | 0.0077581 | 0 | 4.8039e-05 | -5.563e-06 | 0.0076772 | 0.0077252 | 0.0077733 | 0.0078213 | 0.0078693 | 0.0078638 | 0.0078582 | 0.0078526 | 0.0078471 | 0.0078415 | 0.007836 | 0.0078304 | 0.0078248 | 0.0078193 | 0.0078137 | 0.0078081 | 0.0078026 | 0.007797 | 0.0077915 | 0.0077859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-159452484 | 6 | 6 | 0.001125 | 0 | 0.0015333 | 0 | 0.001547 | 0 | 1.1666e-05 | 6.8145e-07 | 0.0014867 | 0.0014983 | 0.00151 | 0.0015217 | 0.0015333 | 0.001534 | 0.0015347 | 0.0015354 | 0.0015361 | 0.0015368 | 0.0015374 | 0.0015381 | 0.0015388 | 0.0015395 | 0.0015402 | 0.0015408 | 0.0015415 | 0.0015422 | 0.0015429 | 0.0015436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-159452607 | 31 | 31 | 0.00078037 | 0 | 0.00088509 | 0 | 0.00081342 | 0 | 2.992e-06 | -3.5834e-06 | 0.00087312 | 0.00087612 | 0.00087911 | 0.0008821 | 0.00088509 | 0.00088151 | 0.00087793 | 0.00087434 | 0.00087076 | 0.00086718 | 0.00086359 | 0.00086001 | 0.00085642 | 0.00085284 | 0.00084926 | 0.00084567 | 0.00084209 | 0.00083851 | 0.00083492 | 0.00083134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-159452714 | 9 | 9 | 0.00059536 | 0 | 0.00075614 | 0 | 0.00077116 | 0 | 4.5937e-06 | 7.5095e-07 | 0.00073777 | 0.00074236 | 0.00074695 | 0.00075155 | 0.00075614 | 0.00075689 | 0.00075764 | 0.00075839 | 0.00075915 | 0.0007599 | 0.00076065 | 0.0007614 | 0.00076215 | 0.0007629 | 0.00076365 | 0.0007644 | 0.00076515 | 0.0007659 | 0.00076666 | 0.00076741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-160294257 | 31 | 31 | 0.0096998 | 0 | 0.012152 | 0 | 0.012163 | 0 | 7.0056e-05 | 5.4225e-07 | 0.011872 | 0.011942 | 0.012012 | 0.012082 | 0.012152 | 0.012152 | 0.012153 | 0.012153 | 0.012154 | 0.012154 | 0.012155 | 0.012156 | 0.012156 | 0.012157 | 0.012157 | 0.012158 | 0.012158 | 0.012159 | 0.012159 | 0.01216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-160411068 | 17 | 17 | 0.0029556 | 0 | 0.0037499 | 0 | 0.0037449 | 0 | 2.2694e-05 | -2.4955e-07 | 0.0036591 | 0.0036818 | 0.0037045 | 0.0037272 | 0.0037499 | 0.0037496 | 0.0037494 | 0.0037491 | 0.0037489 | 0.0037486 | 0.0037484 | 0.0037481 | 0.0037479 | 0.0037476 | 0.0037474 | 0.0037471 | 0.0037469 | 0.0037466 | 0.0037464 | 0.0037461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-160411194 | 37 | 37 | 0.001501 | 0 | 0.0020655 | 0 | 0.0017275 | 0 | 1.6129e-05 | -1.6901e-05 | 0.002001 | 0.0020171 | 0.0020332 | 0.0020494 | 0.0020655 | 0.0020486 | 0.0020317 | 0.0020148 | 0.0019979 | 0.001981 | 0.0019641 | 0.0019472 | 0.0019303 | 0.0019134 | 0.0018965 | 0.0018796 | 0.0018627 | 0.0018458 | 0.0018289 | 0.001812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-160424470 | 60 | 60 | 0.0080293 | 0 | 0.010156 | 0 | 0.010186 | 0 | 6.0768e-05 | 1.4806e-06 | 0.0099131 | 0.0099738 | 0.010035 | 0.010095 | 0.010156 | 0.010158 | 0.010159 | 0.010161 | 0.010162 | 0.010164 | 0.010165 | 0.010167 | 0.010168 | 0.010169 | 0.010171 | 0.010172 | 0.010174 | 0.010175 | 0.010177 | 0.010178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-160437576 | 15 | 15 | 0.002987 | 0 | 0.0039362 | 0 | 0.0035215 | 0 | 2.7119e-05 | -2.0734e-05 | 0.0038277 | 0.0038548 | 0.0038819 | 0.003909 | 0.0039362 | 0.0039154 | 0.0038947 | 0.0038739 | 0.0038532 | 0.0038325 | 0.0038117 | 0.003791 | 0.0037703 | 0.0037495 | 0.0037288 | 0.0037081 | 0.0036873 | 0.0036666 | 0.0036459 | 0.0036251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-160437658 | 35 | 35 | 0.0026154 | 0 | 0.0032937 | 0 | 0.0029489 | 0 | 1.9378e-05 | -1.7238e-05 | 0.0032162 | 0.0032355 | 0.0032549 | 0.0032743 | 0.0032937 | 0.0032764 | 0.0032592 | 0.0032419 | 0.0032247 | 0.0032075 | 0.0031902 | 0.003173 | 0.0031558 | 0.0031385 | 0.0031213 | 0.003104 | 0.0030868 | 0.0030696 | 0.0030523 | 0.0030351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-160438050 | 38 | 38 | 0.0080054 | 0 | 0.0106 | 0 | 0.010836 | 0 | 7.4138e-05 | 1.1788e-05 | 0.010304 | 0.010378 | 0.010452 | 0.010526 | 0.0106 | 0.010612 | 0.010624 | 0.010636 | 0.010647 | 0.010659 | 0.010671 | 0.010683 | 0.010695 | 0.010706 | 0.010718 | 0.01073 | 0.010742 | 0.010753 | 0.010765 | 0.010777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-160438389 | 28 | 28 | 0.0039583 | 0 | 0.0050756 | 0 | 0.0046699 | 0 | 3.1921e-05 | -2.0283e-05 | 0.0049479 | 0.0049798 | 0.0050117 | 0.0050436 | 0.0050756 | 0.0050553 | 0.005035 | 0.0050147 | 0.0049944 | 0.0049741 | 0.0049539 | 0.0049336 | 0.0049133 | 0.004893 | 0.0048727 | 0.0048524 | 0.0048322 | 0.0048119 | 0.0047916 | 0.0047713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-160438554 | 35 | 35 | 0.0045346 | 0 | 0.0056844 | 0 | 0.0049406 | 0 | 3.2853e-05 | -3.7191e-05 | 0.005553 | 0.0055859 | 0.0056187 | 0.0056516 | 0.0056844 | 0.0056472 | 0.00561 | 0.0055729 | 0.0055357 | 0.0054985 | 0.0054613 | 0.0054241 | 0.0053869 | 0.0053497 | 0.0053125 | 0.0052753 | 0.0052381 | 0.0052009 | 0.0051638 | 0.0051266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-160438797 | 24 | 24 | 1.23e-05 | 0 | 1.59e-05 | 0 | 1.39e-05 | 0 | 1.0286e-07 | -1e-07 | 1.5489e-05 | 1.5591e-05 | 1.5694e-05 | 1.5797e-05 | 1.59e-05 | 1.58e-05 | 1.57e-05 | 1.56e-05 | 1.55e-05 | 1.54e-05 | 1.53e-05 | 1.52e-05 | 1.51e-05 | 1.5e-05 | 1.49e-05 | 1.48e-05 | 1.47e-05 | 1.46e-05 | 1.45e-05 | 1.44e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-160439137 | 27 | 27 | 1.39e-05 | 0 | 1.79e-05 | 0 | 1.7e-05 | 0 | 1.1429e-07 | -4.5e-08 | 1.7443e-05 | 1.7557e-05 | 1.7671e-05 | 1.7786e-05 | 1.79e-05 | 1.7855e-05 | 1.781e-05 | 1.7765e-05 | 1.772e-05 | 1.7675e-05 | 1.763e-05 | 1.7585e-05 | 1.754e-05 | 1.7495e-05 | 1.745e-05 | 1.7405e-05 | 1.736e-05 | 1.7315e-05 | 1.727e-05 | 1.7225e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-163582339 | 34 | 34 | 0.01119 | 0 | 0.014961 | 0 | 0.013334 | 0 | 0.00010774 | -8.1358e-05 | 0.01453 | 0.014638 | 0.014746 | 0.014853 | 0.014961 | 0.01488 | 0.014798 | 0.014717 | 0.014636 | 0.014554 | 0.014473 | 0.014392 | 0.01431 | 0.014229 | 0.014147 | 0.014066 | 0.013985 | 0.013903 | 0.013822 | 0.013741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-163582585 | 6 | 6 | 4.77e-06 | 0 | 6.38e-06 | 0 | 5.6e-06 | 0 | 4.6e-08 | -3.9e-08 | 6.196e-06 | 6.242e-06 | 6.288e-06 | 6.334e-06 | 6.38e-06 | 6.341e-06 | 6.302e-06 | 6.263e-06 | 6.224e-06 | 6.185e-06 | 6.146e-06 | 6.107e-06 | 6.068e-06 | 6.029e-06 | 5.99e-06 | 5.951e-06 | 5.912e-06 | 5.873e-06 | 5.834e-06 | 5.795e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-163582753 | 5 | 5 | 9.06e-06 | 0 | 1.22e-05 | 0 | 1.18e-05 | 0 | 8.9714e-08 | -2e-08 | 1.1841e-05 | 1.1931e-05 | 1.2021e-05 | 1.211e-05 | 1.22e-05 | 1.218e-05 | 1.216e-05 | 1.214e-05 | 1.212e-05 | 1.21e-05 | 1.208e-05 | 1.206e-05 | 1.204e-05 | 1.202e-05 | 1.2e-05 | 1.198e-05 | 1.196e-05 | 1.194e-05 | 1.192e-05 | 1.19e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-163606098 | 40 | 40 | 0.014499 | 0 | 0.018865 | 0 | 0.018721 | 0 | 0.00012475 | -7.1975e-06 | 0.018366 | 0.018491 | 0.018615 | 0.01874 | 0.018865 | 0.018858 | 0.018851 | 0.018843 | 0.018836 | 0.018829 | 0.018822 | 0.018815 | 0.018807 | 0.0188 | 0.018793 | 0.018786 | 0.018779 | 0.018771 | 0.018764 | 0.018757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-163606269 | 8 | 8 | 0.00035978 | 0 | 0.00048088 | 0 | 0.00048729 | 0 | 3.4599e-06 | 3.2045e-07 | 0.00046704 | 0.0004705 | 0.00047396 | 0.00047742 | 0.00048088 | 0.0004812 | 0.00048152 | 0.00048184 | 0.00048216 | 0.00048248 | 0.0004828 | 0.00048312 | 0.00048344 | 0.00048376 | 0.00048408 | 0.0004844 | 0.00048472 | 0.00048504 | 0.00048537 | 0.00048569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-163794865 | 40 | 40 | 0.0011438 | 0 | 0.0015197 | 0 | 0.0013343 | 0 | 1.0739e-05 | -9.2674e-06 | 0.0014767 | 0.0014875 | 0.0014982 | 0.0015089 | 0.0015197 | 0.0015104 | 0.0015012 | 0.0014919 | 0.0014826 | 0.0014734 | 0.0014641 | 0.0014548 | 0.0014455 | 0.0014363 | 0.001427 | 0.0014177 | 0.0014085 | 0.0013992 | 0.0013899 | 0.0013807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-163794980 | 25 | 25 | 1.86e-05 | 0 | 2.47e-05 | 0 | 2.14e-05 | 0 | 1.7429e-07 | -1.65e-07 | 2.4003e-05 | 2.4177e-05 | 2.4351e-05 | 2.4526e-05 | 2.47e-05 | 2.4535e-05 | 2.437e-05 | 2.4205e-05 | 2.404e-05 | 2.3875e-05 | 2.371e-05 | 2.3545e-05 | 2.338e-05 | 2.3215e-05 | 2.305e-05 | 2.2885e-05 | 2.272e-05 | 2.2555e-05 | 2.239e-05 | 2.2225e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-163795111 | 38 | 38 | 3.81e-06 | 0 | 4.92e-06 | 0 | 4.52e-06 | 0 | 3.1714e-08 | -2e-08 | 4.7931e-06 | 4.8249e-06 | 4.8566e-06 | 4.8883e-06 | 4.92e-06 | 4.9e-06 | 4.88e-06 | 4.86e-06 | 4.84e-06 | 4.82e-06 | 4.8e-06 | 4.78e-06 | 4.76e-06 | 4.74e-06 | 4.72e-06 | 4.7e-06 | 4.68e-06 | 4.66e-06 | 4.64e-06 | 4.62e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-163795268 | 22 | 22 | 4.04e-05 | 0 | 5.31e-05 | 0 | 5.12e-05 | 0 | 3.6286e-07 | -9.5e-08 | 5.1649e-05 | 5.2011e-05 | 5.2374e-05 | 5.2737e-05 | 5.31e-05 | 5.3005e-05 | 5.291e-05 | 5.2815e-05 | 5.272e-05 | 5.2625e-05 | 5.253e-05 | 5.2435e-05 | 5.234e-05 | 5.2245e-05 | 5.215e-05 | 5.2055e-05 | 5.196e-05 | 5.1865e-05 | 5.177e-05 | 5.1675e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-24599744 | 263 | 81 | 0.0050686 | 0.0026352 | 0.0065478 | 0.0034477 | 0.0056316 | 0.0029475 | 4.226e-05 | -4.5806e-05 | 0.0063787 | 0.006421 | 0.0064632 | 0.0065055 | 0.0065478 | 0.0065019 | 0.0064561 | 0.0064103 | 0.0063645 | 0.0063187 | 0.0062729 | 0.0062271 | 0.0061813 | 0.0061355 | 0.0060897 | 0.0060439 | 0.0059981 | 0.0059523 | 0.0059065 | 0.0058607 | 2.3216e-05 | -2.5013e-05 | 0.0033549 | 0.0033781 | 0.0034013 | 0.0034245 | 0.0034477 | 0.0034227 | 0.0033977 | 0.0033727 | 0.0033477 | 0.0033227 | 0.0032977 | 0.0032726 | 0.0032476 | 0.0032226 | 0.0031976 | 0.0031726 | 0.0031476 | 0.0031226 | 0.0030975 | 0.0030725
| HSM004-24599758 | 391 | 151 | 0.0062466 | 0.0019384 | 0.0075707 | 0.0023709 | 0.00675 | 0.0021054 | 3.7831e-05 | -4.1034e-05 | 0.0074194 | 0.0074572 | 0.007495 | 0.0075329 | 0.0075707 | 0.0075297 | 0.0074886 | 0.0074476 | 0.0074066 | 0.0073655 | 0.0073245 | 0.0072835 | 0.0072424 | 0.0072014 | 0.0071603 | 0.0071193 | 0.0070783 | 0.0070372 | 0.0069962 | 0.0069552 | 1.2359e-05 | -1.3276e-05 | 0.0023215 | 0.0023339 | 0.0023462 | 0.0023586 | 0.0023709 | 0.0023577 | 0.0023444 | 0.0023311 | 0.0023178 | 0.0023046 | 0.0022913 | 0.002278 | 0.0022647 | 0.0022515 | 0.0022382 | 0.0022249 | 0.0022116 | 0.0021984 | 0.0021851 | 0.0021718
| HSM004-24604904 | 1510 | 590 | 0.010844 | 0.014425 | 0.013935 | 0.018702 | 0.014163 | 0.018982 | 8.8305e-05 | 1.1395e-05 | 0.013582 | 0.01367 | 0.013759 | 0.013847 | 0.013935 | 0.013947 | 0.013958 | 0.013969 | 0.013981 | 0.013992 | 0.014003 | 0.014015 | 0.014026 | 0.014038 | 0.014049 | 0.01406 | 0.014072 | 0.014083 | 0.014095 | 0.014106 | 0.00012222 | 1.3962e-05 | 0.018214 | 0.018336 | 0.018458 | 0.01858 | 0.018702 | 0.018716 | 0.01873 | 0.018744 | 0.018758 | 0.018772 | 0.018786 | 0.0188 | 0.018814 | 0.018828 | 0.018842 | 0.018856 | 0.01887 | 0.018884 | 0.018898 | 0.018912
| HSM004-76359867 | 21 | 21 | 0.0024363 | 0 | 0.0030572 | 0 | 0.0027363 | 0 | 1.774e-05 | -1.6044e-05 | 0.0029862 | 0.0030039 | 0.0030217 | 0.0030394 | 0.0030572 | 0.0030411 | 0.0030251 | 0.003009 | 0.002993 | 0.0029769 | 0.0029609 | 0.0029449 | 0.0029288 | 0.0029128 | 0.0028967 | 0.0028807 | 0.0028646 | 0.0028486 | 0.0028325 | 0.0028165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM004-96221391 | 51 | 51 | 0.0069329 | 0 | 0.0087623 | 0 | 0.0086394 | 0 | 5.2268e-05 | -6.1482e-06 | 0.0085533 | 0.0086055 | 0.0086578 | 0.0087101 | 0.0087623 | 0.0087562 | 0.00875 | 0.0087439 | 0.0087377 | 0.0087316 | 0.0087254 | 0.0087193 | 0.0087131 | 0.008707 | 0.0087008 | 0.0086947 | 0.0086885 | 0.0086824 | 0.0086763 | 0.0086701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM005-121050437 | 1355 | 1194 | 0.0056351 | 0.0042307 | 0.0076707 | 0.0062307 | 0.0078048 | 0.0064513 | 5.8159e-05 | 6.7079e-06 | 0.007438 | 0.0074962 | 0.0075543 | 0.0076125 | 0.0076707 | 0.0076774 | 0.0076841 | 0.0076908 | 0.0076975 | 0.0077042 | 0.0077109 | 0.0077176 | 0.0077243 | 0.007731 | 0.0077377 | 0.0077444 | 0.0077512 | 0.0077579 | 0.0077646 | 0.0077713 | 5.7142e-05 | 1.1029e-05 | 0.0060021 | 0.0060592 | 0.0061164 | 0.0061735 | 0.0062307 | 0.0062417 | 0.0062527 | 0.0062638 | 0.0062748 | 0.0062858 | 0.0062968 | 0.0063079 | 0.0063189 | 0.0063299 | 0.006341 | 0.006352 | 0.006363 | 0.0063741 | 0.0063851 | 0.0063961
| HSM005-15416442 | 1666 | 245 | 0.030157 | 0.0048621 | 0.039656 | 0.006804 | 0.039529 | 0.0068969 | 0.00027139 | -6.3408e-06 | 0.03857 | 0.038841 | 0.039113 | 0.039384 | 0.039656 | 0.039649 | 0.039643 | 0.039636 | 0.03963 | 0.039624 | 0.039617 | 0.039611 | 0.039605 | 0.039598 | 0.039592 | 0.039586 | 0.039579 | 0.039573 | 0.039567 | 0.03956 | 5.5483e-05 | 4.6442e-06 | 0.0065821 | 0.0066376 | 0.0066931 | 0.0067486 | 0.006804 | 0.0068087 | 0.0068133 | 0.006818 | 0.0068226 | 0.0068273 | 0.0068319 | 0.0068365 | 0.0068412 | 0.0068458 | 0.0068505 | 0.0068551 | 0.0068598 | 0.0068644 | 0.0068691 | 0.0068737
| HSM005-159947157 | 24 | 24 | 0.0069143 | 0 | 0.0095291 | 0 | 0.0091913 | 0 | 7.4708e-05 | -1.6887e-05 | 0.0092303 | 0.009305 | 0.0093797 | 0.0094544 | 0.0095291 | 0.0095122 | 0.0094953 | 0.0094784 | 0.0094615 | 0.0094447 | 0.0094278 | 0.0094109 | 0.009394 | 0.0093771 | 0.0093602 | 0.0093433 | 0.0093264 | 0.0093096 | 0.0092927 | 0.0092758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM005-160318639 | 16 | 16 | 0.0070794 | 0 | 0.010511 | 0 | 0.0099794 | 0 | 9.8036e-05 | -2.6566e-05 | 0.010119 | 0.010217 | 0.010315 | 0.010413 | 0.010511 | 0.010484 | 0.010458 | 0.010431 | 0.010404 | 0.010378 | 0.010351 | 0.010325 | 0.010298 | 0.010272 | 0.010245 | 0.010218 | 0.010192 | 0.010165 | 0.010139 | 0.010112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM005-160319214 | 20 | 20 | 0.0053319 | 0 | 0.0073787 | 0 | 0.007223 | 0 | 5.8482e-05 | -7.7869e-06 | 0.0071448 | 0.0072033 | 0.0072618 | 0.0073203 | 0.0073787 | 0.007371 | 0.0073632 | 0.0073554 | 0.0073476 | 0.0073398 | 0.007332 | 0.0073242 | 0.0073164 | 0.0073087 | 0.0073009 | 0.0072931 | 0.0072853 | 0.0072775 | 0.0072697 | 0.0072619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM005-160415406 | 32 | 32 | 0.0053685 | 0 | 0.0075984 | 0 | 0.007467 | 0 | 6.3711e-05 | -6.5699e-06 | 0.0073436 | 0.0074073 | 0.007471 | 0.0075347 | 0.0075984 | 0.0075918 | 0.0075853 | 0.0075787 | 0.0075721 | 0.0075656 | 0.007559 | 0.0075524 | 0.0075459 | 0.0075393 | 0.0075327 | 0.0075261 | 0.0075196 | 0.007513 | 0.0075064 | 0.0074999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM005-160415504 | 9 | 9 | 0.0031165 | 0 | 0.0045398 | 0 | 0.0044685 | 0 | 4.0667e-05 | -3.5675e-06 | 0.0043771 | 0.0044178 | 0.0044585 | 0.0044991 | 0.0045398 | 0.0045362 | 0.0045327 | 0.0045291 | 0.0045255 | 0.004522 | 0.0045184 | 0.0045148 | 0.0045113 | 0.0045077 | 0.0045041 | 0.0045006 | 0.004497 | 0.0044934 | 0.0044899 | 0.0044863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM005-160419737 | 19 | 19 | 0.0038014 | 0 | 0.0054852 | 0 | 0.0055121 | 0 | 4.811e-05 | 1.3408e-06 | 0.0052928 | 0.0053409 | 0.005389 | 0.0054371 | 0.0054852 | 0.0054866 | 0.0054879 | 0.0054893 | 0.0054906 | 0.0054919 | 0.0054933 | 0.0054946 | 0.005496 | 0.0054973 | 0.0054986 | 0.0055 | 0.0055013 | 0.0055027 | 0.005504 | 0.0055054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM005-160419880 | 27 | 27 | 0.0020299 | 0 | 0.0028836 | 0 | 0.0029389 | 0 | 2.4393e-05 | 2.763e-06 | 0.0027861 | 0.0028104 | 0.0028348 | 0.0028592 | 0.0028836 | 0.0028864 | 0.0028892 | 0.0028919 | 0.0028947 | 0.0028974 | 0.0029002 | 0.002903 | 0.0029057 | 0.0029085 | 0.0029113 | 0.002914 | 0.0029168 | 0.0029195 | 0.0029223 | 0.0029251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM005-160419993 | 13 | 13 | 0.0022883 | 0 | 0.0033252 | 0 | 0.0034487 | 0 | 2.9626e-05 | 6.1714e-06 | 0.0032067 | 0.0032364 | 0.003266 | 0.0032956 | 0.0033252 | 0.0033314 | 0.0033376 | 0.0033437 | 0.0033499 | 0.0033561 | 0.0033623 | 0.0033684 | 0.0033746 | 0.0033808 | 0.0033869 | 0.0033931 | 0.0033993 | 0.0034055 | 0.0034116 | 0.0034178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM005-160647192 | 28 | 28 | 0.0073173 | 0 | 0.010344 | 0 | 0.010072 | 0 | 8.6488e-05 | -1.362e-05 | 0.0099984 | 0.010085 | 0.010171 | 0.010258 | 0.010344 | 0.010331 | 0.010317 | 0.010303 | 0.01029 | 0.010276 | 0.010263 | 0.010249 | 0.010235 | 0.010222 | 0.010208 | 0.010195 | 0.010181 | 0.010167 | 0.010154 | 0.01014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM006-153767042 | 20 | 20 | 0.0057729 | 0 | 0.0079717 | 0 | 0.0076127 | 0 | 6.282e-05 | -1.7947e-05 | 0.0077204 | 0.0077832 | 0.007846 | 0.0079088 | 0.0079717 | 0.0079537 | 0.0079358 | 0.0079178 | 0.0078999 | 0.0078819 | 0.007864 | 0.007846 | 0.0078281 | 0.0078101 | 0.0077922 | 0.0077742 | 0.0077563 | 0.0077383 | 0.0077204 | 0.0077024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM006-15416692 | 2916 | 1694 | 0.00090478 | 0.000499 | 0.0012906 | 0.00072379 | 0.001276 | 0.00072002 | 1.1023e-05 | -7.271e-07 | 0.0012465 | 0.0012575 | 0.0012685 | 0.0012796 | 0.0012906 | 0.0012899 | 0.0012891 | 0.0012884 | 0.0012877 | 0.001287 | 0.0012862 | 0.0012855 | 0.0012848 | 0.001284 | 0.0012833 | 0.0012826 | 0.0012819 | 0.0012811 | 0.0012804 | 0.0012797 | 6.4226e-06 | -1.8865e-07 | 0.0006981 | 0.00070452 | 0.00071095 | 0.00071737 | 0.00072379 | 0.0007236 | 0.00072341 | 0.00072323 | 0.00072304 | 0.00072285 | 0.00072266 | 0.00072247 | 0.00072228 | 0.00072209 | 0.00072191 | 0.00072172 | 0.00072153 | 0.00072134 | 0.00072115 | 0.00072096
| HSM006-15416703 | 2924 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM006-160434642 | 11 | 11 | 0.0068857 | 0 | 0.0098839 | 0 | 0.0099524 | 0 | 8.5663e-05 | 3.4237e-06 | 0.0095413 | 0.0096269 | 0.0097126 | 0.0097983 | 0.0098839 | 0.0098873 | 0.0098908 | 0.0098942 | 0.0098976 | 0.009901 | 0.0099045 | 0.0099079 | 0.0099113 | 0.0099147 | 0.0099182 | 0.0099216 | 0.009925 | 0.0099284 | 0.0099318 | 0.0099353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM006-160439280 | 17 | 17 | 0.00076646 | 0 | 0.0011427 | 0 | 0.0011216 | 0 | 1.0751e-05 | -1.0552e-06 | 0.0010997 | 0.0011105 | 0.0011212 | 0.001132 | 0.0011427 | 0.0011417 | 0.0011406 | 0.0011396 | 0.0011385 | 0.0011375 | 0.0011364 | 0.0011354 | 0.0011343 | 0.0011332 | 0.0011322 | 0.0011311 | 0.0011301 | 0.001129 | 0.001128 | 0.0011269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM006-160439382 | 9 | 9 | 2.83e-05 | 0 | 4.2e-05 | 0 | 4.35e-05 | 0 | 3.9143e-07 | 7.5e-08 | 4.0434e-05 | 4.0826e-05 | 4.1217e-05 | 4.1609e-05 | 4.2e-05 | 4.2075e-05 | 4.215e-05 | 4.2225e-05 | 4.23e-05 | 4.2375e-05 | 4.245e-05 | 4.2525e-05 | 4.26e-05 | 4.2675e-05 | 4.275e-05 | 4.2825e-05 | 4.29e-05 | 4.2975e-05 | 4.305e-05 | 4.3125e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM006-160439464 | 23 | 23 | 0.00348 | 0 | 0.0048686 | 0 | 0.0047207 | 0 | 3.9676e-05 | -7.3983e-06 | 0.0047099 | 0.0047496 | 0.0047893 | 0.004829 | 0.0048686 | 0.0048612 | 0.0048539 | 0.0048465 | 0.0048391 | 0.0048317 | 0.0048243 | 0.0048169 | 0.0048095 | 0.0048021 | 0.0047947 | 0.0047873 | 0.0047799 | 0.0047725 | 0.0047651 | 0.0047577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM006-160439562 | 63 | 63 | 0.006735 | 0 | 0.0094258 | 0 | 0.0091878 | 0 | 7.688e-05 | -1.19e-05 | 0.0091182 | 0.0091951 | 0.009272 | 0.0093489 | 0.0094258 | 0.0094139 | 0.009402 | 0.0093901 | 0.0093782 | 0.0093663 | 0.0093544 | 0.0093425 | 0.0093306 | 0.0093187 | 0.0093068 | 0.0092949 | 0.009283 | 0.0092711 | 0.0092592 | 0.0092473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM006-160439782 | 18 | 18 | 0.00036124 | 0 | 0.0005381 | 0 | 0.00054053 | 0 | 5.0532e-06 | 1.2155e-07 | 0.00051789 | 0.00052294 | 0.00052799 | 0.00053305 | 0.0005381 | 0.00053822 | 0.00053834 | 0.00053847 | 0.00053859 | 0.00053871 | 0.00053883 | 0.00053895 | 0.00053907 | 0.00053919 | 0.00053932 | 0.00053944 | 0.00053956 | 0.00053968 | 0.0005398 | 0.00053992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM006-163605855 | 6 | 6 | 1.99e-05 | 0 | 2.77e-05 | 0 | 2.79e-05 | 0 | 2.2286e-07 | 1e-08 | 2.6809e-05 | 2.7031e-05 | 2.7254e-05 | 2.7477e-05 | 2.77e-05 | 2.771e-05 | 2.772e-05 | 2.773e-05 | 2.774e-05 | 2.775e-05 | 2.776e-05 | 2.777e-05 | 2.778e-05 | 2.779e-05 | 2.78e-05 | 2.781e-05 | 2.782e-05 | 2.783e-05 | 2.784e-05 | 2.785e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM006-201967868 | 1131 | 1007 | 0.016492 | 0.0059387 | 0.022606 | 0.0083571 | 0.021973 | 0.0081426 | 0.00017468 | -3.1647e-05 | 0.021907 | 0.022082 | 0.022257 | 0.022431 | 0.022606 | 0.022575 | 0.022543 | 0.022511 | 0.02248 | 0.022448 | 0.022416 | 0.022385 | 0.022353 | 0.022321 | 0.02229 | 0.022258 | 0.022226 | 0.022195 | 0.022163 | 0.022131 | 6.9097e-05 | -1.0725e-05 | 0.0080807 | 0.0081498 | 0.0082189 | 0.008288 | 0.0083571 | 0.0083464 | 0.0083357 | 0.0083249 | 0.0083142 | 0.0083035 | 0.0082928 | 0.008282 | 0.0082713 | 0.0082606 | 0.0082499 | 0.0082391 | 0.0082284 | 0.0082177 | 0.008207 | 0.0081962
| HSM006-24597826 | 1222 | 48 | 0.0028458 | 0.0040748 | 0.0042128 | 0.0060844 | 0.0042488 | 0.0061463 | 3.9057e-05 | 1.8018e-06 | 0.0040565 | 0.0040956 | 0.0041347 | 0.0041737 | 0.0042128 | 0.0042146 | 0.0042164 | 0.0042182 | 0.00422 | 0.0042218 | 0.0042236 | 0.0042254 | 0.0042272 | 0.004229 | 0.0042308 | 0.0042326 | 0.0042344 | 0.0042362 | 0.004238 | 0.0042398 | 5.7417e-05 | 3.0958e-06 | 0.0058547 | 0.0059121 | 0.0059696 | 0.006027 | 0.0060844 | 0.0060875 | 0.0060906 | 0.0060937 | 0.0060968 | 0.0060999 | 0.006103 | 0.0061061 | 0.0061092 | 0.0061123 | 0.0061154 | 0.0061185 | 0.0061215 | 0.0061246 | 0.0061277 | 0.0061308
| HSM009-15416366 | 3348 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM009-15416379 | 3339 | 3339 | 0.018093 | 0 | 0.022848 | 0 | 0.022008 | 0 | 0.00013586 | -4.1991e-05 | 0.022305 | 0.022441 | 0.022577 | 0.022712 | 0.022848 | 0.022806 | 0.022764 | 0.022722 | 0.02268 | 0.022638 | 0.022596 | 0.022554 | 0.022512 | 0.02247 | 0.022428 | 0.022386 | 0.022344 | 0.022302 | 0.02226 | 0.022218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM010-15416755 | 3229 | 3229 | 0.03688 | 0 | 0.046998 | 0 | 0.046057 | 0 | 0.00028908 | -4.7029e-05 | 0.045842 | 0.046131 | 0.04642 | 0.046709 | 0.046998 | 0.046951 | 0.046904 | 0.046857 | 0.04681 | 0.046763 | 0.046716 | 0.046669 | 0.046622 | 0.046575 | 0.046528 | 0.046481 | 0.046434 | 0.046387 | 0.04634 | 0.046293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-155712659 | 38 | 38 | 0.00056718 | 0 | 0.00067752 | 0 | 0.00044031 | 0 | 3.1525e-06 | -1.186e-05 | 0.00066491 | 0.00066806 | 0.00067122 | 0.00067437 | 0.00067752 | 0.00066566 | 0.0006538 | 0.00064194 | 0.00063008 | 0.00061822 | 0.00060636 | 0.0005945 | 0.00058264 | 0.00057078 | 0.00055892 | 0.00054706 | 0.0005352 | 0.00052334 | 0.00051148 | 0.00049961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-156981207 | 28 | 28 | 0.0017246 | 0 | 0.0025773 | 0 | 0.0018369 | 0 | 2.4361e-05 | -3.7018e-05 | 0.0024798 | 0.0025042 | 0.0025285 | 0.0025529 | 0.0025773 | 0.0025403 | 0.0025032 | 0.0024662 | 0.0024292 | 0.0023922 | 0.0023552 | 0.0023181 | 0.0022811 | 0.0022441 | 0.0022071 | 0.0021701 | 0.0021331 | 0.002096 | 0.002059 | 0.002022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-157405209 | 15 | 15 | 8.14e-05 | 0 | 0.00011355 | 0 | 8.69e-05 | 0 | 9.1851e-07 | -1.3324e-06 | 0.00010987 | 0.00011079 | 0.00011171 | 0.00011263 | 0.00011355 | 0.00011222 | 0.00011088 | 0.00010955 | 0.00010822 | 0.00010689 | 0.00010555 | 0.00010422 | 0.00010289 | 0.00010156 | 0.00010022 | 9.8892e-05 | 9.7559e-05 | 9.6227e-05 | 9.4894e-05 | 9.3562e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-157405424 | 18 | 18 | 4.92e-05 | 0 | 7.01e-05 | 0 | 5.54e-05 | 0 | 5.9714e-07 | -7.35e-07 | 6.7711e-05 | 6.8309e-05 | 6.8906e-05 | 6.9503e-05 | 7.01e-05 | 6.9365e-05 | 6.863e-05 | 6.7895e-05 | 6.716e-05 | 6.6425e-05 | 6.569e-05 | 6.4955e-05 | 6.422e-05 | 6.3485e-05 | 6.275e-05 | 6.2015e-05 | 6.128e-05 | 6.0545e-05 | 5.981e-05 | 5.9075e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-157405677 | 48 | 48 | 0.0028721 | 0 | 0.0038028 | 0 | 0.0027976 | 0 | 2.6589e-05 | -5.026e-05 | 0.0036964 | 0.003723 | 0.0037496 | 0.0037762 | 0.0038028 | 0.0037525 | 0.0037023 | 0.003652 | 0.0036017 | 0.0035515 | 0.0035012 | 0.003451 | 0.0034007 | 0.0033504 | 0.0033002 | 0.0032499 | 0.0031997 | 0.0031494 | 0.0030991 | 0.0030489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-157406255 | 27 | 27 | 0.0017005 | 0 | 0.0024049 | 0 | 0.0019561 | 0 | 2.0126e-05 | -2.2444e-05 | 0.0023244 | 0.0023445 | 0.0023647 | 0.0023848 | 0.0024049 | 0.0023825 | 0.00236 | 0.0023376 | 0.0023152 | 0.0022927 | 0.0022703 | 0.0022478 | 0.0022254 | 0.0022029 | 0.0021805 | 0.002158 | 0.0021356 | 0.0021132 | 0.0020907 | 0.0020683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-157406464 | 20 | 20 | 0.0012141 | 0 | 0.001801 | 0 | 0.0014333 | 0 | 1.6767e-05 | -1.8381e-05 | 0.0017339 | 0.0017507 | 0.0017674 | 0.0017842 | 0.001801 | 0.0017826 | 0.0017642 | 0.0017458 | 0.0017274 | 0.0017091 | 0.0016907 | 0.0016723 | 0.0016539 | 0.0016355 | 0.0016171 | 0.0015988 | 0.0015804 | 0.001562 | 0.0015436 | 0.0015252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-157406612 | 14 | 14 | 0.0016289 | 0 | 0.0024092 | 0 | 0.0017332 | 0 | 2.2296e-05 | -3.3804e-05 | 0.00232 | 0.0023423 | 0.0023646 | 0.0023869 | 0.0024092 | 0.0023754 | 0.0023416 | 0.0023078 | 0.002274 | 0.0022402 | 0.0022064 | 0.0021726 | 0.0021388 | 0.002105 | 0.0020712 | 0.0020374 | 0.0020036 | 0.0019698 | 0.001936 | 0.0019022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-162645268 | 6 | 6 | 4.48e-06 | 0 | 6.35e-06 | 0 | 4.89e-06 | 0 | 5.3429e-08 | -7.3e-08 | 6.1363e-06 | 6.1897e-06 | 6.2431e-06 | 6.2966e-06 | 6.35e-06 | 6.277e-06 | 6.204e-06 | 6.131e-06 | 6.058e-06 | 5.985e-06 | 5.912e-06 | 5.839e-06 | 5.766e-06 | 5.693e-06 | 5.62e-06 | 5.547e-06 | 5.474e-06 | 5.401e-06 | 5.328e-06 | 5.255e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-162645611 | 7 | 7 | 7.19e-05 | 0 | 9.75e-05 | 0 | 7.25e-05 | 0 | 7.3143e-07 | -1.25e-06 | 9.4574e-05 | 9.5306e-05 | 9.6037e-05 | 9.6769e-05 | 9.75e-05 | 9.625e-05 | 9.5e-05 | 9.375e-05 | 9.25e-05 | 9.125e-05 | 9e-05 | 8.875e-05 | 8.75e-05 | 8.625e-05 | 8.5e-05 | 8.375e-05 | 8.25e-05 | 8.125e-05 | 8e-05 | 7.875e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-190418895 | 776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-190418905 | 776 | 37 | 0.0076497 | 0.0010612 | 0.0094759 | 0.0015787 | 0.0082496 | 0.0012398 | 5.2179e-05 | -6.1318e-05 | 0.0092672 | 0.0093194 | 0.0093716 | 0.0094238 | 0.0094759 | 0.0094146 | 0.0093533 | 0.009292 | 0.0092307 | 0.0091694 | 0.009108 | 0.0090467 | 0.0089854 | 0.0089241 | 0.0088628 | 0.0088014 | 0.0087401 | 0.0086788 | 0.0086175 | 0.0085562 | 1.4788e-05 | -1.6945e-05 | 0.0015196 | 0.0015344 | 0.0015492 | 0.0015639 | 0.0015787 | 0.0015618 | 0.0015448 | 0.0015279 | 0.001511 | 0.001494 | 0.0014771 | 0.0014601 | 0.0014432 | 0.0014262 | 0.0014093 | 0.0013923 | 0.0013754 | 0.0013584 | 0.0013415 | 0.0013246
| HTN011-24613192 | 739 | 518 | 0.0081504 | 0.0034406 | 0.01025 | 0.0045611 | 0.0080707 | 0.0033633 | 5.999e-05 | -0.00010897 | 0.01001 | 0.01007 | 0.01013 | 0.01019 | 0.01025 | 0.010141 | 0.010032 | 0.0099232 | 0.0098142 | 0.0097052 | 0.0095963 | 0.0094873 | 0.0093783 | 0.0092694 | 0.0091604 | 0.0090514 | 0.0089425 | 0.0088335 | 0.0087245 | 0.0086156 | 3.2015e-05 | -5.9891e-05 | 0.004433 | 0.004465 | 0.0044971 | 0.0045291 | 0.0045611 | 0.0045012 | 0.0044413 | 0.0043814 | 0.0043215 | 0.0042616 | 0.0042017 | 0.0041418 | 0.004082 | 0.0040221 | 0.0039622 | 0.0039023 | 0.0038424 | 0.0037825 | 0.0037226 | 0.0036627
| HTN012-140933454 | 25 | 25 | 0.0024794 | 0 | 0.0034419 | 0 | 0.0026558 | 0 | 2.7499e-05 | -3.9305e-05 | 0.0033319 | 0.0033594 | 0.0033869 | 0.0034144 | 0.0034419 | 0.0034026 | 0.0033633 | 0.003324 | 0.0032846 | 0.0032453 | 0.003206 | 0.0031667 | 0.0031274 | 0.0030881 | 0.0030488 | 0.0030095 | 0.0029702 | 0.0029309 | 0.0028916 | 0.0028523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-140933685 | 14 | 14 | 0.0013333 | 0 | 0.0021085 | 0 | 0.0012227 | 0 | 2.2149e-05 | -4.4292e-05 | 0.0020199 | 0.002042 | 0.0020642 | 0.0020863 | 0.0021085 | 0.0020642 | 0.0020199 | 0.0019756 | 0.0019313 | 0.001887 | 0.0018427 | 0.0017984 | 0.0017542 | 0.0017099 | 0.0016656 | 0.0016213 | 0.001577 | 0.0015327 | 0.0014884 | 0.0014441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-140933990 | 15 | 15 | 3.51e-05 | 0 | 6e-05 | 0 | 3.76e-05 | 0 | 7.1143e-07 | -1.12e-06 | 5.7154e-05 | 5.7866e-05 | 5.8577e-05 | 5.9289e-05 | 6e-05 | 5.888e-05 | 5.776e-05 | 5.664e-05 | 5.552e-05 | 5.44e-05 | 5.328e-05 | 5.216e-05 | 5.104e-05 | 4.992e-05 | 4.88e-05 | 4.768e-05 | 4.656e-05 | 4.544e-05 | 4.432e-05 | 4.32e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-160319327 | 17 | 17 | 0.0092121 | 0 | 0.010683 | 0 | 0.0096966 | 0 | 4.2021e-05 | -4.9312e-05 | 0.010515 | 0.010557 | 0.010599 | 0.010641 | 0.010683 | 0.010633 | 0.010584 | 0.010535 | 0.010486 | 0.010436 | 0.010387 | 0.010338 | 0.010288 | 0.010239 | 0.01019 | 0.01014 | 0.010091 | 0.010042 | 0.0099924 | 0.0099431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-160319432 | 9 | 9 | 0.0016577 | 0 | 0.0023598 | 0 | 0.0019306 | 0 | 2.0058e-05 | -2.1456e-05 | 0.0022795 | 0.0022996 | 0.0023196 | 0.0023397 | 0.0023598 | 0.0023383 | 0.0023168 | 0.0022954 | 0.0022739 | 0.0022525 | 0.002231 | 0.0022096 | 0.0021881 | 0.0021667 | 0.0021452 | 0.0021237 | 0.0021023 | 0.0020808 | 0.0020594 | 0.0020379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-160319528 | 11 | 11 | 0.00038476 | 0 | 0.00055493 | 0 | 0.00046603 | 0 | 4.862e-06 | -4.4449e-06 | 0.00053548 | 0.00054034 | 0.0005452 | 0.00055006 | 0.00055493 | 0.00055048 | 0.00054604 | 0.00054159 | 0.00053715 | 0.0005327 | 0.00052826 | 0.00052381 | 0.00051937 | 0.00051492 | 0.00051048 | 0.00050603 | 0.00050159 | 0.00049714 | 0.0004927 | 0.00048825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-160338385 | 31 | 31 | 0.0022909 | 0 | 0.0033766 | 0 | 0.0023592 | 0 | 3.1018e-05 | -5.087e-05 | 0.0032525 | 0.0032835 | 0.0033145 | 0.0033456 | 0.0033766 | 0.0033257 | 0.0032748 | 0.003224 | 0.0031731 | 0.0031222 | 0.0030714 | 0.0030205 | 0.0029696 | 0.0029188 | 0.0028679 | 0.002817 | 0.0027661 | 0.0027153 | 0.0026644 | 0.0026135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-160338483 | 41 | 41 | 0.0015392 | 0 | 0.0023772 | 0 | 0.0018702 | 0 | 2.3942e-05 | -2.5347e-05 | 0.0022814 | 0.0023054 | 0.0023293 | 0.0023532 | 0.0023772 | 0.0023518 | 0.0023265 | 0.0023011 | 0.0022758 | 0.0022504 | 0.0022251 | 0.0021997 | 0.0021744 | 0.0021491 | 0.0021237 | 0.0020984 | 0.002073 | 0.0020477 | 0.0020223 | 0.001997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-160338601 | 42 | 42 | 0.0014573 | 0 | 0.0023197 | 0 | 0.0015167 | 0 | 2.464e-05 | -4.0151e-05 | 0.0022211 | 0.0022458 | 0.0022704 | 0.002295 | 0.0023197 | 0.0022795 | 0.0022394 | 0.0021992 | 0.0021591 | 0.0021189 | 0.0020788 | 0.0020386 | 0.0019985 | 0.0019583 | 0.0019182 | 0.001878 | 0.0018379 | 0.0017977 | 0.0017576 | 0.0017174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-160411348 | 13 | 13 | 0.00046624 | 0 | 0.00071829 | 0 | 0.00049349 | 0 | 7.2013e-06 | -1.124e-05 | 0.00068948 | 0.00069669 | 0.00070389 | 0.00071109 | 0.00071829 | 0.00070705 | 0.00069581 | 0.00068457 | 0.00067333 | 0.00066209 | 0.00065085 | 0.00063961 | 0.00062837 | 0.00061713 | 0.00060589 | 0.00059465 | 0.00058341 | 0.00057217 | 0.00056093 | 0.00054969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-160437866 | 47 | 47 | 0.00011527 | 0 | 0.0001814 | 0 | 0.0001386 | 0 | 1.8893e-06 | -2.14e-06 | 0.00017384 | 0.00017573 | 0.00017762 | 0.00017951 | 0.0001814 | 0.00017926 | 0.00017712 | 0.00017498 | 0.00017284 | 0.0001707 | 0.00016856 | 0.00016642 | 0.00016428 | 0.00016214 | 0.00016 | 0.00015786 | 0.00015572 | 0.00015358 | 0.00015144 | 0.0001493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-162615153 | 1 | 1 | 3.8e-06 | 0 | 6.03e-06 | 0 | 3.8e-06 | 0 | 6.3714e-08 | -1.115e-07 | 5.7751e-06 | 5.8389e-06 | 5.9026e-06 | 5.9663e-06 | 6.03e-06 | 5.9185e-06 | 5.807e-06 | 5.6955e-06 | 5.584e-06 | 5.4725e-06 | 5.361e-06 | 5.2495e-06 | 5.138e-06 | 5.0265e-06 | 4.915e-06 | 4.8035e-06 | 4.692e-06 | 4.5805e-06 | 4.469e-06 | 4.3575e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-162615767 | 13 | 13 | 0.00034992 | 0 | 0.00050363 | 0 | 0.00040455 | 0 | 4.3917e-06 | -4.9542e-06 | 0.00048606 | 0.00049045 | 0.00049485 | 0.00049924 | 0.00050363 | 0.00049867 | 0.00049372 | 0.00048877 | 0.00048381 | 0.00047886 | 0.0004739 | 0.00046895 | 0.000464 | 0.00045904 | 0.00045409 | 0.00044913 | 0.00044418 | 0.00043923 | 0.00043427 | 0.00042932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-162670168 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-190418858 | 1859 | 647 | 0.00052314 | 7.4e-05 | 0.00065085 | 0.00011179 | 0.00056451 | 8.88e-05 | 3.6488e-06 | -4.317e-06 | 0.00063625 | 0.0006399 | 0.00064355 | 0.0006472 | 0.00065085 | 0.00064653 | 0.00064222 | 0.0006379 | 0.00063358 | 0.00062926 | 0.00062495 | 0.00062063 | 0.00061631 | 0.000612 | 0.00060768 | 0.00060336 | 0.00059905 | 0.00059473 | 0.00059041 | 0.00058609 | 1.0798e-06 | -1.1496e-06 | 0.00010747 | 0.00010855 | 0.00010963 | 0.00011071 | 0.00011179 | 0.00011064 | 0.00010949 | 0.00010834 | 0.00010719 | 0.00010604 | 0.00010489 | 0.00010374 | 0.0001026 | 0.00010145 | 0.0001003 | 9.9146e-05 | 9.7997e-05 | 9.6847e-05 | 9.5698e-05 | 9.4548e-05
| HTN012-24597770 | 1212 | 931 | 0.01093 | 0.0056038 | 0.015714 | 0.0079759 | 0.01132 | 0.0058334 | 0.00013669 | -0.00021968 | 0.015167 | 0.015304 | 0.015441 | 0.015577 | 0.015714 | 0.015494 | 0.015275 | 0.015055 | 0.014835 | 0.014616 | 0.014396 | 0.014176 | 0.013957 | 0.013737 | 0.013517 | 0.013298 | 0.013078 | 0.012858 | 0.012638 | 0.012419 | 6.7776e-05 | -0.00010713 | 0.0077048 | 0.0077726 | 0.0078404 | 0.0079082 | 0.0079759 | 0.0078688 | 0.0077617 | 0.0076546 | 0.0075474 | 0.0074403 | 0.0073332 | 0.0072261 | 0.0071189 | 0.0070118 | 0.0069047 | 0.0067975 | 0.0066904 | 0.0065833 | 0.0064762 | 0.006369
| HTN013-100723362 | 2205 | 642 | 0.0016278 | 0.0022648 | 0.0021885 | 0.0027588 | 0.0019879 | 0.0024696 | 1.6021e-05 | -1.003e-05 | 0.0021244 | 0.0021405 | 0.0021565 | 0.0021725 | 0.0021885 | 0.0021785 | 0.0021685 | 0.0021584 | 0.0021484 | 0.0021384 | 0.0021284 | 0.0021183 | 0.0021083 | 0.0020983 | 0.0020882 | 0.0020782 | 0.0020682 | 0.0020581 | 0.0020481 | 0.0020381 | 1.4116e-05 | -1.446e-05 | 0.0027024 | 0.0027165 | 0.0027306 | 0.0027447 | 0.0027588 | 0.0027444 | 0.0027299 | 0.0027155 | 0.002701 | 0.0026865 | 0.0026721 | 0.0026576 | 0.0026432 | 0.0026287 | 0.0026142 | 0.0025998 | 0.0025853 | 0.0025709 | 0.0025564 | 0.0025419
| HTN013-142439156 | 24 | 24 | 0.0069556 | 0 | 0.0085429 | 0 | 0.0076005 | 0 | 4.5353e-05 | -4.712e-05 | 0.0083615 | 0.0084068 | 0.0084522 | 0.0084975 | 0.0085429 | 0.0084958 | 0.0084487 | 0.0084015 | 0.0083544 | 0.0083073 | 0.0082602 | 0.0082131 | 0.0081659 | 0.0081188 | 0.0080717 | 0.0080246 | 0.0079775 | 0.0079303 | 0.0078832 | 0.0078361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-142439579 | 16 | 16 | 0.0015838 | 0 | 0.0019965 | 0 | 0.0018349 | 0 | 1.1789e-05 | -8.079e-06 | 0.0019493 | 0.0019611 | 0.0019729 | 0.0019847 | 0.0019965 | 0.0019884 | 0.0019803 | 0.0019722 | 0.0019641 | 0.0019561 | 0.001948 | 0.0019399 | 0.0019318 | 0.0019237 | 0.0019157 | 0.0019076 | 0.0018995 | 0.0018914 | 0.0018834 | 0.0018753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-142439718 | 31 | 31 | 0.00049046 | 0 | 0.00059337 | 0 | 0.00053597 | 0 | 2.9402e-06 | -2.8702e-06 | 0.00058161 | 0.00058455 | 0.00058749 | 0.00059043 | 0.00059337 | 0.0005905 | 0.00058763 | 0.00058476 | 0.00058189 | 0.00057902 | 0.00057615 | 0.00057328 | 0.00057041 | 0.00056754 | 0.00056467 | 0.0005618 | 0.00055893 | 0.00055606 | 0.00055319 | 0.00055032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-142440041 | 48 | 48 | 0.001825 | 0 | 0.0024232 | 0 | 0.0022003 | 0 | 1.709e-05 | -1.1144e-05 | 0.0023548 | 0.0023719 | 0.002389 | 0.0024061 | 0.0024232 | 0.0024121 | 0.0024009 | 0.0023898 | 0.0023786 | 0.0023675 | 0.0023563 | 0.0023452 | 0.0023341 | 0.0023229 | 0.0023118 | 0.0023006 | 0.0022895 | 0.0022783 | 0.0022672 | 0.0022561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-153173736 | 1205 | 57 | 0.0021396 | 0.0027986 | 0.0027104 | 0.0033343 | 0.0024457 | 0.0029775 | 1.631e-05 | -1.3236e-05 | 0.0026452 | 0.0026615 | 0.0026778 | 0.0026941 | 0.0027104 | 0.0026972 | 0.002684 | 0.0026707 | 0.0026575 | 0.0026442 | 0.002631 | 0.0026178 | 0.0026045 | 0.0025913 | 0.0025781 | 0.0025648 | 0.0025516 | 0.0025384 | 0.0025251 | 0.0025119 | 1.5306e-05 | -1.7841e-05 | 0.0032731 | 0.0032884 | 0.0033037 | 0.003319 | 0.0033343 | 0.0033165 | 0.0032987 | 0.0032808 | 0.003263 | 0.0032451 | 0.0032273 | 0.0032095 | 0.0031916 | 0.0031738 | 0.0031559 | 0.0031381 | 0.0031203 | 0.0031024 | 0.0030846 | 0.0030667
| HTN013-158639235 | 10 | 10 | 0.0022986 | 0 | 0.0027737 | 0 | 0.0024862 | 0 | 1.3574e-05 | -1.4375e-05 | 0.0027194 | 0.002733 | 0.0027466 | 0.0027601 | 0.0027737 | 0.0027593 | 0.002745 | 0.0027306 | 0.0027162 | 0.0027018 | 0.0026875 | 0.0026731 | 0.0026587 | 0.0026443 | 0.00263 | 0.0026156 | 0.0026012 | 0.0025868 | 0.0025725 | 0.0025581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-158639340 | 28 | 28 | 0.00065128 | 0 | 0.00085992 | 0 | 0.00078037 | 0 | 5.9612e-06 | -3.9775e-06 | 0.00083607 | 0.00084203 | 0.000848 | 0.00085396 | 0.00085992 | 0.00085594 | 0.00085196 | 0.00084799 | 0.00084401 | 0.00084003 | 0.00083605 | 0.00083208 | 0.0008281 | 0.00082412 | 0.00082014 | 0.00081617 | 0.00081219 | 0.00080821 | 0.00080423 | 0.00080026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-159365790 | 18 | 18 | 0.00044027 | 0 | 0.00052719 | 0 | 0.00046007 | 0 | 2.4835e-06 | -3.3558e-06 | 0.00051726 | 0.00051974 | 0.00052222 | 0.00052471 | 0.00052719 | 0.00052383 | 0.00052048 | 0.00051712 | 0.00051377 | 0.00051041 | 0.00050705 | 0.0005037 | 0.00050034 | 0.00049699 | 0.00049363 | 0.00049028 | 0.00048692 | 0.00048356 | 0.00048021 | 0.00047685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-159366167 | 19 | 19 | 0.00029792 | 0 | 0.00035507 | 0 | 0.00031615 | 0 | 1.6329e-06 | -1.9459e-06 | 0.00034854 | 0.00035017 | 0.00035181 | 0.00035344 | 0.00035507 | 0.00035313 | 0.00035118 | 0.00034923 | 0.00034729 | 0.00034534 | 0.0003434 | 0.00034145 | 0.0003395 | 0.00033756 | 0.00033561 | 0.00033367 | 0.00033172 | 0.00032977 | 0.00032783 | 0.00032588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-159381071 | 20 | 20 | 0.0016871 | 0 | 0.0019977 | 0 | 0.0017809 | 0 | 8.8744e-06 | -1.084e-05 | 0.0019623 | 0.0019711 | 0.00198 | 0.0019889 | 0.0019977 | 0.0019869 | 0.0019761 | 0.0019652 | 0.0019544 | 0.0019435 | 0.0019327 | 0.0019219 | 0.001911 | 0.0019002 | 0.0018893 | 0.0018785 | 0.0018677 | 0.0018568 | 0.001846 | 0.0018351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-159381283 | 11 | 11 | 0.0023301 | 0 | 0.0027522 | 0 | 0.0024261 | 0 | 1.2062e-05 | -1.6304e-05 | 0.002704 | 0.002716 | 0.0027281 | 0.0027402 | 0.0027522 | 0.0027359 | 0.0027196 | 0.0027033 | 0.002687 | 0.0026707 | 0.0026544 | 0.0026381 | 0.0026218 | 0.0026055 | 0.0025892 | 0.0025729 | 0.0025566 | 0.0025403 | 0.002524 | 0.0025077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-160286800 | 23 | 23 | 0.0039773 | 0 | 0.0048803 | 0 | 0.0043799 | 0 | 2.5798e-05 | -2.5016e-05 | 0.0047771 | 0.0048029 | 0.0048287 | 0.0048545 | 0.0048803 | 0.0048553 | 0.0048302 | 0.0048052 | 0.0047802 | 0.0047552 | 0.0047302 | 0.0047052 | 0.0046801 | 0.0046551 | 0.0046301 | 0.0046051 | 0.0045801 | 0.0045551 | 0.00453 | 0.004505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-160451212 | 21 | 21 | 0.00077846 | 0 | 0.0010568 | 0 | 0.00097244 | 0 | 7.9539e-06 | -4.2203e-06 | 0.001025 | 0.001033 | 0.0010409 | 0.0010489 | 0.0010568 | 0.0010526 | 0.0010484 | 0.0010442 | 0.00104 | 0.0010357 | 0.0010315 | 0.0010273 | 0.0010231 | 0.0010189 | 0.0010146 | 0.0010104 | 0.0010062 | 0.001002 | 0.00099776 | 0.00099354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-160451319 | 16 | 16 | 5.67e-06 | 0 | 7.21e-06 | 0 | 6.3e-06 | 0 | 4.4e-08 | -4.55e-08 | 7.034e-06 | 7.078e-06 | 7.122e-06 | 7.166e-06 | 7.21e-06 | 7.1645e-06 | 7.119e-06 | 7.0735e-06 | 7.028e-06 | 6.9825e-06 | 6.937e-06 | 6.8915e-06 | 6.846e-06 | 6.8005e-06 | 6.755e-06 | 6.7095e-06 | 6.664e-06 | 6.6185e-06 | 6.573e-06 | 6.5275e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-160451462 | 15 | 15 | 0.0014999 | 0 | 0.0019494 | 0 | 0.0017152 | 0 | 1.2843e-05 | -1.1712e-05 | 0.0018981 | 0.0019109 | 0.0019237 | 0.0019366 | 0.0019494 | 0.0019377 | 0.001926 | 0.0019143 | 0.0019026 | 0.0018909 | 0.0018792 | 0.0018674 | 0.0018557 | 0.001844 | 0.0018323 | 0.0018206 | 0.0018089 | 0.0017972 | 0.0017855 | 0.0017737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-160772532 | 19 | 19 | 0.00092881 | 0 | 0.0011139 | 0 | 0.00099715 | 0 | 5.2881e-06 | -5.8375e-06 | 0.0010927 | 0.001098 | 0.0011033 | 0.0011086 | 0.0011139 | 0.0011081 | 0.0011022 | 0.0010964 | 0.0010905 | 0.0010847 | 0.0010789 | 0.001073 | 0.0010672 | 0.0010614 | 0.0010555 | 0.0010497 | 0.0010438 | 0.001038 | 0.0010322 | 0.0010263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-162802647 | 2 | 2 | 0.0002168 | 0 | 0.0002565 | 0 | 0.00022921 | 0 | 1.1341e-06 | -1.3641e-06 | 0.00025196 | 0.00025309 | 0.00025423 | 0.00025536 | 0.0002565 | 0.00025513 | 0.00025377 | 0.0002524 | 0.00025104 | 0.00024968 | 0.00024831 | 0.00024695 | 0.00024558 | 0.00024422 | 0.00024285 | 0.00024149 | 0.00024013 | 0.00023876 | 0.0002374 | 0.00023603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-162821734 | 49 | 49 | 0.0033298 | 0 | 0.0048733 | 0 | 0.0042956 | 0 | 4.4099e-05 | -2.8887e-05 | 0.0046969 | 0.004741 | 0.0047851 | 0.0048292 | 0.0048733 | 0.0048444 | 0.0048155 | 0.0047866 | 0.0047578 | 0.0047289 | 0.0047 | 0.0046711 | 0.0046422 | 0.0046133 | 0.0045844 | 0.0045556 | 0.0045267 | 0.0044978 | 0.0044689 | 0.00444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-162978763 | 6 | 6 | 8.02e-06 | 0 | 1.04e-05 | 0 | 9.37e-06 | 0 | 6.8e-08 | -5.15e-08 | 1.0128e-05 | 1.0196e-05 | 1.0264e-05 | 1.0332e-05 | 1.04e-05 | 1.0349e-05 | 1.0297e-05 | 1.0246e-05 | 1.0194e-05 | 1.0143e-05 | 1.0091e-05 | 1.004e-05 | 9.988e-06 | 9.9365e-06 | 9.885e-06 | 9.8335e-06 | 9.782e-06 | 9.7305e-06 | 9.679e-06 | 9.6275e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-163073376 | 31 | 31 | 0.002584 | 0 | 0.0030747 | 0 | 0.0027748 | 0 | 1.4021e-05 | -1.4995e-05 | 0.0030186 | 0.0030327 | 0.0030467 | 0.0030607 | 0.0030747 | 0.0030597 | 0.0030447 | 0.0030297 | 0.0030147 | 0.0029998 | 0.0029848 | 0.0029698 | 0.0029548 | 0.0029398 | 0.0029248 | 0.0029098 | 0.0028948 | 0.0028798 | 0.0028648 | 0.0028498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-163073497 | 13 | 13 | 1.13e-06 | 0 | 1.55e-06 | 0 | 1.31e-06 | 0 | 1.2e-08 | -1.2e-08 | 1.502e-06 | 1.514e-06 | 1.526e-06 | 1.538e-06 | 1.55e-06 | 1.538e-06 | 1.526e-06 | 1.514e-06 | 1.502e-06 | 1.49e-06 | 1.478e-06 | 1.466e-06 | 1.454e-06 | 1.442e-06 | 1.43e-06 | 1.418e-06 | 1.406e-06 | 1.394e-06 | 1.382e-06 | 1.37e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-163073657 | 14 | 14 | 1.46e-05 | 0 | 1.98e-05 | 0 | 1.72e-05 | 0 | 1.4857e-07 | -1.3e-07 | 1.9206e-05 | 1.9354e-05 | 1.9503e-05 | 1.9651e-05 | 1.98e-05 | 1.967e-05 | 1.954e-05 | 1.941e-05 | 1.928e-05 | 1.915e-05 | 1.902e-05 | 1.889e-05 | 1.876e-05 | 1.863e-05 | 1.85e-05 | 1.837e-05 | 1.824e-05 | 1.811e-05 | 1.798e-05 | 1.785e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-163073840 | 46 | 46 | 0.0017836 | 0 | 0.002186 | 0 | 0.0019037 | 0 | 1.1497e-05 | -1.4114e-05 | 0.00214 | 0.0021515 | 0.002163 | 0.0021745 | 0.002186 | 0.0021719 | 0.0021578 | 0.0021437 | 0.0021296 | 0.0021155 | 0.0021013 | 0.0020872 | 0.0020731 | 0.002059 | 0.0020449 | 0.0020308 | 0.0020167 | 0.0020025 | 0.0019884 | 0.0019743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-163074070 | 5 | 5 | 0.00022686 | 0 | 0.00028477 | 0 | 0.00026249 | 0 | 1.6546e-06 | -1.1143e-06 | 0.00027815 | 0.00027981 | 0.00028146 | 0.00028312 | 0.00028477 | 0.00028366 | 0.00028254 | 0.00028143 | 0.00028031 | 0.0002792 | 0.00027809 | 0.00027697 | 0.00027586 | 0.00027474 | 0.00027363 | 0.00027251 | 0.0002714 | 0.00027029 | 0.00026917 | 0.00026806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-171202197 | 29 | 29 | 0.0040009 | 0 | 0.004815 | 0 | 0.0044216 | 0 | 2.3258e-05 | -1.9669e-05 | 0.0047219 | 0.0047452 | 0.0047684 | 0.0047917 | 0.004815 | 0.0047953 | 0.0047756 | 0.004756 | 0.0047363 | 0.0047166 | 0.0046969 | 0.0046773 | 0.0046576 | 0.0046379 | 0.0046183 | 0.0045986 | 0.0045789 | 0.0045593 | 0.0045396 | 0.0045199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-182145838 | 274 | 94 | 0.005191 | 0.0045662 | 0.006611 | 0.0056868 | 0.0060455 | 0.0051354 | 4.0572e-05 | -2.8279e-05 | 0.0064488 | 0.0064893 | 0.0065299 | 0.0065705 | 0.006611 | 0.0065828 | 0.0065545 | 0.0065262 | 0.0064979 | 0.0064696 | 0.0064414 | 0.0064131 | 0.0063848 | 0.0063565 | 0.0063282 | 0.0063 | 0.0062717 | 0.0062434 | 0.0062151 | 0.0061869 | 3.2015e-05 | -2.7569e-05 | 0.0055587 | 0.0055907 | 0.0056227 | 0.0056547 | 0.0056868 | 0.0056592 | 0.0056316 | 0.005604 | 0.0055765 | 0.0055489 | 0.0055213 | 0.0054938 | 0.0054662 | 0.0054386 | 0.0054111 | 0.0053835 | 0.0053559 | 0.0053284 | 0.0053008 | 0.0052732
| HTN013-190418811 | 2423 | 129 | 0.0035892 | 0.0023945 | 0.0052165 | 0.0033257 | 0.004598 | 0.0029304 | 4.6495e-05 | -3.0922e-05 | 0.0050305 | 0.005077 | 0.0051235 | 0.00517 | 0.0052165 | 0.0051856 | 0.0051546 | 0.0051237 | 0.0050928 | 0.0050619 | 0.0050309 | 0.005 | 0.0049691 | 0.0049382 | 0.0049073 | 0.0048763 | 0.0048454 | 0.0048145 | 0.0047836 | 0.0047526 | 2.6605e-05 | -1.9763e-05 | 0.0032193 | 0.0032459 | 0.0032725 | 0.0032991 | 0.0033257 | 0.0033059 | 0.0032862 | 0.0032664 | 0.0032466 | 0.0032269 | 0.0032071 | 0.0031873 | 0.0031676 | 0.0031478 | 0.003128 | 0.0031083 | 0.0030885 | 0.0030688 | 0.003049 | 0.0030292
| HTN013-192570901 | 40 | 40 | 0.0020979 | 0 | 0.0028818 | 0 | 0.0025521 | 0 | 2.2395e-05 | -1.6485e-05 | 0.0027922 | 0.0028146 | 0.002837 | 0.0028594 | 0.0028818 | 0.0028653 | 0.0028488 | 0.0028323 | 0.0028158 | 0.0027993 | 0.0027828 | 0.0027664 | 0.0027499 | 0.0027334 | 0.0027169 | 0.0027004 | 0.0026839 | 0.0026674 | 0.002651 | 0.0026345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN013-201063848 | 960 | 947 | 0.0039199 | 9.87e-07 | 0.0047467 | 1.35e-06 | 0.0041846 | 1.14e-06 | 2.3624e-05 | -2.8105e-05 | 0.0046522 | 0.0046758 | 0.0046995 | 0.0047231 | 0.0047467 | 0.0047186 | 0.0046905 | 0.0046624 | 0.0046343 | 0.0046062 | 0.0045781 | 0.00455 | 0.0045219 | 0.0044938 | 0.0044657 | 0.0044376 | 0.0044094 | 0.0043813 | 0.0043532 | 0.0043251 | 1.0371e-08 | -1.05e-08 | 1.3085e-06 | 1.3189e-06 | 1.3293e-06 | 1.3396e-06 | 1.35e-06 | 1.3395e-06 | 1.329e-06 | 1.3185e-06 | 1.308e-06 | 1.2975e-06 | 1.287e-06 | 1.2765e-06 | 1.266e-06 | 1.2555e-06 | 1.245e-06 | 1.2345e-06 | 1.224e-06 | 1.2135e-06 | 1.203e-06 | 1.1925e-06
| HTN032-159373067 | 34 | 34 | 0.0019016 | 0 | 0.0029365 | 0 | 0.0024283 | 0 | 2.9567e-05 | -2.5411e-05 | 0.0028182 | 0.0028478 | 0.0028774 | 0.0029069 | 0.0029365 | 0.0029111 | 0.0028857 | 0.0028603 | 0.0028349 | 0.0028094 | 0.002784 | 0.0027586 | 0.0027332 | 0.0027078 | 0.0026824 | 0.002657 | 0.0026316 | 0.0026062 | 0.0025807 | 0.0025553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-159377664 | 25 | 25 | 0.0029381 | 0 | 0.0039947 | 0 | 0.0035094 | 0 | 3.0189e-05 | -2.4263e-05 | 0.0038739 | 0.0039041 | 0.0039343 | 0.0039645 | 0.0039947 | 0.0039704 | 0.0039461 | 0.0039219 | 0.0038976 | 0.0038733 | 0.0038491 | 0.0038248 | 0.0038006 | 0.0037763 | 0.003752 | 0.0037278 | 0.0037035 | 0.0036792 | 0.003655 | 0.0036307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-159377774 | 54 | 54 | 0.0017859 | 0 | 0.0021229 | 0 | 0.0020057 | 0 | 9.6282e-06 | -5.8621e-06 | 0.0020844 | 0.002094 | 0.0021037 | 0.0021133 | 0.0021229 | 0.0021171 | 0.0021112 | 0.0021053 | 0.0020995 | 0.0020936 | 0.0020877 | 0.0020819 | 0.002076 | 0.0020702 | 0.0020643 | 0.0020584 | 0.0020526 | 0.0020467 | 0.0020408 | 0.002035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-159443241 | 18 | 18 | 0.00026231 | 0 | 0.00027487 | 0 | 0.00026571 | 0 | 3.5906e-07 | -4.5805e-07 | 0.00027344 | 0.0002738 | 0.00027416 | 0.00027451 | 0.00027487 | 0.00027442 | 0.00027396 | 0.0002735 | 0.00027304 | 0.00027258 | 0.00027213 | 0.00027167 | 0.00027121 | 0.00027075 | 0.00027029 | 0.00026984 | 0.00026938 | 0.00026892 | 0.00026846 | 0.000268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-159443483 | 34 | 34 | 0.0071613 | 0 | 0.0086085 | 0 | 0.0079229 | 0 | 4.1349e-05 | -3.428e-05 | 0.0084431 | 0.0084845 | 0.0085258 | 0.0085672 | 0.0086085 | 0.0085742 | 0.00854 | 0.0085057 | 0.0084714 | 0.0084371 | 0.0084028 | 0.0083686 | 0.0083343 | 0.0083 | 0.0082657 | 0.0082315 | 0.0081972 | 0.0081629 | 0.0081286 | 0.0080943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-159944977 | 21 | 21 | 0.0056291 | 0 | 0.0078471 | 0 | 0.0071687 | 0 | 6.3372e-05 | -3.3918e-05 | 0.0075936 | 0.007657 | 0.0077204 | 0.0077837 | 0.0078471 | 0.0078132 | 0.0077793 | 0.0077453 | 0.0077114 | 0.0076775 | 0.0076436 | 0.0076097 | 0.0075758 | 0.0075418 | 0.0075079 | 0.007474 | 0.0074401 | 0.0074062 | 0.0073722 | 0.0073383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-160369507 | 13 | 13 | 0.0019644 | 0 | 0.0028403 | 0 | 0.0023258 | 0 | 2.5026e-05 | -2.5726e-05 | 0.0027402 | 0.0027652 | 0.0027902 | 0.0028153 | 0.0028403 | 0.0028146 | 0.0027888 | 0.0027631 | 0.0027374 | 0.0027117 | 0.0026859 | 0.0026602 | 0.0026345 | 0.0026088 | 0.002583 | 0.0025573 | 0.0025316 | 0.0025059 | 0.0024801 | 0.0024544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-160369615 | 15 | 15 | 0.0022602 | 0 | 0.0032998 | 0 | 0.0028896 | 0 | 2.9703e-05 | -2.051e-05 | 0.003181 | 0.0032107 | 0.0032404 | 0.0032701 | 0.0032998 | 0.0032793 | 0.0032588 | 0.0032383 | 0.0032178 | 0.0031973 | 0.0031768 | 0.0031563 | 0.0031358 | 0.0031152 | 0.0030947 | 0.0030742 | 0.0030537 | 0.0030332 | 0.0030127 | 0.0029922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-160369738 | 22 | 22 | 0.0030609 | 0 | 0.0042027 | 0 | 0.003572 | 0 | 3.2623e-05 | -3.1534e-05 | 0.0040722 | 0.0041048 | 0.0041374 | 0.00417 | 0.0042027 | 0.0041711 | 0.0041396 | 0.004108 | 0.0040765 | 0.004045 | 0.0040134 | 0.0039819 | 0.0039504 | 0.0039188 | 0.0038873 | 0.0038558 | 0.0038242 | 0.0037927 | 0.0037612 | 0.0037296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-162635166 | 5 | 5 | 1.18e-05 | 0 | 1.92e-05 | 0 | 1.74e-05 | 0 | 2.1143e-07 | -9e-08 | 1.8354e-05 | 1.8566e-05 | 1.8777e-05 | 1.8989e-05 | 1.92e-05 | 1.911e-05 | 1.902e-05 | 1.893e-05 | 1.884e-05 | 1.875e-05 | 1.866e-05 | 1.857e-05 | 1.848e-05 | 1.839e-05 | 1.83e-05 | 1.821e-05 | 1.812e-05 | 1.803e-05 | 1.794e-05 | 1.785e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-162645765 | 10 | 10 | 0.0028981 | 0 | 0.0038198 | 0 | 0.003399 | 0 | 2.6334e-05 | -2.104e-05 | 0.0037144 | 0.0037408 | 0.0037671 | 0.0037934 | 0.0038198 | 0.0037987 | 0.0037777 | 0.0037566 | 0.0037356 | 0.0037146 | 0.0036935 | 0.0036725 | 0.0036514 | 0.0036304 | 0.0036094 | 0.0035883 | 0.0035673 | 0.0035462 | 0.0035252 | 0.0035042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-162671033 | 18 | 18 | 0.001736 | 0 | 0.0024236 | 0 | 0.0019874 | 0 | 1.9645e-05 | -2.1809e-05 | 0.002345 | 0.0023647 | 0.0023843 | 0.002404 | 0.0024236 | 0.0024018 | 0.00238 | 0.0023582 | 0.0023364 | 0.0023146 | 0.0022928 | 0.002271 | 0.0022491 | 0.0022273 | 0.0022055 | 0.0021837 | 0.0021619 | 0.0021401 | 0.0021183 | 0.0020965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-162671207 | 3 | 3 | 0.00029068 | 0 | 0.00041878 | 0 | 0.00037934 | 0 | 3.6599e-06 | -1.972e-06 | 0.00040414 | 0.0004078 | 0.00041146 | 0.00041512 | 0.00041878 | 0.00041681 | 0.00041484 | 0.00041286 | 0.00041089 | 0.00040892 | 0.00040695 | 0.00040498 | 0.000403 | 0.00040103 | 0.00039906 | 0.00039709 | 0.00039512 | 0.00039314 | 0.00039117 | 0.0003892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-162798482 | 32 | 32 | 0.0029338 | 0 | 0.0036899 | 0 | 0.0034354 | 0 | 2.1603e-05 | -1.2725e-05 | 0.0036035 | 0.0036251 | 0.0036467 | 0.0036683 | 0.0036899 | 0.0036772 | 0.0036644 | 0.0036517 | 0.003639 | 0.0036263 | 0.0036135 | 0.0036008 | 0.0035881 | 0.0035754 | 0.0035626 | 0.0035499 | 0.0035372 | 0.0035245 | 0.0035117 | 0.003499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN032-187419014 | 927 | 697 | 0.014927 | 0.0065244 | 0.020397 | 0.0085278 | 0.018305 | 0.007583 | 0.00015628 | -0.00010456 | 0.019771 | 0.019928 | 0.020084 | 0.02024 | 0.020397 | 0.020292 | 0.020187 | 0.020083 | 0.019978 | 0.019874 | 0.019769 | 0.019665 | 0.01956 | 0.019456 | 0.019351 | 0.019246 | 0.019142 | 0.019037 | 0.018933 | 0.018828 | 5.7238e-05 | -4.7237e-05 | 0.0082988 | 0.0083561 | 0.0084133 | 0.0084705 | 0.0085278 | 0.0084805 | 0.0084333 | 0.0083861 | 0.0083388 | 0.0082916 | 0.0082444 | 0.0081971 | 0.0081499 | 0.0081026 | 0.0080554 | 0.0080082 | 0.0079609 | 0.0079137 | 0.0078665 | 0.0078192
| HTN032-190418526 | 3106 | 2105 | 0.027478 | 0.0040159 | 0.03361 | 0.0056656 | 0.029572 | 0.0046191 | 0.0001752 | -0.00020189 | 0.032909 | 0.033084 | 0.033259 | 0.033434 | 0.03361 | 0.033408 | 0.033206 | 0.033004 | 0.032802 | 0.0326 | 0.032398 | 0.032196 | 0.031995 | 0.031793 | 0.031591 | 0.031389 | 0.031187 | 0.030985 | 0.030783 | 0.030581 | 4.7134e-05 | -5.2325e-05 | 0.0054771 | 0.0055242 | 0.0055714 | 0.0056185 | 0.0056656 | 0.0056133 | 0.005561 | 0.0055087 | 0.0054563 | 0.005404 | 0.0053517 | 0.0052994 | 0.005247 | 0.0051947 | 0.0051424 | 0.0050901 | 0.0050377 | 0.0049854 | 0.0049331 | 0.0048807
| HTN033-107035043 | 27 | 27 | 0.0019794 | 0 | 0.0025119 | 0 | 0.0024024 | 0 | 1.5214e-05 | -5.476e-06 | 0.0024511 | 0.0024663 | 0.0024815 | 0.0024967 | 0.0025119 | 0.0025064 | 0.002501 | 0.0024955 | 0.00249 | 0.0024845 | 0.0024791 | 0.0024736 | 0.0024681 | 0.0024626 | 0.0024572 | 0.0024517 | 0.0024462 | 0.0024407 | 0.0024352 | 0.0024298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN033-142434533 | 29 | 29 | 0.0026313 | 0 | 0.0034622 | 0 | 0.0032542 | 0 | 2.374e-05 | -1.0397e-05 | 0.0033672 | 0.003391 | 0.0034147 | 0.0034384 | 0.0034622 | 0.0034518 | 0.0034414 | 0.003431 | 0.0034206 | 0.0034102 | 0.0033998 | 0.0033894 | 0.003379 | 0.0033686 | 0.0033582 | 0.0033478 | 0.0033374 | 0.003327 | 0.0033166 | 0.0033062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN033-159363700 | 41 | 41 | 0.00064703 | 0 | 0.00088586 | 0 | 0.00076213 | 0 | 6.8237e-06 | -6.1862e-06 | 0.00085856 | 0.00086539 | 0.00087221 | 0.00087904 | 0.00088586 | 0.00087967 | 0.00087349 | 0.0008673 | 0.00086111 | 0.00085493 | 0.00084874 | 0.00084256 | 0.00083637 | 0.00083018 | 0.000824 | 0.00081781 | 0.00081162 | 0.00080544 | 0.00079925 | 0.00079307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN033-159373503 | 19 | 19 | 0.0030593 | 0 | 0.0040107 | 0 | 0.0036334 | 0 | 2.7185e-05 | -1.8867e-05 | 0.003902 | 0.0039292 | 0.0039564 | 0.0039836 | 0.0040107 | 0.0039919 | 0.003973 | 0.0039541 | 0.0039353 | 0.0039164 | 0.0038975 | 0.0038787 | 0.0038598 | 0.0038409 | 0.0038221 | 0.0038032 | 0.0037843 | 0.0037655 | 0.0037466 | 0.0037277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN033-159373599 | 27 | 27 | 0.0061954 | 0 | 0.0077439 | 0 | 0.0069525 | 0 | 4.4243e-05 | -3.9568e-05 | 0.0075669 | 0.0076111 | 0.0076554 | 0.0076996 | 0.0077439 | 0.0077043 | 0.0076647 | 0.0076252 | 0.0075856 | 0.007546 | 0.0075065 | 0.0074669 | 0.0074273 | 0.0073878 | 0.0073482 | 0.0073086 | 0.0072691 | 0.0072295 | 0.0071899 | 0.0071504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN033-159944283 | 34 | 34 | 0.0027165 | 0 | 0.0036325 | 0 | 0.0033401 | 0 | 2.6172e-05 | -1.4624e-05 | 0.0035279 | 0.003554 | 0.0035802 | 0.0036064 | 0.0036325 | 0.0036179 | 0.0036033 | 0.0035887 | 0.003574 | 0.0035594 | 0.0035448 | 0.0035302 | 0.0035156 | 0.0035009 | 0.0034863 | 0.0034717 | 0.0034571 | 0.0034424 | 0.0034278 | 0.0034132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN033-159944367 | 20 | 20 | 0.0015839 | 0 | 0.0023006 | 0 | 0.0019362 | 0 | 2.0479e-05 | -1.822e-05 | 0.0022187 | 0.0022392 | 0.0022597 | 0.0022801 | 0.0023006 | 0.0022824 | 0.0022642 | 0.002246 | 0.0022277 | 0.0022095 | 0.0021913 | 0.0021731 | 0.0021549 | 0.0021366 | 0.0021184 | 0.0021002 | 0.002082 | 0.0020638 | 0.0020455 | 0.0020273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN033-159944491 | 32 | 32 | 0.0018702 | 0 | 0.0024545 | 0 | 0.002197 | 0 | 1.6695e-05 | -1.2877e-05 | 0.0023877 | 0.0024044 | 0.0024211 | 0.0024378 | 0.0024545 | 0.0024416 | 0.0024288 | 0.0024159 | 0.002403 | 0.0023901 | 0.0023773 | 0.0023644 | 0.0023515 | 0.0023386 | 0.0023258 | 0.0023129 | 0.0023 | 0.0022871 | 0.0022742 | 0.0022614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN033-159944618 | 17 | 17 | 0.0020907 | 0 | 0.0027785 | 0 | 0.0024223 | 0 | 1.9654e-05 | -1.781e-05 | 0.0026999 | 0.0027196 | 0.0027392 | 0.0027589 | 0.0027785 | 0.0027607 | 0.0027429 | 0.0027251 | 0.0027073 | 0.0026895 | 0.0026717 | 0.0026539 | 0.0026361 | 0.0026183 | 0.0026004 | 0.0025826 | 0.0025648 | 0.002547 | 0.0025292 | 0.0025114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN033-162626258 | 3 | 3 | 0.0015133 | 0 | 0.0021242 | 0 | 0.001833 | 0 | 1.7454e-05 | -1.456e-05 | 0.0020544 | 0.0020718 | 0.0020893 | 0.0021067 | 0.0021242 | 0.0021096 | 0.0020951 | 0.0020805 | 0.0020659 | 0.0020514 | 0.0020368 | 0.0020223 | 0.0020077 | 0.0019931 | 0.0019786 | 0.001964 | 0.0019495 | 0.0019349 | 0.0019204 | 0.0019058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN033-162670429 | 1 | 1 | 8.57e-06 | 0 | 1.12e-05 | 0 | 1.04e-05 | 0 | 7.5143e-08 | -4e-08 | 1.0899e-05 | 1.0975e-05 | 1.105e-05 | 1.1125e-05 | 1.12e-05 | 1.116e-05 | 1.112e-05 | 1.108e-05 | 1.104e-05 | 1.1e-05 | 1.096e-05 | 1.092e-05 | 1.088e-05 | 1.084e-05 | 1.08e-05 | 1.076e-05 | 1.072e-05 | 1.068e-05 | 1.064e-05 | 1.06e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN033-162670652 | 4 | 4 | 3.06e-05 | 0 | 3.1e-05 | 0 | 3.07e-05 | 0 | 1.1429e-08 | -1.5e-08 | 3.0954e-05 | 3.0966e-05 | 3.0977e-05 | 3.0989e-05 | 3.1e-05 | 3.0985e-05 | 3.097e-05 | 3.0955e-05 | 3.094e-05 | 3.0925e-05 | 3.091e-05 | 3.0895e-05 | 3.088e-05 | 3.0865e-05 | 3.085e-05 | 3.0835e-05 | 3.082e-05 | 3.0805e-05 | 3.079e-05 | 3.0775e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN033-182145786 | 572 | 259 | 0.0062238 | 0.0046692 | 0.0065925 | 0.0050234 | 0.0063218 | 0.0047652 | 1.0534e-05 | -1.3532e-05 | 0.0065503 | 0.0065609 | 0.0065714 | 0.006582 | 0.0065925 | 0.006579 | 0.0065654 | 0.0065519 | 0.0065384 | 0.0065248 | 0.0065113 | 0.0064978 | 0.0064842 | 0.0064707 | 0.0064572 | 0.0064436 | 0.0064301 | 0.0064166 | 0.006403 | 0.0063895 | 1.012e-05 | -1.2912e-05 | 0.004983 | 0.0049931 | 0.0050032 | 0.0050133 | 0.0050234 | 0.0050105 | 0.0049976 | 0.0049847 | 0.0049718 | 0.0049589 | 0.004946 | 0.0049331 | 0.0049202 | 0.0049072 | 0.0048943 | 0.0048814 | 0.0048685 | 0.0048556 | 0.0048427 | 0.0048298
| HTN033-190418479 | 3373 | 2801 | 0.0057257 | 0.0011733 | 0.0082611 | 0.0017531 | 0.0066906 | 0.0013994 | 7.2438e-05 | -7.8524e-05 | 0.0079713 | 0.0080437 | 0.0081162 | 0.0081886 | 0.0082611 | 0.0081825 | 0.008104 | 0.0080255 | 0.007947 | 0.0078684 | 0.0077899 | 0.0077114 | 0.0076329 | 0.0075543 | 0.0074758 | 0.0073973 | 0.0073188 | 0.0072402 | 0.0071617 | 0.0070832 | 1.6565e-05 | -1.7686e-05 | 0.0016868 | 0.0017034 | 0.00172 | 0.0017365 | 0.0017531 | 0.0017354 | 0.0017177 | 0.0017 | 0.0016823 | 0.0016647 | 0.001647 | 0.0016293 | 0.0016116 | 0.0015939 | 0.0015762 | 0.0015585 | 0.0015409 | 0.0015232 | 0.0015055 | 0.0014878
| HTN034-100723274 | 213 | 50 | 0.00069714 | 0.0028021 | 0.00084523 | 0.0034181 | 0.00074308 | 0.0029992 | 4.231e-06 | -5.1072e-06 | 0.0008283 | 0.00083254 | 0.00083677 | 0.000841 | 0.00084523 | 0.00084012 | 0.00083501 | 0.00082991 | 0.0008248 | 0.00081969 | 0.00081458 | 0.00080948 | 0.00080437 | 0.00079926 | 0.00079416 | 0.00078905 | 0.00078394 | 0.00077883 | 0.00077373 | 0.00076862 | 1.76e-05 | -2.0946e-05 | 0.0033477 | 0.0033653 | 0.0033829 | 0.0034005 | 0.0034181 | 0.0033972 | 0.0033762 | 0.0033553 | 0.0033344 | 0.0033134 | 0.0032925 | 0.0032715 | 0.0032506 | 0.0032296 | 0.0032087 | 0.0031877 | 0.0031668 | 0.0031458 | 0.0031249 | 0.003104
| HTN034-108340859 | 561 | 184 | 0.014772 | 0.0072704 | 0.018508 | 0.0092059 | 0.016325 | 0.0080623 | 0.00010675 | -0.00010916 | 0.018081 | 0.018188 | 0.018295 | 0.018401 | 0.018508 | 0.018399 | 0.01829 | 0.018181 | 0.018071 | 0.017962 | 0.017853 | 0.017744 | 0.017635 | 0.017526 | 0.017416 | 0.017307 | 0.017198 | 0.017089 | 0.01698 | 0.016871 | 5.5297e-05 | -5.7176e-05 | 0.0089847 | 0.00904 | 0.0090953 | 0.0091506 | 0.0092059 | 0.0091487 | 0.0090915 | 0.0090343 | 0.0089772 | 0.00892 | 0.0088628 | 0.0088056 | 0.0087485 | 0.0086913 | 0.0086341 | 0.0085769 | 0.0085198 | 0.0084626 | 0.0084054 | 0.0083482
| HTN034-142233453 | 19 | 19 | 0.0073595 | 0 | 0.0098876 | 0 | 0.0069741 | 0 | 7.223e-05 | -0.00014568 | 0.0095987 | 0.0096709 | 0.0097431 | 0.0098153 | 0.0098876 | 0.0097419 | 0.0095962 | 0.0094505 | 0.0093049 | 0.0091592 | 0.0090135 | 0.0088678 | 0.0087222 | 0.0085765 | 0.0084308 | 0.0082851 | 0.0081395 | 0.0079938 | 0.0078481 | 0.0077024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-142233590 | 26 | 26 | 0.0025058 | 0 | 0.0035909 | 0 | 0.0028042 | 0 | 3.1002e-05 | -3.9335e-05 | 0.0034669 | 0.0034979 | 0.0035289 | 0.0035599 | 0.0035909 | 0.0035516 | 0.0035122 | 0.0034729 | 0.0034336 | 0.0033942 | 0.0033549 | 0.0033156 | 0.0032762 | 0.0032369 | 0.0031976 | 0.0031582 | 0.0031189 | 0.0030796 | 0.0030402 | 0.0030009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-142234012 | 38 | 38 | 0.0032214 | 0 | 0.0038605 | 0 | 0.0033931 | 0 | 1.8257e-05 | -2.337e-05 | 0.0037874 | 0.0038057 | 0.0038239 | 0.0038422 | 0.0038605 | 0.0038371 | 0.0038137 | 0.0037903 | 0.003767 | 0.0037436 | 0.0037202 | 0.0036969 | 0.0036735 | 0.0036501 | 0.0036268 | 0.0036034 | 0.00358 | 0.0035566 | 0.0035333 | 0.0035099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-157456094 | 25 | 25 | 0.00022379 | 0 | 0.00027763 | 0 | 0.00024612 | 0 | 1.5381e-06 | -1.5751e-06 | 0.00027147 | 0.00027301 | 0.00027455 | 0.00027609 | 0.00027763 | 0.00027605 | 0.00027448 | 0.0002729 | 0.00027133 | 0.00026975 | 0.00026818 | 0.0002666 | 0.00026503 | 0.00026345 | 0.00026188 | 0.0002603 | 0.00025873 | 0.00025715 | 0.00025558 | 0.000254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-157599634 | 28 | 28 | 0.0019596 | 0 | 0.0023354 | 0 | 0.0020884 | 0 | 1.0738e-05 | -1.2354e-05 | 0.0022925 | 0.0023032 | 0.002314 | 0.0023247 | 0.0023354 | 0.0023231 | 0.0023107 | 0.0022984 | 0.002286 | 0.0022737 | 0.0022613 | 0.002249 | 0.0022366 | 0.0022243 | 0.0022119 | 0.0021995 | 0.0021872 | 0.0021748 | 0.0021625 | 0.0021501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-157998388 | 19 | 19 | 0.001912 | 0 | 0.0023635 | 0 | 0.0020355 | 0 | 1.29e-05 | -1.6399e-05 | 0.0023119 | 0.0023248 | 0.0023377 | 0.0023506 | 0.0023635 | 0.0023471 | 0.0023307 | 0.0023143 | 0.0022979 | 0.0022815 | 0.0022651 | 0.0022487 | 0.0022323 | 0.0022159 | 0.0021995 | 0.0021831 | 0.0021667 | 0.0021503 | 0.0021339 | 0.0021175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-157998738 | 11 | 11 | 0.00090028 | 0 | 0.0011251 | 0 | 0.00091282 | 0 | 6.4228e-06 | -1.0613e-05 | 0.0010994 | 0.0011058 | 0.0011122 | 0.0011187 | 0.0011251 | 0.0011145 | 0.0011038 | 0.0010932 | 0.0010826 | 0.001072 | 0.0010614 | 0.0010508 | 0.0010402 | 0.0010296 | 0.0010189 | 0.0010083 | 0.00099772 | 0.00098711 | 0.0009765 | 0.00096588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-157999069 | 24 | 24 | 0.0021377 | 0 | 0.0026245 | 0 | 0.0022804 | 0 | 1.3908e-05 | -1.7206e-05 | 0.0025689 | 0.0025828 | 0.0025967 | 0.0026106 | 0.0026245 | 0.0026073 | 0.0025901 | 0.0025729 | 0.0025557 | 0.0025385 | 0.0025213 | 0.0025041 | 0.0024869 | 0.0024697 | 0.0024525 | 0.0024353 | 0.0024181 | 0.0024009 | 0.0023836 | 0.0023664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158085792 | 19 | 19 | 0.00091461 | 0 | 0.001283 | 0 | 0.0010214 | 0 | 1.0525e-05 | -1.3081e-05 | 0.0012409 | 0.0012514 | 0.0012619 | 0.0012725 | 0.001283 | 0.0012699 | 0.0012568 | 0.0012437 | 0.0012307 | 0.0012176 | 0.0012045 | 0.0011914 | 0.0011783 | 0.0011653 | 0.0011522 | 0.0011391 | 0.001126 | 0.0011129 | 0.0010999 | 0.0010868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158085879 | 53 | 53 | 0.0032346 | 0 | 0.0044752 | 0 | 0.0037759 | 0 | 3.5443e-05 | -3.4964e-05 | 0.0043334 | 0.0043688 | 0.0044043 | 0.0044397 | 0.0044752 | 0.0044402 | 0.0044052 | 0.0043703 | 0.0043353 | 0.0043003 | 0.0042654 | 0.0042304 | 0.0041954 | 0.0041605 | 0.0041255 | 0.0040906 | 0.0040556 | 0.0040206 | 0.0039857 | 0.0039507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158086014 | 13 | 13 | 1.66e-06 | 0 | 2.58e-06 | 0 | 2.09e-06 | 0 | 2.6286e-08 | -2.45e-08 | 2.4749e-06 | 2.5011e-06 | 2.5274e-06 | 2.5537e-06 | 2.58e-06 | 2.5555e-06 | 2.531e-06 | 2.5065e-06 | 2.482e-06 | 2.4575e-06 | 2.433e-06 | 2.4085e-06 | 2.384e-06 | 2.3595e-06 | 2.335e-06 | 2.3105e-06 | 2.286e-06 | 2.2615e-06 | 2.237e-06 | 2.2125e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158095163 | 5 | 5 | 0.0074855 | 0 | 0.0088787 | 0 | 0.008092 | 0 | 3.9805e-05 | -3.9335e-05 | 0.0087195 | 0.0087593 | 0.0087991 | 0.0088389 | 0.0088787 | 0.0088393 | 0.0088 | 0.0087607 | 0.0087213 | 0.008682 | 0.0086427 | 0.0086033 | 0.008564 | 0.0085247 | 0.0084853 | 0.008446 | 0.0084067 | 0.0083673 | 0.008328 | 0.0082887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158103724 | 14 | 14 | 0.0040285 | 0 | 0.0051345 | 0 | 0.0043468 | 0 | 3.16e-05 | -3.9383e-05 | 0.0050081 | 0.0050397 | 0.0050713 | 0.0051029 | 0.0051345 | 0.0050951 | 0.0050557 | 0.0050163 | 0.004977 | 0.0049376 | 0.0048982 | 0.0048588 | 0.0048194 | 0.00478 | 0.0047407 | 0.0047013 | 0.0046619 | 0.0046225 | 0.0045831 | 0.0045437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158130464 | 27 | 27 | 0.0013083 | 0 | 0.0016339 | 0 | 0.0013932 | 0 | 9.3014e-06 | -1.2034e-05 | 0.0015967 | 0.001606 | 0.0016153 | 0.0016246 | 0.0016339 | 0.0016219 | 0.0016098 | 0.0015978 | 0.0015858 | 0.0015737 | 0.0015617 | 0.0015497 | 0.0015376 | 0.0015256 | 0.0015136 | 0.0015015 | 0.0014895 | 0.0014775 | 0.0014654 | 0.0014534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158139663 | 23 | 23 | 0.00037499 | 0 | 0.00045627 | 0 | 0.00040201 | 0 | 2.3223e-06 | -2.713e-06 | 0.00044698 | 0.0004493 | 0.00045162 | 0.00045395 | 0.00045627 | 0.00045356 | 0.00045084 | 0.00044813 | 0.00044542 | 0.0004427 | 0.00043999 | 0.00043728 | 0.00043456 | 0.00043185 | 0.00042914 | 0.00042643 | 0.00042371 | 0.000421 | 0.00041829 | 0.00041557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158494823 | 53 | 53 | 0.0058696 | 0 | 0.0080387 | 0 | 0.0060643 | 0 | 6.1975e-05 | -9.8719e-05 | 0.0077908 | 0.0078528 | 0.0079148 | 0.0079767 | 0.0080387 | 0.00794 | 0.0078413 | 0.0077426 | 0.0076438 | 0.0075451 | 0.0074464 | 0.0073477 | 0.007249 | 0.0071502 | 0.0070515 | 0.0069528 | 0.0068541 | 0.0067554 | 0.0066566 | 0.0065579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158495102 | 10 | 10 | 0.00060203 | 0 | 0.00093607 | 0 | 0.00076539 | 0 | 9.5441e-06 | -8.5342e-06 | 0.0008979 | 0.00090744 | 0.00091698 | 0.00092653 | 0.00093607 | 0.00092754 | 0.000919 | 0.00091047 | 0.00090194 | 0.0008934 | 0.00088487 | 0.00087633 | 0.0008678 | 0.00085926 | 0.00085073 | 0.0008422 | 0.00083366 | 0.00082513 | 0.00081659 | 0.00080806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158495212 | 28 | 28 | 0.0003312 | 0 | 0.00046188 | 0 | 0.00036682 | 0 | 3.7338e-06 | -4.7531e-06 | 0.00044695 | 0.00045068 | 0.00045441 | 0.00045815 | 0.00046188 | 0.00045713 | 0.00045237 | 0.00044762 | 0.00044287 | 0.00043812 | 0.00043336 | 0.00042861 | 0.00042386 | 0.0004191 | 0.00041435 | 0.0004096 | 0.00040484 | 0.00040009 | 0.00039534 | 0.00039058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158638369 | 24 | 24 | 0.0010616 | 0 | 0.0014464 | 0 | 0.0011664 | 0 | 1.0994e-05 | -1.3999e-05 | 0.0014024 | 0.0014134 | 0.0014244 | 0.0014354 | 0.0014464 | 0.0014324 | 0.0014184 | 0.0014044 | 0.0013904 | 0.0013764 | 0.0013624 | 0.0013484 | 0.0013344 | 0.0013204 | 0.0013064 | 0.0012924 | 0.0012784 | 0.0012644 | 0.0012504 | 0.0012364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158638445 | 19 | 19 | 0.00084246 | 0 | 0.0011903 | 0 | 0.0008365 | 0 | 9.9371e-06 | -1.7688e-05 | 0.0011505 | 0.0011604 | 0.0011704 | 0.0011803 | 0.0011903 | 0.0011726 | 0.0011549 | 0.0011372 | 0.0011195 | 0.0011018 | 0.0010841 | 0.0010664 | 0.0010488 | 0.0010311 | 0.0010134 | 0.00099569 | 0.000978 | 0.00096031 | 0.00094263 | 0.00092494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158638542 | 31 | 31 | 0.0016827 | 0 | 0.0021401 | 0 | 0.0016407 | 0 | 1.307e-05 | -2.4968e-05 | 0.0020878 | 0.0021009 | 0.002114 | 0.002127 | 0.0021401 | 0.0021151 | 0.0020902 | 0.0020652 | 0.0020402 | 0.0020153 | 0.0019903 | 0.0019653 | 0.0019404 | 0.0019154 | 0.0018904 | 0.0018655 | 0.0018405 | 0.0018155 | 0.0017906 | 0.0017656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158638725 | 13 | 13 | 0.0015122 | 0 | 0.0021835 | 0 | 0.0018094 | 0 | 1.918e-05 | -1.8708e-05 | 0.0021068 | 0.002126 | 0.0021452 | 0.0021644 | 0.0021835 | 0.0021648 | 0.0021461 | 0.0021274 | 0.0021087 | 0.00209 | 0.0020713 | 0.0020526 | 0.0020339 | 0.0020152 | 0.0019965 | 0.0019777 | 0.001959 | 0.0019403 | 0.0019216 | 0.0019029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158639522 | 11 | 11 | 4.76e-06 | 0 | 5.79e-06 | 0 | 5.18e-06 | 0 | 2.9429e-08 | -3.05e-08 | 5.6723e-06 | 5.7017e-06 | 5.7311e-06 | 5.7606e-06 | 5.79e-06 | 5.7595e-06 | 5.729e-06 | 5.6985e-06 | 5.668e-06 | 5.6375e-06 | 5.607e-06 | 5.5765e-06 | 5.546e-06 | 5.5155e-06 | 5.485e-06 | 5.4545e-06 | 5.424e-06 | 5.3935e-06 | 5.363e-06 | 5.3325e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158639644 | 19 | 19 | 0.0014039 | 0 | 0.0020195 | 0 | 0.0016174 | 0 | 1.7589e-05 | -2.0103e-05 | 0.0019491 | 0.0019667 | 0.0019843 | 0.0020019 | 0.0020195 | 0.0019994 | 0.0019793 | 0.0019592 | 0.0019391 | 0.001919 | 0.0018989 | 0.0018788 | 0.0018587 | 0.0018386 | 0.0018185 | 0.0017984 | 0.0017783 | 0.0017582 | 0.001738 | 0.0017179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158639828 | 11 | 11 | 0.0013593 | 0 | 0.0017006 | 0 | 0.0013908 | 0 | 9.7517e-06 | -1.549e-05 | 0.0016616 | 0.0016714 | 0.0016811 | 0.0016909 | 0.0017006 | 0.0016852 | 0.0016697 | 0.0016542 | 0.0016387 | 0.0016232 | 0.0016077 | 0.0015922 | 0.0015767 | 0.0015612 | 0.0015457 | 0.0015303 | 0.0015148 | 0.0014993 | 0.0014838 | 0.0014683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158639936 | 1 | 1 | 0.0038775 | 0 | 0.0048308 | 0 | 0.0037758 | 0 | 2.7236e-05 | -5.275e-05 | 0.0047218 | 0.0047491 | 0.0047763 | 0.0048035 | 0.0048308 | 0.004778 | 0.0047253 | 0.0046725 | 0.0046198 | 0.004567 | 0.0045143 | 0.0044615 | 0.0044088 | 0.004356 | 0.0043033 | 0.0042505 | 0.0041978 | 0.004145 | 0.0040923 | 0.0040395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158640079 | 18 | 18 | 1.12e-05 | 0 | 1.44e-05 | 0 | 1.28e-05 | 0 | 9.1429e-08 | -8e-08 | 1.4034e-05 | 1.4126e-05 | 1.4217e-05 | 1.4309e-05 | 1.44e-05 | 1.432e-05 | 1.424e-05 | 1.416e-05 | 1.408e-05 | 1.4e-05 | 1.392e-05 | 1.384e-05 | 1.376e-05 | 1.368e-05 | 1.36e-05 | 1.352e-05 | 1.344e-05 | 1.336e-05 | 1.328e-05 | 1.32e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158770728 | 38 | 38 | 0.00090902 | 0 | 0.00098498 | 0 | 0.00091991 | 0 | 2.1703e-06 | -3.2534e-06 | 0.0009763 | 0.00097847 | 0.00098064 | 0.00098281 | 0.00098498 | 0.00098173 | 0.00097847 | 0.00097522 | 0.00097197 | 0.00096871 | 0.00096546 | 0.00096221 | 0.00095895 | 0.0009557 | 0.00095245 | 0.00094919 | 0.00094594 | 0.00094269 | 0.00093943 | 0.00093618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-158770892 | 56 | 56 | 0.0046931 | 0 | 0.0068741 | 0 | 0.0046283 | 0 | 6.2314e-05 | -0.00011229 | 0.0066248 | 0.0066871 | 0.0067495 | 0.0068118 | 0.0068741 | 0.0067618 | 0.0066495 | 0.0065372 | 0.0064249 | 0.0063126 | 0.0062003 | 0.0060881 | 0.0059758 | 0.0058635 | 0.0057512 | 0.0056389 | 0.0055266 | 0.0054143 | 0.005302 | 0.0051897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-160807148 | 23 | 23 | 0.0015226 | 0 | 0.0022546 | 0 | 0.0016591 | 0 | 2.0915e-05 | -2.9773e-05 | 0.0021709 | 0.0021919 | 0.0022128 | 0.0022337 | 0.0022546 | 0.0022248 | 0.0021951 | 0.0021653 | 0.0021355 | 0.0021057 | 0.002076 | 0.0020462 | 0.0020164 | 0.0019866 | 0.0019569 | 0.0019271 | 0.0018973 | 0.0018675 | 0.0018378 | 0.001808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-161079325 | 22 | 22 | 0.0092012 | 0 | 0.012057 | 0 | 0.0097814 | 0 | 8.1586e-05 | -0.00011377 | 0.01173 | 0.011812 | 0.011894 | 0.011975 | 0.012057 | 0.011943 | 0.011829 | 0.011715 | 0.011602 | 0.011488 | 0.011374 | 0.01126 | 0.011147 | 0.011033 | 0.010919 | 0.010805 | 0.010691 | 0.010578 | 0.010464 | 0.01035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-161093808 | 19 | 19 | 0.0090088 | 0 | 0.011642 | 0 | 0.010195 | 0 | 7.5228e-05 | -7.2353e-05 | 0.011341 | 0.011416 | 0.011491 | 0.011567 | 0.011642 | 0.011569 | 0.011497 | 0.011425 | 0.011352 | 0.01128 | 0.011208 | 0.011135 | 0.011063 | 0.010991 | 0.010918 | 0.010846 | 0.010774 | 0.010701 | 0.010629 | 0.010557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-162616477 | 7 | 7 | 0.00038636 | 0 | 0.00051466 | 0 | 0.00043473 | 0 | 3.6658e-06 | -3.9965e-06 | 0.0005 | 0.00050366 | 0.00050733 | 0.00051099 | 0.00051466 | 0.00051066 | 0.00050667 | 0.00050267 | 0.00049867 | 0.00049468 | 0.00049068 | 0.00048668 | 0.00048269 | 0.00047869 | 0.00047469 | 0.0004707 | 0.0004667 | 0.0004627 | 0.00045871 | 0.00045471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-162616681 | 4 | 4 | 0.00039374 | 0 | 0.000485 | 0 | 0.00042578 | 0 | 2.6073e-06 | -2.9608e-06 | 0.00047457 | 0.00047718 | 0.00047978 | 0.00048239 | 0.000485 | 0.00048204 | 0.00047908 | 0.00047611 | 0.00047315 | 0.00047019 | 0.00046723 | 0.00046427 | 0.00046131 | 0.00045835 | 0.00045539 | 0.00045243 | 0.00044947 | 0.00044651 | 0.00044355 | 0.00044059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-162616888 | 3 | 3 | 0.00084032 | 0 | 0.0010065 | 0 | 0.00090715 | 0 | 4.7484e-06 | -4.9678e-06 | 0.00098752 | 0.00099227 | 0.00099701 | 0.0010018 | 0.0010065 | 0.0010015 | 0.00099658 | 0.00099161 | 0.00098664 | 0.00098167 | 0.0009767 | 0.00097174 | 0.00096677 | 0.0009618 | 0.00095683 | 0.00095187 | 0.0009469 | 0.00094193 | 0.00093696 | 0.00093199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-162617230 | 1 | 1 | 0.0043675 | 0 | 0.005631 | 0 | 0.0048358 | 0 | 3.61e-05 | -3.9761e-05 | 0.0054866 | 0.0055227 | 0.0055588 | 0.0055949 | 0.005631 | 0.0055912 | 0.0055515 | 0.0055117 | 0.0054719 | 0.0054322 | 0.0053924 | 0.0053527 | 0.0053129 | 0.0052731 | 0.0052334 | 0.0051936 | 0.0051539 | 0.0051141 | 0.0050743 | 0.0050346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-162626507 | 6 | 6 | 0.00082811 | 0 | 0.0013719 | 0 | 0.00083507 | 0 | 1.5537e-05 | -2.6842e-05 | 0.0013098 | 0.0013253 | 0.0013408 | 0.0013564 | 0.0013719 | 0.0013451 | 0.0013182 | 0.0012914 | 0.0012645 | 0.0012377 | 0.0012109 | 0.001184 | 0.0011572 | 0.0011303 | 0.0011035 | 0.0010766 | 0.0010498 | 0.001023 | 0.00099612 | 0.00096928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-162646056 | 11 | 11 | 0.0018309 | 0 | 0.0022721 | 0 | 0.0019574 | 0 | 1.2607e-05 | -1.5735e-05 | 0.0022217 | 0.0022343 | 0.0022469 | 0.0022595 | 0.0022721 | 0.0022564 | 0.0022406 | 0.0022249 | 0.0022092 | 0.0021934 | 0.0021777 | 0.002162 | 0.0021462 | 0.0021305 | 0.0021148 | 0.002099 | 0.0020833 | 0.0020675 | 0.0020518 | 0.0020361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-162671356 | 5 | 5 | 0.0016151 | 0 | 0.0024653 | 0 | 0.0015343 | 0 | 2.4291e-05 | -4.6551e-05 | 0.0023681 | 0.0023924 | 0.0024167 | 0.002441 | 0.0024653 | 0.0024188 | 0.0023722 | 0.0023257 | 0.0022791 | 0.0022326 | 0.002186 | 0.0021395 | 0.0020929 | 0.0020463 | 0.0019998 | 0.0019532 | 0.0019067 | 0.0018601 | 0.0018136 | 0.001767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-162794244 | 22 | 22 | 1.56e-05 | 0 | 2.02e-05 | 0 | 1.86e-05 | 0 | 1.3143e-07 | -8e-08 | 1.9674e-05 | 1.9806e-05 | 1.9937e-05 | 2.0069e-05 | 2.02e-05 | 2.012e-05 | 2.004e-05 | 1.996e-05 | 1.988e-05 | 1.98e-05 | 1.972e-05 | 1.964e-05 | 1.956e-05 | 1.948e-05 | 1.94e-05 | 1.932e-05 | 1.924e-05 | 1.916e-05 | 1.908e-05 | 1.9e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-162794768 | 6 | 6 | 0.0014689 | 0 | 0.0018033 | 0 | 0.0015802 | 0 | 9.5567e-06 | -1.1158e-05 | 0.0017651 | 0.0017747 | 0.0017842 | 0.0017938 | 0.0018033 | 0.0017922 | 0.001781 | 0.0017699 | 0.0017587 | 0.0017476 | 0.0017364 | 0.0017252 | 0.0017141 | 0.0017029 | 0.0016918 | 0.0016806 | 0.0016695 | 0.0016583 | 0.0016471 | 0.001636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-167870005 | 21 | 21 | 0.0016508 | 0 | 0.002252 | 0 | 0.0019321 | 0 | 1.7179e-05 | -1.5995e-05 | 0.0021833 | 0.0022005 | 0.0022177 | 0.0022349 | 0.002252 | 0.002236 | 0.0022201 | 0.0022041 | 0.0021881 | 0.0021721 | 0.0021561 | 0.0021401 | 0.0021241 | 0.0021081 | 0.0020921 | 0.0020761 | 0.0020601 | 0.0020441 | 0.0020281 | 0.0020121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-172348553 | 7 | 7 | 1.78e-05 | 0 | 2.12e-05 | 0 | 1.88e-05 | 0 | 9.7143e-08 | -1.2e-07 | 2.0811e-05 | 2.0909e-05 | 2.1006e-05 | 2.1103e-05 | 2.12e-05 | 2.108e-05 | 2.096e-05 | 2.084e-05 | 2.072e-05 | 2.06e-05 | 2.048e-05 | 2.036e-05 | 2.024e-05 | 2.012e-05 | 2e-05 | 1.988e-05 | 1.976e-05 | 1.964e-05 | 1.952e-05 | 1.94e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN034-182145724 | 1456 | 367 | 0.018212 | 0.0071918 | 0.02302 | 0.0096546 | 0.018664 | 0.0074052 | 0.00013738 | -0.00021784 | 0.022471 | 0.022608 | 0.022746 | 0.022883 | 0.02302 | 0.022802 | 0.022585 | 0.022367 | 0.022149 | 0.021931 | 0.021713 | 0.021495 | 0.021278 | 0.02106 | 0.020842 | 0.020624 | 0.020406 | 0.020188 | 0.019971 | 0.019753 | 7.0365e-05 | -0.00011247 | 0.0093731 | 0.0094435 | 0.0095139 | 0.0095842 | 0.0096546 | 0.0095421 | 0.0094297 | 0.0093172 | 0.0092047 | 0.0090922 | 0.0089798 | 0.0088673 | 0.0087548 | 0.0086424 | 0.0085299 | 0.0084174 | 0.0083049 | 0.0081925 | 0.00808 | 0.0079675
| HTN034-182145744 | 377 | 233 | 0.0067474 | 0.0022066 | 0.0086719 | 0.0029352 | 0.0072884 | 0.0024128 | 5.4985e-05 | -6.9174e-05 | 0.008452 | 0.008507 | 0.008562 | 0.0086169 | 0.0086719 | 0.0086028 | 0.0085336 | 0.0084644 | 0.0083952 | 0.0083261 | 0.0082569 | 0.0081877 | 0.0081185 | 0.0080494 | 0.0079802 | 0.007911 | 0.0078418 | 0.0077727 | 0.0077035 | 0.0076343 | 2.0815e-05 | -2.6118e-05 | 0.0028519 | 0.0028727 | 0.0028935 | 0.0029143 | 0.0029352 | 0.002909 | 0.0028829 | 0.0028568 | 0.0028307 | 0.0028046 | 0.0027785 | 0.0027523 | 0.0027262 | 0.0027001 | 0.002674 | 0.0026479 | 0.0026217 | 0.0025956 | 0.0025695 | 0.0025434
| HTN034-182145765 | 185 | 86 | 0.0082337 | 0.0035637 | 0.010292 | 0.004493 | 0.0093559 | 0.0040802 | 5.8817e-05 | -4.6823e-05 | 0.010057 | 0.010116 | 0.010175 | 0.010234 | 0.010292 | 0.010246 | 0.010199 | 0.010152 | 0.010105 | 0.010058 | 0.010011 | 0.0099646 | 0.0099178 | 0.0098709 | 0.0098241 | 0.0097773 | 0.0097305 | 0.0096837 | 0.0096368 | 0.00959 | 2.6552e-05 | -2.0641e-05 | 0.0043868 | 0.0044134 | 0.0044399 | 0.0044665 | 0.004493 | 0.0044724 | 0.0044518 | 0.0044311 | 0.0044105 | 0.0043898 | 0.0043692 | 0.0043485 | 0.0043279 | 0.0043073 | 0.0042866 | 0.004266 | 0.0042453 | 0.0042247 | 0.0042041 | 0.0041834
| HTN034-190418432 | 1853 | 20 | 0.0010209 | 0.0016979 | 0.0014519 | 0.0024035 | 0.0011736 | 0.0019456 | 1.2314e-05 | -1.3916e-05 | 0.0014026 | 0.0014149 | 0.0014273 | 0.0014396 | 0.0014519 | 0.001438 | 0.001424 | 0.0014101 | 0.0013962 | 0.0013823 | 0.0013684 | 0.0013545 | 0.0013406 | 0.0013266 | 0.0013127 | 0.0012988 | 0.0012849 | 0.001271 | 0.0012571 | 0.0012431 | 2.0159e-05 | -2.2896e-05 | 0.0023229 | 0.002343 | 0.0023632 | 0.0023833 | 0.0024035 | 0.0023806 | 0.0023577 | 0.0023348 | 0.0023119 | 0.002289 | 0.0022661 | 0.0022432 | 0.0022203 | 0.0021974 | 0.0021745 | 0.0021516 | 0.0021288 | 0.0021059 | 0.002083 | 0.0020601
| HTN034-84443403 | 693 | 80 | 0.00302 | 0.000937 | 0.0036163 | 0.0011362 | 0.0032013 | 0.00099374 | 1.7036e-05 | -2.0747e-05 | 0.0035481 | 0.0035652 | 0.0035822 | 0.0035992 | 0.0036163 | 0.0035955 | 0.0035748 | 0.003554 | 0.0035333 | 0.0035125 | 0.0034918 | 0.0034711 | 0.0034503 | 0.0034296 | 0.0034088 | 0.0033881 | 0.0033673 | 0.0033466 | 0.0033258 | 0.0033051 | 5.6922e-06 | -7.1242e-06 | 0.0011135 | 0.0011191 | 0.0011248 | 0.0011305 | 0.0011362 | 0.0011291 | 0.001122 | 0.0011149 | 0.0011077 | 0.0011006 | 0.0010935 | 0.0010864 | 0.0010792 | 0.0010721 | 0.001065 | 0.0010579 | 0.0010507 | 0.0010436 | 0.0010365 | 0.0010294
| HYT011-157370486 | 26 | 26 | 0.00035553 | 0 | 0.00045367 | 0 | 0.00025566 | 0 | 2.8039e-06 | -9.9003e-06 | 0.00044245 | 0.00044525 | 0.00044806 | 0.00045086 | 0.00045367 | 0.00044376 | 0.00043386 | 0.00042396 | 0.00041406 | 0.00040416 | 0.00039426 | 0.00038436 | 0.00037446 | 0.00036456 | 0.00035466 | 0.00034476 | 0.00033486 | 0.00032496 | 0.00031506 | 0.00030516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HYT011-157370579 | 12 | 12 | 0.0011377 | 0 | 0.0014503 | 0 | 0.00088362 | 0 | 8.9303e-06 | -2.8334e-05 | 0.0014146 | 0.0014235 | 0.0014324 | 0.0014414 | 0.0014503 | 0.001422 | 0.0013936 | 0.0013653 | 0.001337 | 0.0013086 | 0.0012803 | 0.001252 | 0.0012236 | 0.0011953 | 0.001167 | 0.0011386 | 0.0011103 | 0.001082 | 0.0010536 | 0.0010253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HYT011-162212996 | 7 | 7 | 0.00033652 | 0 | 0.00044217 | 0 | 0.00025876 | 0 | 3.0185e-06 | -9.1703e-06 | 0.00043009 | 0.00043311 | 0.00043613 | 0.00043915 | 0.00044217 | 0.000433 | 0.00042383 | 0.00041466 | 0.00040549 | 0.00039632 | 0.00038715 | 0.00037798 | 0.00036881 | 0.00035964 | 0.00035047 | 0.0003413 | 0.00033213 | 0.00032296 | 0.00031379 | 0.00030462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HYT011-162213233 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HYT011-41829518 | 165 | 93 | 0.010902 | 0.0017228 | 0.013589 | 0.0022222 | 0.010867 | 0.0016299 | 7.6774e-05 | -0.00013613 | 0.013282 | 0.013359 | 0.013436 | 0.013513 | 0.013589 | 0.013453 | 0.013317 | 0.013181 | 0.013045 | 0.012909 | 0.012773 | 0.012637 | 0.0125 | 0.012364 | 0.012228 | 0.012092 | 0.011956 | 0.01182 | 0.011684 | 0.011548 | 1.4271e-05 | -2.9617e-05 | 0.0021652 | 0.0021794 | 0.0021937 | 0.002208 | 0.0022222 | 0.0021926 | 0.002163 | 0.0021334 | 0.0021038 | 0.0020742 | 0.0020445 | 0.0020149 | 0.0019853 | 0.0019557 | 0.0019261 | 0.0018964 | 0.0018668 | 0.0018372 | 0.0018076 | 0.001778
| HYT011-82429866 | 14 | 14 | 0.0010639 | 0 | 0.001375 | 0 | 0.0010112 | 0 | 8.8872e-06 | -1.8186e-05 | 0.0013394 | 0.0013483 | 0.0013572 | 0.0013661 | 0.001375 | 0.0013568 | 0.0013386 | 0.0013204 | 0.0013022 | 0.001284 | 0.0012658 | 0.0012477 | 0.0012295 | 0.0012113 | 0.0011931 | 0.0011749 | 0.0011567 | 0.0011385 | 0.0011204 | 0.0011022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT002-15430186 | 2269 | 2229 | 0.0084817 | 0.0027107 | 0.01097 | 0.0034519 | 0.012316 | 0.003778 | 7.1084e-05 | 6.7325e-05 | 0.010685 | 0.010756 | 0.010827 | 0.010899 | 0.01097 | 0.011037 | 0.011104 | 0.011172 | 0.011239 | 0.011306 | 0.011374 | 0.011441 | 0.011508 | 0.011576 | 0.011643 | 0.01171 | 0.011778 | 0.011845 | 0.011912 | 0.011979 | 2.1175e-05 | 1.6307e-05 | 0.0033672 | 0.0033883 | 0.0034095 | 0.0034307 | 0.0034519 | 0.0034682 | 0.0034845 | 0.0035008 | 0.0035171 | 0.0035334 | 0.0035497 | 0.003566 | 0.0035823 | 0.0035986 | 0.0036149 | 0.0036312 | 0.0036475 | 0.0036638 | 0.0036802 | 0.0036965
| KGT002-24605712 | 40 | 40 | 0.0060858 | 0 | 0.0075239 | 0 | 0.0081736 | 0 | 4.1088e-05 | 3.2486e-05 | 0.0073595 | 0.0074006 | 0.0074417 | 0.0074828 | 0.0075239 | 0.0075564 | 0.0075889 | 0.0076214 | 0.0076538 | 0.0076863 | 0.0077188 | 0.0077513 | 0.0077838 | 0.0078163 | 0.0078488 | 0.0078812 | 0.0079137 | 0.0079462 | 0.0079787 | 0.0080112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-119555477 | 665 | 659 | 0.0129 | 0.0020302 | 0.013416 | 0.002065 | 0.01318 | 0.0020496 | 1.4756e-05 | -1.1803e-05 | 0.013357 | 0.013372 | 0.013387 | 0.013401 | 0.013416 | 0.013404 | 0.013393 | 0.013381 | 0.013369 | 0.013357 | 0.013345 | 0.013333 | 0.013322 | 0.01331 | 0.013298 | 0.013286 | 0.013274 | 0.013263 | 0.013251 | 0.013239 | 9.9406e-07 | -7.718e-07 | 0.002061 | 0.002062 | 0.002063 | 0.002064 | 0.002065 | 0.0020642 | 0.0020635 | 0.0020627 | 0.0020619 | 0.0020612 | 0.0020604 | 0.0020596 | 0.0020588 | 0.0020581 | 0.0020573 | 0.0020565 | 0.0020557 | 0.002055 | 0.0020542 | 0.0020534
| KGT003-15424502 | 1306 | 160 | 0.0020942 | 0.003821 | 0.0027155 | 0.0050125 | 0.0030747 | 0.0057788 | 1.7751e-05 | 1.7959e-05 | 0.0026445 | 0.0026623 | 0.00268 | 0.0026978 | 0.0027155 | 0.0027335 | 0.0027514 | 0.0027694 | 0.0027874 | 0.0028053 | 0.0028233 | 0.0028412 | 0.0028592 | 0.0028772 | 0.0028951 | 0.0029131 | 0.002931 | 0.002949 | 0.0029669 | 0.0029849 | 3.4043e-05 | 3.8313e-05 | 0.0048763 | 0.0049104 | 0.0049444 | 0.0049785 | 0.0050125 | 0.0050508 | 0.0050891 | 0.0051274 | 0.0051658 | 0.0052041 | 0.0052424 | 0.0052807 | 0.005319 | 0.0053573 | 0.0053956 | 0.0054339 | 0.0054723 | 0.0055106 | 0.0055489 | 0.0055872
| KGT003-155046250 | 11 | 11 | 0.0038696 | 0 | 0.0053194 | 0 | 0.0059243 | 0 | 4.1421e-05 | 3.0245e-05 | 0.0051537 | 0.0051951 | 0.0052365 | 0.0052779 | 0.0053194 | 0.0053496 | 0.0053798 | 0.0054101 | 0.0054403 | 0.0054706 | 0.0055008 | 0.0055311 | 0.0055613 | 0.0055916 | 0.0056218 | 0.0056521 | 0.0056823 | 0.0057125 | 0.0057428 | 0.005773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155046371 | 4 | 4 | 4.09e-05 | 0 | 5.81e-05 | 0 | 6.77e-05 | 0 | 4.9143e-07 | 4.8e-07 | 5.6134e-05 | 5.6626e-05 | 5.7117e-05 | 5.7609e-05 | 5.81e-05 | 5.858e-05 | 5.906e-05 | 5.954e-05 | 6.002e-05 | 6.05e-05 | 6.098e-05 | 6.146e-05 | 6.194e-05 | 6.242e-05 | 6.29e-05 | 6.338e-05 | 6.386e-05 | 6.434e-05 | 6.482e-05 | 6.53e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155131479 | 18 | 18 | 0.00057323 | 0 | 0.00077183 | 0 | 0.00091749 | 0 | 5.6743e-06 | 7.2828e-06 | 0.00074913 | 0.00075481 | 0.00076048 | 0.00076616 | 0.00077183 | 0.00077911 | 0.0007864 | 0.00079368 | 0.00080096 | 0.00080825 | 0.00081553 | 0.00082281 | 0.00083009 | 0.00083738 | 0.00084466 | 0.00085194 | 0.00085922 | 0.00086651 | 0.00087379 | 0.00088107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155165277 | 6 | 6 | 0.0016584 | 0 | 0.0021391 | 0 | 0.0025432 | 0 | 1.3733e-05 | 2.0204e-05 | 0.0020841 | 0.0020979 | 0.0021116 | 0.0021253 | 0.0021391 | 0.0021593 | 0.0021795 | 0.0021997 | 0.0022199 | 0.0022401 | 0.0022603 | 0.0022805 | 0.0023007 | 0.0023209 | 0.0023411 | 0.0023613 | 0.0023815 | 0.0024017 | 0.0024219 | 0.0024421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155165426 | 16 | 16 | 0.0044523 | 0 | 0.0057675 | 0 | 0.0066225 | 0 | 3.7576e-05 | 4.2753e-05 | 0.0056172 | 0.0056547 | 0.0056923 | 0.0057299 | 0.0057675 | 0.0058102 | 0.005853 | 0.0058957 | 0.0059385 | 0.0059812 | 0.006024 | 0.0060667 | 0.0061095 | 0.0061522 | 0.006195 | 0.0062377 | 0.0062805 | 0.0063232 | 0.006366 | 0.0064088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155165521 | 18 | 18 | 0.0049761 | 0 | 0.0065026 | 0 | 0.0072203 | 0 | 4.3613e-05 | 3.5884e-05 | 0.0063281 | 0.0063718 | 0.0064154 | 0.006459 | 0.0065026 | 0.0065385 | 0.0065744 | 0.0066102 | 0.0066461 | 0.006682 | 0.0067179 | 0.0067538 | 0.0067897 | 0.0068255 | 0.0068614 | 0.0068973 | 0.0069332 | 0.0069691 | 0.007005 | 0.0070409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155165638 | 16 | 16 | 0.0054504 | 0 | 0.0067715 | 0 | 0.0080074 | 0 | 3.7747e-05 | 6.1793e-05 | 0.0066206 | 0.0066583 | 0.006696 | 0.0067338 | 0.0067715 | 0.0068333 | 0.0068951 | 0.0069569 | 0.0070187 | 0.0070805 | 0.0071423 | 0.0072041 | 0.0072659 | 0.0073277 | 0.0073895 | 0.0074513 | 0.0075131 | 0.0075749 | 0.0076366 | 0.0076984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155165904 | 13 | 13 | 0.0055132 | 0 | 0.0073303 | 0 | 0.0081977 | 0 | 5.1918e-05 | 4.3373e-05 | 0.0071226 | 0.0071745 | 0.0072265 | 0.0072784 | 0.0073303 | 0.0073737 | 0.007417 | 0.0074604 | 0.0075038 | 0.0075471 | 0.0075905 | 0.0076339 | 0.0076773 | 0.0077206 | 0.007764 | 0.0078074 | 0.0078508 | 0.0078941 | 0.0079375 | 0.0079809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155166011 | 8 | 8 | 0.0010794 | 0 | 0.0014351 | 0 | 0.0016727 | 0 | 1.0161e-05 | 1.188e-05 | 0.0013944 | 0.0014046 | 0.0014147 | 0.0014249 | 0.0014351 | 0.0014469 | 0.0014588 | 0.0014707 | 0.0014826 | 0.0014945 | 0.0015063 | 0.0015182 | 0.0015301 | 0.001542 | 0.0015539 | 0.0015657 | 0.0015776 | 0.0015895 | 0.0016014 | 0.0016133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155166153 | 7 | 7 | 0.0051274 | 0 | 0.0067832 | 0 | 0.0075252 | 0 | 4.7307e-05 | 3.7103e-05 | 0.0065939 | 0.0066412 | 0.0066885 | 0.0067359 | 0.0067832 | 0.0068203 | 0.0068574 | 0.0068945 | 0.0069316 | 0.0069687 | 0.0070058 | 0.0070429 | 0.00708 | 0.0071171 | 0.0071542 | 0.0071913 | 0.0072284 | 0.0072655 | 0.0073026 | 0.0073397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155166380 | 9 | 9 | 0.0040136 | 0 | 0.0050869 | 0 | 0.0060892 | 0 | 3.0666e-05 | 5.0113e-05 | 0.0049643 | 0.0049949 | 0.0050256 | 0.0050563 | 0.0050869 | 0.0051371 | 0.0051872 | 0.0052373 | 0.0052874 | 0.0053375 | 0.0053876 | 0.0054377 | 0.0054878 | 0.005538 | 0.0055881 | 0.0056382 | 0.0056883 | 0.0057384 | 0.0057885 | 0.0058386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155177979 | 13 | 13 | 0.012552 | 0 | 0.017323 | 0 | 0.018394 | 0 | 0.00013632 | 5.3548e-05 | 0.016778 | 0.016914 | 0.01705 | 0.017187 | 0.017323 | 0.017376 | 0.01743 | 0.017483 | 0.017537 | 0.017591 | 0.017644 | 0.017698 | 0.017751 | 0.017805 | 0.017858 | 0.017912 | 0.017965 | 0.018019 | 0.018073 | 0.018126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155178122 | 6 | 6 | 5.91e-05 | 0 | 7.61e-05 | 0 | 9.15e-05 | 0 | 4.8571e-07 | 7.7e-07 | 7.4157e-05 | 7.4643e-05 | 7.5129e-05 | 7.5614e-05 | 7.61e-05 | 7.687e-05 | 7.764e-05 | 7.841e-05 | 7.918e-05 | 7.995e-05 | 8.072e-05 | 8.149e-05 | 8.226e-05 | 8.303e-05 | 8.38e-05 | 8.457e-05 | 8.534e-05 | 8.611e-05 | 8.688e-05 | 8.765e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-155178538 | 7 | 7 | 3.75e-05 | 0 | 4.82e-05 | 0 | 5.8e-05 | 0 | 3.0571e-07 | 4.9e-07 | 4.6977e-05 | 4.7283e-05 | 4.7589e-05 | 4.7894e-05 | 4.82e-05 | 4.869e-05 | 4.918e-05 | 4.967e-05 | 5.016e-05 | 5.065e-05 | 5.114e-05 | 5.163e-05 | 5.212e-05 | 5.261e-05 | 5.31e-05 | 5.359e-05 | 5.408e-05 | 5.457e-05 | 5.506e-05 | 5.555e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT003-84636133 | 434 | 322 | 0.046446 | 0.016247 | 0.05879 | 0.021953 | 0.061286 | 0.024341 | 0.00035267 | 0.00012481 | 0.057379 | 0.057732 | 0.058084 | 0.058437 | 0.05879 | 0.058915 | 0.059039 | 0.059164 | 0.059289 | 0.059414 | 0.059539 | 0.059663 | 0.059788 | 0.059913 | 0.060038 | 0.060163 | 0.060288 | 0.060412 | 0.060537 | 0.060662 | 0.00016303 | 0.0001194 | 0.021301 | 0.021464 | 0.021627 | 0.02179 | 0.021953 | 0.022073 | 0.022192 | 0.022311 | 0.022431 | 0.02255 | 0.02267 | 0.022789 | 0.022908 | 0.023028 | 0.023147 | 0.023267 | 0.023386 | 0.023505 | 0.023625 | 0.023744
| KGT004-15430149 | 1477 | 53 | 0.0011838 | 0.0025703 | 0.0015551 | 0.0034298 | 0.0018075 | 0.004078 | 1.0609e-05 | 1.2619e-05 | 0.0015126 | 0.0015232 | 0.0015339 | 0.0015445 | 0.0015551 | 0.0015677 | 0.0015803 | 0.0015929 | 0.0016056 | 0.0016182 | 0.0016308 | 0.0016434 | 0.001656 | 0.0016686 | 0.0016813 | 0.0016939 | 0.0017065 | 0.0017191 | 0.0017317 | 0.0017444 | 2.4555e-05 | 3.2414e-05 | 0.0033315 | 0.0033561 | 0.0033806 | 0.0034052 | 0.0034298 | 0.0034622 | 0.0034946 | 0.003527 | 0.0035594 | 0.0035918 | 0.0036242 | 0.0036567 | 0.0036891 | 0.0037215 | 0.0037539 | 0.0037863 | 0.0038187 | 0.0038511 | 0.0038836 | 0.003916
| KGT004-154877585 | 21 | 21 | 1.82e-05 | 0 | 2.52e-05 | 0 | 3.07e-05 | 0 | 2e-07 | 2.75e-07 | 2.44e-05 | 2.46e-05 | 2.48e-05 | 2.5e-05 | 2.52e-05 | 2.5475e-05 | 2.575e-05 | 2.6025e-05 | 2.63e-05 | 2.6575e-05 | 2.685e-05 | 2.7125e-05 | 2.74e-05 | 2.7675e-05 | 2.795e-05 | 2.8225e-05 | 2.85e-05 | 2.8775e-05 | 2.905e-05 | 2.9325e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT004-154878038 | 14 | 14 | 0.0023842 | 0 | 0.003173 | 0 | 0.0038068 | 0 | 2.2537e-05 | 3.1693e-05 | 0.0030828 | 0.0031054 | 0.0031279 | 0.0031504 | 0.003173 | 0.0032047 | 0.0032363 | 0.003268 | 0.0032997 | 0.0033314 | 0.0033631 | 0.0033948 | 0.0034265 | 0.0034582 | 0.0034899 | 0.0035216 | 0.0035533 | 0.003585 | 0.0036167 | 0.0036484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT004-154878151 | 26 | 26 | 0.0039956 | 0 | 0.0049364 | 0 | 0.0054419 | 0 | 2.6881e-05 | 2.5275e-05 | 0.0048289 | 0.0048558 | 0.0048827 | 0.0049096 | 0.0049364 | 0.0049617 | 0.004987 | 0.0050123 | 0.0050375 | 0.0050628 | 0.0050881 | 0.0051134 | 0.0051386 | 0.0051639 | 0.0051892 | 0.0052145 | 0.0052397 | 0.005265 | 0.0052903 | 0.0053156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT004-154878281 | 21 | 21 | 0.0024951 | 0 | 0.0033487 | 0 | 0.003974 | 0 | 2.4389e-05 | 3.1262e-05 | 0.0032512 | 0.0032755 | 0.0032999 | 0.0033243 | 0.0033487 | 0.00338 | 0.0034112 | 0.0034425 | 0.0034738 | 0.003505 | 0.0035363 | 0.0035676 | 0.0035988 | 0.0036301 | 0.0036613 | 0.0036926 | 0.0037239 | 0.0037551 | 0.0037864 | 0.0038176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT004-154878429 | 44 | 44 | 0.0063501 | 0 | 0.0082287 | 0 | 0.009908 | 0 | 5.3674e-05 | 8.3967e-05 | 0.008014 | 0.0080676 | 0.0081213 | 0.008175 | 0.0082287 | 0.0083126 | 0.0083966 | 0.0084806 | 0.0085645 | 0.0086485 | 0.0087325 | 0.0088164 | 0.0089004 | 0.0089844 | 0.0090683 | 0.0091523 | 0.0092363 | 0.0093202 | 0.0094042 | 0.0094882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT004-154971301 | 10 | 10 | 0.00010846 | 0 | 0.00014568 | 0 | 0.00017585 | 0 | 1.0635e-06 | 1.5082e-06 | 0.00014143 | 0.00014249 | 0.00014356 | 0.00014462 | 0.00014568 | 0.00014719 | 0.0001487 | 0.00015021 | 0.00015171 | 0.00015322 | 0.00015473 | 0.00015624 | 0.00015775 | 0.00015926 | 0.00016076 | 0.00016227 | 0.00016378 | 0.00016529 | 0.0001668 | 0.00016831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT004-154971445 | 1 | 1 | 4.03e-05 | 0 | 5.5e-05 | 0 | 6.77e-05 | 0 | 4.2e-07 | 6.35e-07 | 5.332e-05 | 5.374e-05 | 5.416e-05 | 5.458e-05 | 5.5e-05 | 5.5635e-05 | 5.627e-05 | 5.6905e-05 | 5.754e-05 | 5.8175e-05 | 5.881e-05 | 5.9445e-05 | 6.008e-05 | 6.0715e-05 | 6.135e-05 | 6.1985e-05 | 6.262e-05 | 6.3255e-05 | 6.389e-05 | 6.4525e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT004-154971580 | 13 | 13 | 0.0005255 | 0 | 0.00071099 | 0 | 0.00081451 | 0 | 5.2997e-06 | 5.1764e-06 | 0.00068979 | 0.00069509 | 0.00070039 | 0.00070569 | 0.00071099 | 0.00071616 | 0.00072134 | 0.00072652 | 0.00073169 | 0.00073687 | 0.00074205 | 0.00074722 | 0.0007524 | 0.00075757 | 0.00076275 | 0.00076793 | 0.0007731 | 0.00077828 | 0.00078346 | 0.00078863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT004-154971674 | 22 | 22 | 7.58e-05 | 0 | 0.00010166 | 0 | 0.00012707 | 0 | 7.3874e-07 | 1.2707e-06 | 9.8701e-05 | 9.944e-05 | 0.00010018 | 0.00010092 | 0.00010166 | 0.00010293 | 0.0001042 | 0.00010547 | 0.00010674 | 0.00010801 | 0.00010928 | 0.00011055 | 0.00011182 | 0.00011309 | 0.00011436 | 0.00011563 | 0.0001169 | 0.00011818 | 0.00011945 | 0.00012072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT004-160450903 | 20 | 20 | 0.0017466 | 0 | 0.0024596 | 0 | 0.0027686 | 0 | 2.0371e-05 | 1.545e-05 | 0.0023781 | 0.0023985 | 0.0024189 | 0.0024392 | 0.0024596 | 0.0024751 | 0.0024905 | 0.002506 | 0.0025214 | 0.0025369 | 0.0025523 | 0.0025678 | 0.0025832 | 0.0025987 | 0.0026141 | 0.0026296 | 0.002645 | 0.0026605 | 0.0026759 | 0.0026914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT004-24604166 | 39 | 39 | 0.0079031 | 0 | 0.010943 | 0 | 0.011802 | 0 | 8.6847e-05 | 4.2969e-05 | 0.010595 | 0.010682 | 0.010769 | 0.010856 | 0.010943 | 0.010986 | 0.011029 | 0.011072 | 0.011115 | 0.011158 | 0.011201 | 0.011243 | 0.011286 | 0.011329 | 0.011372 | 0.011415 | 0.011458 | 0.011501 | 0.011544 | 0.011587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT004-24604180 | 152 | 152 | 0.0051615 | 0 | 0.0068056 | 0 | 0.0079387 | 0 | 4.6973e-05 | 5.6656e-05 | 0.0066177 | 0.0066647 | 0.0067117 | 0.0067586 | 0.0068056 | 0.0068623 | 0.0069189 | 0.0069756 | 0.0070322 | 0.0070889 | 0.0071456 | 0.0072022 | 0.0072589 | 0.0073155 | 0.0073722 | 0.0074288 | 0.0074855 | 0.0075422 | 0.0075988 | 0.0076555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT004-24605698 | 1157 | 245 | 0.011858 | 0.0013595 | 0.015115 | 0.0017809 | 0.017459 | 0.002169 | 9.3052e-05 | 0.00011719 | 0.014743 | 0.014836 | 0.014929 | 0.015022 | 0.015115 | 0.015233 | 0.01535 | 0.015467 | 0.015584 | 0.015701 | 0.015818 | 0.015936 | 0.016053 | 0.01617 | 0.016287 | 0.016404 | 0.016522 | 0.016639 | 0.016756 | 0.016873 | 1.2038e-05 | 1.9408e-05 | 0.0017327 | 0.0017448 | 0.0017568 | 0.0017689 | 0.0017809 | 0.0018003 | 0.0018197 | 0.0018391 | 0.0018585 | 0.0018779 | 0.0018973 | 0.0019167 | 0.0019362 | 0.0019556 | 0.001975 | 0.0019944 | 0.0020138 | 0.0020332 | 0.0020526 | 0.002072
| KGT004-24605978 | 202 | 95 | 0.0075295 | 0.0043251 | 0.0078876 | 0.0044419 | 0.0077276 | 0.0043901 | 1.0232e-05 | -7.9977e-06 | 0.0078467 | 0.0078569 | 0.0078671 | 0.0078774 | 0.0078876 | 0.0078796 | 0.0078716 | 0.0078636 | 0.0078556 | 0.0078476 | 0.0078396 | 0.0078316 | 0.0078236 | 0.0078156 | 0.0078076 | 0.0077996 | 0.0077916 | 0.0077836 | 0.0077756 | 0.0077676 | 3.3387e-06 | -2.5922e-06 | 0.0044286 | 0.0044319 | 0.0044352 | 0.0044386 | 0.0044419 | 0.0044393 | 0.0044367 | 0.0044341 | 0.0044315 | 0.004429 | 0.0044264 | 0.0044238 | 0.0044212 | 0.0044186 | 0.004416 | 0.0044134 | 0.0044108 | 0.0044082 | 0.0044056 | 0.004403
| KGT004-55202181 | 760 | 701 | 0.010674 | 0.001675 | 0.014672 | 0.0023689 | 0.016112 | 0.0026664 | 0.00011423 | 7.199e-05 | 0.014215 | 0.01433 | 0.014444 | 0.014558 | 0.014672 | 0.014744 | 0.014816 | 0.014888 | 0.01496 | 0.015032 | 0.015104 | 0.015176 | 0.015248 | 0.01532 | 0.015392 | 0.015464 | 0.015536 | 0.015608 | 0.01568 | 0.015752 | 1.9826e-05 | 1.4874e-05 | 0.0022896 | 0.0023094 | 0.0023293 | 0.0023491 | 0.0023689 | 0.0023838 | 0.0023987 | 0.0024135 | 0.0024284 | 0.0024433 | 0.0024582 | 0.002473 | 0.0024879 | 0.0025028 | 0.0025177 | 0.0025325 | 0.0025474 | 0.0025623 | 0.0025772 | 0.002592
| KRT012-118960990 | 27 | 27 | 0.00084469 | 0 | 0.0012056 | 0 | 0.00073851 | 0 | 1.0312e-05 | -2.3355e-05 | 0.0011644 | 0.0011747 | 0.001185 | 0.0011953 | 0.0012056 | 0.0011823 | 0.0011589 | 0.0011355 | 0.0011122 | 0.0010888 | 0.0010655 | 0.0010421 | 0.0010188 | 0.00099542 | 0.00097206 | 0.00094871 | 0.00092535 | 0.000902 | 0.00087864 | 0.00085529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT012-141850121 | 24 | 24 | 0.0013221 | 0 | 0.0019686 | 0 | 0.00135 | 0 | 1.847e-05 | -3.0929e-05 | 0.0018947 | 0.0019132 | 0.0019317 | 0.0019501 | 0.0019686 | 0.0019377 | 0.0019067 | 0.0018758 | 0.0018449 | 0.001814 | 0.001783 | 0.0017521 | 0.0017212 | 0.0016902 | 0.0016593 | 0.0016284 | 0.0015975 | 0.0015665 | 0.0015356 | 0.0015047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT012-141850552 | 31 | 31 | 0.0017454 | 0 | 0.0026197 | 0 | 0.0017819 | 0 | 2.4981e-05 | -4.1891e-05 | 0.0025198 | 0.0025448 | 0.0025697 | 0.0025947 | 0.0026197 | 0.0025778 | 0.0025359 | 0.002494 | 0.0024521 | 0.0024102 | 0.0023684 | 0.0023265 | 0.0022846 | 0.0022427 | 0.0022008 | 0.0021589 | 0.002117 | 0.0020751 | 0.0020332 | 0.0019913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT012-141850665 | 32 | 32 | 0.0015112 | 0 | 0.0016439 | 0 | 0.0015492 | 0 | 3.7927e-06 | -4.7382e-06 | 0.0016288 | 0.0016326 | 0.0016364 | 0.0016402 | 0.0016439 | 0.0016392 | 0.0016345 | 0.0016297 | 0.001625 | 0.0016203 | 0.0016155 | 0.0016108 | 0.001606 | 0.0016013 | 0.0015966 | 0.0015918 | 0.0015871 | 0.0015824 | 0.0015776 | 0.0015729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT012-15397067 | 1183 | 555 | 0.0012228 | 0.0011545 | 0.0015883 | 0.0015171 | 0.0010873 | 0.0010287 | 1.0445e-05 | -2.5055e-05 | 0.0015466 | 0.001557 | 0.0015675 | 0.0015779 | 0.0015883 | 0.0015633 | 0.0015382 | 0.0015132 | 0.0014881 | 0.0014631 | 0.001438 | 0.001413 | 0.0013879 | 0.0013629 | 0.0013378 | 0.0013127 | 0.0012877 | 0.0012626 | 0.0012376 | 0.0012125 | 1.036e-05 | -2.442e-05 | 0.0014757 | 0.0014861 | 0.0014964 | 0.0015068 | 0.0015171 | 0.0014927 | 0.0014683 | 0.0014439 | 0.0014195 | 0.001395 | 0.0013706 | 0.0013462 | 0.0013218 | 0.0012974 | 0.0012729 | 0.0012485 | 0.0012241 | 0.0011997 | 0.0011753 | 0.0011508
| KRT012-160501273 | 25 | 25 | 0.00038866 | 0 | 0.00055684 | 0 | 0.00033075 | 0 | 4.8051e-06 | -1.1305e-05 | 0.00053762 | 0.00054243 | 0.00054723 | 0.00055204 | 0.00055684 | 0.00054554 | 0.00053423 | 0.00052293 | 0.00051163 | 0.00050032 | 0.00048902 | 0.00047771 | 0.00046641 | 0.0004551 | 0.0004438 | 0.00043249 | 0.00042119 | 0.00040988 | 0.00039858 | 0.00038728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT012-163206103 | 12 | 12 | 1.22e-05 | 0 | 1.91e-05 | 0 | 8.4e-06 | 0 | 1.9714e-07 | -5.35e-07 | 1.8311e-05 | 1.8509e-05 | 1.8706e-05 | 1.8903e-05 | 1.91e-05 | 1.8565e-05 | 1.803e-05 | 1.7495e-05 | 1.696e-05 | 1.6425e-05 | 1.589e-05 | 1.5355e-05 | 1.482e-05 | 1.4285e-05 | 1.375e-05 | 1.3215e-05 | 1.268e-05 | 1.2145e-05 | 1.161e-05 | 1.1075e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT012-163310215 | 10 | 10 | 0.00021842 | 0 | 0.00034851 | 0 | 0.00022553 | 0 | 3.7169e-06 | -6.1494e-06 | 0.00033365 | 0.00033736 | 0.00034108 | 0.0003448 | 0.00034851 | 0.00034237 | 0.00033622 | 0.00033007 | 0.00032392 | 0.00031777 | 0.00031162 | 0.00030547 | 0.00029932 | 0.00029317 | 0.00028702 | 0.00028087 | 0.00027472 | 0.00026857 | 0.00026242 | 0.00025627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT012-163310404 | 9 | 9 | 3.68e-05 | 0 | 5.66e-05 | 0 | 3.59e-05 | 0 | 5.6571e-07 | -1.035e-06 | 5.4337e-05 | 5.4903e-05 | 5.5469e-05 | 5.6034e-05 | 5.66e-05 | 5.5565e-05 | 5.453e-05 | 5.3495e-05 | 5.246e-05 | 5.1425e-05 | 5.039e-05 | 4.9355e-05 | 4.832e-05 | 4.7285e-05 | 4.625e-05 | 4.5215e-05 | 4.418e-05 | 4.3145e-05 | 4.211e-05 | 4.1075e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT012-163313957 | 7 | 7 | 1.47e-05 | 0 | 2.21e-05 | 0 | 1.2e-05 | 0 | 2.1143e-07 | -5.05e-07 | 2.1254e-05 | 2.1466e-05 | 2.1677e-05 | 2.1889e-05 | 2.21e-05 | 2.1595e-05 | 2.109e-05 | 2.0585e-05 | 2.008e-05 | 1.9575e-05 | 1.907e-05 | 1.8565e-05 | 1.806e-05 | 1.7555e-05 | 1.705e-05 | 1.6545e-05 | 1.604e-05 | 1.5535e-05 | 1.503e-05 | 1.4525e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT012-24598034 | 569 | 451 | 0.00067613 | 0.00093745 | 0.00098106 | 0.0013858 | 0.00061294 | 0.00082012 | 8.7124e-06 | -1.8406e-05 | 0.00094621 | 0.00095492 | 0.00096364 | 0.00097235 | 0.00098106 | 0.00096265 | 0.00094425 | 0.00092584 | 0.00090744 | 0.00088903 | 0.00087062 | 0.00085222 | 0.00083381 | 0.00081541 | 0.000797 | 0.00077859 | 0.00076019 | 0.00074178 | 0.00072337 | 0.00070497 | 1.281e-05 | -2.8284e-05 | 0.0013345 | 0.0013474 | 0.0013602 | 0.001373 | 0.0013858 | 0.0013575 | 0.0013292 | 0.0013009 | 0.0012727 | 0.0012444 | 0.0012161 | 0.0011878 | 0.0011595 | 0.0011312 | 0.001103 | 0.0010747 | 0.0010464 | 0.0010181 | 0.00098982 | 0.00096153
| KRT013-146237675 | 9 | 9 | 0.001118 | 0 | 0.0017404 | 0 | 0.0011656 | 0 | 1.7784e-05 | -2.8741e-05 | 0.0016693 | 0.0016871 | 0.0017048 | 0.0017226 | 0.0017404 | 0.0017117 | 0.0016829 | 0.0016542 | 0.0016255 | 0.0015967 | 0.001568 | 0.0015392 | 0.0015105 | 0.0014817 | 0.001453 | 0.0014243 | 0.0013955 | 0.0013668 | 0.001338 | 0.0013093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-15397117 | 2510 | 1226 | 0.0017609 | 0.0002396 | 0.0024259 | 0.00034217 | 0.0017138 | 0.0002417 | 1.9002e-05 | -3.5609e-05 | 0.0023499 | 0.0023689 | 0.0023879 | 0.0024069 | 0.0024259 | 0.0023903 | 0.0023547 | 0.0023191 | 0.0022835 | 0.0022479 | 0.0022123 | 0.0021767 | 0.0021411 | 0.0021055 | 0.0020699 | 0.0020342 | 0.0019986 | 0.001963 | 0.0019274 | 0.0018918 | 2.9304e-06 | -5.0233e-06 | 0.00033044 | 0.00033337 | 0.00033631 | 0.00033924 | 0.00034217 | 0.00033714 | 0.00033212 | 0.0003271 | 0.00032207 | 0.00031705 | 0.00031203 | 0.000307 | 0.00030198 | 0.00029696 | 0.00029193 | 0.00028691 | 0.00028189 | 0.00027686 | 0.00027184 | 0.00026682
| KRT013-15397128 | 2512 | 2 | 0 | 6.17e-07 | 0 | 8.37e-07 | 0 | 5.1e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2857e-09 | -1.635e-08 | 8.1186e-07 | 8.1814e-07 | 8.2443e-07 | 8.3071e-07 | 8.37e-07 | 8.2065e-07 | 8.043e-07 | 7.8795e-07 | 7.716e-07 | 7.5525e-07 | 7.389e-07 | 7.2255e-07 | 7.062e-07 | 6.8985e-07 | 6.735e-07 | 6.5715e-07 | 6.408e-07 | 6.2445e-07 | 6.081e-07 | 5.9175e-07
| KRT013-157932507 | 23 | 23 | 0.00037312 | 0 | 0.00051567 | 0 | 0.00035844 | 0 | 4.0729e-06 | -7.8615e-06 | 0.00049938 | 0.00050345 | 0.00050752 | 0.0005116 | 0.00051567 | 0.00050781 | 0.00049995 | 0.00049208 | 0.00048422 | 0.00047636 | 0.0004685 | 0.00046064 | 0.00045278 | 0.00044492 | 0.00043705 | 0.00042919 | 0.00042133 | 0.00041347 | 0.00040561 | 0.00039775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-159317752 | 40 | 40 | 0.00017354 | 0 | 0.00023792 | 0 | 0.00016717 | 0 | 1.8393e-06 | -3.5376e-06 | 0.00023056 | 0.0002324 | 0.00023424 | 0.00023608 | 0.00023792 | 0.00023438 | 0.00023085 | 0.00022731 | 0.00022377 | 0.00022023 | 0.0002167 | 0.00021316 | 0.00020962 | 0.00020608 | 0.00020254 | 0.00019901 | 0.00019547 | 0.00019193 | 0.00018839 | 0.00018486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-159427901 | 28 | 28 | 0.00037169 | 0 | 0.00046426 | 0 | 0.00029733 | 0 | 2.6449e-06 | -8.3463e-06 | 0.00045368 | 0.00045633 | 0.00045897 | 0.00046162 | 0.00046426 | 0.00045591 | 0.00044757 | 0.00043922 | 0.00043087 | 0.00042253 | 0.00041418 | 0.00040584 | 0.00039749 | 0.00038914 | 0.0003808 | 0.00037245 | 0.0003641 | 0.00035576 | 0.00034741 | 0.00033906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-161097284 | 41 | 41 | 0.0014692 | 0 | 0.0019788 | 0 | 0.0015285 | 0 | 1.4561e-05 | -2.2516e-05 | 0.0019206 | 0.0019352 | 0.0019497 | 0.0019643 | 0.0019788 | 0.0019563 | 0.0019338 | 0.0019113 | 0.0018888 | 0.0018663 | 0.0018437 | 0.0018212 | 0.0017987 | 0.0017762 | 0.0017537 | 0.0017312 | 0.0017086 | 0.0016861 | 0.0016636 | 0.0016411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-161918444 | 11 | 11 | 0.00026076 | 0 | 0.00035943 | 0 | 0.00026857 | 0 | 2.8191e-06 | -4.5431e-06 | 0.00034815 | 0.00035097 | 0.00035379 | 0.00035661 | 0.00035943 | 0.00035488 | 0.00035034 | 0.0003458 | 0.00034125 | 0.00033671 | 0.00033217 | 0.00032763 | 0.00032308 | 0.00031854 | 0.000314 | 0.00030945 | 0.00030491 | 0.00030037 | 0.00029582 | 0.00029128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-163312849 | 9 | 9 | 0.0001696 | 0 | 0.00022825 | 0 | 0.00017458 | 0 | 1.6757e-06 | -2.6836e-06 | 0.00022155 | 0.00022322 | 0.0002249 | 0.00022657 | 0.00022825 | 0.00022556 | 0.00022288 | 0.0002202 | 0.00021751 | 0.00021483 | 0.00021215 | 0.00020946 | 0.00020678 | 0.0002041 | 0.00020141 | 0.00019873 | 0.00019604 | 0.00019336 | 0.00019068 | 0.00018799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-163376810 | 45 | 45 | 0.00024663 | 0 | 0.00035151 | 0 | 0.00026521 | 0 | 2.9967e-06 | -4.3154e-06 | 0.00033953 | 0.00034252 | 0.00034552 | 0.00034852 | 0.00035151 | 0.0003472 | 0.00034288 | 0.00033857 | 0.00033425 | 0.00032994 | 0.00032562 | 0.00032131 | 0.00031699 | 0.00031268 | 0.00030836 | 0.00030404 | 0.00029973 | 0.00029541 | 0.0002911 | 0.00028678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-163377041 | 12 | 12 | 1.19e-05 | 0 | 1.74e-05 | 0 | 1.1e-05 | 0 | 1.5714e-07 | -3.2e-07 | 1.6771e-05 | 1.6929e-05 | 1.7086e-05 | 1.7243e-05 | 1.74e-05 | 1.708e-05 | 1.676e-05 | 1.644e-05 | 1.612e-05 | 1.58e-05 | 1.548e-05 | 1.516e-05 | 1.484e-05 | 1.452e-05 | 1.42e-05 | 1.388e-05 | 1.356e-05 | 1.324e-05 | 1.292e-05 | 1.26e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-163377167 | 45 | 45 | 0.00022173 | 0 | 0.00033204 | 0 | 0.00024315 | 0 | 3.1515e-06 | -4.4441e-06 | 0.00031943 | 0.00032258 | 0.00032573 | 0.00032888 | 0.00033204 | 0.00032759 | 0.00032315 | 0.0003187 | 0.00031426 | 0.00030981 | 0.00030537 | 0.00030093 | 0.00029648 | 0.00029204 | 0.00028759 | 0.00028315 | 0.00027871 | 0.00027426 | 0.00026982 | 0.00026537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-163377432 | 5 | 5 | 0.00044902 | 0 | 0.00061378 | 0 | 0.00043317 | 0 | 4.7074e-06 | -9.0306e-06 | 0.00059495 | 0.00059965 | 0.00060436 | 0.00060907 | 0.00061378 | 0.00060475 | 0.00059571 | 0.00058668 | 0.00057765 | 0.00056862 | 0.00055959 | 0.00055056 | 0.00054153 | 0.0005325 | 0.00052347 | 0.00051444 | 0.00050541 | 0.00049638 | 0.00048735 | 0.00047832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-163377643 | 13 | 13 | 1.26e-05 | 0 | 1.9e-05 | 0 | 1.03e-05 | 0 | 1.8286e-07 | -4.35e-07 | 1.8269e-05 | 1.8451e-05 | 1.8634e-05 | 1.8817e-05 | 1.9e-05 | 1.8565e-05 | 1.813e-05 | 1.7695e-05 | 1.726e-05 | 1.6825e-05 | 1.639e-05 | 1.5955e-05 | 1.552e-05 | 1.5085e-05 | 1.465e-05 | 1.4215e-05 | 1.378e-05 | 1.3345e-05 | 1.291e-05 | 1.2475e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-163377831 | 10 | 10 | 0.00039611 | 0 | 0.00053616 | 0 | 0.00036002 | 0 | 4.0015e-06 | -8.8071e-06 | 0.00052015 | 0.00052415 | 0.00052815 | 0.00053216 | 0.00053616 | 0.00052735 | 0.00051854 | 0.00050974 | 0.00050093 | 0.00049212 | 0.00048332 | 0.00047451 | 0.0004657 | 0.00045689 | 0.00044809 | 0.00043928 | 0.00043047 | 0.00042167 | 0.00041286 | 0.00040405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-24611768 | 50 | 0 | 0.001172 | 7.37e-05 | 0.0015687 | 0.00010312 | 0.001336 | 8.58e-05 | 1.1335e-05 | -1.1635e-05 | 0.0015233 | 0.0015347 | 0.001546 | 0.0015574 | 0.0015687 | 0.0015571 | 0.0015454 | 0.0015338 | 0.0015221 | 0.0015105 | 0.0014989 | 0.0014872 | 0.0014756 | 0.001464 | 0.0014523 | 0.0014407 | 0.0014291 | 0.0014174 | 0.0014058 | 0.0013942 | 8.4051e-07 | -8.659e-07 | 9.9756e-05 | 0.0001006 | 0.00010144 | 0.00010228 | 0.00010312 | 0.00010225 | 0.00010139 | 0.00010052 | 9.9654e-05 | 9.8789e-05 | 9.7923e-05 | 9.7057e-05 | 9.6191e-05 | 9.5325e-05 | 9.4459e-05 | 9.3593e-05 | 9.2727e-05 | 9.1861e-05 | 9.0995e-05 | 9.013e-05
| KRT013-79724634 | 592 | 497 | 0.00018972 | 0.00020005 | 0.00026292 | 0.00029255 | 0.00021994 | 0.00023817 | 2.0914e-06 | -2.1491e-06 | 0.00025456 | 0.00025665 | 0.00025874 | 0.00026083 | 0.00026292 | 0.00026077 | 0.00025862 | 0.00025647 | 0.00025432 | 0.00025218 | 0.00025003 | 0.00024788 | 0.00024573 | 0.00024358 | 0.00024143 | 0.00023928 | 0.00023713 | 0.00023498 | 0.00023283 | 0.00023068 | 2.643e-06 | -2.7194e-06 | 0.00028198 | 0.00028462 | 0.00028727 | 0.00028991 | 0.00029255 | 0.00028983 | 0.00028712 | 0.0002844 | 0.00028168 | 0.00027896 | 0.00027624 | 0.00027352 | 0.0002708 | 0.00026808 | 0.00026536 | 0.00026264 | 0.00025992 | 0.0002572 | 0.00025448 | 0.00025176
| KRT013-79724804 | 679 | 496 | 0.0042949 | 0.0025855 | 0.0054089 | 0.0034559 | 0.0037769 | 0.0020207 | 3.183e-05 | -8.1602e-05 | 0.0052816 | 0.0053134 | 0.0053452 | 0.0053771 | 0.0054089 | 0.0053273 | 0.0052457 | 0.0051641 | 0.0050825 | 0.0050009 | 0.0049193 | 0.0048377 | 0.0047561 | 0.0046745 | 0.0045929 | 0.0045113 | 0.0044297 | 0.0043481 | 0.0042665 | 0.0041849 | 2.4869e-05 | -7.1759e-05 | 0.0033564 | 0.0033813 | 0.0034061 | 0.003431 | 0.0034559 | 0.0033841 | 0.0033123 | 0.0032406 | 0.0031688 | 0.0030971 | 0.0030253 | 0.0029535 | 0.0028818 | 0.00281 | 0.0027383 | 0.0026665 | 0.0025948 | 0.002523 | 0.0024512 | 0.0023795
| KRT022-15396980 | 3037 | 636 | 0.00090448 | 6.3e-05 | 0.001435 | 0.00010143 | 0.00082607 | 5.56e-05 | 1.5158e-05 | -3.0448e-05 | 0.0013744 | 0.0013895 | 0.0014047 | 0.0014199 | 0.001435 | 0.0014046 | 0.0013741 | 0.0013437 | 0.0013132 | 0.0012828 | 0.0012523 | 0.0012219 | 0.0011914 | 0.001161 | 0.0011305 | 0.0011001 | 0.0010697 | 0.0010392 | 0.0010088 | 0.00097831 | 1.0981e-06 | -2.2917e-06 | 9.7042e-05 | 9.814e-05 | 9.9238e-05 | 0.00010034 | 0.00010143 | 9.9142e-05 | 9.6851e-05 | 9.4559e-05 | 9.2267e-05 | 8.9975e-05 | 8.7684e-05 | 8.5392e-05 | 8.31e-05 | 8.0809e-05 | 7.8517e-05 | 7.6225e-05 | 7.3934e-05 | 7.1642e-05 | 6.935e-05 | 6.7058e-05
| KRT022-72389353 | 2401 | 2401 | 0.0025169 | 0 | 0.0032435 | 0 | 0.0028179 | 0 | 2.0761e-05 | -2.1279e-05 | 0.0031605 | 0.0031812 | 0.003202 | 0.0032227 | 0.0032435 | 0.0032222 | 0.0032009 | 0.0031797 | 0.0031584 | 0.0031371 | 0.0031158 | 0.0030946 | 0.0030733 | 0.003052 | 0.0030307 | 0.0030094 | 0.0029882 | 0.0029669 | 0.0029456 | 0.0029243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT023-15396956 | 1792 | 1792 | 1.38e-05 | 0 | 1.88e-05 | 0 | 1.53e-05 | 0 | 1.4286e-07 | -1.75e-07 | 1.8229e-05 | 1.8371e-05 | 1.8514e-05 | 1.8657e-05 | 1.88e-05 | 1.8625e-05 | 1.845e-05 | 1.8275e-05 | 1.81e-05 | 1.7925e-05 | 1.775e-05 | 1.7575e-05 | 1.74e-05 | 1.7225e-05 | 1.705e-05 | 1.6875e-05 | 1.67e-05 | 1.6525e-05 | 1.635e-05 | 1.6175e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT031-15433128 | 166 | 158 | 0.00011372 | 0.00015276 | 0.00017429 | 0.00023461 | 8.47e-05 | 0.00011402 | 1.7305e-06 | -4.4795e-06 | 0.00016737 | 0.0001691 | 0.00017083 | 0.00017256 | 0.00017429 | 0.00016981 | 0.00016533 | 0.00016085 | 0.00015637 | 0.00015189 | 0.00014741 | 0.00014293 | 0.00013845 | 0.00013397 | 0.0001295 | 0.00012502 | 0.00012054 | 0.00011606 | 0.00011158 | 0.0001071 | 2.3387e-06 | -6.0294e-06 | 0.00022526 | 0.0002276 | 0.00022994 | 0.00023228 | 0.00023461 | 0.00022858 | 0.00022256 | 0.00021653 | 0.0002105 | 0.00020447 | 0.00019844 | 0.00019241 | 0.00018638 | 0.00018035 | 0.00017432 | 0.00016829 | 0.00016226 | 0.00015623 | 0.0001502 | 0.00014417
| KRT031-163356648 | 8 | 8 | 0.00025298 | 0 | 0.00038833 | 0 | 0.00018904 | 0 | 3.867e-06 | -9.9644e-06 | 0.00037286 | 0.00037673 | 0.0003806 | 0.00038446 | 0.00038833 | 0.00037836 | 0.0003684 | 0.00035844 | 0.00034847 | 0.00033851 | 0.00032854 | 0.00031858 | 0.00030861 | 0.00029865 | 0.00028869 | 0.00027872 | 0.00026876 | 0.00025879 | 0.00024883 | 0.00023886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM001-15421949 | 593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM001-15421988 | 593 | 575 | 0.011697 | 0.00020407 | 0.015284 | 0.00028386 | 0.016984 | 0.00033073 | 0.00010249 | 8.5015e-05 | 0.014874 | 0.014977 | 0.015079 | 0.015182 | 0.015284 | 0.015369 | 0.015454 | 0.015539 | 0.015624 | 0.015709 | 0.015794 | 0.015879 | 0.015964 | 0.016049 | 0.016134 | 0.016219 | 0.016304 | 0.016389 | 0.016474 | 0.016559 | 2.2798e-06 | 2.3435e-06 | 0.00027474 | 0.00027702 | 0.0002793 | 0.00028158 | 0.00028386 | 0.0002862 | 0.00028855 | 0.00029089 | 0.00029323 | 0.00029558 | 0.00029792 | 0.00030026 | 0.00030261 | 0.00030495 | 0.00030729 | 0.00030964 | 0.00031198 | 0.00031432 | 0.00031667 | 0.00031901
| KYM001-155421580 | 6 | 6 | 6.88e-06 | 0 | 9.13e-06 | 0 | 1.11e-05 | 0 | 6.4286e-08 | 9.85e-08 | 8.8729e-06 | 8.9371e-06 | 9.0014e-06 | 9.0657e-06 | 9.13e-06 | 9.2285e-06 | 9.327e-06 | 9.4255e-06 | 9.524e-06 | 9.6225e-06 | 9.721e-06 | 9.8195e-06 | 9.918e-06 | 1.0016e-05 | 1.0115e-05 | 1.0213e-05 | 1.0312e-05 | 1.041e-05 | 1.0509e-05 | 1.0607e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM001-155421922 | 12 | 12 | 0.00023317 | 0 | 0.00030978 | 0 | 0.00037016 | 0 | 2.1887e-06 | 3.0189e-06 | 0.00030102 | 0.00030321 | 0.0003054 | 0.00030759 | 0.00030978 | 0.0003128 | 0.00031582 | 0.00031884 | 0.00032185 | 0.00032487 | 0.00032789 | 0.00033091 | 0.00033393 | 0.00033695 | 0.00033997 | 0.00034299 | 0.00034601 | 0.00034902 | 0.00035204 | 0.00035506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM002-15422060 | 1072 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM002-15422073 | 1070 | 1070 | 0.0010312 | 0 | 0.0011348 | 0 | 0.0011382 | 0 | 2.9597e-06 | 1.74e-07 | 0.0011229 | 0.0011259 | 0.0011288 | 0.0011318 | 0.0011348 | 0.0011349 | 0.0011351 | 0.0011353 | 0.0011355 | 0.0011356 | 0.0011358 | 0.001136 | 0.0011362 | 0.0011363 | 0.0011365 | 0.0011367 | 0.0011369 | 0.001137 | 0.0011372 | 0.0011374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM002-182106953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM003-15421938 | 1159 | 756 | 0.0037513 | 0.00091977 | 0.0047016 | 0.0012047 | 0.0054001 | 0.0015167 | 2.7153e-05 | 3.4925e-05 | 0.004593 | 0.0046202 | 0.0046473 | 0.0046745 | 0.0047016 | 0.0047365 | 0.0047715 | 0.0048064 | 0.0048413 | 0.0048762 | 0.0049112 | 0.0049461 | 0.004981 | 0.0050159 | 0.0050509 | 0.0050858 | 0.0051207 | 0.0051556 | 0.0051906 | 0.0052255 | 8.1408e-06 | 1.56e-05 | 0.0011721 | 0.0011803 | 0.0011884 | 0.0011966 | 0.0012047 | 0.0012203 | 0.0012359 | 0.0012515 | 0.0012671 | 0.0012827 | 0.0012983 | 0.0013139 | 0.0013295 | 0.0013451 | 0.0013607 | 0.0013763 | 0.0013919 | 0.0014075 | 0.0014231 | 0.0014387
| KYM003-155504708 | 15 | 15 | 0.0024472 | 0 | 0.0031583 | 0 | 0.0037432 | 0 | 2.0317e-05 | 2.9244e-05 | 0.0030771 | 0.0030974 | 0.0031177 | 0.003138 | 0.0031583 | 0.0031876 | 0.0032168 | 0.0032461 | 0.0032753 | 0.0033045 | 0.0033338 | 0.003363 | 0.0033923 | 0.0034215 | 0.0034508 | 0.00348 | 0.0035092 | 0.0035385 | 0.0035677 | 0.003597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM003-163531836 | 13 | 13 | 0.00030919 | 0 | 0.0003928 | 0 | 0.00048808 | 0 | 2.3889e-06 | 4.7639e-06 | 0.00038324 | 0.00038563 | 0.00038802 | 0.00039041 | 0.0003928 | 0.00039756 | 0.00040233 | 0.00040709 | 0.00041186 | 0.00041662 | 0.00042138 | 0.00042615 | 0.00043091 | 0.00043567 | 0.00044044 | 0.0004452 | 0.00044997 | 0.00045473 | 0.00045949 | 0.00046426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM003-24602826 | 403 | 375 | 0.006895 | 0.0014996 | 0.0082213 | 0.0018885 | 0.0095428 | 0.0022998 | 3.7894e-05 | 6.6073e-05 | 0.0080697 | 0.0081076 | 0.0081455 | 0.0081834 | 0.0082213 | 0.0082874 | 0.0083534 | 0.0084195 | 0.0084856 | 0.0085517 | 0.0086177 | 0.0086838 | 0.0087499 | 0.008816 | 0.008882 | 0.0089481 | 0.0090142 | 0.0090802 | 0.0091463 | 0.0092124 | 1.1111e-05 | 2.0565e-05 | 0.001844 | 0.0018551 | 0.0018662 | 0.0018774 | 0.0018885 | 0.001909 | 0.0019296 | 0.0019502 | 0.0019707 | 0.0019913 | 0.0020119 | 0.0020324 | 0.002053 | 0.0020735 | 0.0020941 | 0.0021147 | 0.0021352 | 0.0021558 | 0.0021764 | 0.0021969
| KYM004-15422136 | 1528 | 1076 | 0.0013058 | 0.00016385 | 0.001632 | 0.00021693 | 0.0017642 | 0.00025529 | 9.3208e-06 | 6.6088e-06 | 0.0015947 | 0.0016041 | 0.0016134 | 0.0016227 | 0.001632 | 0.0016386 | 0.0016452 | 0.0016518 | 0.0016584 | 0.0016651 | 0.0016717 | 0.0016783 | 0.0016849 | 0.0016915 | 0.0016981 | 0.0017047 | 0.0017113 | 0.0017179 | 0.0017245 | 0.0017311 | 1.5163e-06 | 1.918e-06 | 0.00021086 | 0.00021238 | 0.00021389 | 0.00021541 | 0.00021693 | 0.00021884 | 0.00022076 | 0.00022268 | 0.0002246 | 0.00022652 | 0.00022843 | 0.00023035 | 0.00023227 | 0.00023419 | 0.00023611 | 0.00023802 | 0.00023994 | 0.00024186 | 0.00024378 | 0.0002457
| KYM004-24596780 | 294 | 294 | 0.0038812 | 0 | 0.0047662 | 0 | 0.0054269 | 0 | 2.5286e-05 | 3.3033e-05 | 0.0046651 | 0.0046904 | 0.0047156 | 0.0047409 | 0.0047662 | 0.0047992 | 0.0048323 | 0.0048653 | 0.0048983 | 0.0049314 | 0.0049644 | 0.0049974 | 0.0050305 | 0.0050635 | 0.0050965 | 0.0051296 | 0.0051626 | 0.0051956 | 0.0052287 | 0.0052617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM004-24596836 | 158 | 158 | 0.010789 | 0 | 0.013566 | 0 | 0.01508 | 0 | 7.9333e-05 | 7.5721e-05 | 0.013248 | 0.013328 | 0.013407 | 0.013486 | 0.013566 | 0.013641 | 0.013717 | 0.013793 | 0.013869 | 0.013944 | 0.01402 | 0.014096 | 0.014171 | 0.014247 | 0.014323 | 0.014399 | 0.014474 | 0.01455 | 0.014626 | 0.014702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM005-15421849 | 2033 | 2033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM006-15422186 | 474 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM006-15422212 | 473 | 473 | 0.001764 | 0 | 0.0023296 | 0 | 0.0027465 | 0 | 1.616e-05 | 2.084e-05 | 0.002265 | 0.0022812 | 0.0022973 | 0.0023135 | 0.0023296 | 0.0023505 | 0.0023713 | 0.0023922 | 0.002413 | 0.0024339 | 0.0024547 | 0.0024755 | 0.0024964 | 0.0025172 | 0.0025381 | 0.0025589 | 0.0025797 | 0.0026006 | 0.0026214 | 0.0026423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV001-15406542 | 5658 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV001-15406555 | 5635 | 3711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV001-24613045 | 1924 | 1924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV002-15406265 | 6572 | 6572 | 0.00011965 | 0 | 0.00016403 | 0 | 0.00017947 | 0 | 1.2681e-06 | 7.7195e-07 | 0.00015896 | 0.00016023 | 0.0001615 | 0.00016277 | 0.00016403 | 0.00016481 | 0.00016558 | 0.00016635 | 0.00016712 | 0.00016789 | 0.00016867 | 0.00016944 | 0.00017021 | 0.00017098 | 0.00017175 | 0.00017253 | 0.0001733 | 0.00017407 | 0.00017484 | 0.00017561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV003-15406616 | 4752 | 4752 | 0.00045714 | 0 | 0.00062337 | 0 | 0.000658 | 0 | 4.7494e-06 | 1.7316e-06 | 0.00060437 | 0.00060912 | 0.00061387 | 0.00061862 | 0.00062337 | 0.0006251 | 0.00062683 | 0.00062856 | 0.00063029 | 0.00063203 | 0.00063376 | 0.00063549 | 0.00063722 | 0.00063895 | 0.00064068 | 0.00064241 | 0.00064415 | 0.00064588 | 0.00064761 | 0.00064934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV004-15406315 | 6072 | 6072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV004-24612407 | 0 | 0 | 0.0022915 | 0 | 0.0029 | 0 | 0.0029183 | 0 | 1.7385e-05 | 9.1545e-07 | 0.0028305 | 0.0028479 | 0.0028652 | 0.0028826 | 0.0029 | 0.0029009 | 0.0029018 | 0.0029028 | 0.0029037 | 0.0029046 | 0.0029055 | 0.0029064 | 0.0029073 | 0.0029082 | 0.0029092 | 0.0029101 | 0.002911 | 0.0029119 | 0.0029128 | 0.0029137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV005-15406664 | 1748 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV005-15406790 | 1498 | 1498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV006-15406376 | 5844 | 2816 | 0.023032 | 0 | 0.033518 | 0 | 0.033223 | 0 | 0.00029958 | -1.473e-05 | 0.032319 | 0.032619 | 0.032918 | 0.033218 | 0.033518 | 0.033503 | 0.033488 | 0.033473 | 0.033459 | 0.033444 | 0.033429 | 0.033414 | 0.0334 | 0.033385 | 0.03337 | 0.033355 | 0.033341 | 0.033326 | 0.033311 | 0.033297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV006-160301671 | 3028 | 3028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV007-15406690 | 3475 | 3475 | 0.00021777 | 0 | 0.00029855 | 0 | 0.00032665 | 0 | 2.3081e-06 | 1.4049e-06 | 0.00028932 | 0.00029163 | 0.00029393 | 0.00029624 | 0.00029855 | 0.00029995 | 0.00030136 | 0.00030276 | 0.00030417 | 0.00030557 | 0.00030698 | 0.00030838 | 0.00030979 | 0.00031119 | 0.0003126 | 0.000314 | 0.00031541 | 0.00031681 | 0.00031822 | 0.00031962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV008-15406413 | 3958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV008-24612803 | 3612 | 3612 | 4.5e-06 | 0 | 7.41e-06 | 0 | 7.22e-06 | 0 | 8.3143e-08 | -9.5e-09 | 7.0774e-06 | 7.1606e-06 | 7.2437e-06 | 7.3269e-06 | 7.41e-06 | 7.4005e-06 | 7.391e-06 | 7.3815e-06 | 7.372e-06 | 7.3625e-06 | 7.353e-06 | 7.3435e-06 | 7.334e-06 | 7.3245e-06 | 7.315e-06 | 7.3055e-06 | 7.296e-06 | 7.2865e-06 | 7.277e-06 | 7.2675e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV008-24612817 | 346 | 346 | 2.33e-05 | 0 | 2.96e-05 | 0 | 3.18e-05 | 0 | 1.8e-07 | 1.1e-07 | 2.888e-05 | 2.906e-05 | 2.924e-05 | 2.942e-05 | 2.96e-05 | 2.971e-05 | 2.982e-05 | 2.993e-05 | 3.004e-05 | 3.015e-05 | 3.026e-05 | 3.037e-05 | 3.048e-05 | 3.059e-05 | 3.07e-05 | 3.081e-05 | 3.092e-05 | 3.103e-05 | 3.114e-05 | 3.125e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV009-15406766 | 3497 | 1145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV009-155428316 | 1889 | 1889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV009-24611519 | 463 | 463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV010-15437621 | 2698 | 2698 | 5.81e-06 | 0 | 7.97e-06 | 0 | 8.72e-06 | 0 | 6.1714e-08 | 3.75e-08 | 7.7231e-06 | 7.7849e-06 | 7.8466e-06 | 7.9083e-06 | 7.97e-06 | 8.0075e-06 | 8.045e-06 | 8.0825e-06 | 8.12e-06 | 8.1575e-06 | 8.195e-06 | 8.2325e-06 | 8.27e-06 | 8.3075e-06 | 8.345e-06 | 8.3825e-06 | 8.42e-06 | 8.4575e-06 | 8.495e-06 | 8.5325e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN021-15436461 | 53 | 53 | 8.26e-06 | 0 | 1.3e-05 | 0 | 1.28e-05 | 0 | 1.3543e-07 | -1e-08 | 1.2458e-05 | 1.2594e-05 | 1.2729e-05 | 1.2865e-05 | 1.3e-05 | 1.299e-05 | 1.298e-05 | 1.297e-05 | 1.296e-05 | 1.295e-05 | 1.294e-05 | 1.293e-05 | 1.292e-05 | 1.291e-05 | 1.29e-05 | 1.289e-05 | 1.288e-05 | 1.287e-05 | 1.286e-05 | 1.285e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN022-131932324 | 1850 | 1850 | 2.43e-05 | 0 | 3.81e-05 | 0 | 3.41e-05 | 0 | 3.9429e-07 | -2e-07 | 3.6523e-05 | 3.6917e-05 | 3.7311e-05 | 3.7706e-05 | 3.81e-05 | 3.79e-05 | 3.77e-05 | 3.75e-05 | 3.73e-05 | 3.71e-05 | 3.69e-05 | 3.67e-05 | 3.65e-05 | 3.63e-05 | 3.61e-05 | 3.59e-05 | 3.57e-05 | 3.55e-05 | 3.53e-05 | 3.51e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN022-15436485 | 4726 | 2876 | 5.87e-05 | 0 | 9.66e-05 | 0 | 9.41e-05 | 0 | 1.0829e-06 | -1.25e-07 | 9.2269e-05 | 9.3351e-05 | 9.4434e-05 | 9.5517e-05 | 9.66e-05 | 9.6475e-05 | 9.635e-05 | 9.6225e-05 | 9.61e-05 | 9.5975e-05 | 9.585e-05 | 9.5725e-05 | 9.56e-05 | 9.5475e-05 | 9.535e-05 | 9.5225e-05 | 9.51e-05 | 9.4975e-05 | 9.485e-05 | 9.4725e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN022-155325443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN023-15436448 | 151 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN024-15436435 | 54 | 54 | 5.24e-05 | 0 | 8.23e-05 | 0 | 8.14e-05 | 0 | 8.5429e-07 | -4.5e-08 | 7.8883e-05 | 7.9737e-05 | 8.0591e-05 | 8.1446e-05 | 8.23e-05 | 8.2255e-05 | 8.221e-05 | 8.2165e-05 | 8.212e-05 | 8.2075e-05 | 8.203e-05 | 8.1985e-05 | 8.194e-05 | 8.1895e-05 | 8.185e-05 | 8.1805e-05 | 8.176e-05 | 8.1715e-05 | 8.167e-05 | 8.1625e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN031-15432398 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN032-15432411 | 248 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN033-15432424 | 158 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN034-15432437 | 108 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN012-15419426 | 2482 | 2482 | 0.013416 | 0 | 0.016884 | 0 | 0.016783 | 0 | 9.9081e-05 | -5.0799e-06 | 0.016488 | 0.016587 | 0.016686 | 0.016785 | 0.016884 | 0.016879 | 0.016874 | 0.016869 | 0.016864 | 0.016859 | 0.016854 | 0.016849 | 0.016844 | 0.016838 | 0.016833 | 0.016828 | 0.016823 | 0.016818 | 0.016813 | 0.016808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN012-15419437 | 2494 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN013-15419363 | 871 | 501 | 0.0008311 | 0.00050144 | 0.0010631 | 0.00066354 | 0.0010776 | 0.00068976 | 6.6295e-06 | 7.237e-07 | 0.0010366 | 0.0010432 | 0.0010499 | 0.0010565 | 0.0010631 | 0.0010639 | 0.0010646 | 0.0010653 | 0.001066 | 0.0010668 | 0.0010675 | 0.0010682 | 0.0010689 | 0.0010696 | 0.0010704 | 0.0010711 | 0.0010718 | 0.0010725 | 0.0010733 | 0.001074 | 4.6315e-06 | 1.3109e-06 | 0.00064501 | 0.00064965 | 0.00065428 | 0.00065891 | 0.00066354 | 0.00066485 | 0.00066616 | 0.00066747 | 0.00066878 | 0.0006701 | 0.00067141 | 0.00067272 | 0.00067403 | 0.00067534 | 0.00067665 | 0.00067796 | 0.00067927 | 0.00068058 | 0.00068189 | 0.00068321
| MBN013-182964938 | 178 | 178 | 0.0019791 | 0 | 0.0026144 | 0 | 0.0025546 | 0 | 1.815e-05 | -2.9901e-06 | 0.0025418 | 0.00256 | 0.0025781 | 0.0025963 | 0.0026144 | 0.0026114 | 0.0026084 | 0.0026054 | 0.0026025 | 0.0025995 | 0.0025965 | 0.0025935 | 0.0025905 | 0.0025875 | 0.0025845 | 0.0025815 | 0.0025785 | 0.0025755 | 0.0025726 | 0.0025696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN013-24605754 | 370 | 192 | 0.0075105 | 0.00093336 | 0.0096645 | 0.0012497 | 0.0093933 | 0.00124 | 6.1541e-05 | -1.3557e-05 | 0.0094183 | 0.0094799 | 0.0095414 | 0.0096029 | 0.0096645 | 0.0096509 | 0.0096374 | 0.0096238 | 0.0096102 | 0.0095967 | 0.0095831 | 0.0095696 | 0.009556 | 0.0095425 | 0.0095289 | 0.0095154 | 0.0095018 | 0.0094882 | 0.0094747 | 0.0094611 | 9.0374e-06 | -4.848e-07 | 0.0012135 | 0.0012226 | 0.0012316 | 0.0012406 | 0.0012497 | 0.0012492 | 0.0012487 | 0.0012482 | 0.0012477 | 0.0012472 | 0.0012468 | 0.0012463 | 0.0012458 | 0.0012453 | 0.0012448 | 0.0012443 | 0.0012439 | 0.0012434 | 0.0012429 | 0.0012424
| MBN014-15419313 | 1044 | 737 | 0.0014256 | 0.00022295 | 0.0018524 | 0.00029084 | 0.0018765 | 0.00029547 | 1.2194e-05 | 1.2051e-06 | 0.0018036 | 0.0018158 | 0.001828 | 0.0018402 | 0.0018524 | 0.0018536 | 0.0018548 | 0.001856 | 0.0018572 | 0.0018584 | 0.0018596 | 0.0018608 | 0.001862 | 0.0018633 | 0.0018645 | 0.0018657 | 0.0018669 | 0.0018681 | 0.0018693 | 0.0018705 | 1.9397e-06 | 2.3145e-07 | 0.00028308 | 0.00028502 | 0.00028696 | 0.0002889 | 0.00029084 | 0.00029107 | 0.0002913 | 0.00029153 | 0.00029177 | 0.000292 | 0.00029223 | 0.00029246 | 0.00029269 | 0.00029292 | 0.00029315 | 0.00029339 | 0.00029362 | 0.00029385 | 0.00029408 | 0.00029431
| MBN014-160652409 | 8 | 8 | 0.00017853 | 0 | 0.00023497 | 0 | 0.00022713 | 0 | 1.6124e-06 | -3.921e-07 | 0.00022852 | 0.00023013 | 0.00023174 | 0.00023335 | 0.00023497 | 0.00023457 | 0.00023418 | 0.00023379 | 0.0002334 | 0.00023301 | 0.00023261 | 0.00023222 | 0.00023183 | 0.00023144 | 0.00023105 | 0.00023065 | 0.00023026 | 0.00022987 | 0.00022948 | 0.00022909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN014-24605768 | 307 | 299 | 0.00079595 | 5.8e-05 | 0.0010479 | 7.76e-05 | 0.0010211 | 7.64e-05 | 7.1983e-06 | -1.3379e-06 | 0.0010191 | 0.0010263 | 0.0010335 | 0.0010407 | 0.0010479 | 0.0010466 | 0.0010452 | 0.0010439 | 0.0010425 | 0.0010412 | 0.0010399 | 0.0010385 | 0.0010372 | 0.0010359 | 0.0010345 | 0.0010332 | 0.0010318 | 0.0010305 | 0.0010292 | 0.0010278 | 5.6e-07 | -6e-08 | 7.536e-05 | 7.592e-05 | 7.648e-05 | 7.704e-05 | 7.76e-05 | 7.754e-05 | 7.748e-05 | 7.742e-05 | 7.736e-05 | 7.73e-05 | 7.724e-05 | 7.718e-05 | 7.712e-05 | 7.706e-05 | 7.7e-05 | 7.694e-05 | 7.688e-05 | 7.682e-05 | 7.676e-05 | 7.67e-05
| MBN023-94547225 | 3283 | 8 | 7e-06 | 7.64e-06 | 7e-06 | 7.64e-06 | 7e-06 | 7.64e-06 | 0 | 0 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 7e-06 | 0 | 0 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06 | 7.64e-06
| MBN023-94547273 | 3275 | 3275 | 0.03441 | 0 | 0.04492 | 0 | 0.044294 | 0 | 0.0003003 | -3.132e-05 | 0.043719 | 0.044019 | 0.04432 | 0.04462 | 0.04492 | 0.044889 | 0.044858 | 0.044826 | 0.044795 | 0.044764 | 0.044732 | 0.044701 | 0.04467 | 0.044638 | 0.044607 | 0.044576 | 0.044544 | 0.044513 | 0.044482 | 0.04445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN031-140147987 | 708 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN031-140148011 | 705 | 616 | 0.00059919 | 7.05e-05 | 0.00079348 | 9.45e-05 | 0.00077557 | 9.3e-05 | 5.5511e-06 | -8.957e-07 | 0.00077128 | 0.00077683 | 0.00078238 | 0.00078793 | 0.00079348 | 0.00079259 | 0.00079169 | 0.0007908 | 0.0007899 | 0.000789 | 0.00078811 | 0.00078721 | 0.00078632 | 0.00078542 | 0.00078453 | 0.00078363 | 0.00078273 | 0.00078184 | 0.00078094 | 0.00078005 | 6.8571e-07 | -7.5e-08 | 9.1757e-05 | 9.2443e-05 | 9.3129e-05 | 9.3814e-05 | 9.45e-05 | 9.4425e-05 | 9.435e-05 | 9.4275e-05 | 9.42e-05 | 9.4125e-05 | 9.405e-05 | 9.3975e-05 | 9.39e-05 | 9.3825e-05 | 9.375e-05 | 9.3675e-05 | 9.36e-05 | 9.3525e-05 | 9.345e-05 | 9.3375e-05
| MBN031-162765180 | 1 | 1 | 1.06e-07 | 0 | 1.41e-07 | 0 | 1.42e-07 | 0 | 1e-09 | 5e-11 | 1.37e-07 | 1.38e-07 | 1.39e-07 | 1.4e-07 | 1.41e-07 | 1.4105e-07 | 1.411e-07 | 1.4115e-07 | 1.412e-07 | 1.4125e-07 | 1.413e-07 | 1.4135e-07 | 1.414e-07 | 1.4145e-07 | 1.415e-07 | 1.4155e-07 | 1.416e-07 | 1.4165e-07 | 1.417e-07 | 1.4175e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN031-24605740 | 89 | 0 | 0.0026824 | 1.66e-05 | 0.0034769 | 1.97e-05 | 0.0034072 | 1.8e-05 | 2.2699e-05 | -3.4845e-06 | 0.0033861 | 0.0034088 | 0.0034315 | 0.0034542 | 0.0034769 | 0.0034734 | 0.0034699 | 0.0034664 | 0.003463 | 0.0034595 | 0.003456 | 0.0034525 | 0.003449 | 0.0034455 | 0.0034421 | 0.0034386 | 0.0034351 | 0.0034316 | 0.0034281 | 0.0034246 | 8.8571e-08 | -8.5e-08 | 1.9346e-05 | 1.9434e-05 | 1.9523e-05 | 1.9611e-05 | 1.97e-05 | 1.9615e-05 | 1.953e-05 | 1.9445e-05 | 1.936e-05 | 1.9275e-05 | 1.919e-05 | 1.9105e-05 | 1.902e-05 | 1.8935e-05 | 1.885e-05 | 1.8765e-05 | 1.868e-05 | 1.8595e-05 | 1.851e-05 | 1.8425e-05
| MBN031-52301620 | 89 | 88 | 0.003327 | 1.06e-07 | 0.0041236 | 1.41e-07 | 0.0039375 | 1.42e-07 | 2.2758e-05 | -9.3018e-06 | 0.0040325 | 0.0040553 | 0.0040781 | 0.0041008 | 0.0041236 | 0.0041143 | 0.004105 | 0.0040957 | 0.0040864 | 0.0040771 | 0.0040678 | 0.0040585 | 0.0040492 | 0.0040399 | 0.0040306 | 0.0040213 | 0.0040119 | 0.0040026 | 0.0039933 | 0.003984 | 1e-09 | 5e-11 | 1.37e-07 | 1.38e-07 | 1.39e-07 | 1.4e-07 | 1.41e-07 | 1.4105e-07 | 1.411e-07 | 1.4115e-07 | 1.412e-07 | 1.4125e-07 | 1.413e-07 | 1.4135e-07 | 1.414e-07 | 1.4145e-07 | 1.415e-07 | 1.4155e-07 | 1.416e-07 | 1.4165e-07 | 1.417e-07 | 1.4175e-07
| MBN032-140148075 | 2319 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN032-140148099 | 2315 | 2315 | 0.0017199 | 0 | 0.0022616 | 0 | 0.0023147 | 0 | 1.5477e-05 | 2.6533e-06 | 0.0021997 | 0.0022152 | 0.0022306 | 0.0022461 | 0.0022616 | 0.0022642 | 0.0022669 | 0.0022696 | 0.0022722 | 0.0022749 | 0.0022775 | 0.0022802 | 0.0022828 | 0.0022855 | 0.0022881 | 0.0022908 | 0.0022934 | 0.0022961 | 0.0022987 | 0.0023014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA022-15412339 | 1762 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA022-15412350 | 1770 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA022-24605196 | 860 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA023-15412302 | 3035 | 2290 | 0.0053277 | 0.00047659 | 0.0067012 | 0.00063177 | 0.006731 | 0.00067447 | 3.9243e-05 | 1.4897e-06 | 0.0065442 | 0.0065835 | 0.0066227 | 0.006662 | 0.0067012 | 0.0067027 | 0.0067042 | 0.0067057 | 0.0067072 | 0.0067087 | 0.0067102 | 0.0067116 | 0.0067131 | 0.0067146 | 0.0067161 | 0.0067176 | 0.0067191 | 0.0067206 | 0.0067221 | 0.0067236 | 4.4335e-06 | 2.1353e-06 | 0.00061403 | 0.00061847 | 0.0006229 | 0.00062733 | 0.00063177 | 0.0006339 | 0.00063604 | 0.00063817 | 0.00064031 | 0.00064244 | 0.00064458 | 0.00064671 | 0.00064885 | 0.00065098 | 0.00065312 | 0.00065525 | 0.00065739 | 0.00065952 | 0.00066166 | 0.0006638
| MDA023-24605266 | 745 | 745 | 0.0026656 | 0 | 0.0034327 | 0 | 0.0034671 | 0 | 2.1919e-05 | 1.7174e-06 | 0.0033451 | 0.003367 | 0.0033889 | 0.0034108 | 0.0034327 | 0.0034344 | 0.0034362 | 0.0034379 | 0.0034396 | 0.0034413 | 0.003443 | 0.0034447 | 0.0034465 | 0.0034482 | 0.0034499 | 0.0034516 | 0.0034533 | 0.0034551 | 0.0034568 | 0.0034585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA024-15412265 | 1323 | 1323 | 0.0102 | 0 | 0.012548 | 0 | 0.012547 | 0 | 6.7081e-05 | -7.81e-08 | 0.01228 | 0.012347 | 0.012414 | 0.012481 | 0.012548 | 0.012548 | 0.012548 | 0.012548 | 0.012548 | 0.012548 | 0.012548 | 0.012548 | 0.012548 | 0.012548 | 0.012547 | 0.012547 | 0.012547 | 0.012547 | 0.012547 | 0.012547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA031-15412215 | 1897 | 1897 | 3.62e-06 | 0 | 4.75e-06 | 0 | 4.72e-06 | 0 | 3.2286e-08 | -1.5e-09 | 4.6209e-06 | 4.6531e-06 | 4.6854e-06 | 4.7177e-06 | 4.75e-06 | 4.7485e-06 | 4.747e-06 | 4.7455e-06 | 4.744e-06 | 4.7425e-06 | 4.741e-06 | 4.7395e-06 | 4.738e-06 | 4.7365e-06 | 4.735e-06 | 4.7335e-06 | 4.732e-06 | 4.7305e-06 | 4.729e-06 | 4.7275e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA032-15412191 | 2138 | 2138 | 0.00040651 | 0 | 0.00046095 | 0 | 0.00043456 | 0 | 1.5555e-06 | -1.3197e-06 | 0.00045473 | 0.00045629 | 0.00045784 | 0.0004594 | 0.00046095 | 0.00045963 | 0.00045831 | 0.00045699 | 0.00045567 | 0.00045435 | 0.00045303 | 0.00045171 | 0.00045039 | 0.00044907 | 0.00044775 | 0.00044643 | 0.00044512 | 0.0004438 | 0.00044248 | 0.00044116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA033-15412154 | 1246 | 1246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA034-15433030 | 1771 | 1771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN011-196478975 | 5616 | 1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN011-24613386 | 4265 | 4265 | 0.0004542 | 0 | 0.0006427 | 0 | 0.00068241 | 0 | 5.3858e-06 | 1.9857e-06 | 0.00062116 | 0.00062654 | 0.00063193 | 0.00063731 | 0.0006427 | 0.00064468 | 0.00064667 | 0.00064866 | 0.00065064 | 0.00065263 | 0.00065461 | 0.0006566 | 0.00065858 | 0.00066057 | 0.00066256 | 0.00066454 | 0.00066653 | 0.00066851 | 0.0006705 | 0.00067249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN012-196479104 | 2717 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN012-24607519 | 102 | 102 | 0.013153 | 0 | 0.018618 | 0 | 0.018477 | 0 | 0.00015616 | -7.0522e-06 | 0.017994 | 0.01815 | 0.018306 | 0.018462 | 0.018618 | 0.018611 | 0.018604 | 0.018597 | 0.01859 | 0.018583 | 0.018576 | 0.018569 | 0.018562 | 0.018555 | 0.018548 | 0.018541 | 0.018534 | 0.018527 | 0.01852 | 0.018512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN012-76356455 | 2330 | 2067 | 0 | 3.18e-05 | 0 | 4.23e-05 | 0 | 4.7e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3e-07 | 2.35e-07 | 4.11e-05 | 4.14e-05 | 4.17e-05 | 4.2e-05 | 4.23e-05 | 4.2535e-05 | 4.277e-05 | 4.3005e-05 | 4.324e-05 | 4.3475e-05 | 4.371e-05 | 4.3945e-05 | 4.418e-05 | 4.4415e-05 | 4.465e-05 | 4.4885e-05 | 4.512e-05 | 4.5355e-05 | 4.559e-05 | 4.5825e-05
| MLN012-84731779 | 263 | 263 | 0.018628 | 0 | 0.026088 | 0 | 0.027489 | 0 | 0.00021313 | 7.003e-05 | 0.025236 | 0.025449 | 0.025662 | 0.025875 | 0.026088 | 0.026158 | 0.026228 | 0.026298 | 0.026368 | 0.026438 | 0.026508 | 0.026578 | 0.026648 | 0.026718 | 0.026788 | 0.026858 | 0.026928 | 0.026998 | 0.027069 | 0.027139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN013-196479162 | 5029 | 5029 | 0.011611 | 0 | 0.016713 | 0 | 0.017804 | 0 | 0.00014577 | 5.4535e-05 | 0.01613 | 0.016276 | 0.016421 | 0.016567 | 0.016713 | 0.016768 | 0.016822 | 0.016877 | 0.016931 | 0.016986 | 0.01704 | 0.017095 | 0.017149 | 0.017204 | 0.017258 | 0.017313 | 0.017367 | 0.017422 | 0.017476 | 0.017531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN014-196479219 | 4643 | 4643 | 0.0060172 | 0 | 0.0078236 | 0 | 0.0085948 | 0 | 5.1612e-05 | 3.856e-05 | 0.0076171 | 0.0076688 | 0.0077204 | 0.007772 | 0.0078236 | 0.0078622 | 0.0079007 | 0.0079393 | 0.0079778 | 0.0080164 | 0.008055 | 0.0080935 | 0.0081321 | 0.0081706 | 0.0082092 | 0.0082478 | 0.0082863 | 0.0083249 | 0.0083634 | 0.008402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN021-196479276 | 5238 | 2008 | 0.0098323 | 0.0034698 | 0.0062417 | 0.0022499 | 0.0067749 | 0.0024567 | -0.00010259 | 2.6659e-05 | 0.0066521 | 0.0065495 | 0.0064469 | 0.0063443 | 0.0062417 | 0.0062684 | 0.006295 | 0.0063217 | 0.0063483 | 0.006375 | 0.0064017 | 0.0064283 | 0.006455 | 0.0064816 | 0.0065083 | 0.0065349 | 0.0065616 | 0.0065883 | 0.0066149 | 0.0066416 | -3.4856e-05 | 1.034e-05 | 0.0023893 | 0.0023545 | 0.0023196 | 0.0022848 | 0.0022499 | 0.0022602 | 0.0022706 | 0.0022809 | 0.0022913 | 0.0023016 | 0.0023119 | 0.0023223 | 0.0023326 | 0.002343 | 0.0023533 | 0.0023636 | 0.002374 | 0.0023843 | 0.0023947 | 0.002405
| MLN021-24600176 | 3230 | 3230 | 0.011381 | 0 | 0.014885 | 0 | 0.015476 | 0 | 0.00010013 | 2.9517e-05 | 0.014485 | 0.014585 | 0.014685 | 0.014785 | 0.014885 | 0.014915 | 0.014944 | 0.014974 | 0.015004 | 0.015033 | 0.015063 | 0.015092 | 0.015122 | 0.015151 | 0.015181 | 0.01521 | 0.01524 | 0.015269 | 0.015299 | 0.015328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN022-160532221 | 1385 | 1003 | 0.027741 | 0.030772 | 0.037462 | 0.043298 | 0.039187 | 0.045537 | 0.00027773 | 8.6264e-05 | 0.036351 | 0.036629 | 0.036906 | 0.037184 | 0.037462 | 0.037548 | 0.037634 | 0.037721 | 0.037807 | 0.037893 | 0.037979 | 0.038066 | 0.038152 | 0.038238 | 0.038325 | 0.038411 | 0.038497 | 0.038583 | 0.03867 | 0.038756 | 0.00035789 | 0.00011197 | 0.041866 | 0.042224 | 0.042582 | 0.04294 | 0.043298 | 0.04341 | 0.043522 | 0.043634 | 0.043746 | 0.043858 | 0.043969 | 0.044081 | 0.044193 | 0.044305 | 0.044417 | 0.044529 | 0.044641 | 0.044753 | 0.044865 | 0.044977
| MLN022-196479342 | 2140 | 755 | 0.0045915 | 0.02034 | 0.0059128 | 0.026274 | 0.0064825 | 0.028778 | 3.775e-05 | 2.8488e-05 | 0.0057618 | 0.0057995 | 0.0058373 | 0.005875 | 0.0059128 | 0.0059413 | 0.0059697 | 0.0059982 | 0.0060267 | 0.0060552 | 0.0060837 | 0.0061122 | 0.0061407 | 0.0061692 | 0.0061977 | 0.0062261 | 0.0062546 | 0.0062831 | 0.0063116 | 0.0063401 | 0.00016954 | 0.00012517 | 0.025596 | 0.025766 | 0.025935 | 0.026105 | 0.026274 | 0.026399 | 0.026524 | 0.02665 | 0.026775 | 0.0269 | 0.027025 | 0.02715 | 0.027276 | 0.027401 | 0.027526 | 0.027651 | 0.027776 | 0.027901 | 0.028027 | 0.028152
| MLN022-83935111 | 367 | 367 | 0.051316 | 0 | 0.07246 | 0 | 0.076256 | 0 | 0.00060412 | 0.00018979 | 0.070044 | 0.070648 | 0.071252 | 0.071856 | 0.07246 | 0.07265 | 0.07284 | 0.07303 | 0.073219 | 0.073409 | 0.073599 | 0.073789 | 0.073978 | 0.074168 | 0.074358 | 0.074548 | 0.074738 | 0.074927 | 0.075117 | 0.075307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN022-84622495 | 15 | 15 | 0.013332 | 0 | 0.017683 | 0 | 0.018302 | 0 | 0.0001243 | 3.0951e-05 | 0.017185 | 0.01731 | 0.017434 | 0.017558 | 0.017683 | 0.017714 | 0.017745 | 0.017776 | 0.017806 | 0.017837 | 0.017868 | 0.017899 | 0.01793 | 0.017961 | 0.017992 | 0.018023 | 0.018054 | 0.018085 | 0.018116 | 0.018147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN023-196479399 | 2957 | 2957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN024-196479455 | 1703 | 1703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN032-196479760 | 3858 | 3858 | 0.0081786 | 0 | 0.010676 | 0 | 0.011759 | 0 | 7.1356e-05 | 5.4138e-05 | 0.010391 | 0.010462 | 0.010533 | 0.010605 | 0.010676 | 0.01073 | 0.010784 | 0.010838 | 0.010893 | 0.010947 | 0.011001 | 0.011055 | 0.011109 | 0.011163 | 0.011217 | 0.011272 | 0.011326 | 0.01138 | 0.011434 | 0.011488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN033-196479827 | 3400 | 3400 | 0.018959 | 0 | 0.024893 | 0 | 0.026412 | 0 | 0.00016955 | 7.5933e-05 | 0.024215 | 0.024385 | 0.024554 | 0.024724 | 0.024893 | 0.024969 | 0.025045 | 0.025121 | 0.025197 | 0.025273 | 0.025349 | 0.025425 | 0.025501 | 0.025577 | 0.025653 | 0.025729 | 0.025804 | 0.02588 | 0.025956 | 0.026032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA013-15432110 | 651 | 2 | 0 | 1.02e-06 | 0 | 1.02e-06 | 0 | 1.02e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06 | 1.02e-06
| MNA013-15432136 | 649 | 649 | 0.0029689 | 0 | 0.0036296 | 0 | 0.0043183 | 0 | 1.8878e-05 | 3.4437e-05 | 0.0035541 | 0.003573 | 0.0035918 | 0.0036107 | 0.0036296 | 0.003664 | 0.0036985 | 0.0037329 | 0.0037673 | 0.0038018 | 0.0038362 | 0.0038707 | 0.0039051 | 0.0039395 | 0.003974 | 0.0040084 | 0.0040428 | 0.0040773 | 0.0041117 | 0.0041461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA014-138630585 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA014-15420920 | 1639 | 457 | 0.0084975 | 0.0012613 | 0.010707 | 0.0016663 | 0.012308 | 0.0020102 | 6.3133e-05 | 8.0066e-05 | 0.010455 | 0.010518 | 0.010581 | 0.010644 | 0.010707 | 0.010787 | 0.010867 | 0.010947 | 0.011027 | 0.011107 | 0.011188 | 0.011268 | 0.011348 | 0.011428 | 0.011508 | 0.011588 | 0.011668 | 0.011748 | 0.011828 | 0.011908 | 1.1572e-05 | 1.7194e-05 | 0.00162 | 0.0016316 | 0.0016432 | 0.0016548 | 0.0016663 | 0.0016835 | 0.0017007 | 0.0017179 | 0.0017351 | 0.0017523 | 0.0017695 | 0.0017867 | 0.0018039 | 0.0018211 | 0.0018383 | 0.0018555 | 0.0018727 | 0.0018899 | 0.0019071 | 0.0019242
| MNA014-157238172 | 20 | 20 | 2.67e-06 | 0 | 3.15e-06 | 0 | 4.11e-06 | 0 | 1.3714e-08 | 4.8e-08 | 3.0951e-06 | 3.1089e-06 | 3.1226e-06 | 3.1363e-06 | 3.15e-06 | 3.198e-06 | 3.246e-06 | 3.294e-06 | 3.342e-06 | 3.39e-06 | 3.438e-06 | 3.486e-06 | 3.534e-06 | 3.582e-06 | 3.63e-06 | 3.678e-06 | 3.726e-06 | 3.774e-06 | 3.822e-06 | 3.87e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA014-157238287 | 18 | 18 | 1.26e-05 | 0 | 1.49e-05 | 0 | 1.94e-05 | 0 | 6.5714e-08 | 2.25e-07 | 1.4637e-05 | 1.4703e-05 | 1.4769e-05 | 1.4834e-05 | 1.49e-05 | 1.5125e-05 | 1.535e-05 | 1.5575e-05 | 1.58e-05 | 1.6025e-05 | 1.625e-05 | 1.6475e-05 | 1.67e-05 | 1.6925e-05 | 1.715e-05 | 1.7375e-05 | 1.76e-05 | 1.7825e-05 | 1.805e-05 | 1.8275e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA014-157238460 | 21 | 21 | 0.00018787 | 0 | 0.00022676 | 0 | 0.00027166 | 0 | 1.1112e-06 | 2.245e-06 | 0.00022231 | 0.00022342 | 0.00022454 | 0.00022565 | 0.00022676 | 0.000229 | 0.00023125 | 0.00023349 | 0.00023574 | 0.00023798 | 0.00024023 | 0.00024247 | 0.00024472 | 0.00024696 | 0.00024921 | 0.00025145 | 0.0002537 | 0.00025594 | 0.00025819 | 0.00026043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA014-163873875 | 24 | 24 | 1.91e-05 | 0 | 2.56e-05 | 0 | 3.18e-05 | 0 | 1.8571e-07 | 3.1e-07 | 2.4857e-05 | 2.5043e-05 | 2.5229e-05 | 2.5414e-05 | 2.56e-05 | 2.591e-05 | 2.622e-05 | 2.653e-05 | 2.684e-05 | 2.715e-05 | 2.746e-05 | 2.777e-05 | 2.808e-05 | 2.839e-05 | 2.87e-05 | 2.901e-05 | 2.932e-05 | 2.963e-05 | 2.994e-05 | 3.025e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA014-164469721 | 6 | 6 | 2.85e-06 | 0 | 3.37e-06 | 0 | 4.39e-06 | 0 | 1.4857e-08 | 5.1e-08 | 3.3106e-06 | 3.3254e-06 | 3.3403e-06 | 3.3551e-06 | 3.37e-06 | 3.421e-06 | 3.472e-06 | 3.523e-06 | 3.574e-06 | 3.625e-06 | 3.676e-06 | 3.727e-06 | 3.778e-06 | 3.829e-06 | 3.88e-06 | 3.931e-06 | 3.982e-06 | 4.033e-06 | 4.084e-06 | 4.135e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA014-167870808 | 9 | 9 | 1.33e-05 | 0 | 1.78e-05 | 0 | 2.22e-05 | 0 | 1.2857e-07 | 2.2e-07 | 1.7286e-05 | 1.7414e-05 | 1.7543e-05 | 1.7671e-05 | 1.78e-05 | 1.802e-05 | 1.824e-05 | 1.846e-05 | 1.868e-05 | 1.89e-05 | 1.912e-05 | 1.934e-05 | 1.956e-05 | 1.978e-05 | 2e-05 | 2.022e-05 | 2.044e-05 | 2.066e-05 | 2.088e-05 | 2.11e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA014-184029858 | 908 | 902 | 0.0079063 | 2.31e-06 | 0.0094612 | 2.75e-06 | 0.011094 | 3.54e-06 | 4.4427e-05 | 8.1621e-05 | 0.0092835 | 0.0093279 | 0.0093724 | 0.0094168 | 0.0094612 | 0.0095428 | 0.0096244 | 0.0097061 | 0.0097877 | 0.0098693 | 0.0099509 | 0.010033 | 0.010114 | 0.010196 | 0.010277 | 0.010359 | 0.010441 | 0.010522 | 0.010604 | 0.010686 | 1.2571e-08 | 3.95e-08 | 2.6997e-06 | 2.7123e-06 | 2.7249e-06 | 2.7374e-06 | 2.75e-06 | 2.7895e-06 | 2.829e-06 | 2.8685e-06 | 2.908e-06 | 2.9475e-06 | 2.987e-06 | 3.0265e-06 | 3.066e-06 | 3.1055e-06 | 3.145e-06 | 3.1845e-06 | 3.224e-06 | 3.2635e-06 | 3.303e-06 | 3.3425e-06
| MNA014-187105725 | 937 | 29 | 3.37e-06 | 2.37e-06 | 4.22e-06 | 2.96e-06 | 5.18e-06 | 3.63e-06 | 2.4286e-08 | 4.8e-08 | 4.1229e-06 | 4.1471e-06 | 4.1714e-06 | 4.1957e-06 | 4.22e-06 | 4.268e-06 | 4.316e-06 | 4.364e-06 | 4.412e-06 | 4.46e-06 | 4.508e-06 | 4.556e-06 | 4.604e-06 | 4.652e-06 | 4.7e-06 | 4.748e-06 | 4.796e-06 | 4.844e-06 | 4.892e-06 | 4.94e-06 | 1.6857e-08 | 3.35e-08 | 2.8926e-06 | 2.9094e-06 | 2.9263e-06 | 2.9431e-06 | 2.96e-06 | 2.9935e-06 | 3.027e-06 | 3.0605e-06 | 3.094e-06 | 3.1275e-06 | 3.161e-06 | 3.1945e-06 | 3.228e-06 | 3.2615e-06 | 3.295e-06 | 3.3285e-06 | 3.362e-06 | 3.3955e-06 | 3.429e-06 | 3.4625e-06
| MNA014-203082790 | 186 | 137 | 0.0027255 | 2.69e-05 | 0.0034099 | 3.37e-05 | 0.0040123 | 4.16e-05 | 1.9556e-05 | 3.0119e-05 | 0.0033317 | 0.0033513 | 0.0033708 | 0.0033904 | 0.0034099 | 0.0034401 | 0.0034702 | 0.0035003 | 0.0035304 | 0.0035605 | 0.0035906 | 0.0036208 | 0.0036509 | 0.003681 | 0.0037111 | 0.0037412 | 0.0037714 | 0.0038015 | 0.0038316 | 0.0038617 | 1.9429e-07 | 3.95e-07 | 3.2923e-05 | 3.3117e-05 | 3.3311e-05 | 3.3506e-05 | 3.37e-05 | 3.4095e-05 | 3.449e-05 | 3.4885e-05 | 3.528e-05 | 3.5675e-05 | 3.607e-05 | 3.6465e-05 | 3.686e-05 | 3.7255e-05 | 3.765e-05 | 3.8045e-05 | 3.844e-05 | 3.8835e-05 | 3.923e-05 | 3.9625e-05
| MNA021-15421016 | 1826 | 244 | 0.013758 | 0.00023662 | 0.01715 | 0.00029728 | 0.018643 | 0.00029769 | 9.6901e-05 | 7.469e-05 | 0.016762 | 0.016859 | 0.016956 | 0.017053 | 0.01715 | 0.017224 | 0.017299 | 0.017374 | 0.017448 | 0.017523 | 0.017598 | 0.017672 | 0.017747 | 0.017822 | 0.017896 | 0.017971 | 0.018046 | 0.018121 | 0.018195 | 0.01827 | 1.7331e-06 | 2.03e-08 | 0.00029035 | 0.00029209 | 0.00029382 | 0.00029555 | 0.00029728 | 0.00029731 | 0.00029733 | 0.00029735 | 0.00029737 | 0.00029739 | 0.00029741 | 0.00029743 | 0.00029745 | 0.00029747 | 0.00029749 | 0.00029751 | 0.00029753 | 0.00029755 | 0.00029757 | 0.00029759
| MNA021-164301884 | 1582 | 1582 | 0.01326 | 0 | 0.016211 | 0 | 0.018805 | 0 | 8.4319e-05 | 0.00012971 | 0.015873 | 0.015958 | 0.016042 | 0.016126 | 0.016211 | 0.01634 | 0.01647 | 0.0166 | 0.01673 | 0.016859 | 0.016989 | 0.017119 | 0.017248 | 0.017378 | 0.017508 | 0.017637 | 0.017767 | 0.017897 | 0.018027 | 0.018156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA022-15421040 | 2163 | 2163 | 0.00037475 | 0 | 0.00045955 | 0 | 0.00057604 | 0 | 2.4228e-06 | 5.8249e-06 | 0.00044985 | 0.00045228 | 0.0004547 | 0.00045712 | 0.00045955 | 0.00046537 | 0.0004712 | 0.00047702 | 0.00048285 | 0.00048867 | 0.0004945 | 0.00050032 | 0.00050615 | 0.00051197 | 0.00051779 | 0.00052362 | 0.00052944 | 0.00053527 | 0.00054109 | 0.00054692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA024-15421140 | 2562 | 2555 | 0.017159 | 2.98e-06 | 0.020599 | 3.66e-06 | 0.023379 | 4.63e-06 | 9.8272e-05 | 0.000139 | 0.020206 | 0.020304 | 0.020402 | 0.020501 | 0.020599 | 0.020738 | 0.020877 | 0.021016 | 0.021155 | 0.021294 | 0.021433 | 0.021572 | 0.021711 | 0.02185 | 0.021989 | 0.022128 | 0.022267 | 0.022406 | 0.022545 | 0.022684 | 1.9429e-08 | 4.85e-08 | 3.5823e-06 | 3.6017e-06 | 3.6211e-06 | 3.6406e-06 | 3.66e-06 | 3.7085e-06 | 3.757e-06 | 3.8055e-06 | 3.854e-06 | 3.9025e-06 | 3.951e-06 | 3.9995e-06 | 4.048e-06 | 4.0965e-06 | 4.145e-06 | 4.1935e-06 | 4.242e-06 | 4.2905e-06 | 4.339e-06 | 4.3875e-06
| MNA024-15421151 | 7 | 7 | 2.98e-06 | 0 | 3.66e-06 | 0 | 4.63e-06 | 0 | 1.9429e-08 | 4.85e-08 | 3.5823e-06 | 3.6017e-06 | 3.6211e-06 | 3.6406e-06 | 3.66e-06 | 3.7085e-06 | 3.757e-06 | 3.8055e-06 | 3.854e-06 | 3.9025e-06 | 3.951e-06 | 3.9995e-06 | 4.048e-06 | 4.0965e-06 | 4.145e-06 | 4.1935e-06 | 4.242e-06 | 4.2905e-06 | 4.339e-06 | 4.3875e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA034-15421279 | 1852 | 501 | 0.016642 | 0.0019196 | 0.019737 | 0.0023577 | 0.02222 | 0.0027463 | 8.843e-05 | 0.00012416 | 0.019383 | 0.019472 | 0.01956 | 0.019649 | 0.019737 | 0.019861 | 0.019985 | 0.02011 | 0.020234 | 0.020358 | 0.020482 | 0.020606 | 0.02073 | 0.020855 | 0.020979 | 0.021103 | 0.021227 | 0.021351 | 0.021475 | 0.0216 | 1.2516e-05 | 1.9432e-05 | 0.0023076 | 0.0023201 | 0.0023326 | 0.0023452 | 0.0023577 | 0.0023771 | 0.0023965 | 0.002416 | 0.0024354 | 0.0024548 | 0.0024743 | 0.0024937 | 0.0025131 | 0.0025326 | 0.002552 | 0.0025714 | 0.0025909 | 0.0026103 | 0.0026297 | 0.0026491
| MNA034-157168509 | 28 | 28 | 0.003448 | 0 | 0.0044892 | 0 | 0.0052225 | 0 | 2.9748e-05 | 3.6666e-05 | 0.0043702 | 0.0044 | 0.0044297 | 0.0044595 | 0.0044892 | 0.0045259 | 0.0045625 | 0.0045992 | 0.0046359 | 0.0046725 | 0.0047092 | 0.0047459 | 0.0047825 | 0.0048192 | 0.0048559 | 0.0048925 | 0.0049292 | 0.0049659 | 0.0050025 | 0.0050392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA034-157168656 | 39 | 39 | 0.002896 | 0 | 0.003841 | 0 | 0.0043961 | 0 | 2.7e-05 | 2.7754e-05 | 0.003733 | 0.00376 | 0.003787 | 0.003814 | 0.003841 | 0.0038687 | 0.0038965 | 0.0039242 | 0.003952 | 0.0039797 | 0.0040075 | 0.0040353 | 0.004063 | 0.0040908 | 0.0041185 | 0.0041463 | 0.004174 | 0.0042018 | 0.0042295 | 0.0042573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA034-157168875 | 27 | 27 | 0.00035024 | 0 | 0.0004629 | 0 | 0.00050738 | 0 | 3.219e-06 | 2.2237e-06 | 0.00045002 | 0.00045324 | 0.00045646 | 0.00045968 | 0.0004629 | 0.00046512 | 0.00046735 | 0.00046957 | 0.0004718 | 0.00047402 | 0.00047624 | 0.00047847 | 0.00048069 | 0.00048291 | 0.00048514 | 0.00048736 | 0.00048959 | 0.00049181 | 0.00049403 | 0.00049626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA034-175612351 | 8 | 8 | 9.24e-06 | 0 | 1.17e-05 | 0 | 1.46e-05 | 0 | 7.0286e-08 | 1.45e-07 | 1.1419e-05 | 1.1489e-05 | 1.1559e-05 | 1.163e-05 | 1.17e-05 | 1.1845e-05 | 1.199e-05 | 1.2135e-05 | 1.228e-05 | 1.2425e-05 | 1.257e-05 | 1.2715e-05 | 1.286e-05 | 1.3005e-05 | 1.315e-05 | 1.3295e-05 | 1.344e-05 | 1.3585e-05 | 1.373e-05 | 1.3875e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA034-181657157 | 1351 | 520 | 0.015419 | 0.0012172 | 0.018866 | 0.0015788 | 0.020172 | 0.0018771 | 9.8476e-05 | 6.5309e-05 | 0.018472 | 0.01857 | 0.018669 | 0.018767 | 0.018866 | 0.018931 | 0.018996 | 0.019062 | 0.019127 | 0.019192 | 0.019258 | 0.019323 | 0.019388 | 0.019454 | 0.019519 | 0.019584 | 0.01965 | 0.019715 | 0.01978 | 0.019845 | 1.0332e-05 | 1.4915e-05 | 0.0015375 | 0.0015478 | 0.0015581 | 0.0015685 | 0.0015788 | 0.0015937 | 0.0016086 | 0.0016235 | 0.0016385 | 0.0016534 | 0.0016683 | 0.0016832 | 0.0016981 | 0.001713 | 0.0017279 | 0.0017429 | 0.0017578 | 0.0017727 | 0.0017876 | 0.0018025
| MNA034-24605112 | 784 | 729 | 0.03475 | 0.0019009 | 0.043959 | 0.0025034 | 0.048601 | 0.0029829 | 0.00026311 | 0.00023213 | 0.042906 | 0.043169 | 0.043433 | 0.043696 | 0.043959 | 0.044191 | 0.044423 | 0.044655 | 0.044887 | 0.045119 | 0.045352 | 0.045584 | 0.045816 | 0.046048 | 0.04628 | 0.046512 | 0.046744 | 0.046976 | 0.047209 | 0.047441 | 1.7216e-05 | 2.3973e-05 | 0.0024346 | 0.0024518 | 0.002469 | 0.0024862 | 0.0025034 | 0.0025274 | 0.0025514 | 0.0025753 | 0.0025993 | 0.0026233 | 0.0026473 | 0.0026712 | 0.0026952 | 0.0027192 | 0.0027432 | 0.0027671 | 0.0027911 | 0.0028151 | 0.002839 | 0.002863
| MRO002-15420142 | 2 | 1 | 0.00015072 | 0 | 0.00015615 | 0 | 0.00015341 | 0 | 1.5509e-07 | -1.37e-07 | 0.00015553 | 0.00015569 | 0.00015584 | 0.000156 | 0.00015615 | 0.00015602 | 0.00015588 | 0.00015574 | 0.0001556 | 0.00015547 | 0.00015533 | 0.00015519 | 0.00015506 | 0.00015492 | 0.00015478 | 0.00015465 | 0.00015451 | 0.00015437 | 0.00015423 | 0.0001541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO002-15420153 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO002-15420179 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO004-15420205 | 1865 | 1865 | 0.028022 | 0 | 0.038447 | 0 | 0.038829 | 0 | 0.00029787 | 1.9082e-05 | 0.037256 | 0.037553 | 0.037851 | 0.038149 | 0.038447 | 0.038466 | 0.038485 | 0.038504 | 0.038523 | 0.038543 | 0.038562 | 0.038581 | 0.0386 | 0.038619 | 0.038638 | 0.038657 | 0.038676 | 0.038695 | 0.038714 | 0.038733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-144335638 | 40 | 40 | 0.0028642 | 0 | 0.0042618 | 0 | 0.0041113 | 0 | 3.9931e-05 | -7.5255e-06 | 0.004102 | 0.004142 | 0.0041819 | 0.0042218 | 0.0042618 | 0.0042542 | 0.0042467 | 0.0042392 | 0.0042317 | 0.0042241 | 0.0042166 | 0.0042091 | 0.0042016 | 0.004194 | 0.0041865 | 0.004179 | 0.0041715 | 0.0041639 | 0.0041564 | 0.0041489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-144335959 | 44 | 44 | 8.62e-05 | 0 | 0.00014011 | 0 | 0.00014627 | 0 | 1.5403e-06 | 3.078e-07 | 0.00013395 | 0.00013549 | 0.00013703 | 0.00013857 | 0.00014011 | 0.00014042 | 0.00014073 | 0.00014103 | 0.00014134 | 0.00014165 | 0.00014196 | 0.00014227 | 0.00014257 | 0.00014288 | 0.00014319 | 0.0001435 | 0.0001438 | 0.00014411 | 0.00014442 | 0.00014473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-144336040 | 12 | 12 | 0.0031563 | 0 | 0.0041013 | 0 | 0.004302 | 0 | 2.6999e-05 | 1.0039e-05 | 0.0039933 | 0.0040203 | 0.0040473 | 0.0040743 | 0.0041013 | 0.0041113 | 0.0041213 | 0.0041314 | 0.0041414 | 0.0041515 | 0.0041615 | 0.0041715 | 0.0041816 | 0.0041916 | 0.0042017 | 0.0042117 | 0.0042217 | 0.0042318 | 0.0042418 | 0.0042519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-144336270 | 16 | 16 | 0.00055955 | 0 | 0.00076951 | 0 | 0.00077435 | 0 | 5.9988e-06 | 2.4205e-07 | 0.00074552 | 0.00075152 | 0.00075751 | 0.00076351 | 0.00076951 | 0.00076975 | 0.00077 | 0.00077024 | 0.00077048 | 0.00077072 | 0.00077096 | 0.00077121 | 0.00077145 | 0.00077169 | 0.00077193 | 0.00077217 | 0.00077242 | 0.00077266 | 0.0007729 | 0.00077314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-15420092 | 2181 | 442 | 0.024064 | 0.0044983 | 0.032743 | 0.0065406 | 0.033118 | 0.0066573 | 0.00024797 | 1.8724e-05 | 0.031751 | 0.031999 | 0.032247 | 0.032495 | 0.032743 | 0.032762 | 0.032781 | 0.032799 | 0.032818 | 0.032837 | 0.032856 | 0.032874 | 0.032893 | 0.032912 | 0.03293 | 0.032949 | 0.032968 | 0.032987 | 0.033005 | 0.033024 | 5.8353e-05 | 5.8351e-06 | 0.0063072 | 0.0063656 | 0.0064239 | 0.0064823 | 0.0065406 | 0.0065465 | 0.0065523 | 0.0065581 | 0.006564 | 0.0065698 | 0.0065756 | 0.0065815 | 0.0065873 | 0.0065931 | 0.006599 | 0.0066048 | 0.0066106 | 0.0066165 | 0.0066223 | 0.0066281
| MRO005-155391758 | 40 | 40 | 0.0030195 | 0 | 0.004242 | 0 | 0.0044402 | 0 | 3.4927e-05 | 9.9121e-06 | 0.0041023 | 0.0041372 | 0.0041721 | 0.004207 | 0.004242 | 0.0042519 | 0.0042618 | 0.0042717 | 0.0042816 | 0.0042915 | 0.0043014 | 0.0043114 | 0.0043213 | 0.0043312 | 0.0043411 | 0.004351 | 0.0043609 | 0.0043708 | 0.0043807 | 0.0043906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-155391898 | 16 | 16 | 0.0057722 | 0 | 0.0083138 | 0 | 0.0085716 | 0 | 7.2618e-05 | 1.2889e-05 | 0.0080233 | 0.008096 | 0.0081686 | 0.0082412 | 0.0083138 | 0.0083267 | 0.0083396 | 0.0083525 | 0.0083654 | 0.0083783 | 0.0083911 | 0.008404 | 0.0084169 | 0.0084298 | 0.0084427 | 0.0084556 | 0.0084685 | 0.0084814 | 0.0084943 | 0.0085071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-155391999 | 42 | 42 | 0.006021 | 0 | 0.0082905 | 0 | 0.008696 | 0 | 6.4842e-05 | 2.0278e-05 | 0.0080311 | 0.0080959 | 0.0081608 | 0.0082256 | 0.0082905 | 0.0083107 | 0.008331 | 0.0083513 | 0.0083716 | 0.0083918 | 0.0084121 | 0.0084324 | 0.0084527 | 0.008473 | 0.0084932 | 0.0085135 | 0.0085338 | 0.0085541 | 0.0085743 | 0.0085946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-155423773 | 46 | 46 | 0.0065449 | 0 | 0.0084494 | 0 | 0.0087324 | 0 | 5.4413e-05 | 1.415e-05 | 0.0082317 | 0.0082861 | 0.0083406 | 0.008395 | 0.0084494 | 0.0084635 | 0.0084777 | 0.0084918 | 0.008506 | 0.0085201 | 0.0085343 | 0.0085484 | 0.0085626 | 0.0085767 | 0.0085909 | 0.008605 | 0.0086192 | 0.0086333 | 0.0086475 | 0.0086616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-155505168 | 31 | 31 | 0.0038166 | 0 | 0.0056969 | 0 | 0.0057917 | 0 | 5.3722e-05 | 4.7407e-06 | 0.005482 | 0.0055357 | 0.0055894 | 0.0056431 | 0.0056969 | 0.0057016 | 0.0057063 | 0.0057111 | 0.0057158 | 0.0057206 | 0.0057253 | 0.00573 | 0.0057348 | 0.0057395 | 0.0057443 | 0.005749 | 0.0057537 | 0.0057585 | 0.0057632 | 0.005768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-155838268 | 17 | 17 | 0.0023073 | 0 | 0.0034565 | 0 | 0.0035921 | 0 | 3.2834e-05 | 6.7791e-06 | 0.0033251 | 0.003358 | 0.0033908 | 0.0034236 | 0.0034565 | 0.0034633 | 0.00347 | 0.0034768 | 0.0034836 | 0.0034904 | 0.0034971 | 0.0035039 | 0.0035107 | 0.0035175 | 0.0035243 | 0.003531 | 0.0035378 | 0.0035446 | 0.0035514 | 0.0035582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-163160444 | 6 | 6 | 0.0030272 | 0 | 0.0046269 | 0 | 0.0045532 | 0 | 4.5705e-05 | -3.6834e-06 | 0.0044441 | 0.0044898 | 0.0045355 | 0.0045812 | 0.0046269 | 0.0046232 | 0.0046195 | 0.0046159 | 0.0046122 | 0.0046085 | 0.0046048 | 0.0046011 | 0.0045974 | 0.0045938 | 0.0045901 | 0.0045864 | 0.0045827 | 0.004579 | 0.0045753 | 0.0045717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-163160605 | 8 | 8 | 0.0039092 | 0 | 0.0056517 | 0 | 0.0059517 | 0 | 4.9785e-05 | 1.4996e-05 | 0.0054526 | 0.0055024 | 0.0055522 | 0.0056019 | 0.0056517 | 0.0056667 | 0.0056817 | 0.0056967 | 0.0057117 | 0.0057267 | 0.0057417 | 0.0057567 | 0.0057717 | 0.0057867 | 0.0058017 | 0.0058167 | 0.0058317 | 0.0058467 | 0.0058617 | 0.0058767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-163160879 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-163161051 | 7 | 7 | 0.0017417 | 0 | 0.0025982 | 0 | 0.0027642 | 0 | 2.4472e-05 | 8.2992e-06 | 0.0025004 | 0.0025248 | 0.0025493 | 0.0025738 | 0.0025982 | 0.0026065 | 0.0026148 | 0.0026231 | 0.0026314 | 0.0026397 | 0.002648 | 0.0026563 | 0.0026646 | 0.0026729 | 0.0026812 | 0.0026895 | 0.0026978 | 0.0027061 | 0.0027144 | 0.0027227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-172349913 | 12 | 12 | 0.0020934 | 0 | 0.0029191 | 0 | 0.0031926 | 0 | 2.359e-05 | 1.3677e-05 | 0.0028247 | 0.0028483 | 0.0028719 | 0.0028955 | 0.0029191 | 0.0029328 | 0.0029465 | 0.0029601 | 0.0029738 | 0.0029875 | 0.0030012 | 0.0030148 | 0.0030285 | 0.0030422 | 0.0030559 | 0.0030696 | 0.0030832 | 0.0030969 | 0.0031106 | 0.0031243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-24606286 | 313 | 261 | 0.023878 | 0.0028036 | 0.03119 | 0.0037282 | 0.032128 | 0.003852 | 0.00020892 | 4.6936e-05 | 0.030354 | 0.030563 | 0.030772 | 0.030981 | 0.03119 | 0.031236 | 0.031283 | 0.03133 | 0.031377 | 0.031424 | 0.031471 | 0.031518 | 0.031565 | 0.031612 | 0.031659 | 0.031706 | 0.031753 | 0.0318 | 0.031847 | 0.031894 | 2.6418e-05 | 6.1892e-06 | 0.0036226 | 0.003649 | 0.0036754 | 0.0037018 | 0.0037282 | 0.0037344 | 0.0037406 | 0.0037468 | 0.003753 | 0.0037592 | 0.0037654 | 0.0037716 | 0.0037778 | 0.003784 | 0.0037901 | 0.0037963 | 0.0038025 | 0.0038087 | 0.0038149 | 0.0038211
| MRO005-24606314 | 1150 | 720 | 0.0069954 | 0.0073912 | 0.0092616 | 0.010224 | 0.0095707 | 0.01061 | 6.4749e-05 | 1.5458e-05 | 0.0090026 | 0.0090673 | 0.0091321 | 0.0091968 | 0.0092616 | 0.009277 | 0.0092925 | 0.009308 | 0.0093234 | 0.0093389 | 0.0093543 | 0.0093698 | 0.0093853 | 0.0094007 | 0.0094162 | 0.0094316 | 0.0094471 | 0.0094625 | 0.009478 | 0.0094935 | 8.0929e-05 | 1.9305e-05 | 0.0099 | 0.0099809 | 0.010062 | 0.010143 | 0.010224 | 0.010243 | 0.010262 | 0.010282 | 0.010301 | 0.01032 | 0.01034 | 0.010359 | 0.010378 | 0.010397 | 0.010417 | 0.010436 | 0.010455 | 0.010475 | 0.010494 | 0.010513
| MRO005-24606328 | 547 | 121 | 0.0071387 | 0.0036989 | 0.0095238 | 0.0054569 | 0.010139 | 0.006003 | 6.8145e-05 | 3.0774e-05 | 0.0092512 | 0.0093193 | 0.0093875 | 0.0094556 | 0.0095238 | 0.0095545 | 0.0095853 | 0.0096161 | 0.0096469 | 0.0096776 | 0.0097084 | 0.0097392 | 0.00977 | 0.0098007 | 0.0098315 | 0.0098623 | 0.0098931 | 0.0099238 | 0.0099546 | 0.0099854 | 5.0229e-05 | 2.7306e-05 | 0.005256 | 0.0053062 | 0.0053564 | 0.0054067 | 0.0054569 | 0.0054842 | 0.0055115 | 0.0055388 | 0.0055661 | 0.0055934 | 0.0056207 | 0.005648 | 0.0056753 | 0.0057026 | 0.00573 | 0.0057573 | 0.0057846 | 0.0058119 | 0.0058392 | 0.0058665
| MRO005-24606858 | 353 | 256 | 0.02434 | 0.0068218 | 0.033473 | 0.0104 | 0.034336 | 0.010826 | 0.00026094 | 4.3147e-05 | 0.032429 | 0.03269 | 0.032951 | 0.033212 | 0.033473 | 0.033516 | 0.033559 | 0.033602 | 0.033645 | 0.033688 | 0.033732 | 0.033775 | 0.033818 | 0.033861 | 0.033904 | 0.033947 | 0.03399 | 0.034034 | 0.034077 | 0.03412 | 0.00010223 | 2.1314e-05 | 0.009991 | 0.010093 | 0.010195 | 0.010298 | 0.0104 | 0.010421 | 0.010443 | 0.010464 | 0.010485 | 0.010506 | 0.010528 | 0.010549 | 0.01057 | 0.010592 | 0.010613 | 0.010634 | 0.010656 | 0.010677 | 0.010698 | 0.01072
| MRO005-73766637 | 38 | 38 | 0.0068016 | 0 | 0.0093466 | 0 | 0.0097756 | 0 | 7.2714e-05 | 2.145e-05 | 0.0090557 | 0.0091284 | 0.0092012 | 0.0092739 | 0.0093466 | 0.009368 | 0.0093895 | 0.0094109 | 0.0094324 | 0.0094538 | 0.0094753 | 0.0094967 | 0.0095182 | 0.0095396 | 0.0095611 | 0.0095825 | 0.009604 | 0.0096254 | 0.0096469 | 0.0096683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO006-15420268 | 1093 | 1093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO007-122640081 | 533 | 470 | 0.018575 | 0.010179 | 0.023471 | 0.013577 | 0.02466 | 0.014433 | 0.00013988 | 5.946e-05 | 0.022911 | 0.023051 | 0.023191 | 0.023331 | 0.023471 | 0.02353 | 0.02359 | 0.023649 | 0.023709 | 0.023768 | 0.023828 | 0.023887 | 0.023946 | 0.024006 | 0.024065 | 0.024125 | 0.024184 | 0.024244 | 0.024303 | 0.024363 | 9.7089e-05 | 4.2759e-05 | 0.013189 | 0.013286 | 0.013383 | 0.01348 | 0.013577 | 0.01362 | 0.013663 | 0.013706 | 0.013748 | 0.013791 | 0.013834 | 0.013877 | 0.013919 | 0.013962 | 0.014005 | 0.014048 | 0.01409 | 0.014133 | 0.014176 | 0.014219
| MRO007-129258735 | 24 | 24 | 0.0098138 | 0 | 0.013634 | 0 | 0.014773 | 0 | 0.00010914 | 5.6945e-05 | 0.013197 | 0.013306 | 0.013415 | 0.013525 | 0.013634 | 0.013691 | 0.013748 | 0.013805 | 0.013862 | 0.013918 | 0.013975 | 0.014032 | 0.014089 | 0.014146 | 0.014203 | 0.01426 | 0.014317 | 0.014374 | 0.014431 | 0.014488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO007-15420070 | 1888 | 691 | 0.011933 | 0.0070991 | 0.015901 | 0.01025 | 0.015738 | 0.01017 | 0.00011339 | -8.165e-06 | 0.015448 | 0.015561 | 0.015675 | 0.015788 | 0.015901 | 0.015893 | 0.015885 | 0.015877 | 0.015869 | 0.015861 | 0.015852 | 0.015844 | 0.015836 | 0.015828 | 0.01582 | 0.015812 | 0.015803 | 0.015795 | 0.015787 | 0.015779 | 9.0028e-05 | -4.0228e-06 | 0.0098899 | 0.0099799 | 0.01007 | 0.01016 | 0.01025 | 0.010246 | 0.010242 | 0.010238 | 0.010234 | 0.01023 | 0.010226 | 0.010222 | 0.010218 | 0.010214 | 0.01021 | 0.010206 | 0.010202 | 0.010198 | 0.010194 | 0.01019
| MRO007-161151299 | 13 | 13 | 0.0067609 | 0 | 0.009789 | 0 | 0.0098151 | 0 | 8.6518e-05 | 1.303e-06 | 0.0094429 | 0.0095295 | 0.009616 | 0.0097025 | 0.009789 | 0.0097903 | 0.0097916 | 0.0097929 | 0.0097942 | 0.0097955 | 0.0097968 | 0.0097981 | 0.0097994 | 0.0098007 | 0.009802 | 0.0098034 | 0.0098047 | 0.009806 | 0.0098073 | 0.0098086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO007-24610986 | 618 | 407 | 0.011394 | 0.0067245 | 0.016769 | 0.010155 | 0.016572 | 0.010057 | 0.00015358 | -9.8456e-06 | 0.016155 | 0.016308 | 0.016462 | 0.016615 | 0.016769 | 0.016759 | 0.016749 | 0.016739 | 0.01673 | 0.01672 | 0.01671 | 0.0167 | 0.01669 | 0.01668 | 0.016671 | 0.016661 | 0.016651 | 0.016641 | 0.016631 | 0.016621 | 9.802e-05 | -4.9102e-06 | 0.0097631 | 0.0098611 | 0.0099592 | 0.010057 | 0.010155 | 0.01015 | 0.010145 | 0.01014 | 0.010136 | 0.010131 | 0.010126 | 0.010121 | 0.010116 | 0.010111 | 0.010106 | 0.010101 | 0.010096 | 0.010091 | 0.010086 | 0.010082
| MRO007-76446321 | 60 | 60 | 0.0056716 | 0 | 0.0080063 | 0 | 0.0080878 | 0 | 6.6708e-05 | 4.0732e-06 | 0.0077395 | 0.0078062 | 0.0078729 | 0.0079396 | 0.0080063 | 0.0080104 | 0.0080145 | 0.0080185 | 0.0080226 | 0.0080267 | 0.0080308 | 0.0080348 | 0.0080389 | 0.008043 | 0.0080471 | 0.0080511 | 0.0080552 | 0.0080593 | 0.0080633 | 0.0080674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO007-76446588 | 52 | 52 | 0.0021257 | 0 | 0.003162 | 0 | 0.0031722 | 0 | 2.961e-05 | 5.0775e-07 | 0.0030436 | 0.0030732 | 0.0031028 | 0.0031324 | 0.003162 | 0.0031626 | 0.0031631 | 0.0031636 | 0.0031641 | 0.0031646 | 0.0031651 | 0.0031656 | 0.0031661 | 0.0031666 | 0.0031671 | 0.0031676 | 0.0031681 | 0.0031686 | 0.0031692 | 0.0031697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO007-76547638 | 39 | 39 | 0.00435 | 0 | 0.0054998 | 0 | 0.0057828 | 0 | 3.2851e-05 | 1.415e-05 | 0.0053684 | 0.0054012 | 0.0054341 | 0.0054669 | 0.0054998 | 0.0055139 | 0.0055281 | 0.0055422 | 0.0055564 | 0.0055705 | 0.0055847 | 0.0055988 | 0.005613 | 0.0056271 | 0.0056413 | 0.0056554 | 0.0056696 | 0.0056837 | 0.0056979 | 0.005712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO007-76547903 | 37 | 37 | 2.29e-05 | 0 | 3.66e-05 | 0 | 3.73e-05 | 0 | 3.9143e-07 | 3.5e-08 | 3.5034e-05 | 3.5426e-05 | 3.5817e-05 | 3.6209e-05 | 3.66e-05 | 3.6635e-05 | 3.667e-05 | 3.6705e-05 | 3.674e-05 | 3.6775e-05 | 3.681e-05 | 3.6845e-05 | 3.688e-05 | 3.6915e-05 | 3.695e-05 | 3.6985e-05 | 3.702e-05 | 3.7055e-05 | 3.709e-05 | 3.7125e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO007-76548012 | 49 | 49 | 0.0029649 | 0 | 0.0042915 | 0 | 0.0043304 | 0 | 3.7904e-05 | 1.9456e-06 | 0.0041399 | 0.0041778 | 0.0042157 | 0.0042536 | 0.0042915 | 0.0042934 | 0.0042954 | 0.0042973 | 0.0042993 | 0.0043012 | 0.0043032 | 0.0043051 | 0.0043071 | 0.004309 | 0.004311 | 0.0043129 | 0.0043149 | 0.0043168 | 0.0043187 | 0.0043207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO008-129258570 | 21 | 21 | 0.0044159 | 0 | 0.0062587 | 0 | 0.0063261 | 0 | 5.2654e-05 | 3.3691e-06 | 0.0060481 | 0.0061008 | 0.0061534 | 0.0062061 | 0.0062587 | 0.0062621 | 0.0062655 | 0.0062688 | 0.0062722 | 0.0062756 | 0.006279 | 0.0062823 | 0.0062857 | 0.0062891 | 0.0062924 | 0.0062958 | 0.0062992 | 0.0063025 | 0.0063059 | 0.0063093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO008-137134221 | 19 | 19 | 0.00088354 | 0 | 0.0012039 | 0 | 0.0012014 | 0 | 9.1537e-06 | -1.2605e-07 | 0.0011673 | 0.0011765 | 0.0011856 | 0.0011948 | 0.0012039 | 0.0012038 | 0.0012037 | 0.0012035 | 0.0012034 | 0.0012033 | 0.0012032 | 0.001203 | 0.0012029 | 0.0012028 | 0.0012027 | 0.0012025 | 0.0012024 | 0.0012023 | 0.0012022 | 0.001202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO008-15411648 | 2858 | 1431 | 0.024645 | 0.0041976 | 0.03059 | 0.0061697 | 0.030604 | 0.0062837 | 0.00016985 | 6.884e-07 | 0.029911 | 0.030081 | 0.03025 | 0.03042 | 0.03059 | 0.030591 | 0.030591 | 0.030592 | 0.030593 | 0.030594 | 0.030594 | 0.030595 | 0.030596 | 0.030596 | 0.030597 | 0.030598 | 0.030598 | 0.030599 | 0.0306 | 0.0306 | 5.6344e-05 | 5.7033e-06 | 0.0059443 | 0.0060006 | 0.006057 | 0.0061133 | 0.0061697 | 0.0061754 | 0.0061811 | 0.0061868 | 0.0061925 | 0.0061982 | 0.0062039 | 0.0062096 | 0.0062153 | 0.006221 | 0.0062267 | 0.0062324 | 0.0062381 | 0.0062438 | 0.0062495 | 0.0062552
| MRO008-156506029 | 1386 | 979 | 0.022744 | 0.0088256 | 0.030817 | 0.012739 | 0.030462 | 0.01257 | 0.00023064 | -1.773e-05 | 0.029894 | 0.030125 | 0.030355 | 0.030586 | 0.030817 | 0.030799 | 0.030781 | 0.030764 | 0.030746 | 0.030728 | 0.03071 | 0.030693 | 0.030675 | 0.030657 | 0.030639 | 0.030622 | 0.030604 | 0.030586 | 0.030569 | 0.030551 | 0.00011182 | -8.4877e-06 | 0.012292 | 0.012404 | 0.012516 | 0.012628 | 0.012739 | 0.012731 | 0.012722 | 0.012714 | 0.012705 | 0.012697 | 0.012688 | 0.01268 | 0.012671 | 0.012663 | 0.012654 | 0.012646 | 0.012638 | 0.012629 | 0.012621 | 0.012612
| MRO008-161918307 | 41 | 41 | 0.0023885 | 0 | 0.0034593 | 0 | 0.0034745 | 0 | 3.0594e-05 | 7.572e-07 | 0.003337 | 0.0033676 | 0.0033982 | 0.0034287 | 0.0034593 | 0.0034601 | 0.0034609 | 0.0034616 | 0.0034624 | 0.0034631 | 0.0034639 | 0.0034646 | 0.0034654 | 0.0034662 | 0.0034669 | 0.0034677 | 0.0034684 | 0.0034692 | 0.0034699 | 0.0034707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO008-24606830 | 225 | 220 | 0.011127 | 2.26e-05 | 0.015935 | 3.71e-05 | 0.015727 | 3.65e-05 | 0.00013737 | -1.0427e-05 | 0.015386 | 0.015523 | 0.015661 | 0.015798 | 0.015935 | 0.015925 | 0.015914 | 0.015904 | 0.015894 | 0.015883 | 0.015873 | 0.015862 | 0.015852 | 0.015841 | 0.015831 | 0.015821 | 0.01581 | 0.0158 | 0.015789 | 0.015779 | 4.1429e-07 | -3e-08 | 3.5443e-05 | 3.5857e-05 | 3.6271e-05 | 3.6686e-05 | 3.71e-05 | 3.707e-05 | 3.704e-05 | 3.701e-05 | 3.698e-05 | 3.695e-05 | 3.692e-05 | 3.689e-05 | 3.686e-05 | 3.683e-05 | 3.68e-05 | 3.677e-05 | 3.674e-05 | 3.671e-05 | 3.668e-05 | 3.665e-05
| MRO008-24606844 | 88 | 88 | 0.010832 | 0 | 0.015987 | 0 | 0.016572 | 0 | 0.00014729 | 2.9262e-05 | 0.015398 | 0.015545 | 0.015692 | 0.01584 | 0.015987 | 0.016016 | 0.016045 | 0.016075 | 0.016104 | 0.016133 | 0.016162 | 0.016192 | 0.016221 | 0.01625 | 0.01628 | 0.016309 | 0.016338 | 0.016367 | 0.016397 | 0.016426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO008-77241441 | 5 | 5 | 4.14e-06 | 0 | 6.52e-06 | 0 | 6.24e-06 | 0 | 6.8e-08 | -1.4e-08 | 6.248e-06 | 6.316e-06 | 6.384e-06 | 6.452e-06 | 6.52e-06 | 6.506e-06 | 6.492e-06 | 6.478e-06 | 6.464e-06 | 6.45e-06 | 6.436e-06 | 6.422e-06 | 6.408e-06 | 6.394e-06 | 6.38e-06 | 6.366e-06 | 6.352e-06 | 6.338e-06 | 6.324e-06 | 6.31e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO008-77241511 | 54 | 54 | 0.0036903 | 0 | 0.0051082 | 0 | 0.0049659 | 0 | 4.0513e-05 | -7.1186e-06 | 0.0049462 | 0.0049867 | 0.0050272 | 0.0050677 | 0.0051082 | 0.0051011 | 0.005094 | 0.0050869 | 0.0050798 | 0.0050726 | 0.0050655 | 0.0050584 | 0.0050513 | 0.0050442 | 0.005037 | 0.0050299 | 0.0050228 | 0.0050157 | 0.0050086 | 0.0050014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-115332434 | 1310 | 89 | 0.012262 | 0.0087579 | 0.0167 | 0.012334 | 0.015971 | 0.011867 | 0.00012681 | -3.6435e-05 | 0.016193 | 0.01632 | 0.016446 | 0.016573 | 0.0167 | 0.016664 | 0.016627 | 0.016591 | 0.016554 | 0.016518 | 0.016481 | 0.016445 | 0.016409 | 0.016372 | 0.016336 | 0.016299 | 0.016263 | 0.016226 | 0.01619 | 0.016153 | 0.00010217 | -2.3353e-05 | 0.011925 | 0.012027 | 0.012129 | 0.012232 | 0.012334 | 0.01231 | 0.012287 | 0.012264 | 0.01224 | 0.012217 | 0.012194 | 0.01217 | 0.012147 | 0.012124 | 0.0121 | 0.012077 | 0.012053 | 0.01203 | 0.012007 | 0.011983
| NHL015-154154899 | 38 | 38 | 0.017913 | 0 | 0.026109 | 0 | 0.023654 | 0 | 0.00023418 | -0.00012278 | 0.025173 | 0.025407 | 0.025641 | 0.025875 | 0.026109 | 0.025987 | 0.025864 | 0.025741 | 0.025618 | 0.025496 | 0.025373 | 0.02525 | 0.025127 | 0.025004 | 0.024882 | 0.024759 | 0.024636 | 0.024513 | 0.024391 | 0.024268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-15417078 | 1551 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-15417104 | 1550 | 132 | 0.0020725 | 0.0019791 | 0.0029065 | 0.0028423 | 0.0026749 | 0.0026257 | 2.383e-05 | -1.1581e-05 | 0.0028112 | 0.0028351 | 0.0028589 | 0.0028827 | 0.0029065 | 0.002895 | 0.0028834 | 0.0028718 | 0.0028602 | 0.0028486 | 0.0028371 | 0.0028255 | 0.0028139 | 0.0028023 | 0.0027907 | 0.0027791 | 0.0027676 | 0.002756 | 0.0027444 | 0.0027328 | 2.4663e-05 | -1.0827e-05 | 0.0027436 | 0.0027683 | 0.0027929 | 0.0028176 | 0.0028423 | 0.0028314 | 0.0028206 | 0.0028098 | 0.002799 | 0.0027881 | 0.0027773 | 0.0027665 | 0.0027556 | 0.0027448 | 0.002734 | 0.0027232 | 0.0027123 | 0.0027015 | 0.0026907 | 0.0026799
| NHL015-157413262 | 25 | 25 | 0.0023955 | 0 | 0.0037914 | 0 | 0.0035183 | 0 | 3.9881e-05 | -1.3656e-05 | 0.0036319 | 0.0036717 | 0.0037116 | 0.0037515 | 0.0037914 | 0.0037777 | 0.0037641 | 0.0037504 | 0.0037368 | 0.0037231 | 0.0037095 | 0.0036958 | 0.0036821 | 0.0036685 | 0.0036548 | 0.0036412 | 0.0036275 | 0.0036139 | 0.0036002 | 0.0035865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-157443574 | 11 | 11 | 0.0010839 | 0 | 0.001675 | 0 | 0.0015601 | 0 | 1.6889e-05 | -5.7442e-06 | 0.0016075 | 0.0016243 | 0.0016412 | 0.0016581 | 0.001675 | 0.0016693 | 0.0016635 | 0.0016578 | 0.001652 | 0.0016463 | 0.0016405 | 0.0016348 | 0.0016291 | 0.0016233 | 0.0016176 | 0.0016118 | 0.0016061 | 0.0016003 | 0.0015946 | 0.0015889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-157455075 | 27 | 27 | 0.0022895 | 0 | 0.0032857 | 0 | 0.003157 | 0 | 2.8464e-05 | -6.4337e-06 | 0.0031719 | 0.0032003 | 0.0032288 | 0.0032572 | 0.0032857 | 0.0032793 | 0.0032728 | 0.0032664 | 0.00326 | 0.0032535 | 0.0032471 | 0.0032407 | 0.0032342 | 0.0032278 | 0.0032214 | 0.0032149 | 0.0032085 | 0.0032021 | 0.0031956 | 0.0031892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-157999738 | 36 | 36 | 0.0051978 | 0 | 0.0076635 | 0 | 0.0070241 | 0 | 7.0451e-05 | -3.1973e-05 | 0.0073817 | 0.0074522 | 0.0075226 | 0.0075931 | 0.0076635 | 0.0076316 | 0.0075996 | 0.0075676 | 0.0075356 | 0.0075037 | 0.0074717 | 0.0074397 | 0.0074078 | 0.0073758 | 0.0073438 | 0.0073118 | 0.0072799 | 0.0072479 | 0.0072159 | 0.0071839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-157999871 | 19 | 19 | 0.002361 | 0 | 0.0036326 | 0 | 0.0033149 | 0 | 3.6333e-05 | -1.5885e-05 | 0.0034873 | 0.0035236 | 0.00356 | 0.0035963 | 0.0036326 | 0.0036167 | 0.0036009 | 0.003585 | 0.0035691 | 0.0035532 | 0.0035373 | 0.0035214 | 0.0035055 | 0.0034897 | 0.0034738 | 0.0034579 | 0.003442 | 0.0034261 | 0.0034102 | 0.0033943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158004096 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158004251 | 13 | 13 | 0.0022066 | 0 | 0.0032242 | 0 | 0.0029968 | 0 | 2.9076e-05 | -1.1371e-05 | 0.0031079 | 0.003137 | 0.0031661 | 0.0031951 | 0.0032242 | 0.0032129 | 0.0032015 | 0.0031901 | 0.0031787 | 0.0031674 | 0.003156 | 0.0031446 | 0.0031333 | 0.0031219 | 0.0031105 | 0.0030991 | 0.0030878 | 0.0030764 | 0.003065 | 0.0030537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158004482 | 10 | 10 | 0.0029244 | 0 | 0.0039396 | 0 | 0.0037229 | 0 | 2.9004e-05 | -1.0834e-05 | 0.0038235 | 0.0038525 | 0.0038815 | 0.0039105 | 0.0039396 | 0.0039287 | 0.0039179 | 0.003907 | 0.0038962 | 0.0038854 | 0.0038745 | 0.0038637 | 0.0038529 | 0.003842 | 0.0038312 | 0.0038204 | 0.0038095 | 0.0037987 | 0.0037879 | 0.003777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158005276 | 26 | 26 | 0.00081988 | 0 | 0.0012323 | 0 | 0.0011504 | 0 | 1.1783e-05 | -4.0947e-06 | 0.0011851 | 0.0011969 | 0.0012087 | 0.0012205 | 0.0012323 | 0.0012282 | 0.0012241 | 0.00122 | 0.0012159 | 0.0012118 | 0.0012077 | 0.0012036 | 0.0011995 | 0.0011954 | 0.0011913 | 0.0011872 | 0.0011831 | 0.001179 | 0.0011749 | 0.0011709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158007892 | 17 | 17 | 0.0015562 | 0 | 0.0021867 | 0 | 0.0020783 | 0 | 1.8016e-05 | -5.422e-06 | 0.0021147 | 0.0021327 | 0.0021507 | 0.0021687 | 0.0021867 | 0.0021813 | 0.0021759 | 0.0021705 | 0.002165 | 0.0021596 | 0.0021542 | 0.0021488 | 0.0021434 | 0.0021379 | 0.0021325 | 0.0021271 | 0.0021217 | 0.0021162 | 0.0021108 | 0.0021054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158008058 | 22 | 22 | 0.012105 | 0 | 0.016531 | 0 | 0.015822 | 0 | 0.00012646 | -3.543e-05 | 0.016025 | 0.016152 | 0.016278 | 0.016405 | 0.016531 | 0.016496 | 0.01646 | 0.016425 | 0.016389 | 0.016354 | 0.016318 | 0.016283 | 0.016248 | 0.016212 | 0.016177 | 0.016141 | 0.016106 | 0.01607 | 0.016035 | 0.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158050824 | 30 | 30 | 0.0028125 | 0 | 0.0039346 | 0 | 0.0038354 | 0 | 3.2061e-05 | -4.9621e-06 | 0.0038064 | 0.0038385 | 0.0038705 | 0.0039026 | 0.0039347 | 0.0039297 | 0.0039247 | 0.0039198 | 0.0039148 | 0.0039098 | 0.0039049 | 0.0038999 | 0.003895 | 0.00389 | 0.003885 | 0.0038801 | 0.0038751 | 0.0038701 | 0.0038652 | 0.0038602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158051013 | 14 | 14 | 2.71e-05 | 0 | 4.18e-05 | 0 | 3.98e-05 | 0 | 4.2e-07 | -1e-07 | 4.012e-05 | 4.054e-05 | 4.096e-05 | 4.138e-05 | 4.18e-05 | 4.17e-05 | 4.16e-05 | 4.15e-05 | 4.14e-05 | 4.13e-05 | 4.12e-05 | 4.11e-05 | 4.1e-05 | 4.09e-05 | 4.08e-05 | 4.07e-05 | 4.06e-05 | 4.05e-05 | 4.04e-05 | 4.03e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158071333 | 36 | 36 | 0.0029399 | 0 | 0.0041677 | 0 | 0.0039527 | 0 | 3.508e-05 | -1.0754e-05 | 0.0040274 | 0.0040625 | 0.0040976 | 0.0041327 | 0.0041677 | 0.004157 | 0.0041462 | 0.0041355 | 0.0041247 | 0.004114 | 0.0041032 | 0.0040925 | 0.0040817 | 0.0040709 | 0.0040602 | 0.0040494 | 0.0040387 | 0.0040279 | 0.0040172 | 0.0040064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158071498 | 9 | 9 | 0.0030743 | 0 | 0.0034402 | 0 | 0.0032029 | 0 | 1.0457e-05 | -1.1867e-05 | 0.0033984 | 0.0034089 | 0.0034193 | 0.0034298 | 0.0034402 | 0.0034284 | 0.0034165 | 0.0034046 | 0.0033928 | 0.0033809 | 0.003369 | 0.0033572 | 0.0033453 | 0.0033334 | 0.0033216 | 0.0033097 | 0.0032978 | 0.003286 | 0.0032741 | 0.0032622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158071668 | 24 | 24 | 0.0013125 | 0 | 0.0019287 | 0 | 0.0018593 | 0 | 1.7605e-05 | -3.4714e-06 | 0.0018583 | 0.0018759 | 0.0018935 | 0.0019111 | 0.0019287 | 0.0019252 | 0.0019218 | 0.0019183 | 0.0019148 | 0.0019114 | 0.0019079 | 0.0019044 | 0.0019009 | 0.0018975 | 0.001894 | 0.0018905 | 0.0018871 | 0.0018836 | 0.0018801 | 0.0018766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158092505 | 12 | 12 | 0.0013296 | 0 | 0.0019524 | 0 | 0.001853 | 0 | 1.7793e-05 | -4.9709e-06 | 0.0018812 | 0.001899 | 0.0019168 | 0.0019346 | 0.0019524 | 0.0019474 | 0.0019425 | 0.0019375 | 0.0019325 | 0.0019275 | 0.0019226 | 0.0019176 | 0.0019126 | 0.0019077 | 0.0019027 | 0.0018977 | 0.0018927 | 0.0018878 | 0.0018828 | 0.0018778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158092654 | 24 | 24 | 0.0043842 | 0 | 0.0065637 | 0 | 0.0060467 | 0 | 6.2271e-05 | -2.5846e-05 | 0.0063146 | 0.0063768 | 0.0064391 | 0.0065014 | 0.0065637 | 0.0065378 | 0.006512 | 0.0064861 | 0.0064603 | 0.0064344 | 0.0064086 | 0.0063827 | 0.0063569 | 0.006331 | 0.0063052 | 0.0062794 | 0.0062535 | 0.0062277 | 0.0062018 | 0.006176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158130266 | 9 | 9 | 0.0010993 | 0 | 0.0015956 | 0 | 0.0014902 | 0 | 1.418e-05 | -5.2692e-06 | 0.0015389 | 0.0015531 | 0.0015672 | 0.0015814 | 0.0015956 | 0.0015903 | 0.0015851 | 0.0015798 | 0.0015745 | 0.0015693 | 0.001564 | 0.0015587 | 0.0015534 | 0.0015482 | 0.0015429 | 0.0015376 | 0.0015324 | 0.0015271 | 0.0015218 | 0.0015166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158130348 | 5 | 5 | 0.0022496 | 0 | 0.0031001 | 0 | 0.0029159 | 0 | 2.4301e-05 | -9.2097e-06 | 0.0030029 | 0.0030272 | 0.0030515 | 0.0030758 | 0.0031001 | 0.0030909 | 0.0030817 | 0.0030725 | 0.0030633 | 0.0030541 | 0.0030448 | 0.0030356 | 0.0030264 | 0.0030172 | 0.003008 | 0.0029988 | 0.0029896 | 0.0029804 | 0.0029712 | 0.002962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158145995 | 35 | 35 | 0.0059583 | 0 | 0.008576 | 0 | 0.007887 | 0 | 7.4791e-05 | -3.4449e-05 | 0.0082768 | 0.0083516 | 0.0084264 | 0.0085012 | 0.008576 | 0.0085415 | 0.0085071 | 0.0084726 | 0.0084382 | 0.0084037 | 0.0083693 | 0.0083348 | 0.0083004 | 0.0082659 | 0.0082315 | 0.008197 | 0.0081626 | 0.0081281 | 0.0080937 | 0.0080592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158146107 | 21 | 21 | 0.006264 | 0 | 0.009337 | 0 | 0.0087914 | 0 | 8.78e-05 | -2.728e-05 | 0.0089858 | 0.0090736 | 0.0091614 | 0.0092492 | 0.009337 | 0.0093098 | 0.0092825 | 0.0092552 | 0.0092279 | 0.0092006 | 0.0091734 | 0.0091461 | 0.0091188 | 0.0090915 | 0.0090642 | 0.009037 | 0.0090097 | 0.0089824 | 0.0089551 | 0.0089278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158377999 | 25 | 25 | 0.0022302 | 0 | 0.0032774 | 0 | 0.0031524 | 0 | 2.9922e-05 | -6.2528e-06 | 0.0031577 | 0.0031877 | 0.0032176 | 0.0032475 | 0.0032774 | 0.0032712 | 0.0032649 | 0.0032587 | 0.0032524 | 0.0032462 | 0.0032399 | 0.0032337 | 0.0032274 | 0.0032212 | 0.0032149 | 0.0032086 | 0.0032024 | 0.0031961 | 0.0031899 | 0.0031836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-164675628 | 8 | 8 | 0.0024741 | 0 | 0.0035106 | 0 | 0.0033436 | 0 | 2.9614e-05 | -8.3513e-06 | 0.0033921 | 0.0034217 | 0.0034514 | 0.003481 | 0.0035106 | 0.0035022 | 0.0034939 | 0.0034855 | 0.0034772 | 0.0034688 | 0.0034605 | 0.0034521 | 0.0034438 | 0.0034354 | 0.0034271 | 0.0034187 | 0.0034104 | 0.003402 | 0.0033937 | 0.0033853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-24600722 | 1173 | 347 | 0.014966 | 0.0072931 | 0.020068 | 0.01023 | 0.018498 | 0.0094944 | 0.00014578 | -7.8505e-05 | 0.019485 | 0.019631 | 0.019776 | 0.019922 | 0.020068 | 0.019989 | 0.019911 | 0.019832 | 0.019754 | 0.019675 | 0.019597 | 0.019518 | 0.01944 | 0.019361 | 0.019283 | 0.019204 | 0.019126 | 0.019047 | 0.018969 | 0.01889 | 8.3913e-05 | -3.6784e-05 | 0.0098944 | 0.0099783 | 0.010062 | 0.010146 | 0.01023 | 0.010193 | 0.010157 | 0.01012 | 0.010083 | 0.010046 | 0.010009 | 0.0099726 | 0.0099358 | 0.009899 | 0.0098622 | 0.0098254 | 0.0097887 | 0.0097519 | 0.0097151 | 0.0096783
| NHL015-24600904 | 669 | 437 | 0.0051728 | 0.0031173 | 0.0074415 | 0.0046559 | 0.006812 | 0.0042798 | 6.4821e-05 | -3.1475e-05 | 0.0071822 | 0.007247 | 0.0073119 | 0.0073767 | 0.0074415 | 0.00741 | 0.0073786 | 0.0073471 | 0.0073156 | 0.0072841 | 0.0072527 | 0.0072212 | 0.0071897 | 0.0071582 | 0.0071267 | 0.0070953 | 0.0070638 | 0.0070323 | 0.0070008 | 0.0069694 | 4.3958e-05 | -1.8801e-05 | 0.00448 | 0.004524 | 0.004568 | 0.0046119 | 0.0046559 | 0.0046371 | 0.0046183 | 0.0045995 | 0.0045807 | 0.0045619 | 0.0045431 | 0.0045243 | 0.0045055 | 0.0044867 | 0.0044679 | 0.0044491 | 0.0044303 | 0.0044115 | 0.0043926 | 0.0043738
| NHL016-15417067 | 1386 | 1152 | 0.0064178 | 0.0028486 | 0.0086217 | 0.003941 | 0.0080828 | 0.003755 | 6.2969e-05 | -2.6943e-05 | 0.0083698 | 0.0084328 | 0.0084957 | 0.0085587 | 0.0086217 | 0.0085947 | 0.0085678 | 0.0085408 | 0.0085139 | 0.0084869 | 0.00846 | 0.0084331 | 0.0084061 | 0.0083792 | 0.0083522 | 0.0083253 | 0.0082983 | 0.0082714 | 0.0082445 | 0.0082175 | 3.1211e-05 | -9.2954e-06 | 0.0038161 | 0.0038473 | 0.0038785 | 0.0039097 | 0.003941 | 0.0039317 | 0.0039224 | 0.0039131 | 0.0039038 | 0.0038945 | 0.0038852 | 0.0038759 | 0.0038666 | 0.0038573 | 0.003848 | 0.0038387 | 0.0038294 | 0.0038201 | 0.0038108 | 0.0038015
| NHL016-157284541 | 17 | 17 | 0.0026619 | 0 | 0.0038681 | 0 | 0.003638 | 0 | 3.4463e-05 | -1.1507e-05 | 0.0037303 | 0.0037647 | 0.0037992 | 0.0038337 | 0.0038681 | 0.0038566 | 0.0038451 | 0.0038336 | 0.0038221 | 0.0038106 | 0.0037991 | 0.0037876 | 0.0037761 | 0.0037646 | 0.0037531 | 0.0037416 | 0.00373 | 0.0037185 | 0.003707 | 0.0036955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL016-157284640 | 19 | 19 | 0.0018761 | 0 | 0.0027 | 0 | 0.00255 | 0 | 2.354e-05 | -7.4984e-06 | 0.0026058 | 0.0026294 | 0.0026529 | 0.0026764 | 0.0027 | 0.0026925 | 0.002685 | 0.0026775 | 0.00267 | 0.0026625 | 0.002655 | 0.0026475 | 0.00264 | 0.0026325 | 0.002625 | 0.0026175 | 0.00261 | 0.0026025 | 0.002595 | 0.0025875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL016-157284729 | 6 | 6 | 0.0024613 | 0 | 0.0036139 | 0 | 0.003302 | 0 | 3.2932e-05 | -1.5591e-05 | 0.0034821 | 0.0035151 | 0.003548 | 0.0035809 | 0.0036139 | 0.0035983 | 0.0035827 | 0.0035671 | 0.0035515 | 0.0035359 | 0.0035203 | 0.0035047 | 0.0034891 | 0.0034735 | 0.0034579 | 0.0034424 | 0.0034268 | 0.0034112 | 0.0033956 | 0.00338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL016-157284831 | 21 | 21 | 0.0026946 | 0 | 0.0041323 | 0 | 0.0038249 | 0 | 4.1079e-05 | -1.537e-05 | 0.003968 | 0.0040091 | 0.0040502 | 0.0040912 | 0.0041323 | 0.0041169 | 0.0041016 | 0.0040862 | 0.0040708 | 0.0040555 | 0.0040401 | 0.0040247 | 0.0040093 | 0.003994 | 0.0039786 | 0.0039632 | 0.0039479 | 0.0039325 | 0.0039171 | 0.0039018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL016-157328241 | 15 | 15 | 0.0013679 | 0 | 0.0021027 | 0 | 0.0018657 | 0 | 2.0992e-05 | -1.1851e-05 | 0.0020187 | 0.0020397 | 0.0020607 | 0.0020817 | 0.0021027 | 0.0020908 | 0.002079 | 0.0020671 | 0.0020553 | 0.0020434 | 0.0020316 | 0.0020197 | 0.0020079 | 0.001996 | 0.0019842 | 0.0019723 | 0.0019605 | 0.0019486 | 0.0019368 | 0.0019249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL016-157328461 | 15 | 15 | 0.003677 | 0 | 0.0055913 | 0 | 0.0052306 | 0 | 5.4694e-05 | -1.8032e-05 | 0.0053725 | 0.0054272 | 0.0054819 | 0.0055366 | 0.0055913 | 0.0055732 | 0.0055552 | 0.0055372 | 0.0055191 | 0.0055011 | 0.0054831 | 0.005465 | 0.005447 | 0.005429 | 0.0054109 | 0.0053929 | 0.0053749 | 0.0053568 | 0.0053388 | 0.0053208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL016-157328563 | 17 | 17 | 0.0010121 | 0 | 0.0015346 | 0 | 0.0013979 | 0 | 1.4929e-05 | -6.8398e-06 | 0.0014749 | 0.0014899 | 0.0015048 | 0.0015197 | 0.0015346 | 0.0015278 | 0.001521 | 0.0015141 | 0.0015073 | 0.0015004 | 0.0014936 | 0.0014868 | 0.0014799 | 0.0014731 | 0.0014662 | 0.0014594 | 0.0014526 | 0.0014457 | 0.0014389 | 0.0014321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL016-162991101 | 6 | 6 | 0.0024993 | 0 | 0.0038303 | 0 | 0.0034389 | 0 | 3.8031e-05 | -1.9572e-05 | 0.0036782 | 0.0037162 | 0.0037543 | 0.0037923 | 0.0038303 | 0.0038108 | 0.0037912 | 0.0037716 | 0.003752 | 0.0037325 | 0.0037129 | 0.0036933 | 0.0036737 | 0.0036542 | 0.0036346 | 0.003615 | 0.0035955 | 0.0035759 | 0.0035563 | 0.0035367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL016-163161231 | 14 | 14 | 0.0046765 | 0 | 0.0072372 | 0 | 0.0070268 | 0 | 7.3162e-05 | -1.0521e-05 | 0.0069445 | 0.0070177 | 0.0070908 | 0.007164 | 0.0072372 | 0.0072266 | 0.0072161 | 0.0072056 | 0.0071951 | 0.0071846 | 0.007174 | 0.0071635 | 0.007153 | 0.0071425 | 0.007132 | 0.0071214 | 0.0071109 | 0.0071004 | 0.0070899 | 0.0070794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL016-163161483 | 7 | 7 | 3.29e-05 | 0 | 4.95e-05 | 0 | 4.71e-05 | 0 | 4.7429e-07 | -1.2e-07 | 4.7603e-05 | 4.8077e-05 | 4.8551e-05 | 4.9026e-05 | 4.95e-05 | 4.938e-05 | 4.926e-05 | 4.914e-05 | 4.902e-05 | 4.89e-05 | 4.878e-05 | 4.866e-05 | 4.854e-05 | 4.842e-05 | 4.83e-05 | 4.818e-05 | 4.806e-05 | 4.794e-05 | 4.782e-05 | 4.77e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL016-24601854 | 234 | 97 | 0.0072545 | 0.0052909 | 0.010509 | 0.0079542 | 0.0097573 | 0.0074122 | 9.2994e-05 | -3.7603e-05 | 0.010137 | 0.01023 | 0.010323 | 0.010416 | 0.010509 | 0.010472 | 0.010434 | 0.010397 | 0.010359 | 0.010321 | 0.010284 | 0.010246 | 0.010209 | 0.010171 | 0.010133 | 0.010096 | 0.010058 | 0.01002 | 0.0099829 | 0.0099453 | 7.6094e-05 | -2.7103e-05 | 0.0076499 | 0.0077259 | 0.007802 | 0.0078781 | 0.0079542 | 0.0079271 | 0.0079 | 0.0078729 | 0.0078458 | 0.0078187 | 0.0077916 | 0.0077645 | 0.0077374 | 0.0077103 | 0.0076832 | 0.0076561 | 0.007629 | 0.0076019 | 0.0075748 | 0.0075477
| NHL031-111738437 | 363 | 170 | 0.008141 | 0.0027194 | 0.010832 | 0.0039018 | 0.0095039 | 0.0034061 | 7.6895e-05 | -6.6423e-05 | 0.010525 | 0.010602 | 0.010679 | 0.010755 | 0.010832 | 0.010766 | 0.010699 | 0.010633 | 0.010567 | 0.0105 | 0.010434 | 0.010367 | 0.010301 | 0.010235 | 0.010168 | 0.010102 | 0.010035 | 0.0099688 | 0.0099024 | 0.009836 | 3.3785e-05 | -2.4787e-05 | 0.0037667 | 0.0038005 | 0.0038343 | 0.003868 | 0.0039018 | 0.003877 | 0.0038522 | 0.0038275 | 0.0038027 | 0.0037779 | 0.0037531 | 0.0037283 | 0.0037035 | 0.0036787 | 0.003654 | 0.0036292 | 0.0036044 | 0.0035796 | 0.0035548 | 0.00353
| NHL031-15417259 | 1338 | 63 | 0.0071604 | 0.0038025 | 0.010029 | 0.0054065 | 0.0092455 | 0.004994 | 8.1959e-05 | -3.9174e-05 | 0.0097011 | 0.0097831 | 0.0098651 | 0.009947 | 0.010029 | 0.0099898 | 0.0099506 | 0.0099115 | 0.0098723 | 0.0098331 | 0.0097939 | 0.0097548 | 0.0097156 | 0.0096764 | 0.0096372 | 0.0095981 | 0.0095589 | 0.0095197 | 0.0094805 | 0.0094414 | 4.5829e-05 | -2.0624e-05 | 0.0052232 | 0.005269 | 0.0053148 | 0.0053606 | 0.0054065 | 0.0053858 | 0.0053652 | 0.0053446 | 0.005324 | 0.0053033 | 0.0052827 | 0.0052621 | 0.0052415 | 0.0052209 | 0.0052002 | 0.0051796 | 0.005159 | 0.0051384 | 0.0051177 | 0.0050971
| NHL031-158072303 | 19 | 19 | 0.0027504 | 0 | 0.0036988 | 0 | 0.0034277 | 0 | 2.7097e-05 | -1.3554e-05 | 0.0035904 | 0.0036175 | 0.0036446 | 0.0036717 | 0.0036988 | 0.0036852 | 0.0036716 | 0.0036581 | 0.0036445 | 0.003631 | 0.0036174 | 0.0036039 | 0.0035903 | 0.0035768 | 0.0035632 | 0.0035497 | 0.0035361 | 0.0035225 | 0.003509 | 0.0034954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158072703 | 19 | 19 | 0.0032451 | 0 | 0.0045015 | 0 | 0.0039178 | 0 | 3.5899e-05 | -2.9188e-05 | 0.0043579 | 0.0043938 | 0.0044297 | 0.0044656 | 0.0045015 | 0.0044723 | 0.0044431 | 0.004414 | 0.0043848 | 0.0043556 | 0.0043264 | 0.0042972 | 0.004268 | 0.0042388 | 0.0042096 | 0.0041805 | 0.0041513 | 0.0041221 | 0.0040929 | 0.0040637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158073136 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158078362 | 25 | 25 | 0.0025897 | 0 | 0.003666 | 0 | 0.0031989 | 0 | 3.0753e-05 | -2.3355e-05 | 0.003543 | 0.0035737 | 0.0036045 | 0.0036353 | 0.003666 | 0.0036426 | 0.0036193 | 0.0035959 | 0.0035726 | 0.0035492 | 0.0035259 | 0.0035025 | 0.0034792 | 0.0034558 | 0.0034325 | 0.0034091 | 0.0033857 | 0.0033624 | 0.003339 | 0.0033157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158078443 | 9 | 9 | 0.00065085 | 0 | 0.0009623 | 0 | 0.00085745 | 0 | 8.8985e-06 | -5.2427e-06 | 0.00092671 | 0.0009356 | 0.0009445 | 0.0009534 | 0.0009623 | 0.00095706 | 0.00095181 | 0.00094657 | 0.00094133 | 0.00093609 | 0.00093084 | 0.0009256 | 0.00092036 | 0.00091512 | 0.00090987 | 0.00090463 | 0.00089939 | 0.00089414 | 0.0008889 | 0.00088366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158078533 | 26 | 26 | 0.0015671 | 0 | 0.0022945 | 0 | 0.0020496 | 0 | 2.0783e-05 | -1.2241e-05 | 0.0022113 | 0.0022321 | 0.0022529 | 0.0022737 | 0.0022945 | 0.0022822 | 0.00227 | 0.0022577 | 0.0022455 | 0.0022332 | 0.002221 | 0.0022088 | 0.0021965 | 0.0021843 | 0.002172 | 0.0021598 | 0.0021476 | 0.0021353 | 0.0021231 | 0.0021108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158078653 | 24 | 24 | 4.42e-05 | 0 | 6.36e-05 | 0 | 5.65e-05 | 0 | 5.5429e-07 | -3.55e-07 | 6.1383e-05 | 6.1937e-05 | 6.2491e-05 | 6.3046e-05 | 6.36e-05 | 6.3245e-05 | 6.289e-05 | 6.2535e-05 | 6.218e-05 | 6.1825e-05 | 6.147e-05 | 6.1115e-05 | 6.076e-05 | 6.0405e-05 | 6.005e-05 | 5.9695e-05 | 5.934e-05 | 5.8985e-05 | 5.863e-05 | 5.8275e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158092744 | 10 | 10 | 0.0016678 | 0 | 0.0024523 | 0 | 0.0022723 | 0 | 2.2413e-05 | -8.9993e-06 | 0.0023626 | 0.002385 | 0.0024074 | 0.0024299 | 0.0024523 | 0.0024433 | 0.0024343 | 0.0024253 | 0.0024163 | 0.0024073 | 0.0023983 | 0.0023893 | 0.0023803 | 0.0023713 | 0.0023623 | 0.0023533 | 0.0023443 | 0.0023353 | 0.0023263 | 0.0023173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158092870 | 7 | 7 | 0.0020438 | 0 | 0.0028793 | 0 | 0.0025173 | 0 | 2.3872e-05 | -1.81e-05 | 0.0027838 | 0.0028077 | 0.0028315 | 0.0028554 | 0.0028793 | 0.0028612 | 0.0028431 | 0.002825 | 0.0028069 | 0.0027888 | 0.0027707 | 0.0027526 | 0.0027345 | 0.0027164 | 0.0026983 | 0.0026802 | 0.0026621 | 0.002644 | 0.0026259 | 0.0026078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158093033 | 26 | 26 | 0.012915 | 0 | 0.018633 | 0 | 0.017111 | 0 | 0.00016338 | -7.609e-05 | 0.01798 | 0.018143 | 0.018306 | 0.01847 | 0.018633 | 0.018557 | 0.018481 | 0.018405 | 0.018329 | 0.018253 | 0.018177 | 0.018101 | 0.018025 | 0.017948 | 0.017872 | 0.017796 | 0.01772 | 0.017644 | 0.017568 | 0.017492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158103926 | 23 | 23 | 0.0024946 | 0 | 0.0035292 | 0 | 0.0032631 | 0 | 2.9558e-05 | -1.3302e-05 | 0.0034109 | 0.0034405 | 0.0034701 | 0.0034996 | 0.0035292 | 0.0035159 | 0.0035026 | 0.0034893 | 0.003476 | 0.0034627 | 0.0034494 | 0.0034361 | 0.0034228 | 0.0034094 | 0.0033961 | 0.0033828 | 0.0033695 | 0.0033562 | 0.0033429 | 0.0033296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158104228 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158104320 | 16 | 16 | 2.66e-05 | 0 | 4.03e-05 | 0 | 3.47e-05 | 0 | 3.9143e-07 | -2.8e-07 | 3.8734e-05 | 3.9126e-05 | 3.9517e-05 | 3.9909e-05 | 4.03e-05 | 4.002e-05 | 3.974e-05 | 3.946e-05 | 3.918e-05 | 3.89e-05 | 3.862e-05 | 3.834e-05 | 3.806e-05 | 3.778e-05 | 3.75e-05 | 3.722e-05 | 3.694e-05 | 3.666e-05 | 3.638e-05 | 3.61e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158104465 | 17 | 17 | 0.001372 | 0 | 0.0020517 | 0 | 0.0018939 | 0 | 1.9421e-05 | -7.8901e-06 | 0.001974 | 0.0019935 | 0.0020129 | 0.0020323 | 0.0020517 | 0.0020438 | 0.0020359 | 0.0020281 | 0.0020202 | 0.0020123 | 0.0020044 | 0.0019965 | 0.0019886 | 0.0019807 | 0.0019728 | 0.0019649 | 0.001957 | 0.0019492 | 0.0019413 | 0.0019334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158118521 | 18 | 18 | 0.001608 | 0 | 0.0023228 | 0 | 0.0021793 | 0 | 2.0424e-05 | -7.1726e-06 | 0.0022411 | 0.0022615 | 0.0022819 | 0.0023024 | 0.0023228 | 0.0023156 | 0.0023084 | 0.0023013 | 0.0022941 | 0.0022869 | 0.0022798 | 0.0022726 | 0.0022654 | 0.0022582 | 0.0022511 | 0.0022439 | 0.0022367 | 0.0022296 | 0.0022224 | 0.0022152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158118640 | 19 | 19 | 0.0010302 | 0 | 0.0014102 | 0 | 0.0012283 | 0 | 1.0857e-05 | -9.0945e-06 | 0.0013667 | 0.0013776 | 0.0013885 | 0.0013993 | 0.0014102 | 0.0014011 | 0.001392 | 0.0013829 | 0.0013738 | 0.0013647 | 0.0013556 | 0.0013465 | 0.0013374 | 0.0013283 | 0.0013192 | 0.0013101 | 0.001301 | 0.0012919 | 0.0012828 | 0.0012738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-159317140 | 46 | 46 | 0.0030181 | 0 | 0.0044753 | 0 | 0.0041358 | 0 | 4.1633e-05 | -1.6971e-05 | 0.0043087 | 0.0043504 | 0.004392 | 0.0044336 | 0.0044753 | 0.0044583 | 0.0044413 | 0.0044243 | 0.0044074 | 0.0043904 | 0.0043734 | 0.0043565 | 0.0043395 | 0.0043225 | 0.0043055 | 0.0042886 | 0.0042716 | 0.0042546 | 0.0042377 | 0.0042207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-159317397 | 7 | 7 | 0.0021487 | 0 | 0.0032853 | 0 | 0.0028897 | 0 | 3.2474e-05 | -1.9781e-05 | 0.0031554 | 0.0031879 | 0.0032204 | 0.0032528 | 0.0032853 | 0.0032655 | 0.0032458 | 0.003226 | 0.0032062 | 0.0031864 | 0.0031666 | 0.0031469 | 0.0031271 | 0.0031073 | 0.0030875 | 0.0030677 | 0.003048 | 0.0030282 | 0.0030084 | 0.0029886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-159338407 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-159449178 | 22 | 22 | 0.0024242 | 0 | 0.0032855 | 0 | 0.0030157 | 0 | 2.4608e-05 | -1.3493e-05 | 0.0031871 | 0.0032117 | 0.0032363 | 0.0032609 | 0.0032855 | 0.003272 | 0.0032586 | 0.0032451 | 0.0032316 | 0.0032181 | 0.0032046 | 0.0031911 | 0.0031776 | 0.0031641 | 0.0031506 | 0.0031371 | 0.0031236 | 0.0031101 | 0.0030966 | 0.0030832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-163378374 | 9 | 9 | 0.0014265 | 0 | 0.0020694 | 0 | 0.0018152 | 0 | 1.8369e-05 | -1.2709e-05 | 0.0019959 | 0.0020143 | 0.0020326 | 0.002051 | 0.0020694 | 0.0020567 | 0.002044 | 0.0020313 | 0.0020185 | 0.0020058 | 0.0019931 | 0.0019804 | 0.0019677 | 0.001955 | 0.0019423 | 0.0019296 | 0.0019169 | 0.0019042 | 0.0018915 | 0.0018787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-171331453 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-187102650 | 1002 | 27 | 0.0020138 | 0.0018755 | 0.0027753 | 0.0027384 | 0.0024437 | 0.0024008 | 2.1756e-05 | -1.6583e-05 | 0.0026883 | 0.00271 | 0.0027318 | 0.0027536 | 0.0027753 | 0.0027587 | 0.0027421 | 0.0027256 | 0.002709 | 0.0026924 | 0.0026758 | 0.0026592 | 0.0026426 | 0.0026261 | 0.0026095 | 0.0025929 | 0.0025763 | 0.0025597 | 0.0025432 | 0.0025266 | 2.4655e-05 | -1.6883e-05 | 0.0026398 | 0.0026644 | 0.0026891 | 0.0027138 | 0.0027384 | 0.0027215 | 0.0027046 | 0.0026878 | 0.0026709 | 0.002654 | 0.0026371 | 0.0026202 | 0.0026034 | 0.0025865 | 0.0025696 | 0.0025527 | 0.0025358 | 0.0025189 | 0.0025021 | 0.0024852
| NHL031-202230824 | 916 | 519 | 0.0068783 | 0.0019877 | 0.0098319 | 0.0028819 | 0.0083952 | 0.0024552 | 8.4388e-05 | -7.1831e-05 | 0.0094943 | 0.0095787 | 0.0096631 | 0.0097475 | 0.0098319 | 0.00976 | 0.0096882 | 0.0096164 | 0.0095445 | 0.0094727 | 0.0094009 | 0.009329 | 0.0092572 | 0.0091854 | 0.0091135 | 0.0090417 | 0.0089699 | 0.0088981 | 0.0088262 | 0.0087544 | 2.555e-05 | -2.1337e-05 | 0.0027797 | 0.0028053 | 0.0028308 | 0.0028564 | 0.0028819 | 0.0028606 | 0.0028393 | 0.0028179 | 0.0027966 | 0.0027752 | 0.0027539 | 0.0027326 | 0.0027112 | 0.0026899 | 0.0026686 | 0.0026472 | 0.0026259 | 0.0026046 | 0.0025832 | 0.0025619
| NHL031-44808373 | 101 | 48 | 0.0033592 | 0.0011028 | 0.0046937 | 0.0016025 | 0.0040378 | 0.0013711 | 3.813e-05 | -3.2797e-05 | 0.0045412 | 0.0045793 | 0.0046175 | 0.0046556 | 0.0046937 | 0.0046609 | 0.0046281 | 0.0045953 | 0.0045625 | 0.0045297 | 0.0044969 | 0.0044641 | 0.0044313 | 0.0043986 | 0.0043658 | 0.004333 | 0.0043002 | 0.0042674 | 0.0042346 | 0.0042018 | 1.4275e-05 | -1.157e-05 | 0.0015454 | 0.0015596 | 0.0015739 | 0.0015882 | 0.0016025 | 0.0015909 | 0.0015793 | 0.0015677 | 0.0015562 | 0.0015446 | 0.001533 | 0.0015215 | 0.0015099 | 0.0014983 | 0.0014868 | 0.0014752 | 0.0014636 | 0.001452 | 0.0014405 | 0.0014289
| NHL031-47809173 | 33 | 24 | 0.0034844 | 0.0012449 | 0.0049879 | 0.0018184 | 0.0043796 | 0.0015944 | 4.2958e-05 | -3.0414e-05 | 0.0048161 | 0.004859 | 0.004902 | 0.004945 | 0.0049879 | 0.0049575 | 0.0049271 | 0.0048967 | 0.0048663 | 0.0048358 | 0.0048054 | 0.004775 | 0.0047446 | 0.0047142 | 0.0046838 | 0.0046534 | 0.0046229 | 0.0045925 | 0.0045621 | 0.0045317 | 1.6384e-05 | -1.1199e-05 | 0.0017528 | 0.0017692 | 0.0017856 | 0.001802 | 0.0018184 | 0.0018072 | 0.001796 | 0.0017848 | 0.0017736 | 0.0017624 | 0.0017512 | 0.00174 | 0.0017288 | 0.0017176 | 0.0017064 | 0.0016952 | 0.001684 | 0.0016728 | 0.0016616 | 0.0016504
| NKA001-111726711 | 23 | 23 | 7.57e-06 | 0 | 1.01e-05 | 0 | 1.22e-05 | 0 | 7.2286e-08 | 1.05e-07 | 9.8109e-06 | 9.8831e-06 | 9.9554e-06 | 1.0028e-05 | 1.01e-05 | 1.0205e-05 | 1.031e-05 | 1.0415e-05 | 1.052e-05 | 1.0625e-05 | 1.073e-05 | 1.0835e-05 | 1.094e-05 | 1.1045e-05 | 1.115e-05 | 1.1255e-05 | 1.136e-05 | 1.1465e-05 | 1.157e-05 | 1.1675e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA001-138135636 | 21 | 21 | 0.00014558 | 0 | 0.00015011 | 0 | 0.00015018 | 0 | 1.2946e-07 | 3.55e-09 | 0.00014959 | 0.00014972 | 0.00014985 | 0.00014998 | 0.00015011 | 0.00015011 | 0.00015012 | 0.00015012 | 0.00015012 | 0.00015013 | 0.00015013 | 0.00015013 | 0.00015014 | 0.00015014 | 0.00015014 | 0.00015015 | 0.00015015 | 0.00015016 | 0.00015016 | 0.00015016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA001-15424552 | 973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA001-15424578 | 973 | 46 | 0.0013168 | 0.0010931 | 0.0016729 | 0.0014325 | 0.0018278 | 0.00163 | 1.0174e-05 | 7.7475e-06 | 0.0016322 | 0.0016424 | 0.0016525 | 0.0016627 | 0.0016729 | 0.0016806 | 0.0016884 | 0.0016961 | 0.0017039 | 0.0017116 | 0.0017194 | 0.0017271 | 0.0017349 | 0.0017426 | 0.0017504 | 0.0017581 | 0.0017659 | 0.0017736 | 0.0017814 | 0.0017891 | 9.6959e-06 | 9.8744e-06 | 0.0013937 | 0.0014034 | 0.0014131 | 0.0014228 | 0.0014325 | 0.0014423 | 0.0014522 | 0.0014621 | 0.001472 | 0.0014818 | 0.0014917 | 0.0015016 | 0.0015115 | 0.0015213 | 0.0015312 | 0.0015411 | 0.001551 | 0.0015608 | 0.0015707 | 0.0015806
| NKA001-161093990 | 24 | 24 | 1.11e-05 | 0 | 1.54e-05 | 0 | 1.8e-05 | 0 | 1.2286e-07 | 1.3e-07 | 1.4909e-05 | 1.5031e-05 | 1.5154e-05 | 1.5277e-05 | 1.54e-05 | 1.553e-05 | 1.566e-05 | 1.579e-05 | 1.592e-05 | 1.605e-05 | 1.618e-05 | 1.631e-05 | 1.644e-05 | 1.657e-05 | 1.67e-05 | 1.683e-05 | 1.696e-05 | 1.709e-05 | 1.722e-05 | 1.735e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA001-24606104 | 370 | 370 | 0.006459 | 0 | 0.0079149 | 0 | 0.0085265 | 0 | 4.1598e-05 | 3.058e-05 | 0.0077485 | 0.0077901 | 0.0078317 | 0.0078733 | 0.0079149 | 0.0079455 | 0.0079761 | 0.0080067 | 0.0080372 | 0.0080678 | 0.0080984 | 0.008129 | 0.0081596 | 0.0081901 | 0.0082207 | 0.0082513 | 0.0082819 | 0.0083125 | 0.008343 | 0.0083736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA001-24606118 | 328 | 284 | 0.0011152 | 8.26e-05 | 0.0014908 | 0.00011339 | 0.0016928 | 0.00013169 | 1.0732e-05 | 1.0095e-05 | 0.0014479 | 0.0014587 | 0.0014694 | 0.0014801 | 0.0014908 | 0.0015009 | 0.001511 | 0.0015211 | 0.0015312 | 0.0015413 | 0.0015514 | 0.0015615 | 0.0015716 | 0.0015817 | 0.0015918 | 0.0016019 | 0.001612 | 0.0016221 | 0.0016322 | 0.0016423 | 8.7974e-07 | 9.149e-07 | 0.00010987 | 0.00011075 | 0.00011163 | 0.00011251 | 0.00011339 | 0.00011431 | 0.00011522 | 0.00011614 | 0.00011705 | 0.00011797 | 0.00011888 | 0.0001198 | 0.00012071 | 0.00012163 | 0.00012254 | 0.00012345 | 0.00012437 | 0.00012528 | 0.0001262 | 0.00012711
| NKA001-96630054 | 557 | 205 | 0.0011669 | 0.00031193 | 0.001518 | 0.00041907 | 0.0016865 | 0.00047785 | 1.0031e-05 | 8.4217e-06 | 0.0014779 | 0.0014879 | 0.001498 | 0.001508 | 0.001518 | 0.0015265 | 0.0015349 | 0.0015433 | 0.0015517 | 0.0015601 | 0.0015686 | 0.001577 | 0.0015854 | 0.0015938 | 0.0016023 | 0.0016107 | 0.0016191 | 0.0016275 | 0.0016359 | 0.0016444 | 3.0612e-06 | 2.9389e-06 | 0.00040683 | 0.00040989 | 0.00041295 | 0.00041601 | 0.00041907 | 0.00042201 | 0.00042495 | 0.00042789 | 0.00043083 | 0.00043377 | 0.0004367 | 0.00043964 | 0.00044258 | 0.00044552 | 0.00044846 | 0.0004514 | 0.00045434 | 0.00045728 | 0.00046022 | 0.00046316
| NKA002-15424741 | 1698 | 1133 | 0.013281 | 0.0015608 | 0.016288 | 0.0019569 | 0.017994 | 0.0022067 | 8.5912e-05 | 8.5345e-05 | 0.015944 | 0.01603 | 0.016116 | 0.016202 | 0.016288 | 0.016373 | 0.016458 | 0.016544 | 0.016629 | 0.016714 | 0.0168 | 0.016885 | 0.01697 | 0.017056 | 0.017141 | 0.017226 | 0.017312 | 0.017397 | 0.017482 | 0.017568 | 1.1316e-05 | 1.2491e-05 | 0.0019116 | 0.001923 | 0.0019343 | 0.0019456 | 0.0019569 | 0.0019694 | 0.0019819 | 0.0019944 | 0.0020069 | 0.0020194 | 0.0020319 | 0.0020443 | 0.0020568 | 0.0020693 | 0.0020818 | 0.0020943 | 0.0021068 | 0.0021193 | 0.0021318 | 0.0021443
| NKA002-15424752 | 1699 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA002-157269526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA002-160426606 | 14 | 14 | 5.33e-07 | 0 | 7.17e-07 | 0 | 8.64e-07 | 0 | 5.2571e-09 | 7.35e-09 | 6.9597e-07 | 7.0123e-07 | 7.0649e-07 | 7.1174e-07 | 7.17e-07 | 7.2435e-07 | 7.317e-07 | 7.3905e-07 | 7.464e-07 | 7.5375e-07 | 7.611e-07 | 7.6845e-07 | 7.758e-07 | 7.8315e-07 | 7.905e-07 | 7.9785e-07 | 8.052e-07 | 8.1255e-07 | 8.199e-07 | 8.2725e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA002-176883603 | 9 | 9 | 0.00090511 | 0 | 0.0011539 | 0 | 0.0012739 | 0 | 7.1068e-06 | 6.0038e-06 | 0.0011254 | 0.0011325 | 0.0011396 | 0.0011467 | 0.0011539 | 0.0011599 | 0.0011659 | 0.0011719 | 0.0011779 | 0.0011839 | 0.0011899 | 0.0011959 | 0.0012019 | 0.0012079 | 0.0012139 | 0.0012199 | 0.0012259 | 0.0012319 | 0.0012379 | 0.0012439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA002-24606230 | 230 | 221 | 0.0037105 | 0.00066544 | 0.0047326 | 0.00085217 | 0.0052603 | 0.00094785 | 2.9204e-05 | 2.6383e-05 | 0.0046158 | 0.004645 | 0.0046742 | 0.0047034 | 0.0047326 | 0.004759 | 0.0047854 | 0.0048117 | 0.0048381 | 0.0048645 | 0.0048909 | 0.0049173 | 0.0049437 | 0.00497 | 0.0049964 | 0.0050228 | 0.0050492 | 0.0050756 | 0.005102 | 0.0051283 | 5.3353e-06 | 4.7837e-06 | 0.00083083 | 0.00083617 | 0.0008415 | 0.00084684 | 0.00085217 | 0.00085696 | 0.00086174 | 0.00086652 | 0.00087131 | 0.00087609 | 0.00088088 | 0.00088566 | 0.00089044 | 0.00089523 | 0.00090001 | 0.00090479 | 0.00090958 | 0.00091436 | 0.00091915 | 0.00092393
| NKA002-24606244 | 321 | 321 | 0.016837 | 0 | 0.020474 | 0 | 0.023729 | 0 | 0.00010391 | 0.00016277 | 0.020058 | 0.020162 | 0.020266 | 0.02037 | 0.020474 | 0.020637 | 0.0208 | 0.020962 | 0.021125 | 0.021288 | 0.021451 | 0.021613 | 0.021776 | 0.021939 | 0.022102 | 0.022265 | 0.022427 | 0.02259 | 0.022753 | 0.022916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA003-15422579 | 651 | 631 | 0.0087339 | 1.46e-05 | 0.01109 | 1.95e-05 | 0.012454 | 2.31e-05 | 6.7319e-05 | 6.8208e-05 | 0.010821 | 0.010888 | 0.010955 | 0.011023 | 0.01109 | 0.011158 | 0.011227 | 0.011295 | 0.011363 | 0.011431 | 0.011499 | 0.011568 | 0.011636 | 0.011704 | 0.011772 | 0.01184 | 0.011909 | 0.011977 | 0.012045 | 0.012113 | 1.4e-07 | 1.8e-07 | 1.894e-05 | 1.908e-05 | 1.922e-05 | 1.936e-05 | 1.95e-05 | 1.968e-05 | 1.986e-05 | 2.004e-05 | 2.022e-05 | 2.04e-05 | 2.058e-05 | 2.076e-05 | 2.094e-05 | 2.112e-05 | 2.13e-05 | 2.148e-05 | 2.166e-05 | 2.184e-05 | 2.202e-05 | 2.22e-05
| NKA003-161248298 | 20 | 20 | 1.58e-05 | 0 | 2.12e-05 | 0 | 2.53e-05 | 0 | 1.5429e-07 | 2.05e-07 | 2.0583e-05 | 2.0737e-05 | 2.0891e-05 | 2.1046e-05 | 2.12e-05 | 2.1405e-05 | 2.161e-05 | 2.1815e-05 | 2.202e-05 | 2.2225e-05 | 2.243e-05 | 2.2635e-05 | 2.284e-05 | 2.3045e-05 | 2.325e-05 | 2.3455e-05 | 2.366e-05 | 2.3865e-05 | 2.407e-05 | 2.4275e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA004-15424817 | 2486 | 2468 | 0.016991 | 1.04e-05 | 0.020045 | 1.37e-05 | 0.021179 | 1.54e-05 | 8.7285e-05 | 5.6658e-05 | 0.019696 | 0.019784 | 0.019871 | 0.019958 | 0.020045 | 0.020102 | 0.020159 | 0.020215 | 0.020272 | 0.020329 | 0.020385 | 0.020442 | 0.020499 | 0.020555 | 0.020612 | 0.020669 | 0.020725 | 0.020782 | 0.020839 | 0.020895 | 9.4286e-08 | 8.5e-08 | 1.3323e-05 | 1.3417e-05 | 1.3511e-05 | 1.3606e-05 | 1.37e-05 | 1.3785e-05 | 1.387e-05 | 1.3955e-05 | 1.404e-05 | 1.4125e-05 | 1.421e-05 | 1.4295e-05 | 1.438e-05 | 1.4465e-05 | 1.455e-05 | 1.4635e-05 | 1.472e-05 | 1.4805e-05 | 1.489e-05 | 1.4975e-05
| NKA004-162977911 | 18 | 18 | 9.41e-06 | 0 | 1.25e-05 | 0 | 1.52e-05 | 0 | 8.8286e-08 | 1.35e-07 | 1.2147e-05 | 1.2235e-05 | 1.2323e-05 | 1.2412e-05 | 1.25e-05 | 1.2635e-05 | 1.277e-05 | 1.2905e-05 | 1.304e-05 | 1.3175e-05 | 1.331e-05 | 1.3445e-05 | 1.358e-05 | 1.3715e-05 | 1.385e-05 | 1.3985e-05 | 1.412e-05 | 1.4255e-05 | 1.439e-05 | 1.4525e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA005-154156915 | 366 | 119 | 0.0026758 | 0.002545 | 0.0036045 | 0.003455 | 0.0042165 | 0.0040686 | 2.6533e-05 | 3.06e-05 | 0.0034984 | 0.0035249 | 0.0035514 | 0.003578 | 0.0036045 | 0.0036351 | 0.0036657 | 0.0036963 | 0.0037269 | 0.0037575 | 0.0037881 | 0.0038187 | 0.0038493 | 0.0038799 | 0.0039105 | 0.0039411 | 0.0039717 | 0.0040023 | 0.0040329 | 0.0040635 | 2.6002e-05 | 3.0678e-05 | 0.003351 | 0.003377 | 0.003403 | 0.003429 | 0.003455 | 0.0034857 | 0.0035164 | 0.0035471 | 0.0035777 | 0.0036084 | 0.0036391 | 0.0036698 | 0.0037004 | 0.0037311 | 0.0037618 | 0.0037925 | 0.0038232 | 0.0038538 | 0.0038845 | 0.0039152
| NKA005-15422555 | 600 | 224 | 0.0023925 | 0.0010144 | 0.0030958 | 0.0013566 | 0.0034637 | 0.0015681 | 2.0096e-05 | 1.8392e-05 | 0.0030154 | 0.0030355 | 0.0030556 | 0.0030757 | 0.0030958 | 0.0031142 | 0.0031326 | 0.003151 | 0.0031694 | 0.0031878 | 0.0032062 | 0.0032246 | 0.003243 | 0.0032614 | 0.0032797 | 0.0032981 | 0.0033165 | 0.0033349 | 0.0033533 | 0.0033717 | 9.7772e-06 | 1.0576e-05 | 0.0013174 | 0.0013272 | 0.001337 | 0.0013468 | 0.0013566 | 0.0013671 | 0.0013777 | 0.0013883 | 0.0013989 | 0.0014094 | 0.00142 | 0.0014306 | 0.0014412 | 0.0014517 | 0.0014623 | 0.0014729 | 0.0014835 | 0.001494 | 0.0015046 | 0.0015152
| NKA005-24606900 | 247 | 247 | 0.012958 | 0 | 0.016447 | 0 | 0.018783 | 0 | 9.9678e-05 | 0.00011682 | 0.016048 | 0.016148 | 0.016247 | 0.016347 | 0.016447 | 0.016563 | 0.01668 | 0.016797 | 0.016914 | 0.017031 | 0.017148 | 0.017264 | 0.017381 | 0.017498 | 0.017615 | 0.017732 | 0.017849 | 0.017965 | 0.018082 | 0.018199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-152812929 | 531 | 484 | 0.012243 | 0.0013088 | 0.015842 | 0.0017479 | 0.01712 | 0.001918 | 0.00010282 | 6.3885e-05 | 0.015431 | 0.015534 | 0.015637 | 0.015739 | 0.015842 | 0.015906 | 0.01597 | 0.016034 | 0.016098 | 0.016162 | 0.016226 | 0.016289 | 0.016353 | 0.016417 | 0.016481 | 0.016545 | 0.016609 | 0.016673 | 0.016737 | 0.016801 | 1.2546e-05 | 8.5063e-06 | 0.0016977 | 0.0017103 | 0.0017228 | 0.0017354 | 0.0017479 | 0.0017564 | 0.0017649 | 0.0017734 | 0.0017819 | 0.0017904 | 0.0017989 | 0.0018074 | 0.0018159 | 0.0018245 | 0.001833 | 0.0018415 | 0.00185 | 0.0018585 | 0.001867 | 0.0018755
| NKA006-15424841 | 1364 | 649 | 0.0088533 | 0.0029889 | 0.011359 | 0.003962 | 0.012814 | 0.0046283 | 7.1579e-05 | 7.2764e-05 | 0.011072 | 0.011144 | 0.011215 | 0.011287 | 0.011359 | 0.011431 | 0.011504 | 0.011577 | 0.01165 | 0.011722 | 0.011795 | 0.011868 | 0.011941 | 0.012013 | 0.012086 | 0.012159 | 0.012232 | 0.012305 | 0.012377 | 0.01245 | 2.7803e-05 | 3.3316e-05 | 0.0038508 | 0.0038786 | 0.0039064 | 0.0039342 | 0.003962 | 0.0039953 | 0.0040286 | 0.0040619 | 0.0040952 | 0.0041286 | 0.0041619 | 0.0041952 | 0.0042285 | 0.0042618 | 0.0042951 | 0.0043285 | 0.0043618 | 0.0043951 | 0.0044284 | 0.0044617
| NKA006-15424865 | 1365 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-160426703 | 32 | 32 | 4.19e-05 | 0 | 5.71e-05 | 0 | 6.98e-05 | 0 | 4.3429e-07 | 6.35e-07 | 5.5363e-05 | 5.5797e-05 | 5.6231e-05 | 5.6666e-05 | 5.71e-05 | 5.7735e-05 | 5.837e-05 | 5.9005e-05 | 5.964e-05 | 6.0275e-05 | 6.091e-05 | 6.1545e-05 | 6.218e-05 | 6.2815e-05 | 6.345e-05 | 6.4085e-05 | 6.472e-05 | 6.5355e-05 | 6.599e-05 | 6.6625e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-160426816 | 14 | 14 | 0.0009965 | 0 | 0.0011384 | 0 | 0.0011456 | 0 | 4.0552e-06 | 3.588e-07 | 0.0011222 | 0.0011263 | 0.0011303 | 0.0011344 | 0.0011384 | 0.0011388 | 0.0011391 | 0.0011395 | 0.0011399 | 0.0011402 | 0.0011406 | 0.0011409 | 0.0011413 | 0.0011417 | 0.001142 | 0.0011424 | 0.0011427 | 0.0011431 | 0.0011435 | 0.0011438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-162978025 | 15 | 15 | 0.001777 | 0 | 0.0022963 | 0 | 0.0025538 | 0 | 1.4837e-05 | 1.2872e-05 | 0.002237 | 0.0022518 | 0.0022667 | 0.0022815 | 0.0022963 | 0.0023092 | 0.0023221 | 0.002335 | 0.0023478 | 0.0023607 | 0.0023736 | 0.0023864 | 0.0023993 | 0.0024122 | 0.0024251 | 0.0024379 | 0.0024508 | 0.0024637 | 0.0024765 | 0.0024894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-163615273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-181987048 | 0 | 0 | 3.45e-08 | 0 | 3.45e-08 | 0 | 3.45e-08 | 0 | 0 | 0 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 3.45e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-192419289 | 88 | 88 | 0.0029646 | 0 | 0.0037209 | 0 | 0.0042603 | 0 | 2.1607e-05 | 2.6974e-05 | 0.0036344 | 0.0036561 | 0.0036777 | 0.0036993 | 0.0037209 | 0.0037478 | 0.0037748 | 0.0038018 | 0.0038288 | 0.0038557 | 0.0038827 | 0.0039097 | 0.0039367 | 0.0039636 | 0.0039906 | 0.0040176 | 0.0040446 | 0.0040715 | 0.0040985 | 0.0041255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-24605964 | 184 | 82 | 0.0014262 | 0.0011405 | 0.0018407 | 0.0014698 | 0.0020731 | 0.0016509 | 1.1843e-05 | 1.1622e-05 | 0.0017933 | 0.0018051 | 0.001817 | 0.0018288 | 0.0018407 | 0.0018523 | 0.0018639 | 0.0018755 | 0.0018872 | 0.0018988 | 0.0019104 | 0.001922 | 0.0019336 | 0.0019453 | 0.0019569 | 0.0019685 | 0.0019801 | 0.0019918 | 0.0020034 | 0.002015 | 9.4092e-06 | 9.0573e-06 | 0.0014322 | 0.0014416 | 0.001451 | 0.0014604 | 0.0014698 | 0.0014789 | 0.0014879 | 0.001497 | 0.001506 | 0.0015151 | 0.0015241 | 0.0015332 | 0.0015423 | 0.0015513 | 0.0015604 | 0.0015694 | 0.0015785 | 0.0015875 | 0.0015966 | 0.0016057
| OYN001-15412732 | 887 | 252 | 0.00054764 | 0.00072293 | 0.00072208 | 0.0010029 | 0.00069635 | 0.00098974 | 4.9839e-06 | -1.2866e-06 | 0.00070215 | 0.00070713 | 0.00071211 | 0.0007171 | 0.00072208 | 0.00072079 | 0.00071951 | 0.00071822 | 0.00071693 | 0.00071565 | 0.00071436 | 0.00071307 | 0.00071179 | 0.0007105 | 0.00070922 | 0.00070793 | 0.00070664 | 0.00070536 | 0.00070407 | 0.00070278 | 7.9979e-06 | -6.562e-07 | 0.00097087 | 0.00097887 | 0.00098686 | 0.00099486 | 0.0010029 | 0.0010022 | 0.0010015 | 0.0010009 | 0.0010002 | 0.00099958 | 0.00099892 | 0.00099827 | 0.00099761 | 0.00099695 | 0.0009963 | 0.00099564 | 0.00099499 | 0.00099433 | 0.00099367 | 0.00099302
| OYN001-15412756 | 888 | 1 | 2.71e-06 | 7.1e-06 | 3.87e-06 | 1.02e-05 | 3.86e-06 | 1.01e-05 | 3.3143e-08 | -5e-10 | 3.7374e-06 | 3.7706e-06 | 3.8037e-06 | 3.8369e-06 | 3.87e-06 | 3.8695e-06 | 3.869e-06 | 3.8685e-06 | 3.868e-06 | 3.8675e-06 | 3.867e-06 | 3.8665e-06 | 3.866e-06 | 3.8655e-06 | 3.865e-06 | 3.8645e-06 | 3.864e-06 | 3.8635e-06 | 3.863e-06 | 3.8625e-06 | 8.8571e-08 | -5e-09 | 9.8457e-06 | 9.9343e-06 | 1.0023e-05 | 1.0111e-05 | 1.02e-05 | 1.0195e-05 | 1.019e-05 | 1.0185e-05 | 1.018e-05 | 1.0175e-05 | 1.017e-05 | 1.0165e-05 | 1.016e-05 | 1.0155e-05 | 1.015e-05 | 1.0145e-05 | 1.014e-05 | 1.0135e-05 | 1.013e-05 | 1.0125e-05
| OYN001-157370670 | 9 | 9 | 0.0012971 | 0 | 0.0017148 | 0 | 0.0016282 | 0 | 1.1936e-05 | -4.3298e-06 | 0.0016671 | 0.001679 | 0.0016909 | 0.0017029 | 0.0017148 | 0.0017105 | 0.0017061 | 0.0017018 | 0.0016975 | 0.0016932 | 0.0016888 | 0.0016845 | 0.0016802 | 0.0016758 | 0.0016715 | 0.0016672 | 0.0016628 | 0.0016585 | 0.0016542 | 0.0016499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157370765 | 2 | 2 | 0.00015716 | 0 | 0.00020855 | 0 | 0.00019623 | 0 | 1.4683e-06 | -6.1605e-07 | 0.00020267 | 0.00020414 | 0.00020561 | 0.00020708 | 0.00020855 | 0.00020793 | 0.00020732 | 0.0002067 | 0.00020608 | 0.00020547 | 0.00020485 | 0.00020424 | 0.00020362 | 0.000203 | 0.00020239 | 0.00020177 | 0.00020116 | 0.00020054 | 0.00019992 | 0.00019931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157425399 | 5 | 5 | 0.00062691 | 0 | 0.00079366 | 0 | 0.00074561 | 0 | 4.7643e-06 | -2.4028e-06 | 0.0007746 | 0.00077937 | 0.00078413 | 0.0007889 | 0.00079366 | 0.00079126 | 0.00078886 | 0.00078645 | 0.00078405 | 0.00078165 | 0.00077925 | 0.00077684 | 0.00077444 | 0.00077204 | 0.00076963 | 0.00076723 | 0.00076483 | 0.00076243 | 0.00076002 | 0.00075762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157599093 | 6 | 6 | 5.94e-06 | 0 | 8.01e-06 | 0 | 7.96e-06 | 0 | 5.9143e-08 | -2.5e-09 | 7.7734e-06 | 7.8326e-06 | 7.8917e-06 | 7.9509e-06 | 8.01e-06 | 8.0075e-06 | 8.005e-06 | 8.0025e-06 | 8e-06 | 7.9975e-06 | 7.995e-06 | 7.9925e-06 | 7.99e-06 | 7.9875e-06 | 7.985e-06 | 7.9825e-06 | 7.98e-06 | 7.9775e-06 | 7.975e-06 | 7.9725e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157599241 | 31 | 31 | 0.00015178 | 0 | 0.00021018 | 0 | 0.00020645 | 0 | 1.6687e-06 | -1.869e-07 | 0.00020351 | 0.00020518 | 0.00020685 | 0.00020852 | 0.00021019 | 0.00021 | 0.00020981 | 0.00020962 | 0.00020944 | 0.00020925 | 0.00020906 | 0.00020888 | 0.00020869 | 0.0002085 | 0.00020832 | 0.00020813 | 0.00020794 | 0.00020776 | 0.00020757 | 0.00020738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157599335 | 20 | 20 | 0.0016468 | 0 | 0.0021849 | 0 | 0.0021043 | 0 | 1.5374e-05 | -4.0309e-06 | 0.0021234 | 0.0021388 | 0.0021542 | 0.0021695 | 0.0021849 | 0.0021809 | 0.0021769 | 0.0021728 | 0.0021688 | 0.0021648 | 0.0021607 | 0.0021567 | 0.0021527 | 0.0021486 | 0.0021446 | 0.0021406 | 0.0021365 | 0.0021325 | 0.0021285 | 0.0021245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157997774 | 16 | 16 | 0.00081451 | 0 | 0.0010919 | 0 | 0.0010532 | 0 | 7.9266e-06 | -1.9349e-06 | 0.0010602 | 0.0010682 | 0.0010761 | 0.001084 | 0.0010919 | 0.00109 | 0.0010881 | 0.0010861 | 0.0010842 | 0.0010823 | 0.0010803 | 0.0010784 | 0.0010765 | 0.0010745 | 0.0010726 | 0.0010707 | 0.0010687 | 0.0010668 | 0.0010649 | 0.0010629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157997885 | 12 | 12 | 0.0042163 | 0 | 0.0055412 | 0 | 0.0053384 | 0 | 3.7856e-05 | -1.0144e-05 | 0.0053898 | 0.0054277 | 0.0054655 | 0.0055034 | 0.0055412 | 0.0055311 | 0.005521 | 0.0055108 | 0.0055007 | 0.0054905 | 0.0054804 | 0.0054702 | 0.0054601 | 0.00545 | 0.0054398 | 0.0054297 | 0.0054195 | 0.0054094 | 0.0053992 | 0.0053891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157997976 | 7 | 7 | 0.00015624 | 0 | 0.00020924 | 0 | 0.00020725 | 0 | 1.5143e-06 | -9.96e-08 | 0.00020318 | 0.00020469 | 0.00020621 | 0.00020772 | 0.00020924 | 0.00020914 | 0.00020904 | 0.00020894 | 0.00020884 | 0.00020874 | 0.00020864 | 0.00020854 | 0.00020844 | 0.00020834 | 0.00020824 | 0.00020814 | 0.00020804 | 0.00020794 | 0.00020784 | 0.00020774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157998086 | 11 | 11 | 0.00036583 | 0 | 0.00050924 | 0 | 0.00051351 | 0 | 4.0974e-06 | 2.136e-07 | 0.00049285 | 0.00049695 | 0.00050105 | 0.00050514 | 0.00050924 | 0.00050945 | 0.00050967 | 0.00050988 | 0.00051009 | 0.00051031 | 0.00051052 | 0.00051074 | 0.00051095 | 0.00051116 | 0.00051138 | 0.00051159 | 0.0005118 | 0.00051202 | 0.00051223 | 0.00051244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157998203 | 8 | 8 | 0.0011958 | 0 | 0.001641 | 0 | 0.001629 | 0 | 1.2721e-05 | -6.0175e-07 | 0.0015901 | 0.0016029 | 0.0016156 | 0.0016283 | 0.001641 | 0.0016404 | 0.0016398 | 0.0016392 | 0.0016386 | 0.001638 | 0.0016374 | 0.0016368 | 0.0016362 | 0.0016356 | 0.001635 | 0.0016344 | 0.0016338 | 0.0016332 | 0.0016326 | 0.001632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157998251 | 13 | 13 | 0.00042436 | 0 | 0.00057499 | 0 | 0.0005763 | 0 | 4.3037e-06 | 6.535e-08 | 0.00055778 | 0.00056208 | 0.00056638 | 0.00057069 | 0.00057499 | 0.00057506 | 0.00057512 | 0.00057519 | 0.00057525 | 0.00057532 | 0.00057538 | 0.00057545 | 0.00057551 | 0.00057558 | 0.00057565 | 0.00057571 | 0.00057578 | 0.00057584 | 0.00057591 | 0.00057597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157998623 | 15 | 15 | 0.00056814 | 0 | 0.00079673 | 0 | 0.00078759 | 0 | 6.5311e-06 | -4.567e-07 | 0.0007706 | 0.00077713 | 0.00078366 | 0.0007902 | 0.00079673 | 0.00079627 | 0.00079581 | 0.00079536 | 0.0007949 | 0.00079444 | 0.00079399 | 0.00079353 | 0.00079307 | 0.00079262 | 0.00079216 | 0.0007917 | 0.00079125 | 0.00079079 | 0.00079033 | 0.00078988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-159943098 | 9 | 9 | 0.0022676 | 0 | 0.0034018 | 0 | 0.0031398 | 0 | 3.2407e-05 | -1.3099e-05 | 0.0032722 | 0.0033046 | 0.003337 | 0.0033694 | 0.0034018 | 0.0033887 | 0.0033756 | 0.0033625 | 0.0033494 | 0.0033363 | 0.0033232 | 0.0033101 | 0.003297 | 0.0032839 | 0.0032708 | 0.0032577 | 0.0032446 | 0.0032315 | 0.0032184 | 0.0032053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-159943284 | 5 | 5 | 0.00074158 | 0 | 0.00090836 | 0 | 0.00086208 | 0 | 4.765e-06 | -2.314e-06 | 0.0008893 | 0.00089406 | 0.00089883 | 0.00090359 | 0.00090836 | 0.00090604 | 0.00090373 | 0.00090141 | 0.0008991 | 0.00089679 | 0.00089447 | 0.00089216 | 0.00088984 | 0.00088753 | 0.00088522 | 0.0008829 | 0.00088059 | 0.00087827 | 0.00087596 | 0.00087365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-161991346 | 8 | 8 | 0.0061953 | 0 | 0.0082098 | 0 | 0.0079194 | 0 | 5.7558e-05 | -1.4521e-05 | 0.0079796 | 0.0080371 | 0.0080947 | 0.0081522 | 0.0082098 | 0.0081953 | 0.0081808 | 0.0081662 | 0.0081517 | 0.0081372 | 0.0081227 | 0.0081082 | 0.0080936 | 0.0080791 | 0.0080646 | 0.0080501 | 0.0080355 | 0.008021 | 0.0080065 | 0.007992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-161991484 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-161991742 | 5 | 5 | 0.0001298 | 0 | 0.0001818 | 0 | 0.00018037 | 0 | 1.4857e-06 | -7.17e-08 | 0.00017586 | 0.00017734 | 0.00017883 | 0.00018031 | 0.0001818 | 0.00018173 | 0.00018166 | 0.00018158 | 0.00018151 | 0.00018144 | 0.00018137 | 0.0001813 | 0.00018123 | 0.00018115 | 0.00018108 | 0.00018101 | 0.00018094 | 0.00018087 | 0.0001808 | 0.00018072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-161991880 | 5 | 5 | 0.00056885 | 0 | 0.00081959 | 0 | 0.00078259 | 0 | 7.1641e-06 | -1.8502e-06 | 0.00079094 | 0.0007981 | 0.00080527 | 0.00081243 | 0.00081959 | 0.00081774 | 0.00081589 | 0.00081404 | 0.00081219 | 0.00081034 | 0.00080849 | 0.00080664 | 0.00080479 | 0.00080294 | 0.00080109 | 0.00079924 | 0.00079739 | 0.00079554 | 0.00079369 | 0.00079184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-161991949 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-24603328 | 87 | 73 | 0.0042635 | 0.0012432 | 0.0064316 | 0.0019898 | 0.0060981 | 0.0019059 | 6.1944e-05 | -1.6673e-05 | 0.0061838 | 0.0062457 | 0.0063077 | 0.0063696 | 0.0064316 | 0.0064149 | 0.0063982 | 0.0063815 | 0.0063649 | 0.0063482 | 0.0063315 | 0.0063148 | 0.0062982 | 0.0062815 | 0.0062648 | 0.0062482 | 0.0062315 | 0.0062148 | 0.0061981 | 0.0061815 | 2.133e-05 | -4.1932e-06 | 0.0019044 | 0.0019258 | 0.0019471 | 0.0019684 | 0.0019898 | 0.0019856 | 0.0019814 | 0.0019772 | 0.001973 | 0.0019688 | 0.0019646 | 0.0019604 | 0.0019562 | 0.001952 | 0.0019478 | 0.0019436 | 0.0019394 | 0.0019352 | 0.001931 | 0.0019269
| OYN001-24604668 | 517 | 317 | 0.0035937 | 0.00235 | 0.0045422 | 0.0030332 | 0.0042984 | 0.0028703 | 2.7101e-05 | -1.2189e-05 | 0.0044338 | 0.0044609 | 0.004488 | 0.0045151 | 0.0045422 | 0.00453 | 0.0045178 | 0.0045056 | 0.0044934 | 0.0044812 | 0.0044691 | 0.0044569 | 0.0044447 | 0.0044325 | 0.0044203 | 0.0044081 | 0.0043959 | 0.0043837 | 0.0043715 | 0.0043594 | 1.9519e-05 | -8.1432e-06 | 0.0029551 | 0.0029747 | 0.0029942 | 0.0030137 | 0.0030332 | 0.0030251 | 0.0030169 | 0.0030088 | 0.0030006 | 0.0029925 | 0.0029843 | 0.0029762 | 0.0029681 | 0.0029599 | 0.0029518 | 0.0029436 | 0.0029355 | 0.0029273 | 0.0029192 | 0.0029111
| OYN001-41898846 | 54 | 46 | 0.0034411 | 0.00043214 | 0.0045655 | 0.00059001 | 0.0043697 | 0.00057493 | 3.2127e-05 | -9.7933e-06 | 0.004437 | 0.0044691 | 0.0045013 | 0.0045334 | 0.0045655 | 0.0045557 | 0.0045459 | 0.0045361 | 0.0045264 | 0.0045166 | 0.0045068 | 0.004497 | 0.0044872 | 0.0044774 | 0.0044676 | 0.0044578 | 0.004448 | 0.0044382 | 0.0044284 | 0.0044186 | 4.5107e-06 | -7.5415e-07 | 0.00057197 | 0.00057648 | 0.00058099 | 0.0005855 | 0.00059001 | 0.00058926 | 0.0005885 | 0.00058775 | 0.000587 | 0.00058624 | 0.00058549 | 0.00058473 | 0.00058398 | 0.00058323 | 0.00058247 | 0.00058172 | 0.00058096 | 0.00058021 | 0.00057945 | 0.0005787
| OYN003-15412682 | 351 | 206 | 0.0005164 | 0.00031303 | 0.00072885 | 0.00045597 | 0.0007318 | 0.00046439 | 6.0701e-06 | 1.473e-07 | 0.00070457 | 0.00071064 | 0.00071671 | 0.00072278 | 0.00072885 | 0.000729 | 0.00072915 | 0.00072929 | 0.00072944 | 0.00072959 | 0.00072974 | 0.00072988 | 0.00073003 | 0.00073018 | 0.00073033 | 0.00073047 | 0.00073062 | 0.00073077 | 0.00073092 | 0.00073106 | 4.0839e-06 | 4.2125e-07 | 0.00043963 | 0.00044372 | 0.0004478 | 0.00045188 | 0.00045597 | 0.00045639 | 0.00045681 | 0.00045723 | 0.00045765 | 0.00045807 | 0.00045849 | 0.00045892 | 0.00045934 | 0.00045976 | 0.00046018 | 0.0004606 | 0.00046102 | 0.00046144 | 0.00046186 | 0.00046229
| OYN003-157425942 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN003-158041159 | 31 | 31 | 0.00051727 | 0 | 0.00075143 | 0 | 0.00076353 | 0 | 6.6901e-06 | 6.052e-07 | 0.00072467 | 0.00073136 | 0.00073805 | 0.00074474 | 0.00075143 | 0.00075203 | 0.00075264 | 0.00075324 | 0.00075385 | 0.00075445 | 0.00075506 | 0.00075566 | 0.00075627 | 0.00075687 | 0.00075748 | 0.00075809 | 0.00075869 | 0.0007593 | 0.0007599 | 0.00076051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN003-158109405 | 8 | 8 | 0.0018558 | 0 | 0.0027025 | 0 | 0.0027298 | 0 | 2.419e-05 | 1.3651e-06 | 0.0026057 | 0.0026299 | 0.0026541 | 0.0026783 | 0.0027025 | 0.0027039 | 0.0027052 | 0.0027066 | 0.002708 | 0.0027093 | 0.0027107 | 0.002712 | 0.0027134 | 0.0027148 | 0.0027161 | 0.0027175 | 0.0027189 | 0.0027202 | 0.0027216 | 0.002723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN003-158109515 | 20 | 20 | 3.87e-06 | 0 | 5.58e-06 | 0 | 5.66e-06 | 0 | 4.8857e-08 | 4e-09 | 5.3846e-06 | 5.4334e-06 | 5.4823e-06 | 5.5311e-06 | 5.58e-06 | 5.584e-06 | 5.588e-06 | 5.592e-06 | 5.596e-06 | 5.6e-06 | 5.604e-06 | 5.608e-06 | 5.612e-06 | 5.616e-06 | 5.62e-06 | 5.624e-06 | 5.628e-06 | 5.632e-06 | 5.636e-06 | 5.64e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN003-158109598 | 22 | 22 | 0.00042917 | 0 | 0.00061586 | 0 | 0.00063103 | 0 | 5.334e-06 | 7.5845e-07 | 0.00059453 | 0.00059986 | 0.00060519 | 0.00061053 | 0.00061586 | 0.00061662 | 0.00061738 | 0.00061814 | 0.0006189 | 0.00061965 | 0.00062041 | 0.00062117 | 0.00062193 | 0.00062269 | 0.00062345 | 0.0006242 | 0.00062496 | 0.00062572 | 0.00062648 | 0.00062724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN003-158109716 | 12 | 12 | 0.00050693 | 0 | 0.00070832 | 0 | 0.00069573 | 0 | 5.7541e-06 | -6.2965e-07 | 0.0006853 | 0.00069106 | 0.00069681 | 0.00070257 | 0.00070832 | 0.00070769 | 0.00070706 | 0.00070643 | 0.0007058 | 0.00070517 | 0.00070454 | 0.00070391 | 0.00070328 | 0.00070265 | 0.00070202 | 0.00070139 | 0.00070076 | 0.00070013 | 0.0006995 | 0.00069888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN003-158109850 | 12 | 12 | 0.00043068 | 0 | 0.00059499 | 0 | 0.00059562 | 0 | 4.6947e-06 | 3.15e-08 | 0.00057621 | 0.00058091 | 0.0005856 | 0.0005903 | 0.00059499 | 0.00059502 | 0.00059505 | 0.00059509 | 0.00059512 | 0.00059515 | 0.00059518 | 0.00059521 | 0.00059524 | 0.00059528 | 0.00059531 | 0.00059534 | 0.00059537 | 0.0005954 | 0.00059543 | 0.00059546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN003-158110054 | 27 | 27 | 0.00070755 | 0 | 0.0010286 | 0 | 0.0010382 | 0 | 9.1721e-06 | 4.824e-07 | 0.00099189 | 0.0010011 | 0.0010102 | 0.0010194 | 0.0010286 | 0.0010291 | 0.0010295 | 0.00103 | 0.0010305 | 0.001031 | 0.0010315 | 0.001032 | 0.0010324 | 0.0010329 | 0.0010334 | 0.0010339 | 0.0010344 | 0.0010348 | 0.0010353 | 0.0010358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN003-161992042 | 7 | 7 | 5.04e-06 | 0 | 7.24e-06 | 0 | 7.14e-06 | 0 | 6.2857e-08 | -5e-09 | 6.9886e-06 | 7.0514e-06 | 7.1143e-06 | 7.1771e-06 | 7.24e-06 | 7.235e-06 | 7.23e-06 | 7.225e-06 | 7.22e-06 | 7.215e-06 | 7.21e-06 | 7.205e-06 | 7.2e-06 | 7.195e-06 | 7.19e-06 | 7.185e-06 | 7.18e-06 | 7.175e-06 | 7.17e-06 | 7.165e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-15412808 | 1276 | 164 | 0.00212 | 0.0010053 | 0.0028193 | 0.0013742 | 0.0027479 | 0.001354 | 1.9981e-05 | -3.5701e-06 | 0.0027394 | 0.0027594 | 0.0027794 | 0.0027994 | 0.0028193 | 0.0028158 | 0.0028122 | 0.0028086 | 0.0028051 | 0.0028015 | 0.0027979 | 0.0027943 | 0.0027908 | 0.0027872 | 0.0027836 | 0.0027801 | 0.0027765 | 0.0027729 | 0.0027694 | 0.0027658 | 1.0541e-05 | -1.0069e-06 | 0.001332 | 0.0013426 | 0.0013531 | 0.0013636 | 0.0013742 | 0.0013732 | 0.0013722 | 0.0013712 | 0.0013702 | 0.0013691 | 0.0013681 | 0.0013671 | 0.0013661 | 0.0013651 | 0.0013641 | 0.0013631 | 0.0013621 | 0.0013611 | 0.0013601 | 0.0013591
| OYN005-159372302 | 15 | 15 | 0.0047073 | 0 | 0.007169 | 0 | 0.0076722 | 0 | 7.0335e-05 | 2.5161e-05 | 0.0068877 | 0.006958 | 0.0070284 | 0.0070987 | 0.007169 | 0.0071942 | 0.0072193 | 0.0072445 | 0.0072697 | 0.0072948 | 0.00732 | 0.0073451 | 0.0073703 | 0.0073955 | 0.0074206 | 0.0074458 | 0.007471 | 0.0074961 | 0.0075213 | 0.0075464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-159377479 | 7 | 7 | 0.00084318 | 0 | 0.0012185 | 0 | 0.0012849 | 0 | 1.0724e-05 | 3.3179e-06 | 0.0011756 | 0.0011864 | 0.0011971 | 0.0012078 | 0.0012185 | 0.0012219 | 0.0012252 | 0.0012285 | 0.0012318 | 0.0012351 | 0.0012384 | 0.0012418 | 0.0012451 | 0.0012484 | 0.0012517 | 0.001255 | 0.0012584 | 0.0012617 | 0.001265 | 0.0012683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160435471 | 13 | 13 | 0.0015674 | 0 | 0.0022779 | 0 | 0.0024393 | 0 | 2.0301e-05 | 8.0688e-06 | 0.0021967 | 0.002217 | 0.0022373 | 0.0022576 | 0.0022779 | 0.002286 | 0.0022941 | 0.0023021 | 0.0023102 | 0.0023183 | 0.0023264 | 0.0023344 | 0.0023425 | 0.0023506 | 0.0023586 | 0.0023667 | 0.0023748 | 0.0023828 | 0.0023909 | 0.002399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160491322 | 10 | 10 | 0.0011685 | 0 | 0.0015958 | 0 | 0.0016933 | 0 | 1.2207e-05 | 4.8776e-06 | 0.001547 | 0.0015592 | 0.0015714 | 0.0015836 | 0.0015958 | 0.0016007 | 0.0016055 | 0.0016104 | 0.0016153 | 0.0016202 | 0.001625 | 0.0016299 | 0.0016348 | 0.0016397 | 0.0016446 | 0.0016494 | 0.0016543 | 0.0016592 | 0.0016641 | 0.0016689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160578653 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160637132 | 5 | 5 | 0.00020337 | 0 | 0.00031134 | 0 | 0.00031816 | 0 | 3.0847e-06 | 3.41e-07 | 0.000299 | 0.00030208 | 0.00030517 | 0.00030825 | 0.00031134 | 0.00031168 | 0.00031202 | 0.00031236 | 0.0003127 | 0.00031304 | 0.00031338 | 0.00031373 | 0.00031407 | 0.00031441 | 0.00031475 | 0.00031509 | 0.00031543 | 0.00031577 | 0.00031611 | 0.00031645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160827931 | 22 | 22 | 0.0030736 | 0 | 0.0043411 | 0 | 0.004346 | 0 | 3.6215e-05 | 2.482e-07 | 0.0041962 | 0.0042324 | 0.0042687 | 0.0043049 | 0.0043411 | 0.0043413 | 0.0043416 | 0.0043418 | 0.0043421 | 0.0043423 | 0.0043426 | 0.0043428 | 0.0043431 | 0.0043433 | 0.0043436 | 0.0043438 | 0.0043441 | 0.0043443 | 0.0043446 | 0.0043448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160828059 | 17 | 17 | 0.0011882 | 0 | 0.0016483 | 0 | 0.0016713 | 0 | 1.3146e-05 | 1.1536e-06 | 0.0015957 | 0.0016088 | 0.001622 | 0.0016351 | 0.0016483 | 0.0016494 | 0.0016506 | 0.0016517 | 0.0016529 | 0.001654 | 0.0016552 | 0.0016564 | 0.0016575 | 0.0016587 | 0.0016598 | 0.001661 | 0.0016621 | 0.0016633 | 0.0016644 | 0.0016656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160828223 | 5 | 5 | 7.94e-06 | 0 | 1.12e-05 | 0 | 1.08e-05 | 0 | 9.3143e-08 | -2e-08 | 1.0827e-05 | 1.0921e-05 | 1.1014e-05 | 1.1107e-05 | 1.12e-05 | 1.118e-05 | 1.116e-05 | 1.114e-05 | 1.112e-05 | 1.11e-05 | 1.108e-05 | 1.106e-05 | 1.104e-05 | 1.102e-05 | 1.1e-05 | 1.098e-05 | 1.096e-05 | 1.094e-05 | 1.092e-05 | 1.09e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160829369 | 24 | 24 | 0.0024053 | 0 | 0.0031955 | 0 | 0.0031453 | 0 | 2.2577e-05 | -2.5098e-06 | 0.0031052 | 0.0031278 | 0.0031504 | 0.0031729 | 0.0031955 | 0.003193 | 0.0031905 | 0.003188 | 0.0031855 | 0.003183 | 0.0031804 | 0.0031779 | 0.0031754 | 0.0031729 | 0.0031704 | 0.0031679 | 0.0031654 | 0.0031629 | 0.0031604 | 0.0031579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160829541 | 13 | 13 | 0.0012848 | 0 | 0.001805 | 0 | 0.0018278 | 0 | 1.4863e-05 | 1.1397e-06 | 0.0017455 | 0.0017604 | 0.0017752 | 0.0017901 | 0.001805 | 0.0018061 | 0.0018073 | 0.0018084 | 0.0018095 | 0.0018107 | 0.0018118 | 0.001813 | 0.0018141 | 0.0018152 | 0.0018164 | 0.0018175 | 0.0018187 | 0.0018198 | 0.0018209 | 0.0018221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160930811 | 24 | 24 | 0.00062338 | 0 | 0.00091215 | 0 | 0.00094094 | 0 | 8.2507e-06 | 1.4393e-06 | 0.00087915 | 0.0008874 | 0.00089565 | 0.0009039 | 0.00091215 | 0.00091359 | 0.00091503 | 0.00091647 | 0.00091791 | 0.00091935 | 0.00092079 | 0.00092223 | 0.00092367 | 0.00092511 | 0.00092655 | 0.00092799 | 0.00092943 | 0.00093086 | 0.0009323 | 0.00093374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160930950 | 27 | 27 | 0.0030041 | 0 | 0.0045183 | 0 | 0.0048189 | 0 | 4.3265e-05 | 1.5029e-05 | 0.0043453 | 0.0043886 | 0.0044318 | 0.0044751 | 0.0045183 | 0.0045334 | 0.0045484 | 0.0045634 | 0.0045785 | 0.0045935 | 0.0046085 | 0.0046235 | 0.0046386 | 0.0046536 | 0.0046686 | 0.0046837 | 0.0046987 | 0.0047137 | 0.0047287 | 0.0047438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160931147 | 8 | 8 | 0.0012714 | 0 | 0.0016772 | 0 | 0.0016824 | 0 | 1.1596e-05 | 2.557e-07 | 0.0016309 | 0.0016425 | 0.001654 | 0.0016656 | 0.0016772 | 0.0016775 | 0.0016778 | 0.001678 | 0.0016783 | 0.0016785 | 0.0016788 | 0.001679 | 0.0016793 | 0.0016795 | 0.0016798 | 0.0016801 | 0.0016803 | 0.0016806 | 0.0016808 | 0.0016811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160960634 | 21 | 21 | 0.0038708 | 0 | 0.0057312 | 0 | 0.0058962 | 0 | 5.3153e-05 | 8.2506e-06 | 0.0055186 | 0.0055717 | 0.0056249 | 0.005678 | 0.0057312 | 0.0057394 | 0.0057477 | 0.0057559 | 0.0057642 | 0.0057724 | 0.0057807 | 0.0057889 | 0.0057972 | 0.0058054 | 0.0058137 | 0.0058219 | 0.0058302 | 0.0058384 | 0.0058467 | 0.0058549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160960891 | 6 | 6 | 0.0010982 | 0 | 0.0015728 | 0 | 0.0016401 | 0 | 1.3559e-05 | 3.3661e-06 | 0.0015186 | 0.0015321 | 0.0015457 | 0.0015592 | 0.0015728 | 0.0015762 | 0.0015795 | 0.0015829 | 0.0015863 | 0.0015896 | 0.001593 | 0.0015964 | 0.0015997 | 0.0016031 | 0.0016065 | 0.0016098 | 0.0016132 | 0.0016166 | 0.0016199 | 0.0016233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-161887259 | 419 | 64 | 0.0030983 | 0.0014694 | 0.004429 | 0.0021283 | 0.0046311 | 0.0022478 | 3.8019e-05 | 1.0108e-05 | 0.0042769 | 0.0043149 | 0.0043529 | 0.004391 | 0.004429 | 0.0044391 | 0.0044492 | 0.0044593 | 0.0044694 | 0.0044795 | 0.0044896 | 0.0044997 | 0.0045098 | 0.0045199 | 0.0045301 | 0.0045402 | 0.0045503 | 0.0045604 | 0.0045705 | 0.0045806 | 1.8826e-05 | 5.9735e-06 | 0.002053 | 0.0020718 | 0.0020907 | 0.0021095 | 0.0021283 | 0.0021343 | 0.0021403 | 0.0021462 | 0.0021522 | 0.0021582 | 0.0021642 | 0.0021701 | 0.0021761 | 0.0021821 | 0.0021881 | 0.002194 | 0.0022 | 0.002206 | 0.0022119 | 0.0022179
| OYN005-162206992 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-162260630 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-162551906 | 18 | 18 | 0.00095168 | 0 | 0.0013423 | 0 | 0.0014468 | 0 | 1.1159e-05 | 5.2287e-06 | 0.0012976 | 0.0013088 | 0.0013199 | 0.0013311 | 0.0013423 | 0.0013475 | 0.0013527 | 0.0013579 | 0.0013632 | 0.0013684 | 0.0013736 | 0.0013789 | 0.0013841 | 0.0013893 | 0.0013945 | 0.0013998 | 0.001405 | 0.0014102 | 0.0014155 | 0.0014207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-162690111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-162952933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-164254226 | 9 | 9 | 0.0010045 | 0 | 0.0015161 | 0 | 0.0015479 | 0 | 1.4618e-05 | 1.5852e-06 | 0.0014577 | 0.0014723 | 0.0014869 | 0.0015015 | 0.0015161 | 0.0015177 | 0.0015193 | 0.0015209 | 0.0015225 | 0.0015241 | 0.0015257 | 0.0015272 | 0.0015288 | 0.0015304 | 0.001532 | 0.0015336 | 0.0015352 | 0.0015368 | 0.0015383 | 0.0015399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-164254377 | 17 | 17 | 0.002249 | 0 | 0.00315 | 0 | 0.0032688 | 0 | 2.5741e-05 | 5.9412e-06 | 0.003047 | 0.0030727 | 0.0030985 | 0.0031242 | 0.00315 | 0.0031559 | 0.0031619 | 0.0031678 | 0.0031737 | 0.0031797 | 0.0031856 | 0.0031916 | 0.0031975 | 0.0032034 | 0.0032094 | 0.0032153 | 0.0032213 | 0.0032272 | 0.0032331 | 0.0032391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-164276023 | 29 | 29 | 0.0035675 | 0 | 0.0046777 | 0 | 0.0045846 | 0 | 3.1718e-05 | -4.6554e-06 | 0.0045508 | 0.0045825 | 0.0046142 | 0.0046459 | 0.0046777 | 0.004673 | 0.0046684 | 0.0046637 | 0.004659 | 0.0046544 | 0.0046497 | 0.0046451 | 0.0046404 | 0.0046358 | 0.0046311 | 0.0046265 | 0.0046218 | 0.0046171 | 0.0046125 | 0.0046078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-164365790 | 25 | 25 | 0.0014226 | 0 | 0.0020869 | 0 | 0.0021033 | 0 | 1.8978e-05 | 8.2055e-07 | 0.0020109 | 0.0020299 | 0.0020489 | 0.0020679 | 0.0020869 | 0.0020877 | 0.0020885 | 0.0020893 | 0.0020901 | 0.002091 | 0.0020918 | 0.0020926 | 0.0020934 | 0.0020942 | 0.0020951 | 0.0020959 | 0.0020967 | 0.0020975 | 0.0020983 | 0.0020992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-164366490 | 19 | 19 | 2.43e-05 | 0 | 3.74e-05 | 0 | 3.92e-05 | 0 | 3.7429e-07 | 9e-08 | 3.5903e-05 | 3.6277e-05 | 3.6651e-05 | 3.7026e-05 | 3.74e-05 | 3.749e-05 | 3.758e-05 | 3.767e-05 | 3.776e-05 | 3.785e-05 | 3.794e-05 | 3.803e-05 | 3.812e-05 | 3.821e-05 | 3.83e-05 | 3.839e-05 | 3.848e-05 | 3.857e-05 | 3.866e-05 | 3.875e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-164366901 | 7 | 7 | 0.0010006 | 0 | 0.0015719 | 0 | 0.0016235 | 0 | 1.6324e-05 | 2.5753e-06 | 0.0015067 | 0.001523 | 0.0015393 | 0.0015556 | 0.0015719 | 0.0015745 | 0.0015771 | 0.0015797 | 0.0015822 | 0.0015848 | 0.0015874 | 0.00159 | 0.0015925 | 0.0015951 | 0.0015977 | 0.0016003 | 0.0016028 | 0.0016054 | 0.001608 | 0.0016106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-203082808 | 54 | 48 | 0.0031193 | 0.00013371 | 0.0045421 | 0.0001952 | 0.0046596 | 0.00020057 | 4.065e-05 | 5.8736e-06 | 0.0043795 | 0.0044201 | 0.0044608 | 0.0045014 | 0.0045421 | 0.004548 | 0.0045538 | 0.0045597 | 0.0045656 | 0.0045715 | 0.0045773 | 0.0045832 | 0.0045891 | 0.004595 | 0.0046008 | 0.0046067 | 0.0046126 | 0.0046184 | 0.0046243 | 0.0046302 | 1.7567e-06 | 2.686e-07 | 0.00018817 | 0.00018993 | 0.00019168 | 0.00019344 | 0.0001952 | 0.00019546 | 0.00019573 | 0.000196 | 0.00019627 | 0.00019654 | 0.00019681 | 0.00019708 | 0.00019734 | 0.00019761 | 0.00019788 | 0.00019815 | 0.00019842 | 0.00019869 | 0.00019896 | 0.00019923
| OYN005-203102592 | 460 | 436 | 3.51e-05 | 8.46e-05 | 5.18e-05 | 0.00012502 | 5.35e-05 | 0.00012909 | 4.7714e-07 | 8.5e-08 | 4.9891e-05 | 5.0369e-05 | 5.0846e-05 | 5.1323e-05 | 5.18e-05 | 5.1885e-05 | 5.197e-05 | 5.2055e-05 | 5.214e-05 | 5.2225e-05 | 5.231e-05 | 5.2395e-05 | 5.248e-05 | 5.2565e-05 | 5.265e-05 | 5.2735e-05 | 5.282e-05 | 5.2905e-05 | 5.299e-05 | 5.3075e-05 | 1.155e-06 | 2.0305e-07 | 0.0001204 | 0.00012156 | 0.00012271 | 0.00012387 | 0.00012502 | 0.00012523 | 0.00012543 | 0.00012563 | 0.00012584 | 0.00012604 | 0.00012624 | 0.00012645 | 0.00012665 | 0.00012685 | 0.00012705 | 0.00012726 | 0.00012746 | 0.00012766 | 0.00012787 | 0.00012807
| OYN005-24603468 | 66 | 0 | 0.0017231 | 0.00072832 | 0.0024899 | 0.001057 | 0.0024865 | 0.0010581 | 2.191e-05 | -1.739e-07 | 0.0024023 | 0.0024242 | 0.0024461 | 0.002468 | 0.0024899 | 0.0024898 | 0.0024896 | 0.0024894 | 0.0024892 | 0.0024891 | 0.0024889 | 0.0024887 | 0.0024885 | 0.0024884 | 0.0024882 | 0.002488 | 0.0024878 | 0.0024877 | 0.0024875 | 0.0024873 | 9.3921e-06 | 5.165e-08 | 0.0010195 | 0.0010289 | 0.0010383 | 0.0010477 | 0.001057 | 0.0010571 | 0.0010571 | 0.0010572 | 0.0010573 | 0.0010573 | 0.0010574 | 0.0010574 | 0.0010575 | 0.0010575 | 0.0010576 | 0.0010576 | 0.0010577 | 0.0010577 | 0.0010578 | 0.0010578
| OYN005-24603482 | 561 | 12 | 0.005682 | 0.0019992 | 0.0080413 | 0.0028551 | 0.0083885 | 0.0029992 | 6.7408e-05 | 1.736e-05 | 0.0077716 | 0.007839 | 0.0079064 | 0.0079739 | 0.0080413 | 0.0080586 | 0.008076 | 0.0080933 | 0.0081107 | 0.0081281 | 0.0081454 | 0.0081628 | 0.0081801 | 0.0081975 | 0.0082149 | 0.0082322 | 0.0082496 | 0.0082669 | 0.0082843 | 0.0083017 | 2.4455e-05 | 7.204e-06 | 0.0027573 | 0.0027818 | 0.0028062 | 0.0028307 | 0.0028551 | 0.0028623 | 0.0028695 | 0.0028767 | 0.0028839 | 0.0028911 | 0.0028983 | 0.0029056 | 0.0029128 | 0.00292 | 0.0029272 | 0.0029344 | 0.0029416 | 0.0029488 | 0.002956 | 0.0029632
| OYN005-84748828 | 315 | 162 | 0.0014756 | 0.0015621 | 0.0021905 | 0.0023713 | 0.0022569 | 0.0024677 | 2.0424e-05 | 3.3202e-06 | 0.0021088 | 0.0021292 | 0.0021496 | 0.00217 | 0.0021905 | 0.0021938 | 0.0021971 | 0.0022004 | 0.0022037 | 0.0022071 | 0.0022104 | 0.0022137 | 0.002217 | 0.0022203 | 0.0022237 | 0.002227 | 0.0022303 | 0.0022336 | 0.0022369 | 0.0022403 | 2.3118e-05 | 4.8208e-06 | 0.0022788 | 0.0023019 | 0.002325 | 0.0023481 | 0.0023713 | 0.0023761 | 0.0023809 | 0.0023857 | 0.0023905 | 0.0023954 | 0.0024002 | 0.002405 | 0.0024098 | 0.0024146 | 0.0024195 | 0.0024243 | 0.0024291 | 0.0024339 | 0.0024388 | 0.0024436
| OYN005-88333607 | 22 | 22 | 0.00081506 | 0 | 0.0011482 | 0 | 0.0011515 | 0 | 9.5172e-06 | 1.6775e-07 | 0.0011101 | 0.0011196 | 0.0011291 | 0.0011386 | 0.0011482 | 0.0011483 | 0.0011485 | 0.0011487 | 0.0011488 | 0.001149 | 0.0011492 | 0.0011493 | 0.0011495 | 0.0011497 | 0.0011498 | 0.00115 | 0.0011502 | 0.0011503 | 0.0011505 | 0.0011507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN007-15412819 | 653 | 653 | 0.00017335 | 0 | 0.00024484 | 0 | 0.00024279 | 0 | 2.0427e-06 | -1.0265e-07 | 0.00023667 | 0.00023872 | 0.00024076 | 0.0002428 | 0.00024485 | 0.00024474 | 0.00024464 | 0.00024454 | 0.00024443 | 0.00024433 | 0.00024423 | 0.00024413 | 0.00024402 | 0.00024392 | 0.00024382 | 0.00024372 | 0.00024361 | 0.00024351 | 0.00024341 | 0.00024331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN007-15412830 | 656 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-128232196 | 910 | 825 | 0.0010917 | 4.32e-05 | 0.0017016 | 6.97e-05 | 0.00088025 | 3.28e-05 | 1.7424e-05 | -4.1066e-05 | 0.0016319 | 0.0016493 | 0.0016667 | 0.0016842 | 0.0017016 | 0.0016605 | 0.0016194 | 0.0015784 | 0.0015373 | 0.0014962 | 0.0014552 | 0.0014141 | 0.001373 | 0.001332 | 0.0012909 | 0.0012498 | 0.0012088 | 0.0011677 | 0.0011266 | 0.0010856 | 7.5714e-07 | -1.845e-06 | 6.6671e-05 | 6.7429e-05 | 6.8186e-05 | 6.8943e-05 | 6.97e-05 | 6.7855e-05 | 6.601e-05 | 6.4165e-05 | 6.232e-05 | 6.0475e-05 | 5.863e-05 | 5.6785e-05 | 5.494e-05 | 5.3095e-05 | 5.125e-05 | 4.9405e-05 | 4.756e-05 | 4.5715e-05 | 4.387e-05 | 4.2025e-05
| PLD001-15398772 | 1935 | 56 | 0.002828 | 0.00028125 | 0.0042323 | 0.00044698 | 0.0023837 | 0.00021251 | 4.0124e-05 | -9.243e-05 | 0.0040718 | 0.0041119 | 0.004152 | 0.0041922 | 0.0042323 | 0.0041399 | 0.0040474 | 0.003955 | 0.0038626 | 0.0037701 | 0.0036777 | 0.0035853 | 0.0034929 | 0.0034004 | 0.003308 | 0.0032156 | 0.0031231 | 0.0030307 | 0.0029383 | 0.0028458 | 4.7352e-06 | -1.1724e-05 | 0.00042804 | 0.00043277 | 0.00043751 | 0.00044224 | 0.00044698 | 0.00043526 | 0.00042353 | 0.00041181 | 0.00040009 | 0.00038836 | 0.00037664 | 0.00036491 | 0.00035319 | 0.00034147 | 0.00032974 | 0.00031802 | 0.0003063 | 0.00029457 | 0.00028285 | 0.00027112
| PLD001-159945085 | 17 | 17 | 0.00016388 | 0 | 0.00022531 | 0 | 0.00015018 | 0 | 1.7551e-06 | -3.7567e-06 | 0.00021829 | 0.00022004 | 0.0002218 | 0.00022355 | 0.00022531 | 0.00022155 | 0.0002178 | 0.00021404 | 0.00021028 | 0.00020653 | 0.00020277 | 0.00019901 | 0.00019526 | 0.0001915 | 0.00018774 | 0.00018399 | 0.00018023 | 0.00017647 | 0.00017272 | 0.00016896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-160255348 | 12 | 12 | 8.94e-05 | 0 | 0.00011922 | 0 | 7.68e-05 | 0 | 8.5209e-07 | -2.1212e-06 | 0.00011581 | 0.00011667 | 0.00011752 | 0.00011837 | 0.00011922 | 0.0001171 | 0.00011498 | 0.00011286 | 0.00011074 | 0.00010862 | 0.0001065 | 0.00010437 | 0.00010225 | 0.00010013 | 9.8011e-05 | 9.589e-05 | 9.3769e-05 | 9.1648e-05 | 8.9527e-05 | 8.7406e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-160255473 | 34 | 34 | 0.00019918 | 0 | 0.0002607 | 0 | 0.00019935 | 0 | 1.7579e-06 | -3.0675e-06 | 0.00025367 | 0.00025543 | 0.00025719 | 0.00025895 | 0.0002607 | 0.00025764 | 0.00025457 | 0.0002515 | 0.00024843 | 0.00024537 | 0.0002423 | 0.00023923 | 0.00023616 | 0.0002331 | 0.00023003 | 0.00022696 | 0.00022389 | 0.00022083 | 0.00021776 | 0.00021469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-160255864 | 26 | 26 | 6.58e-06 | 0 | 1.1e-05 | 0 | 4.63e-06 | 0 | 1.2629e-07 | -3.185e-07 | 1.0495e-05 | 1.0621e-05 | 1.0747e-05 | 1.0874e-05 | 1.1e-05 | 1.0682e-05 | 1.0363e-05 | 1.0045e-05 | 9.726e-06 | 9.4075e-06 | 9.089e-06 | 8.7705e-06 | 8.452e-06 | 8.1335e-06 | 7.815e-06 | 7.4965e-06 | 7.178e-06 | 6.8595e-06 | 6.541e-06 | 6.2225e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-160255960 | 25 | 25 | 6.32e-06 | 0 | 7.7e-06 | 0 | 3.57e-06 | 0 | 3.9429e-08 | -2.065e-07 | 7.5423e-06 | 7.5817e-06 | 7.6211e-06 | 7.6606e-06 | 7.7e-06 | 7.4935e-06 | 7.287e-06 | 7.0805e-06 | 6.874e-06 | 6.6675e-06 | 6.461e-06 | 6.2545e-06 | 6.048e-06 | 5.8415e-06 | 5.635e-06 | 5.4285e-06 | 5.222e-06 | 5.0155e-06 | 4.809e-06 | 4.6025e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-160286437 | 22 | 22 | 3.7e-06 | 0 | 5.5e-06 | 0 | 3.18e-06 | 0 | 5.1429e-08 | -1.16e-07 | 5.2943e-06 | 5.3457e-06 | 5.3971e-06 | 5.4486e-06 | 5.5e-06 | 5.384e-06 | 5.268e-06 | 5.152e-06 | 5.036e-06 | 4.92e-06 | 4.804e-06 | 4.688e-06 | 4.572e-06 | 4.456e-06 | 4.34e-06 | 4.224e-06 | 4.108e-06 | 3.992e-06 | 3.876e-06 | 3.76e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-160286548 | 28 | 28 | 0.0013076 | 0 | 0.0014738 | 0 | 0.001367 | 0 | 4.7464e-06 | -5.3361e-06 | 0.0014548 | 0.0014595 | 0.0014643 | 0.001469 | 0.0014738 | 0.0014684 | 0.0014631 | 0.0014578 | 0.0014524 | 0.0014471 | 0.0014418 | 0.0014364 | 0.0014311 | 0.0014257 | 0.0014204 | 0.0014151 | 0.0014097 | 0.0014044 | 0.0013991 | 0.0013937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-160286649 | 34 | 34 | 0.00068063 | 0 | 0.00084433 | 0 | 0.00047897 | 0 | 4.6771e-06 | -1.8268e-05 | 0.00082562 | 0.00083029 | 0.00083497 | 0.00083965 | 0.00084433 | 0.00082606 | 0.00080779 | 0.00078952 | 0.00077126 | 0.00075299 | 0.00073472 | 0.00071645 | 0.00069818 | 0.00067992 | 0.00066165 | 0.00064338 | 0.00062511 | 0.00060685 | 0.00058858 | 0.00057031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-162206790 | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-162207166 | 12 | 12 | 6.54e-06 | 0 | 8.96e-06 | 0 | 3.87e-06 | 0 | 6.9143e-08 | -2.545e-07 | 8.6834e-06 | 8.7526e-06 | 8.8217e-06 | 8.8909e-06 | 8.96e-06 | 8.7055e-06 | 8.451e-06 | 8.1965e-06 | 7.942e-06 | 7.6875e-06 | 7.433e-06 | 7.1785e-06 | 6.924e-06 | 6.6695e-06 | 6.415e-06 | 6.1605e-06 | 5.906e-06 | 5.6515e-06 | 5.397e-06 | 5.1425e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-162213349 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-162290445 | 24 | 24 | 0.00027728 | 0 | 0.00038466 | 0 | 0.0002106 | 0 | 3.0677e-06 | -8.7029e-06 | 0.00037238 | 0.00037545 | 0.00037852 | 0.00038159 | 0.00038465 | 0.00037595 | 0.00036725 | 0.00035855 | 0.00034984 | 0.00034114 | 0.00033244 | 0.00032374 | 0.00031503 | 0.00030633 | 0.00029763 | 0.00028892 | 0.00028022 | 0.00027152 | 0.00026282 | 0.00025411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-162290662 | 7 | 7 | 3.47e-05 | 0 | 4.84e-05 | 0 | 2.56e-05 | 0 | 3.9143e-07 | -1.14e-06 | 4.6834e-05 | 4.7226e-05 | 4.7617e-05 | 4.8009e-05 | 4.84e-05 | 4.726e-05 | 4.612e-05 | 4.498e-05 | 4.384e-05 | 4.27e-05 | 4.156e-05 | 4.042e-05 | 3.928e-05 | 3.814e-05 | 3.7e-05 | 3.586e-05 | 3.472e-05 | 3.358e-05 | 3.244e-05 | 3.13e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-162291051 | 16 | 16 | 4.06e-05 | 0 | 5.49e-05 | 0 | 2.81e-05 | 0 | 4.0857e-07 | -1.34e-06 | 5.3266e-05 | 5.3674e-05 | 5.4083e-05 | 5.4491e-05 | 5.49e-05 | 5.356e-05 | 5.222e-05 | 5.088e-05 | 4.954e-05 | 4.82e-05 | 4.686e-05 | 4.552e-05 | 4.418e-05 | 4.284e-05 | 4.15e-05 | 4.016e-05 | 3.882e-05 | 3.748e-05 | 3.614e-05 | 3.48e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-162377877 | 8 | 8 | 3.59e-06 | 0 | 5.07e-06 | 0 | 2.43e-06 | 0 | 4.2286e-08 | -1.32e-07 | 4.9009e-06 | 4.9431e-06 | 4.9854e-06 | 5.0277e-06 | 5.07e-06 | 4.938e-06 | 4.806e-06 | 4.674e-06 | 4.542e-06 | 4.41e-06 | 4.278e-06 | 4.146e-06 | 4.014e-06 | 3.882e-06 | 3.75e-06 | 3.618e-06 | 3.486e-06 | 3.354e-06 | 3.222e-06 | 3.09e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-163864241 | 40 | 40 | 0.00015816 | 0 | 0.00021906 | 0 | 0.00014095 | 0 | 1.74e-06 | -3.9057e-06 | 0.0002121 | 0.00021384 | 0.00021558 | 0.00021732 | 0.00021906 | 0.00021516 | 0.00021125 | 0.00020734 | 0.00020344 | 0.00019953 | 0.00019563 | 0.00019172 | 0.00018782 | 0.00018391 | 0.00018 | 0.0001761 | 0.00017219 | 0.00016829 | 0.00016438 | 0.00016047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-24597198 | 1313 | 272 | 0.0011834 | 0.00029822 | 0.0014962 | 0.00038427 | 0.00092604 | 0.00023589 | 8.9357e-06 | -2.8506e-05 | 0.0014604 | 0.0014694 | 0.0014783 | 0.0014872 | 0.0014962 | 0.0014677 | 0.0014392 | 0.0014106 | 0.0013821 | 0.0013536 | 0.0013251 | 0.0012966 | 0.0012681 | 0.0012396 | 0.0012111 | 0.0011826 | 0.0011541 | 0.0011256 | 0.0010971 | 0.0010686 | 2.4584e-06 | -7.4187e-06 | 0.00037443 | 0.00037689 | 0.00037935 | 0.00038181 | 0.00038427 | 0.00037685 | 0.00036943 | 0.00036201 | 0.00035459 | 0.00034717 | 0.00033975 | 0.00033234 | 0.00032492 | 0.0003175 | 0.00031008 | 0.00030266 | 0.00029524 | 0.00028782 | 0.00028041 | 0.00027299
| PLD001-24611964 | 566 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-95142888 | 56 | 56 | 0.00026284 | 0 | 0.00034903 | 0 | 0.00022007 | 0 | 2.4625e-06 | -6.448e-06 | 0.00033918 | 0.00034164 | 0.0003441 | 0.00034657 | 0.00034903 | 0.00034258 | 0.00033613 | 0.00032969 | 0.00032324 | 0.00031679 | 0.00031034 | 0.00030389 | 0.00029745 | 0.000291 | 0.00028455 | 0.0002781 | 0.00027165 | 0.00026521 | 0.00025876 | 0.00025231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD002-15398648 | 16 | 0 | 0 | 1.64e-07 | 0 | 2.96e-07 | 0 | 8.77e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7714e-09 | -1.0415e-08 | 2.8091e-07 | 2.8469e-07 | 2.8846e-07 | 2.9223e-07 | 2.96e-07 | 2.8559e-07 | 2.7517e-07 | 2.6476e-07 | 2.5434e-07 | 2.4393e-07 | 2.3351e-07 | 2.231e-07 | 2.1268e-07 | 2.0227e-07 | 1.9185e-07 | 1.8144e-07 | 1.7102e-07 | 1.6061e-07 | 1.5019e-07 | 1.3978e-07
| PLD002-15398661 | 16 | 16 | 0.001086 | 0 | 0.0017344 | 0 | 0.00081449 | 0 | 1.8524e-05 | -4.5995e-05 | 0.0016603 | 0.0016788 | 0.0016973 | 0.0017159 | 0.0017344 | 0.0016884 | 0.0016424 | 0.0015964 | 0.0015504 | 0.0015044 | 0.0014584 | 0.0014124 | 0.0013664 | 0.0013204 | 0.0012744 | 0.0012284 | 0.0011824 | 0.0011365 | 0.0010905 | 0.0010445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-110224899 | 9 | 9 | 1.02e-06 | 0 | 1.83e-06 | 0 | 5.43e-07 | 0 | 2.3143e-08 | -6.435e-08 | 1.7374e-06 | 1.7606e-06 | 1.7837e-06 | 1.8069e-06 | 1.83e-06 | 1.7656e-06 | 1.7013e-06 | 1.6369e-06 | 1.5726e-06 | 1.5082e-06 | 1.4439e-06 | 1.3795e-06 | 1.3152e-06 | 1.2508e-06 | 1.1865e-06 | 1.1221e-06 | 1.0578e-06 | 9.9345e-07 | 9.291e-07 | 8.6475e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-147733185 | 568 | 28 | 0.00054629 | 0.00018222 | 0.00075388 | 0.00025935 | 0.00042372 | 0.00012184 | 5.9312e-06 | -1.6508e-05 | 0.00073016 | 0.00073609 | 0.00074202 | 0.00074795 | 0.00075388 | 0.00073738 | 0.00072087 | 0.00070436 | 0.00068785 | 0.00067134 | 0.00065484 | 0.00063833 | 0.00062182 | 0.00060531 | 0.0005888 | 0.00057229 | 0.00055579 | 0.00053928 | 0.00052277 | 0.00050626 | 2.2038e-06 | -6.8755e-06 | 0.00025054 | 0.00025274 | 0.00025494 | 0.00025715 | 0.00025935 | 0.00025248 | 0.0002456 | 0.00023873 | 0.00023185 | 0.00022497 | 0.0002181 | 0.00021122 | 0.00020435 | 0.00019747 | 0.0001906 | 0.00018372 | 0.00017685 | 0.00016997 | 0.0001631 | 0.00015622
| PLD003-15398748 | 1113 | 54 | 0.00029799 | 0.00026131 | 0.00047914 | 0.00041274 | 0.00021745 | 0.0002024 | 5.1757e-06 | -1.3085e-05 | 0.00045844 | 0.00046362 | 0.00046879 | 0.00047397 | 0.00047914 | 0.00046606 | 0.00045297 | 0.00043989 | 0.0004268 | 0.00041372 | 0.00040063 | 0.00038755 | 0.00037447 | 0.00036138 | 0.0003483 | 0.00033521 | 0.00032213 | 0.00030904 | 0.00029596 | 0.00028287 | 4.3264e-06 | -1.0517e-05 | 0.00039543 | 0.00039976 | 0.00040408 | 0.00040841 | 0.00041274 | 0.00040222 | 0.0003917 | 0.00038119 | 0.00037067 | 0.00036015 | 0.00034964 | 0.00033912 | 0.0003286 | 0.00031808 | 0.00030757 | 0.00029705 | 0.00028653 | 0.00027602 | 0.0002655 | 0.00025498
| PLD003-160436494 | 19 | 19 | 2.04e-06 | 0 | 3.11e-06 | 0 | 1.18e-06 | 0 | 3.0571e-08 | -9.65e-08 | 2.9877e-06 | 3.0183e-06 | 3.0489e-06 | 3.0794e-06 | 3.11e-06 | 3.0135e-06 | 2.917e-06 | 2.8205e-06 | 2.724e-06 | 2.6275e-06 | 2.531e-06 | 2.4345e-06 | 2.338e-06 | 2.2415e-06 | 2.145e-06 | 2.0485e-06 | 1.952e-06 | 1.8555e-06 | 1.759e-06 | 1.6625e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-160436674 | 27 | 27 | 0.0019918 | 0 | 0.002966 | 0 | 0.0018161 | 0 | 2.7835e-05 | -5.7493e-05 | 0.0028546 | 0.0028825 | 0.0029103 | 0.0029381 | 0.002966 | 0.0029085 | 0.002851 | 0.0027935 | 0.002736 | 0.0026785 | 0.002621 | 0.0025635 | 0.002506 | 0.0024485 | 0.002391 | 0.0023336 | 0.0022761 | 0.0022186 | 0.0021611 | 0.0021036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-160451735 | 51 | 51 | 0.00097368 | 0 | 0.0015129 | 0 | 0.00076211 | 0 | 1.5406e-05 | -3.7539e-05 | 0.0014513 | 0.0014667 | 0.0014821 | 0.0014975 | 0.0015129 | 0.0014754 | 0.0014378 | 0.0014003 | 0.0013627 | 0.0013252 | 0.0012877 | 0.0012501 | 0.0012126 | 0.001175 | 0.0011375 | 0.0011 | 0.0010624 | 0.0010249 | 0.00098735 | 0.00094981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-160519395 | 8 | 8 | 0.0025158 | 0 | 0.0037903 | 0 | 0.0020472 | 0 | 3.6415e-05 | -8.7154e-05 | 0.0036446 | 0.003681 | 0.0037174 | 0.0037539 | 0.0037903 | 0.0037031 | 0.003616 | 0.0035288 | 0.0034417 | 0.0033545 | 0.0032673 | 0.0031802 | 0.003093 | 0.0030059 | 0.0029187 | 0.0028316 | 0.0027444 | 0.0026573 | 0.0025701 | 0.002483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-160519570 | 15 | 15 | 0.0019635 | 0 | 0.0031506 | 0 | 0.0016493 | 0 | 3.3918e-05 | -7.5062e-05 | 0.0030149 | 0.0030488 | 0.0030828 | 0.0031167 | 0.0031506 | 0.0030755 | 0.0030005 | 0.0029254 | 0.0028503 | 0.0027753 | 0.0027002 | 0.0026252 | 0.0025501 | 0.002475 | 0.0024 | 0.0023249 | 0.0022498 | 0.0021748 | 0.0020997 | 0.0020247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-160519700 | 30 | 30 | 0.00012277 | 0 | 0.0001654 | 0 | 9.72e-05 | 0 | 1.2179e-06 | -3.4098e-06 | 0.00016052 | 0.00016174 | 0.00016296 | 0.00016418 | 0.0001654 | 0.00016199 | 0.00015858 | 0.00015517 | 0.00015176 | 0.00014835 | 0.00014494 | 0.00014153 | 0.00013812 | 0.00013471 | 0.0001313 | 0.00012789 | 0.00012448 | 0.00012107 | 0.00011766 | 0.00011425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-160519896 | 26 | 26 | 0.00039102 | 0 | 0.00056381 | 0 | 0.00025557 | 0 | 4.9369e-06 | -1.5412e-05 | 0.00054406 | 0.000549 | 0.00055394 | 0.00055887 | 0.00056381 | 0.0005484 | 0.00053299 | 0.00051757 | 0.00050216 | 0.00048675 | 0.00047134 | 0.00045593 | 0.00044051 | 0.0004251 | 0.00040969 | 0.00039428 | 0.00037887 | 0.00036345 | 0.00034804 | 0.00033263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-160520056 | 17 | 17 | 4.5e-05 | 0 | 6.71e-05 | 0 | 2.61e-05 | 0 | 6.3143e-07 | -2.05e-06 | 6.4574e-05 | 6.5206e-05 | 6.5837e-05 | 6.6469e-05 | 6.71e-05 | 6.505e-05 | 6.3e-05 | 6.095e-05 | 5.89e-05 | 5.685e-05 | 5.48e-05 | 5.275e-05 | 5.07e-05 | 4.865e-05 | 4.66e-05 | 4.455e-05 | 4.25e-05 | 4.045e-05 | 3.84e-05 | 3.635e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-160574293 | 34 | 34 | 0.0026494 | 0 | 0.0038977 | 0 | 0.0025165 | 0 | 3.5667e-05 | -6.9062e-05 | 0.003755 | 0.0037907 | 0.0038264 | 0.003862 | 0.0038977 | 0.0038286 | 0.0037596 | 0.0036905 | 0.0036215 | 0.0035524 | 0.0034833 | 0.0034143 | 0.0033452 | 0.0032762 | 0.0032071 | 0.003138 | 0.003069 | 0.0029999 | 0.0029308 | 0.0028618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-160574380 | 18 | 18 | 8.24e-05 | 0 | 0.00010925 | 0 | 7.85e-05 | 0 | 7.6729e-07 | -1.5378e-06 | 0.00010619 | 0.00010695 | 0.00010772 | 0.00010849 | 0.00010925 | 0.00010772 | 0.00010618 | 0.00010464 | 0.0001031 | 0.00010157 | 0.00010003 | 9.8491e-05 | 9.6953e-05 | 9.5415e-05 | 9.3878e-05 | 9.234e-05 | 9.0802e-05 | 8.9264e-05 | 8.7727e-05 | 8.6189e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-160574486 | 13 | 13 | 0.0011069 | 0 | 0.0016987 | 0 | 0.0010725 | 0 | 1.6908e-05 | -3.1309e-05 | 0.001631 | 0.0016479 | 0.0016648 | 0.0016817 | 0.0016987 | 0.0016673 | 0.001636 | 0.0016047 | 0.0015734 | 0.0015421 | 0.0015108 | 0.0014795 | 0.0014482 | 0.0014169 | 0.0013856 | 0.0013543 | 0.0013229 | 0.0012916 | 0.0012603 | 0.001229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-160574588 | 42 | 42 | 0.00050886 | 0 | 0.00071536 | 0 | 0.00034826 | 0 | 5.9e-06 | -1.8355e-05 | 0.00069176 | 0.00069766 | 0.00070356 | 0.00070946 | 0.00071536 | 0.00069701 | 0.00067865 | 0.0006603 | 0.00064194 | 0.00062358 | 0.00060523 | 0.00058687 | 0.00056852 | 0.00055016 | 0.00053181 | 0.00051345 | 0.0004951 | 0.00047674 | 0.00045839 | 0.00044003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-162199489 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-162199732 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-162199939 | 23 | 23 | 2.85e-05 | 0 | 4.14e-05 | 0 | 1.86e-05 | 0 | 3.6857e-07 | -1.14e-06 | 3.9926e-05 | 4.0294e-05 | 4.0663e-05 | 4.1031e-05 | 4.14e-05 | 4.026e-05 | 3.912e-05 | 3.798e-05 | 3.684e-05 | 3.57e-05 | 3.456e-05 | 3.342e-05 | 3.228e-05 | 3.114e-05 | 3e-05 | 2.886e-05 | 2.772e-05 | 2.658e-05 | 2.544e-05 | 2.43e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-162260412 | 6 | 6 | 5.46e-05 | 0 | 8.68e-05 | 0 | 4.68e-05 | 0 | 9.2e-07 | -2e-06 | 8.312e-05 | 8.404e-05 | 8.496e-05 | 8.588e-05 | 8.68e-05 | 8.48e-05 | 8.28e-05 | 8.08e-05 | 7.88e-05 | 7.68e-05 | 7.48e-05 | 7.28e-05 | 7.08e-05 | 6.88e-05 | 6.68e-05 | 6.48e-05 | 6.28e-05 | 6.08e-05 | 5.88e-05 | 5.68e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-162378154 | 6 | 6 | 8.44e-05 | 0 | 0.00012339 | 0 | 5.18e-05 | 0 | 1.1141e-06 | -3.5796e-06 | 0.00011894 | 0.00012005 | 0.00012116 | 0.00012228 | 0.00012339 | 0.00011981 | 0.00011623 | 0.00011265 | 0.00010907 | 0.00010549 | 0.00010192 | 9.8335e-05 | 9.4756e-05 | 9.1176e-05 | 8.7596e-05 | 8.4017e-05 | 8.0437e-05 | 7.6858e-05 | 7.3278e-05 | 6.9698e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-162378402 | 10 | 10 | 9.9e-05 | 0 | 0.00014136 | 0 | 7.18e-05 | 0 | 1.2103e-06 | -3.4781e-06 | 0.00013652 | 0.00013773 | 0.00013894 | 0.00014015 | 0.00014136 | 0.00013788 | 0.0001344 | 0.00013093 | 0.00012745 | 0.00012397 | 0.00012049 | 0.00011701 | 0.00011354 | 0.00011006 | 0.00010658 | 0.0001031 | 9.9624e-05 | 9.6146e-05 | 9.2668e-05 | 8.919e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-163610230 | 15 | 15 | 1.38e-07 | 0 | 2.66e-07 | 0 | 7.33e-08 | 0 | 3.6571e-09 | -9.635e-09 | 2.5137e-07 | 2.5503e-07 | 2.5869e-07 | 2.6234e-07 | 2.66e-07 | 2.5636e-07 | 2.4673e-07 | 2.3709e-07 | 2.2746e-07 | 2.1783e-07 | 2.0819e-07 | 1.9856e-07 | 1.8892e-07 | 1.7929e-07 | 1.6965e-07 | 1.6002e-07 | 1.5038e-07 | 1.4075e-07 | 1.3111e-07 | 1.2148e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-163610492 | 8 | 8 | 0.001168 | 0 | 0.0017377 | 0 | 0.0010604 | 0 | 1.6275e-05 | -3.3864e-05 | 0.0016726 | 0.0016889 | 0.0017051 | 0.0017214 | 0.0017377 | 0.0017038 | 0.00167 | 0.0016361 | 0.0016022 | 0.0015684 | 0.0015345 | 0.0015006 | 0.0014668 | 0.0014329 | 0.001399 | 0.0013652 | 0.0013313 | 0.0012974 | 0.0012636 | 0.0012297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-24597170 | 375 | 186 | 0.00054494 | 0.00048249 | 0.00077716 | 0.00068713 | 0.00039873 | 0.00038079 | 6.6346e-06 | -1.8921e-05 | 0.00075062 | 0.00075725 | 0.00076389 | 0.00077052 | 0.00077716 | 0.00075823 | 0.00073931 | 0.00072039 | 0.00070147 | 0.00068255 | 0.00066363 | 0.00064471 | 0.00062579 | 0.00060686 | 0.00058794 | 0.00056902 | 0.0005501 | 0.00053118 | 0.00051226 | 0.00049334 | 5.8469e-06 | -1.5317e-05 | 0.00066375 | 0.00066959 | 0.00067544 | 0.00068129 | 0.00068713 | 0.00067182 | 0.0006565 | 0.00064118 | 0.00062586 | 0.00061055 | 0.00059523 | 0.00057991 | 0.0005646 | 0.00054928 | 0.00053396 | 0.00051865 | 0.00050333 | 0.00048801 | 0.00047269 | 0.00045738
| PLD003-24597184 | 540 | 361 | 0.0086747 | 0.0028762 | 0.01139 | 0.0041477 | 0.0083432 | 0.0025795 | 7.7573e-05 | -0.00015233 | 0.011079 | 0.011157 | 0.011235 | 0.011312 | 0.01139 | 0.011237 | 0.011085 | 0.010933 | 0.01078 | 0.010628 | 0.010476 | 0.010323 | 0.010171 | 0.010019 | 0.0098665 | 0.0097141 | 0.0095618 | 0.0094095 | 0.0092572 | 0.0091048 | 3.6329e-05 | -7.8409e-05 | 0.0040024 | 0.0040387 | 0.004075 | 0.0041114 | 0.0041477 | 0.0040693 | 0.0039909 | 0.0039125 | 0.0038341 | 0.0037557 | 0.0036772 | 0.0035988 | 0.0035204 | 0.003442 | 0.0033636 | 0.0032852 | 0.0032068 | 0.0031284 | 0.00305 | 0.0029716
| PLD003-24605460 | 661 | 93 | 0.00054345 | 2.75e-05 | 0.00078801 | 4.23e-05 | 0.00048315 | 2.32e-05 | 6.9875e-06 | -1.5243e-05 | 0.00076006 | 0.00076705 | 0.00077404 | 0.00078103 | 0.00078801 | 0.00077277 | 0.00075753 | 0.00074228 | 0.00072704 | 0.0007118 | 0.00069656 | 0.00068131 | 0.00066607 | 0.00065083 | 0.00063558 | 0.00062034 | 0.0006051 | 0.00058985 | 0.00057461 | 0.00055937 | 4.2286e-07 | -9.55e-07 | 4.0609e-05 | 4.1031e-05 | 4.1454e-05 | 4.1877e-05 | 4.23e-05 | 4.1345e-05 | 4.039e-05 | 3.9435e-05 | 3.848e-05 | 3.7525e-05 | 3.657e-05 | 3.5615e-05 | 3.466e-05 | 3.3705e-05 | 3.275e-05 | 3.1795e-05 | 3.084e-05 | 2.9885e-05 | 2.893e-05 | 2.7975e-05
| PLD004-121146862 | 884 | 884 | 0.0026864 | 0 | 0.0038909 | 0 | 0.0024022 | 0 | 3.4414e-05 | -7.4431e-05 | 0.0037532 | 0.0037876 | 0.003822 | 0.0038564 | 0.0038909 | 0.0038164 | 0.003742 | 0.0036676 | 0.0035931 | 0.0035187 | 0.0034443 | 0.0033698 | 0.0032954 | 0.003221 | 0.0031465 | 0.0030721 | 0.0029977 | 0.0029233 | 0.0028488 | 0.0027744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD004-15398624 | 2874 | 1035 | 0.00078441 | 0.00016041 | 0.0011592 | 0.00026337 | 0.00066417 | 0.00011452 | 1.0708e-05 | -2.4751e-05 | 0.0011164 | 0.0011271 | 0.0011378 | 0.0011485 | 0.0011592 | 0.0011344 | 0.0011097 | 0.0010849 | 0.0010602 | 0.0010354 | 0.0010107 | 0.00098594 | 0.00096118 | 0.00093643 | 0.00091168 | 0.00088693 | 0.00086218 | 0.00083743 | 0.00081268 | 0.00078793 | 2.9419e-06 | -7.4428e-06 | 0.00025161 | 0.00025455 | 0.00025749 | 0.00026043 | 0.00026338 | 0.00025593 | 0.00024849 | 0.00024105 | 0.0002336 | 0.00022616 | 0.00021872 | 0.00021128 | 0.00020383 | 0.00019639 | 0.00018895 | 0.0001815 | 0.00017406 | 0.00016662 | 0.00015918 | 0.00015173
| PLD004-72962767 | 955 | 955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD005-15398737 | 174 | 174 | 0.002717 | 0 | 0.0040845 | 0 | 0.0022651 | 0 | 3.907e-05 | -9.0969e-05 | 0.0039282 | 0.0039673 | 0.0040063 | 0.0040454 | 0.0040845 | 0.0039935 | 0.0039025 | 0.0038116 | 0.0037206 | 0.0036296 | 0.0035387 | 0.0034477 | 0.0033567 | 0.0032658 | 0.0031748 | 0.0030838 | 0.0029929 | 0.0029019 | 0.0028109 | 0.0027199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD005-15398783 | 175 | 1 | 0 | 1.17e-06 | 0 | 2.11e-06 | 0 | 6.25e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6857e-08 | -7.425e-08 | 2.0026e-06 | 2.0294e-06 | 2.0563e-06 | 2.0831e-06 | 2.11e-06 | 2.0358e-06 | 1.9615e-06 | 1.8873e-06 | 1.813e-06 | 1.7388e-06 | 1.6645e-06 | 1.5903e-06 | 1.516e-06 | 1.4418e-06 | 1.3675e-06 | 1.2933e-06 | 1.219e-06 | 1.1448e-06 | 1.0705e-06 | 9.9625e-07
| PLD006-15398587 | 3423 | 365 | 0.0012316 | 0.001965 | 0.0017378 | 0.0033142 | 0.0010843 | 0.0015666 | 1.4461e-05 | -3.2671e-05 | 0.0016799 | 0.0016944 | 0.0017089 | 0.0017233 | 0.0017378 | 0.0017051 | 0.0016724 | 0.0016398 | 0.0016071 | 0.0015744 | 0.0015417 | 0.0015091 | 0.0014764 | 0.0014437 | 0.0014111 | 0.0013784 | 0.0013457 | 0.001313 | 0.0012804 | 0.0012477 | 3.8548e-05 | -8.7379e-05 | 0.00316 | 0.0031985 | 0.0032371 | 0.0032756 | 0.0033142 | 0.0032268 | 0.0031394 | 0.0030521 | 0.0029647 | 0.0028773 | 0.0027899 | 0.0027025 | 0.0026152 | 0.0025278 | 0.0024404 | 0.002353 | 0.0022656 | 0.0021783 | 0.0020909 | 0.0020035
| PLD006-161891725 | 34 | 34 | 0.00044575 | 0 | 0.00072834 | 0 | 0.00031726 | 0 | 8.0739e-06 | -2.0554e-05 | 0.00069605 | 0.00070412 | 0.00071219 | 0.00072027 | 0.00072834 | 0.00070779 | 0.00068723 | 0.00066668 | 0.00064613 | 0.00062557 | 0.00060502 | 0.00058446 | 0.00056391 | 0.00054336 | 0.0005228 | 0.00050225 | 0.00048169 | 0.00046114 | 0.00044059 | 0.00042003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD006-161892052 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD006-162198254 | 3 | 3 | 6.53e-09 | 0 | 1.14e-08 | 0 | 3.26e-09 | 0 | 1.3914e-10 | -4.07e-10 | 1.0843e-08 | 1.0983e-08 | 1.1122e-08 | 1.1261e-08 | 1.14e-08 | 1.0993e-08 | 1.0586e-08 | 1.0179e-08 | 9.772e-09 | 9.365e-09 | 8.958e-09 | 8.551e-09 | 8.144e-09 | 7.737e-09 | 7.33e-09 | 6.923e-09 | 6.516e-09 | 6.109e-09 | 5.702e-09 | 5.295e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD006-162198466 | 10 | 10 | 0.00034513 | 0 | 0.00040632 | 0 | 0.00036738 | 0 | 1.7484e-06 | -1.9469e-06 | 0.00039933 | 0.00040107 | 0.00040282 | 0.00040457 | 0.00040632 | 0.00040437 | 0.00040243 | 0.00040048 | 0.00039853 | 0.00039659 | 0.00039464 | 0.00039269 | 0.00039074 | 0.0003888 | 0.00038685 | 0.0003849 | 0.00038296 | 0.00038101 | 0.00037906 | 0.00037712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD006-162198656 | 16 | 16 | 0.00064858 | 0 | 0.0010402 | 0 | 0.00051916 | 0 | 1.1189e-05 | -2.6052e-05 | 0.00099544 | 0.0010066 | 0.0010178 | 0.001029 | 0.0010402 | 0.0010141 | 0.0009881 | 0.00096205 | 0.00093599 | 0.00090994 | 0.00088389 | 0.00085784 | 0.00083179 | 0.00080573 | 0.00077968 | 0.00075363 | 0.00072758 | 0.00070153 | 0.00067547 | 0.00064942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD006-162260039 | 5 | 5 | 5.51e-06 | 0 | 1.1e-05 | 0 | 3.86e-06 | 0 | 1.5686e-07 | -3.57e-07 | 1.0373e-05 | 1.0529e-05 | 1.0686e-05 | 1.0843e-05 | 1.1e-05 | 1.0643e-05 | 1.0286e-05 | 9.929e-06 | 9.572e-06 | 9.215e-06 | 8.858e-06 | 8.501e-06 | 8.144e-06 | 7.787e-06 | 7.43e-06 | 7.073e-06 | 6.716e-06 | 6.359e-06 | 6.002e-06 | 5.645e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD006-162260159 | 1 | 1 | 0.0015913 | 0 | 0.0027562 | 0 | 0.0012469 | 0 | 3.3283e-05 | -7.5468e-05 | 0.0026231 | 0.0026564 | 0.0026897 | 0.0027229 | 0.0027562 | 0.0026808 | 0.0026053 | 0.0025298 | 0.0024544 | 0.0023789 | 0.0023034 | 0.0022279 | 0.0021525 | 0.002077 | 0.0020015 | 0.0019261 | 0.0018506 | 0.0017751 | 0.0016997 | 0.0016242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD006-162260296 | 28 | 28 | 0.00014521 | 0 | 0.00017878 | 0 | 0.00013846 | 0 | 9.5906e-07 | -2.0161e-06 | 0.00017494 | 0.0001759 | 0.00017686 | 0.00017782 | 0.00017878 | 0.00017676 | 0.00017475 | 0.00017273 | 0.00017071 | 0.0001687 | 0.00016668 | 0.00016467 | 0.00016265 | 0.00016063 | 0.00015862 | 0.0001566 | 0.00015459 | 0.00015257 | 0.00015055 | 0.00014854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD006-202509382 | 2772 | 2761 | 0.0013965 | 0.00037718 | 0.0015285 | 0.00041806 | 0.0013707 | 0.00036918 | 3.771e-06 | -7.8868e-06 | 0.0015134 | 0.0015172 | 0.0015209 | 0.0015247 | 0.0015285 | 0.0015206 | 0.0015127 | 0.0015048 | 0.0014969 | 0.0014891 | 0.0014812 | 0.0014733 | 0.0014654 | 0.0014575 | 0.0014496 | 0.0014417 | 0.0014338 | 0.001426 | 0.0014181 | 0.0014102 | 1.1678e-06 | -2.4437e-06 | 0.00041339 | 0.00041455 | 0.00041572 | 0.00041689 | 0.00041806 | 0.00041561 | 0.00041317 | 0.00041073 | 0.00040828 | 0.00040584 | 0.00040339 | 0.00040095 | 0.00039851 | 0.00039606 | 0.00039362 | 0.00039118 | 0.00038873 | 0.00038629 | 0.00038385 | 0.0003814
| PLD006-24597156 | 286 | 195 | 0.0020576 | 0.0010749 | 0.0031109 | 0.0016524 | 0.0016386 | 0.00085949 | 3.0092e-05 | -7.3614e-05 | 0.0029905 | 0.0030206 | 0.0030507 | 0.0030808 | 0.0031109 | 0.0030372 | 0.0029636 | 0.00289 | 0.0028164 | 0.0027428 | 0.0026692 | 0.0025956 | 0.0025219 | 0.0024483 | 0.0023747 | 0.0023011 | 0.0022275 | 0.0021539 | 0.0020803 | 0.0020066 | 1.6501e-05 | -3.9646e-05 | 0.0015864 | 0.0016029 | 0.0016194 | 0.0016359 | 0.0016524 | 0.0016128 | 0.0015731 | 0.0015335 | 0.0014938 | 0.0014542 | 0.0014145 | 0.0013749 | 0.0013352 | 0.0012956 | 0.001256 | 0.0012163 | 0.0011767 | 0.001137 | 0.0010974 | 0.0010577
| RCT011-15430907 | 811 | 811 | 0.018082 | 0 | 0.022725 | 0 | 0.023091 | 0 | 0.00013264 | 1.831e-05 | 0.022194 | 0.022327 | 0.022459 | 0.022592 | 0.022725 | 0.022743 | 0.022761 | 0.022779 | 0.022798 | 0.022816 | 0.022834 | 0.022853 | 0.022871 | 0.022889 | 0.022908 | 0.022926 | 0.022944 | 0.022963 | 0.022981 | 0.022999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT012-109224809 | 1 | 1 | 4.61e-05 | 0 | 6.19e-05 | 0 | 6.84e-05 | 0 | 4.5143e-07 | 3.25e-07 | 6.0094e-05 | 6.0546e-05 | 6.0997e-05 | 6.1449e-05 | 6.19e-05 | 6.2225e-05 | 6.255e-05 | 6.2875e-05 | 6.32e-05 | 6.3525e-05 | 6.385e-05 | 6.4175e-05 | 6.45e-05 | 6.4825e-05 | 6.515e-05 | 6.5475e-05 | 6.58e-05 | 6.6125e-05 | 6.645e-05 | 6.6775e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT013-15430798 | 632 | 208 | 0.0098986 | 0.0025593 | 0.012665 | 0.0033411 | 0.013044 | 0.003518 | 7.9029e-05 | 1.8957e-05 | 0.012348 | 0.012427 | 0.012507 | 0.012586 | 0.012665 | 0.012684 | 0.012702 | 0.012721 | 0.01274 | 0.012759 | 0.012778 | 0.012797 | 0.012816 | 0.012835 | 0.012854 | 0.012873 | 0.012892 | 0.012911 | 0.01293 | 0.012949 | 2.2338e-05 | 8.843e-06 | 0.0032518 | 0.0032741 | 0.0032965 | 0.0033188 | 0.0033411 | 0.00335 | 0.0033588 | 0.0033677 | 0.0033765 | 0.0033854 | 0.0033942 | 0.003403 | 0.0034119 | 0.0034207 | 0.0034296 | 0.0034384 | 0.0034473 | 0.0034561 | 0.0034649 | 0.0034738
| RCT013-24605168 | 150 | 150 | 0.056192 | 0 | 0.068449 | 0 | 0.067102 | 0 | 0.00035017 | -6.7323e-05 | 0.067048 | 0.067398 | 0.067748 | 0.068098 | 0.068449 | 0.068381 | 0.068314 | 0.068247 | 0.068179 | 0.068112 | 0.068045 | 0.067977 | 0.06791 | 0.067843 | 0.067775 | 0.067708 | 0.067641 | 0.067573 | 0.067506 | 0.067439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT013-24605182 | 274 | 274 | 0.0055374 | 0 | 0.0058519 | 0 | 0.0055999 | 0 | 8.986e-06 | -1.2599e-05 | 0.0058159 | 0.0058249 | 0.0058339 | 0.0058429 | 0.0058519 | 0.0058393 | 0.0058267 | 0.0058141 | 0.0058015 | 0.0057889 | 0.0057763 | 0.0057637 | 0.0057511 | 0.0057385 | 0.0057259 | 0.0057133 | 0.0057007 | 0.0056881 | 0.0056755 | 0.0056629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT014-15430846 | 351 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT014-24605126 | 119 | 119 | 3.68e-05 | 0 | 4.83e-05 | 0 | 5.01e-05 | 0 | 3.2857e-07 | 9e-08 | 4.6986e-05 | 4.7314e-05 | 4.7643e-05 | 4.7971e-05 | 4.83e-05 | 4.839e-05 | 4.848e-05 | 4.857e-05 | 4.866e-05 | 4.875e-05 | 4.884e-05 | 4.893e-05 | 4.902e-05 | 4.911e-05 | 4.92e-05 | 4.929e-05 | 4.938e-05 | 4.947e-05 | 4.956e-05 | 4.965e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT014-24611042 | 212 | 93 | 0.014206 | 1.27e-05 | 0.018297 | 1.69e-05 | 0.018894 | 1.79e-05 | 0.00011689 | 2.9821e-05 | 0.01783 | 0.017947 | 0.018064 | 0.01818 | 0.018297 | 0.018327 | 0.018357 | 0.018387 | 0.018417 | 0.018446 | 0.018476 | 0.018506 | 0.018536 | 0.018566 | 0.018596 | 0.018625 | 0.018655 | 0.018685 | 0.018715 | 0.018745 | 1.2e-07 | 5e-08 | 1.642e-05 | 1.654e-05 | 1.666e-05 | 1.678e-05 | 1.69e-05 | 1.695e-05 | 1.7e-05 | 1.705e-05 | 1.71e-05 | 1.715e-05 | 1.72e-05 | 1.725e-05 | 1.73e-05 | 1.735e-05 | 1.74e-05 | 1.745e-05 | 1.75e-05 | 1.755e-05 | 1.76e-05 | 1.765e-05
| RCT015-15430944 | 20 | 20 | 0.0020968 | 0 | 0.0028052 | 0 | 0.0030241 | 0 | 2.024e-05 | 1.0944e-05 | 0.0027243 | 0.0027445 | 0.0027647 | 0.002785 | 0.0028052 | 0.0028162 | 0.0028271 | 0.0028381 | 0.002849 | 0.0028599 | 0.0028709 | 0.0028818 | 0.0028928 | 0.0029037 | 0.0029147 | 0.0029256 | 0.0029366 | 0.0029475 | 0.0029584 | 0.0029694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT021-15430691 | 655 | 590 | 0.0058524 | 0.00038525 | 0.0076339 | 0.00051187 | 0.0080258 | 0.00054787 | 5.0902e-05 | 1.9595e-05 | 0.0074303 | 0.0074812 | 0.0075321 | 0.007583 | 0.0076339 | 0.0076535 | 0.0076731 | 0.0076927 | 0.0077123 | 0.0077319 | 0.0077515 | 0.0077711 | 0.0077907 | 0.0078103 | 0.0078299 | 0.0078495 | 0.0078691 | 0.0078887 | 0.0079083 | 0.0079279 | 3.6176e-06 | 1.8001e-06 | 0.0004974 | 0.00050102 | 0.00050464 | 0.00050825 | 0.00051187 | 0.00051367 | 0.00051547 | 0.00051727 | 0.00051907 | 0.00052087 | 0.00052267 | 0.00052447 | 0.00052627 | 0.00052807 | 0.00052987 | 0.00053167 | 0.00053347 | 0.00053527 | 0.00053707 | 0.00053887
| RCT021-24612845 | 65 | 65 | 0.0010156 | 0 | 0.0012893 | 0 | 0.0013356 | 0 | 7.8219e-06 | 2.311e-06 | 0.0012581 | 0.0012659 | 0.0012737 | 0.0012815 | 0.0012893 | 0.0012917 | 0.001294 | 0.0012963 | 0.0012986 | 0.0013009 | 0.0013032 | 0.0013055 | 0.0013078 | 0.0013101 | 0.0013124 | 0.0013148 | 0.0013171 | 0.0013194 | 0.0013217 | 0.001324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT022-109224755 | 838 | 763 | 0.0052477 | 0.00021239 | 0.0066129 | 0.00027846 | 0.0068334 | 0.0002997 | 3.9003e-05 | 1.1027e-05 | 0.0064568 | 0.0064959 | 0.0065349 | 0.0065739 | 0.0066129 | 0.0066239 | 0.0066349 | 0.0066459 | 0.006657 | 0.006668 | 0.006679 | 0.0066901 | 0.0067011 | 0.0067121 | 0.0067231 | 0.0067342 | 0.0067452 | 0.0067562 | 0.0067672 | 0.0067783 | 1.8879e-06 | 1.0619e-06 | 0.00027091 | 0.0002728 | 0.00027469 | 0.00027658 | 0.00027847 | 0.00027953 | 0.00028059 | 0.00028165 | 0.00028271 | 0.00028377 | 0.00028484 | 0.0002859 | 0.00028696 | 0.00028802 | 0.00028908 | 0.00029015 | 0.00029121 | 0.00029227 | 0.00029333 | 0.00029439
| RCT022-160254089 | 4 | 4 | 0.00072173 | 0 | 0.000931 | 0 | 0.00097311 | 0 | 5.9792e-06 | 2.1056e-06 | 0.00090709 | 0.00091306 | 0.00091904 | 0.00092502 | 0.000931 | 0.00093311 | 0.00093521 | 0.00093732 | 0.00093942 | 0.00094153 | 0.00094364 | 0.00094574 | 0.00094785 | 0.00094995 | 0.00095206 | 0.00095416 | 0.00095627 | 0.00095837 | 0.00096048 | 0.00096259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT022-160254223 | 5 | 5 | 0.0033731 | 0 | 0.0044859 | 0 | 0.0044918 | 0 | 3.1793e-05 | 2.995e-07 | 0.0043587 | 0.0043905 | 0.0044223 | 0.0044541 | 0.0044859 | 0.0044862 | 0.0044865 | 0.0044868 | 0.0044871 | 0.0044874 | 0.0044877 | 0.004488 | 0.0044883 | 0.0044886 | 0.0044889 | 0.0044892 | 0.0044895 | 0.0044897 | 0.00449 | 0.0044903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT022-160652528 | 21 | 21 | 4.91e-07 | 0 | 6.15e-07 | 0 | 6.46e-07 | 0 | 3.5429e-09 | 1.55e-09 | 6.0083e-07 | 6.0437e-07 | 6.0791e-07 | 6.1146e-07 | 6.15e-07 | 6.1655e-07 | 6.181e-07 | 6.1965e-07 | 6.212e-07 | 6.2275e-07 | 6.243e-07 | 6.2585e-07 | 6.274e-07 | 6.2895e-07 | 6.305e-07 | 6.3205e-07 | 6.336e-07 | 6.3515e-07 | 6.367e-07 | 6.3825e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT022-162765375 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT022-187104623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT022-201142435 | 30 | 21 | 0.0090691 | 0.0018564 | 0.010877 | 0.0023255 | 0.010783 | 0.0023822 | 5.1644e-05 | -4.7001e-06 | 0.01067 | 0.010722 | 0.010773 | 0.010825 | 0.010877 | 0.010872 | 0.010867 | 0.010863 | 0.010858 | 0.010853 | 0.010848 | 0.010844 | 0.010839 | 0.010834 | 0.01083 | 0.010825 | 0.01082 | 0.010816 | 0.010811 | 0.010806 | 1.3402e-05 | 2.8347e-06 | 0.0022719 | 0.0022853 | 0.0022987 | 0.0023121 | 0.0023255 | 0.0023283 | 0.0023311 | 0.002334 | 0.0023368 | 0.0023396 | 0.0023425 | 0.0023453 | 0.0023481 | 0.002351 | 0.0023538 | 0.0023566 | 0.0023595 | 0.0023623 | 0.0023652 | 0.002368
| RCT022-74940140 | 74 | 23 | 0.00015677 | 0.0001074 | 0.00020156 | 0.00013825 | 0.0002154 | 0.00014801 | 1.2795e-06 | 6.9205e-07 | 0.00019644 | 0.00019772 | 0.000199 | 0.00020028 | 0.00020156 | 0.00020225 | 0.00020294 | 0.00020363 | 0.00020433 | 0.00020502 | 0.00020571 | 0.0002064 | 0.00020709 | 0.00020779 | 0.00020848 | 0.00020917 | 0.00020986 | 0.00021055 | 0.00021125 | 0.00021194 | 8.8149e-07 | 4.882e-07 | 0.00013472 | 0.0001356 | 0.00013649 | 0.00013737 | 0.00013825 | 0.00013874 | 0.00013922 | 0.00013971 | 0.0001402 | 0.00014069 | 0.00014118 | 0.00014167 | 0.00014215 | 0.00014264 | 0.00014313 | 0.00014362 | 0.00014411 | 0.00014459 | 0.00014508 | 0.00014557
| RCT023-15430737 | 2209 | 1613 | 0.00035148 | 4.43e-05 | 0.00044546 | 5.8e-05 | 0.00046145 | 6.25e-05 | 2.685e-06 | 7.997e-07 | 0.00043472 | 0.0004374 | 0.00044009 | 0.00044277 | 0.00044546 | 0.00044626 | 0.00044706 | 0.00044786 | 0.00044866 | 0.00044946 | 0.00045026 | 0.00045106 | 0.00045186 | 0.00045266 | 0.00045346 | 0.00045426 | 0.00045506 | 0.00045586 | 0.00045666 | 0.00045746 | 3.9143e-07 | 2.25e-07 | 5.6434e-05 | 5.6826e-05 | 5.7217e-05 | 5.7609e-05 | 5.8e-05 | 5.8225e-05 | 5.845e-05 | 5.8675e-05 | 5.89e-05 | 5.9125e-05 | 5.935e-05 | 5.9575e-05 | 5.98e-05 | 6.0025e-05 | 6.025e-05 | 6.0475e-05 | 6.07e-05 | 6.0925e-05 | 6.115e-05 | 6.1375e-05
| RCT023-159364712 | 10 | 10 | 0.00032473 | 0 | 0.00040678 | 0 | 0.00040346 | 0 | 2.3442e-06 | -1.66e-07 | 0.0003974 | 0.00039974 | 0.00040209 | 0.00040443 | 0.00040678 | 0.00040661 | 0.00040644 | 0.00040628 | 0.00040611 | 0.00040595 | 0.00040578 | 0.00040561 | 0.00040545 | 0.00040528 | 0.00040512 | 0.00040495 | 0.00040478 | 0.00040462 | 0.00040445 | 0.00040429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-159364841 | 28 | 28 | 0.00062097 | 0 | 0.00075536 | 0 | 0.0007499 | 0 | 3.8397e-06 | -2.728e-07 | 0.00074 | 0.00074384 | 0.00074768 | 0.00075152 | 0.00075536 | 0.00075509 | 0.00075481 | 0.00075454 | 0.00075427 | 0.00075399 | 0.00075372 | 0.00075345 | 0.00075318 | 0.0007529 | 0.00075263 | 0.00075236 | 0.00075208 | 0.00075181 | 0.00075154 | 0.00075127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-159364971 | 28 | 28 | 0.00047549 | 0 | 0.00061622 | 0 | 0.00061894 | 0 | 4.0208e-06 | 1.362e-07 | 0.00060014 | 0.00060416 | 0.00060818 | 0.0006122 | 0.00061622 | 0.00061636 | 0.00061649 | 0.00061663 | 0.00061676 | 0.0006169 | 0.00061704 | 0.00061717 | 0.00061731 | 0.00061745 | 0.00061758 | 0.00061772 | 0.00061785 | 0.00061799 | 0.00061813 | 0.00061826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-159365116 | 12 | 12 | 0.00010377 | 0 | 0.00013382 | 0 | 0.0001333 | 0 | 8.586e-07 | -2.63e-08 | 0.00013039 | 0.00013125 | 0.0001321 | 0.00013296 | 0.00013382 | 0.0001338 | 0.00013377 | 0.00013374 | 0.00013372 | 0.00013369 | 0.00013366 | 0.00013364 | 0.00013361 | 0.00013359 | 0.00013356 | 0.00013353 | 0.00013351 | 0.00013348 | 0.00013345 | 0.00013343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-159365240 | 11 | 11 | 3.32e-05 | 0 | 4.14e-05 | 0 | 4.18e-05 | 0 | 2.3429e-07 | 2e-08 | 4.0463e-05 | 4.0697e-05 | 4.0931e-05 | 4.1166e-05 | 4.14e-05 | 4.142e-05 | 4.144e-05 | 4.146e-05 | 4.148e-05 | 4.15e-05 | 4.152e-05 | 4.154e-05 | 4.156e-05 | 4.158e-05 | 4.16e-05 | 4.162e-05 | 4.164e-05 | 4.166e-05 | 4.168e-05 | 4.17e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-159365351 | 21 | 21 | 9.38e-05 | 0 | 0.00011691 | 0 | 0.0001137 | 0 | 6.602e-07 | -1.606e-07 | 0.00011427 | 0.00011493 | 0.00011559 | 0.00011625 | 0.00011691 | 0.00011675 | 0.00011659 | 0.00011643 | 0.00011626 | 0.0001161 | 0.00011594 | 0.00011578 | 0.00011562 | 0.00011546 | 0.0001153 | 0.00011514 | 0.00011498 | 0.00011482 | 0.00011466 | 0.0001145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-159365509 | 2 | 2 | 6.38e-07 | 0 | 8.37e-07 | 0 | 8.94e-07 | 0 | 5.6857e-09 | 2.85e-09 | 8.1426e-07 | 8.1994e-07 | 8.2563e-07 | 8.3131e-07 | 8.37e-07 | 8.3985e-07 | 8.427e-07 | 8.4555e-07 | 8.484e-07 | 8.5125e-07 | 8.541e-07 | 8.5695e-07 | 8.598e-07 | 8.6265e-07 | 8.655e-07 | 8.6835e-07 | 8.712e-07 | 8.7405e-07 | 8.769e-07 | 8.7975e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-160652906 | 4 | 4 | 0.00036715 | 0 | 0.00047444 | 0 | 0.00047067 | 0 | 3.0655e-06 | -1.8815e-07 | 0.00046218 | 0.00046524 | 0.00046831 | 0.00047137 | 0.00047444 | 0.00047425 | 0.00047406 | 0.00047387 | 0.00047369 | 0.0004735 | 0.00047331 | 0.00047312 | 0.00047293 | 0.00047274 | 0.00047256 | 0.00047237 | 0.00047218 | 0.00047199 | 0.0004718 | 0.00047162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-162905845 | 10 | 10 | 0.0041349 | 0 | 0.0052921 | 0 | 0.0053275 | 0 | 3.3062e-05 | 1.7699e-06 | 0.0051598 | 0.0051929 | 0.005226 | 0.005259 | 0.0052921 | 0.0052938 | 0.0052956 | 0.0052974 | 0.0052992 | 0.0053009 | 0.0053027 | 0.0053045 | 0.0053062 | 0.005308 | 0.0053098 | 0.0053115 | 0.0053133 | 0.0053151 | 0.0053169 | 0.0053186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-162905960 | 3 | 3 | 0.00029885 | 0 | 0.00039195 | 0 | 0.00038278 | 0 | 2.6602e-06 | -4.5865e-07 | 0.00038131 | 0.00038397 | 0.00038663 | 0.00038929 | 0.00039195 | 0.00039149 | 0.00039103 | 0.00039058 | 0.00039012 | 0.00038966 | 0.0003892 | 0.00038874 | 0.00038828 | 0.00038782 | 0.00038736 | 0.00038691 | 0.00038645 | 0.00038599 | 0.00038553 | 0.00038507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-162906075 | 32 | 32 | 0.0012199 | 0 | 0.00156 | 0 | 0.0015786 | 0 | 9.718e-06 | 9.329e-07 | 0.0015211 | 0.0015308 | 0.0015405 | 0.0015503 | 0.00156 | 0.0015609 | 0.0015618 | 0.0015628 | 0.0015637 | 0.0015646 | 0.0015656 | 0.0015665 | 0.0015674 | 0.0015684 | 0.0015693 | 0.0015702 | 0.0015712 | 0.0015721 | 0.001573 | 0.001574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-24605614 | 285 | 24 | 0.0021286 | 7.98e-05 | 0.0026858 | 9.72e-05 | 0.0027628 | 9.48e-05 | 1.5921e-05 | 3.8475e-06 | 0.0026221 | 0.0026381 | 0.002654 | 0.0026699 | 0.0026858 | 0.0026897 | 0.0026935 | 0.0026974 | 0.0027012 | 0.0027051 | 0.0027089 | 0.0027128 | 0.0027166 | 0.0027205 | 0.0027243 | 0.0027281 | 0.002732 | 0.0027358 | 0.0027397 | 0.0027435 | 4.9714e-07 | -1.2e-07 | 9.5211e-05 | 9.5709e-05 | 9.6206e-05 | 9.6703e-05 | 9.72e-05 | 9.708e-05 | 9.696e-05 | 9.684e-05 | 9.672e-05 | 9.66e-05 | 9.648e-05 | 9.636e-05 | 9.624e-05 | 9.612e-05 | 9.6e-05 | 9.588e-05 | 9.576e-05 | 9.564e-05 | 9.552e-05 | 9.54e-05
| RCT023-24605628 | 311 | 311 | 0.002594 | 0 | 0.0033544 | 0 | 0.0035093 | 0 | 2.1727e-05 | 7.7434e-06 | 0.0032675 | 0.0032892 | 0.0033109 | 0.0033327 | 0.0033544 | 0.0033621 | 0.0033699 | 0.0033776 | 0.0033854 | 0.0033931 | 0.0034009 | 0.0034086 | 0.0034163 | 0.0034241 | 0.0034318 | 0.0034396 | 0.0034473 | 0.0034551 | 0.0034628 | 0.0034706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-24606802 | 150 | 35 | 0.0046742 | 0.0020735 | 0.0056679 | 0.0025412 | 0.005578 | 0.0025345 | 2.8393e-05 | -4.4948e-06 | 0.0055544 | 0.0055828 | 0.0056112 | 0.0056395 | 0.0056679 | 0.0056634 | 0.005659 | 0.0056545 | 0.00565 | 0.0056455 | 0.005641 | 0.0056365 | 0.005632 | 0.0056275 | 0.005623 | 0.0056185 | 0.005614 | 0.0056095 | 0.005605 | 0.0056005 | 1.3363e-05 | -3.3405e-07 | 0.0024878 | 0.0025011 | 0.0025145 | 0.0025279 | 0.0025412 | 0.0025409 | 0.0025405 | 0.0025402 | 0.0025399 | 0.0025395 | 0.0025392 | 0.0025389 | 0.0025385 | 0.0025382 | 0.0025379 | 0.0025375 | 0.0025372 | 0.0025369 | 0.0025365 | 0.0025362
| RCT023-24611339 | 261 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-85530600 | 248 | 58 | 4.32e-05 | 0.00012375 | 5.48e-05 | 0.00015727 | 5.75e-05 | 0.00016543 | 3.3143e-07 | 1.35e-07 | 5.3474e-05 | 5.3806e-05 | 5.4137e-05 | 5.4469e-05 | 5.48e-05 | 5.4935e-05 | 5.507e-05 | 5.5205e-05 | 5.534e-05 | 5.5475e-05 | 5.561e-05 | 5.5745e-05 | 5.588e-05 | 5.6015e-05 | 5.615e-05 | 5.6285e-05 | 5.642e-05 | 5.6555e-05 | 5.669e-05 | 5.6825e-05 | 9.5757e-07 | 4.0815e-07 | 0.00015344 | 0.0001544 | 0.00015535 | 0.00015631 | 0.00015727 | 0.00015768 | 0.00015809 | 0.00015849 | 0.0001589 | 0.00015931 | 0.00015972 | 0.00016013 | 0.00016054 | 0.00016094 | 0.00016135 | 0.00016176 | 0.00016217 | 0.00016258 | 0.00016298 | 0.00016339
| RVL001-15418899 | 858 | 1 | 0 | 4.71e-05 | 0 | 6.76e-05 | 0 | 6.76e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8571e-07 | 0 | 6.5257e-05 | 6.5843e-05 | 6.6429e-05 | 6.7014e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05
| RVL001-15418912 | 857 | 857 | 0.010892 | 0 | 0.014342 | 0 | 0.013849 | 0 | 9.8584e-05 | -2.4628e-05 | 0.013948 | 0.014046 | 0.014145 | 0.014243 | 0.014342 | 0.014317 | 0.014293 | 0.014268 | 0.014243 | 0.014219 | 0.014194 | 0.01417 | 0.014145 | 0.01412 | 0.014096 | 0.014071 | 0.014046 | 0.014022 | 0.013997 | 0.013973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RVL004-15418812 | 231 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RVL004-15418838 | 230 | 230 | 0.007708 | 0 | 0.009715 | 0 | 0.0092759 | 0 | 5.7344e-05 | -2.1954e-05 | 0.0094857 | 0.009543 | 0.0096003 | 0.0096577 | 0.009715 | 0.0096931 | 0.0096711 | 0.0096492 | 0.0096272 | 0.0096053 | 0.0095833 | 0.0095614 | 0.0095394 | 0.0095174 | 0.0094955 | 0.0094735 | 0.0094516 | 0.0094296 | 0.0094077 | 0.0093857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RVL004-162771521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RVL006-15418762 | 585 | 585 | 0.00345 | 0 | 0.0044139 | 0 | 0.0042493 | 0 | 2.7541e-05 | -8.2291e-06 | 0.0043038 | 0.0043313 | 0.0043588 | 0.0043864 | 0.0044139 | 0.0044057 | 0.0043975 | 0.0043892 | 0.004381 | 0.0043728 | 0.0043646 | 0.0043563 | 0.0043481 | 0.0043399 | 0.0043316 | 0.0043234 | 0.0043152 | 0.0043069 | 0.0042987 | 0.0042905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RVL008-15418862 | 215 | 82 | 0.001278 | 0.00088993 | 0.0017377 | 0.0012341 | 0.0017166 | 0.0012381 | 1.3134e-05 | -1.0549e-06 | 0.0016851 | 0.0016983 | 0.0017114 | 0.0017245 | 0.0017377 | 0.0017366 | 0.0017355 | 0.0017345 | 0.0017334 | 0.0017324 | 0.0017313 | 0.0017303 | 0.0017292 | 0.0017282 | 0.0017271 | 0.0017261 | 0.001725 | 0.0017239 | 0.0017229 | 0.0017218 | 9.8322e-06 | 2.0105e-07 | 0.0011947 | 0.0012046 | 0.0012144 | 0.0012242 | 0.0012341 | 0.0012343 | 0.0012345 | 0.0012347 | 0.0012349 | 0.0012351 | 0.0012353 | 0.0012355 | 0.0012357 | 0.0012359 | 0.0012361 | 0.0012363 | 0.0012365 | 0.0012367 | 0.0012369 | 0.0012371
| RVL008-24613925 | 133 | 133 | 0.006495 | 0 | 0.008802 | 0 | 0.0087144 | 0 | 6.5915e-05 | -4.38e-06 | 0.0085384 | 0.0086043 | 0.0086702 | 0.0087361 | 0.008802 | 0.0087976 | 0.0087933 | 0.0087889 | 0.0087845 | 0.0087801 | 0.0087757 | 0.0087714 | 0.008767 | 0.0087626 | 0.0087582 | 0.0087538 | 0.0087495 | 0.0087451 | 0.0087407 | 0.0087363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA001-15410791 | 1932 | 1918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA001-15410802 | 14 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA001-15411152 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA002-15410828 | 2670 | 1563 | 4.02e-05 | 0 | 5.45e-05 | 0 | 5.56e-05 | 0 | 4.0857e-07 | 5.5e-08 | 5.2866e-05 | 5.3274e-05 | 5.3683e-05 | 5.4091e-05 | 5.45e-05 | 5.4555e-05 | 5.461e-05 | 5.4665e-05 | 5.472e-05 | 5.4775e-05 | 5.483e-05 | 5.4885e-05 | 5.494e-05 | 5.4995e-05 | 5.505e-05 | 5.5105e-05 | 5.516e-05 | 5.5215e-05 | 5.527e-05 | 5.5325e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA002-24612976 | 1107 | 1107 | 6.62e-05 | 0 | 8.93e-05 | 0 | 9.12e-05 | 0 | 6.6e-07 | 9.5e-08 | 8.666e-05 | 8.732e-05 | 8.798e-05 | 8.864e-05 | 8.93e-05 | 8.9395e-05 | 8.949e-05 | 8.9585e-05 | 8.968e-05 | 8.9775e-05 | 8.987e-05 | 8.9965e-05 | 9.006e-05 | 9.0155e-05 | 9.025e-05 | 9.0345e-05 | 9.044e-05 | 9.0535e-05 | 9.063e-05 | 9.0725e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA003-15410891 | 3078 | 587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA003-24613059 | 2491 | 2491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA004-15410928 | 2655 | 2655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA005-15411004 | 3711 | 2152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA005-24614201 | 1559 | 1559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA006-15411054 | 2177 | 1323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA006-24612920 | 854 | 854 | 0.0012434 | 0 | 0.0017706 | 0 | 0.0017606 | 0 | 1.5062e-05 | -4.9985e-07 | 0.0017103 | 0.0017254 | 0.0017404 | 0.0017555 | 0.0017706 | 0.0017701 | 0.0017696 | 0.0017691 | 0.0017686 | 0.0017681 | 0.0017676 | 0.0017671 | 0.0017666 | 0.0017661 | 0.0017656 | 0.0017651 | 0.0017646 | 0.0017641 | 0.0017636 | 0.0017631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA007-111739222 | 3763 | 3763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA007-15411091 | 7104 | 3341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA009-15436559 | 5448 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA009-15436572 | 5435 | 1878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA009-76846685 | 3557 | 3557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA010-15436583 | 2687 | 482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA010-24613811 | 2205 | 2205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA011-15436594 | 4065 | 4065 | 0.0041058 | 0 | 0.0053675 | 0 | 0.0055766 | 0 | 3.6049e-05 | 1.0455e-05 | 0.0052233 | 0.0052594 | 0.0052954 | 0.0053315 | 0.0053675 | 0.005378 | 0.0053884 | 0.0053989 | 0.0054093 | 0.0054198 | 0.0054303 | 0.0054407 | 0.0054512 | 0.0054616 | 0.0054721 | 0.0054825 | 0.005493 | 0.0055034 | 0.0055139 | 0.0055244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA012-15437079 | 272 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-15428689 | 342 | 177 | 0.0084205 | 0.0045858 | 0.012122 | 0.0067786 | 0.013168 | 0.0074801 | 0.00010576 | 5.2271e-05 | 0.011699 | 0.011805 | 0.011911 | 0.012016 | 0.012122 | 0.012174 | 0.012227 | 0.012279 | 0.012331 | 0.012383 | 0.012436 | 0.012488 | 0.01254 | 0.012593 | 0.012645 | 0.012697 | 0.012749 | 0.012802 | 0.012854 | 0.012906 | 6.2651e-05 | 3.5073e-05 | 0.006528 | 0.0065906 | 0.0066533 | 0.006716 | 0.0067786 | 0.0068137 | 0.0068487 | 0.0068838 | 0.0069189 | 0.006954 | 0.006989 | 0.0070241 | 0.0070592 | 0.0070943 | 0.0071293 | 0.0071644 | 0.0071995 | 0.0072346 | 0.0072696 | 0.0073047
| SHL001-155492469 | 0 | 0 | 6.77e-05 | 0 | 9.8e-05 | 0 | 0.00010694 | 0 | 8.6571e-07 | 4.471e-07 | 9.4537e-05 | 9.5403e-05 | 9.6269e-05 | 9.7134e-05 | 9.8e-05 | 9.8447e-05 | 9.8894e-05 | 9.9341e-05 | 9.9788e-05 | 0.00010024 | 0.00010068 | 0.00010113 | 0.00010158 | 0.00010202 | 0.00010247 | 0.00010292 | 0.00010337 | 0.00010381 | 0.00010426 | 0.00010471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-160435720 | 19 | 19 | 0.0014769 | 0 | 0.0020934 | 0 | 0.0022781 | 0 | 1.7613e-05 | 9.2387e-06 | 0.0020229 | 0.0020405 | 0.0020581 | 0.0020757 | 0.0020934 | 0.0021026 | 0.0021118 | 0.0021211 | 0.0021303 | 0.0021395 | 0.0021488 | 0.002158 | 0.0021673 | 0.0021765 | 0.0021857 | 0.002195 | 0.0022042 | 0.0022135 | 0.0022227 | 0.0022319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-160435873 | 32 | 32 | 0.003828 | 0 | 0.0053842 | 0 | 0.0059467 | 0 | 4.4462e-05 | 2.8127e-05 | 0.0052064 | 0.0052508 | 0.0052953 | 0.0053397 | 0.0053842 | 0.0054123 | 0.0054405 | 0.0054686 | 0.0054967 | 0.0055248 | 0.005553 | 0.0055811 | 0.0056092 | 0.0056373 | 0.0056655 | 0.0056936 | 0.0057217 | 0.0057498 | 0.005778 | 0.0058061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-160436010 | 27 | 27 | 0.0037569 | 0 | 0.0056647 | 0 | 0.0061824 | 0 | 5.4508e-05 | 2.5884e-05 | 0.0054467 | 0.0055012 | 0.0055557 | 0.0056102 | 0.0056647 | 0.0056906 | 0.0057165 | 0.0057424 | 0.0057682 | 0.0057941 | 0.00582 | 0.0058459 | 0.0058718 | 0.0058977 | 0.0059235 | 0.0059494 | 0.0059753 | 0.0060012 | 0.0060271 | 0.006053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-160450736 | 6 | 6 | 3.93e-05 | 0 | 5.77e-05 | 0 | 5.98e-05 | 0 | 5.2571e-07 | 1.05e-07 | 5.5597e-05 | 5.6123e-05 | 5.6649e-05 | 5.7174e-05 | 5.77e-05 | 5.7805e-05 | 5.791e-05 | 5.8015e-05 | 5.812e-05 | 5.8225e-05 | 5.833e-05 | 5.8435e-05 | 5.854e-05 | 5.8645e-05 | 5.875e-05 | 5.8855e-05 | 5.896e-05 | 5.9065e-05 | 5.917e-05 | 5.9275e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-160450820 | 7 | 7 | 0.00023969 | 0 | 0.00035618 | 0 | 0.00036502 | 0 | 3.3285e-06 | 4.416e-07 | 0.00034287 | 0.0003462 | 0.00034953 | 0.00035285 | 0.00035618 | 0.00035662 | 0.00035707 | 0.00035751 | 0.00035795 | 0.00035839 | 0.00035883 | 0.00035927 | 0.00035972 | 0.00036016 | 0.0003606 | 0.00036104 | 0.00036148 | 0.00036192 | 0.00036237 | 0.00036281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-160491672 | 15 | 15 | 0.0035132 | 0 | 0.003559 | 0 | 0.0035387 | 0 | 1.3058e-06 | -1.0123e-06 | 0.0035537 | 0.003555 | 0.0035563 | 0.0035576 | 0.003559 | 0.0035579 | 0.0035569 | 0.0035559 | 0.0035549 | 0.0035539 | 0.0035529 | 0.0035519 | 0.0035509 | 0.0035498 | 0.0035488 | 0.0035478 | 0.0035468 | 0.0035458 | 0.0035448 | 0.0035438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-160682032 | 18 | 18 | 0.0018515 | 0 | 0.0025863 | 0 | 0.0028449 | 0 | 2.0993e-05 | 1.293e-05 | 0.0025023 | 0.0025233 | 0.0025443 | 0.0025653 | 0.0025863 | 0.0025992 | 0.0026122 | 0.0026251 | 0.002638 | 0.002651 | 0.0026639 | 0.0026768 | 0.0026897 | 0.0027027 | 0.0027156 | 0.0027285 | 0.0027415 | 0.0027544 | 0.0027673 | 0.0027803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-162130935 | 3 | 3 | 3e-05 | 0 | 4.29e-05 | 0 | 4.75e-05 | 0 | 3.6857e-07 | 2.3e-07 | 4.1426e-05 | 4.1794e-05 | 4.2163e-05 | 4.2531e-05 | 4.29e-05 | 4.313e-05 | 4.336e-05 | 4.359e-05 | 4.382e-05 | 4.405e-05 | 4.428e-05 | 4.451e-05 | 4.474e-05 | 4.497e-05 | 4.52e-05 | 4.543e-05 | 4.566e-05 | 4.589e-05 | 4.612e-05 | 4.635e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-162641927 | 4 | 4 | 3.88e-05 | 0 | 5.86e-05 | 0 | 6.18e-05 | 0 | 5.6571e-07 | 1.6e-07 | 5.6337e-05 | 5.6903e-05 | 5.7469e-05 | 5.8034e-05 | 5.86e-05 | 5.876e-05 | 5.892e-05 | 5.908e-05 | 5.924e-05 | 5.94e-05 | 5.956e-05 | 5.972e-05 | 5.988e-05 | 6.004e-05 | 6.02e-05 | 6.036e-05 | 6.052e-05 | 6.068e-05 | 6.084e-05 | 6.1e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-162662602 | 13 | 13 | 0.0020543 | 0 | 0.0029065 | 0 | 0.0031865 | 0 | 2.435e-05 | 1.4001e-05 | 0.0028091 | 0.0028335 | 0.0028578 | 0.0028822 | 0.0029065 | 0.0029205 | 0.0029345 | 0.0029485 | 0.0029625 | 0.0029765 | 0.0029905 | 0.0030045 | 0.0030185 | 0.0030325 | 0.0030465 | 0.0030605 | 0.0030745 | 0.0030885 | 0.0031025 | 0.0031165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-162662856 | 16 | 16 | 0.0039385 | 0 | 0.0057789 | 0 | 0.006014 | 0 | 5.2584e-05 | 1.1752e-05 | 0.0055686 | 0.0056212 | 0.0056738 | 0.0057263 | 0.0057789 | 0.0057907 | 0.0058024 | 0.0058142 | 0.0058259 | 0.0058377 | 0.0058494 | 0.0058612 | 0.0058729 | 0.0058847 | 0.0058965 | 0.0059082 | 0.00592 | 0.0059317 | 0.0059435 | 0.0059552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-162663030 | 5 | 5 | 0.0018921 | 0 | 0.0027425 | 0 | 0.0028911 | 0 | 2.4296e-05 | 7.4339e-06 | 0.0026453 | 0.0026696 | 0.0026939 | 0.0027182 | 0.0027425 | 0.0027499 | 0.0027573 | 0.0027648 | 0.0027722 | 0.0027796 | 0.0027871 | 0.0027945 | 0.0028019 | 0.0028094 | 0.0028168 | 0.0028242 | 0.0028317 | 0.0028391 | 0.0028465 | 0.002854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-162760066 | 0 | 0 | 0.00012051 | 0 | 0.00017787 | 0 | 0.00018888 | 0 | 1.6388e-06 | 5.5045e-07 | 0.00017132 | 0.00017295 | 0.00017459 | 0.00017623 | 0.00017787 | 0.00017842 | 0.00017897 | 0.00017952 | 0.00018007 | 0.00018062 | 0.00018117 | 0.00018172 | 0.00018227 | 0.00018283 | 0.00018338 | 0.00018393 | 0.00018448 | 0.00018503 | 0.00018558 | 0.00018613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL002-15428854 | 1218 | 100 | 0.0023003 | 0.0014907 | 0.0031552 | 0.0021087 | 0.0033067 | 0.0022469 | 2.4426e-05 | 7.5736e-06 | 0.0030575 | 0.003082 | 0.0031064 | 0.0031308 | 0.0031552 | 0.0031628 | 0.0031704 | 0.003178 | 0.0031855 | 0.0031931 | 0.0032007 | 0.0032083 | 0.0032158 | 0.0032234 | 0.003231 | 0.0032386 | 0.0032461 | 0.0032537 | 0.0032613 | 0.0032688 | 1.7658e-05 | 6.9115e-06 | 0.0020381 | 0.0020557 | 0.0020734 | 0.002091 | 0.0021087 | 0.0021156 | 0.0021225 | 0.0021294 | 0.0021363 | 0.0021433 | 0.0021502 | 0.0021571 | 0.002164 | 0.0021709 | 0.0021778 | 0.0021847 | 0.0021916 | 0.0021986 | 0.0022055 | 0.0022124
| SHL002-160491442 | 12 | 12 | 0.00058104 | 0 | 0.00083499 | 0 | 0.00083992 | 0 | 7.2557e-06 | 2.4645e-07 | 0.00080597 | 0.00081323 | 0.00082048 | 0.00082774 | 0.00083499 | 0.00083524 | 0.00083549 | 0.00083573 | 0.00083598 | 0.00083623 | 0.00083647 | 0.00083672 | 0.00083696 | 0.00083721 | 0.00083746 | 0.0008377 | 0.00083795 | 0.0008382 | 0.00083844 | 0.00083869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL002-160491563 | 22 | 22 | 0.00022673 | 0 | 0.00032752 | 0 | 0.00033779 | 0 | 2.8798e-06 | 5.1345e-07 | 0.000316 | 0.00031888 | 0.00032176 | 0.00032464 | 0.00032752 | 0.00032804 | 0.00032855 | 0.00032906 | 0.00032958 | 0.00033009 | 0.0003306 | 0.00033112 | 0.00033163 | 0.00033214 | 0.00033266 | 0.00033317 | 0.00033368 | 0.0003342 | 0.00033471 | 0.00033522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL002-161866668 | 27 | 27 | 0.00029994 | 0 | 0.00043937 | 0 | 0.00045537 | 0 | 3.9835e-06 | 8.003e-07 | 0.00042343 | 0.00042742 | 0.0004314 | 0.00043538 | 0.00043937 | 0.00044017 | 0.00044097 | 0.00044177 | 0.00044257 | 0.00044337 | 0.00044417 | 0.00044497 | 0.00044577 | 0.00044657 | 0.00044737 | 0.00044817 | 0.00044897 | 0.00044977 | 0.00045057 | 0.00045137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL002-162436238 | 10 | 10 | 3.56e-05 | 0 | 5.21e-05 | 0 | 5.39e-05 | 0 | 4.7143e-07 | 9e-08 | 5.0214e-05 | 5.0686e-05 | 5.1157e-05 | 5.1629e-05 | 5.21e-05 | 5.219e-05 | 5.228e-05 | 5.237e-05 | 5.246e-05 | 5.255e-05 | 5.264e-05 | 5.273e-05 | 5.282e-05 | 5.291e-05 | 5.3e-05 | 5.309e-05 | 5.318e-05 | 5.327e-05 | 5.336e-05 | 5.345e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL002-162436334 | 14 | 14 | 0.00023132 | 0 | 0.00032571 | 0 | 0.00033643 | 0 | 2.6968e-06 | 5.361e-07 | 0.00031492 | 0.00031762 | 0.00032031 | 0.00032301 | 0.00032571 | 0.00032624 | 0.00032678 | 0.00032732 | 0.00032785 | 0.00032839 | 0.00032892 | 0.00032946 | 0.00033 | 0.00033053 | 0.00033107 | 0.00033161 | 0.00033214 | 0.00033268 | 0.00033321 | 0.00033375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL002-162436442 | 3 | 3 | 7.44e-05 | 0 | 0.00010874 | 0 | 0.00010731 | 0 | 9.812e-07 | -7.15e-08 | 0.00010482 | 0.0001058 | 0.00010678 | 0.00010776 | 0.00010874 | 0.00010867 | 0.0001086 | 0.00010853 | 0.00010846 | 0.00010838 | 0.00010831 | 0.00010824 | 0.00010817 | 0.0001081 | 0.00010803 | 0.00010796 | 0.00010788 | 0.00010781 | 0.00010774 | 0.00010767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL002-162485158 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL002-24604026 | 1118 | 345 | 0.0073416 | 0.0012997 | 0.010273 | 0.0018533 | 0.010637 | 0.0019369 | 8.3763e-05 | 1.8208e-05 | 0.0099382 | 0.010022 | 0.010106 | 0.01019 | 0.010273 | 0.010292 | 0.01031 | 0.010328 | 0.010346 | 0.010364 | 0.010383 | 0.010401 | 0.010419 | 0.010437 | 0.010455 | 0.010474 | 0.010492 | 0.01051 | 0.010528 | 0.010546 | 1.5816e-05 | 4.1827e-06 | 0.00179 | 0.0018058 | 0.0018217 | 0.0018375 | 0.0018533 | 0.0018575 | 0.0018617 | 0.0018658 | 0.00187 | 0.0018742 | 0.0018784 | 0.0018826 | 0.0018868 | 0.0018909 | 0.0018951 | 0.0018993 | 0.0019035 | 0.0019077 | 0.0019119 | 0.001916
| SHL002-24604040 | 306 | 92 | 0.0041336 | 0.0011303 | 0.005655 | 0.0015379 | 0.0057282 | 0.0015441 | 4.3467e-05 | 3.6613e-06 | 0.0054811 | 0.0055246 | 0.005568 | 0.0056115 | 0.005655 | 0.0056586 | 0.0056623 | 0.005666 | 0.0056696 | 0.0056733 | 0.0056769 | 0.0056806 | 0.0056843 | 0.0056879 | 0.0056916 | 0.0056952 | 0.0056989 | 0.0057026 | 0.0057062 | 0.0057099 | 1.1647e-05 | 3.1135e-07 | 0.0014913 | 0.001503 | 0.0015146 | 0.0015263 | 0.0015379 | 0.0015382 | 0.0015385 | 0.0015389 | 0.0015392 | 0.0015395 | 0.0015398 | 0.0015401 | 0.0015404 | 0.0015407 | 0.001541 | 0.0015413 | 0.0015417 | 0.001542 | 0.0015423 | 0.0015426
| SHL002-24614570 | 214 | 211 | 0.01639 | 5.81e-05 | 0.019978 | 8.63e-05 | 0.019202 | 8.66e-05 | 0.00010251 | -3.8825e-05 | 0.019568 | 0.019671 | 0.019773 | 0.019876 | 0.019978 | 0.019939 | 0.0199 | 0.019862 | 0.019823 | 0.019784 | 0.019745 | 0.019706 | 0.019667 | 0.019629 | 0.01959 | 0.019551 | 0.019512 | 0.019473 | 0.019435 | 0.019396 | 8.0571e-07 | 1.5e-08 | 8.3077e-05 | 8.3883e-05 | 8.4689e-05 | 8.5494e-05 | 8.63e-05 | 8.6315e-05 | 8.633e-05 | 8.6345e-05 | 8.636e-05 | 8.6375e-05 | 8.639e-05 | 8.6405e-05 | 8.642e-05 | 8.6435e-05 | 8.645e-05 | 8.6465e-05 | 8.648e-05 | 8.6495e-05 | 8.651e-05 | 8.6525e-05
| SHL002-42163201 | 440 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL002-54520142 | 91 | 31 | 0.0026463 | 0.00033279 | 0.0026749 | 0.00033375 | 0.0026622 | 0.00033333 | 8.1669e-07 | -6.3605e-07 | 0.0026717 | 0.0026725 | 0.0026733 | 0.0026741 | 0.0026749 | 0.0026743 | 0.0026736 | 0.002673 | 0.0026724 | 0.0026717 | 0.0026711 | 0.0026705 | 0.0026698 | 0.0026692 | 0.0026686 | 0.0026679 | 0.0026673 | 0.0026666 | 0.002666 | 0.0026654 | 2.7429e-08 | -2.125e-08 | 0.00033364 | 0.00033367 | 0.0003337 | 0.00033372 | 0.00033375 | 0.00033373 | 0.00033371 | 0.00033369 | 0.00033367 | 0.00033364 | 0.00033362 | 0.0003336 | 0.00033358 | 0.00033356 | 0.00033354 | 0.00033352 | 0.0003335 | 0.00033347 | 0.00033345 | 0.00033343
| SHL004-15428865 | 1437 | 501 | 0.0025849 | 0.0010952 | 0.0036352 | 0.0015497 | 0.0038589 | 0.0016517 | 3.0011e-05 | 1.1183e-05 | 0.0035152 | 0.0035452 | 0.0035752 | 0.0036052 | 0.0036352 | 0.0036464 | 0.0036576 | 0.0036688 | 0.00368 | 0.0036912 | 0.0037023 | 0.0037135 | 0.0037247 | 0.0037359 | 0.0037471 | 0.0037583 | 0.0037694 | 0.0037806 | 0.0037918 | 0.003803 | 1.2987e-05 | 5.0975e-06 | 0.0014978 | 0.0015107 | 0.0015237 | 0.0015367 | 0.0015497 | 0.0015548 | 0.0015599 | 0.001565 | 0.0015701 | 0.0015752 | 0.0015803 | 0.0015854 | 0.0015905 | 0.0015956 | 0.0016007 | 0.0016058 | 0.0016109 | 0.001616 | 0.0016211 | 0.0016262
| SHL004-24604082 | 567 | 567 | 0.015735 | 0 | 0.022956 | 0 | 0.023121 | 0 | 0.00020632 | 8.2523e-06 | 0.022131 | 0.022337 | 0.022543 | 0.02275 | 0.022956 | 0.022964 | 0.022972 | 0.022981 | 0.022989 | 0.022997 | 0.023005 | 0.023014 | 0.023022 | 0.02303 | 0.023038 | 0.023047 | 0.023055 | 0.023063 | 0.023071 | 0.02308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL004-24612892 | 369 | 369 | 0.012013 | 0 | 0.016529 | 0 | 0.016843 | 0 | 0.00012902 | 1.5721e-05 | 0.016013 | 0.016142 | 0.016271 | 0.0164 | 0.016529 | 0.016544 | 0.01656 | 0.016576 | 0.016591 | 0.016607 | 0.016623 | 0.016639 | 0.016654 | 0.01667 | 0.016686 | 0.016702 | 0.016717 | 0.016733 | 0.016749 | 0.016764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL005-15428600 | 15 | 15 | 0.0001298 | 0 | 0.00018777 | 0 | 0.0002049 | 0 | 1.6565e-06 | 8.5655e-07 | 0.00018115 | 0.0001828 | 0.00018446 | 0.00018612 | 0.00018777 | 0.00018863 | 0.00018949 | 0.00019034 | 0.0001912 | 0.00019206 | 0.00019291 | 0.00019377 | 0.00019463 | 0.00019548 | 0.00019634 | 0.0001972 | 0.00019805 | 0.00019891 | 0.00019977 | 0.00020062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL005-15428613 | 1139 | 707 | 0.0058716 | 0.003514 | 0.0079372 | 0.0048832 | 0.0084306 | 0.0053018 | 5.9018e-05 | 2.4671e-05 | 0.0077011 | 0.0077601 | 0.0078191 | 0.0078782 | 0.0079372 | 0.0079618 | 0.0079865 | 0.0080112 | 0.0080359 | 0.0080605 | 0.0080852 | 0.0081099 | 0.0081345 | 0.0081592 | 0.0081839 | 0.0082085 | 0.0082332 | 0.0082579 | 0.0082826 | 0.0083072 | 3.9119e-05 | 2.0928e-05 | 0.0047267 | 0.0047659 | 0.004805 | 0.0048441 | 0.0048832 | 0.0049042 | 0.0049251 | 0.004946 | 0.0049669 | 0.0049879 | 0.0050088 | 0.0050297 | 0.0050506 | 0.0050716 | 0.0050925 | 0.0051134 | 0.0051344 | 0.0051553 | 0.0051762 | 0.0051971
| SHL005-15428624 | 1142 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL005-24604390 | 176 | 176 | 0.013437 | 0 | 0.018607 | 0 | 0.01979 | 0 | 0.00014773 | 5.9153e-05 | 0.018016 | 0.018164 | 0.018312 | 0.01846 | 0.018607 | 0.018667 | 0.018726 | 0.018785 | 0.018844 | 0.018903 | 0.018962 | 0.019021 | 0.019081 | 0.01914 | 0.019199 | 0.019258 | 0.019317 | 0.019376 | 0.019436 | 0.019495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL005-24613604 | 241 | 241 | 0.0073168 | 0 | 0.010207 | 0 | 0.011121 | 0 | 8.2589e-05 | 4.5691e-05 | 0.0098771 | 0.0099596 | 0.010042 | 0.010125 | 0.010207 | 0.010253 | 0.010299 | 0.010344 | 0.01039 | 0.010436 | 0.010482 | 0.010527 | 0.010573 | 0.010619 | 0.010664 | 0.01071 | 0.010756 | 0.010801 | 0.010847 | 0.010893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL007-15428576 | 2061 | 1079 | 0.00027333 | 0 | 0.00040931 | 0 | 0.00042854 | 0 | 3.8851e-06 | 9.6145e-07 | 0.00039377 | 0.00039765 | 0.00040154 | 0.00040542 | 0.00040931 | 0.00041027 | 0.00041123 | 0.00041219 | 0.00041315 | 0.00041412 | 0.00041508 | 0.00041604 | 0.000417 | 0.00041796 | 0.00041892 | 0.00041988 | 0.00042085 | 0.00042181 | 0.00042277 | 0.00042373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL007-181581220 | 982 | 982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL008-15428954 | 2682 | 1206 | 8e-05 | 6.61e-06 | 0.00011581 | 9.56e-06 | 0.00012637 | 1.04e-05 | 1.0231e-06 | 5.2825e-07 | 0.00011172 | 0.00011274 | 0.00011376 | 0.00011478 | 0.00011581 | 0.00011634 | 0.00011686 | 0.00011739 | 0.00011792 | 0.00011845 | 0.00011898 | 0.00011951 | 0.00012003 | 0.00012056 | 0.00012109 | 0.00012162 | 0.00012215 | 0.00012268 | 0.0001232 | 0.00012373 | 8.4286e-08 | 4.2e-08 | 9.2229e-06 | 9.3071e-06 | 9.3914e-06 | 9.4757e-06 | 9.56e-06 | 9.602e-06 | 9.644e-06 | 9.686e-06 | 9.728e-06 | 9.77e-06 | 9.812e-06 | 9.854e-06 | 9.896e-06 | 9.938e-06 | 9.98e-06 | 1.0022e-05 | 1.0064e-05 | 1.0106e-05 | 1.0148e-05 | 1.019e-05
| SHL008-181581109 | 1476 | 1476 | 0.0036046 | 0 | 0.0051715 | 0 | 0.0056119 | 0 | 4.477e-05 | 2.202e-05 | 0.0049924 | 0.0050372 | 0.005082 | 0.0051267 | 0.0051715 | 0.0051935 | 0.0052156 | 0.0052376 | 0.0052596 | 0.0052816 | 0.0053036 | 0.0053257 | 0.0053477 | 0.0053697 | 0.0053917 | 0.0054137 | 0.0054358 | 0.0054578 | 0.0054798 | 0.0055018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN011-130746986 | 39 | 39 | 6.05e-06 | 0 | 9.52e-06 | 0 | 1.12e-05 | 0 | 9.9143e-08 | 8.4e-08 | 9.1234e-06 | 9.2226e-06 | 9.3217e-06 | 9.4209e-06 | 9.52e-06 | 9.604e-06 | 9.688e-06 | 9.772e-06 | 9.856e-06 | 9.94e-06 | 1.0024e-05 | 1.0108e-05 | 1.0192e-05 | 1.0276e-05 | 1.036e-05 | 1.0444e-05 | 1.0528e-05 | 1.0612e-05 | 1.0696e-05 | 1.078e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN011-175612776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN011-200057131 | 1767 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN011-24605252 | 1183 | 1131 | 0.015196 | 1.89e-05 | 0.019132 | 2.41e-05 | 0.021247 | 2.77e-05 | 0.00011245 | 0.00010578 | 0.018682 | 0.018794 | 0.018907 | 0.019019 | 0.019132 | 0.019238 | 0.019343 | 0.019449 | 0.019555 | 0.019661 | 0.019766 | 0.019872 | 0.019978 | 0.020084 | 0.02019 | 0.020295 | 0.020401 | 0.020507 | 0.020613 | 0.020718 | 1.4857e-07 | 1.8e-07 | 2.3506e-05 | 2.3654e-05 | 2.3803e-05 | 2.3951e-05 | 2.41e-05 | 2.428e-05 | 2.446e-05 | 2.464e-05 | 2.482e-05 | 2.5e-05 | 2.518e-05 | 2.536e-05 | 2.554e-05 | 2.572e-05 | 2.59e-05 | 2.608e-05 | 2.626e-05 | 2.644e-05 | 2.662e-05 | 2.68e-05
| SHN011-95830821 | 13 | 13 | 2.56e-05 | 0 | 3.15e-05 | 0 | 3.45e-05 | 0 | 1.6857e-07 | 1.5e-07 | 3.0826e-05 | 3.0994e-05 | 3.1163e-05 | 3.1331e-05 | 3.15e-05 | 3.165e-05 | 3.18e-05 | 3.195e-05 | 3.21e-05 | 3.225e-05 | 3.24e-05 | 3.255e-05 | 3.27e-05 | 3.285e-05 | 3.3e-05 | 3.315e-05 | 3.33e-05 | 3.345e-05 | 3.36e-05 | 3.375e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN012-200057355 | 2576 | 1309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN012-24613290 | 1267 | 1267 | 0.0023613 | 0 | 0.0030118 | 0 | 0.0034412 | 0 | 1.8586e-05 | 2.1471e-05 | 0.0029375 | 0.0029561 | 0.0029746 | 0.0029932 | 0.0030118 | 0.0030333 | 0.0030548 | 0.0030762 | 0.0030977 | 0.0031192 | 0.0031406 | 0.0031621 | 0.0031836 | 0.003205 | 0.0032265 | 0.003248 | 0.0032695 | 0.0032909 | 0.0033124 | 0.0033339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN014-15423299 | 355 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN014-200219171 | 353 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN021-15423325 | 2427 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN021-200219341 | 2421 | 2421 | 0.018524 | 0 | 0.021638 | 0 | 0.022481 | 0 | 8.8964e-05 | 4.215e-05 | 0.021282 | 0.021371 | 0.02146 | 0.021549 | 0.021638 | 0.02168 | 0.021722 | 0.021764 | 0.021806 | 0.021849 | 0.021891 | 0.021933 | 0.021975 | 0.022017 | 0.022059 | 0.022102 | 0.022144 | 0.022186 | 0.022228 | 0.02227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN022-200219453 | 1883 | 1883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN023-200219561 | 1003 | 1003 | 0.00041631 | 0 | 0.00051537 | 0 | 0.00053589 | 0 | 2.8304e-06 | 1.0261e-06 | 0.00050405 | 0.00050688 | 0.00050971 | 0.00051254 | 0.00051537 | 0.0005164 | 0.00051743 | 0.00051845 | 0.00051948 | 0.0005205 | 0.00052153 | 0.00052256 | 0.00052358 | 0.00052461 | 0.00052563 | 0.00052666 | 0.00052769 | 0.00052871 | 0.00052974 | 0.00053076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN024-159278517 | 23 | 23 | 3.07e-06 | 0 | 4.01e-06 | 0 | 5.01e-06 | 0 | 2.6857e-08 | 5e-08 | 3.9026e-06 | 3.9294e-06 | 3.9563e-06 | 3.9831e-06 | 4.01e-06 | 4.06e-06 | 4.11e-06 | 4.16e-06 | 4.21e-06 | 4.26e-06 | 4.31e-06 | 4.36e-06 | 4.41e-06 | 4.46e-06 | 4.51e-06 | 4.56e-06 | 4.61e-06 | 4.66e-06 | 4.71e-06 | 4.76e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN024-160253686 | 10 | 10 | 3.6e-07 | 0 | 5.16e-07 | 0 | 6.15e-07 | 0 | 4.4571e-09 | 4.95e-09 | 4.9817e-07 | 5.0263e-07 | 5.0709e-07 | 5.1154e-07 | 5.16e-07 | 5.2095e-07 | 5.259e-07 | 5.3085e-07 | 5.358e-07 | 5.4075e-07 | 5.457e-07 | 5.5065e-07 | 5.556e-07 | 5.6055e-07 | 5.655e-07 | 5.7045e-07 | 5.754e-07 | 5.8035e-07 | 5.853e-07 | 5.9025e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN024-164487380 | 15 | 15 | 7.81e-07 | 0 | 1.08e-06 | 0 | 1.3e-06 | 0 | 8.5429e-09 | 1.1e-08 | 1.0458e-06 | 1.0544e-06 | 1.0629e-06 | 1.0715e-06 | 1.08e-06 | 1.091e-06 | 1.102e-06 | 1.113e-06 | 1.124e-06 | 1.135e-06 | 1.146e-06 | 1.157e-06 | 1.168e-06 | 1.179e-06 | 1.19e-06 | 1.201e-06 | 1.212e-06 | 1.223e-06 | 1.234e-06 | 1.245e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN024-200219667 | 1073 | 646 | 0.00063265 | 0.00021124 | 0.00076326 | 0.00026553 | 0.0008505 | 0.00033376 | 3.7317e-06 | 4.362e-06 | 0.00074833 | 0.00075206 | 0.00075579 | 0.00075953 | 0.00076326 | 0.00076762 | 0.00077198 | 0.00077634 | 0.00078071 | 0.00078507 | 0.00078943 | 0.00079379 | 0.00079815 | 0.00080252 | 0.00080688 | 0.00081124 | 0.0008156 | 0.00081996 | 0.00082433 | 0.00082869 | 1.5512e-06 | 3.4115e-06 | 0.00025932 | 0.00026088 | 0.00026243 | 0.00026398 | 0.00026553 | 0.00026894 | 0.00027235 | 0.00027576 | 0.00027918 | 0.00028259 | 0.000286 | 0.00028941 | 0.00029282 | 0.00029623 | 0.00029964 | 0.00030306 | 0.00030647 | 0.00030988 | 0.00031329 | 0.0003167
| SHN024-24605390 | 412 | 379 | 0.0016509 | 2.94e-06 | 0.0021281 | 3.87e-06 | 0.0024697 | 4.75e-06 | 1.3635e-05 | 1.708e-05 | 0.0020735 | 0.0020872 | 0.0021008 | 0.0021145 | 0.0021281 | 0.0021452 | 0.0021622 | 0.0021793 | 0.0021964 | 0.0022135 | 0.0022306 | 0.0022476 | 0.0022647 | 0.0022818 | 0.0022989 | 0.002316 | 0.002333 | 0.0023501 | 0.0023672 | 0.0023843 | 2.6571e-08 | 4.4e-08 | 3.7637e-06 | 3.7903e-06 | 3.8169e-06 | 3.8434e-06 | 3.87e-06 | 3.914e-06 | 3.958e-06 | 4.002e-06 | 4.046e-06 | 4.09e-06 | 4.134e-06 | 4.178e-06 | 4.222e-06 | 4.266e-06 | 4.31e-06 | 4.354e-06 | 4.398e-06 | 4.442e-06 | 4.486e-06 | 4.53e-06
| SHP011-15432563 | 706 | 154 | 0.0013616 | 4.76e-05 | 0.0015515 | 5.31e-05 | 0.001615 | 5.32e-05 | 5.4245e-06 | 3.1772e-06 | 0.0015298 | 0.0015352 | 0.0015407 | 0.0015461 | 0.0015515 | 0.0015547 | 0.0015579 | 0.001561 | 0.0015642 | 0.0015674 | 0.0015706 | 0.0015737 | 0.0015769 | 0.0015801 | 0.0015833 | 0.0015864 | 0.0015896 | 0.0015928 | 0.001596 | 0.0015992 | 1.5714e-07 | 5e-09 | 5.2471e-05 | 5.2629e-05 | 5.2786e-05 | 5.2943e-05 | 5.31e-05 | 5.3105e-05 | 5.311e-05 | 5.3115e-05 | 5.312e-05 | 5.3125e-05 | 5.313e-05 | 5.3135e-05 | 5.314e-05 | 5.3145e-05 | 5.315e-05 | 5.3155e-05 | 5.316e-05 | 5.3165e-05 | 5.317e-05 | 5.3175e-05
| SHP011-164003814 | 18 | 18 | 1.11e-05 | 0 | 1.54e-05 | 0 | 1.89e-05 | 0 | 1.2286e-07 | 1.75e-07 | 1.4909e-05 | 1.5031e-05 | 1.5154e-05 | 1.5277e-05 | 1.54e-05 | 1.5575e-05 | 1.575e-05 | 1.5925e-05 | 1.61e-05 | 1.6275e-05 | 1.645e-05 | 1.6625e-05 | 1.68e-05 | 1.6975e-05 | 1.715e-05 | 1.7325e-05 | 1.75e-05 | 1.7675e-05 | 1.785e-05 | 1.8025e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP011-24602590 | 552 | 534 | 0.0020472 | 9.84e-06 | 0.0026028 | 1.35e-05 | 0.0029844 | 1.71e-05 | 1.5877e-05 | 1.9076e-05 | 0.0025393 | 0.0025552 | 0.0025711 | 0.002587 | 0.0026028 | 0.0026219 | 0.002641 | 0.0026601 | 0.0026791 | 0.0026982 | 0.0027173 | 0.0027364 | 0.0027554 | 0.0027745 | 0.0027936 | 0.0028127 | 0.0028318 | 0.0028508 | 0.0028699 | 0.002889 | 1.0457e-07 | 1.8e-07 | 1.3082e-05 | 1.3186e-05 | 1.3291e-05 | 1.3395e-05 | 1.35e-05 | 1.368e-05 | 1.386e-05 | 1.404e-05 | 1.422e-05 | 1.44e-05 | 1.458e-05 | 1.476e-05 | 1.494e-05 | 1.512e-05 | 1.53e-05 | 1.548e-05 | 1.566e-05 | 1.584e-05 | 1.602e-05 | 1.62e-05
| SHP012-153588795 | 78 | 78 | 0.0045021 | 0 | 0.0056855 | 0 | 0.0066513 | 0 | 3.3811e-05 | 4.8292e-05 | 0.0055503 | 0.0055841 | 0.0056179 | 0.0056517 | 0.0056855 | 0.0057338 | 0.0057821 | 0.0058304 | 0.0058787 | 0.005927 | 0.0059753 | 0.0060236 | 0.0060718 | 0.0061201 | 0.0061684 | 0.0062167 | 0.006265 | 0.0063133 | 0.0063616 | 0.0064099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP012-15432576 | 2262 | 1347 | 0.0086264 | 0.0045659 | 0.010853 | 0.0060594 | 0.012154 | 0.0071124 | 6.3604e-05 | 6.5062e-05 | 0.010598 | 0.010662 | 0.010725 | 0.010789 | 0.010853 | 0.010918 | 0.010983 | 0.011048 | 0.011113 | 0.011178 | 0.011243 | 0.011308 | 0.011373 | 0.011438 | 0.011503 | 0.011568 | 0.011633 | 0.011698 | 0.011763 | 0.011828 | 4.267e-05 | 5.265e-05 | 0.0058887 | 0.0059314 | 0.005974 | 0.0060167 | 0.0060594 | 0.006112 | 0.0061647 | 0.0062173 | 0.00627 | 0.0063226 | 0.0063753 | 0.0064279 | 0.0064806 | 0.0065332 | 0.0065859 | 0.0066385 | 0.0066912 | 0.0067438 | 0.0067965 | 0.0068491
| SHP012-160253286 | 9 | 9 | 4.44e-06 | 0 | 5.67e-06 | 0 | 7.03e-06 | 0 | 3.5143e-08 | 6.8e-08 | 5.5294e-06 | 5.5646e-06 | 5.5997e-06 | 5.6349e-06 | 5.67e-06 | 5.738e-06 | 5.806e-06 | 5.874e-06 | 5.942e-06 | 6.01e-06 | 6.078e-06 | 6.146e-06 | 6.214e-06 | 6.282e-06 | 6.35e-06 | 6.418e-06 | 6.486e-06 | 6.554e-06 | 6.622e-06 | 6.69e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP012-160253407 | 27 | 27 | 1.46e-05 | 0 | 2.11e-05 | 0 | 2.41e-05 | 0 | 1.8571e-07 | 1.5e-07 | 2.0357e-05 | 2.0543e-05 | 2.0729e-05 | 2.0914e-05 | 2.11e-05 | 2.125e-05 | 2.14e-05 | 2.155e-05 | 2.17e-05 | 2.185e-05 | 2.2e-05 | 2.215e-05 | 2.23e-05 | 2.245e-05 | 2.26e-05 | 2.275e-05 | 2.29e-05 | 2.305e-05 | 2.32e-05 | 2.335e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP012-160253550 | 13 | 13 | 2.29e-05 | 0 | 3.29e-05 | 0 | 3.54e-05 | 0 | 2.8571e-07 | 1.25e-07 | 3.1757e-05 | 3.2043e-05 | 3.2329e-05 | 3.2614e-05 | 3.29e-05 | 3.3025e-05 | 3.315e-05 | 3.3275e-05 | 3.34e-05 | 3.3525e-05 | 3.365e-05 | 3.3775e-05 | 3.39e-05 | 3.4025e-05 | 3.415e-05 | 3.4275e-05 | 3.44e-05 | 3.4525e-05 | 3.465e-05 | 3.4775e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP012-163378080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP012-164366336 | 12 | 12 | 4.51e-06 | 0 | 5.9e-06 | 0 | 7.25e-06 | 0 | 3.9714e-08 | 6.75e-08 | 5.7411e-06 | 5.7809e-06 | 5.8206e-06 | 5.8603e-06 | 5.9e-06 | 5.9675e-06 | 6.035e-06 | 6.1025e-06 | 6.17e-06 | 6.2375e-06 | 6.305e-06 | 6.3725e-06 | 6.44e-06 | 6.5075e-06 | 6.575e-06 | 6.6425e-06 | 6.71e-06 | 6.7775e-06 | 6.845e-06 | 6.9125e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP012-24603174 | 752 | 712 | 0.0022915 | 3.58e-05 | 0.0029125 | 4.71e-05 | 0.0032601 | 5.52e-05 | 1.7742e-05 | 1.7384e-05 | 0.0028415 | 0.0028592 | 0.002877 | 0.0028947 | 0.0029125 | 0.0029299 | 0.0029472 | 0.0029646 | 0.002982 | 0.0029994 | 0.0030168 | 0.0030342 | 0.0030515 | 0.0030689 | 0.0030863 | 0.0031037 | 0.0031211 | 0.0031385 | 0.0031558 | 0.0031732 | 3.2286e-07 | 4.05e-07 | 4.5809e-05 | 4.6131e-05 | 4.6454e-05 | 4.6777e-05 | 4.71e-05 | 4.7505e-05 | 4.791e-05 | 4.8315e-05 | 4.872e-05 | 4.9125e-05 | 4.953e-05 | 4.9935e-05 | 5.034e-05 | 5.0745e-05 | 5.115e-05 | 5.1555e-05 | 5.196e-05 | 5.2365e-05 | 5.277e-05 | 5.3175e-05
| SHP012-24612048 | 816 | 64 | 0.0093121 | 0.0010547 | 0.011502 | 0.0013051 | 0.013322 | 0.0014859 | 6.2572e-05 | 9.0971e-05 | 0.011252 | 0.011314 | 0.011377 | 0.01144 | 0.011502 | 0.011593 | 0.011684 | 0.011775 | 0.011866 | 0.011957 | 0.012048 | 0.012139 | 0.01223 | 0.012321 | 0.012412 | 0.012503 | 0.012594 | 0.012685 | 0.012776 | 0.012867 | 7.1556e-06 | 9.0375e-06 | 0.0012765 | 0.0012836 | 0.0012908 | 0.001298 | 0.0013051 | 0.0013141 | 0.0013232 | 0.0013322 | 0.0013413 | 0.0013503 | 0.0013593 | 0.0013684 | 0.0013774 | 0.0013864 | 0.0013955 | 0.0014045 | 0.0014136 | 0.0014226 | 0.0014316 | 0.0014407
| SHP014-15432602 | 1669 | 127 | 0.0017839 | 0.00067496 | 0.0021999 | 0.00084605 | 0.002536 | 0.00099507 | 1.1885e-05 | 1.6806e-05 | 0.0021523 | 0.0021642 | 0.0021761 | 0.002188 | 0.0021999 | 0.0022167 | 0.0022335 | 0.0022503 | 0.0022671 | 0.0022839 | 0.0023007 | 0.0023175 | 0.0023343 | 0.0023511 | 0.0023679 | 0.0023847 | 0.0024015 | 0.0024183 | 0.0024351 | 0.0024519 | 4.8883e-06 | 7.4509e-06 | 0.0008265 | 0.00083139 | 0.00083628 | 0.00084116 | 0.00084605 | 0.0008535 | 0.00086095 | 0.00086841 | 0.00087586 | 0.00088331 | 0.00089076 | 0.00089821 | 0.00090566 | 0.00091311 | 0.00092056 | 0.00092801 | 0.00093546 | 0.00094291 | 0.00095037 | 0.00095782
| SHP014-164366107 | 23 | 23 | 0.00040178 | 0 | 0.00052412 | 0 | 0.00060601 | 0 | 3.4953e-06 | 4.0944e-06 | 0.00051014 | 0.00051363 | 0.00051713 | 0.00052062 | 0.00052412 | 0.00052821 | 0.00053231 | 0.0005364 | 0.0005405 | 0.00054459 | 0.00054869 | 0.00055278 | 0.00055687 | 0.00056097 | 0.00056506 | 0.00056916 | 0.00057325 | 0.00057735 | 0.00058144 | 0.00058553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP014-177037469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP014-24602550 | 1040 | 992 | 0.025821 | 0.00024772 | 0.031301 | 0.00033698 | 0.035385 | 0.00042237 | 0.00015658 | 0.00020416 | 0.030675 | 0.030832 | 0.030988 | 0.031145 | 0.031301 | 0.031506 | 0.03171 | 0.031914 | 0.032118 | 0.032322 | 0.032526 | 0.032731 | 0.032935 | 0.033139 | 0.033343 | 0.033547 | 0.033751 | 0.033955 | 0.03416 | 0.034364 | 2.5505e-06 | 4.2691e-06 | 0.00032678 | 0.00032933 | 0.00033188 | 0.00033443 | 0.00033698 | 0.00034125 | 0.00034552 | 0.00034979 | 0.00035406 | 0.00035833 | 0.0003626 | 0.00036687 | 0.00037114 | 0.00037541 | 0.00037967 | 0.00038394 | 0.00038821 | 0.00039248 | 0.00039675 | 0.00040102
| SHP014-24602854 | 375 | 375 | 0.00033768 | 0 | 0.00040568 | 0 | 0.00049028 | 0 | 1.9427e-06 | 4.2304e-06 | 0.00039791 | 0.00039985 | 0.00040179 | 0.00040373 | 0.00040568 | 0.00040991 | 0.00041414 | 0.00041837 | 0.0004226 | 0.00042683 | 0.00043106 | 0.00043529 | 0.00043952 | 0.00044375 | 0.00044798 | 0.00045221 | 0.00045644 | 0.00046067 | 0.0004649 | 0.00046913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP014-24602868 | 127 | 127 | 0.003684 | 0 | 0.0046791 | 0 | 0.0057736 | 0 | 2.843e-05 | 5.4727e-05 | 0.0045654 | 0.0045938 | 0.0046222 | 0.0046507 | 0.0046791 | 0.0047338 | 0.0047885 | 0.0048433 | 0.004898 | 0.0049527 | 0.0050074 | 0.0050622 | 0.0051169 | 0.0051716 | 0.0052264 | 0.0052811 | 0.0053358 | 0.0053905 | 0.0054453 | 0.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-120932535 | 56 | 56 | 3.57e-05 | 0 | 4.5e-05 | 0 | 4.96e-05 | 0 | 2.6571e-07 | 2.3e-07 | 4.3937e-05 | 4.4203e-05 | 4.4469e-05 | 4.4734e-05 | 4.5e-05 | 4.523e-05 | 4.546e-05 | 4.569e-05 | 4.592e-05 | 4.615e-05 | 4.638e-05 | 4.661e-05 | 4.684e-05 | 4.707e-05 | 4.73e-05 | 4.753e-05 | 4.776e-05 | 4.799e-05 | 4.822e-05 | 4.845e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-129439859 | 35 | 35 | 2.33e-05 | 0 | 3.31e-05 | 0 | 3.62e-05 | 0 | 2.8e-07 | 1.55e-07 | 3.198e-05 | 3.226e-05 | 3.254e-05 | 3.282e-05 | 3.31e-05 | 3.3255e-05 | 3.341e-05 | 3.3565e-05 | 3.372e-05 | 3.3875e-05 | 3.403e-05 | 3.4185e-05 | 3.434e-05 | 3.4495e-05 | 3.465e-05 | 3.4805e-05 | 3.496e-05 | 3.5115e-05 | 3.527e-05 | 3.5425e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-134953488 | 51 | 51 | 0.00095157 | 0 | 0.0012831 | 0 | 0.0014129 | 0 | 9.4731e-06 | 6.4876e-06 | 0.0012452 | 0.0012547 | 0.0012642 | 0.0012737 | 0.0012831 | 0.0012896 | 0.0012961 | 0.0013026 | 0.0013091 | 0.0013156 | 0.0013221 | 0.0013285 | 0.001335 | 0.0013415 | 0.001348 | 0.0013545 | 0.001361 | 0.0013675 | 0.001374 | 0.0013804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-134953623 | 79 | 79 | 0.0021093 | 0 | 0.0027317 | 0 | 0.0029803 | 0 | 1.7783e-05 | 1.2432e-05 | 0.0026606 | 0.0026784 | 0.0026961 | 0.0027139 | 0.0027317 | 0.0027441 | 0.0027566 | 0.002769 | 0.0027814 | 0.0027939 | 0.0028063 | 0.0028187 | 0.0028312 | 0.0028436 | 0.002856 | 0.0028685 | 0.0028809 | 0.0028933 | 0.0029058 | 0.0029182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-137932835 | 16 | 16 | 3.62e-07 | 0 | 5.1e-07 | 0 | 6.34e-07 | 0 | 4.2286e-09 | 6.2e-09 | 4.9309e-07 | 4.9731e-07 | 5.0154e-07 | 5.0577e-07 | 5.1e-07 | 5.162e-07 | 5.224e-07 | 5.286e-07 | 5.348e-07 | 5.41e-07 | 5.472e-07 | 5.534e-07 | 5.596e-07 | 5.658e-07 | 5.72e-07 | 5.782e-07 | 5.844e-07 | 5.906e-07 | 5.968e-07 | 6.03e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-138133628 | 39 | 39 | 0.0030886 | 0 | 0.0040858 | 0 | 0.0042735 | 0 | 2.8492e-05 | 9.3861e-06 | 0.0039718 | 0.0040003 | 0.0040288 | 0.0040573 | 0.0040858 | 0.0040952 | 0.0041046 | 0.004114 | 0.0041234 | 0.0041327 | 0.0041421 | 0.0041515 | 0.0041609 | 0.0041703 | 0.0041797 | 0.0041891 | 0.0041984 | 0.0042078 | 0.0042172 | 0.0042266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-15437442 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-15437455 | 718 | 78 | 0.00053175 | 2.59e-07 | 0.00061668 | 3.62e-07 | 0.00063728 | 4.37e-07 | 2.4268e-06 | 1.0299e-06 | 0.00060697 | 0.0006094 | 0.00061183 | 0.00061426 | 0.00061668 | 0.00061771 | 0.00061874 | 0.00061977 | 0.0006208 | 0.00062183 | 0.00062286 | 0.00062389 | 0.00062492 | 0.00062595 | 0.00062698 | 0.00062801 | 0.00062904 | 0.00063007 | 0.0006311 | 0.00063213 | 2.9429e-09 | 3.75e-09 | 3.5023e-07 | 3.5317e-07 | 3.5611e-07 | 3.5906e-07 | 3.62e-07 | 3.6575e-07 | 3.695e-07 | 3.7325e-07 | 3.77e-07 | 3.8075e-07 | 3.845e-07 | 3.8825e-07 | 3.92e-07 | 3.9575e-07 | 3.995e-07 | 4.0325e-07 | 4.07e-07 | 4.1075e-07 | 4.145e-07 | 4.1825e-07
| SHP021-155422659 | 12 | 12 | 4.63e-06 | 0 | 6.42e-06 | 0 | 7.96e-06 | 0 | 5.1143e-08 | 7.7e-08 | 6.2154e-06 | 6.2666e-06 | 6.3177e-06 | 6.3689e-06 | 6.42e-06 | 6.497e-06 | 6.574e-06 | 6.651e-06 | 6.728e-06 | 6.805e-06 | 6.882e-06 | 6.959e-06 | 7.036e-06 | 7.113e-06 | 7.19e-06 | 7.267e-06 | 7.344e-06 | 7.421e-06 | 7.498e-06 | 7.575e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-157015365 | 25 | 25 | 0.00017855 | 0 | 0.00023475 | 0 | 0.00027951 | 0 | 1.6055e-06 | 2.2383e-06 | 0.00022832 | 0.00022993 | 0.00023153 | 0.00023314 | 0.00023475 | 0.00023698 | 0.00023922 | 0.00024146 | 0.0002437 | 0.00024594 | 0.00024818 | 0.00025041 | 0.00025265 | 0.00025489 | 0.00025713 | 0.00025937 | 0.00026161 | 0.00026384 | 0.00026608 | 0.00026832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-157015736 | 25 | 25 | 0.002021 | 0 | 0.0027748 | 0 | 0.0030801 | 0 | 2.1536e-05 | 1.5266e-05 | 0.0026886 | 0.0027102 | 0.0027317 | 0.0027532 | 0.0027748 | 0.00279 | 0.0028053 | 0.0028206 | 0.0028358 | 0.0028511 | 0.0028664 | 0.0028816 | 0.0028969 | 0.0029122 | 0.0029274 | 0.0029427 | 0.002958 | 0.0029732 | 0.0029885 | 0.0030038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-164271438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-164488411 | 12 | 12 | 0.002977 | 0 | 0.0038577 | 0 | 0.0042133 | 0 | 2.5163e-05 | 1.7785e-05 | 0.003757 | 0.0037822 | 0.0038073 | 0.0038325 | 0.0038577 | 0.0038754 | 0.0038932 | 0.003911 | 0.0039288 | 0.0039466 | 0.0039644 | 0.0039821 | 0.0039999 | 0.0040177 | 0.0040355 | 0.0040533 | 0.0040711 | 0.0040889 | 0.0041066 | 0.0041244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-24614288 | 640 | 14 | 1.82e-06 | 8.22e-07 | 2.5e-06 | 1.13e-06 | 2.95e-06 | 1.33e-06 | 1.9429e-08 | 2.25e-08 | 2.4223e-06 | 2.4417e-06 | 2.4611e-06 | 2.4806e-06 | 2.5e-06 | 2.5225e-06 | 2.545e-06 | 2.5675e-06 | 2.59e-06 | 2.6125e-06 | 2.635e-06 | 2.6575e-06 | 2.68e-06 | 2.7025e-06 | 2.725e-06 | 2.7475e-06 | 2.77e-06 | 2.7925e-06 | 2.815e-06 | 2.8375e-06 | 8.8e-09 | 1e-08 | 1.0948e-06 | 1.1036e-06 | 1.1124e-06 | 1.1212e-06 | 1.13e-06 | 1.14e-06 | 1.15e-06 | 1.16e-06 | 1.17e-06 | 1.18e-06 | 1.19e-06 | 1.2e-06 | 1.21e-06 | 1.22e-06 | 1.23e-06 | 1.24e-06 | 1.25e-06 | 1.26e-06 | 1.27e-06 | 1.28e-06
| SHP021-24614430 | 610 | 137 | 0.0053483 | 0.0013133 | 0.0062495 | 0.0017272 | 0.0067561 | 0.0020926 | 2.5749e-05 | 2.5331e-05 | 0.0061465 | 0.0061722 | 0.006198 | 0.0062237 | 0.0062495 | 0.0062748 | 0.0063001 | 0.0063255 | 0.0063508 | 0.0063761 | 0.0064015 | 0.0064268 | 0.0064521 | 0.0064775 | 0.0065028 | 0.0065281 | 0.0065535 | 0.0065788 | 0.0066041 | 0.0066295 | 1.1824e-05 | 1.827e-05 | 0.0016799 | 0.0016917 | 0.0017035 | 0.0017153 | 0.0017272 | 0.0017454 | 0.0017637 | 0.001782 | 0.0018003 | 0.0018185 | 0.0018368 | 0.0018551 | 0.0018733 | 0.0018916 | 0.0019099 | 0.0019281 | 0.0019464 | 0.0019647 | 0.0019829 | 0.0020012
| SHP021-66719539 | 240 | 75 | 1.07e-05 | 0.00024602 | 1.5e-05 | 0.00034776 | 1.56e-05 | 0.00036232 | 1.2286e-07 | 3e-08 | 1.4509e-05 | 1.4631e-05 | 1.4754e-05 | 1.4877e-05 | 1.5e-05 | 1.503e-05 | 1.506e-05 | 1.509e-05 | 1.512e-05 | 1.515e-05 | 1.518e-05 | 1.521e-05 | 1.524e-05 | 1.527e-05 | 1.53e-05 | 1.533e-05 | 1.536e-05 | 1.539e-05 | 1.542e-05 | 1.545e-05 | 2.9068e-06 | 7.28e-07 | 0.00033613 | 0.00033904 | 0.00034195 | 0.00034485 | 0.00034776 | 0.00034849 | 0.00034922 | 0.00034994 | 0.00035067 | 0.0003514 | 0.00035213 | 0.00035286 | 0.00035358 | 0.00035431 | 0.00035504 | 0.00035577 | 0.0003565 | 0.00035722 | 0.00035795 | 0.00035868
| SHP021-85424826 | 132 | 64 | 0.0019236 | 6.18e-06 | 0.0026073 | 8.56e-06 | 0.0031691 | 1.07e-05 | 1.9533e-05 | 2.8093e-05 | 0.0025292 | 0.0025487 | 0.0025682 | 0.0025878 | 0.0026073 | 0.0026354 | 0.0026635 | 0.0026916 | 0.0027197 | 0.0027478 | 0.0027758 | 0.0028039 | 0.002832 | 0.0028601 | 0.0028882 | 0.0029163 | 0.0029444 | 0.0029725 | 0.0030006 | 0.0030287 | 6.8e-08 | 1.07e-07 | 8.288e-06 | 8.356e-06 | 8.424e-06 | 8.492e-06 | 8.56e-06 | 8.667e-06 | 8.774e-06 | 8.881e-06 | 8.988e-06 | 9.095e-06 | 9.202e-06 | 9.309e-06 | 9.416e-06 | 9.523e-06 | 9.63e-06 | 9.737e-06 | 9.844e-06 | 9.951e-06 | 1.0058e-05 | 1.0165e-05
| SSE011-15435228 | 1136 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE011-201930324 | 1125 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE012-152773219 | 1939 | 1939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE012-201930283 | 3007 | 1068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE013-201930225 | 2119 | 586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE013-74144019 | 1533 | 1533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE014-201930170 | 3891 | 2602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE014-24597938 | 1289 | 1289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE031-15437545 | 5875 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE031-201930106 | 5860 | 2939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE031-24597896 | 1460 | 1460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE031-24597910 | 1461 | 1461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE032-156444372 | 1568 | 1568 | 0.0013261 | 0 | 0.0017152 | 0 | 0.0017659 | 0 | 1.1116e-05 | 2.5342e-06 | 0.0016707 | 0.0016818 | 0.0016929 | 0.0017041 | 0.0017152 | 0.0017177 | 0.0017202 | 0.0017228 | 0.0017253 | 0.0017278 | 0.0017304 | 0.0017329 | 0.0017355 | 0.001738 | 0.0017405 | 0.0017431 | 0.0017456 | 0.0017481 | 0.0017507 | 0.0017532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE032-201929980 | 2957 | 1389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE033-201929907 | 3920 | 3920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE034-201929860 | 2597 | 1272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE034-24597952 | 1325 | 1325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL004-15415692 | 1614 | 1614 | 0.00232 | 0 | 0.0031194 | 0 | 0.0031589 | 0 | 2.284e-05 | 1.9771e-06 | 0.003028 | 0.0030508 | 0.0030737 | 0.0030965 | 0.0031194 | 0.0031213 | 0.0031233 | 0.0031253 | 0.0031273 | 0.0031293 | 0.0031312 | 0.0031332 | 0.0031352 | 0.0031372 | 0.0031391 | 0.0031411 | 0.0031431 | 0.0031451 | 0.0031471 | 0.003149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL005-141432115 | 21 | 21 | 0.0002489 | 0 | 0.0003254 | 0 | 0.00034151 | 0 | 2.1859e-06 | 8.0525e-07 | 0.00031666 | 0.00031885 | 0.00032103 | 0.00032322 | 0.0003254 | 0.00032621 | 0.00032701 | 0.00032782 | 0.00032862 | 0.00032943 | 0.00033023 | 0.00033104 | 0.00033185 | 0.00033265 | 0.00033346 | 0.00033426 | 0.00033507 | 0.00033587 | 0.00033668 | 0.00033748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL005-142032974 | 26 | 26 | 0.0020372 | 0 | 0.0028337 | 0 | 0.002791 | 0 | 2.2759e-05 | -2.1393e-06 | 0.0027427 | 0.0027655 | 0.0027882 | 0.002811 | 0.0028337 | 0.0028316 | 0.0028295 | 0.0028273 | 0.0028252 | 0.002823 | 0.0028209 | 0.0028188 | 0.0028166 | 0.0028145 | 0.0028124 | 0.0028102 | 0.0028081 | 0.0028059 | 0.0028038 | 0.0028017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL005-143031921 | 41 | 41 | 0.001201 | 0 | 0.0015719 | 0 | 0.0016259 | 0 | 1.0598e-05 | 2.6987e-06 | 0.0015295 | 0.0015401 | 0.0015507 | 0.0015613 | 0.0015719 | 0.0015746 | 0.0015773 | 0.00158 | 0.0015827 | 0.0015854 | 0.0015881 | 0.0015908 | 0.0015935 | 0.0015962 | 0.0015989 | 0.0016016 | 0.0016043 | 0.001607 | 0.0016097 | 0.0016124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL005-15415831 | 2555 | 1497 | 0.0035296 | 0.0009079 | 0.0049548 | 0.0012838 | 0.0050678 | 0.0013115 | 4.0721e-05 | 5.6477e-06 | 0.004792 | 0.0048327 | 0.0048734 | 0.0049141 | 0.0049548 | 0.0049605 | 0.0049661 | 0.0049718 | 0.0049774 | 0.0049831 | 0.0049887 | 0.0049944 | 0.005 | 0.0050057 | 0.0050113 | 0.005017 | 0.0050226 | 0.0050283 | 0.0050339 | 0.0050396 | 1.0739e-05 | 1.3852e-06 | 0.0012408 | 0.0012515 | 0.0012623 | 0.001273 | 0.0012838 | 0.0012851 | 0.0012865 | 0.0012879 | 0.0012893 | 0.0012907 | 0.0012921 | 0.0012934 | 0.0012948 | 0.0012962 | 0.0012976 | 0.001299 | 0.0013004 | 0.0013018 | 0.0013031 | 0.0013045
| STL005-155503897 | 20 | 20 | 4.5e-06 | 0 | 5.97e-06 | 0 | 6.52e-06 | 0 | 4.2e-08 | 2.75e-08 | 5.802e-06 | 5.844e-06 | 5.886e-06 | 5.928e-06 | 5.97e-06 | 5.9975e-06 | 6.025e-06 | 6.0525e-06 | 6.08e-06 | 6.1075e-06 | 6.135e-06 | 6.1625e-06 | 6.19e-06 | 6.2175e-06 | 6.245e-06 | 6.2725e-06 | 6.3e-06 | 6.3275e-06 | 6.355e-06 | 6.3825e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL005-164675419 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL005-24599604 | 721 | 654 | 0.0087368 | 0.001541 | 0.011244 | 0.0020338 | 0.011415 | 0.0020536 | 7.1625e-05 | 8.5495e-06 | 0.010957 | 0.011029 | 0.0111 | 0.011172 | 0.011244 | 0.011252 | 0.011261 | 0.011269 | 0.011278 | 0.011286 | 0.011295 | 0.011303 | 0.011312 | 0.011321 | 0.011329 | 0.011338 | 0.011346 | 0.011355 | 0.011363 | 0.011372 | 1.4083e-05 | 9.8535e-07 | 0.0019775 | 0.0019916 | 0.0020057 | 0.0020198 | 0.0020338 | 0.0020348 | 0.0020358 | 0.0020368 | 0.0020378 | 0.0020388 | 0.0020398 | 0.0020407 | 0.0020417 | 0.0020427 | 0.0020437 | 0.0020447 | 0.0020457 | 0.0020467 | 0.0020476 | 0.0020486
| STL005-24613578 | 266 | 186 | 0.0067522 | 0.0017548 | 0.0088386 | 0.0021848 | 0.0088009 | 0.0021621 | 5.9609e-05 | -1.8845e-06 | 0.0086001 | 0.0086597 | 0.0087193 | 0.0087789 | 0.0088386 | 0.0088367 | 0.0088348 | 0.0088329 | 0.008831 | 0.0088291 | 0.0088272 | 0.0088254 | 0.0088235 | 0.0088216 | 0.0088197 | 0.0088178 | 0.0088159 | 0.0088141 | 0.0088122 | 0.0088103 | 1.2286e-05 | -1.1308e-06 | 0.0021356 | 0.0021479 | 0.0021602 | 0.0021725 | 0.0021848 | 0.0021836 | 0.0021825 | 0.0021814 | 0.0021802 | 0.0021791 | 0.002178 | 0.0021769 | 0.0021757 | 0.0021746 | 0.0021735 | 0.0021723 | 0.0021712 | 0.0021701 | 0.0021689 | 0.0021678
| STL005-78736488 | 7 | 7 | 0.0023773 | 0 | 0.0031221 | 0 | 0.0030046 | 0 | 2.1279e-05 | -5.8769e-06 | 0.003037 | 0.0030583 | 0.0030795 | 0.0031008 | 0.0031221 | 0.0031162 | 0.0031104 | 0.0031045 | 0.0030986 | 0.0030927 | 0.0030868 | 0.003081 | 0.0030751 | 0.0030692 | 0.0030633 | 0.0030575 | 0.0030516 | 0.0030457 | 0.0030398 | 0.003034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL005-78747550 | 27 | 27 | 0.00035836 | 0 | 0.00048849 | 0 | 0.00048167 | 0 | 3.7179e-06 | -3.411e-07 | 0.00047362 | 0.00047733 | 0.00048105 | 0.00048477 | 0.00048849 | 0.00048815 | 0.00048781 | 0.00048746 | 0.00048712 | 0.00048678 | 0.00048644 | 0.0004861 | 0.00048576 | 0.00048542 | 0.00048508 | 0.00048474 | 0.00048439 | 0.00048405 | 0.00048371 | 0.00048337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL005-78747613 | 34 | 34 | 0.0019454 | 0 | 0.0027645 | 0 | 0.0026545 | 0 | 2.3404e-05 | -5.5017e-06 | 0.0026709 | 0.0026943 | 0.0027177 | 0.0027411 | 0.0027645 | 0.002759 | 0.0027535 | 0.002748 | 0.0027425 | 0.002737 | 0.0027315 | 0.002726 | 0.0027205 | 0.002715 | 0.0027095 | 0.002704 | 0.0026985 | 0.002693 | 0.0026875 | 0.002682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL005-84921818 | 1058 | 37 | 0.0039005 | 0.0024558 | 0.0053158 | 0.003384 | 0.0052633 | 0.0033529 | 4.0436e-05 | -2.6229e-06 | 0.005154 | 0.0051945 | 0.0052349 | 0.0052753 | 0.0053158 | 0.0053132 | 0.0053105 | 0.0053079 | 0.0053053 | 0.0053027 | 0.0053 | 0.0052974 | 0.0052948 | 0.0052922 | 0.0052896 | 0.0052869 | 0.0052843 | 0.0052817 | 0.0052791 | 0.0052764 | 2.6521e-05 | -1.5544e-06 | 0.0032779 | 0.0033045 | 0.003331 | 0.0033575 | 0.003384 | 0.0033825 | 0.0033809 | 0.0033794 | 0.0033778 | 0.0033763 | 0.0033747 | 0.0033731 | 0.0033716 | 0.00337 | 0.0033685 | 0.0033669 | 0.0033654 | 0.0033638 | 0.0033623 | 0.0033607
| STL006-144106192 | 47 | 47 | 0.00040692 | 0 | 0.00056785 | 0 | 0.00055566 | 0 | 4.5979e-06 | -6.095e-07 | 0.00054946 | 0.00055405 | 0.00055865 | 0.00056325 | 0.00056785 | 0.00056724 | 0.00056663 | 0.00056602 | 0.00056541 | 0.0005648 | 0.00056419 | 0.00056358 | 0.00056297 | 0.00056236 | 0.00056175 | 0.00056114 | 0.00056053 | 0.00055992 | 0.00055932 | 0.00055871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-144106506 | 29 | 29 | 2.82e-05 | 0 | 4.02e-05 | 0 | 4.17e-05 | 0 | 3.4286e-07 | 7.5e-08 | 3.8829e-05 | 3.9171e-05 | 3.9514e-05 | 3.9857e-05 | 4.02e-05 | 4.0275e-05 | 4.035e-05 | 4.0425e-05 | 4.05e-05 | 4.0575e-05 | 4.065e-05 | 4.0725e-05 | 4.08e-05 | 4.0875e-05 | 4.095e-05 | 4.1025e-05 | 4.11e-05 | 4.1175e-05 | 4.125e-05 | 4.1325e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-144106734 | 61 | 61 | 0.0093639 | 0 | 0.012789 | 0 | 0.012562 | 0 | 9.7865e-05 | -1.134e-05 | 0.012398 | 0.012496 | 0.012594 | 0.012691 | 0.012789 | 0.012778 | 0.012767 | 0.012755 | 0.012744 | 0.012733 | 0.012721 | 0.01271 | 0.012699 | 0.012687 | 0.012676 | 0.012664 | 0.012653 | 0.012642 | 0.01263 | 0.012619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-144631935 | 29 | 29 | 0.0036498 | 0 | 0.0053572 | 0 | 0.0053018 | 0 | 4.8783e-05 | -2.771e-06 | 0.0051621 | 0.0052109 | 0.0052597 | 0.0053084 | 0.0053572 | 0.0053545 | 0.0053517 | 0.0053489 | 0.0053461 | 0.0053434 | 0.0053406 | 0.0053378 | 0.0053351 | 0.0053323 | 0.0053295 | 0.0053267 | 0.005324 | 0.0053212 | 0.0053184 | 0.0053157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-144632294 | 41 | 41 | 0.0090683 | 0 | 0.013187 | 0 | 0.013047 | 0 | 0.00011767 | -6.9974e-06 | 0.012716 | 0.012834 | 0.012951 | 0.013069 | 0.013187 | 0.01318 | 0.013173 | 0.013166 | 0.013159 | 0.013152 | 0.013145 | 0.013138 | 0.013131 | 0.013124 | 0.013117 | 0.01311 | 0.013103 | 0.013096 | 0.013089 | 0.013082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-15415768 | 1605 | 56 | 0.0074777 | 0.0035127 | 0.0094949 | 0.0047714 | 0.0094326 | 0.0047734 | 5.7632e-05 | -3.1107e-06 | 0.0092643 | 0.009322 | 0.0093796 | 0.0094372 | 0.0094949 | 0.0094917 | 0.0094886 | 0.0094855 | 0.0094824 | 0.0094793 | 0.0094762 | 0.0094731 | 0.00947 | 0.0094669 | 0.0094637 | 0.0094606 | 0.0094575 | 0.0094544 | 0.0094513 | 0.0094482 | 3.5963e-05 | 9.975e-08 | 0.0046276 | 0.0046635 | 0.0046995 | 0.0047355 | 0.0047714 | 0.0047715 | 0.0047716 | 0.0047717 | 0.0047718 | 0.0047719 | 0.004772 | 0.0047721 | 0.0047722 | 0.0047723 | 0.0047724 | 0.0047725 | 0.0047726 | 0.0047727 | 0.0047728 | 0.0047729
| STL006-155132358 | 57 | 57 | 0.0026679 | 0 | 0.0038134 | 0 | 0.0040145 | 0 | 3.2729e-05 | 1.0054e-05 | 0.0036825 | 0.0037152 | 0.003748 | 0.0037807 | 0.0038134 | 0.0038235 | 0.0038335 | 0.0038436 | 0.0038536 | 0.0038637 | 0.0038737 | 0.0038838 | 0.0038938 | 0.0039039 | 0.003914 | 0.003924 | 0.0039341 | 0.0039441 | 0.0039542 | 0.0039642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155132567 | 13 | 13 | 3.51e-06 | 0 | 5.08e-06 | 0 | 5.37e-06 | 0 | 4.4857e-08 | 1.45e-08 | 4.9006e-06 | 4.9454e-06 | 4.9903e-06 | 5.0351e-06 | 5.08e-06 | 5.0945e-06 | 5.109e-06 | 5.1235e-06 | 5.138e-06 | 5.1525e-06 | 5.167e-06 | 5.1815e-06 | 5.196e-06 | 5.2105e-06 | 5.225e-06 | 5.2395e-06 | 5.254e-06 | 5.2685e-06 | 5.283e-06 | 5.2975e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155132685 | 40 | 40 | 0.0061086 | 0 | 0.0080806 | 0 | 0.008254 | 0 | 5.6343e-05 | 8.6707e-06 | 0.0078552 | 0.0079116 | 0.0079679 | 0.0080243 | 0.0080806 | 0.0080893 | 0.008098 | 0.0081066 | 0.0081153 | 0.008124 | 0.0081326 | 0.0081413 | 0.00815 | 0.0081586 | 0.0081673 | 0.008176 | 0.0081847 | 0.0081933 | 0.008202 | 0.0082107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155132926 | 17 | 17 | 0.0038539 | 0 | 0.0055466 | 0 | 0.0057798 | 0 | 4.8364e-05 | 1.1657e-05 | 0.0053532 | 0.0054016 | 0.0054499 | 0.0054983 | 0.0055466 | 0.0055583 | 0.00557 | 0.0055816 | 0.0055933 | 0.0056049 | 0.0056166 | 0.0056282 | 0.0056399 | 0.0056516 | 0.0056632 | 0.0056749 | 0.0056865 | 0.0056982 | 0.0057098 | 0.0057215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155133021 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155133103 | 24 | 24 | 0.0012101 | 0 | 0.0016566 | 0 | 0.0016319 | 0 | 1.2757e-05 | -1.2345e-06 | 0.0016056 | 0.0016184 | 0.0016311 | 0.0016439 | 0.0016566 | 0.0016554 | 0.0016542 | 0.0016529 | 0.0016517 | 0.0016505 | 0.0016492 | 0.001648 | 0.0016468 | 0.0016455 | 0.0016443 | 0.0016431 | 0.0016418 | 0.0016406 | 0.0016394 | 0.0016381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155133222 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155178765 | 42 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155178849 | 16 | 16 | 0.0023842 | 0 | 0.0035873 | 0 | 0.0035403 | 0 | 3.4374e-05 | -2.3491e-06 | 0.0034498 | 0.0034842 | 0.0035186 | 0.0035529 | 0.0035873 | 0.003585 | 0.0035826 | 0.0035803 | 0.0035779 | 0.0035756 | 0.0035732 | 0.0035709 | 0.0035685 | 0.0035662 | 0.0035638 | 0.0035615 | 0.0035591 | 0.0035568 | 0.0035544 | 0.0035521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155178947 | 15 | 15 | 0.0021453 | 0 | 0.0032329 | 0 | 0.003135 | 0 | 3.1073e-05 | -4.8941e-06 | 0.0031086 | 0.0031397 | 0.0031707 | 0.0032018 | 0.0032329 | 0.003228 | 0.0032231 | 0.0032182 | 0.0032133 | 0.0032084 | 0.0032035 | 0.0031986 | 0.0031937 | 0.0031888 | 0.0031839 | 0.003179 | 0.0031741 | 0.0031693 | 0.0031644 | 0.0031595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155179094 | 20 | 20 | 0.00056489 | 0 | 0.00082173 | 0 | 0.00079908 | 0 | 7.3384e-06 | -1.1328e-06 | 0.00079238 | 0.00079972 | 0.00080706 | 0.00081439 | 0.00082173 | 0.0008206 | 0.00081947 | 0.00081833 | 0.0008172 | 0.00081607 | 0.00081494 | 0.0008138 | 0.00081267 | 0.00081154 | 0.00081041 | 0.00080927 | 0.00080814 | 0.00080701 | 0.00080587 | 0.00080474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155189552 | 20 | 20 | 0.0021827 | 0 | 0.0033419 | 0 | 0.0033418 | 0 | 3.3122e-05 | -9.2e-09 | 0.0032095 | 0.0032426 | 0.0032757 | 0.0033088 | 0.0033419 | 0.0033419 | 0.0033419 | 0.0033419 | 0.0033419 | 0.0033419 | 0.0033419 | 0.0033419 | 0.0033419 | 0.0033419 | 0.0033418 | 0.0033418 | 0.0033418 | 0.0033418 | 0.0033418 | 0.0033418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155189674 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155189763 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155189877 | 36 | 36 | 1.04e-05 | 0 | 1.6e-05 | 0 | 1.71e-05 | 0 | 1.6e-07 | 5.5e-08 | 1.536e-05 | 1.552e-05 | 1.568e-05 | 1.584e-05 | 1.6e-05 | 1.6055e-05 | 1.611e-05 | 1.6165e-05 | 1.622e-05 | 1.6275e-05 | 1.633e-05 | 1.6385e-05 | 1.644e-05 | 1.6495e-05 | 1.655e-05 | 1.6605e-05 | 1.666e-05 | 1.6715e-05 | 1.677e-05 | 1.6825e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155190011 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155190105 | 10 | 10 | 0.0012745 | 0 | 0.0016643 | 0 | 0.0016767 | 0 | 1.1137e-05 | 6.2135e-07 | 0.0016198 | 0.0016309 | 0.001642 | 0.0016532 | 0.0016643 | 0.0016649 | 0.0016656 | 0.0016662 | 0.0016668 | 0.0016674 | 0.001668 | 0.0016687 | 0.0016693 | 0.0016699 | 0.0016705 | 0.0016711 | 0.0016718 | 0.0016724 | 0.001673 | 0.0016736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155193804 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155193946 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155249643 | 18 | 18 | 0.0015005 | 0 | 0.0021402 | 0 | 0.0021234 | 0 | 1.8277e-05 | -8.375e-07 | 0.0020671 | 0.0020853 | 0.0021036 | 0.0021219 | 0.0021402 | 0.0021393 | 0.0021385 | 0.0021377 | 0.0021368 | 0.002136 | 0.0021351 | 0.0021343 | 0.0021335 | 0.0021326 | 0.0021318 | 0.002131 | 0.0021301 | 0.0021293 | 0.0021284 | 0.0021276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155249816 | 21 | 21 | 0.0018396 | 0 | 0.0026785 | 0 | 0.0028551 | 0 | 2.3969e-05 | 8.8311e-06 | 0.0025826 | 0.0026066 | 0.0026306 | 0.0026545 | 0.0026785 | 0.0026873 | 0.0026962 | 0.002705 | 0.0027138 | 0.0027227 | 0.0027315 | 0.0027403 | 0.0027491 | 0.002758 | 0.0027668 | 0.0027756 | 0.0027845 | 0.0027933 | 0.0028021 | 0.002811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155250434 | 12 | 12 | 0.00042105 | 0 | 0.00060895 | 0 | 0.0006044 | 0 | 5.3683e-06 | -2.2715e-07 | 0.00058747 | 0.00059284 | 0.00059821 | 0.00060358 | 0.00060895 | 0.00060872 | 0.00060849 | 0.00060826 | 0.00060804 | 0.00060781 | 0.00060758 | 0.00060736 | 0.00060713 | 0.0006069 | 0.00060667 | 0.00060645 | 0.00060622 | 0.00060599 | 0.00060577 | 0.00060554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155392225 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-182934752 | 1260 | 352 | 8.85e-06 | 4.67e-05 | 1.36e-05 | 7.18e-05 | 1.35e-05 | 7.15e-05 | 1.3571e-07 | -5e-09 | 1.3057e-05 | 1.3193e-05 | 1.3329e-05 | 1.3464e-05 | 1.36e-05 | 1.3595e-05 | 1.359e-05 | 1.3585e-05 | 1.358e-05 | 1.3575e-05 | 1.357e-05 | 1.3565e-05 | 1.356e-05 | 1.3555e-05 | 1.355e-05 | 1.3545e-05 | 1.354e-05 | 1.3535e-05 | 1.353e-05 | 1.3525e-05 | 7.1714e-07 | -1.5e-08 | 6.8931e-05 | 6.9649e-05 | 7.0366e-05 | 7.1083e-05 | 7.18e-05 | 7.1785e-05 | 7.177e-05 | 7.1755e-05 | 7.174e-05 | 7.1725e-05 | 7.171e-05 | 7.1695e-05 | 7.168e-05 | 7.1665e-05 | 7.165e-05 | 7.1635e-05 | 7.162e-05 | 7.1605e-05 | 7.159e-05 | 7.1575e-05
| STL006-24599342 | 214 | 71 | 0.001554 | 0.00090556 | 0.0022202 | 0.0012979 | 0.0023339 | 0.0013659 | 1.9034e-05 | 5.6886e-06 | 0.002144 | 0.0021631 | 0.0021821 | 0.0022011 | 0.0022202 | 0.0022258 | 0.0022315 | 0.0022372 | 0.0022429 | 0.0022486 | 0.0022543 | 0.00226 | 0.0022657 | 0.0022714 | 0.002277 | 0.0022827 | 0.0022884 | 0.0022941 | 0.0022998 | 0.0023055 | 1.1211e-05 | 3.397e-06 | 0.0012531 | 0.0012643 | 0.0012755 | 0.0012867 | 0.0012979 | 0.0013013 | 0.0013047 | 0.0013081 | 0.0013115 | 0.0013149 | 0.0013183 | 0.0013217 | 0.0013251 | 0.0013285 | 0.0013319 | 0.0013353 | 0.0013387 | 0.0013421 | 0.0013455 | 0.0013489
| STL006-24601812 | 493 | 338 | 0.0017267 | 0.0014184 | 0.0023838 | 0.0020812 | 0.0023421 | 0.0020825 | 1.8775e-05 | -2.0865e-06 | 0.0023087 | 0.0023275 | 0.0023463 | 0.002365 | 0.0023838 | 0.0023817 | 0.0023796 | 0.0023775 | 0.0023755 | 0.0023734 | 0.0023713 | 0.0023692 | 0.0023671 | 0.002365 | 0.0023629 | 0.0023609 | 0.0023588 | 0.0023567 | 0.0023546 | 0.0023525 | 1.8937e-05 | 6.495e-08 | 0.0020054 | 0.0020244 | 0.0020433 | 0.0020622 | 0.0020812 | 0.0020812 | 0.0020813 | 0.0020814 | 0.0020814 | 0.0020815 | 0.0020816 | 0.0020816 | 0.0020817 | 0.0020818 | 0.0020818 | 0.0020819 | 0.0020819 | 0.002082 | 0.0020821 | 0.0020821
| STL006-24613426 | 1405 | 86 | 0.0055407 | 0.00045515 | 0.0076067 | 0.00067099 | 0.0077044 | 0.00068471 | 5.9027e-05 | 4.8843e-06 | 0.0073706 | 0.0074296 | 0.0074886 | 0.0075477 | 0.0076067 | 0.0076116 | 0.0076165 | 0.0076213 | 0.0076262 | 0.0076311 | 0.007636 | 0.0076409 | 0.0076458 | 0.0076506 | 0.0076555 | 0.0076604 | 0.0076653 | 0.0076702 | 0.0076751 | 0.00768 | 6.1671e-06 | 6.8575e-07 | 0.00064632 | 0.00065249 | 0.00065866 | 0.00066483 | 0.00067099 | 0.00067168 | 0.00067236 | 0.00067305 | 0.00067374 | 0.00067442 | 0.00067511 | 0.00067579 | 0.00067648 | 0.00067716 | 0.00067785 | 0.00067854 | 0.00067922 | 0.00067991 | 0.00068059 | 0.00068128
| STL006-56211052 | 144 | 28 | 0.00032647 | 0.0010089 | 0.00034602 | 0.001078 | 0.00034229 | 0.0010654 | 5.5863e-07 | -1.8695e-07 | 0.00034379 | 0.00034435 | 0.00034491 | 0.00034547 | 0.00034602 | 0.00034584 | 0.00034565 | 0.00034546 | 0.00034528 | 0.00034509 | 0.0003449 | 0.00034472 | 0.00034453 | 0.00034434 | 0.00034415 | 0.00034397 | 0.00034378 | 0.00034359 | 0.00034341 | 0.00034322 | 1.9746e-06 | -6.309e-07 | 0.0010701 | 0.0010721 | 0.001074 | 0.001076 | 0.001078 | 0.0010774 | 0.0010767 | 0.0010761 | 0.0010755 | 0.0010748 | 0.0010742 | 0.0010736 | 0.0010729 | 0.0010723 | 0.0010717 | 0.001071 | 0.0010704 | 0.0010698 | 0.0010692 | 0.0010685
| STL006-82629266 | 17 | 17 | 0.0017791 | 0 | 0.0024338 | 0 | 0.0023981 | 0 | 1.8705e-05 | -1.7859e-06 | 0.002359 | 0.0023777 | 0.0023964 | 0.0024151 | 0.0024338 | 0.002432 | 0.0024302 | 0.0024284 | 0.0024266 | 0.0024248 | 0.0024231 | 0.0024213 | 0.0024195 | 0.0024177 | 0.0024159 | 0.0024141 | 0.0024123 | 0.0024106 | 0.0024088 | 0.002407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-83365075 | 38 | 38 | 0.0016345 | 0 | 0.0022332 | 0 | 0.0021843 | 0 | 1.7104e-05 | -2.4456e-06 | 0.0021648 | 0.0021819 | 0.002199 | 0.0022161 | 0.0022332 | 0.0022307 | 0.0022283 | 0.0022258 | 0.0022234 | 0.002221 | 0.0022185 | 0.0022161 | 0.0022136 | 0.0022112 | 0.0022087 | 0.0022063 | 0.0022038 | 0.0022014 | 0.0021989 | 0.0021965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL007-143136191 | 70 | 70 | 3.42e-06 | 0 | 5.07e-06 | 0 | 5.27e-06 | 0 | 4.7143e-08 | 1e-08 | 4.8814e-06 | 4.9286e-06 | 4.9757e-06 | 5.0229e-06 | 5.07e-06 | 5.08e-06 | 5.09e-06 | 5.1e-06 | 5.11e-06 | 5.12e-06 | 5.13e-06 | 5.14e-06 | 5.15e-06 | 5.16e-06 | 5.17e-06 | 5.18e-06 | 5.19e-06 | 5.2e-06 | 5.21e-06 | 5.22e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL007-143136451 | 61 | 61 | 0.0013105 | 0 | 0.0020377 | 0 | 0.0020271 | 0 | 2.0778e-05 | -5.306e-07 | 0.0019546 | 0.0019753 | 0.0019961 | 0.0020169 | 0.0020377 | 0.0020371 | 0.0020366 | 0.0020361 | 0.0020356 | 0.002035 | 0.0020345 | 0.002034 | 0.0020334 | 0.0020329 | 0.0020324 | 0.0020318 | 0.0020313 | 0.0020308 | 0.0020303 | 0.0020297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL007-15415881 | 821 | 168 | 0.0042999 | 0.0019796 | 0.0055845 | 0.0026866 | 0.0056305 | 0.0027259 | 3.6704e-05 | 2.2995e-06 | 0.0054377 | 0.0054744 | 0.0055111 | 0.0055478 | 0.0055845 | 0.0055868 | 0.0055891 | 0.0055914 | 0.0055937 | 0.005596 | 0.0055983 | 0.0056006 | 0.0056029 | 0.0056052 | 0.0056075 | 0.0056098 | 0.0056121 | 0.0056144 | 0.0056167 | 0.005619 | 2.0201e-05 | 1.9636e-06 | 0.0026058 | 0.002626 | 0.0026462 | 0.0026664 | 0.0026866 | 0.0026886 | 0.0026905 | 0.0026925 | 0.0026945 | 0.0026964 | 0.0026984 | 0.0027003 | 0.0027023 | 0.0027043 | 0.0027062 | 0.0027082 | 0.0027102 | 0.0027121 | 0.0027141 | 0.002716
| STL007-155179441 | 10 | 10 | 2.62e-05 | 0 | 4e-05 | 0 | 4.04e-05 | 0 | 3.9429e-07 | 2e-08 | 3.8423e-05 | 3.8817e-05 | 3.9211e-05 | 3.9606e-05 | 4e-05 | 4.002e-05 | 4.004e-05 | 4.006e-05 | 4.008e-05 | 4.01e-05 | 4.012e-05 | 4.014e-05 | 4.016e-05 | 4.018e-05 | 4.02e-05 | 4.022e-05 | 4.024e-05 | 4.026e-05 | 4.028e-05 | 4.03e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL007-155179565 | 35 | 35 | 0.0014574 | 0 | 0.0019249 | 0 | 0.0019945 | 0 | 1.3356e-05 | 3.4791e-06 | 0.0018715 | 0.0018848 | 0.0018982 | 0.0019115 | 0.0019249 | 0.0019284 | 0.0019319 | 0.0019353 | 0.0019388 | 0.0019423 | 0.0019458 | 0.0019493 | 0.0019527 | 0.0019562 | 0.0019597 | 0.0019632 | 0.0019666 | 0.0019701 | 0.0019736 | 0.0019771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL007-155179964 | 17 | 17 | 0.00016949 | 0 | 0.00024219 | 0 | 0.00024683 | 0 | 2.0769e-06 | 2.323e-07 | 0.00023388 | 0.00023595 | 0.00023803 | 0.00024011 | 0.00024218 | 0.00024242 | 0.00024265 | 0.00024288 | 0.00024311 | 0.00024335 | 0.00024358 | 0.00024381 | 0.00024404 | 0.00024428 | 0.00024451 | 0.00024474 | 0.00024497 | 0.0002452 | 0.00024544 | 0.00024567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL007-162910244 | 40 | 40 | 0.0066683 | 0 | 0.0093843 | 0 | 0.0098273 | 0 | 7.7599e-05 | 2.2148e-05 | 0.0090739 | 0.0091515 | 0.0092291 | 0.0093067 | 0.0093843 | 0.0094065 | 0.0094286 | 0.0094507 | 0.0094729 | 0.009495 | 0.0095172 | 0.0095393 | 0.0095615 | 0.0095836 | 0.0096058 | 0.0096279 | 0.0096501 | 0.0096722 | 0.0096944 | 0.0097165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL007-183308767 | 10 | 10 | 5.36e-05 | 0 | 7.89e-05 | 0 | 8.16e-05 | 0 | 7.2286e-07 | 1.35e-07 | 7.6009e-05 | 7.6731e-05 | 7.7454e-05 | 7.8177e-05 | 7.89e-05 | 7.9035e-05 | 7.917e-05 | 7.9305e-05 | 7.944e-05 | 7.9575e-05 | 7.971e-05 | 7.9845e-05 | 7.998e-05 | 8.0115e-05 | 8.025e-05 | 8.0385e-05 | 8.052e-05 | 8.0655e-05 | 8.079e-05 | 8.0925e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL007-76065702 | 39 | 39 | 0.0015138 | 0 | 0.0020261 | 0 | 0.0019766 | 0 | 1.4639e-05 | -2.4765e-06 | 0.0019676 | 0.0019822 | 0.0019969 | 0.0020115 | 0.0020261 | 0.0020237 | 0.0020212 | 0.0020187 | 0.0020162 | 0.0020138 | 0.0020113 | 0.0020088 | 0.0020063 | 0.0020038 | 0.0020014 | 0.0019989 | 0.0019964 | 0.0019939 | 0.0019915 | 0.001989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL007-85224567 | 604 | 98 | 0.0018943 | 0.00060661 | 0.002575 | 0.00083533 | 0.0026265 | 0.00085356 | 1.9448e-05 | 2.5724e-06 | 0.0024973 | 0.0025167 | 0.0025361 | 0.0025556 | 0.002575 | 0.0025776 | 0.0025802 | 0.0025828 | 0.0025853 | 0.0025879 | 0.0025905 | 0.0025931 | 0.0025956 | 0.0025982 | 0.0026008 | 0.0026033 | 0.0026059 | 0.0026085 | 0.0026111 | 0.0026136 | 6.5349e-06 | 9.1115e-07 | 0.0008092 | 0.00081573 | 0.00082227 | 0.0008288 | 0.00083533 | 0.00083625 | 0.00083716 | 0.00083807 | 0.00083898 | 0.00083989 | 0.0008408 | 0.00084171 | 0.00084262 | 0.00084354 | 0.00084445 | 0.00084536 | 0.00084627 | 0.00084718 | 0.00084809 | 0.000849
| STL007-87836091 | 496 | 273 | 0.010583 | 0.0021799 | 0.012918 | 0.0029409 | 0.012996 | 0.0030402 | 6.6715e-05 | 3.9036e-06 | 0.012651 | 0.012718 | 0.012784 | 0.012851 | 0.012918 | 0.012922 | 0.012926 | 0.012929 | 0.012933 | 0.012937 | 0.012941 | 0.012945 | 0.012949 | 0.012953 | 0.012957 | 0.012961 | 0.012965 | 0.012968 | 0.012972 | 0.012976 | 2.1741e-05 | 4.9665e-06 | 0.0028539 | 0.0028756 | 0.0028974 | 0.0029191 | 0.0029409 | 0.0029458 | 0.0029508 | 0.0029558 | 0.0029607 | 0.0029657 | 0.0029707 | 0.0029756 | 0.0029806 | 0.0029856 | 0.0029905 | 0.0029955 | 0.0030005 | 0.0030054 | 0.0030104 | 0.0030154
| STN011-130745907 | 52 | 52 | 0.0010733 | 0 | 0.0014146 | 0 | 0.0014718 | 0 | 9.7516e-06 | 2.8589e-06 | 0.0013756 | 0.0013854 | 0.0013951 | 0.0014049 | 0.0014146 | 0.0014175 | 0.0014203 | 0.0014232 | 0.001426 | 0.0014289 | 0.0014318 | 0.0014346 | 0.0014375 | 0.0014403 | 0.0014432 | 0.0014461 | 0.0014489 | 0.0014518 | 0.0014546 | 0.0014575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN011-160424610 | 32 | 32 | 0.0012648 | 0 | 0.0016639 | 0 | 0.0017182 | 0 | 1.1402e-05 | 2.7173e-06 | 0.0016183 | 0.0016297 | 0.0016411 | 0.0016525 | 0.0016639 | 0.0016666 | 0.0016693 | 0.001672 | 0.0016747 | 0.0016775 | 0.0016802 | 0.0016829 | 0.0016856 | 0.0016883 | 0.001691 | 0.0016938 | 0.0016965 | 0.0016992 | 0.0017019 | 0.0017046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN011-164271487 | 15 | 15 | 1.31e-06 | 0 | 1.65e-06 | 0 | 1.93e-06 | 0 | 9.7143e-09 | 1.4e-08 | 1.6111e-06 | 1.6209e-06 | 1.6306e-06 | 1.6403e-06 | 1.65e-06 | 1.664e-06 | 1.678e-06 | 1.692e-06 | 1.706e-06 | 1.72e-06 | 1.734e-06 | 1.748e-06 | 1.762e-06 | 1.776e-06 | 1.79e-06 | 1.804e-06 | 1.818e-06 | 1.832e-06 | 1.846e-06 | 1.86e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN011-184475628 | 162 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN011-200055388 | 1015 | 788 | 0.0023234 | 0.00053476 | 0.0029088 | 0.00068855 | 0.0032339 | 0.00076114 | 1.6726e-05 | 1.6255e-05 | 0.0028419 | 0.0028586 | 0.0028753 | 0.002892 | 0.0029088 | 0.002925 | 0.0029413 | 0.0029575 | 0.0029738 | 0.00299 | 0.0030063 | 0.0030226 | 0.0030388 | 0.0030551 | 0.0030713 | 0.0030876 | 0.0031038 | 0.0031201 | 0.0031363 | 0.0031526 | 4.394e-06 | 3.6295e-06 | 0.00067097 | 0.00067536 | 0.00067976 | 0.00068415 | 0.00068855 | 0.00069218 | 0.0006958 | 0.00069943 | 0.00070306 | 0.00070669 | 0.00071032 | 0.00071395 | 0.00071758 | 0.00072121 | 0.00072484 | 0.00072847 | 0.0007321 | 0.00073573 | 0.00073936 | 0.00074299
| STN012-200055438 | 3409 | 1405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN012-72075245 | 2004 | 2004 | 4.63e-05 | 0 | 5.83e-05 | 0 | 7.44e-05 | 0 | 3.4286e-07 | 8.05e-07 | 5.6929e-05 | 5.7271e-05 | 5.7614e-05 | 5.7957e-05 | 5.83e-05 | 5.9105e-05 | 5.991e-05 | 6.0715e-05 | 6.152e-05 | 6.2325e-05 | 6.313e-05 | 6.3935e-05 | 6.474e-05 | 6.5545e-05 | 6.635e-05 | 6.7155e-05 | 6.796e-05 | 6.8765e-05 | 6.957e-05 | 7.0375e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN013-15421517 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN013-200055508 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN014-200055610 | 692 | 692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN021-164443076 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN021-164443183 | 46 | 46 | 0.00033724 | 0 | 0.0004346 | 0 | 0.00049731 | 0 | 2.7815e-06 | 3.1354e-06 | 0.00042347 | 0.00042625 | 0.00042903 | 0.00043182 | 0.0004346 | 0.00043773 | 0.00044087 | 0.000444 | 0.00044714 | 0.00045027 | 0.00045341 | 0.00045655 | 0.00045968 | 0.00046282 | 0.00046595 | 0.00046909 | 0.00047222 | 0.00047536 | 0.00047849 | 0.00048163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN021-193604803 | 896 | 838 | 0.0085034 | 0.00023222 | 0.010662 | 0.00029789 | 0.012249 | 0.00034954 | 6.1687e-05 | 7.9312e-05 | 0.010416 | 0.010477 | 0.010539 | 0.010601 | 0.010662 | 0.010742 | 0.010821 | 0.0109 | 0.01098 | 0.011059 | 0.011138 | 0.011218 | 0.011297 | 0.011376 | 0.011456 | 0.011535 | 0.011614 | 0.011693 | 0.011773 | 0.011852 | 1.8763e-06 | 2.5826e-06 | 0.00029038 | 0.00029226 | 0.00029414 | 0.00029601 | 0.00029789 | 0.00030047 | 0.00030305 | 0.00030564 | 0.00030822 | 0.0003108 | 0.00031338 | 0.00031597 | 0.00031855 | 0.00032113 | 0.00032371 | 0.0003263 | 0.00032888 | 0.00033146 | 0.00033405 | 0.00033663
| STN021-200055789 | 2008 | 1112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN022-200055843 | 2919 | 2919 | 2.13e-06 | 0 | 2.13e-06 | 0 | 2.13e-06 | 0 | 0 | 0 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 2.13e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN023-200055989 | 267 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN024-138232567 | 33 | 33 | 0.00062999 | 0 | 0.00082003 | 0 | 0.00090515 | 0 | 5.4298e-06 | 4.256e-06 | 0.00079831 | 0.00080374 | 0.00080917 | 0.0008146 | 0.00082003 | 0.00082429 | 0.00082854 | 0.0008328 | 0.00083706 | 0.00084131 | 0.00084557 | 0.00084982 | 0.00085408 | 0.00085834 | 0.00086259 | 0.00086685 | 0.0008711 | 0.00087536 | 0.00087962 | 0.00088387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN024-160253800 | 6 | 6 | 2.19e-06 | 0 | 3.03e-06 | 0 | 3.66e-06 | 0 | 2.4e-08 | 3.15e-08 | 2.934e-06 | 2.958e-06 | 2.982e-06 | 3.006e-06 | 3.03e-06 | 3.0615e-06 | 3.093e-06 | 3.1245e-06 | 3.156e-06 | 3.1875e-06 | 3.219e-06 | 3.2505e-06 | 3.282e-06 | 3.3135e-06 | 3.345e-06 | 3.3765e-06 | 3.408e-06 | 3.4395e-06 | 3.471e-06 | 3.5025e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN024-160253882 | 29 | 29 | 7.27e-07 | 0 | 9.89e-07 | 0 | 1.19e-06 | 0 | 7.4857e-09 | 1.005e-08 | 9.5906e-07 | 9.6654e-07 | 9.7403e-07 | 9.8151e-07 | 9.89e-07 | 9.9905e-07 | 1.0091e-06 | 1.0192e-06 | 1.0292e-06 | 1.0393e-06 | 1.0493e-06 | 1.0594e-06 | 1.0694e-06 | 1.0795e-06 | 1.0895e-06 | 1.0996e-06 | 1.1096e-06 | 1.1197e-06 | 1.1297e-06 | 1.1398e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN024-200056045 | 1222 | 753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN024-24605670 | 469 | 374 | 0.0011984 | 0.00019608 | 0.0015845 | 0.0002742 | 0.0016932 | 0.00030571 | 1.1032e-05 | 5.4336e-06 | 0.0015404 | 0.0015514 | 0.0015625 | 0.0015735 | 0.0015845 | 0.0015899 | 0.0015954 | 0.0016008 | 0.0016062 | 0.0016117 | 0.0016171 | 0.0016226 | 0.001628 | 0.0016334 | 0.0016389 | 0.0016443 | 0.0016497 | 0.0016552 | 0.0016606 | 0.001666 | 2.2319e-06 | 1.5754e-06 | 0.00026527 | 0.0002675 | 0.00026974 | 0.00027197 | 0.0002742 | 0.00027578 | 0.00027735 | 0.00027893 | 0.0002805 | 0.00028208 | 0.00028365 | 0.00028523 | 0.0002868 | 0.00028838 | 0.00028995 | 0.00029153 | 0.0002931 | 0.00029468 | 0.00029625 | 0.00029783
| STN024-24611992 | 27 | 27 | 1.3e-05 | 0 | 1.79e-05 | 0 | 2.16e-05 | 0 | 1.4e-07 | 1.85e-07 | 1.734e-05 | 1.748e-05 | 1.762e-05 | 1.776e-05 | 1.79e-05 | 1.8085e-05 | 1.827e-05 | 1.8455e-05 | 1.864e-05 | 1.8825e-05 | 1.901e-05 | 1.9195e-05 | 1.938e-05 | 1.9565e-05 | 1.975e-05 | 1.9935e-05 | 2.012e-05 | 2.0305e-05 | 2.049e-05 | 2.0675e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN031-200777976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN031-200778008 | 0 | 0 | 0.0024597 | 0 | 0.002915 | 0 | 0.0032114 | 0 | 1.3007e-05 | 1.4824e-05 | 0.0028629 | 0.0028759 | 0.002889 | 0.002902 | 0.002915 | 0.0029298 | 0.0029446 | 0.0029594 | 0.0029743 | 0.0029891 | 0.0030039 | 0.0030187 | 0.0030336 | 0.0030484 | 0.0030632 | 0.003078 | 0.0030929 | 0.0031077 | 0.0031225 | 0.0031373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU011-94649597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU012-24612934 | 1788 | 1788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU012-24613115 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU012-94649646 | 3551 | 1760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU013-94649695 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU015-24612538 | 2154 | 2154 | 0.00032587 | 0 | 0.00034665 | 0 | 0.0003566 | 0 | 5.938e-07 | 4.976e-07 | 0.00034428 | 0.00034487 | 0.00034546 | 0.00034606 | 0.00034665 | 0.00034715 | 0.00034765 | 0.00034814 | 0.00034864 | 0.00034914 | 0.00034964 | 0.00035013 | 0.00035063 | 0.00035113 | 0.00035163 | 0.00035212 | 0.00035262 | 0.00035312 | 0.00035362 | 0.00035412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU015-94649793 | 4994 | 661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU015-98840126 | 2179 | 2179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU021-40665700 | 1623 | 1623 | 0.00094117 | 0 | 0.0011778 | 0 | 0.0012895 | 0 | 6.7612e-06 | 5.5854e-06 | 0.0011508 | 0.0011575 | 0.0011643 | 0.001171 | 0.0011778 | 0.0011834 | 0.001189 | 0.0011946 | 0.0012002 | 0.0012057 | 0.0012113 | 0.0012169 | 0.0012225 | 0.0012281 | 0.0012337 | 0.0012392 | 0.0012448 | 0.0012504 | 0.001256 | 0.0012616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU021-94649866 | 3579 | 1956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU022-186913526 | 3568 | 3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU022-94649915 | 5302 | 1734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU023-94649964 | 1534 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU024-94650013 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU034-94650323 | 78 | 78 | 1.55e-06 | 0 | 2.13e-06 | 0 | 2.25e-06 | 0 | 1.6571e-08 | 6e-09 | 2.0637e-06 | 2.0803e-06 | 2.0969e-06 | 2.1134e-06 | 2.13e-06 | 2.136e-06 | 2.142e-06 | 2.148e-06 | 2.154e-06 | 2.16e-06 | 2.166e-06 | 2.172e-06 | 2.178e-06 | 2.184e-06 | 2.19e-06 | 2.196e-06 | 2.202e-06 | 2.208e-06 | 2.214e-06 | 2.22e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU035-183159191 | 3999 | 3999 | 0.00018651 | 0 | 0.00025248 | 0 | 0.00028403 | 0 | 1.8849e-06 | 1.5775e-06 | 0.00024494 | 0.00024682 | 0.00024871 | 0.00025059 | 0.00025248 | 0.00025406 | 0.00025563 | 0.00025721 | 0.00025879 | 0.00026037 | 0.00026194 | 0.00026352 | 0.0002651 | 0.00026668 | 0.00026825 | 0.00026983 | 0.00027141 | 0.00027299 | 0.00027456 | 0.00027614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU035-24612255 | 4993 | 994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU035-94650372 | 4993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA011-155056985 | 7297 | 7297 | 0.015332 | 0 | 0.021904 | 0 | 0.02432 | 0 | 0.00018777 | 0.0001208 | 0.021153 | 0.021341 | 0.021528 | 0.021716 | 0.021904 | 0.022025 | 0.022145 | 0.022266 | 0.022387 | 0.022508 | 0.022629 | 0.022749 | 0.02287 | 0.022991 | 0.023112 | 0.023233 | 0.023353 | 0.023474 | 0.023595 | 0.023716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA012-182581784 | 6941 | 6941 | 0.0055057 | 0 | 0.0077851 | 0 | 0.0084425 | 0 | 6.5125e-05 | 3.2871e-05 | 0.0075246 | 0.0075897 | 0.0076548 | 0.0077199 | 0.0077851 | 0.0078179 | 0.0078508 | 0.0078837 | 0.0079165 | 0.0079494 | 0.0079823 | 0.0080151 | 0.008048 | 0.0080809 | 0.0081138 | 0.0081466 | 0.0081795 | 0.0082124 | 0.0082452 | 0.0082781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA014-154750885 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA021-154751071 | 2495 | 633 | 0.010149 | 0.00015614 | 0.014733 | 0.00023169 | 0.016418 | 0.00025939 | 0.00013097 | 8.4249e-05 | 0.014209 | 0.01434 | 0.014471 | 0.014602 | 0.014733 | 0.014817 | 0.014901 | 0.014985 | 0.01507 | 0.015154 | 0.015238 | 0.015322 | 0.015407 | 0.015491 | 0.015575 | 0.015659 | 0.015744 | 0.015828 | 0.015912 | 0.015996 | 2.1586e-06 | 1.3851e-06 | 0.00022305 | 0.00022521 | 0.00022737 | 0.00022953 | 0.00023169 | 0.00023307 | 0.00023446 | 0.00023584 | 0.00023723 | 0.00023861 | 0.00024 | 0.00024138 | 0.00024277 | 0.00024415 | 0.00024554 | 0.00024693 | 0.00024831 | 0.0002497 | 0.00025108 | 0.00025247
| TNA021-158086216 | 1862 | 1862 | 0.00019902 | 0 | 0.00029532 | 0 | 0.00033063 | 0 | 2.7515e-06 | 1.7655e-06 | 0.00028432 | 0.00028707 | 0.00028982 | 0.00029257 | 0.00029532 | 0.00029709 | 0.00029885 | 0.00030062 | 0.00030238 | 0.00030415 | 0.00030591 | 0.00030768 | 0.00030945 | 0.00031121 | 0.00031298 | 0.00031474 | 0.00031651 | 0.00031827 | 0.00032004 | 0.0003218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA022-182581504 | 7362 | 2006 | 0.0049329 | 0.006587 | 0.0068496 | 0.008978 | 0.0074074 | 0.0096821 | 5.4763e-05 | 2.789e-05 | 0.0066306 | 0.0066853 | 0.0067401 | 0.0067949 | 0.0068496 | 0.0068775 | 0.0069054 | 0.0069333 | 0.0069612 | 0.0069891 | 0.007017 | 0.0070448 | 0.0070727 | 0.0071006 | 0.0071285 | 0.0071564 | 0.0071843 | 0.0072122 | 0.0072401 | 0.007268 | 6.8316e-05 | 3.5205e-05 | 0.0087048 | 0.0087731 | 0.0088414 | 0.0089097 | 0.008978 | 0.0090133 | 0.0090485 | 0.0090837 | 0.0091189 | 0.0091541 | 0.0091893 | 0.0092245 | 0.0092597 | 0.0092949 | 0.0093301 | 0.0093653 | 0.0094005 | 0.0094357 | 0.0094709 | 0.0095061
| TNA022-184844358 | 5356 | 56 | 0.0059422 | 0.00070636 | 0.0081507 | 0.00099125 | 0.0089227 | 0.0010903 | 6.3101e-05 | 3.8602e-05 | 0.0078983 | 0.0079614 | 0.0080245 | 0.0080876 | 0.0081507 | 0.0081893 | 0.0082279 | 0.0082665 | 0.0083051 | 0.0083437 | 0.0083823 | 0.0084209 | 0.0084595 | 0.0084981 | 0.0085367 | 0.0085753 | 0.0086139 | 0.0086525 | 0.0086911 | 0.0087297 | 8.1395e-06 | 4.9516e-06 | 0.00095869 | 0.00096683 | 0.00097497 | 0.00098311 | 0.00099125 | 0.0009962 | 0.0010012 | 0.0010061 | 0.0010111 | 0.001016 | 0.001021 | 0.0010259 | 0.0010309 | 0.0010358 | 0.0010408 | 0.0010457 | 0.0010507 | 0.0010556 | 0.0010606 | 0.0010655
| TNA022-187163239 | 3766 | 888 | 0.00038626 | 0 | 0.00060608 | 0 | 0.00064045 | 0 | 6.2808e-06 | 1.7184e-06 | 0.00058096 | 0.00058724 | 0.00059352 | 0.0005998 | 0.00060608 | 0.0006078 | 0.00060952 | 0.00061124 | 0.00061296 | 0.00061467 | 0.00061639 | 0.00061811 | 0.00061983 | 0.00062155 | 0.00062327 | 0.00062498 | 0.0006267 | 0.00062842 | 0.00063014 | 0.00063186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA022-194840439 | 1534 | 1534 | 0.0030477 | 0 | 0.0041606 | 0 | 0.0043367 | 0 | 3.1796e-05 | 8.8063e-06 | 0.0040334 | 0.0040652 | 0.004097 | 0.0041288 | 0.0041606 | 0.0041694 | 0.0041782 | 0.004187 | 0.0041958 | 0.0042046 | 0.0042134 | 0.0042222 | 0.004231 | 0.0042398 | 0.0042486 | 0.0042574 | 0.0042662 | 0.004275 | 0.0042838 | 0.0042926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA023-154633087 | 4874 | 4874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA023-154751161 | 4874 | 0 | 0.00011834 | 0 | 0.00011834 | 0 | 0.00011834 | 0 | 0 | 0 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0.00011834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA024-154751243 | 493 | 493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA031-188490107 | 2813 | 2813 | 0.00033437 | 0 | 0.00048295 | 0 | 0.0005254 | 0 | 4.2451e-06 | 2.1226e-06 | 0.00046597 | 0.00047021 | 0.00047446 | 0.0004787 | 0.00048295 | 0.00048507 | 0.00048719 | 0.00048932 | 0.00049144 | 0.00049356 | 0.00049568 | 0.00049781 | 0.00049993 | 0.00050205 | 0.00050417 | 0.0005063 | 0.00050842 | 0.00051054 | 0.00051266 | 0.00051479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA033-153234693 | 5554 | 5554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA033-178283696 | 6857 | 1303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA033-188490077 | 6922 | 65 | 6.41e-05 | 0 | 0.00010544 | 0 | 0.00010277 | 0 | 1.1811e-06 | -1.3345e-07 | 0.00010071 | 0.00010189 | 0.00010308 | 0.00010426 | 0.00010544 | 0.0001053 | 0.00010517 | 0.00010504 | 0.0001049 | 0.00010477 | 0.00010464 | 0.0001045 | 0.00010437 | 0.00010424 | 0.0001041 | 0.00010397 | 0.00010384 | 0.0001037 | 0.00010357 | 0.00010344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TQY021-185165057 | 2790 | 1061 | 0.0080426 | 0.00079908 | 0.011451 | 0.0011973 | 0.010832 | 0.0011356 | 9.7381e-05 | -3.0935e-05 | 0.011061 | 0.011159 | 0.011256 | 0.011354 | 0.011451 | 0.01142 | 0.011389 | 0.011358 | 0.011327 | 0.011296 | 0.011265 | 0.011234 | 0.011203 | 0.011172 | 0.011142 | 0.011111 | 0.01108 | 0.011049 | 0.011018 | 0.010987 | 1.1377e-05 | -3.0812e-06 | 0.0011518 | 0.0011631 | 0.0011745 | 0.0011859 | 0.0011973 | 0.0011942 | 0.0011911 | 0.001188 | 0.0011849 | 0.0011819 | 0.0011788 | 0.0011757 | 0.0011726 | 0.0011695 | 0.0011665 | 0.0011634 | 0.0011603 | 0.0011572 | 0.0011541 | 0.001151
| TQY021-187647017 | 4210 | 1420 | 0.0053208 | 0.0028197 | 0.007564 | 0.0043561 | 0.0066749 | 0.0038396 | 6.4089e-05 | -4.445e-05 | 0.0073076 | 0.0073717 | 0.0074358 | 0.0074999 | 0.007564 | 0.0075195 | 0.0074751 | 0.0074306 | 0.0073862 | 0.0073417 | 0.0072973 | 0.0072528 | 0.0072084 | 0.0071639 | 0.0071195 | 0.007075 | 0.0070306 | 0.0069861 | 0.0069417 | 0.0068972 | 4.3899e-05 | -2.5829e-05 | 0.0041805 | 0.0042244 | 0.0042683 | 0.0043122 | 0.0043561 | 0.0043303 | 0.0043045 | 0.0042787 | 0.0042528 | 0.004227 | 0.0042012 | 0.0041753 | 0.0041495 | 0.0041237 | 0.0040979 | 0.004072 | 0.0040462 | 0.0040204 | 0.0039945 | 0.0039687
| TQY021-192995237 | 4210 | 0 | 0.0057772 | 0.0011685 | 0.0085841 | 0.0017906 | 0.0084564 | 0.0017849 | 8.0198e-05 | -6.3835e-06 | 0.0082633 | 0.0083435 | 0.0084237 | 0.0085039 | 0.0085841 | 0.0085777 | 0.0085713 | 0.0085649 | 0.0085585 | 0.0085522 | 0.0085458 | 0.0085394 | 0.008533 | 0.0085266 | 0.0085202 | 0.0085139 | 0.0085075 | 0.0085011 | 0.0084947 | 0.0084883 | 1.7773e-05 | -2.8425e-07 | 0.0017195 | 0.0017373 | 0.001755 | 0.0017728 | 0.0017906 | 0.0017903 | 0.00179 | 0.0017897 | 0.0017894 | 0.0017892 | 0.0017889 | 0.0017886 | 0.0017883 | 0.001788 | 0.0017877 | 0.0017875 | 0.0017872 | 0.0017869 | 0.0017866 | 0.0017863
| TQY021-24613536 | 1729 | 1729 | 0.0058289 | 0 | 0.0061413 | 0 | 0.0056011 | 0 | 8.9266e-06 | -2.7009e-05 | 0.0061056 | 0.0061145 | 0.0061235 | 0.0061324 | 0.0061413 | 0.0061143 | 0.0060873 | 0.0060603 | 0.0060333 | 0.0060063 | 0.0059793 | 0.0059522 | 0.0059252 | 0.0058982 | 0.0058712 | 0.0058442 | 0.0058172 | 0.0057902 | 0.0057632 | 0.0057362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TQY022-192995279 | 3002 | 0 | 0.0037642 | 0.0025469 | 0.0045277 | 0.0035785 | 0.0044899 | 0.0036039 | 2.1813e-05 | -1.8883e-06 | 0.0044404 | 0.0044622 | 0.004484 | 0.0045058 | 0.0045277 | 0.0045258 | 0.0045239 | 0.004522 | 0.0045201 | 0.0045182 | 0.0045163 | 0.0045144 | 0.0045125 | 0.0045107 | 0.0045088 | 0.0045069 | 0.004505 | 0.0045031 | 0.0045012 | 0.0044993 | 2.9473e-05 | 1.2696e-06 | 0.0034606 | 0.0034901 | 0.0035195 | 0.003549 | 0.0035785 | 0.0035797 | 0.003581 | 0.0035823 | 0.0035836 | 0.0035848 | 0.0035861 | 0.0035874 | 0.0035886 | 0.0035899 | 0.0035912 | 0.0035924 | 0.0035937 | 0.003595 | 0.0035962 | 0.0035975
| TQY022-88336509 | 3002 | 3002 | 0.0042954 | 0 | 0.0059511 | 0 | 0.0056878 | 0 | 4.7305e-05 | -1.3164e-05 | 0.0057619 | 0.0058092 | 0.0058565 | 0.0059038 | 0.0059511 | 0.0059379 | 0.0059247 | 0.0059116 | 0.0058984 | 0.0058853 | 0.0058721 | 0.0058589 | 0.0058458 | 0.0058326 | 0.0058194 | 0.0058063 | 0.0057931 | 0.0057799 | 0.0057668 | 0.0057536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TQY031-156447550 | 2063 | 2063 | 0.01307 | 0 | 0.014167 | 0 | 0.012501 | 0 | 3.1343e-05 | -8.3269e-05 | 0.014041 | 0.014073 | 0.014104 | 0.014135 | 0.014167 | 0.014083 | 0.014 | 0.013917 | 0.013834 | 0.01375 | 0.013667 | 0.013584 | 0.0135 | 0.013417 | 0.013334 | 0.013251 | 0.013167 | 0.013084 | 0.013001 | 0.012918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TQY031-192995335 | 2063 | 0 | 0.0053769 | 0.0013203 | 0.006024 | 0.0014999 | 0.0050561 | 0.0012324 | 1.8489e-05 | -4.8398e-05 | 0.0059501 | 0.0059686 | 0.005987 | 0.0060055 | 0.006024 | 0.0059756 | 0.0059272 | 0.0058788 | 0.0058304 | 0.005782 | 0.0057336 | 0.0056852 | 0.0056368 | 0.0055884 | 0.00554 | 0.0054916 | 0.0054432 | 0.0053948 | 0.0053464 | 0.005298 | 5.131e-06 | -1.3378e-05 | 0.0014794 | 0.0014845 | 0.0014897 | 0.0014948 | 0.0014999 | 0.0014866 | 0.0014732 | 0.0014598 | 0.0014464 | 0.001433 | 0.0014197 | 0.0014063 | 0.0013929 | 0.0013795 | 0.0013662 | 0.0013528 | 0.0013394 | 0.001326 | 0.0013126 | 0.0012993
| TQY032-192995307 | 159 | 0 | 0.045178 | 0 | 0.055207 | 0 | 0.049044 | 0 | 0.00028656 | -0.00030817 | 0.054061 | 0.054348 | 0.054634 | 0.054921 | 0.055207 | 0.054899 | 0.054591 | 0.054283 | 0.053975 | 0.053666 | 0.053358 | 0.05305 | 0.052742 | 0.052434 | 0.052126 | 0.051817 | 0.051509 | 0.051201 | 0.050893 | 0.050585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-154491390 | 0 | 0 | 6.12e-06 | 0 | 9.34e-06 | 0 | 8.37e-06 | 0 | 9.2e-08 | -4.85e-08 | 8.972e-06 | 9.064e-06 | 9.156e-06 | 9.248e-06 | 9.34e-06 | 9.2915e-06 | 9.243e-06 | 9.1945e-06 | 9.146e-06 | 9.0975e-06 | 9.049e-06 | 9.0005e-06 | 8.952e-06 | 8.9035e-06 | 8.855e-06 | 8.8065e-06 | 8.758e-06 | 8.7095e-06 | 8.661e-06 | 8.6125e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158166546 | 0 | 0 | 7.08e-06 | 0 | 1.02e-05 | 0 | 8.76e-06 | 0 | 8.9143e-08 | -7.2e-08 | 9.8434e-06 | 9.9326e-06 | 1.0022e-05 | 1.0111e-05 | 1.02e-05 | 1.0128e-05 | 1.0056e-05 | 9.984e-06 | 9.912e-06 | 9.84e-06 | 9.768e-06 | 9.696e-06 | 9.624e-06 | 9.552e-06 | 9.48e-06 | 9.408e-06 | 9.336e-06 | 9.264e-06 | 9.192e-06 | 9.12e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158166806 | 0 | 0 | 2.94e-07 | 0 | 4.71e-07 | 0 | 3.28e-07 | 0 | 5.0571e-09 | -7.15e-09 | 4.5077e-07 | 4.5583e-07 | 4.6089e-07 | 4.6594e-07 | 4.71e-07 | 4.6385e-07 | 4.567e-07 | 4.4955e-07 | 4.424e-07 | 4.3525e-07 | 4.281e-07 | 4.2095e-07 | 4.138e-07 | 4.0665e-07 | 3.995e-07 | 3.9235e-07 | 3.852e-07 | 3.7805e-07 | 3.709e-07 | 3.6375e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158205190 | 0 | 0 | 5.92e-06 | 0 | 9.97e-06 | 0 | 9.64e-06 | 0 | 1.1571e-07 | -1.65e-08 | 9.5071e-06 | 9.6229e-06 | 9.7386e-06 | 9.8543e-06 | 9.97e-06 | 9.9535e-06 | 9.937e-06 | 9.9205e-06 | 9.904e-06 | 9.8875e-06 | 9.871e-06 | 9.8545e-06 | 9.838e-06 | 9.8215e-06 | 9.805e-06 | 9.7885e-06 | 9.772e-06 | 9.7555e-06 | 9.739e-06 | 9.7225e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158205316 | 0 | 0 | 4.16e-06 | 0 | 6.59e-06 | 0 | 4.55e-06 | 0 | 6.9429e-08 | -1.02e-07 | 6.3123e-06 | 6.3817e-06 | 6.4511e-06 | 6.5206e-06 | 6.59e-06 | 6.488e-06 | 6.386e-06 | 6.284e-06 | 6.182e-06 | 6.08e-06 | 5.978e-06 | 5.876e-06 | 5.774e-06 | 5.672e-06 | 5.57e-06 | 5.468e-06 | 5.366e-06 | 5.264e-06 | 5.162e-06 | 5.06e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158205503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158205673 | 0 | 0 | 6.81e-06 | 0 | 1.02e-05 | 0 | 7.27e-06 | 0 | 9.6857e-08 | -1.465e-07 | 9.8126e-06 | 9.9094e-06 | 1.0006e-05 | 1.0103e-05 | 1.02e-05 | 1.0054e-05 | 9.907e-06 | 9.7605e-06 | 9.614e-06 | 9.4675e-06 | 9.321e-06 | 9.1745e-06 | 9.028e-06 | 8.8815e-06 | 8.735e-06 | 8.5885e-06 | 8.442e-06 | 8.2955e-06 | 8.149e-06 | 8.0025e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158205847 | 0 | 0 | 4.85e-07 | 0 | 7.69e-07 | 0 | 5.87e-07 | 0 | 8.1143e-09 | -9.1e-09 | 7.3654e-07 | 7.4466e-07 | 7.5277e-07 | 7.6089e-07 | 7.69e-07 | 7.599e-07 | 7.508e-07 | 7.417e-07 | 7.326e-07 | 7.235e-07 | 7.144e-07 | 7.053e-07 | 6.962e-07 | 6.871e-07 | 6.78e-07 | 6.689e-07 | 6.598e-07 | 6.507e-07 | 6.416e-07 | 6.325e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-163035708 | 0 | 0 | 1.36e-06 | 0 | 2.47e-06 | 0 | 1.77e-06 | 0 | 3.1714e-08 | -3.5e-08 | 2.3431e-06 | 2.3749e-06 | 2.4066e-06 | 2.4383e-06 | 2.47e-06 | 2.435e-06 | 2.4e-06 | 2.365e-06 | 2.33e-06 | 2.295e-06 | 2.26e-06 | 2.225e-06 | 2.19e-06 | 2.155e-06 | 2.12e-06 | 2.085e-06 | 2.05e-06 | 2.015e-06 | 1.98e-06 | 1.945e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-163036120 | 0 | 0 | 0.00081518 | 0 | 0.0011976 | 0 | 0.0010484 | 0 | 1.0925e-05 | -7.4586e-06 | 0.0011539 | 0.0011648 | 0.0011757 | 0.0011866 | 0.0011976 | 0.0011901 | 0.0011826 | 0.0011752 | 0.0011677 | 0.0011603 | 0.0011528 | 0.0011453 | 0.0011379 | 0.0011304 | 0.001123 | 0.0011155 | 0.0011081 | 0.0011006 | 0.0010931 | 0.0010857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-24598160 | 0 | 0 | 4.43e-05 | 4.97e-05 | 6.13e-05 | 7.22e-05 | 5.1e-05 | 5.85e-05 | 4.8571e-07 | -5.15e-07 | 5.9357e-05 | 5.9843e-05 | 6.0329e-05 | 6.0814e-05 | 6.13e-05 | 6.0785e-05 | 6.027e-05 | 5.9755e-05 | 5.924e-05 | 5.8725e-05 | 5.821e-05 | 5.7695e-05 | 5.718e-05 | 5.6665e-05 | 5.615e-05 | 5.5635e-05 | 5.512e-05 | 5.4605e-05 | 5.409e-05 | 5.3575e-05 | 6.4286e-07 | -6.85e-07 | 6.9629e-05 | 7.0271e-05 | 7.0914e-05 | 7.1557e-05 | 7.22e-05 | 7.1515e-05 | 7.083e-05 | 7.0145e-05 | 6.946e-05 | 6.8775e-05 | 6.809e-05 | 6.7405e-05 | 6.672e-05 | 6.6035e-05 | 6.535e-05 | 6.4665e-05 | 6.398e-05 | 6.3295e-05 | 6.261e-05 | 6.1925e-05
| TRG002-24598202 | 0 | 0 | 1.73e-06 | 1.35e-06 | 1.73e-06 | 1.35e-06 | 1.73e-06 | 1.35e-06 | 0 | 0 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 1.73e-06 | 0 | 0 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06 | 1.35e-06
| TRG003-162785300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-162785510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-163036413 | 0 | 0 | 1.96e-05 | 0 | 1.96e-05 | 0 | 1.96e-05 | 0 | 0 | 0 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 1.96e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-163036890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-163037137 | 0 | 0 | 1.29e-06 | 0 | 2.11e-06 | 0 | 1.51e-06 | 0 | 2.3429e-08 | -3e-08 | 2.0163e-06 | 2.0397e-06 | 2.0631e-06 | 2.0866e-06 | 2.11e-06 | 2.08e-06 | 2.05e-06 | 2.02e-06 | 1.99e-06 | 1.96e-06 | 1.93e-06 | 1.9e-06 | 1.87e-06 | 1.84e-06 | 1.81e-06 | 1.78e-06 | 1.75e-06 | 1.72e-06 | 1.69e-06 | 1.66e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-163066379 | 0 | 0 | 7.63e-07 | 0 | 1.36e-06 | 0 | 1e-06 | 0 | 1.7057e-08 | -1.8e-08 | 1.2918e-06 | 1.3088e-06 | 1.3259e-06 | 1.3429e-06 | 1.36e-06 | 1.342e-06 | 1.324e-06 | 1.306e-06 | 1.288e-06 | 1.27e-06 | 1.252e-06 | 1.234e-06 | 1.216e-06 | 1.198e-06 | 1.18e-06 | 1.162e-06 | 1.144e-06 | 1.126e-06 | 1.108e-06 | 1.09e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-60700569 | 0 | 0 | 6.42e-08 | 0 | 7.52e-08 | 0 | 6.17e-08 | 0 | 3.1429e-10 | -6.75e-10 | 7.3943e-08 | 7.4257e-08 | 7.4571e-08 | 7.4886e-08 | 7.52e-08 | 7.4525e-08 | 7.385e-08 | 7.3175e-08 | 7.25e-08 | 7.1825e-08 | 7.115e-08 | 7.0475e-08 | 6.98e-08 | 6.9125e-08 | 6.845e-08 | 6.7775e-08 | 6.71e-08 | 6.6425e-08 | 6.575e-08 | 6.5075e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG004-158007081 | 0 | 0 | 7.62e-08 | 0 | 7.62e-08 | 0 | 7.62e-08 | 0 | 0 | 0 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 7.62e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG004-162802539 | 0 | 0 | 7.12e-06 | 0 | 1.29e-05 | 0 | 9.1e-06 | 0 | 1.6514e-07 | -1.9e-07 | 1.2239e-05 | 1.2405e-05 | 1.257e-05 | 1.2735e-05 | 1.29e-05 | 1.271e-05 | 1.252e-05 | 1.233e-05 | 1.214e-05 | 1.195e-05 | 1.176e-05 | 1.157e-05 | 1.138e-05 | 1.119e-05 | 1.1e-05 | 1.081e-05 | 1.062e-05 | 1.043e-05 | 1.024e-05 | 1.005e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG004-24598258 | 0 | 0 | 1.18e-06 | 1.66e-09 | 1.2e-06 | 1.66e-09 | 1.19e-06 | 1.66e-09 | 5.7143e-10 | -5e-10 | 1.1977e-06 | 1.1983e-06 | 1.1989e-06 | 1.1994e-06 | 1.2e-06 | 1.1995e-06 | 1.199e-06 | 1.1985e-06 | 1.198e-06 | 1.1975e-06 | 1.197e-06 | 1.1965e-06 | 1.196e-06 | 1.1955e-06 | 1.195e-06 | 1.1945e-06 | 1.194e-06 | 1.1935e-06 | 1.193e-06 | 1.1925e-06 | 0 | 0 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09 | 1.66e-09
| TRG005-117365806 | 0 | 0 | 1.13e-06 | 0 | 1.45e-06 | 0 | 9.34e-07 | 0 | 9.1429e-09 | -2.58e-08 | 1.4134e-06 | 1.4226e-06 | 1.4317e-06 | 1.4409e-06 | 1.45e-06 | 1.4242e-06 | 1.3984e-06 | 1.3726e-06 | 1.3468e-06 | 1.321e-06 | 1.2952e-06 | 1.2694e-06 | 1.2436e-06 | 1.2178e-06 | 1.192e-06 | 1.1662e-06 | 1.1404e-06 | 1.1146e-06 | 1.0888e-06 | 1.063e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG005-158041024 | 0 | 0 | 1.55e-06 | 0 | 2.49e-06 | 0 | 1.55e-06 | 0 | 2.6857e-08 | -4.7e-08 | 2.3826e-06 | 2.4094e-06 | 2.4363e-06 | 2.4631e-06 | 2.49e-06 | 2.443e-06 | 2.396e-06 | 2.349e-06 | 2.302e-06 | 2.255e-06 | 2.208e-06 | 2.161e-06 | 2.114e-06 | 2.067e-06 | 2.02e-06 | 1.973e-06 | 1.926e-06 | 1.879e-06 | 1.832e-06 | 1.785e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG005-162822850 | 0 | 0 | 1.37e-06 | 0 | 2.25e-06 | 0 | 1.31e-06 | 0 | 2.5143e-08 | -4.7e-08 | 2.1494e-06 | 2.1746e-06 | 2.1997e-06 | 2.2249e-06 | 2.25e-06 | 2.203e-06 | 2.156e-06 | 2.109e-06 | 2.062e-06 | 2.015e-06 | 1.968e-06 | 1.921e-06 | 1.874e-06 | 1.827e-06 | 1.78e-06 | 1.733e-06 | 1.686e-06 | 1.639e-06 | 1.592e-06 | 1.545e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG005-162823024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG005-24598286 | 0 | 0 | 0.00010876 | 1.64e-06 | 0.00016407 | 2.62e-06 | 0.0001136 | 1.64e-06 | 1.5805e-06 | -2.5236e-06 | 0.00015775 | 0.00015933 | 0.00016091 | 0.00016249 | 0.00016407 | 0.00016155 | 0.00015903 | 0.0001565 | 0.00015398 | 0.00015146 | 0.00014893 | 0.00014641 | 0.00014389 | 0.00014136 | 0.00013884 | 0.00013631 | 0.00013379 | 0.00013127 | 0.00012874 | 0.00012622 | 2.8e-08 | -4.9e-08 | 2.508e-06 | 2.536e-06 | 2.564e-06 | 2.592e-06 | 2.62e-06 | 2.571e-06 | 2.522e-06 | 2.473e-06 | 2.424e-06 | 2.375e-06 | 2.326e-06 | 2.277e-06 | 2.228e-06 | 2.179e-06 | 2.13e-06 | 2.081e-06 | 2.032e-06 | 1.983e-06 | 1.934e-06 | 1.885e-06
| TRG005-60700588 | 0 | 0 | 1.09e-06 | 0 | 2.72e-06 | 0 | 1.53e-06 | 0 | 4.6571e-08 | -5.95e-08 | 2.5337e-06 | 2.5803e-06 | 2.6269e-06 | 2.6734e-06 | 2.72e-06 | 2.6605e-06 | 2.601e-06 | 2.5415e-06 | 2.482e-06 | 2.4225e-06 | 2.363e-06 | 2.3035e-06 | 2.244e-06 | 2.1845e-06 | 2.125e-06 | 2.0655e-06 | 2.006e-06 | 1.9465e-06 | 1.887e-06 | 1.8275e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG005-74127795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG011-185851173 | 433 | 433 | 0.0025644 | 0 | 0.003759 | 0 | 0.0030227 | 0 | 3.4132e-05 | -3.6816e-05 | 0.0036225 | 0.0036566 | 0.0036907 | 0.0037249 | 0.003759 | 0.0037222 | 0.0036854 | 0.0036486 | 0.0036117 | 0.0035749 | 0.0035381 | 0.0035013 | 0.0034645 | 0.0034277 | 0.0033908 | 0.003354 | 0.0033172 | 0.0032804 | 0.0032436 | 0.0032068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-162785300 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-162785510 | 16 | 16 | 1.45e-06 | 0 | 2.09e-06 | 0 | 1.57e-06 | 0 | 1.8286e-08 | -2.6e-08 | 2.0169e-06 | 2.0351e-06 | 2.0534e-06 | 2.0717e-06 | 2.09e-06 | 2.064e-06 | 2.038e-06 | 2.012e-06 | 1.986e-06 | 1.96e-06 | 1.934e-06 | 1.908e-06 | 1.882e-06 | 1.856e-06 | 1.83e-06 | 1.804e-06 | 1.778e-06 | 1.752e-06 | 1.726e-06 | 1.7e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-162806327 | 10 | 10 | 4.38e-05 | 0 | 9.18e-05 | 0 | 6.43e-05 | 0 | 1.3714e-06 | -1.375e-06 | 8.6314e-05 | 8.7686e-05 | 8.9057e-05 | 9.0429e-05 | 9.18e-05 | 9.0425e-05 | 8.905e-05 | 8.7675e-05 | 8.63e-05 | 8.4925e-05 | 8.355e-05 | 8.2175e-05 | 8.08e-05 | 7.9425e-05 | 7.805e-05 | 7.6675e-05 | 7.53e-05 | 7.3925e-05 | 7.255e-05 | 7.1175e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-162823585 | 24 | 24 | 0.00034092 | 0 | 0.00048919 | 0 | 0.00038784 | 0 | 4.2364e-06 | -5.0676e-06 | 0.00047224 | 0.00047648 | 0.00048072 | 0.00048495 | 0.00048919 | 0.00048412 | 0.00047905 | 0.00047399 | 0.00046892 | 0.00046385 | 0.00045878 | 0.00045372 | 0.00044865 | 0.00044358 | 0.00043851 | 0.00043345 | 0.00042838 | 0.00042331 | 0.00041824 | 0.00041317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-162823910 | 18 | 18 | 4.3e-06 | 0 | 6.98e-06 | 0 | 4.84e-06 | 0 | 7.6571e-08 | -1.07e-07 | 6.6737e-06 | 6.7503e-06 | 6.8269e-06 | 6.9034e-06 | 6.98e-06 | 6.873e-06 | 6.766e-06 | 6.659e-06 | 6.552e-06 | 6.445e-06 | 6.338e-06 | 6.231e-06 | 6.124e-06 | 6.017e-06 | 5.91e-06 | 5.803e-06 | 5.696e-06 | 5.589e-06 | 5.482e-06 | 5.375e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-162824119 | 18 | 18 | 6.93e-08 | 0 | 1.73e-07 | 0 | 9.7e-08 | 0 | 2.9629e-09 | -3.8e-09 | 1.6115e-07 | 1.6411e-07 | 1.6707e-07 | 1.7004e-07 | 1.73e-07 | 1.692e-07 | 1.654e-07 | 1.616e-07 | 1.578e-07 | 1.54e-07 | 1.502e-07 | 1.464e-07 | 1.426e-07 | 1.388e-07 | 1.35e-07 | 1.312e-07 | 1.274e-07 | 1.236e-07 | 1.198e-07 | 1.16e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-163036413 | 3 | 3 | 1.48e-07 | 0 | 2.24e-07 | 0 | 1.73e-07 | 0 | 2.1714e-09 | -2.55e-09 | 2.1531e-07 | 2.1749e-07 | 2.1966e-07 | 2.2183e-07 | 2.24e-07 | 2.2145e-07 | 2.189e-07 | 2.1635e-07 | 2.138e-07 | 2.1125e-07 | 2.087e-07 | 2.0615e-07 | 2.036e-07 | 2.0105e-07 | 1.985e-07 | 1.9595e-07 | 1.934e-07 | 1.9085e-07 | 1.883e-07 | 1.8575e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-163036626 | 2 | 2 | 6.71e-08 | 0 | 1.81e-07 | 0 | 1.21e-07 | 0 | 3.2543e-09 | -3e-09 | 1.6798e-07 | 1.7124e-07 | 1.7449e-07 | 1.7775e-07 | 1.81e-07 | 1.78e-07 | 1.75e-07 | 1.72e-07 | 1.69e-07 | 1.66e-07 | 1.63e-07 | 1.6e-07 | 1.57e-07 | 1.54e-07 | 1.51e-07 | 1.48e-07 | 1.45e-07 | 1.42e-07 | 1.39e-07 | 1.36e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-163036890 | 10 | 10 | 2.96e-07 | 0 | 5.58e-07 | 0 | 3.76e-07 | 0 | 7.4857e-09 | -9.1e-09 | 5.2806e-07 | 5.3554e-07 | 5.4303e-07 | 5.5051e-07 | 5.58e-07 | 5.489e-07 | 5.398e-07 | 5.307e-07 | 5.216e-07 | 5.125e-07 | 5.034e-07 | 4.943e-07 | 4.852e-07 | 4.761e-07 | 4.67e-07 | 4.579e-07 | 4.488e-07 | 4.397e-07 | 4.306e-07 | 4.215e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-163037137 | 5 | 5 | 0.00034565 | 0 | 0.00047457 | 0 | 0.00038446 | 0 | 3.6834e-06 | -4.5055e-06 | 0.00045983 | 0.00046352 | 0.0004672 | 0.00047088 | 0.00047457 | 0.00047006 | 0.00046556 | 0.00046105 | 0.00045654 | 0.00045204 | 0.00044753 | 0.00044303 | 0.00043852 | 0.00043402 | 0.00042951 | 0.00042501 | 0.0004205 | 0.00041599 | 0.00041149 | 0.00040698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-163037241 | 4 | 4 | 0.0003891 | 0 | 0.00053997 | 0 | 0.00043402 | 0 | 4.3108e-06 | -5.2977e-06 | 0.00052273 | 0.00052704 | 0.00053135 | 0.00053566 | 0.00053997 | 0.00053468 | 0.00052938 | 0.00052408 | 0.00051878 | 0.00051349 | 0.00050819 | 0.00050289 | 0.00049759 | 0.0004923 | 0.000487 | 0.0004817 | 0.0004764 | 0.0004711 | 0.00046581 | 0.00046051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-163065605 | 18 | 18 | 3.91e-06 | 0 | 6.13e-06 | 0 | 4.38e-06 | 0 | 6.3429e-08 | -8.75e-08 | 5.8763e-06 | 5.9397e-06 | 6.0031e-06 | 6.0666e-06 | 6.13e-06 | 6.0425e-06 | 5.955e-06 | 5.8675e-06 | 5.78e-06 | 5.6925e-06 | 5.605e-06 | 5.5175e-06 | 5.43e-06 | 5.3425e-06 | 5.255e-06 | 5.1675e-06 | 5.08e-06 | 4.9925e-06 | 4.905e-06 | 4.8175e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-163065814 | 10 | 10 | 1.83e-05 | 0 | 2.46e-05 | 0 | 1.86e-05 | 0 | 1.8e-07 | -3e-07 | 2.388e-05 | 2.406e-05 | 2.424e-05 | 2.442e-05 | 2.46e-05 | 2.43e-05 | 2.4e-05 | 2.37e-05 | 2.34e-05 | 2.31e-05 | 2.28e-05 | 2.25e-05 | 2.22e-05 | 2.19e-05 | 2.16e-05 | 2.13e-05 | 2.1e-05 | 2.07e-05 | 2.04e-05 | 2.01e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-163066137 | 16 | 16 | 0.00026431 | 0 | 0.00048861 | 0 | 0.00032511 | 0 | 6.4087e-06 | -8.1751e-06 | 0.00046298 | 0.00046939 | 0.0004758 | 0.00048221 | 0.00048862 | 0.00048044 | 0.00047226 | 0.00046409 | 0.00045591 | 0.00044774 | 0.00043956 | 0.00043139 | 0.00042321 | 0.00041504 | 0.00040686 | 0.00039869 | 0.00039051 | 0.00038234 | 0.00037416 | 0.00036599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-163066379 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-163066765 | 9 | 9 | 2.54e-05 | 0 | 4.52e-05 | 0 | 3.08e-05 | 0 | 5.6571e-07 | -7.2e-07 | 4.2937e-05 | 4.3503e-05 | 4.4069e-05 | 4.4634e-05 | 4.52e-05 | 4.448e-05 | 4.376e-05 | 4.304e-05 | 4.232e-05 | 4.16e-05 | 4.088e-05 | 4.016e-05 | 3.944e-05 | 3.872e-05 | 3.8e-05 | 3.728e-05 | 3.656e-05 | 3.584e-05 | 3.512e-05 | 3.44e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-176898414 | 668 | 208 | 0.00063266 | 0.00057061 | 0.00098314 | 0.00090884 | 0.00068375 | 0.00061916 | 1.0014e-05 | -1.4969e-05 | 0.00094308 | 0.0009531 | 0.00096311 | 0.00097312 | 0.00098314 | 0.00096817 | 0.0009532 | 0.00093823 | 0.00092326 | 0.00090829 | 0.00089332 | 0.00087835 | 0.00086338 | 0.00084841 | 0.00083344 | 0.00081848 | 0.00080351 | 0.00078854 | 0.00077357 | 0.0007586 | 9.6637e-06 | -1.4484e-05 | 0.00087018 | 0.00087985 | 0.00088951 | 0.00089917 | 0.00090884 | 0.00089435 | 0.00087987 | 0.00086539 | 0.0008509 | 0.00083642 | 0.00082194 | 0.00080745 | 0.00079297 | 0.00077849 | 0.000764 | 0.00074952 | 0.00073503 | 0.00072055 | 0.00070607 | 0.00069158
| TRG013-176898441 | 1379 | 644 | 0.00011138 | 0.00030182 | 0.00015506 | 0.00042687 | 0.00012396 | 0.00033826 | 1.248e-06 | -1.5551e-06 | 0.00015007 | 0.00015132 | 0.00015257 | 0.00015381 | 0.00015506 | 0.00015351 | 0.00015195 | 0.0001504 | 0.00014884 | 0.00014729 | 0.00014573 | 0.00014418 | 0.00014262 | 0.00014107 | 0.00013951 | 0.00013795 | 0.0001364 | 0.00013484 | 0.00013329 | 0.00013173 | 3.5728e-06 | -4.4302e-06 | 0.00041257 | 0.00041615 | 0.00041972 | 0.00042329 | 0.00042687 | 0.00042244 | 0.00041801 | 0.00041358 | 0.00040914 | 0.00040471 | 0.00040028 | 0.00039585 | 0.00039142 | 0.00038699 | 0.00038256 | 0.00037813 | 0.0003737 | 0.00036927 | 0.00036484 | 0.00036041
| TRG013-185851126 | 1717 | 310 | 0.0017127 | 0.00015691 | 0.0023899 | 0.00023815 | 0.0019492 | 0.00018462 | 1.9349e-05 | -2.2037e-05 | 0.0023125 | 0.0023319 | 0.0023512 | 0.0023706 | 0.0023899 | 0.0023679 | 0.0023458 | 0.0023238 | 0.0023018 | 0.0022797 | 0.0022577 | 0.0022357 | 0.0022136 | 0.0021916 | 0.0021696 | 0.0021475 | 0.0021255 | 0.0021034 | 0.0020814 | 0.0020594 | 2.3211e-06 | -2.6767e-06 | 0.00022887 | 0.00023119 | 0.00023351 | 0.00023583 | 0.00023815 | 0.00023547 | 0.0002328 | 0.00023012 | 0.00022744 | 0.00022477 | 0.00022209 | 0.00021941 | 0.00021674 | 0.00021406 | 0.00021138 | 0.00020871 | 0.00020603 | 0.00020335 | 0.00020068 | 0.000198
| TRG013-60700569 | 382 | 382 | 0.0011216 | 0 | 0.0012089 | 0 | 0.001101 | 0 | 2.4942e-06 | -5.391e-06 | 0.0011989 | 0.0012014 | 0.0012039 | 0.0012064 | 0.0012089 | 0.0012035 | 0.0011981 | 0.0011927 | 0.0011873 | 0.0011819 | 0.0011765 | 0.0011711 | 0.0011657 | 0.0011603 | 0.001155 | 0.0011496 | 0.0011442 | 0.0011388 | 0.0011334 | 0.001128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG014-158007081 | 16 | 16 | 3.99e-06 | 0 | 6.12e-06 | 0 | 3.86e-06 | 0 | 6.0857e-08 | -1.13e-07 | 5.8766e-06 | 5.9374e-06 | 5.9983e-06 | 6.0591e-06 | 6.12e-06 | 6.007e-06 | 5.894e-06 | 5.781e-06 | 5.668e-06 | 5.555e-06 | 5.442e-06 | 5.329e-06 | 5.216e-06 | 5.103e-06 | 4.99e-06 | 4.877e-06 | 4.764e-06 | 4.651e-06 | 4.538e-06 | 4.425e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG014-162802339 | 14 | 14 | 5.37e-05 | 0 | 7.17e-05 | 0 | 5.24e-05 | 0 | 5.1429e-07 | -9.65e-07 | 6.9643e-05 | 7.0157e-05 | 7.0671e-05 | 7.1186e-05 | 7.17e-05 | 7.0735e-05 | 6.977e-05 | 6.8805e-05 | 6.784e-05 | 6.6875e-05 | 6.591e-05 | 6.4945e-05 | 6.398e-05 | 6.3015e-05 | 6.205e-05 | 6.1085e-05 | 6.012e-05 | 5.9155e-05 | 5.819e-05 | 5.7225e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG014-162802539 | 7 | 7 | 0.00013688 | 0 | 0.00020774 | 0 | 0.00016199 | 0 | 2.0246e-06 | -2.2875e-06 | 0.00019965 | 0.00020167 | 0.00020369 | 0.00020572 | 0.00020774 | 0.00020546 | 0.00020317 | 0.00020088 | 0.00019859 | 0.00019631 | 0.00019402 | 0.00019173 | 0.00018944 | 0.00018716 | 0.00018487 | 0.00018258 | 0.00018029 | 0.00017801 | 0.00017572 | 0.00017343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG014-182935203 | 18 | 18 | 2.32e-06 | 0 | 3.26e-06 | 0 | 2.46e-06 | 0 | 2.6857e-08 | -4e-08 | 3.1526e-06 | 3.1794e-06 | 3.2063e-06 | 3.2331e-06 | 3.26e-06 | 3.22e-06 | 3.18e-06 | 3.14e-06 | 3.1e-06 | 3.06e-06 | 3.02e-06 | 2.98e-06 | 2.94e-06 | 2.9e-06 | 2.86e-06 | 2.82e-06 | 2.78e-06 | 2.74e-06 | 2.7e-06 | 2.66e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG014-185851238 | 1623 | 1122 | 0.0011043 | 1.67e-05 | 0.0016271 | 2.78e-05 | 0.0013443 | 2.18e-05 | 1.4936e-05 | -1.4141e-05 | 0.0015674 | 0.0015823 | 0.0015972 | 0.0016122 | 0.0016271 | 0.001613 | 0.0015988 | 0.0015847 | 0.0015705 | 0.0015564 | 0.0015423 | 0.0015281 | 0.001514 | 0.0014998 | 0.0014857 | 0.0014716 | 0.0014574 | 0.0014433 | 0.0014291 | 0.001415 | 3.1714e-07 | -3e-07 | 2.6531e-05 | 2.6849e-05 | 2.7166e-05 | 2.7483e-05 | 2.78e-05 | 2.75e-05 | 2.72e-05 | 2.69e-05 | 2.66e-05 | 2.63e-05 | 2.6e-05 | 2.57e-05 | 2.54e-05 | 2.51e-05 | 2.48e-05 | 2.45e-05 | 2.42e-05 | 2.39e-05 | 2.36e-05 | 2.33e-05
| TRG014-24598258 | 501 | 430 | 0.0016265 | 0.00014595 | 0.0020964 | 0.00019092 | 0.0017901 | 0.00016148 | 1.3425e-05 | -1.5315e-05 | 0.0020427 | 0.0020561 | 0.0020695 | 0.002083 | 0.0020964 | 0.0020811 | 0.0020658 | 0.0020505 | 0.0020351 | 0.0020198 | 0.0020045 | 0.0019892 | 0.0019739 | 0.0019586 | 0.0019432 | 0.0019279 | 0.0019126 | 0.0018973 | 0.001882 | 0.0018667 | 1.2849e-06 | -1.4719e-06 | 0.00018578 | 0.00018707 | 0.00018835 | 0.00018964 | 0.00019092 | 0.00018945 | 0.00018798 | 0.0001865 | 0.00018503 | 0.00018356 | 0.00018209 | 0.00018062 | 0.00017914 | 0.00017767 | 0.0001762 | 0.00017473 | 0.00017326 | 0.00017179 | 0.00017031 | 0.00016884
| TRG022-142033811 | 60 | 60 | 0.00060139 | 0 | 0.0009322 | 0 | 0.00076414 | 0 | 9.4517e-06 | -8.403e-06 | 0.00089439 | 0.00090384 | 0.0009133 | 0.00092275 | 0.0009322 | 0.0009238 | 0.00091539 | 0.00090699 | 0.00089859 | 0.00089018 | 0.00088178 | 0.00087338 | 0.00086497 | 0.00085657 | 0.00084817 | 0.00083977 | 0.00083136 | 0.00082296 | 0.00081456 | 0.00080615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-154491351 | 21 | 21 | 0.00051527 | 0 | 0.00071941 | 0 | 0.00064831 | 0 | 5.8325e-06 | -3.5548e-06 | 0.00069608 | 0.00070191 | 0.00070774 | 0.00071358 | 0.00071941 | 0.00071585 | 0.0007123 | 0.00070874 | 0.00070519 | 0.00070163 | 0.00069808 | 0.00069453 | 0.00069097 | 0.00068742 | 0.00068386 | 0.00068031 | 0.00067675 | 0.0006732 | 0.00066964 | 0.00066609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-154491390 | 25 | 25 | 0.00032455 | 0 | 0.00043687 | 0 | 0.00041895 | 0 | 3.2092e-06 | -8.9625e-07 | 0.00042404 | 0.00042725 | 0.00043046 | 0.00043367 | 0.00043687 | 0.00043598 | 0.00043508 | 0.00043419 | 0.00043329 | 0.00043239 | 0.0004315 | 0.0004306 | 0.0004297 | 0.00042881 | 0.00042791 | 0.00042702 | 0.00042612 | 0.00042522 | 0.00042433 | 0.00042343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-158166546 | 5 | 5 | 0.00015393 | 0 | 0.00021127 | 0 | 0.00017735 | 0 | 1.6381e-06 | -1.6957e-06 | 0.00020471 | 0.00020635 | 0.00020799 | 0.00020963 | 0.00021127 | 0.00020957 | 0.00020788 | 0.00020618 | 0.00020448 | 0.00020279 | 0.00020109 | 0.0001994 | 0.0001977 | 0.00019601 | 0.00019431 | 0.00019261 | 0.00019092 | 0.00018922 | 0.00018753 | 0.00018583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-158166693 | 18 | 18 | 0.00038847 | 0 | 0.00060119 | 0 | 0.00043136 | 0 | 6.0777e-06 | -8.4917e-06 | 0.00057688 | 0.00058296 | 0.00058903 | 0.00059511 | 0.00060119 | 0.0005927 | 0.00058421 | 0.00057572 | 0.00056722 | 0.00055873 | 0.00055024 | 0.00054175 | 0.00053326 | 0.00052477 | 0.00051627 | 0.00050778 | 0.00049929 | 0.0004908 | 0.00048231 | 0.00047382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-158166806 | 35 | 35 | 0.00069119 | 0 | 0.00096713 | 0 | 0.00079081 | 0 | 7.884e-06 | -8.8161e-06 | 0.00093559 | 0.00094348 | 0.00095136 | 0.00095924 | 0.00096713 | 0.00095831 | 0.00094949 | 0.00094068 | 0.00093186 | 0.00092305 | 0.00091423 | 0.00090541 | 0.0008966 | 0.00088778 | 0.00087897 | 0.00087015 | 0.00086133 | 0.00085252 | 0.0008437 | 0.00083489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-158204991 | 36 | 36 | 0.0013375 | 0 | 0.001806 | 0 | 0.0015498 | 0 | 1.3385e-05 | -1.2808e-05 | 0.0017525 | 0.0017658 | 0.0017792 | 0.0017926 | 0.001806 | 0.0017932 | 0.0017804 | 0.0017676 | 0.0017548 | 0.001742 | 0.0017292 | 0.0017163 | 0.0017035 | 0.0016907 | 0.0016779 | 0.0016651 | 0.0016523 | 0.0016395 | 0.0016267 | 0.0016139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-158205190 | 41 | 41 | 0.00063481 | 0 | 0.0007838 | 0 | 0.00072597 | 0 | 4.2568e-06 | -2.8916e-06 | 0.00076677 | 0.00077103 | 0.00077529 | 0.00077955 | 0.0007838 | 0.00078091 | 0.00077802 | 0.00077513 | 0.00077224 | 0.00076934 | 0.00076645 | 0.00076356 | 0.00076067 | 0.00075778 | 0.00075489 | 0.00075199 | 0.0007491 | 0.00074621 | 0.00074332 | 0.00074043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-158205316 | 43 | 43 | 0.0012784 | 0 | 0.0018838 | 0 | 0.0014085 | 0 | 1.7297e-05 | -2.3767e-05 | 0.0018146 | 0.0018319 | 0.0018492 | 0.0018665 | 0.0018838 | 0.0018601 | 0.0018363 | 0.0018125 | 0.0017888 | 0.001765 | 0.0017412 | 0.0017174 | 0.0016937 | 0.0016699 | 0.0016461 | 0.0016224 | 0.0015986 | 0.0015748 | 0.0015511 | 0.0015273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-158205503 | 40 | 40 | 0.0017608 | 0 | 0.002796 | 0 | 0.0022855 | 0 | 2.9579e-05 | -2.5525e-05 | 0.0026777 | 0.0027073 | 0.0027369 | 0.0027665 | 0.002796 | 0.0027705 | 0.002745 | 0.0027195 | 0.0026939 | 0.0026684 | 0.0026429 | 0.0026174 | 0.0025918 | 0.0025663 | 0.0025408 | 0.0025153 | 0.0024897 | 0.0024642 | 0.0024387 | 0.0024132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-158205673 | 24 | 24 | 3.31e-05 | 0 | 5.36e-05 | 0 | 3.63e-05 | 0 | 5.8571e-07 | -8.65e-07 | 5.1257e-05 | 5.1843e-05 | 5.2429e-05 | 5.3014e-05 | 5.36e-05 | 5.2735e-05 | 5.187e-05 | 5.1005e-05 | 5.014e-05 | 4.9275e-05 | 4.841e-05 | 4.7545e-05 | 4.668e-05 | 4.5815e-05 | 4.495e-05 | 4.4085e-05 | 4.322e-05 | 4.2355e-05 | 4.149e-05 | 4.0625e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-158205847 | 23 | 23 | 2.55e-05 | 0 | 4.04e-05 | 0 | 3.08e-05 | 0 | 4.2571e-07 | -4.8e-07 | 3.8697e-05 | 3.9123e-05 | 3.9549e-05 | 3.9974e-05 | 4.04e-05 | 3.992e-05 | 3.944e-05 | 3.896e-05 | 3.848e-05 | 3.8e-05 | 3.752e-05 | 3.704e-05 | 3.656e-05 | 3.608e-05 | 3.56e-05 | 3.512e-05 | 3.464e-05 | 3.416e-05 | 3.368e-05 | 3.32e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-158206040 | 14 | 14 | 9e-06 | 0 | 1.47e-05 | 0 | 1.13e-05 | 0 | 1.6286e-07 | -1.7e-07 | 1.4049e-05 | 1.4211e-05 | 1.4374e-05 | 1.4537e-05 | 1.47e-05 | 1.453e-05 | 1.436e-05 | 1.419e-05 | 1.402e-05 | 1.385e-05 | 1.368e-05 | 1.351e-05 | 1.334e-05 | 1.317e-05 | 1.3e-05 | 1.283e-05 | 1.266e-05 | 1.249e-05 | 1.232e-05 | 1.215e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-160930593 | 34 | 34 | 0.00061604 | 0 | 0.00090216 | 0 | 0.00071319 | 0 | 8.1747e-06 | -9.4485e-06 | 0.00086946 | 0.00087763 | 0.00088581 | 0.00089398 | 0.00090216 | 0.00089271 | 0.00088326 | 0.00087381 | 0.00086436 | 0.00085491 | 0.00084547 | 0.00083602 | 0.00082657 | 0.00081712 | 0.00080767 | 0.00079822 | 0.00078877 | 0.00077933 | 0.00076988 | 0.00076043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-163035515 | 4 | 4 | 4.78e-06 | 0 | 7.93e-06 | 0 | 5.83e-06 | 0 | 9e-08 | -1.05e-07 | 7.57e-06 | 7.66e-06 | 7.75e-06 | 7.84e-06 | 7.93e-06 | 7.825e-06 | 7.72e-06 | 7.615e-06 | 7.51e-06 | 7.405e-06 | 7.3e-06 | 7.195e-06 | 7.09e-06 | 6.985e-06 | 6.88e-06 | 6.775e-06 | 6.67e-06 | 6.565e-06 | 6.46e-06 | 6.355e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-163035708 | 6 | 6 | 1.29e-05 | 0 | 2.33e-05 | 0 | 1.67e-05 | 0 | 2.9714e-07 | -3.3e-07 | 2.2111e-05 | 2.2409e-05 | 2.2706e-05 | 2.3003e-05 | 2.33e-05 | 2.297e-05 | 2.264e-05 | 2.231e-05 | 2.198e-05 | 2.165e-05 | 2.132e-05 | 2.099e-05 | 2.066e-05 | 2.033e-05 | 2e-05 | 1.967e-05 | 1.934e-05 | 1.901e-05 | 1.868e-05 | 1.835e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-163035922 | 4 | 4 | 0.00069822 | 0 | 0.0010568 | 0 | 0.00080261 | 0 | 1.0245e-05 | -1.2708e-05 | 0.0010158 | 0.001026 | 0.0010363 | 0.0010465 | 0.0010568 | 0.0010441 | 0.0010314 | 0.0010187 | 0.0010059 | 0.00099324 | 0.00098053 | 0.00096782 | 0.00095511 | 0.0009424 | 0.0009297 | 0.00091699 | 0.00090428 | 0.00089157 | 0.00087886 | 0.00086615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-163036120 | 5 | 5 | 7.33e-06 | 0 | 1.12e-05 | 0 | 9.77e-06 | 0 | 1.1057e-07 | -7.15e-08 | 1.0758e-05 | 1.0868e-05 | 1.0979e-05 | 1.1089e-05 | 1.12e-05 | 1.1128e-05 | 1.1057e-05 | 1.0986e-05 | 1.0914e-05 | 1.0843e-05 | 1.0771e-05 | 1.07e-05 | 1.0628e-05 | 1.0557e-05 | 1.0485e-05 | 1.0414e-05 | 1.0342e-05 | 1.0271e-05 | 1.0199e-05 | 1.0128e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-163036215 | 15 | 15 | 6.99e-07 | 0 | 1.18e-06 | 0 | 8.43e-07 | 0 | 1.3743e-08 | -1.685e-08 | 1.125e-06 | 1.1388e-06 | 1.1525e-06 | 1.1663e-06 | 1.18e-06 | 1.1631e-06 | 1.1463e-06 | 1.1294e-06 | 1.1126e-06 | 1.0957e-06 | 1.0789e-06 | 1.062e-06 | 1.0452e-06 | 1.0283e-06 | 1.0115e-06 | 9.9465e-07 | 9.778e-07 | 9.6095e-07 | 9.441e-07 | 9.2725e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-171344186 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-176898220 | 1600 | 861 | 0.0036725 | 0.0010847 | 0.0050497 | 0.0017084 | 0.0042319 | 0.0013379 | 3.9347e-05 | -4.0891e-05 | 0.0048923 | 0.0049316 | 0.004971 | 0.0050103 | 0.0050497 | 0.0050088 | 0.0049679 | 0.004927 | 0.0048861 | 0.0048452 | 0.0048043 | 0.0047634 | 0.0047226 | 0.0046817 | 0.0046408 | 0.0045999 | 0.004559 | 0.0045181 | 0.0044772 | 0.0044363 | 1.7819e-05 | -1.8525e-05 | 0.0016371 | 0.0016549 | 0.0016727 | 0.0016906 | 0.0017084 | 0.0016898 | 0.0016713 | 0.0016528 | 0.0016343 | 0.0016157 | 0.0015972 | 0.0015787 | 0.0015602 | 0.0015416 | 0.0015231 | 0.0015046 | 0.0014861 | 0.0014675 | 0.001449 | 0.0014305
| TRG022-176898350 | 338 | 264 | 0.0022405 | 0.00054597 | 0.0023998 | 0.00058375 | 0.0023049 | 0.00056122 | 4.5499e-06 | -4.7438e-06 | 0.0023816 | 0.0023861 | 0.0023907 | 0.0023952 | 0.0023998 | 0.002395 | 0.0023903 | 0.0023855 | 0.0023808 | 0.0023761 | 0.0023713 | 0.0023666 | 0.0023618 | 0.0023571 | 0.0023523 | 0.0023476 | 0.0023429 | 0.0023381 | 0.0023334 | 0.0023286 | 1.0794e-06 | -1.1264e-06 | 0.00057943 | 0.00058051 | 0.00058159 | 0.00058267 | 0.00058375 | 0.00058262 | 0.0005815 | 0.00058037 | 0.00057924 | 0.00057812 | 0.00057699 | 0.00057586 | 0.00057474 | 0.00057361 | 0.00057249 | 0.00057136 | 0.00057023 | 0.00056911 | 0.00056798 | 0.00056685
| TRG022-176898385 | 683 | 89 | 0.00055527 | 0.00072069 | 0.00074803 | 0.00099463 | 0.00060393 | 0.00078762 | 5.5073e-06 | -7.2047e-06 | 0.000726 | 0.0007315 | 0.00073701 | 0.00074252 | 0.00074802 | 0.00074082 | 0.00073362 | 0.00072641 | 0.00071921 | 0.000712 | 0.0007048 | 0.00069759 | 0.00069039 | 0.00068318 | 0.00067598 | 0.00066877 | 0.00066157 | 0.00065436 | 0.00064716 | 0.00063995 | 7.8268e-06 | -1.035e-05 | 0.00096332 | 0.00097115 | 0.00097897 | 0.0009868 | 0.00099463 | 0.00098428 | 0.00097393 | 0.00096357 | 0.00095322 | 0.00094287 | 0.00093252 | 0.00092217 | 0.00091182 | 0.00090147 | 0.00089112 | 0.00088077 | 0.00087042 | 0.00086007 | 0.00084972 | 0.00083937
| TRG022-185851624 | 2005 | 67 | 0.00069809 | 0.0005621 | 0.0011392 | 0.00082234 | 0.00087719 | 0.00066768 | 1.2602e-05 | -1.3099e-05 | 0.0010888 | 0.0011014 | 0.001114 | 0.0011266 | 0.0011392 | 0.0011261 | 0.001113 | 0.0010999 | 0.0010868 | 0.0010737 | 0.0010606 | 0.0010475 | 0.0010344 | 0.0010213 | 0.0010082 | 0.00099508 | 0.00098198 | 0.00096888 | 0.00095578 | 0.00094269 | 7.4355e-06 | -7.7334e-06 | 0.0007926 | 0.00080004 | 0.00080747 | 0.00081491 | 0.00082234 | 0.00081461 | 0.00080688 | 0.00079914 | 0.00079141 | 0.00078368 | 0.00077594 | 0.00076821 | 0.00076048 | 0.00075274 | 0.00074501 | 0.00073728 | 0.00072954 | 0.00072181 | 0.00071408 | 0.00070634
| TRG022-24598160 | 297 | 151 | 0.0013063 | 0.0017645 | 0.0017346 | 0.0024736 | 0.001395 | 0.0018876 | 1.2236e-05 | -1.6978e-05 | 0.0016857 | 0.0016979 | 0.0017101 | 0.0017224 | 0.0017346 | 0.0017176 | 0.0017006 | 0.0016837 | 0.0016667 | 0.0016497 | 0.0016327 | 0.0016158 | 0.0015988 | 0.0015818 | 0.0015648 | 0.0015478 | 0.0015309 | 0.0015139 | 0.0014969 | 0.0014799 | 2.0258e-05 | -2.9297e-05 | 0.0023925 | 0.0024128 | 0.0024331 | 0.0024533 | 0.0024736 | 0.0024443 | 0.002415 | 0.0023857 | 0.0023564 | 0.0023271 | 0.0022978 | 0.0022685 | 0.0022392 | 0.0022099 | 0.0021806 | 0.0021513 | 0.002122 | 0.0020927 | 0.0020634 | 0.0020341
| TRG022-24598202 | 283 | 100 | 0.0012566 | 0.00085573 | 0.001959 | 0.0012716 | 0.0016035 | 0.0010579 | 2.0068e-05 | -1.7775e-05 | 0.0018787 | 0.0018988 | 0.0019189 | 0.0019389 | 0.001959 | 0.0019412 | 0.0019234 | 0.0019057 | 0.0018879 | 0.0018701 | 0.0018523 | 0.0018346 | 0.0018168 | 0.001799 | 0.0017812 | 0.0017635 | 0.0017457 | 0.0017279 | 0.0017101 | 0.0016924 | 1.1882e-05 | -1.0682e-05 | 0.0012241 | 0.001236 | 0.0012478 | 0.0012597 | 0.0012716 | 0.0012609 | 0.0012502 | 0.0012396 | 0.0012289 | 0.0012182 | 0.0012075 | 0.0011968 | 0.0011861 | 0.0011755 | 0.0011648 | 0.0011541 | 0.0011434 | 0.0011327 | 0.001122 | 0.0011114
| TRG024-117365806 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-158041024 | 33 | 33 | 0.00038213 | 0 | 0.0004926 | 0 | 0.00041099 | 0 | 3.1562e-06 | -4.0804e-06 | 0.00047997 | 0.00048313 | 0.00048629 | 0.00048944 | 0.0004926 | 0.00048852 | 0.00048444 | 0.00048036 | 0.00047628 | 0.0004722 | 0.00046812 | 0.00046404 | 0.00045996 | 0.00045588 | 0.0004518 | 0.00044772 | 0.00044363 | 0.00043955 | 0.00043547 | 0.00043139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-158742698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-162822011 | 7 | 7 | 0.00038337 | 0 | 0.00056232 | 0 | 0.00037265 | 0 | 5.1128e-06 | -9.4833e-06 | 0.00054187 | 0.00054698 | 0.00055209 | 0.00055721 | 0.00056232 | 0.00055284 | 0.00054335 | 0.00053387 | 0.00052439 | 0.0005149 | 0.00050542 | 0.00049594 | 0.00048645 | 0.00047697 | 0.00046749 | 0.000458 | 0.00044852 | 0.00043904 | 0.00042955 | 0.00042007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-162822186 | 6 | 6 | 4.71e-07 | 0 | 9.94e-07 | 0 | 5.23e-07 | 0 | 1.4943e-08 | -2.355e-08 | 9.3423e-07 | 9.4917e-07 | 9.6411e-07 | 9.7906e-07 | 9.94e-07 | 9.7045e-07 | 9.469e-07 | 9.2335e-07 | 8.998e-07 | 8.7625e-07 | 8.527e-07 | 8.2915e-07 | 8.056e-07 | 7.8205e-07 | 7.585e-07 | 7.3495e-07 | 7.114e-07 | 6.8785e-07 | 6.643e-07 | 6.4075e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-162822411 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-162822646 | 7 | 7 | 5.73e-08 | 0 | 8.46e-08 | 0 | 4.64e-08 | 0 | 7.8e-10 | -1.91e-09 | 8.148e-08 | 8.226e-08 | 8.304e-08 | 8.382e-08 | 8.46e-08 | 8.269e-08 | 8.078e-08 | 7.887e-08 | 7.696e-08 | 7.505e-08 | 7.314e-08 | 7.123e-08 | 6.932e-08 | 6.741e-08 | 6.55e-08 | 6.359e-08 | 6.168e-08 | 5.977e-08 | 5.786e-08 | 5.595e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-162822850 | 21 | 21 | 0.00029614 | 0 | 0.00044828 | 0 | 0.00030191 | 0 | 4.3469e-06 | -7.3186e-06 | 0.0004309 | 0.00043524 | 0.00043959 | 0.00044394 | 0.00044828 | 0.00044097 | 0.00043365 | 0.00042633 | 0.00041901 | 0.00041169 | 0.00040437 | 0.00039705 | 0.00038974 | 0.00038242 | 0.0003751 | 0.00036778 | 0.00036046 | 0.00035314 | 0.00034582 | 0.00033851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-162823024 | 6 | 6 | 3.5e-06 | 0 | 4.92e-06 | 0 | 3.72e-06 | 0 | 4.0571e-08 | -6e-08 | 4.7577e-06 | 4.7983e-06 | 4.8389e-06 | 4.8794e-06 | 4.92e-06 | 4.86e-06 | 4.8e-06 | 4.74e-06 | 4.68e-06 | 4.62e-06 | 4.56e-06 | 4.5e-06 | 4.44e-06 | 4.38e-06 | 4.32e-06 | 4.26e-06 | 4.2e-06 | 4.14e-06 | 4.08e-06 | 4.02e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-162823256 | 15 | 15 | 9.56e-07 | 0 | 1.53e-06 | 0 | 9.56e-07 | 0 | 1.64e-08 | -2.87e-08 | 1.4644e-06 | 1.4808e-06 | 1.4972e-06 | 1.5136e-06 | 1.53e-06 | 1.5013e-06 | 1.4726e-06 | 1.4439e-06 | 1.4152e-06 | 1.3865e-06 | 1.3578e-06 | 1.3291e-06 | 1.3004e-06 | 1.2717e-06 | 1.243e-06 | 1.2143e-06 | 1.1856e-06 | 1.1569e-06 | 1.1282e-06 | 1.0995e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-185851718 | 652 | 39 | 1.59e-07 | 3.21e-07 | 2.82e-07 | 5.71e-07 | 2.16e-07 | 4.37e-07 | 3.5143e-09 | -3.3e-09 | 2.6794e-07 | 2.7146e-07 | 2.7497e-07 | 2.7849e-07 | 2.82e-07 | 2.787e-07 | 2.754e-07 | 2.721e-07 | 2.688e-07 | 2.655e-07 | 2.622e-07 | 2.589e-07 | 2.556e-07 | 2.523e-07 | 2.49e-07 | 2.457e-07 | 2.424e-07 | 2.391e-07 | 2.358e-07 | 2.325e-07 | 7.1429e-09 | -6.7e-09 | 5.4243e-07 | 5.4957e-07 | 5.5671e-07 | 5.6386e-07 | 5.71e-07 | 5.643e-07 | 5.576e-07 | 5.509e-07 | 5.442e-07 | 5.375e-07 | 5.308e-07 | 5.241e-07 | 5.174e-07 | 5.107e-07 | 5.04e-07 | 4.973e-07 | 4.906e-07 | 4.839e-07 | 4.772e-07 | 4.705e-07
| TRG024-24598286 | 601 | 145 | 8.55e-05 | 9.87e-05 | 0.00012204 | 0.00014035 | 8.26e-05 | 9.76e-05 | 1.0439e-06 | -1.9718e-06 | 0.00011786 | 0.0001189 | 0.00011995 | 0.00012099 | 0.00012204 | 0.00012006 | 0.00011809 | 0.00011612 | 0.00011415 | 0.00011218 | 0.0001102 | 0.00010823 | 0.00010626 | 0.00010429 | 0.00010232 | 0.00010035 | 9.8374e-05 | 9.6402e-05 | 9.4431e-05 | 9.2459e-05 | 1.1901e-06 | -2.1376e-06 | 0.00013559 | 0.00013678 | 0.00013797 | 0.00013916 | 0.00014035 | 0.00013822 | 0.00013608 | 0.00013394 | 0.0001318 | 0.00012966 | 0.00012753 | 0.00012539 | 0.00012325 | 0.00012111 | 0.00011898 | 0.00011684 | 0.0001147 | 0.00011256 | 0.00011043 | 0.00010829
| TRG024-60700588 | 421 | 418 | 0.00089541 | 0 | 0.0014146 | 0 | 0.00091829 | 0 | 1.4834e-05 | -2.4816e-05 | 0.0013553 | 0.0013701 | 0.0013849 | 0.0013998 | 0.0014146 | 0.0013898 | 0.001365 | 0.0013402 | 0.0013153 | 0.0012905 | 0.0012657 | 0.0012409 | 0.0012161 | 0.0011913 | 0.0011664 | 0.0011416 | 0.0011168 | 0.001092 | 0.0010672 | 0.0010424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-74127795 | 1069 | 403 | 0.00094029 | 0.0005304 | 0.0014539 | 0.00078657 | 0.0011744 | 0.00064596 | 1.4673e-05 | -1.3975e-05 | 0.0013952 | 0.0014098 | 0.0014245 | 0.0014392 | 0.0014539 | 0.0014399 | 0.0014259 | 0.0014119 | 0.001398 | 0.001384 | 0.00137 | 0.001356 | 0.0013421 | 0.0013281 | 0.0013141 | 0.0013001 | 0.0012862 | 0.0012722 | 0.0012582 | 0.0012442 | 7.319e-06 | -7.0306e-06 | 0.00075729 | 0.00076461 | 0.00077193 | 0.00077925 | 0.00078657 | 0.00077954 | 0.00077251 | 0.00076548 | 0.00075845 | 0.00075142 | 0.00074439 | 0.00073736 | 0.00073033 | 0.0007233 | 0.00071626 | 0.00070923 | 0.0007022 | 0.00069517 | 0.00068814 | 0.00068111
| WBE011-203216132 | 2457 | 2457 | 0.0024689 | 0 | 0.0029608 | 0 | 0.003054 | 0 | 1.4056e-05 | 4.6576e-06 | 0.0029046 | 0.0029187 | 0.0029327 | 0.0029468 | 0.0029608 | 0.0029655 | 0.0029702 | 0.0029748 | 0.0029795 | 0.0029841 | 0.0029888 | 0.0029934 | 0.0029981 | 0.0030028 | 0.0030074 | 0.0030121 | 0.0030167 | 0.0030214 | 0.0030261 | 0.0030307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE011-41045910 | 2466 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE012-203216204 | 2237 | 2237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE013-203216284 | 5164 | 1780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE014-203216348 | 6472 | 6472 | 0.00096843 | 0 | 0.0012447 | 0 | 0.0013201 | 0 | 7.8941e-06 | 3.7682e-06 | 0.0012131 | 0.001221 | 0.0012289 | 0.0012368 | 0.0012447 | 0.0012485 | 0.0012523 | 0.001256 | 0.0012598 | 0.0012636 | 0.0012673 | 0.0012711 | 0.0012749 | 0.0012786 | 0.0012824 | 0.0012862 | 0.0012899 | 0.0012937 | 0.0012975 | 0.0013012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE021-203216532 | 2981 | 2981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE022-203216606 | 1530 | 1530 | 0.004511 | 0 | 0.0060695 | 0 | 0.0062629 | 0 | 4.453e-05 | 9.6701e-06 | 0.0058914 | 0.005936 | 0.0059805 | 0.006025 | 0.0060695 | 0.0060792 | 0.0060889 | 0.0060986 | 0.0061082 | 0.0061179 | 0.0061276 | 0.0061372 | 0.0061469 | 0.0061566 | 0.0061662 | 0.0061759 | 0.0061856 | 0.0061953 | 0.0062049 | 0.0062146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE023-139765778 | 712 | 712 | 0.006458 | 0 | 0.0083952 | 0 | 0.0089173 | 0 | 5.5346e-05 | 2.6107e-05 | 0.0081738 | 0.0082291 | 0.0082845 | 0.0083398 | 0.0083952 | 0.0084213 | 0.0084474 | 0.0084735 | 0.0084996 | 0.0085257 | 0.0085518 | 0.0085779 | 0.008604 | 0.0086301 | 0.0086562 | 0.0086823 | 0.0087084 | 0.0087345 | 0.0087607 | 0.0087868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE023-203216893 | 6051 | 5339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE024-203216929 | 3482 | 3482 | 0.001032 | 0 | 0.0014173 | 0 | 0.0015517 | 0 | 1.1008e-05 | 6.7215e-06 | 0.0013733 | 0.0013843 | 0.0013953 | 0.0014063 | 0.0014173 | 0.001424 | 0.0014307 | 0.0014375 | 0.0014442 | 0.0014509 | 0.0014576 | 0.0014643 | 0.0014711 | 0.0014778 | 0.0014845 | 0.0014912 | 0.001498 | 0.0015047 | 0.0015114 | 0.0015181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE031-15425070 | 6385 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE031-203217123 | 6363 | 1337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE031-24612962 | 5026 | 5026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE032-203217195 | 4805 | 1798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE032-24612505 | 3007 | 3007 | 0.0060877 | 0 | 0.007679 | 0 | 0.0079478 | 0 | 4.5465e-05 | 1.3439e-05 | 0.0074972 | 0.0075426 | 0.0075881 | 0.0076336 | 0.007679 | 0.0076925 | 0.0077059 | 0.0077193 | 0.0077328 | 0.0077462 | 0.0077597 | 0.0077731 | 0.0077865 | 0.0078 | 0.0078134 | 0.0078269 | 0.0078403 | 0.0078537 | 0.0078672 | 0.0078806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE033-203217267 | 5055 | 5055 | 0.0061607 | 0 | 0.0080313 | 0 | 0.0086945 | 0 | 5.3447e-05 | 3.3159e-05 | 0.0078175 | 0.007871 | 0.0079244 | 0.0079779 | 0.0080313 | 0.0080645 | 0.0080976 | 0.0081308 | 0.008164 | 0.0081971 | 0.0082303 | 0.0082634 | 0.0082966 | 0.0083298 | 0.0083629 | 0.0083961 | 0.0084292 | 0.0084624 | 0.0084956 | 0.0085287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE033-65838252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE034-182145993 | 1691 | 1691 | 1.21e-05 | 0 | 1.65e-05 | 0 | 1.74e-05 | 0 | 1.2571e-07 | 4.5e-08 | 1.5997e-05 | 1.6123e-05 | 1.6249e-05 | 1.6374e-05 | 1.65e-05 | 1.6545e-05 | 1.659e-05 | 1.6635e-05 | 1.668e-05 | 1.6725e-05 | 1.677e-05 | 1.6815e-05 | 1.686e-05 | 1.6905e-05 | 1.695e-05 | 1.6995e-05 | 1.704e-05 | 1.7085e-05 | 1.713e-05 | 1.7175e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE034-203217365 | 3887 | 1105 | 8.29e-07 | 1.13e-06 | 1.23e-06 | 1.67e-06 | 1.3e-06 | 1.77e-06 | 1.1457e-08 | 3.5e-09 | 1.1842e-06 | 1.1956e-06 | 1.2071e-06 | 1.2185e-06 | 1.23e-06 | 1.2335e-06 | 1.237e-06 | 1.2405e-06 | 1.244e-06 | 1.2475e-06 | 1.251e-06 | 1.2545e-06 | 1.258e-06 | 1.2615e-06 | 1.265e-06 | 1.2685e-06 | 1.272e-06 | 1.2755e-06 | 1.279e-06 | 1.2825e-06 | 1.5429e-08 | 5e-09 | 1.6083e-06 | 1.6237e-06 | 1.6391e-06 | 1.6546e-06 | 1.67e-06 | 1.675e-06 | 1.68e-06 | 1.685e-06 | 1.69e-06 | 1.695e-06 | 1.7e-06 | 1.705e-06 | 1.71e-06 | 1.715e-06 | 1.72e-06 | 1.725e-06 | 1.73e-06 | 1.735e-06 | 1.74e-06 | 1.745e-06
| WBE034-24612477 | 1091 | 1091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL002-15395911 | 1958 | 1955 | 0.00011785 | 0 | 0.00015949 | 0 | 0.00012978 | 0 | 1.1896e-06 | -1.4854e-06 | 0.00015473 | 0.00015592 | 0.00015711 | 0.0001583 | 0.00015949 | 0.000158 | 0.00015652 | 0.00015503 | 0.00015355 | 0.00015206 | 0.00015058 | 0.00014909 | 0.0001476 | 0.00014612 | 0.00014463 | 0.00014315 | 0.00014166 | 0.00014018 | 0.00013869 | 0.00013721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL002-15395961 | 1960 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL002-163162028 | 3 | 3 | 1.61e-07 | 0 | 2.36e-07 | 0 | 1.38e-07 | 0 | 2.1429e-09 | -4.9e-09 | 2.2743e-07 | 2.2957e-07 | 2.3171e-07 | 2.3386e-07 | 2.36e-07 | 2.311e-07 | 2.262e-07 | 2.213e-07 | 2.164e-07 | 2.115e-07 | 2.066e-07 | 2.017e-07 | 1.968e-07 | 1.919e-07 | 1.87e-07 | 1.821e-07 | 1.772e-07 | 1.723e-07 | 1.674e-07 | 1.625e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL003-15396013 | 2033 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL003-15396026 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL003-15396039 | 2022 | 2011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL004-15395887 | 2115 | 934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL004-24598022 | 1181 | 1181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL005-153526296 | 660 | 591 | 0.0018183 | 0.00019697 | 0.0025644 | 0.00028216 | 0.0017519 | 0.00018748 | 2.1315e-05 | -4.0625e-05 | 0.0024791 | 0.0025004 | 0.0025218 | 0.0025431 | 0.0025644 | 0.0025238 | 0.0024831 | 0.0024425 | 0.0024019 | 0.0023613 | 0.0023206 | 0.00228 | 0.0022394 | 0.0021988 | 0.0021581 | 0.0021175 | 0.0020769 | 0.0020363 | 0.0019956 | 0.001955 | 2.4339e-06 | -4.7339e-06 | 0.00027242 | 0.00027485 | 0.00027729 | 0.00027972 | 0.00028216 | 0.00027742 | 0.00027269 | 0.00026795 | 0.00026322 | 0.00025849 | 0.00025375 | 0.00024902 | 0.00024428 | 0.00023955 | 0.00023482 | 0.00023008 | 0.00022535 | 0.00022061 | 0.00021588 | 0.00021115
| WBL005-15396050 | 2612 | 1915 | 0.00016088 | 9.81e-06 | 0.00018745 | 1.21e-05 | 0.00016862 | 1.05e-05 | 7.5917e-07 | -9.415e-07 | 0.00018441 | 0.00018517 | 0.00018593 | 0.00018669 | 0.00018745 | 0.00018651 | 0.00018557 | 0.00018462 | 0.00018368 | 0.00018274 | 0.0001818 | 0.00018086 | 0.00017992 | 0.00017898 | 0.00017803 | 0.00017709 | 0.00017615 | 0.00017521 | 0.00017427 | 0.00017333 | 6.5429e-08 | -8e-08 | 1.1838e-05 | 1.1904e-05 | 1.1969e-05 | 1.2035e-05 | 1.21e-05 | 1.202e-05 | 1.194e-05 | 1.186e-05 | 1.178e-05 | 1.17e-05 | 1.162e-05 | 1.154e-05 | 1.146e-05 | 1.138e-05 | 1.13e-05 | 1.122e-05 | 1.114e-05 | 1.106e-05 | 1.098e-05 | 1.09e-05
| WBL005-158638825 | 31 | 31 | 0.0003259 | 0 | 0.00052027 | 0 | 0.00036743 | 0 | 5.5534e-06 | -7.6421e-06 | 0.00049806 | 0.00050361 | 0.00050917 | 0.00051472 | 0.00052027 | 0.00051263 | 0.00050499 | 0.00049735 | 0.0004897 | 0.00048206 | 0.00047442 | 0.00046678 | 0.00045914 | 0.00045149 | 0.00044385 | 0.00043621 | 0.00042857 | 0.00042093 | 0.00041328 | 0.00040564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL005-158639092 | 33 | 33 | 5.57e-05 | 0 | 7.53e-05 | 0 | 5.09e-05 | 0 | 5.6e-07 | -1.22e-06 | 7.306e-05 | 7.362e-05 | 7.418e-05 | 7.474e-05 | 7.53e-05 | 7.408e-05 | 7.286e-05 | 7.164e-05 | 7.042e-05 | 6.92e-05 | 6.798e-05 | 6.676e-05 | 6.554e-05 | 6.432e-05 | 6.31e-05 | 6.188e-05 | 6.066e-05 | 5.944e-05 | 5.822e-05 | 5.7e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL005-158702306 | 23 | 23 | 0.0026174 | 0 | 0.0027341 | 0 | 0.0026509 | 0 | 3.335e-06 | -4.1582e-06 | 0.0027208 | 0.0027241 | 0.0027274 | 0.0027308 | 0.0027341 | 0.0027299 | 0.0027258 | 0.0027216 | 0.0027175 | 0.0027133 | 0.0027091 | 0.002705 | 0.0027008 | 0.0026967 | 0.0026925 | 0.0026884 | 0.0026842 | 0.00268 | 0.0026759 | 0.0026717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL005-163161673 | 5 | 5 | 1.34e-05 | 0 | 2.31e-05 | 0 | 1.68e-05 | 0 | 2.7714e-07 | -3.15e-07 | 2.1991e-05 | 2.2269e-05 | 2.2546e-05 | 2.2823e-05 | 2.31e-05 | 2.2785e-05 | 2.247e-05 | 2.2155e-05 | 2.184e-05 | 2.1525e-05 | 2.121e-05 | 2.0895e-05 | 2.058e-05 | 2.0265e-05 | 1.995e-05 | 1.9635e-05 | 1.932e-05 | 1.9005e-05 | 1.869e-05 | 1.8375e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL005-163161826 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL006-15435914 | 2868 | 2868 | 6.7e-08 | 0 | 9.38e-08 | 0 | 7.47e-08 | 0 | 7.6571e-10 | -9.55e-10 | 9.0737e-08 | 9.1503e-08 | 9.2269e-08 | 9.3034e-08 | 9.38e-08 | 9.2845e-08 | 9.189e-08 | 9.0935e-08 | 8.998e-08 | 8.9025e-08 | 8.807e-08 | 8.7115e-08 | 8.616e-08 | 8.5205e-08 | 8.425e-08 | 8.3295e-08 | 8.234e-08 | 8.1385e-08 | 8.043e-08 | 7.9475e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL008-15395863 | 2348 | 2348 | 0.00044601 | 0 | 0.00048726 | 0 | 0.00045832 | 0 | 1.1784e-06 | -1.4467e-06 | 0.00048254 | 0.00048372 | 0.0004849 | 0.00048608 | 0.00048726 | 0.00048581 | 0.00048436 | 0.00048292 | 0.00048147 | 0.00048002 | 0.00047858 | 0.00047713 | 0.00047568 | 0.00047424 | 0.00047279 | 0.00047134 | 0.0004699 | 0.00046845 | 0.000467 | 0.00046556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL010-15395826 | 1130 | 1130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-153865449 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-162960471 | 3 | 3 | 5.92e-07 | 0 | 8.61e-07 | 0 | 5.92e-07 | 0 | 7.6857e-09 | -1.345e-08 | 8.3026e-07 | 8.3794e-07 | 8.4563e-07 | 8.5331e-07 | 8.61e-07 | 8.4755e-07 | 8.341e-07 | 8.2065e-07 | 8.072e-07 | 7.9375e-07 | 7.803e-07 | 7.6685e-07 | 7.534e-07 | 7.3995e-07 | 7.265e-07 | 7.1305e-07 | 6.996e-07 | 6.8615e-07 | 6.727e-07 | 6.5925e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-162960671 | 12 | 12 | 1.4e-06 | 0 | 2.38e-06 | 0 | 1.41e-06 | 0 | 2.8e-08 | -4.85e-08 | 2.268e-06 | 2.296e-06 | 2.324e-06 | 2.352e-06 | 2.38e-06 | 2.3315e-06 | 2.283e-06 | 2.2345e-06 | 2.186e-06 | 2.1375e-06 | 2.089e-06 | 2.0405e-06 | 1.992e-06 | 1.9435e-06 | 1.895e-06 | 1.8465e-06 | 1.798e-06 | 1.7495e-06 | 1.701e-06 | 1.6525e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-162960865 | 12 | 12 | 3.31e-06 | 0 | 5.15e-06 | 0 | 2.76e-06 | 0 | 5.2571e-08 | -1.195e-07 | 4.9397e-06 | 4.9923e-06 | 5.0449e-06 | 5.0974e-06 | 5.15e-06 | 5.0305e-06 | 4.911e-06 | 4.7915e-06 | 4.672e-06 | 4.5525e-06 | 4.433e-06 | 4.3135e-06 | 4.194e-06 | 4.0745e-06 | 3.955e-06 | 3.8355e-06 | 3.716e-06 | 3.5965e-06 | 3.477e-06 | 3.3575e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163034361 | 6 | 6 | 2.27e-06 | 0 | 4.05e-06 | 0 | 2.66e-06 | 0 | 5.0857e-08 | -6.95e-08 | 3.8466e-06 | 3.8974e-06 | 3.9483e-06 | 3.9991e-06 | 4.05e-06 | 3.9805e-06 | 3.911e-06 | 3.8415e-06 | 3.772e-06 | 3.7025e-06 | 3.633e-06 | 3.5635e-06 | 3.494e-06 | 3.4245e-06 | 3.355e-06 | 3.2855e-06 | 3.216e-06 | 3.1465e-06 | 3.077e-06 | 3.0075e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163034588 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163150328 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163162276 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163162391 | 11 | 11 | 5.69e-05 | 0 | 8.27e-05 | 0 | 5.95e-05 | 0 | 7.3714e-07 | -1.16e-06 | 7.9751e-05 | 8.0489e-05 | 8.1226e-05 | 8.1963e-05 | 8.27e-05 | 8.154e-05 | 8.038e-05 | 7.922e-05 | 7.806e-05 | 7.69e-05 | 7.574e-05 | 7.458e-05 | 7.342e-05 | 7.226e-05 | 7.11e-05 | 6.994e-05 | 6.878e-05 | 6.762e-05 | 6.646e-05 | 6.53e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163162602 | 5 | 5 | 5.53e-05 | 0 | 9.85e-05 | 0 | 6.59e-05 | 0 | 1.2343e-06 | -1.63e-06 | 9.3563e-05 | 9.4797e-05 | 9.6031e-05 | 9.7266e-05 | 9.85e-05 | 9.687e-05 | 9.524e-05 | 9.361e-05 | 9.198e-05 | 9.035e-05 | 8.872e-05 | 8.709e-05 | 8.546e-05 | 8.383e-05 | 8.22e-05 | 8.057e-05 | 7.894e-05 | 7.731e-05 | 7.568e-05 | 7.405e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163162797 | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163162997 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163205557 | 31 | 31 | 9.23e-07 | 0 | 1.44e-06 | 0 | 7.69e-07 | 0 | 1.4771e-08 | -3.355e-08 | 1.3809e-06 | 1.3957e-06 | 1.4105e-06 | 1.4252e-06 | 1.44e-06 | 1.4064e-06 | 1.3729e-06 | 1.3393e-06 | 1.3058e-06 | 1.2722e-06 | 1.2387e-06 | 1.2051e-06 | 1.1716e-06 | 1.138e-06 | 1.1045e-06 | 1.0709e-06 | 1.0374e-06 | 1.0038e-06 | 9.703e-07 | 9.3675e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163205740 | 5 | 5 | 5.79e-11 | 0 | 8.09e-11 | 0 | 6.45e-11 | 0 | 6.5714e-13 | -8.2e-13 | 7.8271e-11 | 7.8929e-11 | 7.9586e-11 | 8.0243e-11 | 8.09e-11 | 8.008e-11 | 7.926e-11 | 7.844e-11 | 7.762e-11 | 7.68e-11 | 7.598e-11 | 7.516e-11 | 7.434e-11 | 7.352e-11 | 7.27e-11 | 7.188e-11 | 7.106e-11 | 7.024e-11 | 6.942e-11 | 6.86e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-171331101 | 26 | 26 | 1.09e-05 | 0 | 1.09e-05 | 0 | 1.09e-05 | 0 | 0 | 0 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 1.09e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-24598048 | 1681 | 1067 | 0.0010063 | 3.79e-06 | 0.0011551 | 5.97e-06 | 0.0010045 | 3e-06 | 4.2511e-06 | -7.5283e-06 | 0.0011381 | 0.0011424 | 0.0011466 | 0.0011509 | 0.0011551 | 0.0011476 | 0.0011401 | 0.0011325 | 0.001125 | 0.0011175 | 0.0011099 | 0.0011024 | 0.0010949 | 0.0010874 | 0.0010798 | 0.0010723 | 0.0010648 | 0.0010572 | 0.0010497 | 0.0010422 | 6.2286e-08 | -1.485e-07 | 5.7209e-06 | 5.7831e-06 | 5.8454e-06 | 5.9077e-06 | 5.97e-06 | 5.8215e-06 | 5.673e-06 | 5.5245e-06 | 5.376e-06 | 5.2275e-06 | 5.079e-06 | 4.9305e-06 | 4.782e-06 | 4.6335e-06 | 4.485e-06 | 4.3365e-06 | 4.188e-06 | 4.0395e-06 | 3.891e-06 | 3.7425e-06
| WBL012-24611149 | 611 | 457 | 0.0002467 | 5.42e-05 | 0.00036819 | 8.25e-05 | 0.0002756 | 6.07e-05 | 3.4713e-06 | -4.6298e-06 | 0.00035431 | 0.00035778 | 0.00036125 | 0.00036472 | 0.00036819 | 0.00036356 | 0.00035893 | 0.0003543 | 0.00034967 | 0.00034504 | 0.00034041 | 0.00033578 | 0.00033115 | 0.00032652 | 0.00032189 | 0.00031726 | 0.00031263 | 0.00030801 | 0.00030338 | 0.00029875 | 8.0857e-07 | -1.09e-06 | 7.9266e-05 | 8.0074e-05 | 8.0883e-05 | 8.1691e-05 | 8.25e-05 | 8.141e-05 | 8.032e-05 | 7.923e-05 | 7.814e-05 | 7.705e-05 | 7.596e-05 | 7.487e-05 | 7.378e-05 | 7.269e-05 | 7.16e-05 | 7.051e-05 | 6.942e-05 | 6.833e-05 | 6.724e-05 | 6.615e-05
| WBL012-88823662 | 2829 | 1148 | 7.02e-05 | 2.67e-05 | 6.96e-05 | 3.73e-05 | 7.01e-05 | 2.97e-05 | -1.7143e-08 | 2.5e-08 | 6.9669e-05 | 6.9651e-05 | 6.9634e-05 | 6.9617e-05 | 6.96e-05 | 6.9625e-05 | 6.965e-05 | 6.9675e-05 | 6.97e-05 | 6.9725e-05 | 6.975e-05 | 6.9775e-05 | 6.98e-05 | 6.9825e-05 | 6.985e-05 | 6.9875e-05 | 6.99e-05 | 6.9925e-05 | 6.995e-05 | 6.9975e-05 | 3.0286e-07 | -3.8e-07 | 3.6089e-05 | 3.6391e-05 | 3.6694e-05 | 3.6997e-05 | 3.73e-05 | 3.692e-05 | 3.654e-05 | 3.616e-05 | 3.578e-05 | 3.54e-05 | 3.502e-05 | 3.464e-05 | 3.426e-05 | 3.388e-05 | 3.35e-05 | 3.312e-05 | 3.274e-05 | 3.236e-05 | 3.198e-05 | 3.16e-05
| WIN011-124931073 | 33 | 33 | 0.0011057 | 0 | 0.0017024 | 0 | 0.0016038 | 0 | 1.7047e-05 | -4.9292e-06 | 0.0016342 | 0.0016512 | 0.0016683 | 0.0016853 | 0.0017024 | 0.0016974 | 0.0016925 | 0.0016876 | 0.0016827 | 0.0016777 | 0.0016728 | 0.0016679 | 0.0016629 | 0.001658 | 0.0016531 | 0.0016482 | 0.0016432 | 0.0016383 | 0.0016334 | 0.0016284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN011-154067565 | 581 | 532 | 0.0011876 | 0.00036194 | 0.0017831 | 0.00055862 | 0.0015769 | 0.00049217 | 1.7012e-05 | -1.0307e-05 | 0.001715 | 0.001732 | 0.001749 | 0.001766 | 0.0017831 | 0.0017727 | 0.0017624 | 0.0017521 | 0.0017418 | 0.0017315 | 0.0017212 | 0.0017109 | 0.0017006 | 0.0016903 | 0.00168 | 0.0016697 | 0.0016594 | 0.0016491 | 0.0016388 | 0.0016284 | 5.6195e-06 | -3.3224e-06 | 0.00053614 | 0.00054176 | 0.00054738 | 0.000553 | 0.00055862 | 0.0005553 | 0.00055198 | 0.00054865 | 0.00054533 | 0.00054201 | 0.00053869 | 0.00053537 | 0.00053204 | 0.00052872 | 0.0005254 | 0.00052208 | 0.00051875 | 0.00051543 | 0.00051211 | 0.00050879
| WIN011-155049323 | 13 | 13 | 2.89e-05 | 0 | 4.7e-05 | 0 | 4.29e-05 | 0 | 5.1714e-07 | -2.05e-07 | 4.4931e-05 | 4.5449e-05 | 4.5966e-05 | 4.6483e-05 | 4.7e-05 | 4.6795e-05 | 4.659e-05 | 4.6385e-05 | 4.618e-05 | 4.5975e-05 | 4.577e-05 | 4.5565e-05 | 4.536e-05 | 4.5155e-05 | 4.495e-05 | 4.4745e-05 | 4.454e-05 | 4.4335e-05 | 4.413e-05 | 4.3925e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN011-157092882 | 38 | 38 | 0.0031783 | 0 | 0.0047622 | 0 | 0.004357 | 0 | 4.5253e-05 | -2.026e-05 | 0.0045812 | 0.0046264 | 0.0046717 | 0.0047169 | 0.0047622 | 0.0047419 | 0.0047217 | 0.0047014 | 0.0046812 | 0.0046609 | 0.0046406 | 0.0046204 | 0.0046001 | 0.0045799 | 0.0045596 | 0.0045393 | 0.0045191 | 0.0044988 | 0.0044786 | 0.0044583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN011-160628518 | 2317 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN011-160628528 | 2315 | 1537 | 0.0045007 | 0.0027208 | 0.0066335 | 0.0041125 | 0.0058939 | 0.0036334 | 6.0936e-05 | -3.698e-05 | 0.0063897 | 0.0064506 | 0.0065116 | 0.0065725 | 0.0066335 | 0.0065965 | 0.0065595 | 0.0065225 | 0.0064855 | 0.0064486 | 0.0064116 | 0.0063746 | 0.0063376 | 0.0063006 | 0.0062637 | 0.0062267 | 0.0061897 | 0.0061527 | 0.0061157 | 0.0060788 | 3.9763e-05 | -2.3957e-05 | 0.0039535 | 0.0039932 | 0.004033 | 0.0040727 | 0.0041125 | 0.0040886 | 0.0040646 | 0.0040406 | 0.0040167 | 0.0039927 | 0.0039688 | 0.0039448 | 0.0039209 | 0.0038969 | 0.0038729 | 0.003849 | 0.003825 | 0.0038011 | 0.0037771 | 0.0037532
| WIN011-72970601 | 33 | 33 | 0.0017706 | 0 | 0.0027015 | 0 | 0.0028113 | 0 | 2.6597e-05 | 5.4885e-06 | 0.0025951 | 0.0026217 | 0.0026483 | 0.0026749 | 0.0027015 | 0.002707 | 0.0027125 | 0.002718 | 0.0027234 | 0.0027289 | 0.0027344 | 0.0027399 | 0.0027454 | 0.0027509 | 0.0027564 | 0.0027619 | 0.0027674 | 0.0027728 | 0.0027783 | 0.0027838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN011-72970660 | 55 | 55 | 0.0013836 | 0 | 0.0023032 | 0 | 0.0022316 | 0 | 2.6274e-05 | -3.577e-06 | 0.0021981 | 0.0022243 | 0.0022506 | 0.0022769 | 0.0023032 | 0.0022996 | 0.002296 | 0.0022924 | 0.0022888 | 0.0022853 | 0.0022817 | 0.0022781 | 0.0022745 | 0.002271 | 0.0022674 | 0.0022638 | 0.0022602 | 0.0022567 | 0.0022531 | 0.0022495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN011-77738018 | 36 | 36 | 0.0012627 | 0 | 0.0020346 | 0 | 0.0017729 | 0 | 2.2056e-05 | -1.3085e-05 | 0.0019464 | 0.0019685 | 0.0019905 | 0.0020126 | 0.0020346 | 0.0020215 | 0.0020085 | 0.0019954 | 0.0019823 | 0.0019692 | 0.0019561 | 0.001943 | 0.0019299 | 0.0019169 | 0.0019038 | 0.0018907 | 0.0018776 | 0.0018645 | 0.0018514 | 0.0018384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN022-160628376 | 1084 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN022-160628386 | 1083 | 968 | 0.0080132 | 0.00016236 | 0.011179 | 0.00023371 | 0.010756 | 0.00022492 | 9.0448e-05 | -2.112e-05 | 0.010817 | 0.010908 | 0.010998 | 0.011088 | 0.011179 | 0.011158 | 0.011137 | 0.011115 | 0.011094 | 0.011073 | 0.011052 | 0.011031 | 0.01101 | 0.010989 | 0.010968 | 0.010947 | 0.010925 | 0.010904 | 0.010883 | 0.010862 | 2.0386e-06 | -4.3955e-07 | 0.00022556 | 0.0002276 | 0.00022964 | 0.00023167 | 0.00023371 | 0.00023327 | 0.00023283 | 0.00023239 | 0.00023195 | 0.00023152 | 0.00023108 | 0.00023064 | 0.0002302 | 0.00022976 | 0.00022932 | 0.00022888 | 0.00022844 | 0.000228 | 0.00022756 | 0.00022712
| WIN022-164674921 | 20 | 20 | 2.84e-06 | 0 | 4.34e-06 | 0 | 4.19e-06 | 0 | 4.2857e-08 | -7.5e-09 | 4.1686e-06 | 4.2114e-06 | 4.2543e-06 | 4.2971e-06 | 4.34e-06 | 4.3325e-06 | 4.325e-06 | 4.3175e-06 | 4.31e-06 | 4.3025e-06 | 4.295e-06 | 4.2875e-06 | 4.28e-06 | 4.2725e-06 | 4.265e-06 | 4.2575e-06 | 4.25e-06 | 4.2425e-06 | 4.235e-06 | 4.2275e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN022-164675227 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN022-183128966 | 24 | 24 | 8.41e-05 | 0 | 0.00010906 | 0 | 0.00010761 | 0 | 7.132e-07 | -7.255e-08 | 0.00010621 | 0.00010692 | 0.00010764 | 0.00010835 | 0.00010906 | 0.00010899 | 0.00010892 | 0.00010884 | 0.00010877 | 0.0001087 | 0.00010863 | 0.00010855 | 0.00010848 | 0.00010841 | 0.00010834 | 0.00010826 | 0.00010819 | 0.00010812 | 0.00010805 | 0.00010797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN022-79032273 | 30 | 30 | 1.79e-05 | 0 | 2.55e-05 | 0 | 2.55e-05 | 0 | 2.1714e-07 | 0 | 2.4631e-05 | 2.4849e-05 | 2.5066e-05 | 2.5283e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 2.55e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN022-79245551 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN023-154876693 | 34 | 34 | 0.00066545 | 0 | 0.00090816 | 0 | 0.0009219 | 0 | 6.9345e-06 | 6.873e-07 | 0.00088042 | 0.00088736 | 0.00089429 | 0.00090122 | 0.00090816 | 0.00090885 | 0.00090953 | 0.00091022 | 0.00091091 | 0.0009116 | 0.00091228 | 0.00091297 | 0.00091366 | 0.00091434 | 0.00091503 | 0.00091572 | 0.00091641 | 0.00091709 | 0.00091778 | 0.00091847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN023-154908067 | 8 | 8 | 1.1e-05 | 0 | 1.69e-05 | 0 | 1.71e-05 | 0 | 1.6857e-07 | 1e-08 | 1.6226e-05 | 1.6394e-05 | 1.6563e-05 | 1.6731e-05 | 1.69e-05 | 1.691e-05 | 1.692e-05 | 1.693e-05 | 1.694e-05 | 1.695e-05 | 1.696e-05 | 1.697e-05 | 1.698e-05 | 1.699e-05 | 1.7e-05 | 1.701e-05 | 1.702e-05 | 1.703e-05 | 1.704e-05 | 1.705e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN023-160628335 | 851 | 755 | 0.0047669 | 0.0012841 | 0.0063613 | 0.0018136 | 0.0066043 | 0.001897 | 4.5553e-05 | 1.215e-05 | 0.0061791 | 0.0062246 | 0.0062702 | 0.0063157 | 0.0063613 | 0.0063734 | 0.0063856 | 0.0063977 | 0.0064099 | 0.006422 | 0.0064342 | 0.0064463 | 0.0064585 | 0.0064706 | 0.0064828 | 0.0064949 | 0.0065071 | 0.0065192 | 0.0065314 | 0.0065435 | 1.5129e-05 | 4.1701e-06 | 0.0017531 | 0.0017682 | 0.0017834 | 0.0017985 | 0.0018136 | 0.0018178 | 0.001822 | 0.0018261 | 0.0018303 | 0.0018345 | 0.0018386 | 0.0018428 | 0.001847 | 0.0018511 | 0.0018553 | 0.0018595 | 0.0018637 | 0.0018678 | 0.001872 | 0.0018762
| WIN023-73352598 | 34 | 34 | 8.67e-05 | 0 | 0.00016015 | 0 | 0.00016015 | 0 | 2.0986e-06 | 0 | 0.00015176 | 0.00015386 | 0.00015595 | 0.00015805 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0.00016015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN023-84419247 | 20 | 20 | 5.12e-05 | 0 | 8.23e-05 | 0 | 8.43e-05 | 0 | 8.8857e-07 | 1e-07 | 7.8746e-05 | 7.9634e-05 | 8.0523e-05 | 8.1411e-05 | 8.23e-05 | 8.24e-05 | 8.25e-05 | 8.26e-05 | 8.27e-05 | 8.28e-05 | 8.29e-05 | 8.3e-05 | 8.31e-05 | 8.32e-05 | 8.33e-05 | 8.34e-05 | 8.35e-05 | 8.36e-05 | 8.37e-05 | 8.38e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WMN013-117981106 | 109 | 38 | 0.004498 | 0.00076403 | 0.0055196 | 0.0011069 | 0.0051669 | 0.0010834 | 2.919e-05 | -1.7635e-05 | 0.0054028 | 0.005432 | 0.0054612 | 0.0054904 | 0.0055196 | 0.005502 | 0.0054843 | 0.0054667 | 0.0054491 | 0.0054314 | 0.0054138 | 0.0053961 | 0.0053785 | 0.0053609 | 0.0053432 | 0.0053256 | 0.005308 | 0.0052903 | 0.0052727 | 0.0052551 | 9.7952e-06 | -1.1738e-06 | 0.0010677 | 0.0010775 | 0.0010873 | 0.0010971 | 0.0011069 | 0.0011057 | 0.0011045 | 0.0011033 | 0.0011022 | 0.001101 | 0.0010998 | 0.0010986 | 0.0010975 | 0.0010963 | 0.0010951 | 0.001094 | 0.0010928 | 0.0010916 | 0.0010904 | 0.0010893
| WMN013-24614054 | 71 | 71 | 0.020096 | 0 | 0.027037 | 0 | 0.026055 | 0 | 0.00019831 | -4.9092e-05 | 0.026244 | 0.026442 | 0.02664 | 0.026839 | 0.027037 | 0.026988 | 0.026939 | 0.02689 | 0.026841 | 0.026792 | 0.026743 | 0.026693 | 0.026644 | 0.026595 | 0.026546 | 0.026497 | 0.026448 | 0.026399 | 0.02635 | 0.026301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WMN014-122227235 | 168 | 168 | 0.0078055 | 0 | 0.0082103 | 0 | 0.0078812 | 0 | 1.1567e-05 | -1.6454e-05 | 0.008164 | 0.0081756 | 0.0081872 | 0.0081987 | 0.0082103 | 0.0081938 | 0.0081774 | 0.0081609 | 0.0081445 | 0.008128 | 0.0081116 | 0.0080951 | 0.0080787 | 0.0080622 | 0.0080458 | 0.0080293 | 0.0080129 | 0.0079964 | 0.0079799 | 0.0079635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WMN014-164366245 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WMN014-42253278 | 10 | 3 | 0.00088019 | 0 | 0.0012952 | 0 | 0.0012981 | 0 | 1.1859e-05 | 1.4225e-07 | 0.0012478 | 0.0012597 | 0.0012715 | 0.0012834 | 0.0012952 | 0.0012954 | 0.0012955 | 0.0012957 | 0.0012958 | 0.0012959 | 0.0012961 | 0.0012962 | 0.0012964 | 0.0012965 | 0.0012967 | 0.0012968 | 0.0012969 | 0.0012971 | 0.0012972 | 0.0012974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WMN014-62615661 | 190 | 12 | 0.003881 | 0.00012831 | 0.0052745 | 0.00019054 | 0.0051591 | 0.00019164 | 3.9813e-05 | -5.7714e-06 | 0.0051152 | 0.005155 | 0.0051949 | 0.0052347 | 0.0052745 | 0.0052687 | 0.0052629 | 0.0052572 | 0.0052514 | 0.0052456 | 0.0052399 | 0.0052341 | 0.0052283 | 0.0052225 | 0.0052168 | 0.005211 | 0.0052052 | 0.0051995 | 0.0051937 | 0.0051879 | 1.7779e-06 | 5.505e-08 | 0.00018343 | 0.0001852 | 0.00018698 | 0.00018876 | 0.00019054 | 0.00019059 | 0.00019065 | 0.0001907 | 0.00019076 | 0.00019081 | 0.00019087 | 0.00019092 | 0.00019098 | 0.00019103 | 0.00019109 | 0.00019114 | 0.0001912 | 0.00019125 | 0.00019131 | 0.00019136
| WMN021-160652994 | 20 | 20 | 0.00024931 | 0 | 0.00037611 | 0 | 0.00037024 | 0 | 3.6228e-06 | -2.935e-07 | 0.00036162 | 0.00036524 | 0.00036886 | 0.00037248 | 0.00037611 | 0.00037581 | 0.00037552 | 0.00037523 | 0.00037493 | 0.00037464 | 0.00037435 | 0.00037405 | 0.00037376 | 0.00037347 | 0.00037317 | 0.00037288 | 0.00037258 | 0.00037229 | 0.000372 | 0.0003717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WMN021-164365974 | 3 | 3 | 0.0024775 | 0 | 0.0033681 | 0 | 0.0033558 | 0 | 2.5447e-05 | -6.1655e-07 | 0.0032663 | 0.0032918 | 0.0033172 | 0.0033427 | 0.0033681 | 0.0033675 | 0.0033669 | 0.0033663 | 0.0033656 | 0.003365 | 0.0033644 | 0.0033638 | 0.0033632 | 0.0033626 | 0.0033619 | 0.0033613 | 0.0033607 | 0.0033601 | 0.0033595 | 0.0033589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WMN021-24614498 | 8 | 8 | 0.0024885 | 0 | 0.0034706 | 0 | 0.0034554 | 0 | 2.806e-05 | -7.5665e-07 | 0.0033583 | 0.0033864 | 0.0034144 | 0.0034425 | 0.0034706 | 0.0034698 | 0.003469 | 0.0034683 | 0.0034675 | 0.0034668 | 0.003466 | 0.0034653 | 0.0034645 | 0.0034638 | 0.003463 | 0.0034622 | 0.0034615 | 0.0034607 | 0.00346 | 0.0034592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WMN021-24614598 | 73 | 42 | 0.00022755 | 0.0013385 | 0.00032 | 0.001943 | 0.00031196 | 0.0019141 | 2.6413e-06 | -4.0175e-07 | 0.00030943 | 0.00031207 | 0.00031471 | 0.00031735 | 0.00032 | 0.00031959 | 0.00031919 | 0.00031879 | 0.00031839 | 0.00031799 | 0.00031758 | 0.00031718 | 0.00031678 | 0.00031638 | 0.00031598 | 0.00031558 | 0.00031517 | 0.00031477 | 0.00031437 | 0.00031397 | 1.7273e-05 | -1.4471e-06 | 0.001874 | 0.0018912 | 0.0019085 | 0.0019258 | 0.001943 | 0.0019416 | 0.0019401 | 0.0019387 | 0.0019373 | 0.0019358 | 0.0019344 | 0.0019329 | 0.0019315 | 0.00193 | 0.0019286 | 0.0019271 | 0.0019257 | 0.0019242 | 0.0019228 | 0.0019213
| WMN021-65221877 | 78 | 5 | 0.002868 | 3.37e-05 | 0.0038836 | 5.08e-05 | 0.0037169 | 5.04e-05 | 2.9019e-05 | -8.3395e-06 | 0.0037676 | 0.0037966 | 0.0038256 | 0.0038546 | 0.0038836 | 0.0038753 | 0.003867 | 0.0038586 | 0.0038503 | 0.0038419 | 0.0038336 | 0.0038253 | 0.0038169 | 0.0038086 | 0.0038002 | 0.0037919 | 0.0037836 | 0.0037752 | 0.0037669 | 0.0037586 | 4.8857e-07 | -2e-08 | 4.8846e-05 | 4.9334e-05 | 4.9823e-05 | 5.0311e-05 | 5.08e-05 | 5.078e-05 | 5.076e-05 | 5.074e-05 | 5.072e-05 | 5.07e-05 | 5.068e-05 | 5.066e-05 | 5.064e-05 | 5.062e-05 | 5.06e-05 | 5.058e-05 | 5.056e-05 | 5.054e-05 | 5.052e-05 | 5.05e-05
| WND011-15425526 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND011-200942344 | 267 | 184 | 0.018801 | 0.0020598 | 0.026844 | 0.0033184 | 0.02916 | 0.0037345 | 0.0002298 | 0.00011581 | 0.025925 | 0.026154 | 0.026384 | 0.026614 | 0.026844 | 0.02696 | 0.027075 | 0.027191 | 0.027307 | 0.027423 | 0.027539 | 0.027654 | 0.02777 | 0.027886 | 0.028002 | 0.028118 | 0.028234 | 0.028349 | 0.028465 | 0.028581 | 3.5962e-05 | 2.0802e-05 | 0.0031746 | 0.0032105 | 0.0032465 | 0.0032825 | 0.0033184 | 0.0033392 | 0.00336 | 0.0033808 | 0.0034016 | 0.0034224 | 0.0034432 | 0.003464 | 0.0034848 | 0.0035056 | 0.0035264 | 0.0035472 | 0.003568 | 0.0035888 | 0.0036097 | 0.0036305
| WND011-74053613 | 29 | 29 | 0.0022202 | 0 | 0.0032692 | 0 | 0.0037791 | 0 | 2.9972e-05 | 2.5498e-05 | 0.0031493 | 0.0031793 | 0.0032092 | 0.0032392 | 0.0032692 | 0.0032947 | 0.0033202 | 0.0033457 | 0.0033712 | 0.0033967 | 0.0034222 | 0.0034477 | 0.0034732 | 0.0034987 | 0.0035242 | 0.0035497 | 0.0035752 | 0.0036007 | 0.0036262 | 0.0036517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND011-79727477 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND012-171309560 | 7 | 7 | 0.0018314 | 0 | 0.0027419 | 0 | 0.003162 | 0 | 2.6012e-05 | 2.1005e-05 | 0.0026378 | 0.0026638 | 0.0026898 | 0.0027159 | 0.0027419 | 0.0027629 | 0.0027839 | 0.0028049 | 0.0028259 | 0.0028469 | 0.0028679 | 0.0028889 | 0.0029099 | 0.0029309 | 0.0029519 | 0.0029729 | 0.0029939 | 0.0030149 | 0.0030359 | 0.0030569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND012-200942480 | 3569 | 1121 | 0.015219 | 0.0020284 | 0.022099 | 0.0028689 | 0.024376 | 0.0030999 | 0.00019656 | 0.00011388 | 0.021313 | 0.021509 | 0.021706 | 0.021902 | 0.022099 | 0.022213 | 0.022327 | 0.02244 | 0.022554 | 0.022668 | 0.022782 | 0.022896 | 0.02301 | 0.023124 | 0.023238 | 0.023351 | 0.023465 | 0.023579 | 0.023693 | 0.023807 | 2.4016e-05 | 1.1549e-05 | 0.0027729 | 0.0027969 | 0.0028209 | 0.0028449 | 0.0028689 | 0.0028805 | 0.002892 | 0.0029036 | 0.0029151 | 0.0029267 | 0.0029382 | 0.0029498 | 0.0029613 | 0.0029729 | 0.0029844 | 0.002996 | 0.0030075 | 0.0030191 | 0.0030306 | 0.0030422
| WND012-24611463 | 2448 | 0 | 0.0028763 | 0.0074739 | 0.0039109 | 0.011099 | 0.0040701 | 0.011707 | 2.9559e-05 | 7.9579e-06 | 0.0037927 | 0.0038222 | 0.0038518 | 0.0038813 | 0.0039109 | 0.0039189 | 0.0039268 | 0.0039348 | 0.0039427 | 0.0039507 | 0.0039586 | 0.0039666 | 0.0039746 | 0.0039825 | 0.0039905 | 0.0039984 | 0.0040064 | 0.0040143 | 0.0040223 | 0.0040303 | 0.00010356 | 3.0399e-05 | 0.010684 | 0.010788 | 0.010892 | 0.010995 | 0.011099 | 0.011129 | 0.011159 | 0.01119 | 0.01122 | 0.011251 | 0.011281 | 0.011311 | 0.011342 | 0.011372 | 0.011403 | 0.011433 | 0.011463 | 0.011494 | 0.011524 | 0.011555
| WND012-72499182 | 41 | 41 | 0.0011672 | 0 | 0.0016887 | 0 | 0.0017526 | 0 | 1.4901e-05 | 3.1915e-06 | 0.0016291 | 0.001644 | 0.0016589 | 0.0016738 | 0.0016887 | 0.0016919 | 0.0016951 | 0.0016983 | 0.0017015 | 0.0017047 | 0.0017079 | 0.0017111 | 0.0017143 | 0.0017175 | 0.0017206 | 0.0017238 | 0.001727 | 0.0017302 | 0.0017334 | 0.0017366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND012-72499328 | 60 | 60 | 0.0042349 | 0 | 0.0059862 | 0 | 0.0068322 | 0 | 5.0037e-05 | 4.2301e-05 | 0.005786 | 0.0058361 | 0.0058861 | 0.0059361 | 0.0059862 | 0.0060285 | 0.0060708 | 0.0061131 | 0.0061554 | 0.0061977 | 0.00624 | 0.0062823 | 0.0063246 | 0.0063669 | 0.0064092 | 0.0064515 | 0.0064938 | 0.0065361 | 0.0065784 | 0.0066207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND012-73767156 | 49 | 49 | 0.0026852 | 0 | 0.0038686 | 0 | 0.0039928 | 0 | 3.3812e-05 | 6.2072e-06 | 0.0037334 | 0.0037672 | 0.003801 | 0.0038348 | 0.0038686 | 0.0038749 | 0.0038811 | 0.0038873 | 0.0038935 | 0.0038997 | 0.0039059 | 0.0039121 | 0.0039183 | 0.0039245 | 0.0039307 | 0.0039369 | 0.0039431 | 0.0039493 | 0.0039555 | 0.0039618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND012-74645078 | 68 | 68 | 0.009026 | 0 | 0.013657 | 0 | 0.015025 | 0 | 0.0001323 | 6.8419e-05 | 0.013127 | 0.01326 | 0.013392 | 0.013524 | 0.013657 | 0.013725 | 0.013793 | 0.013862 | 0.01393 | 0.013999 | 0.014067 | 0.014136 | 0.014204 | 0.014272 | 0.014341 | 0.014409 | 0.014478 | 0.014546 | 0.014614 | 0.014683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND012-74645220 | 18 | 18 | 0.0017408 | 0 | 0.0025289 | 0 | 0.0029166 | 0 | 2.2517e-05 | 1.9382e-05 | 0.0024389 | 0.0024614 | 0.0024839 | 0.0025064 | 0.0025289 | 0.0025483 | 0.0025677 | 0.0025871 | 0.0026065 | 0.0026258 | 0.0026452 | 0.0026646 | 0.002684 | 0.0027034 | 0.0027228 | 0.0027421 | 0.0027615 | 0.0027809 | 0.0028003 | 0.0028197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND012-77737071 | 9 | 9 | 0.00076524 | 0 | 0.001172 | 0 | 0.0012939 | 0 | 1.1621e-05 | 6.0984e-06 | 0.0011255 | 0.0011371 | 0.0011487 | 0.0011604 | 0.001172 | 0.0011781 | 0.0011842 | 0.0011903 | 0.0011964 | 0.0012025 | 0.0012086 | 0.0012147 | 0.0012208 | 0.0012269 | 0.001233 | 0.0012391 | 0.0012452 | 0.0012513 | 0.0012574 | 0.0012635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND012-78928850 | 8 | 8 | 0.00010452 | 0 | 0.00015461 | 0 | 0.00016494 | 0 | 1.4312e-06 | 5.164e-07 | 0.00014889 | 0.00015032 | 0.00015175 | 0.00015318 | 0.00015461 | 0.00015513 | 0.00015564 | 0.00015616 | 0.00015668 | 0.00015719 | 0.00015771 | 0.00015823 | 0.00015874 | 0.00015926 | 0.00015978 | 0.00016029 | 0.00016081 | 0.00016133 | 0.00016184 | 0.00016236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND012-85319302 | 30 | 30 | 0.002125 | 0 | 0.00333 | 0 | 0.003647 | 0 | 3.4428e-05 | 1.5852e-05 | 0.0031923 | 0.0032267 | 0.0032612 | 0.0032956 | 0.00333 | 0.0033459 | 0.0033617 | 0.0033776 | 0.0033934 | 0.0034093 | 0.0034251 | 0.003441 | 0.0034568 | 0.0034727 | 0.0034885 | 0.0035044 | 0.0035202 | 0.0035361 | 0.0035519 | 0.0035678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND012-88220025 | 39 | 39 | 0.0062364 | 0 | 0.0088131 | 0 | 0.0095721 | 0 | 7.3622e-05 | 3.7948e-05 | 0.0085187 | 0.0085923 | 0.0086659 | 0.0087395 | 0.0088131 | 0.0088511 | 0.008889 | 0.008927 | 0.0089649 | 0.0090029 | 0.0090408 | 0.0090788 | 0.0091167 | 0.0091547 | 0.0091926 | 0.0092306 | 0.0092685 | 0.0093065 | 0.0093444 | 0.0093824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND012-93532503 | 1257 | 1219 | 0.0021923 | 0.0016386 | 0.0033552 | 0.0025738 | 0.0036554 | 0.0028199 | 3.3226e-05 | 1.5013e-05 | 0.0032223 | 0.0032555 | 0.0032887 | 0.003322 | 0.0033552 | 0.0033702 | 0.0033852 | 0.0034002 | 0.0034152 | 0.0034303 | 0.0034453 | 0.0034603 | 0.0034753 | 0.0034903 | 0.0035053 | 0.0035203 | 0.0035353 | 0.0035504 | 0.0035654 | 0.0035804 | 2.6721e-05 | 1.2304e-05 | 0.0024669 | 0.0024937 | 0.0025204 | 0.0025471 | 0.0025738 | 0.0025861 | 0.0025984 | 0.0026107 | 0.002623 | 0.0026353 | 0.0026476 | 0.00266 | 0.0026723 | 0.0026846 | 0.0026969 | 0.0027092 | 0.0027215 | 0.0027338 | 0.0027461 | 0.0027584
| WND012-93532641 | 2157 | 900 | 0.0008241 | 0.0015989 | 0.0012562 | 0.0025171 | 0.0013305 | 0.0026781 | 1.2346e-05 | 3.7159e-06 | 0.0012068 | 0.0012192 | 0.0012315 | 0.0012439 | 0.0012562 | 0.0012599 | 0.0012637 | 0.0012674 | 0.0012711 | 0.0012748 | 0.0012785 | 0.0012822 | 0.0012859 | 0.0012897 | 0.0012934 | 0.0012971 | 0.0013008 | 0.0013045 | 0.0013082 | 0.001312 | 2.6236e-05 | 8.0503e-06 | 0.0024122 | 0.0024384 | 0.0024647 | 0.0024909 | 0.0025171 | 0.0025252 | 0.0025332 | 0.0025413 | 0.0025493 | 0.0025574 | 0.0025654 | 0.0025735 | 0.0025815 | 0.0025896 | 0.0025976 | 0.0026057 | 0.0026137 | 0.0026218 | 0.0026298 | 0.0026379
| WND013-139460835 | 904 | 687 | 0.0069096 | 0.0040624 | 0.0094296 | 0.0060994 | 0.010231 | 0.0068495 | 7.1999e-05 | 4.0083e-05 | 0.0091416 | 0.0092136 | 0.0092856 | 0.0093576 | 0.0094296 | 0.0094697 | 0.0095097 | 0.0095498 | 0.0095899 | 0.00963 | 0.0096701 | 0.0097101 | 0.0097502 | 0.0097903 | 0.0098304 | 0.0098705 | 0.0099106 | 0.0099506 | 0.0099907 | 0.010031 | 5.82e-05 | 3.7505e-05 | 0.0058666 | 0.0059248 | 0.005983 | 0.0060412 | 0.0060994 | 0.0061369 | 0.0061744 | 0.0062119 | 0.0062494 | 0.0062869 | 0.0063244 | 0.0063619 | 0.0063994 | 0.0064369 | 0.0064744 | 0.0065119 | 0.0065494 | 0.0065869 | 0.0066244 | 0.0066619
| WND013-163356845 | 3 | 3 | 0.0011557 | 0 | 0.0018527 | 0 | 0.0021043 | 0 | 1.9915e-05 | 1.2578e-05 | 0.0017731 | 0.001793 | 0.0018129 | 0.0018328 | 0.0018527 | 0.0018653 | 0.0018779 | 0.0018905 | 0.001903 | 0.0019156 | 0.0019282 | 0.0019408 | 0.0019534 | 0.0019659 | 0.0019785 | 0.0019911 | 0.0020037 | 0.0020162 | 0.0020288 | 0.0020414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-172348741 | 7 | 7 | 0.0011526 | 0 | 0.0017483 | 0 | 0.0020158 | 0 | 1.7022e-05 | 1.3373e-05 | 0.0016802 | 0.0016973 | 0.0017143 | 0.0017313 | 0.0017483 | 0.0017617 | 0.0017751 | 0.0017885 | 0.0018018 | 0.0018152 | 0.0018286 | 0.0018419 | 0.0018553 | 0.0018687 | 0.0018821 | 0.0018954 | 0.0019088 | 0.0019222 | 0.0019356 | 0.0019489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-200942552 | 2863 | 1584 | 0.0050226 | 0.006616 | 0.0061676 | 0.009907 | 0.006494 | 0.011115 | 3.2714e-05 | 1.632e-05 | 0.0060368 | 0.0060695 | 0.0061022 | 0.0061349 | 0.0061676 | 0.0061839 | 0.0062003 | 0.0062166 | 0.0062329 | 0.0062492 | 0.0062655 | 0.0062819 | 0.0062982 | 0.0063145 | 0.0063308 | 0.0063471 | 0.0063635 | 0.0063798 | 0.0063961 | 0.0064124 | 9.4029e-05 | 6.0379e-05 | 0.0095309 | 0.0096249 | 0.009719 | 0.009813 | 0.009907 | 0.0099674 | 0.010028 | 0.010088 | 0.010149 | 0.010209 | 0.010269 | 0.01033 | 0.01039 | 0.01045 | 0.010511 | 0.010571 | 0.010632 | 0.010692 | 0.010752 | 0.010813
| WND013-76546155 | 67 | 67 | 0.0030896 | 0 | 0.0044367 | 0 | 0.004905 | 0 | 3.849e-05 | 2.3414e-05 | 0.0042828 | 0.0043212 | 0.0043597 | 0.0043982 | 0.0044367 | 0.0044601 | 0.0044835 | 0.004507 | 0.0045304 | 0.0045538 | 0.0045772 | 0.0046006 | 0.004624 | 0.0046474 | 0.0046709 | 0.0046943 | 0.0047177 | 0.0047411 | 0.0047645 | 0.0047879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-76546231 | 74 | 74 | 0.0052344 | 0 | 0.0073762 | 0 | 0.008598 | 0 | 6.1194e-05 | 6.1092e-05 | 0.0071314 | 0.0071926 | 0.0072538 | 0.007315 | 0.0073762 | 0.0074373 | 0.0074984 | 0.0075594 | 0.0076205 | 0.0076816 | 0.0077427 | 0.0078038 | 0.0078649 | 0.007926 | 0.0079871 | 0.0080482 | 0.0081093 | 0.0081704 | 0.0082315 | 0.0082926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-76546307 | 17 | 17 | 0.0035173 | 0 | 0.0050328 | 0 | 0.0057471 | 0 | 4.3297e-05 | 3.5716e-05 | 0.0048596 | 0.0049029 | 0.0049462 | 0.0049895 | 0.0050328 | 0.0050685 | 0.0051042 | 0.0051399 | 0.0051756 | 0.0052113 | 0.005247 | 0.0052828 | 0.0053185 | 0.0053542 | 0.0053899 | 0.0054256 | 0.0054613 | 0.0054971 | 0.0055328 | 0.0055685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-76546404 | 76 | 76 | 0.0074165 | 0 | 0.010645 | 0 | 0.012215 | 0 | 9.225e-05 | 7.8494e-05 | 0.010276 | 0.010369 | 0.010461 | 0.010553 | 0.010645 | 0.010724 | 0.010802 | 0.010881 | 0.010959 | 0.011038 | 0.011116 | 0.011195 | 0.011273 | 0.011352 | 0.01143 | 0.011509 | 0.011587 | 0.011666 | 0.011744 | 0.011823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-76546454 | 13 | 13 | 0.0037371 | 0 | 0.005594 | 0 | 0.0065485 | 0 | 5.3052e-05 | 4.7725e-05 | 0.0053817 | 0.0054348 | 0.0054879 | 0.0055409 | 0.005594 | 0.0056417 | 0.0056894 | 0.0057371 | 0.0057849 | 0.0058326 | 0.0058803 | 0.005928 | 0.0059758 | 0.0060235 | 0.0060712 | 0.0061189 | 0.0061667 | 0.0062144 | 0.0062621 | 0.0063098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-76546631 | 20 | 20 | 0.0011347 | 0 | 0.0016264 | 0 | 0.0018899 | 0 | 1.4046e-05 | 1.3177e-05 | 0.0015702 | 0.0015842 | 0.0015983 | 0.0016123 | 0.0016264 | 0.0016395 | 0.0016527 | 0.0016659 | 0.0016791 | 0.0016923 | 0.0017054 | 0.0017186 | 0.0017318 | 0.001745 | 0.0017581 | 0.0017713 | 0.0017845 | 0.0017977 | 0.0018108 | 0.001824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-76546854 | 25 | 25 | 0.0050701 | 0 | 0.0076904 | 0 | 0.0086143 | 0 | 7.4863e-05 | 4.6196e-05 | 0.0073909 | 0.0074658 | 0.0075406 | 0.0076155 | 0.0076904 | 0.0077366 | 0.0077828 | 0.0078289 | 0.0078751 | 0.0079213 | 0.0079675 | 0.0080137 | 0.0080599 | 0.0081061 | 0.0081523 | 0.0081985 | 0.0082447 | 0.0082909 | 0.0083371 | 0.0083833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-78928894 | 42 | 42 | 0.00031606 | 0 | 0.00050375 | 0 | 0.00059309 | 0 | 5.3625e-06 | 4.4667e-06 | 0.0004823 | 0.00048767 | 0.00049303 | 0.00049839 | 0.00050375 | 0.00050822 | 0.00051269 | 0.00051715 | 0.00052162 | 0.00052609 | 0.00053055 | 0.00053502 | 0.00053949 | 0.00054395 | 0.00054842 | 0.00055289 | 0.00055735 | 0.00056182 | 0.00056629 | 0.00057075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-78928958 | 24 | 24 | 0.012435 | 0 | 0.017761 | 0 | 0.020493 | 0 | 0.00015219 | 0.00013662 | 0.017152 | 0.017304 | 0.017457 | 0.017609 | 0.017761 | 0.017898 | 0.018034 | 0.018171 | 0.018308 | 0.018444 | 0.018581 | 0.018717 | 0.018854 | 0.018991 | 0.019127 | 0.019264 | 0.0194 | 0.019537 | 0.019674 | 0.01981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-78929121 | 29 | 29 | 0.0025696 | 0 | 0.0038852 | 0 | 0.0043083 | 0 | 3.7589e-05 | 2.1154e-05 | 0.0037349 | 0.0037724 | 0.00381 | 0.0038476 | 0.0038852 | 0.0039064 | 0.0039275 | 0.0039487 | 0.0039698 | 0.003991 | 0.0040121 | 0.0040333 | 0.0040544 | 0.0040756 | 0.0040968 | 0.0041179 | 0.0041391 | 0.0041602 | 0.0041814 | 0.0042025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-78929255 | 24 | 24 | 0.0011599 | 0 | 0.0017262 | 0 | 0.0018795 | 0 | 1.6179e-05 | 7.6666e-06 | 0.0016615 | 0.0016776 | 0.0016938 | 0.00171 | 0.0017262 | 0.0017338 | 0.0017415 | 0.0017492 | 0.0017568 | 0.0017645 | 0.0017722 | 0.0017798 | 0.0017875 | 0.0017952 | 0.0018028 | 0.0018105 | 0.0018182 | 0.0018258 | 0.0018335 | 0.0018412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-78929377 | 42 | 42 | 0.0018145 | 0 | 0.0028918 | 0 | 0.0032036 | 0 | 3.0779e-05 | 1.5594e-05 | 0.0027687 | 0.0027994 | 0.0028302 | 0.002861 | 0.0028918 | 0.0029074 | 0.002923 | 0.0029386 | 0.0029541 | 0.0029697 | 0.0029853 | 0.0030009 | 0.0030165 | 0.0030321 | 0.0030477 | 0.0030633 | 0.0030789 | 0.0030945 | 0.0031101 | 0.0031257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-85319062 | 23 | 23 | 0.00014987 | 0 | 0.00023152 | 0 | 0.0002567 | 0 | 2.3329e-06 | 1.2591e-06 | 0.00022219 | 0.00022452 | 0.00022685 | 0.00022919 | 0.00023152 | 0.00023278 | 0.00023404 | 0.0002353 | 0.00023656 | 0.00023781 | 0.00023907 | 0.00024033 | 0.00024159 | 0.00024285 | 0.00024411 | 0.00024537 | 0.00024663 | 0.00024789 | 0.00024915 | 0.00025041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-85319560 | 10 | 10 | 0.0016903 | 0 | 0.0025333 | 0 | 0.0029204 | 0 | 2.4085e-05 | 1.9358e-05 | 0.0024369 | 0.002461 | 0.0024851 | 0.0025092 | 0.0025333 | 0.0025526 | 0.002572 | 0.0025913 | 0.0026107 | 0.0026301 | 0.0026494 | 0.0026688 | 0.0026881 | 0.0027075 | 0.0027268 | 0.0027462 | 0.0027656 | 0.0027849 | 0.0028043 | 0.0028236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-85319645 | 4 | 4 | 0.0006745 | 0 | 0.00070732 | 0 | 0.00069918 | 0 | 9.3786e-07 | -4.0715e-07 | 0.00070357 | 0.00070451 | 0.00070545 | 0.00070638 | 0.00070732 | 0.00070691 | 0.00070651 | 0.0007061 | 0.00070569 | 0.00070529 | 0.00070488 | 0.00070447 | 0.00070406 | 0.00070366 | 0.00070325 | 0.00070284 | 0.00070244 | 0.00070203 | 0.00070162 | 0.00070121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-85319854 | 12 | 12 | 0.00074734 | 0 | 0.0011879 | 0 | 0.0012949 | 0 | 1.2588e-05 | 5.3481e-06 | 0.0011376 | 0.0011502 | 0.0011627 | 0.0011753 | 0.0011879 | 0.0011933 | 0.0011986 | 0.001204 | 0.0012093 | 0.0012147 | 0.00122 | 0.0012254 | 0.0012307 | 0.0012361 | 0.0012414 | 0.0012468 | 0.0012521 | 0.0012574 | 0.0012628 | 0.0012681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-85833772 | 45 | 45 | 0.0045413 | 0 | 0.0059491 | 0 | 0.006588 | 0 | 4.0222e-05 | 3.1948e-05 | 0.0057882 | 0.0058284 | 0.0058686 | 0.0059089 | 0.0059491 | 0.005981 | 0.006013 | 0.0060449 | 0.0060769 | 0.0061088 | 0.0061408 | 0.0061727 | 0.0062047 | 0.0062366 | 0.0062686 | 0.0063005 | 0.0063324 | 0.0063644 | 0.0063963 | 0.0064283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND013-89020589 | 28 | 28 | 0.00023311 | 0 | 0.00037277 | 0 | 0.00043943 | 0 | 3.9903e-06 | 3.3332e-06 | 0.00035681 | 0.0003608 | 0.00036479 | 0.00036878 | 0.00037277 | 0.0003761 | 0.00037943 | 0.00038277 | 0.0003861 | 0.00038943 | 0.00039277 | 0.0003961 | 0.00039943 | 0.00040277 | 0.0004061 | 0.00040943 | 0.00041277 | 0.0004161 | 0.00041943 | 0.00042277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND014-153585710 | 70 | 70 | 0.0071171 | 0 | 0.010684 | 0 | 0.011834 | 0 | 0.00010191 | 5.7515e-05 | 0.010276 | 0.010378 | 0.01048 | 0.010582 | 0.010684 | 0.010741 | 0.010799 | 0.010856 | 0.010914 | 0.010971 | 0.011029 | 0.011087 | 0.011144 | 0.011202 | 0.011259 | 0.011317 | 0.011374 | 0.011432 | 0.011489 | 0.011547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND014-15425582 | 2973 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND014-200942632 | 2969 | 2769 | 0.012985 | 0.0098531 | 0.017482 | 0.013949 | 0.018792 | 0.015341 | 0.00012849 | 6.5497e-05 | 0.016968 | 0.017097 | 0.017225 | 0.017354 | 0.017482 | 0.017548 | 0.017613 | 0.017679 | 0.017744 | 0.01781 | 0.017875 | 0.017941 | 0.018006 | 0.018072 | 0.018137 | 0.018203 | 0.018268 | 0.018334 | 0.018399 | 0.018465 | 0.00011703 | 6.9578e-05 | 0.013481 | 0.013598 | 0.013715 | 0.013832 | 0.013949 | 0.014019 | 0.014088 | 0.014158 | 0.014227 | 0.014297 | 0.014367 | 0.014436 | 0.014506 | 0.014575 | 0.014645 | 0.014714 | 0.014784 | 0.014854 | 0.014923 | 0.014993
| WND014-79365293 | 26 | 26 | 0.0032932 | 0 | 0.0050344 | 0 | 0.0056158 | 0 | 4.9747e-05 | 2.9069e-05 | 0.0048354 | 0.0048852 | 0.0049349 | 0.0049847 | 0.0050344 | 0.0050635 | 0.0050925 | 0.0051216 | 0.0051507 | 0.0051797 | 0.0052088 | 0.0052379 | 0.005267 | 0.005296 | 0.0053251 | 0.0053542 | 0.0053832 | 0.0054123 | 0.0054414 | 0.0054704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND014-79365390 | 19 | 19 | 0.00084668 | 0 | 0.001284 | 0 | 0.0014976 | 0 | 1.2495e-05 | 1.0682e-05 | 0.001234 | 0.0012465 | 0.001259 | 0.0012715 | 0.001284 | 0.0012947 | 0.0013054 | 0.0013161 | 0.0013267 | 0.0013374 | 0.0013481 | 0.0013588 | 0.0013695 | 0.0013801 | 0.0013908 | 0.0014015 | 0.0014122 | 0.0014229 | 0.0014336 | 0.0014442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND014-79365841 | 85 | 85 | 0.0074324 | 0 | 0.010727 | 0 | 0.012203 | 0 | 9.4142e-05 | 7.3804e-05 | 0.010351 | 0.010445 | 0.010539 | 0.010633 | 0.010727 | 0.010801 | 0.010875 | 0.010949 | 0.011023 | 0.011096 | 0.01117 | 0.011244 | 0.011318 | 0.011392 | 0.011465 | 0.011539 | 0.011613 | 0.011687 | 0.011761 | 0.011834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND021-15425634 | 828 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND021-200942770 | 825 | 825 | 0.012452 | 0 | 0.018089 | 0 | 0.019918 | 0 | 0.00016105 | 9.145e-05 | 0.017444 | 0.017605 | 0.017766 | 0.017927 | 0.018089 | 0.01818 | 0.018271 | 0.018363 | 0.018454 | 0.018546 | 0.018637 | 0.018729 | 0.01882 | 0.018912 | 0.019003 | 0.019095 | 0.019186 | 0.019277 | 0.019369 | 0.01946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND022-15425649 | 688 | 4 | 0 | 8.36e-06 | 0 | 1.44e-05 | 0 | 1.65e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7257e-07 | 1.05e-07 | 1.371e-05 | 1.3882e-05 | 1.4055e-05 | 1.4227e-05 | 1.44e-05 | 1.4505e-05 | 1.461e-05 | 1.4715e-05 | 1.482e-05 | 1.4925e-05 | 1.503e-05 | 1.5135e-05 | 1.524e-05 | 1.5345e-05 | 1.545e-05 | 1.5555e-05 | 1.566e-05 | 1.5765e-05 | 1.587e-05 | 1.5975e-05
| WND022-200942838 | 684 | 684 | 0.028061 | 0 | 0.042922 | 0 | 0.04779 | 0 | 0.00042459 | 0.00024343 | 0.041223 | 0.041648 | 0.042072 | 0.042497 | 0.042922 | 0.043165 | 0.043409 | 0.043652 | 0.043895 | 0.044139 | 0.044382 | 0.044626 | 0.044869 | 0.045113 | 0.045356 | 0.045599 | 0.045843 | 0.046086 | 0.04633 | 0.046573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND023-200942910 | 1516 | 1326 | 0.020286 | 0.003471 | 0.028831 | 0.0050146 | 0.030048 | 0.0052291 | 0.00024414 | 6.0855e-05 | 0.027855 | 0.028099 | 0.028343 | 0.028587 | 0.028831 | 0.028892 | 0.028953 | 0.029014 | 0.029075 | 0.029136 | 0.029196 | 0.029257 | 0.029318 | 0.029379 | 0.02944 | 0.029501 | 0.029561 | 0.029622 | 0.029683 | 0.029744 | 4.4101e-05 | 1.0725e-05 | 0.0048382 | 0.0048823 | 0.0049264 | 0.0049705 | 0.0050146 | 0.0050253 | 0.005036 | 0.0050467 | 0.0050575 | 0.0050682 | 0.0050789 | 0.0050896 | 0.0051004 | 0.0051111 | 0.0051218 | 0.0051325 | 0.0051433 | 0.005154 | 0.0051647 | 0.0051754
| WND023-73768060 | 60 | 60 | 0.0020529 | 0 | 0.0027975 | 0 | 0.002925 | 0 | 2.1274e-05 | 6.3783e-06 | 0.0027124 | 0.0027337 | 0.0027549 | 0.0027762 | 0.0027975 | 0.0028039 | 0.0028102 | 0.0028166 | 0.002823 | 0.0028294 | 0.0028357 | 0.0028421 | 0.0028485 | 0.0028549 | 0.0028613 | 0.0028676 | 0.002874 | 0.0028804 | 0.0028868 | 0.0028932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND023-73768112 | 30 | 30 | 0.0020305 | 0 | 0.0031921 | 0 | 0.0035179 | 0 | 3.319e-05 | 1.6288e-05 | 0.0030594 | 0.0030926 | 0.0031257 | 0.0031589 | 0.0031921 | 0.0032084 | 0.0032247 | 0.003241 | 0.0032573 | 0.0032736 | 0.0032899 | 0.0033061 | 0.0033224 | 0.0033387 | 0.003355 | 0.0033713 | 0.0033876 | 0.0034039 | 0.0034202 | 0.0034364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND023-73768165 | 52 | 52 | 0.0027659 | 0 | 0.0039252 | 0 | 0.0043271 | 0 | 3.3125e-05 | 2.0091e-05 | 0.0037927 | 0.0038259 | 0.003859 | 0.0038921 | 0.0039252 | 0.0039453 | 0.0039654 | 0.0039855 | 0.0040056 | 0.0040257 | 0.0040458 | 0.0040659 | 0.004086 | 0.0041061 | 0.0041261 | 0.0041462 | 0.0041663 | 0.0041864 | 0.0042065 | 0.0042266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND023-73948116 | 28 | 28 | 0.0010808 | 0 | 0.0015731 | 0 | 0.0017022 | 0 | 1.4065e-05 | 6.4555e-06 | 0.0015168 | 0.0015309 | 0.0015449 | 0.001559 | 0.0015731 | 0.0015795 | 0.001586 | 0.0015924 | 0.0015989 | 0.0016053 | 0.0016118 | 0.0016182 | 0.0016247 | 0.0016312 | 0.0016376 | 0.0016441 | 0.0016505 | 0.001657 | 0.0016634 | 0.0016699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND023-73948154 | 20 | 20 | 0.0020254 | 0 | 0.0027876 | 0 | 0.0029249 | 0 | 2.1777e-05 | 6.8628e-06 | 0.0027005 | 0.0027223 | 0.0027441 | 0.0027658 | 0.0027876 | 0.0027945 | 0.0028013 | 0.0028082 | 0.0028151 | 0.0028219 | 0.0028288 | 0.0028357 | 0.0028425 | 0.0028494 | 0.0028563 | 0.0028631 | 0.00287 | 0.0028768 | 0.0028837 | 0.0028906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND024-167870308 | 39 | 39 | 0.0015964 | 0 | 0.0021416 | 0 | 0.0024344 | 0 | 1.5579e-05 | 1.4637e-05 | 0.0020793 | 0.0020949 | 0.0021105 | 0.002126 | 0.0021416 | 0.0021562 | 0.0021709 | 0.0021855 | 0.0022002 | 0.0022148 | 0.0022294 | 0.0022441 | 0.0022587 | 0.0022733 | 0.002288 | 0.0023026 | 0.0023173 | 0.0023319 | 0.0023465 | 0.0023612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND024-183316836 | 1648 | 973 | 0.01332 | 0.0023377 | 0.015998 | 0.0031674 | 0.01691 | 0.003678 | 7.6498e-05 | 4.5617e-05 | 0.015692 | 0.015768 | 0.015845 | 0.015921 | 0.015998 | 0.016043 | 0.016089 | 0.016135 | 0.01618 | 0.016226 | 0.016272 | 0.016317 | 0.016363 | 0.016408 | 0.016454 | 0.0165 | 0.016545 | 0.016591 | 0.016636 | 0.016682 | 2.3705e-05 | 2.5532e-05 | 0.0030726 | 0.0030963 | 0.00312 | 0.0031437 | 0.0031674 | 0.0031929 | 0.0032185 | 0.003244 | 0.0032695 | 0.0032951 | 0.0033206 | 0.0033461 | 0.0033717 | 0.0033972 | 0.0034227 | 0.0034482 | 0.0034738 | 0.0034993 | 0.0035248 | 0.0035504
| WND024-184539432 | 49 | 49 | 4.9e-06 | 0 | 7.34e-06 | 0 | 9.41e-06 | 0 | 6.9714e-08 | 1.035e-07 | 7.0611e-06 | 7.1309e-06 | 7.2006e-06 | 7.2703e-06 | 7.34e-06 | 7.4435e-06 | 7.547e-06 | 7.6505e-06 | 7.754e-06 | 7.8575e-06 | 7.961e-06 | 8.0645e-06 | 8.168e-06 | 8.2715e-06 | 8.375e-06 | 8.4785e-06 | 8.582e-06 | 8.6855e-06 | 8.789e-06 | 8.8925e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND024-192414587 | 471 | 471 | 0.023906 | 0 | 0.029404 | 0 | 0.031312 | 0 | 0.00015709 | 9.5413e-05 | 0.028776 | 0.028933 | 0.02909 | 0.029247 | 0.029404 | 0.029499 | 0.029595 | 0.02969 | 0.029786 | 0.029881 | 0.029977 | 0.030072 | 0.030167 | 0.030263 | 0.030358 | 0.030454 | 0.030549 | 0.030644 | 0.03074 | 0.030835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND024-200942990 | 2045 | 346 | 0.0093582 | 0.0021953 | 0.013238 | 0.0033771 | 0.014374 | 0.0037793 | 0.00011085 | 5.6778e-05 | 0.012795 | 0.012905 | 0.013016 | 0.013127 | 0.013238 | 0.013295 | 0.013352 | 0.013408 | 0.013465 | 0.013522 | 0.013579 | 0.013635 | 0.013692 | 0.013749 | 0.013806 | 0.013863 | 0.013919 | 0.013976 | 0.014033 | 0.01409 | 3.3766e-05 | 2.0112e-05 | 0.003242 | 0.0032758 | 0.0033096 | 0.0033433 | 0.0033771 | 0.0033972 | 0.0034173 | 0.0034374 | 0.0034575 | 0.0034776 | 0.0034978 | 0.0035179 | 0.003538 | 0.0035581 | 0.0035782 | 0.0035983 | 0.0036184 | 0.0036385 | 0.0036587 | 0.0036788
| WND024-79365148 | 9 | 9 | 0.0013749 | 0 | 0.0018678 | 0 | 0.0021572 | 0 | 1.4085e-05 | 1.4468e-05 | 0.0018115 | 0.0018256 | 0.0018397 | 0.0018537 | 0.0018678 | 0.0018823 | 0.0018968 | 0.0019112 | 0.0019257 | 0.0019402 | 0.0019546 | 0.0019691 | 0.0019836 | 0.001998 | 0.0020125 | 0.002027 | 0.0020415 | 0.0020559 | 0.0020704 | 0.0020849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD011-15399272 | 1846 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD011-15399285 | 1835 | 1835 | 0.0053684 | 0 | 0.0067228 | 0 | 0.0068358 | 0 | 3.8698e-05 | 5.6501e-06 | 0.006568 | 0.0066067 | 0.0066454 | 0.0066841 | 0.0067228 | 0.0067285 | 0.0067341 | 0.0067398 | 0.0067454 | 0.0067511 | 0.0067567 | 0.0067624 | 0.006768 | 0.0067737 | 0.0067793 | 0.006785 | 0.0067906 | 0.0067963 | 0.0068019 | 0.0068076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD012-15436728 | 4690 | 2427 | 0.0054607 | 3.71e-07 | 0.0070662 | 4.47e-07 | 0.0070976 | 3.8e-07 | 4.5871e-05 | 1.568e-06 | 0.0068827 | 0.0069286 | 0.0069745 | 0.0070203 | 0.0070662 | 0.0070678 | 0.0070693 | 0.0070709 | 0.0070725 | 0.007074 | 0.0070756 | 0.0070772 | 0.0070787 | 0.0070803 | 0.0070819 | 0.0070834 | 0.007085 | 0.0070866 | 0.0070881 | 0.0070897 | 2.1714e-09 | -3.35e-09 | 4.3831e-07 | 4.4049e-07 | 4.4266e-07 | 4.4483e-07 | 4.47e-07 | 4.4365e-07 | 4.403e-07 | 4.3695e-07 | 4.336e-07 | 4.3025e-07 | 4.269e-07 | 4.2355e-07 | 4.202e-07 | 4.1685e-07 | 4.135e-07 | 4.1015e-07 | 4.068e-07 | 4.0345e-07 | 4.001e-07 | 3.9675e-07
| WPD012-24603816 | 2263 | 2263 | 0.0048681 | 0 | 0.0062894 | 0 | 0.0063397 | 0 | 4.0608e-05 | 2.513e-06 | 0.006127 | 0.0061676 | 0.0062082 | 0.0062488 | 0.0062894 | 0.0062919 | 0.0062944 | 0.0062969 | 0.0062994 | 0.006302 | 0.0063045 | 0.006307 | 0.0063095 | 0.006312 | 0.0063145 | 0.006317 | 0.0063196 | 0.0063221 | 0.0063246 | 0.0063271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD013-178115477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD013-40657711 | 55 | 55 | 0.0027601 | 0 | 0.0035362 | 0 | 0.0035558 | 0 | 2.2175e-05 | 9.7765e-07 | 0.0034475 | 0.0034697 | 0.0034919 | 0.0035141 | 0.0035362 | 0.0035372 | 0.0035382 | 0.0035392 | 0.0035402 | 0.0035411 | 0.0035421 | 0.0035431 | 0.0035441 | 0.003545 | 0.003546 | 0.003547 | 0.003548 | 0.003549 | 0.0035499 | 0.0035509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD014-15399222 | 1634 | 1549 | 0.0050463 | 0.0031645 | 0.0051532 | 0.003218 | 0.0049926 | 0.0031361 | 3.0541e-06 | -8.0277e-06 | 0.005141 | 0.005144 | 0.0051471 | 0.0051501 | 0.0051532 | 0.0051452 | 0.0051371 | 0.0051291 | 0.0051211 | 0.0051131 | 0.005105 | 0.005097 | 0.005089 | 0.0050809 | 0.0050729 | 0.0050649 | 0.0050569 | 0.0050488 | 0.0050408 | 0.0050328 | 1.5276e-06 | -4.0944e-06 | 0.0032119 | 0.0032134 | 0.0032149 | 0.0032165 | 0.003218 | 0.0032139 | 0.0032098 | 0.0032057 | 0.0032016 | 0.0031975 | 0.0031934 | 0.0031893 | 0.0031852 | 0.0031811 | 0.003177 | 0.0031729 | 0.0031688 | 0.0031648 | 0.0031607 | 0.0031566
| WPD014-15399233 | 85 | 85 | 0.0024674 | 0 | 0.0031136 | 0 | 0.003083 | 0 | 1.8464e-05 | -1.5326e-06 | 0.0030398 | 0.0030582 | 0.0030767 | 0.0030951 | 0.0031136 | 0.0031121 | 0.0031105 | 0.003109 | 0.0031075 | 0.0031059 | 0.0031044 | 0.0031029 | 0.0031014 | 0.0030998 | 0.0030983 | 0.0030968 | 0.0030952 | 0.0030937 | 0.0030922 | 0.0030906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD021-15399198 | 2276 | 2276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD022-15399022 | 5191 | 3479 | 0.024751 | 0.011331 | 0.025222 | 0.011447 | 0.024508 | 0.011276 | 1.346e-05 | -3.5697e-05 | 0.025168 | 0.025182 | 0.025195 | 0.025209 | 0.025222 | 0.025187 | 0.025151 | 0.025115 | 0.025079 | 0.025044 | 0.025008 | 0.024972 | 0.024937 | 0.024901 | 0.024865 | 0.02483 | 0.024794 | 0.024758 | 0.024723 | 0.024687 | 3.2933e-06 | -8.5502e-06 | 0.011433 | 0.011437 | 0.01144 | 0.011443 | 0.011447 | 0.011438 | 0.01143 | 0.011421 | 0.011412 | 0.011404 | 0.011395 | 0.011387 | 0.011378 | 0.01137 | 0.011361 | 0.011353 | 0.011344 | 0.011335 | 0.011327 | 0.011318
| WPD022-72495720 | 1712 | 1712 | 0.0040461 | 0 | 0.0043656 | 0 | 0.0039768 | 0 | 9.1266e-06 | -1.9438e-05 | 0.0043291 | 0.0043382 | 0.0043473 | 0.0043564 | 0.0043656 | 0.0043461 | 0.0043267 | 0.0043072 | 0.0042878 | 0.0042684 | 0.0042489 | 0.0042295 | 0.00421 | 0.0041906 | 0.0041712 | 0.0041517 | 0.0041323 | 0.0041129 | 0.0040934 | 0.004074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD024-15398985 | 5439 | 5439 | 0.011645 | 0 | 0.013912 | 0 | 0.013463 | 0 | 6.4772e-05 | -2.2433e-05 | 0.013653 | 0.013718 | 0.013782 | 0.013847 | 0.013912 | 0.013889 | 0.013867 | 0.013845 | 0.013822 | 0.0138 | 0.013777 | 0.013755 | 0.013732 | 0.01371 | 0.013688 | 0.013665 | 0.013643 | 0.01362 | 0.013598 | 0.013575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD031-15399072 | 3692 | 2242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD031-80918872 | 1450 | 1450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD033-153773704 | 218 | 218 | 0.0063529 | 0 | 0.0088335 | 0 | 0.0095063 | 0 | 7.0873e-05 | 3.3641e-05 | 0.00855 | 0.0086209 | 0.0086918 | 0.0087626 | 0.0088335 | 0.0088671 | 0.0089008 | 0.0089344 | 0.0089681 | 0.0090017 | 0.0090353 | 0.009069 | 0.0091026 | 0.0091363 | 0.0091699 | 0.0092035 | 0.0092372 | 0.0092708 | 0.0093045 | 0.0093381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD033-15399135 | 3692 | 2570 | 0.0093228 | 0.0045884 | 0.01103 | 0.0060381 | 0.011224 | 0.0064 | 4.8764e-05 | 9.7104e-06 | 0.010834 | 0.010883 | 0.010932 | 0.010981 | 0.01103 | 0.011039 | 0.011049 | 0.011059 | 0.011068 | 0.011078 | 0.011088 | 0.011098 | 0.011107 | 0.011117 | 0.011127 | 0.011136 | 0.011146 | 0.011156 | 0.011165 | 0.011175 | 4.1418e-05 | 1.8095e-05 | 0.0058724 | 0.0059138 | 0.0059552 | 0.0059966 | 0.0060381 | 0.0060562 | 0.0060743 | 0.0060924 | 0.0061104 | 0.0061285 | 0.0061466 | 0.0061647 | 0.0061828 | 0.0062009 | 0.006219 | 0.0062371 | 0.0062552 | 0.0062733 | 0.0062914 | 0.0063095
| WPD033-63732110 | 904 | 904 | 0.02074 | 0 | 0.023653 | 0 | 0.022738 | 0 | 8.3207e-05 | -4.5731e-05 | 0.02332 | 0.023403 | 0.023486 | 0.023569 | 0.023653 | 0.023607 | 0.023561 | 0.023515 | 0.02347 | 0.023424 | 0.023378 | 0.023333 | 0.023287 | 0.023241 | 0.023195 | 0.02315 | 0.023104 | 0.023058 | 0.023012 | 0.022967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Powercor
Pole bushfire resilience program
|  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046
| Feeder | Feeder | 2026: 10% POE (MW) max summer or winter | 50% POE (MW) max summer or winter | [20 empty] | Weighted average demand (MW) | [20 empty] | Weighted average demand per customer (MW/cust)
|  | customer numbers | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47
| AC024 | 1 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125
| AC025 | 12.5 | 4.44 | 4.51 | 4.61 | 4.63 | 4.61 | 4.67 | 4.82 | 4.91 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.3 | 4.36 | 4.47 | 4.5 | 4.48 | 4.52 | 4.66 | 4.76 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 2.171 | 2.2025 | 2.256 | 2.2695 | 2.2595 | 2.2825 | 2.354 | 2.4025 | 2.3825 | 2.3825 | 2.3825 | 2.3825 | 2.3825 | 2.3825 | 2.3825 | 2.3825 | 2.3825 | 2.3825 | 2.3825 | 2.3825 | 2.3825 | 0.17368 | 0.1762 | 0.18048 | 0.18156 | 0.18076 | 0.1826 | 0.18832 | 0.1922 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906
| AC031 | 9 | 2.09 | 2.12 | 2.11 | 2.11 | 2.09 | 2.08 | 2.08 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 1.84 | 1.87 | 1.86 | 1.85 | 1.84 | 1.84 | 1.83 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 0.9575 | 0.9725 | 0.9675 | 0.964 | 0.9575 | 0.956 | 0.9525 | 0.9575 | 0.9575 | 0.9575 | 0.9575 | 0.9575 | 0.9575 | 0.9575 | 0.9575 | 0.9575 | 0.9575 | 0.9575 | 0.9575 | 0.9575 | 0.9575 | 0.10639 | 0.10806 | 0.1075 | 0.10711 | 0.10639 | 0.10622 | 0.10583 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639
| AL002 | 316.5 | 3.93 | 4.13 | 4.13 | 4.13 | 4.11 | 4.1 | 4.13 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 4.16 | 3.63 | 3.82 | 3.83 | 3.82 | 3.8 | 3.78 | 3.8 | 3.83 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 1.86 | 1.9565 | 1.96 | 1.9565 | 1.9465 | 1.938 | 1.9495 | 1.9645 | 1.961 | 1.961 | 1.961 | 1.961 | 1.961 | 1.961 | 1.961 | 1.961 | 1.961 | 1.961 | 1.961 | 1.961 | 1.961 | 0.0058768 | 0.0061817 | 0.0061927 | 0.0061817 | 0.0061501 | 0.0061232 | 0.0061596 | 0.006207 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959
| AL006 | 2033.5 | 4.89 | 4.98 | 5.07 | 5.15 | 5.21 | 5.28 | 5.38 | 5.49 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 4.25 | 4.35 | 4.41 | 4.46 | 4.51 | 4.56 | 4.64 | 4.73 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 4.79 | 2.221 | 2.2695 | 2.304 | 2.3335 | 2.36 | 2.388 | 2.431 | 2.479 | 2.512 | 2.512 | 2.512 | 2.512 | 2.512 | 2.512 | 2.512 | 2.512 | 2.512 | 2.512 | 2.512 | 2.512 | 2.512 | 0.0010922 | 0.0011161 | 0.001133 | 0.0011475 | 0.0011606 | 0.0011743 | 0.0011955 | 0.0012191 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353
| AL007 | 1018.5 | 3.47 | 3.5 | 3.53 | 3.55 | 3.59 | 3.63 | 3.7 | 3.74 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3 | 3.04 | 3.07 | 3.1 | 3.15 | 3.2 | 3.26 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 1.5705 | 1.589 | 1.604 | 1.6175 | 1.641 | 1.6645 | 1.696 | 1.716 | 1.7175 | 1.7175 | 1.7175 | 1.7175 | 1.7175 | 1.7175 | 1.7175 | 1.7175 | 1.7175 | 1.7175 | 1.7175 | 1.7175 | 1.7175 | 0.001542 | 0.0015601 | 0.0015749 | 0.0015881 | 0.0016112 | 0.0016343 | 0.0016652 | 0.0016848 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863
| AL011 | 131 | 5.55 | 5.53 | 5.53 | 5.51 | 5.48 | 5.48 | 5.51 | 5.51 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 3.59 | 3.61 | 3.59 | 3.57 | 3.54 | 3.54 | 3.56 | 3.57 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 2.089 | 2.093 | 2.086 | 2.076 | 2.061 | 2.061 | 2.0725 | 2.076 | 2.071 | 2.071 | 2.071 | 2.071 | 2.071 | 2.071 | 2.071 | 2.071 | 2.071 | 2.071 | 2.071 | 2.071 | 2.071 | 0.015947 | 0.015977 | 0.015924 | 0.015847 | 0.015733 | 0.015733 | 0.015821 | 0.015847 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809
| AL012 | 1779.5 | 4.13 | 4.2 | 4.26 | 4.3 | 4.33 | 4.38 | 4.44 | 4.51 | 4.59 | 4.59 | 4.59 | 4.59 | 4.59 | 4.59 | 4.59 | 4.59 | 4.59 | 4.59 | 4.59 | 4.59 | 4.59 | 3.82 | 3.89 | 3.94 | 3.98 | 4.01 | 4.05 | 4.16 | 4.3 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 4.41 | 1.9565 | 1.9915 | 2.018 | 2.038 | 2.053 | 2.0745 | 2.122 | 2.1815 | 2.232 | 2.232 | 2.232 | 2.232 | 2.232 | 2.232 | 2.232 | 2.232 | 2.232 | 2.232 | 2.232 | 2.232 | 2.232 | 0.0010995 | 0.0011191 | 0.001134 | 0.0011453 | 0.0011537 | 0.0011658 | 0.0011925 | 0.0012259 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543
| AL013 | 1 | 1.41 | 1.42 | 1.41 | 1.4 | 1.4 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.18 | 1.17 | 1.17 | 1.16 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 0.6245 | 0.6225 | 0.621 | 0.616 | 0.6125 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.6245 | 0.6225 | 0.621 | 0.616 | 0.6125 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611 | 0.611
| AL014 | 2090.5 | 8.4 | 8.54 | 8.62 | 8.68 | 8.67 | 8.69 | 8.78 | 8.91 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 7.41 | 7.49 | 7.54 | 7.6 | 7.6 | 7.63 | 7.73 | 7.83 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 3.8535 | 3.9025 | 3.932 | 3.962 | 3.9605 | 3.974 | 4.0225 | 4.077 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 0.0018433 | 0.0018668 | 0.0018809 | 0.0018952 | 0.0018945 | 0.001901 | 0.0019242 | 0.0019503 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565
| ART023 | 1035 | 5.31 | 5.26 | 5.22 | 5.16 | 5.1 | 5.06 | 5.06 | 5.05 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 5 | 4.95 | 4.92 | 4.87 | 4.81 | 4.78 | 4.78 | 4.78 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 2.5465 | 2.5215 | 2.505 | 2.4785 | 2.4485 | 2.432 | 2.432 | 2.4305 | 2.4005 | 2.4005 | 2.4005 | 2.4005 | 2.4005 | 2.4005 | 2.4005 | 2.4005 | 2.4005 | 2.4005 | 2.4005 | 2.4005 | 2.4005 | 0.0024604 | 0.0024362 | 0.0024203 | 0.0023947 | 0.0023657 | 0.0023498 | 0.0023498 | 0.0023483 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193
| ART031 | 1452.5 | 3.98 | 3.98 | 3.96 | 3.94 | 3.9 | 3.87 | 3.87 | 3.87 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.58 | 3.58 | 3.56 | 3.54 | 3.5 | 3.52 | 3.58 | 3.62 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 3.63 | 1.85 | 1.85 | 1.84 | 1.83 | 1.81 | 1.8125 | 1.8335 | 1.8475 | 1.8465 | 1.8465 | 1.8465 | 1.8465 | 1.8465 | 1.8465 | 1.8465 | 1.8465 | 1.8465 | 1.8465 | 1.8465 | 1.8465 | 1.8465 | 0.0012737 | 0.0012737 | 0.0012668 | 0.0012599 | 0.0012461 | 0.0012478 | 0.0012623 | 0.0012719 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713
| ART033 | 1900.5 | 3.67 | 3.69 | 3.72 | 3.73 | 3.71 | 3.73 | 3.78 | 3.81 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.45 | 3.46 | 3.49 | 3.49 | 3.47 | 3.48 | 3.53 | 3.56 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 1.758 | 1.7645 | 1.7795 | 1.781 | 1.771 | 1.7775 | 1.8025 | 1.8175 | 1.7925 | 1.7925 | 1.7925 | 1.7925 | 1.7925 | 1.7925 | 1.7925 | 1.7925 | 1.7925 | 1.7925 | 1.7925 | 1.7925 | 1.7925 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317
| ART034 | 2431.5 | 5.62 | 5.63 | 5.61 | 5.59 | 5.54 | 5.51 | 5.52 | 5.53 | 5.51 | 5.51 | 5.51 | 5.51 | 5.51 | 5.51 | 5.51 | 5.51 | 5.51 | 5.51 | 5.51 | 5.51 | 5.51 | 5.05 | 5.05 | 5.02 | 4.99 | 4.93 | 4.92 | 4.98 | 5.01 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2.6105 | 2.612 | 2.5985 | 2.585 | 2.5565 | 2.5485 | 2.571 | 2.583 | 2.5765 | 2.5765 | 2.5765 | 2.5765 | 2.5765 | 2.5765 | 2.5765 | 2.5765 | 2.5765 | 2.5765 | 2.5765 | 2.5765 | 2.5765 | 0.0010736 | 0.0010742 | 0.0010687 | 0.0010631 | 0.0010514 | 0.0010481 | 0.0010574 | 0.0010623 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596
| BAN001 | 487.5 | 6.32 | 6.29 | 6.3 | 6.28 | 6.26 | 6.3 | 6.36 | 6.42 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.06 | 6.04 | 6.05 | 6.04 | 6.03 | 6.06 | 6.13 | 6.18 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 3.069 | 3.0575 | 3.0625 | 3.056 | 3.0495 | 3.066 | 3.0995 | 3.126 | 3.1145 | 3.1145 | 3.1145 | 3.1145 | 3.1145 | 3.1145 | 3.1145 | 3.1145 | 3.1145 | 3.1145 | 3.1145 | 3.1145 | 3.1145 | 0.0062954 | 0.0062718 | 0.0062821 | 0.0062687 | 0.0062554 | 0.0062892 | 0.0063579 | 0.0064123 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887
| BAN002 | 1544 | 9.7 | 9.78 | 9.76 | 9.73 | 9.69 | 9.66 | 9.69 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 8.79 | 8.77 | 8.76 | 8.74 | 8.72 | 8.74 | 8.81 | 8.86 | 8.87 | 8.87 | 8.87 | 8.87 | 8.87 | 8.87 | 8.87 | 8.87 | 8.87 | 8.87 | 8.87 | 8.87 | 8.87 | 4.5315 | 4.5365 | 4.53 | 4.5185 | 4.5055 | 4.508 | 4.537 | 4.5575 | 4.561 | 4.561 | 4.561 | 4.561 | 4.561 | 4.561 | 4.561 | 4.561 | 4.561 | 4.561 | 4.561 | 4.561 | 4.561 | 0.0029349 | 0.0029381 | 0.0029339 | 0.0029265 | 0.0029181 | 0.0029197 | 0.0029385 | 0.0029517 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954
| BAN003 | 4155.5 | 11.12 | 11.39 | 11.7 | 11.94 | 12.16 | 12.47 | 12.88 | 13.18 | 13.34 | 13.34 | 13.34 | 13.34 | 13.34 | 13.34 | 13.34 | 13.34 | 13.34 | 13.34 | 13.34 | 13.34 | 13.34 | 9.29 | 9.53 | 9.81 | 10.04 | 10.23 | 10.51 | 10.86 | 11.15 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 4.9195 | 5.044 | 5.1885 | 5.305 | 5.4045 | 5.549 | 5.733 | 5.8795 | 5.9525 | 5.9525 | 5.9525 | 5.9525 | 5.9525 | 5.9525 | 5.9525 | 5.9525 | 5.9525 | 5.9525 | 5.9525 | 5.9525 | 5.9525 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324
| BAN004 | 1328.5 | 10.79 | 11.46 | 11.39 | 11.31 | 11.24 | 11.16 | 11.16 | 11.2 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 10.25 | 10.33 | 10.32 | 10.29 | 10.24 | 10.25 | 10.3 | 10.33 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 5.206 | 5.3345 | 5.3205 | 5.298 | 5.27 | 5.2615 | 5.279 | 5.2955 | 5.2785 | 5.2785 | 5.2785 | 5.2785 | 5.2785 | 5.2785 | 5.2785 | 5.2785 | 5.2785 | 5.2785 | 5.2785 | 5.2785 | 5.2785 | 0.0039187 | 0.0040154 | 0.0040049 | 0.003988 | 0.0039669 | 0.0039605 | 0.0039737 | 0.0039861 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733
| BAN005 | 1444.5 | 11.38 | 12.36 | 12.33 | 12.34 | 12.26 | 12.2 | 12.24 | 12.34 | 12.34 | 12.34 | 12.34 | 12.34 | 12.34 | 12.34 | 12.34 | 12.34 | 12.34 | 12.34 | 12.34 | 12.34 | 12.34 | 10.49 | 11.24 | 11.23 | 11.22 | 11.14 | 11.11 | 11.16 | 11.24 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 5.3785 | 5.788 | 5.78 | 5.778 | 5.738 | 5.7185 | 5.742 | 5.785 | 5.7815 | 5.7815 | 5.7815 | 5.7815 | 5.7815 | 5.7815 | 5.7815 | 5.7815 | 5.7815 | 5.7815 | 5.7815 | 5.7815 | 5.7815 | 0.0037234 | 0.0040069 | 0.0040014 | 0.004 | 0.0039723 | 0.0039588 | 0.0039751 | 0.0040048 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024
| BAN006 | 5479.5 | 11.45 | 11.69 | 12.09 | 12.45 | 12.79 | 13.22 | 13.71 | 14.14 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 10.84 | 11.13 | 11.52 | 11.88 | 12.22 | 12.63 | 13.11 | 13.53 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 13.77 | 5.5115 | 5.649 | 5.8455 | 6.0255 | 6.1955 | 6.4035 | 6.645 | 6.8565 | 6.975 | 6.975 | 6.975 | 6.975 | 6.975 | 6.975 | 6.975 | 6.975 | 6.975 | 6.975 | 6.975 | 6.975 | 6.975 | 0.0010058 | 0.0010309 | 0.0010668 | 0.0010996 | 0.0011307 | 0.0011686 | 0.0012127 | 0.0012513 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729
| BAN007 | 4789.5 | 10.72 | 1.07 | 1.1 | 1.13 | 1.16 | 1.19 | 1.23 | 1.26 | 1.28 | 1.28 | 1.28 | 1.28 | 1.28 | 1.28 | 1.28 | 1.28 | 1.28 | 1.28 | 1.28 | 1.28 | 1.28 | 9.36 | 1.03 | 1.06 | 1.08 | 1.11 | 1.14 | 1.18 | 1.21 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 4.884 | 0.521 | 0.536 | 0.5475 | 0.5625 | 0.5775 | 0.5975 | 0.6125 | 0.626 | 0.626 | 0.626 | 0.626 | 0.626 | 0.626 | 0.626 | 0.626 | 0.626 | 0.626 | 0.626 | 0.626 | 0.626 | 0.0010197 | 0.00010878 | 0.00011191 | 0.00011431 | 0.00011744 | 0.00012058 | 0.00012475 | 0.00012788 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307
| BAN008 | 3698.5 | 9.17 | 9.48 | 9.46 | 0.1 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 8.69 | 9 | 8.68 | 0.1 | 0.1 | 0.11 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 4.417 | 4.572 | 4.457 | 0.05 | 0.0515 | 0.055 | 0.0565 | 0.0565 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.0011943 | 0.0012362 | 0.0012051 | 1.3519e-05 | 1.3925e-05 | 1.4871e-05 | 1.5276e-05 | 1.5276e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05
| BAN009 | 3363.5 | 10.19 | 10.32 | 10.55 | 10.73 | 10.9 | 11.15 | 11.46 | 11.73 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 9.64 | 9.73 | 9.91 | 10.08 | 10.21 | 10.44 | 10.74 | 10.98 | 11.09 | 11.09 | 11.09 | 11.09 | 11.09 | 11.09 | 11.09 | 11.09 | 11.09 | 11.09 | 11.09 | 11.09 | 11.09 | 4.9025 | 4.9535 | 5.051 | 5.1375 | 5.2085 | 5.3265 | 5.478 | 5.6025 | 5.659 | 5.659 | 5.659 | 5.659 | 5.659 | 5.659 | 5.659 | 5.659 | 5.659 | 5.659 | 5.659 | 5.659 | 5.659 | 0.0014576 | 0.0014727 | 0.0015017 | 0.0015274 | 0.0015485 | 0.0015836 | 0.0016287 | 0.0016657 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825
| BAN011 | 561 | 14.94 | 15.31 | 15.66 | 15.87 | 15.83 | 15.89 | 16.3 | 16.78 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 12.69 | 13.02 | 13.3 | 13.5 | 13.46 | 13.52 | 13.86 | 14.29 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 6.6825 | 6.8535 | 7.004 | 7.1055 | 7.0855 | 7.1155 | 7.296 | 7.5185 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 0.011912 | 0.012217 | 0.012485 | 0.012666 | 0.01263 | 0.012684 | 0.013005 | 0.013402 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324
| BAN013 | 2712.5 | 12.04 | 12.47 | 13.01 | 13.56 | 14.05 | 14.67 | 15.4 | 15.98 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 11.44 | 11.82 | 12.31 | 12.81 | 13.31 | 13.9 | 14.58 | 15.19 | 15.69 | 15.69 | 15.69 | 15.69 | 15.69 | 15.69 | 15.69 | 15.69 | 15.69 | 15.69 | 15.69 | 15.69 | 15.69 | 5.81 | 6.0075 | 6.26 | 6.5175 | 6.766 | 7.0655 | 7.413 | 7.7135 | 7.965 | 7.965 | 7.965 | 7.965 | 7.965 | 7.965 | 7.965 | 7.965 | 7.965 | 7.965 | 7.965 | 7.965 | 7.965 | 0.0021419 | 0.0022147 | 0.0023078 | 0.0024028 | 0.0024944 | 0.0026048 | 0.0027329 | 0.0028437 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364
| BAN015 | 5401.5 | 10.82 | 10.96 | 11.11 | 8.34 | 8.71 | 9.15 | 9.61 | 10 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 10.28 | 9.72 | 10.14 | 9.93 | 7.82 | 8.16 | 8.57 | 9.01 | 9.39 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 5.025 | 5.193 | 5.142 | 3.988 | 4.1625 | 4.372 | 4.595 | 4.7865 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 0.0009303 | 0.0009614 | 0.00095196 | 0.00073831 | 0.00077062 | 0.0008094 | 0.00085069 | 0.00088614 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271
| BAS011 | 6024 | 14.15 | 8.54 | 8.68 | 8.81 | 8.82 | 8.9 | 9.08 | 9.31 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 12 | 7.23 | 7.37 | 7.57 | 7.78 | 8.07 | 8.42 | 8.73 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 6.3225 | 3.8115 | 3.8815 | 3.971 | 4.046 | 4.1595 | 4.309 | 4.452 | 4.533 | 4.533 | 4.533 | 4.533 | 4.533 | 4.533 | 4.533 | 4.533 | 4.533 | 4.533 | 4.533 | 4.533 | 4.533 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249
| BAS012 | 2346 | 8.16 | 7.14 | 6.98 | 6.95 | 6.95 | 7 | 7.1 | 7.15 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.17 | 7.12 | 6.61 | 6.62 | 6.61 | 6.6 | 6.64 | 6.72 | 6.76 | 6.78 | 6.78 | 6.78 | 6.78 | 6.78 | 6.78 | 6.78 | 6.78 | 6.78 | 6.78 | 6.78 | 6.78 | 6.78 | 3.716 | 3.3845 | 3.364 | 3.356 | 3.3525 | 3.374 | 3.417 | 3.4385 | 3.4485 | 3.4485 | 3.4485 | 3.4485 | 3.4485 | 3.4485 | 3.4485 | 3.4485 | 3.4485 | 3.4485 | 3.4485 | 3.4485 | 3.4485 | 0.001584 | 0.0014427 | 0.0014339 | 0.0014305 | 0.001429 | 0.0014382 | 0.0014565 | 0.0014657 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699
| BAS014 | 2707.5 | 8.82 | 8.78 | 8.88 | 8.93 | 8.99 | 9.12 | 9.31 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 9.45 | 8.32 | 8.35 | 8.44 | 8.5 | 8.53 | 8.65 | 8.85 | 8.99 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 4.235 | 4.2395 | 4.286 | 4.3145 | 4.334 | 4.3955 | 4.494 | 4.564 | 4.5605 | 4.5605 | 4.5605 | 4.5605 | 4.5605 | 4.5605 | 4.5605 | 4.5605 | 4.5605 | 4.5605 | 4.5605 | 4.5605 | 4.5605 | 0.0015642 | 0.0015658 | 0.001583 | 0.0015935 | 0.0016007 | 0.0016235 | 0.0016598 | 0.0016857 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844
| BAS022 | 6237 | 12.34 | 12.55 | 12.72 | 9.59 | 9.97 | 10.45 | 10.98 | 11.45 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.43 | 11.91 | 11.58 | 9.26 | 9.64 | 10.1 | 10.6 | 11.05 | 11.39 | 11.39 | 11.39 | 11.39 | 11.39 | 11.39 | 11.39 | 11.39 | 11.39 | 11.39 | 11.39 | 11.39 | 11.39 | 5.8515 | 6.051 | 5.961 | 4.6795 | 4.8695 | 5.1025 | 5.357 | 5.585 | 5.7565 | 5.7565 | 5.7565 | 5.7565 | 5.7565 | 5.7565 | 5.7565 | 5.7565 | 5.7565 | 5.7565 | 5.7565 | 5.7565 | 5.7565 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296
| BAS023 | 4513.5 | 8.76 | 2.12 | 2.19 | 2.26 | 2.33 | 2.43 | 2.54 | 2.63 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 8.09 | 2.02 | 2.09 | 2.16 | 2.23 | 2.33 | 2.43 | 2.52 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 4.1455 | 1.025 | 1.06 | 1.095 | 1.13 | 1.18 | 1.2315 | 1.2765 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 0.00091847 | 0.0002271 | 0.00023485 | 0.00024261 | 0.00025036 | 0.00026144 | 0.00027285 | 0.00028282 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057
| BAS024 | 5306 | 15.7 | 10.01 | 10.53 | 11.01 | 11.48 | 12.04 | 12.69 | 13.26 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.73 | 13.61 | 9.37 | 9.85 | 10.32 | 10.78 | 11.33 | 11.93 | 12.49 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 7.1185 | 4.781 | 5.027 | 5.2635 | 5.495 | 5.7715 | 6.079 | 6.3605 | 6.585 | 6.585 | 6.585 | 6.585 | 6.585 | 6.585 | 6.585 | 6.585 | 6.585 | 6.585 | 6.585 | 6.585 | 6.585 | 0.0013416 | 0.00090106 | 0.00094742 | 0.00099199 | 0.0010356 | 0.0010877 | 0.0011457 | 0.0011987 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241
| BAS032 | 4743 | 11.82 | 11.9 | 12.06 | 12.52 | 13.09 | 13.64 | 14.24 | 14.76 | 15.22 | 15.22 | 15.22 | 15.22 | 15.22 | 15.22 | 15.22 | 15.22 | 15.22 | 15.22 | 15.22 | 15.22 | 15.22 | 10.66 | 11 | 11.44 | 11.9 | 12.36 | 12.88 | 13.44 | 13.94 | 14.35 | 14.35 | 14.35 | 14.35 | 14.35 | 14.35 | 14.35 | 14.35 | 14.35 | 14.35 | 14.35 | 14.35 | 14.35 | 5.504 | 5.635 | 5.813 | 6.043 | 6.2895 | 6.554 | 6.84 | 7.093 | 7.3055 | 7.3055 | 7.3055 | 7.3055 | 7.3055 | 7.3055 | 7.3055 | 7.3055 | 7.3055 | 7.3055 | 7.3055 | 7.3055 | 7.3055 | 0.0011604 | 0.0011881 | 0.0012256 | 0.0012741 | 0.0013261 | 0.0013818 | 0.0014421 | 0.0014955 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403
| BAS033 | 6639 | 9.34 | 8.57 | 8.91 | 9.22 | 9.5 | 9.87 | 10.32 | 10.7 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 7.78 | 7.43 | 7.73 | 8 | 8.23 | 8.56 | 8.94 | 9.29 | 9.51 | 9.51 | 9.51 | 9.51 | 9.51 | 9.51 | 9.51 | 9.51 | 9.51 | 9.51 | 9.51 | 9.51 | 9.51 | 4.124 | 3.886 | 4.042 | 4.183 | 4.3055 | 4.4765 | 4.677 | 4.8565 | 4.971 | 4.971 | 4.971 | 4.971 | 4.971 | 4.971 | 4.971 | 4.971 | 4.971 | 4.971 | 4.971 | 4.971 | 4.971 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876
| BAS034 | 5437.5 | 8.92 | 8.92 | 8.99 | 9.18 | 9.35 | 9.58 | 9.85 | 10.07 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 10.21 | 8.13 | 8.24 | 8.45 | 8.65 | 8.82 | 9.05 | 9.32 | 9.55 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 4.1835 | 4.222 | 4.306 | 4.4045 | 4.4895 | 4.6045 | 4.7395 | 4.853 | 4.9265 | 4.9265 | 4.9265 | 4.9265 | 4.9265 | 4.9265 | 4.9265 | 4.9265 | 4.9265 | 4.9265 | 4.9265 | 4.9265 | 4.9265 | 0.00076938 | 0.00077646 | 0.00079191 | 0.00081002 | 0.00082566 | 0.0008468 | 0.00087163 | 0.00089251 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602
| BBD013 | 144.5 | 11.45 | 12.45 | 12.67 | 12.77 | 12.7 | 12.69 | 12.87 | 13.15 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 13.11 | 10.37 | 11.44 | 11.63 | 11.72 | 11.65 | 11.63 | 11.82 | 12.07 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 5.347 | 5.8715 | 5.971 | 6.0175 | 5.9825 | 5.974 | 6.0675 | 6.197 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 6.17 | 0.037003 | 0.040633 | 0.041322 | 0.041644 | 0.041401 | 0.041343 | 0.04199 | 0.042886 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699
| BBD014 | 124 | 11.76 | 11.7 | 11.52 | 11.33 | 11.07 | 10.86 | 10.76 | 10.69 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.73 | 10.67 | 10.51 | 10.33 | 10.11 | 9.92 | 9.82 | 9.76 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 5.5195 | 5.4895 | 5.4065 | 5.315 | 5.199 | 5.101 | 5.051 | 5.0195 | 4.928 | 4.928 | 4.928 | 4.928 | 4.928 | 4.928 | 4.928 | 4.928 | 4.928 | 4.928 | 4.928 | 4.928 | 4.928 | 0.044512 | 0.04427 | 0.043601 | 0.042863 | 0.041927 | 0.041137 | 0.040734 | 0.04048 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742
| BBD021 | 204 | 8.81 | 8.91 | 8.96 | 8.97 | 8.86 | 8.79 | 8.89 | 9.02 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8 | 8.1 | 8.15 | 8.15 | 8.06 | 7.98 | 8.06 | 8.19 | 8.12 | 8.12 | 8.12 | 8.12 | 8.12 | 8.12 | 8.12 | 8.12 | 8.12 | 8.12 | 8.12 | 8.12 | 8.12 | 4.1215 | 4.1715 | 4.1965 | 4.198 | 4.15 | 4.1115 | 4.1545 | 4.2195 | 4.1815 | 4.1815 | 4.1815 | 4.1815 | 4.1815 | 4.1815 | 4.1815 | 4.1815 | 4.1815 | 4.1815 | 4.1815 | 4.1815 | 4.1815 | 0.020203 | 0.020449 | 0.020571 | 0.020578 | 0.020343 | 0.020154 | 0.020365 | 0.020684 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498
| BBD022 | 5 | 7.26 | 7.31 | 7.32 | 7.29 | 7.19 | 7.12 | 7.16 | 7.23 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 7.14 | 6.55 | 6.59 | 6.6 | 6.57 | 6.48 | 6.42 | 6.46 | 6.52 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 3.3815 | 3.403 | 3.408 | 3.393 | 3.3465 | 3.315 | 3.335 | 3.3665 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 0.6763 | 0.6806 | 0.6816 | 0.6786 | 0.6693 | 0.663 | 0.667 | 0.6733 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665
| BET001 | 5586.5 | 15.07 | 15.22 | 15.27 | 15.33 | 15.34 | 15.37 | 15.49 | 15.63 | 15.71 | 15.71 | 15.71 | 15.71 | 15.71 | 15.71 | 15.71 | 15.71 | 15.71 | 15.71 | 15.71 | 15.71 | 15.71 | 14.01 | 14.17 | 14.23 | 14.28 | 14.27 | 14.31 | 14.42 | 14.55 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 7.164 | 7.2425 | 7.271 | 7.2975 | 7.2955 | 7.314 | 7.3705 | 7.437 | 7.4805 | 7.4805 | 7.4805 | 7.4805 | 7.4805 | 7.4805 | 7.4805 | 7.4805 | 7.4805 | 7.4805 | 7.4805 | 7.4805 | 7.4805 | 0.0012824 | 0.0012964 | 0.0013015 | 0.0013063 | 0.0013059 | 0.0013092 | 0.0013193 | 0.0013312 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339
| BET002 | 3155.5 | 6.58 | 6.65 | 6.69 | 6.72 | 6.83 | 7.03 | 7.25 | 7.45 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 7.57 | 6.22 | 6.29 | 6.34 | 6.38 | 6.48 | 6.67 | 6.88 | 7.07 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 3.164 | 3.199 | 3.2225 | 3.241 | 3.2925 | 3.389 | 3.4955 | 3.592 | 3.6555 | 3.6555 | 3.6555 | 3.6555 | 3.6555 | 3.6555 | 3.6555 | 3.6555 | 3.6555 | 3.6555 | 3.6555 | 3.6555 | 3.6555 | 0.0010027 | 0.0010138 | 0.0010212 | 0.0010271 | 0.0010434 | 0.001074 | 0.0011077 | 0.0011383 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585
| BET003 | 331 | 2.85 | 2.86 | 2.89 | 2.91 | 2.93 | 2.96 | 3.02 | 3.06 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 2.69 | 2.7 | 2.72 | 2.73 | 2.74 | 2.77 | 2.82 | 2.86 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 2.87 | 1.369 | 1.374 | 1.3855 | 1.392 | 1.3985 | 1.4135 | 1.44 | 1.46 | 1.468 | 1.468 | 1.468 | 1.468 | 1.468 | 1.468 | 1.468 | 1.468 | 1.468 | 1.468 | 1.468 | 1.468 | 1.468 | 0.004136 | 0.0041511 | 0.0041858 | 0.0042054 | 0.0042251 | 0.0042704 | 0.0043505 | 0.0044109 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435
| BET004 | 3418.5 | 10.3 | 10.41 | 10.45 | 10.53 | 10.56 | 10.61 | 10.76 | 10.91 | 10.99 | 10.99 | 10.99 | 10.99 | 10.99 | 10.99 | 10.99 | 10.99 | 10.99 | 10.99 | 10.99 | 10.99 | 10.99 | 9.58 | 9.73 | 9.82 | 9.91 | 9.95 | 10.01 | 10.16 | 10.33 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 4.898 | 4.967 | 5.0045 | 5.048 | 5.0665 | 5.095 | 5.17 | 5.252 | 5.32 | 5.32 | 5.32 | 5.32 | 5.32 | 5.32 | 5.32 | 5.32 | 5.32 | 5.32 | 5.32 | 5.32 | 5.32 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562
| BET005 | 3686.5 | 14.97 | 15.2 | 15.41 | 15.59 | 15.65 | 15.77 | 16.07 | 16.39 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 16.49 | 12.62 | 12.85 | 13.02 | 13.16 | 13.21 | 13.31 | 13.53 | 13.78 | 13.88 | 13.88 | 13.88 | 13.88 | 13.88 | 13.88 | 13.88 | 13.88 | 13.88 | 13.88 | 13.88 | 13.88 | 13.88 | 6.6625 | 6.7775 | 6.8685 | 6.9445 | 6.971 | 7.024 | 7.146 | 7.2815 | 7.3315 | 7.3315 | 7.3315 | 7.3315 | 7.3315 | 7.3315 | 7.3315 | 7.3315 | 7.3315 | 7.3315 | 7.3315 | 7.3315 | 7.3315 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887
| BET006 | 5543.5 | 17.36 | 17.61 | 17.81 | 17.96 | 18.02 | 18.14 | 18.42 | 18.74 | 18.86 | 18.86 | 18.86 | 18.86 | 18.86 | 18.86 | 18.86 | 18.86 | 18.86 | 18.86 | 18.86 | 18.86 | 18.86 | 15.71 | 15.9 | 16.07 | 16.2 | 16.24 | 16.37 | 16.6 | 16.87 | 16.98 | 16.98 | 16.98 | 16.98 | 16.98 | 16.98 | 16.98 | 16.98 | 16.98 | 16.98 | 16.98 | 16.98 | 16.98 | 8.1025 | 8.2065 | 8.296 | 8.364 | 8.387 | 8.4505 | 8.573 | 8.7155 | 8.772 | 8.772 | 8.772 | 8.772 | 8.772 | 8.772 | 8.772 | 8.772 | 8.772 | 8.772 | 8.772 | 8.772 | 8.772 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824
| BET007 | 5439 | 13.66 | 13.95 | 14.18 | 14.37 | 14.61 | 15.25 | 15.96 | 16.6 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 17.05 | 12.4 | 12.63 | 12.85 | 13.42 | 13.96 | 14.59 | 15.28 | 15.9 | 16.36 | 16.36 | 16.36 | 16.36 | 16.36 | 16.36 | 16.36 | 16.36 | 16.36 | 16.36 | 16.36 | 16.36 | 16.36 | 6.389 | 6.513 | 6.6245 | 6.8525 | 7.0775 | 7.394 | 7.742 | 8.055 | 8.2835 | 8.2835 | 8.2835 | 8.2835 | 8.2835 | 8.2835 | 8.2835 | 8.2835 | 8.2835 | 8.2835 | 8.2835 | 8.2835 | 8.2835 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523
| BET008 | 2928 | 11.36 | 11.6 | 11.53 | 11.44 | 11.28 | 11.16 | 11.17 | 11.22 | 11.19 | 11.19 | 11.19 | 11.19 | 11.19 | 11.19 | 11.19 | 11.19 | 11.19 | 11.19 | 11.19 | 11.19 | 11.19 | 10.27 | 10.5 | 10.42 | 10.35 | 10.25 | 10.19 | 10.21 | 10.25 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 5.2985 | 5.415 | 5.3765 | 5.3385 | 5.2795 | 5.2405 | 5.249 | 5.2705 | 5.2625 | 5.2625 | 5.2625 | 5.2625 | 5.2625 | 5.2625 | 5.2625 | 5.2625 | 5.2625 | 5.2625 | 5.2625 | 5.2625 | 5.2625 | 0.0018096 | 0.0018494 | 0.0018362 | 0.0018233 | 0.0018031 | 0.0017898 | 0.0017927 | 0.0018 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973
| BGO011 | 445 | 4.19 | 4.17 | 4.11 | 4.03 | 3.96 | 3.9 | 3.85 | 3.82 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.81 | 3.79 | 3.73 | 3.66 | 3.59 | 3.52 | 3.48 | 3.45 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 1.962 | 1.952 | 1.922 | 1.8855 | 1.8505 | 1.817 | 1.7955 | 1.7805 | 1.7605 | 1.7605 | 1.7605 | 1.7605 | 1.7605 | 1.7605 | 1.7605 | 1.7605 | 1.7605 | 1.7605 | 1.7605 | 1.7605 | 1.7605 | 0.004409 | 0.0043865 | 0.0043191 | 0.0042371 | 0.0041584 | 0.0040831 | 0.0040348 | 0.0040011 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562
| BGO012 | 2579 | 7.06 | 7.08 | 7.05 | 7.02 | 6.95 | 6.92 | 6.93 | 6.95 | 6.94 | 6.94 | 6.94 | 6.94 | 6.94 | 6.94 | 6.94 | 6.94 | 6.94 | 6.94 | 6.94 | 6.94 | 6.94 | 6.62 | 6.62 | 6.59 | 6.56 | 6.48 | 6.44 | 6.45 | 6.45 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 3.376 | 3.379 | 3.364 | 3.349 | 3.3105 | 3.292 | 3.297 | 3.3 | 3.288 | 3.288 | 3.288 | 3.288 | 3.288 | 3.288 | 3.288 | 3.288 | 3.288 | 3.288 | 3.288 | 3.288 | 3.288 | 0.001309 | 0.0013102 | 0.0013044 | 0.0012986 | 0.0012836 | 0.0012765 | 0.0012784 | 0.0012796 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749
| BGO013 | 2704.5 | 13.15 | 13.45 | 13.71 | 13.95 | 14.13 | 14.34 | 14.64 | 14.96 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 10.54 | 10.82 | 11.03 | 11.23 | 11.39 | 11.57 | 11.82 | 12.1 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 12.29 | 5.6615 | 5.8045 | 5.917 | 6.023 | 6.106 | 6.2005 | 6.333 | 6.479 | 6.5815 | 6.5815 | 6.5815 | 6.5815 | 6.5815 | 6.5815 | 6.5815 | 6.5815 | 6.5815 | 6.5815 | 6.5815 | 6.5815 | 6.5815 | 0.0020934 | 0.0021462 | 0.0021878 | 0.002227 | 0.0022577 | 0.0022927 | 0.0023417 | 0.0023956 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335
| BGO014 | 526 | 3.43 | 3.41 | 3.35 | 3.28 | 3.21 | 3.14 | 3.09 | 3.05 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2.98 | 2.97 | 2.92 | 2.86 | 2.8 | 2.73 | 2.69 | 2.67 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 1.5575 | 1.551 | 1.5245 | 1.493 | 1.4615 | 1.4265 | 1.405 | 1.392 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 0.002961 | 0.0029487 | 0.0028983 | 0.0028384 | 0.0027785 | 0.002712 | 0.0026711 | 0.0026464 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055
| BGO022 | 4585.5 | 11.71 | 11.82 | 11.84 | 11.86 | 11.84 | 11.79 | 11.86 | 11.97 | 12.07 | 12.07 | 12.07 | 12.07 | 12.07 | 12.07 | 12.07 | 12.07 | 12.07 | 12.07 | 12.07 | 12.07 | 12.07 | 10.66 | 10.79 | 10.84 | 10.88 | 10.87 | 10.91 | 11.23 | 11.49 | 11.61 | 11.61 | 11.61 | 11.61 | 11.61 | 11.61 | 11.61 | 11.61 | 11.61 | 11.61 | 11.61 | 11.61 | 11.61 | 5.4875 | 5.5495 | 5.57 | 5.587 | 5.5805 | 5.587 | 5.7095 | 5.817 | 5.874 | 5.874 | 5.874 | 5.874 | 5.874 | 5.874 | 5.874 | 5.874 | 5.874 | 5.874 | 5.874 | 5.874 | 5.874 | 0.0011967 | 0.0012102 | 0.0012147 | 0.0012184 | 0.001217 | 0.0012184 | 0.0012451 | 0.0012686 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281
| BGO023 | 2974.5 | 12.61 | 12.78 | 12.87 | 12.93 | 12.97 | 13 | 13.17 | 13.34 | 13.44 | 13.44 | 13.44 | 13.44 | 13.44 | 13.44 | 13.44 | 13.44 | 13.44 | 13.44 | 13.44 | 13.44 | 13.44 | 11.6 | 11.77 | 11.86 | 11.94 | 11.97 | 12.02 | 12.18 | 12.37 | 12.46 | 12.46 | 12.46 | 12.46 | 12.46 | 12.46 | 12.46 | 12.46 | 12.46 | 12.46 | 12.46 | 12.46 | 12.46 | 5.9515 | 6.0365 | 6.0815 | 6.1185 | 6.135 | 6.157 | 6.2385 | 6.3305 | 6.377 | 6.377 | 6.377 | 6.377 | 6.377 | 6.377 | 6.377 | 6.377 | 6.377 | 6.377 | 6.377 | 6.377 | 6.377 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439
| BGO024 | 469 | 7.64 | 7.61 | 7.52 | 7.39 | 7.21 | 7.07 | 7 | 6.95 | 6.79 | 6.79 | 6.79 | 6.79 | 6.79 | 6.79 | 6.79 | 6.79 | 6.79 | 6.79 | 6.79 | 6.79 | 6.79 | 6.47 | 6.43 | 6.34 | 6.23 | 6.09 | 5.97 | 5.91 | 5.88 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 3.4105 | 3.392 | 3.347 | 3.289 | 3.213 | 3.15 | 3.1185 | 3.1005 | 3.038 | 3.038 | 3.038 | 3.038 | 3.038 | 3.038 | 3.038 | 3.038 | 3.038 | 3.038 | 3.038 | 3.038 | 3.038 | 0.0072719 | 0.0072324 | 0.0071365 | 0.0070128 | 0.0068507 | 0.0067164 | 0.0066493 | 0.0066109 | 0.0064776 | 0.0064776 | 0.0064776 | 0.0064776 | 0.0064776 | 0.0064776 | 0.0064776 | 0.0064776 | 0.0064776 | 0.0064776 | 0.0064776 | 0.0064776 | 0.0064776
| BLT016 | 671 | 19.89 | 20.18 | 20.55 | 20.85 | 21.06 | 21.53 | 22.14 | 22.76 | 22.96 | 22.96 | 22.96 | 22.96 | 22.96 | 22.96 | 22.96 | 22.96 | 22.96 | 22.96 | 22.96 | 22.96 | 22.96 | 12.54 | 12.82 | 13.18 | 13.57 | 13.98 | 14.51 | 15.1 | 15.63 | 15.99 | 15.99 | 15.99 | 15.99 | 15.99 | 15.99 | 15.99 | 15.99 | 15.99 | 15.99 | 15.99 | 15.99 | 15.99 | 7.3725 | 7.514 | 7.6955 | 7.877 | 8.052 | 8.308 | 8.606 | 8.8845 | 9.0405 | 9.0405 | 9.0405 | 9.0405 | 9.0405 | 9.0405 | 9.0405 | 9.0405 | 9.0405 | 9.0405 | 9.0405 | 9.0405 | 9.0405 | 0.010987 | 0.011198 | 0.011469 | 0.011739 | 0.012 | 0.012382 | 0.012826 | 0.013241 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473
| BLT017 | 2067 | 8.04 | 8.09 | 8.05 | 8.11 | 8.15 | 8.28 | 8.42 | 8.58 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 7.19 | 7.25 | 7.29 | 7.31 | 7.3 | 7.43 | 7.63 | 7.81 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 7.88 | 3.7225 | 3.751 | 3.759 | 3.775 | 3.7775 | 3.8425 | 3.9335 | 4.0205 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 0.0018009 | 0.0018147 | 0.0018186 | 0.0018263 | 0.0018275 | 0.001859 | 0.001903 | 0.0019451 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606
| BLT020 | 57.5 | 8.44 | 8.75 | 8.87 | 9 | 9.1 | 9.2 | 9.32 | 9.46 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 9.58 | 7.83 | 7.97 | 8.08 | 8.18 | 8.29 | 8.39 | 8.51 | 8.63 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 4.0065 | 4.102 | 4.1585 | 4.213 | 4.2665 | 4.3165 | 4.3765 | 4.4395 | 4.4925 | 4.4925 | 4.4925 | 4.4925 | 4.4925 | 4.4925 | 4.4925 | 4.4925 | 4.4925 | 4.4925 | 4.4925 | 4.4925 | 4.4925 | 0.069678 | 0.071339 | 0.072322 | 0.07327 | 0.0742 | 0.07507 | 0.076113 | 0.077209 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813
| BLT021 | 1141.5 | 8.61 | 8.77 | 8.82 | 8.82 | 8.79 | 8.89 | 9.06 | 9.18 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 7.56 | 7.85 | 7.89 | 7.93 | 7.9 | 7.87 | 8.02 | 8.15 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 3.9375 | 4.063 | 4.0845 | 4.0985 | 4.0835 | 4.088 | 4.166 | 4.2295 | 4.2045 | 4.2045 | 4.2045 | 4.2045 | 4.2045 | 4.2045 | 4.2045 | 4.2045 | 4.2045 | 4.2045 | 4.2045 | 4.2045 | 4.2045 | 0.0034494 | 0.0035594 | 0.0035782 | 0.0035905 | 0.0035773 | 0.0035813 | 0.0036496 | 0.0037052 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833
| BLT022 | 1635.5 | 7.29 | 7.32 | 7.41 | 7.41 | 7.38 | 7.44 | 7.6 | 7.74 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 6.91 | 6.94 | 7.02 | 7 | 6.96 | 7.02 | 7.18 | 7.3 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 7.22 | 3.512 | 3.527 | 3.5685 | 3.5615 | 3.543 | 3.573 | 3.653 | 3.716 | 3.6745 | 3.6745 | 3.6745 | 3.6745 | 3.6745 | 3.6745 | 3.6745 | 3.6745 | 3.6745 | 3.6745 | 3.6745 | 3.6745 | 3.6745 | 0.0021474 | 0.0021565 | 0.0021819 | 0.0021776 | 0.0021663 | 0.0021847 | 0.0022336 | 0.0022721 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467
| BLT030 | 2408 | 7.45 | 7.55 | 7.7 | 7.83 | 7.94 | 8.11 | 8.32 | 8.5 | 8.59 | 8.59 | 8.59 | 8.59 | 8.59 | 8.59 | 8.59 | 8.59 | 8.59 | 8.59 | 8.59 | 8.59 | 8.59 | 6.51 | 6.58 | 6.63 | 6.67 | 6.68 | 6.7 | 6.78 | 6.87 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 3.396 | 3.4355 | 3.4755 | 3.509 | 3.529 | 3.5615 | 3.621 | 3.6795 | 3.721 | 3.721 | 3.721 | 3.721 | 3.721 | 3.721 | 3.721 | 3.721 | 3.721 | 3.721 | 3.721 | 3.721 | 3.721 | 0.0014103 | 0.0014267 | 0.0014433 | 0.0014572 | 0.0014655 | 0.001479 | 0.0015037 | 0.001528 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453
| BLT031 | 367.5 | 2.53 | 2.57 | 2.58 | 2.59 | 2.58 | 2.58 | 2.6 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.35 | 2.39 | 2.4 | 2.41 | 2.4 | 2.39 | 2.42 | 2.46 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 1.202 | 1.222 | 1.227 | 1.232 | 1.227 | 1.2235 | 1.237 | 1.257 | 1.2535 | 1.2535 | 1.2535 | 1.2535 | 1.2535 | 1.2535 | 1.2535 | 1.2535 | 1.2535 | 1.2535 | 1.2535 | 1.2535 | 1.2535 | 0.0032707 | 0.0033252 | 0.0033388 | 0.0033524 | 0.0033388 | 0.0033293 | 0.003366 | 0.0034204 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109
| BMH003 | 3675.5 | 9.78 | 10.09 | 10.36 | 10.62 | 10.77 | 11.02 | 11.36 | 11.83 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 8.36 | 8.64 | 9.03 | 9.42 | 9.78 | 10.23 | 10.75 | 11.22 | 11.59 | 11.59 | 11.59 | 11.59 | 11.59 | 11.59 | 11.59 | 11.59 | 11.59 | 11.59 | 11.59 | 11.59 | 11.59 | 4.393 | 4.5375 | 4.7145 | 4.89 | 5.0385 | 5.2335 | 5.4665 | 5.7015 | 5.882 | 5.882 | 5.882 | 5.882 | 5.882 | 5.882 | 5.882 | 5.882 | 5.882 | 5.882 | 5.882 | 5.882 | 5.882 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003
| BMH004 | 3726.5 | 9.72 | 10.04 | 10.35 | 10.63 | 10.89 | 11.16 | 11.56 | 12.01 | 12.31 | 12.31 | 12.31 | 12.31 | 12.31 | 12.31 | 12.31 | 12.31 | 12.31 | 12.31 | 12.31 | 12.31 | 12.31 | 8.84 | 9.15 | 9.43 | 9.7 | 9.92 | 10.2 | 10.57 | 10.97 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 11.29 | 4.552 | 4.7085 | 4.853 | 4.9895 | 5.1055 | 5.244 | 5.4335 | 5.641 | 5.798 | 5.798 | 5.798 | 5.798 | 5.798 | 5.798 | 5.798 | 5.798 | 5.798 | 5.798 | 5.798 | 5.798 | 5.798 | 0.0012215 | 0.0012635 | 0.0013023 | 0.0013389 | 0.0013701 | 0.0014072 | 0.0014581 | 0.0015138 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559
| BMH005 | 4107.5 | 11.8 | 12.2 | 12.58 | 12.91 | 13.17 | 13.52 | 13.99 | 14.46 | 14.82 | 14.82 | 14.82 | 14.82 | 14.82 | 14.82 | 14.82 | 14.82 | 14.82 | 14.82 | 14.82 | 14.82 | 14.82 | 11.04 | 11.42 | 11.74 | 12.06 | 12.33 | 12.64 | 13.07 | 13.52 | 13.85 | 13.85 | 13.85 | 13.85 | 13.85 | 13.85 | 13.85 | 13.85 | 13.85 | 13.85 | 13.85 | 13.85 | 13.85 | 5.634 | 5.827 | 5.996 | 6.1575 | 6.291 | 6.452 | 6.673 | 6.901 | 7.0705 | 7.0705 | 7.0705 | 7.0705 | 7.0705 | 7.0705 | 7.0705 | 7.0705 | 7.0705 | 7.0705 | 7.0705 | 7.0705 | 7.0705 | 0.0013716 | 0.0014186 | 0.0014598 | 0.0014991 | 0.0015316 | 0.0015708 | 0.0016246 | 0.0016801 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214
| BMH006 | 929 | 6.13 | 6.26 | 6.36 | 6.42 | 6.45 | 6.5 | 6.65 | 6.88 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 4.85 | 4.97 | 5.07 | 5.15 | 5.19 | 5.37 | 5.6 | 5.78 | 5.87 | 5.87 | 5.87 | 5.87 | 5.87 | 5.87 | 5.87 | 5.87 | 5.87 | 5.87 | 5.87 | 5.87 | 5.87 | 2.617 | 2.6785 | 2.7285 | 2.7655 | 2.784 | 2.8545 | 2.9575 | 3.055 | 3.094 | 3.094 | 3.094 | 3.094 | 3.094 | 3.094 | 3.094 | 3.094 | 3.094 | 3.094 | 3.094 | 3.094 | 3.094 | 0.002817 | 0.0028832 | 0.002937 | 0.0029769 | 0.0029968 | 0.0030727 | 0.0031835 | 0.0032885 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305
| CDN001 | 1682 | 9.14 | 9.15 | 9.2 | 9.18 | 9.13 | 9.18 | 9.31 | 9.35 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 7.72 | 7.74 | 7.8 | 7.8 | 7.76 | 7.81 | 7.92 | 7.98 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 7.86 | 4.073 | 4.0815 | 4.11 | 4.107 | 4.0855 | 4.1105 | 4.1685 | 4.1955 | 4.1325 | 4.1325 | 4.1325 | 4.1325 | 4.1325 | 4.1325 | 4.1325 | 4.1325 | 4.1325 | 4.1325 | 4.1325 | 4.1325 | 4.1325 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569
| CDN002 | 510 | 2.03 | 2.05 | 2.06 | 2.07 | 2.05 | 2.04 | 2.06 | 2.09 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 2.07 | 1.85 | 1.88 | 1.89 | 1.89 | 1.88 | 1.86 | 1.88 | 1.91 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 0.952 | 0.9655 | 0.9705 | 0.972 | 0.9655 | 0.957 | 0.967 | 0.982 | 0.9755 | 0.9755 | 0.9755 | 0.9755 | 0.9755 | 0.9755 | 0.9755 | 0.9755 | 0.9755 | 0.9755 | 0.9755 | 0.9755 | 0.9755 | 0.0018667 | 0.0018931 | 0.0019029 | 0.0019059 | 0.0018931 | 0.0018765 | 0.0018961 | 0.0019255 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127
| CDN003 | 1721.5 | 3.54 | 3.54 | 3.54 | 3.53 | 3.51 | 3.51 | 3.53 | 3.54 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.42 | 3.41 | 3.41 | 3.4 | 3.38 | 3.37 | 3.39 | 3.4 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 1.728 | 1.7245 | 1.7245 | 1.7195 | 1.7095 | 1.706 | 1.716 | 1.721 | 1.711 | 1.711 | 1.711 | 1.711 | 1.711 | 1.711 | 1.711 | 1.711 | 1.711 | 1.711 | 1.711 | 1.711 | 1.711 | 0.0010038 | 0.0010017 | 0.0010017 | 0.00099884 | 0.00099303 | 0.000991 | 0.00099681 | 0.00099971 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939
| CDN004 | 787 | 1.55 | 1.55 | 1.57 | 1.57 | 1.55 | 1.54 | 1.56 | 1.58 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 1.5 | 1.51 | 1.52 | 1.52 | 1.5 | 1.49 | 1.52 | 1.53 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 1.51 | 0.7575 | 0.761 | 0.7675 | 0.7675 | 0.7575 | 0.7525 | 0.766 | 0.7725 | 0.7625 | 0.7625 | 0.7625 | 0.7625 | 0.7625 | 0.7625 | 0.7625 | 0.7625 | 0.7625 | 0.7625 | 0.7625 | 0.7625 | 0.7625 | 0.00096252 | 0.00096696 | 0.00097522 | 0.00097522 | 0.00096252 | 0.00095616 | 0.00097332 | 0.00098158 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887
| CDN006 | 987 | 2.69 | 2.69 | 2.7 | 2.67 | 2.64 | 2.63 | 2.66 | 2.67 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.51 | 2.5 | 2.51 | 2.48 | 2.45 | 2.44 | 2.47 | 2.48 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 1.282 | 1.2785 | 1.2835 | 1.2685 | 1.2535 | 1.2485 | 1.2635 | 1.2685 | 1.2385 | 1.2385 | 1.2385 | 1.2385 | 1.2385 | 1.2385 | 1.2385 | 1.2385 | 1.2385 | 1.2385 | 1.2385 | 1.2385 | 1.2385 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548
| CHA003 | 1208 | 3.76 | 3.76 | 3.73 | 3.7 | 3.64 | 3.59 | 3.57 | 3.56 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.57 | 3.57 | 3.55 | 3.52 | 3.46 | 3.42 | 3.4 | 3.39 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 1.8135 | 1.8135 | 1.802 | 1.787 | 1.757 | 1.7355 | 1.7255 | 1.7205 | 1.6955 | 1.6955 | 1.6955 | 1.6955 | 1.6955 | 1.6955 | 1.6955 | 1.6955 | 1.6955 | 1.6955 | 1.6955 | 1.6955 | 1.6955 | 0.0015012 | 0.0015012 | 0.0014917 | 0.0014793 | 0.0014545 | 0.0014367 | 0.0014284 | 0.0014243 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036
| CHA005 | 1341 | 5.27 | 5.33 | 5.34 | 5.35 | 5.29 | 5.26 | 5.32 | 5.41 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 4.89 | 4.94 | 4.98 | 4.99 | 4.93 | 4.9 | 4.96 | 5.04 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2.502 | 2.5285 | 2.544 | 2.549 | 2.519 | 2.504 | 2.534 | 2.5755 | 2.554 | 2.554 | 2.554 | 2.554 | 2.554 | 2.554 | 2.554 | 2.554 | 2.554 | 2.554 | 2.554 | 2.554 | 2.554 | 0.0018658 | 0.0018855 | 0.0018971 | 0.0019008 | 0.0018784 | 0.0018673 | 0.0018896 | 0.0019206 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045
| CHA006 | 1854 | 8.15 | 8.23 | 8.25 | 8.24 | 8.13 | 8.07 | 8.13 | 8.23 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 7.44 | 7.5 | 7.54 | 7.53 | 7.44 | 7.38 | 7.44 | 7.53 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 3.8265 | 3.8595 | 3.8765 | 3.8715 | 3.8235 | 3.7935 | 3.8235 | 3.87 | 3.825 | 3.825 | 3.825 | 3.825 | 3.825 | 3.825 | 3.825 | 3.825 | 3.825 | 3.825 | 3.825 | 3.825 | 3.825 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631
| CHA007 | 1 | 0.2 | 0.2 | 0.19 | 0.19 | 0.18 | 0.18 | 0.18 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.16 | 0.16 | 0.16 | 0.15 | 0.15 | 0.15 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.086 | 0.086 | 0.0845 | 0.081 | 0.0795 | 0.0795 | 0.076 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.086 | 0.086 | 0.0845 | 0.081 | 0.0795 | 0.0795 | 0.076 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745
| CHA008 | 1 | 0.14 | 0.14 | 0.14 | 0.13 | 0.13 | 0.13 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.14 | 0.14 | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.07 | 0.07 | 0.0665 | 0.065 | 0.065 | 0.065 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.07 | 0.07 | 0.0665 | 0.065 | 0.065 | 0.065 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| CHM011 | 1539.5 | 2.63 | 2.57 | 2.56 | 2.53 | 2.49 | 2.46 | 2.46 | 2.47 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.32 | 2.28 | 2.27 | 2.24 | 2.2 | 2.17 | 2.17 | 2.18 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 1.2065 | 1.1835 | 1.1785 | 1.1635 | 1.1435 | 1.1285 | 1.1285 | 1.1335 | 1.117 | 1.117 | 1.117 | 1.117 | 1.117 | 1.117 | 1.117 | 1.117 | 1.117 | 1.117 | 1.117 | 1.117 | 1.117 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556
| CLC001 | 1690 | 9.99 | 9.88 | 9.66 | 9.47 | 9.29 | 9.28 | 9.31 | 9.29 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26 | 9.26 | 8.34 | 8.28 | 8.23 | 8.16 | 8.11 | 8.11 | 8.11 | 8.13 | 8.11 | 8.11 | 8.11 | 8.11 | 8.11 | 8.11 | 8.11 | 8.11 | 8.11 | 8.11 | 8.11 | 8.11 | 8.11 | 4.4175 | 4.38 | 4.3295 | 4.2765 | 4.232 | 4.2305 | 4.235 | 4.239 | 4.2275 | 4.2275 | 4.2275 | 4.2275 | 4.2275 | 4.2275 | 4.2275 | 4.2275 | 4.2275 | 4.2275 | 4.2275 | 4.2275 | 4.2275 | 0.0026139 | 0.0025917 | 0.0025618 | 0.0025305 | 0.0025041 | 0.0025033 | 0.0025059 | 0.0025083 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015
| CLC002 | 2992 | 6.08 | 6.03 | 5.97 | 5.95 | 6.02 | 6.15 | 6.3 | 6.42 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 6.46 | 5.43 | 5.48 | 5.58 | 5.65 | 5.72 | 5.85 | 5.99 | 6.12 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 2.8125 | 2.8225 | 2.8485 | 2.87 | 2.905 | 2.97 | 3.0415 | 3.105 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125 | 0.00094001 | 0.00094335 | 0.00095204 | 0.00095922 | 0.00097092 | 0.00099265 | 0.0010165 | 0.0010378 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445
| CLC003 | 2794.5 | 7 | 7.09 | 7.12 | 7.14 | 7.11 | 7.1 | 7.15 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 6.56 | 6.6 | 6.66 | 6.67 | 6.65 | 6.68 | 6.78 | 6.85 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 3.346 | 3.3735 | 3.399 | 3.4055 | 3.394 | 3.403 | 3.4455 | 3.4835 | 3.466 | 3.466 | 3.466 | 3.466 | 3.466 | 3.466 | 3.466 | 3.466 | 3.466 | 3.466 | 3.466 | 3.466 | 3.466 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403
| CLC004 | 2438.5 | 10.52 | 10.83 | 10.79 | 10.75 | 10.68 | 10.68 | 10.75 | 10.79 | 10.74 | 10.74 | 10.74 | 10.74 | 10.74 | 10.74 | 10.74 | 10.74 | 10.74 | 10.74 | 10.74 | 10.74 | 10.74 | 10.21 | 10.42 | 10.42 | 10.4 | 10.35 | 10.37 | 10.43 | 10.48 | 10.43 | 10.43 | 10.43 | 10.43 | 10.43 | 10.43 | 10.43 | 10.43 | 10.43 | 10.43 | 10.43 | 10.43 | 10.43 | 5.1515 | 5.2715 | 5.2655 | 5.2525 | 5.2245 | 5.2315 | 5.263 | 5.2865 | 5.2615 | 5.2615 | 5.2615 | 5.2615 | 5.2615 | 5.2615 | 5.2615 | 5.2615 | 5.2615 | 5.2615 | 5.2615 | 5.2615 | 5.2615 | 0.0021126 | 0.0021618 | 0.0021593 | 0.002154 | 0.0021425 | 0.0021454 | 0.0021583 | 0.0021679 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577
| CLC006 | 1564.5 | 12.22 | 12.22 | 12.09 | 12.04 | 11.85 | 11.73 | 11.67 | 11.64 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.01 | 10.96 | 10.85 | 10.74 | 10.62 | 10.51 | 10.49 | 10.45 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 10.38 | 5.6865 | 5.669 | 5.611 | 5.565 | 5.4945 | 5.438 | 5.422 | 5.4035 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324
| CLC013 | 3089 | 8.24 | 8.3 | 8.4 | 8.44 | 8.43 | 8.51 | 8.62 | 8.72 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 7.19 | 7.25 | 7.33 | 7.36 | 7.35 | 7.39 | 7.49 | 7.57 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 7.53 | 3.7525 | 3.7825 | 3.8255 | 3.842 | 3.837 | 3.863 | 3.9145 | 3.9575 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747
| CLC014 | 1496.5 | 6.37 | 6.37 | 6.4 | 6.39 | 6.35 | 6.35 | 6.38 | 6.39 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 5.3 | 5.3 | 5.33 | 5.32 | 5.29 | 5.29 | 5.32 | 5.33 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 2.8105 | 2.8105 | 2.8255 | 2.8205 | 2.804 | 2.804 | 2.819 | 2.824 | 2.7975 | 2.7975 | 2.7975 | 2.7975 | 2.7975 | 2.7975 | 2.7975 | 2.7975 | 2.7975 | 2.7975 | 2.7975 | 2.7975 | 2.7975 | 0.001878 | 0.001878 | 0.0018881 | 0.0018847 | 0.0018737 | 0.0018737 | 0.0018837 | 0.0018871 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694
| CME014 | 3711.5 | 10.93 | 11.04 | 11.18 | 11.25 | 11.3 | 11.42 | 11.62 | 11.77 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 10.32 | 10.35 | 10.48 | 10.55 | 10.6 | 10.72 | 10.89 | 11.05 | 11.08 | 11.08 | 11.08 | 11.08 | 11.08 | 11.08 | 11.08 | 11.08 | 11.08 | 11.08 | 11.08 | 11.08 | 11.08 | 5.2515 | 5.2785 | 5.345 | 5.38 | 5.405 | 5.465 | 5.5545 | 5.633 | 5.648 | 5.648 | 5.648 | 5.648 | 5.648 | 5.648 | 5.648 | 5.648 | 5.648 | 5.648 | 5.648 | 5.648 | 5.648 | 0.0014149 | 0.0014222 | 0.0014401 | 0.0014495 | 0.0014563 | 0.0014725 | 0.0014966 | 0.0015177 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218
| CME015 | 1237.5 | 9.37 | 9.36 | 9.31 | 9.24 | 9.12 | 9.02 | 9 | 9.01 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 7.04 | 7.07 | 7.03 | 6.98 | 6.89 | 6.82 | 6.81 | 6.82 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 3.8695 | 3.8785 | 3.857 | 3.829 | 3.7795 | 3.74 | 3.7335 | 3.7385 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 0.0031269 | 0.0031341 | 0.0031168 | 0.0030941 | 0.0030541 | 0.0030222 | 0.003017 | 0.003021 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903
| CME016 | 2680 | 9.76 | 9.94 | 10.09 | 10.19 | 10.22 | 10.29 | 10.46 | 10.66 | 10.69 | 10.69 | 10.69 | 10.69 | 10.69 | 10.69 | 10.69 | 10.69 | 10.69 | 10.69 | 10.69 | 10.69 | 10.69 | 8.74 | 8.89 | 9.03 | 9.13 | 9.15 | 9.2 | 9.35 | 9.53 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 9.56 | 4.523 | 4.6025 | 4.674 | 4.724 | 4.7355 | 4.7635 | 4.8415 | 4.9345 | 4.9495 | 4.9495 | 4.9495 | 4.9495 | 4.9495 | 4.9495 | 4.9495 | 4.9495 | 4.9495 | 4.9495 | 4.9495 | 4.9495 | 4.9495 | 0.0016877 | 0.0017174 | 0.001744 | 0.0017627 | 0.001767 | 0.0017774 | 0.0018065 | 0.0018412 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468
| CME021 | 2092 | 8.24 | 8.25 | 8.22 | 8.16 | 8.06 | 7.98 | 7.96 | 7.96 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.89 | 7.68 | 7.7 | 7.67 | 7.62 | 7.52 | 7.44 | 7.41 | 7.41 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 7.35 | 3.924 | 3.9325 | 3.9175 | 3.891 | 3.841 | 3.801 | 3.7875 | 3.7875 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 0.0018757 | 0.0018798 | 0.0018726 | 0.0018599 | 0.001836 | 0.0018169 | 0.0018105 | 0.0018105 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954
| CME022 | 449.5 | 12.08 | 12.05 | 11.84 | 11.62 | 11.39 | 11.19 | 11.03 | 10.89 | 10.75 | 10.75 | 10.75 | 10.75 | 10.75 | 10.75 | 10.75 | 10.75 | 10.75 | 10.75 | 10.75 | 10.75 | 10.75 | 10.83 | 10.81 | 10.64 | 10.45 | 10.26 | 10.08 | 9.94 | 9.82 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 5.6025 | 5.591 | 5.5 | 5.4005 | 5.2995 | 5.2065 | 5.1335 | 5.0705 | 5.0075 | 5.0075 | 5.0075 | 5.0075 | 5.0075 | 5.0075 | 5.0075 | 5.0075 | 5.0075 | 5.0075 | 5.0075 | 5.0075 | 5.0075 | 0.012464 | 0.012438 | 0.012236 | 0.012014 | 0.01179 | 0.011583 | 0.01142 | 0.01128 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114
| CMN001 | 4990 | 4.38 | 4.47 | 4.6 | 4.7 | 4.8 | 4.92 | 5.07 | 5.19 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 4 | 4.09 | 4.21 | 4.32 | 4.41 | 4.54 | 4.68 | 4.8 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 2.057 | 2.102 | 2.1635 | 2.217 | 2.2635 | 2.327 | 2.3985 | 2.4585 | 2.4935 | 2.4935 | 2.4935 | 2.4935 | 2.4935 | 2.4935 | 2.4935 | 2.4935 | 2.4935 | 2.4935 | 2.4935 | 2.4935 | 2.4935 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997
| CMN002 | 1563.5 | 3.93 | 3.93 | 3.95 | 3.95 | 3.94 | 3.95 | 3.98 | 4 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.7 | 3.7 | 3.72 | 3.72 | 3.71 | 3.73 | 3.75 | 3.78 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 1.8845 | 1.8845 | 1.8945 | 1.8945 | 1.8895 | 1.898 | 1.9095 | 1.923 | 1.918 | 1.918 | 1.918 | 1.918 | 1.918 | 1.918 | 1.918 | 1.918 | 1.918 | 1.918 | 1.918 | 1.918 | 1.918 | 0.0012053 | 0.0012053 | 0.0012117 | 0.0012117 | 0.0012085 | 0.0012139 | 0.0012213 | 0.0012299 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267
| CMN003 | 3015.5 | 7.44 | 7.59 | 7.81 | 7.97 | 8.12 | 8.34 | 8.6 | 8.83 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 8.92 | 6.94 | 7.09 | 7.3 | 7.48 | 7.63 | 7.84 | 8.1 | 8.31 | 8.42 | 8.42 | 8.42 | 8.42 | 8.42 | 8.42 | 8.42 | 8.42 | 8.42 | 8.42 | 8.42 | 8.42 | 8.42 | 3.545 | 3.62 | 3.7265 | 3.8135 | 3.8885 | 3.995 | 4.125 | 4.233 | 4.285 | 4.285 | 4.285 | 4.285 | 4.285 | 4.285 | 4.285 | 4.285 | 4.285 | 4.285 | 4.285 | 4.285 | 4.285 | 0.0011756 | 0.0012005 | 0.0012358 | 0.0012646 | 0.0012895 | 0.0013248 | 0.0013679 | 0.0014037 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421
| CMN004 | 1752 | 3.46 | 3.47 | 3.49 | 3.51 | 3.49 | 3.51 | 3.56 | 3.61 | 3.61 | 3.61 | 3.61 | 3.61 | 3.61 | 3.61 | 3.61 | 3.61 | 3.61 | 3.61 | 3.61 | 3.61 | 3.61 | 3.23 | 3.24 | 3.26 | 3.27 | 3.27 | 3.3 | 3.36 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 1.6495 | 1.6545 | 1.6645 | 1.671 | 1.668 | 1.6815 | 1.71 | 1.735 | 1.735 | 1.735 | 1.735 | 1.735 | 1.735 | 1.735 | 1.735 | 1.735 | 1.735 | 1.735 | 1.735 | 1.735 | 1.735 | 0.0009415 | 0.00094435 | 0.00095006 | 0.00095377 | 0.00095205 | 0.00095976 | 0.00097603 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903
| CMN005 | 1063 | 9.39 | 9.35 | 9.32 | 9.28 | 9.22 | 9.2 | 9.19 | 9.17 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 9.13 | 8.82 | 8.78 | 8.74 | 8.71 | 8.67 | 8.66 | 8.66 | 8.65 | 8.61 | 8.61 | 8.61 | 8.61 | 8.61 | 8.61 | 8.61 | 8.61 | 8.61 | 8.61 | 8.61 | 8.61 | 8.61 | 4.4955 | 4.4755 | 4.457 | 4.4405 | 4.4175 | 4.411 | 4.4095 | 4.403 | 4.383 | 4.383 | 4.383 | 4.383 | 4.383 | 4.383 | 4.383 | 4.383 | 4.383 | 4.383 | 4.383 | 4.383 | 4.383 | 0.0042291 | 0.0042103 | 0.0041929 | 0.0041773 | 0.0041557 | 0.0041496 | 0.0041482 | 0.0041421 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232
| COB011 | 829.5 | 7.35 | 7.47 | 7.6 | 7.66 | 7.63 | 7.62 | 7.77 | 7.95 | 7.91 | 7.91 | 7.91 | 7.91 | 7.91 | 7.91 | 7.91 | 7.91 | 7.91 | 7.91 | 7.91 | 7.91 | 7.91 | 5.32 | 5.44 | 5.52 | 5.57 | 5.54 | 5.54 | 5.64 | 5.78 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 2.9645 | 3.0245 | 3.072 | 3.0985 | 3.0835 | 3.082 | 3.1395 | 3.2155 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523
| COB012 | 33 | 1.33 | 1.32 | 1.29 | 1.27 | 1.24 | 1.22 | 1.2 | 1.18 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.16 | 1.14 | 1.11 | 1.09 | 1.07 | 1.05 | 1.04 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 0.609 | 0.604 | 0.5925 | 0.579 | 0.5675 | 0.5575 | 0.5475 | 0.541 | 0.5325 | 0.5325 | 0.5325 | 0.5325 | 0.5325 | 0.5325 | 0.5325 | 0.5325 | 0.5325 | 0.5325 | 0.5325 | 0.5325 | 0.5325 | 0.018455 | 0.018303 | 0.017955 | 0.017545 | 0.017197 | 0.016894 | 0.016591 | 0.016394 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136
| COB021 | 14 | 4.83 | 4.79 | 4.7 | 4.6 | 4.5 | 4.4 | 4.32 | 4.25 | 4.18 | 4.18 | 4.18 | 4.18 | 4.18 | 4.18 | 4.18 | 4.18 | 4.18 | 4.18 | 4.18 | 4.18 | 4.18 | 4.72 | 4.68 | 4.58 | 4.49 | 4.39 | 4.3 | 4.22 | 4.16 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 2.3765 | 2.3565 | 2.308 | 2.2615 | 2.2115 | 2.165 | 2.125 | 2.0935 | 2.0585 | 2.0585 | 2.0585 | 2.0585 | 2.0585 | 2.0585 | 2.0585 | 2.0585 | 2.0585 | 2.0585 | 2.0585 | 2.0585 | 2.0585 | 0.16975 | 0.16832 | 0.16486 | 0.16154 | 0.15796 | 0.15464 | 0.15179 | 0.14954 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704
| COB022 | 3 | 7.93 | 7.78 | 7.61 | 7.45 | 7.28 | 7.14 | 7.02 | 6.91 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.82 | 6.68 | 6.54 | 6.4 | 6.26 | 6.13 | 6.03 | 5.94 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 3.5765 | 3.505 | 3.4305 | 3.3575 | 3.283 | 3.2165 | 3.1635 | 3.1155 | 3.064 | 3.064 | 3.064 | 3.064 | 3.064 | 3.064 | 3.064 | 3.064 | 3.064 | 3.064 | 3.064 | 3.064 | 3.064 | 1.1922 | 1.1683 | 1.1435 | 1.1192 | 1.0943 | 1.0722 | 1.0545 | 1.0385 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213
| CRO013 | 3531 | 4.36 | 4.4 | 4.42 | 4.42 | 4.41 | 4.41 | 4.46 | 4.53 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 3.96 | 3.99 | 4 | 4.02 | 4.01 | 4.02 | 4.18 | 4.31 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 2.04 | 2.0565 | 2.063 | 2.07 | 2.065 | 2.0685 | 2.132 | 2.188 | 2.228 | 2.228 | 2.228 | 2.228 | 2.228 | 2.228 | 2.228 | 2.228 | 2.228 | 2.228 | 2.228 | 2.228 | 2.228 | 0.00057774 | 0.00058241 | 0.00058425 | 0.00058624 | 0.00058482 | 0.00058581 | 0.00060379 | 0.00061965 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098
| CRO014 | 37 | 2.86 | 2.85 | 2.84 | 2.83 | 2.82 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.49 | 2.48 | 2.47 | 2.46 | 2.45 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 1.3005 | 1.2955 | 1.2905 | 1.2855 | 1.2805 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 1.2755 | 0.035149 | 0.035014 | 0.034878 | 0.034743 | 0.034608 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473
| CRO021 | 865 | 5.19 | 5.19 | 5.2 | 5.15 | 5.09 | 5.09 | 5.16 | 5.2 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 4.68 | 4.66 | 4.68 | 4.66 | 4.61 | 4.62 | 4.68 | 4.71 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 4.65 | 2.4165 | 2.4095 | 2.418 | 2.4035 | 2.377 | 2.3805 | 2.412 | 2.4285 | 2.3985 | 2.3985 | 2.3985 | 2.3985 | 2.3985 | 2.3985 | 2.3985 | 2.3985 | 2.3985 | 2.3985 | 2.3985 | 2.3985 | 2.3985 | 0.0027936 | 0.0027855 | 0.0027954 | 0.0027786 | 0.002748 | 0.002752 | 0.0027884 | 0.0028075 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728
| CRO022 | 3058 | 3.47 | 3.48 | 3.47 | 3.47 | 3.44 | 3.44 | 3.47 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.51 | 3.07 | 3.08 | 3.08 | 3.08 | 3.07 | 3.07 | 3.11 | 3.14 | 3.16 | 3.16 | 3.16 | 3.16 | 3.16 | 3.16 | 3.16 | 3.16 | 3.16 | 3.16 | 3.16 | 3.16 | 3.16 | 1.595 | 1.6 | 1.5985 | 1.5985 | 1.5905 | 1.5905 | 1.609 | 1.6255 | 1.6325 | 1.6325 | 1.6325 | 1.6325 | 1.6325 | 1.6325 | 1.6325 | 1.6325 | 1.6325 | 1.6325 | 1.6325 | 1.6325 | 1.6325 | 0.00052158 | 0.00052322 | 0.00052273 | 0.00052273 | 0.00052011 | 0.00052011 | 0.00052616 | 0.00053156 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385
| CRO023 | 299 | 1.06 | 1.06 | 1.05 | 1.04 | 1.03 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 0.92 | 0.92 | 0.91 | 0.91 | 0.9 | 0.9 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.481 | 0.481 | 0.476 | 0.4745 | 0.4695 | 0.468 | 0.4715 | 0.4715 | 0.4715 | 0.4715 | 0.4715 | 0.4715 | 0.4715 | 0.4715 | 0.4715 | 0.4715 | 0.4715 | 0.4715 | 0.4715 | 0.4715 | 0.4715 | 0.0016087 | 0.0016087 | 0.001592 | 0.001587 | 0.0015702 | 0.0015652 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769
| CRO024 | 12.5 | 0.44 | 0.44 | 0.45 | 0.45 | 0.45 | 0.45 | 0.46 | 0.47 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.38 | 0.38 | 0.39 | 0.39 | 0.38 | 0.39 | 0.4 | 0.4 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.199 | 0.199 | 0.204 | 0.204 | 0.2005 | 0.204 | 0.209 | 0.2105 | 0.2055 | 0.2055 | 0.2055 | 0.2055 | 0.2055 | 0.2055 | 0.2055 | 0.2055 | 0.2055 | 0.2055 | 0.2055 | 0.2055 | 0.2055 | 0.01592 | 0.01592 | 0.01632 | 0.01632 | 0.01604 | 0.01632 | 0.01672 | 0.01684 | 0.01644 | 0.01644 | 0.01644 | 0.01644 | 0.01644 | 0.01644 | 0.01644 | 0.01644 | 0.01644 | 0.01644 | 0.01644 | 0.01644 | 0.01644
| CRO031 | 1 | 5.69 | 5.65 | 5.57 | 5.49 | 5.4 | 5.32 | 5.26 | 5.2 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.58 | 5.54 | 5.46 | 5.38 | 5.3 | 5.22 | 5.16 | 5.11 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 5.05 | 2.8065 | 2.7865 | 2.7465 | 2.7065 | 2.665 | 2.625 | 2.595 | 2.5685 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.8065 | 2.7865 | 2.7465 | 2.7065 | 2.665 | 2.625 | 2.595 | 2.5685 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54
| CRO032 | 6.5 | 13.33 | 13.54 | 13.9 | 13.96 | 13.91 | 14.06 | 14.53 | 14.87 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 13.21 | 13.43 | 13.77 | 13.83 | 13.77 | 13.94 | 14.41 | 14.72 | 14.57 | 14.57 | 14.57 | 14.57 | 14.57 | 14.57 | 14.57 | 14.57 | 14.57 | 14.57 | 14.57 | 14.57 | 14.57 | 6.623 | 6.7315 | 6.9045 | 6.9345 | 6.906 | 6.988 | 7.223 | 7.3825 | 7.3045 | 7.3045 | 7.3045 | 7.3045 | 7.3045 | 7.3045 | 7.3045 | 7.3045 | 7.3045 | 7.3045 | 7.3045 | 7.3045 | 7.3045 | 1.0189 | 1.0356 | 1.0622 | 1.0668 | 1.0625 | 1.0751 | 1.1112 | 1.1358 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238
| CRO033 | 16 | 4.69 | 4.66 | 4.6 | 4.53 | 4.47 | 4.4 | 4.35 | 4.31 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.27 | 4.26 | 4.24 | 4.18 | 4.12 | 4.06 | 4 | 3.95 | 3.92 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88 | 2.1945 | 2.183 | 2.153 | 2.1215 | 2.0915 | 2.06 | 2.035 | 2.0185 | 1.9985 | 1.9985 | 1.9985 | 1.9985 | 1.9985 | 1.9985 | 1.9985 | 1.9985 | 1.9985 | 1.9985 | 1.9985 | 1.9985 | 1.9985 | 0.13716 | 0.13644 | 0.13456 | 0.13259 | 0.13072 | 0.12875 | 0.12719 | 0.12616 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491
| CRO034 | 1360 | 5.22 | 5.22 | 5.19 | 5.16 | 5.09 | 5.05 | 5.06 | 5.08 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 5.04 | 4.65 | 4.67 | 4.64 | 4.6 | 4.54 | 4.49 | 4.5 | 4.51 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 4.48 | 2.4105 | 2.4175 | 2.4025 | 2.384 | 2.3525 | 2.329 | 2.334 | 2.3405 | 2.324 | 2.324 | 2.324 | 2.324 | 2.324 | 2.324 | 2.324 | 2.324 | 2.324 | 2.324 | 2.324 | 2.324 | 2.324 | 0.0017724 | 0.0017776 | 0.0017665 | 0.0017529 | 0.0017298 | 0.0017125 | 0.0017162 | 0.001721 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088
| CTN001 | 1628 | 7.59 | 10.13 | 10.18 | 10.15 | 10.06 | 10.02 | 10.07 | 10.12 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 6.7 | 9.3 | 9.37 | 9.35 | 9.27 | 9.23 | 9.27 | 9.32 | 9.25 | 9.25 | 9.25 | 9.25 | 9.25 | 9.25 | 9.25 | 9.25 | 9.25 | 9.25 | 9.25 | 9.25 | 9.25 | 3.4835 | 4.7745 | 4.8065 | 4.795 | 4.7535 | 4.7335 | 4.755 | 4.78 | 4.7405 | 4.7405 | 4.7405 | 4.7405 | 4.7405 | 4.7405 | 4.7405 | 4.7405 | 4.7405 | 4.7405 | 4.7405 | 4.7405 | 4.7405 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119
| CTN002 | 1154 | 2.97 | 2.98 | 2.97 | 2.96 | 2.93 | 2.9 | 2.91 | 2.92 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.65 | 2.65 | 2.64 | 2.62 | 2.59 | 2.56 | 2.56 | 2.57 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 1.373 | 1.3745 | 1.3695 | 1.361 | 1.346 | 1.331 | 1.3325 | 1.3375 | 1.3225 | 1.3225 | 1.3225 | 1.3225 | 1.3225 | 1.3225 | 1.3225 | 1.3225 | 1.3225 | 1.3225 | 1.3225 | 1.3225 | 1.3225 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146
| CTN003 | 1198.5 | 2.29 | 2.3 | 2.3 | 2.29 | 2.26 | 2.23 | 2.24 | 2.24 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.12 | 2.13 | 2.13 | 2.11 | 2.08 | 2.06 | 2.06 | 2.06 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 1.0855 | 1.0905 | 1.0905 | 1.082 | 1.067 | 1.0555 | 1.057 | 1.057 | 1.0435 | 1.0435 | 1.0435 | 1.0435 | 1.0435 | 1.0435 | 1.0435 | 1.0435 | 1.0435 | 1.0435 | 1.0435 | 1.0435 | 1.0435 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067
| CTN004 | 1262 | 3.26 | 3.23 | 3.2 | 3.15 | 3.1 | 3.07 | 3.05 | 3.03 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 3.12 | 3.1 | 3.06 | 3.02 | 2.97 | 2.93 | 2.91 | 2.89 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 1.581 | 1.5695 | 1.551 | 1.5295 | 1.5045 | 1.486 | 1.476 | 1.466 | 1.4425 | 1.4425 | 1.4425 | 1.4425 | 1.4425 | 1.4425 | 1.4425 | 1.4425 | 1.4425 | 1.4425 | 1.4425 | 1.4425 | 1.4425 | 0.0012528 | 0.0012437 | 0.001229 | 0.001212 | 0.0011922 | 0.0011775 | 0.0011696 | 0.0011616 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143
| CTN005 | 647.5 | 1.55 | 1.55 | 1.54 | 1.52 | 1.5 | 1.48 | 1.47 | 1.46 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.43 | 1.43 | 1.42 | 1.4 | 1.38 | 1.36 | 1.35 | 1.34 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 0.733 | 0.733 | 0.728 | 0.718 | 0.708 | 0.698 | 0.693 | 0.688 | 0.678 | 0.678 | 0.678 | 0.678 | 0.678 | 0.678 | 0.678 | 0.678 | 0.678 | 0.678 | 0.678 | 0.678 | 0.678 | 0.001132 | 0.001132 | 0.0011243 | 0.0011089 | 0.0010934 | 0.001078 | 0.0010703 | 0.0010625 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471
| CTN006 | 1971 | 6.7 | 6.67 | 6.63 | 6.57 | 6.46 | 6.37 | 6.34 | 6.32 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.16 | 6.14 | 6.1 | 6.03 | 5.93 | 5.85 | 5.82 | 5.8 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 3.161 | 3.1495 | 3.1295 | 3.096 | 3.0445 | 3.003 | 2.988 | 2.978 | 2.9365 | 2.9365 | 2.9365 | 2.9365 | 2.9365 | 2.9365 | 2.9365 | 2.9365 | 2.9365 | 2.9365 | 2.9365 | 2.9365 | 2.9365 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899
| DDL011 | 5059.5 | 11.99 | 12.3 | 12.59 | 12.86 | 13.1 | 13.33 | 13.69 | 14.09 | 14.39 | 14.39 | 14.39 | 14.39 | 14.39 | 14.39 | 14.39 | 14.39 | 14.39 | 14.39 | 14.39 | 14.39 | 14.39 | 10.53 | 10.81 | 11.05 | 11.29 | 11.45 | 11.6 | 12.02 | 12.54 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 5.484 | 5.6285 | 5.756 | 5.8805 | 5.9725 | 6.0595 | 6.2605 | 6.5025 | 6.6805 | 6.6805 | 6.6805 | 6.6805 | 6.6805 | 6.6805 | 6.6805 | 6.6805 | 6.6805 | 6.6805 | 6.6805 | 6.6805 | 6.6805 | 0.0010839 | 0.0011125 | 0.0011377 | 0.0011623 | 0.0011805 | 0.0011976 | 0.0012374 | 0.0012852 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204
| DDL012 | 4312.5 | 10.74 | 10.92 | 11.02 | 11.09 | 11.12 | 11.17 | 11.3 | 11.47 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 11.58 | 9.11 | 9.25 | 9.32 | 9.39 | 9.45 | 9.5 | 9.61 | 9.76 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 4.7995 | 4.8755 | 4.915 | 4.95 | 4.9755 | 5.0005 | 5.0585 | 5.1365 | 5.2405 | 5.2405 | 5.2405 | 5.2405 | 5.2405 | 5.2405 | 5.2405 | 5.2405 | 5.2405 | 5.2405 | 5.2405 | 5.2405 | 5.2405 | 0.0011129 | 0.0011306 | 0.0011397 | 0.0011478 | 0.0011537 | 0.0011595 | 0.001173 | 0.0011911 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152
| DDL013 | 5862.5 | 12.73 | 13.1 | 13.4 | 13.68 | 13.92 | 14.13 | 14.45 | 14.8 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 11.06 | 11.36 | 11.63 | 11.92 | 12.13 | 12.33 | 12.62 | 12.96 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 5.7805 | 5.941 | 6.0805 | 6.224 | 6.3335 | 6.435 | 6.5845 | 6.756 | 6.894 | 6.894 | 6.894 | 6.894 | 6.894 | 6.894 | 6.894 | 6.894 | 6.894 | 6.894 | 6.894 | 6.894 | 6.894 | 0.00098601 | 0.0010134 | 0.0010372 | 0.0010617 | 0.0010803 | 0.0010977 | 0.0011232 | 0.0011524 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759
| DDL014 | 5028.5 | 10.88 | 11.06 | 11.22 | 11.39 | 11.45 | 11.55 | 12.06 | 12.55 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 9.8 | 9.98 | 10.13 | 10.23 | 10.29 | 10.71 | 11.23 | 11.69 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 5.062 | 5.152 | 5.2285 | 5.289 | 5.319 | 5.481 | 5.7395 | 5.974 | 6.1605 | 6.1605 | 6.1605 | 6.1605 | 6.1605 | 6.1605 | 6.1605 | 6.1605 | 6.1605 | 6.1605 | 6.1605 | 6.1605 | 6.1605 | 0.0010067 | 0.0010246 | 0.0010398 | 0.0010518 | 0.0010578 | 0.00109 | 0.0011414 | 0.001188 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251
| DDL021 | 3801.5 | 9.74 | 10.04 | 10.28 | 10.51 | 10.67 | 10.85 | 11.13 | 11.42 | 11.65 | 11.65 | 11.65 | 11.65 | 11.65 | 11.65 | 11.65 | 11.65 | 11.65 | 11.65 | 11.65 | 11.65 | 11.65 | 8.82 | 9.08 | 9.29 | 9.5 | 9.66 | 9.83 | 10.08 | 10.36 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 4.548 | 4.684 | 4.7935 | 4.9015 | 4.9815 | 5.068 | 5.1975 | 5.339 | 5.447 | 5.447 | 5.447 | 5.447 | 5.447 | 5.447 | 5.447 | 5.447 | 5.447 | 5.447 | 5.447 | 5.447 | 5.447 | 0.0011964 | 0.0012321 | 0.0012609 | 0.0012894 | 0.0013104 | 0.0013332 | 0.0013672 | 0.0014044 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329
| DDL022 | 5025 | 11.19 | 11.63 | 12.07 | 12.46 | 12.82 | 13.21 | 13.82 | 14.61 | 15.28 | 15.28 | 15.28 | 15.28 | 15.28 | 15.28 | 15.28 | 15.28 | 15.28 | 15.28 | 15.28 | 15.28 | 15.28 | 9.92 | 10.31 | 10.68 | 11.03 | 11.58 | 12.32 | 13.1 | 13.85 | 14.45 | 14.45 | 14.45 | 14.45 | 14.45 | 14.45 | 14.45 | 14.45 | 14.45 | 14.45 | 14.45 | 14.45 | 14.45 | 5.1505 | 5.353 | 5.5485 | 5.7295 | 5.976 | 6.2935 | 6.658 | 7.039 | 7.3495 | 7.3495 | 7.3495 | 7.3495 | 7.3495 | 7.3495 | 7.3495 | 7.3495 | 7.3495 | 7.3495 | 7.3495 | 7.3495 | 7.3495 | 0.001025 | 0.0010653 | 0.0011042 | 0.0011402 | 0.0011893 | 0.0012524 | 0.001325 | 0.0014008 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626
| DDL023 | 3293.5 | 12.82 | 13.32 | 13.75 | 14.1 | 14.43 | 14.79 | 15.26 | 15.74 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 11.6 | 12.06 | 12.44 | 12.83 | 13.12 | 13.44 | 13.88 | 14.32 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 5.983 | 6.219 | 6.4165 | 6.6055 | 6.7565 | 6.9225 | 7.147 | 7.373 | 7.5435 | 7.5435 | 7.5435 | 7.5435 | 7.5435 | 7.5435 | 7.5435 | 7.5435 | 7.5435 | 7.5435 | 7.5435 | 7.5435 | 7.5435 | 0.0018166 | 0.0018883 | 0.0019482 | 0.0020056 | 0.0020515 | 0.0021019 | 0.00217 | 0.0022387 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904
| DDL024 | 3737.5 | 10.68 | 10.99 | 11.23 | 11.44 | 11.61 | 11.82 | 12.16 | 12.5 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 9.26 | 9.54 | 9.79 | 10.02 | 10.2 | 10.61 | 11.15 | 11.66 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 12.06 | 4.843 | 4.9875 | 5.111 | 5.223 | 5.3115 | 5.4865 | 5.7265 | 5.956 | 6.132 | 6.132 | 6.132 | 6.132 | 6.132 | 6.132 | 6.132 | 6.132 | 6.132 | 6.132 | 6.132 | 6.132 | 6.132 | 0.0012958 | 0.0013344 | 0.0013675 | 0.0013975 | 0.0014211 | 0.001468 | 0.0015322 | 0.0015936 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407
| DLF001 | 1868.5 | 6.67 | 7.13 | 7.39 | 7.69 | 7.97 | 8.25 | 8.57 | 8.87 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 6.19 | 6.61 | 6.86 | 7.15 | 7.4 | 7.66 | 7.97 | 8.28 | 8.54 | 8.54 | 8.54 | 8.54 | 8.54 | 8.54 | 8.54 | 8.54 | 8.54 | 8.54 | 8.54 | 8.54 | 8.54 | 3.167 | 3.383 | 3.5095 | 3.656 | 3.7855 | 3.9185 | 4.075 | 4.2285 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 0.0016949 | 0.0018105 | 0.0018782 | 0.0019566 | 0.002026 | 0.0020971 | 0.0021809 | 0.002263 | 0.0023334 | 0.0023334 | 0.0023334 | 0.0023334 | 0.0023334 | 0.0023334 | 0.0023334 | 0.0023334 | 0.0023334 | 0.0023334 | 0.0023334 | 0.0023334 | 0.0023334
| ECA001 | 2273 | 6.88 | 6.93 | 6.92 | 6.92 | 6.88 | 6.86 | 6.87 | 6.9 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.3 | 6.32 | 6.32 | 6.31 | 6.27 | 6.25 | 6.28 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 3.237 | 3.2515 | 3.25 | 3.2465 | 3.2265 | 3.2165 | 3.2285 | 3.2435 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 0.0014241 | 0.0014305 | 0.0014298 | 0.0014283 | 0.0014195 | 0.0014151 | 0.0014204 | 0.001427 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263
| ECA003 | 2496 | 8.22 | 8.25 | 8.21 | 8.18 | 8.12 | 8.09 | 8.12 | 8.16 | 8.15 | 8.15 | 8.15 | 8.15 | 8.15 | 8.15 | 8.15 | 8.15 | 8.15 | 8.15 | 8.15 | 8.15 | 8.15 | 7.55 | 7.58 | 7.55 | 7.5 | 7.45 | 7.42 | 7.44 | 7.47 | 7.45 | 7.45 | 7.45 | 7.45 | 7.45 | 7.45 | 7.45 | 7.45 | 7.45 | 7.45 | 7.45 | 7.45 | 7.45 | 3.8755 | 3.8905 | 3.874 | 3.852 | 3.8255 | 3.8105 | 3.822 | 3.8385 | 3.83 | 3.83 | 3.83 | 3.83 | 3.83 | 3.83 | 3.83 | 3.83 | 3.83 | 3.83 | 3.83 | 3.83 | 3.83 | 0.0015527 | 0.0015587 | 0.0015521 | 0.0015433 | 0.0015327 | 0.0015266 | 0.0015313 | 0.0015379 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345
| ECA005 | 885.5 | 13.78 | 13.98 | 13.95 | 13.93 | 13.84 | 13.75 | 13.76 | 13.83 | 13.81 | 13.81 | 13.81 | 13.81 | 13.81 | 13.81 | 13.81 | 13.81 | 13.81 | 13.81 | 13.81 | 13.81 | 13.81 | 10.17 | 10.19 | 10.2 | 10.16 | 10.09 | 10.06 | 10.08 | 10.12 | 10.04 | 10.04 | 10.04 | 10.04 | 10.04 | 10.04 | 10.04 | 10.04 | 10.04 | 10.04 | 10.04 | 10.04 | 10.04 | 5.6265 | 5.6635 | 5.6625 | 5.6455 | 5.6075 | 5.5835 | 5.592 | 5.6165 | 5.5855 | 5.5855 | 5.5855 | 5.5855 | 5.5855 | 5.5855 | 5.5855 | 5.5855 | 5.5855 | 5.5855 | 5.5855 | 5.5855 | 5.5855 | 0.006354 | 0.0063958 | 0.0063947 | 0.0063755 | 0.0063326 | 0.0063055 | 0.0063151 | 0.0063427 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077
| ECA007 | 1172.5 | 5.05 | 5.14 | 5.17 | 5.2 | 5.19 | 5.18 | 5.24 | 5.29 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 5.28 | 3.13 | 3.18 | 3.22 | 3.24 | 3.23 | 3.21 | 3.26 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 1.853 | 1.884 | 1.9025 | 1.914 | 1.909 | 1.9005 | 1.927 | 1.945 | 1.9435 | 1.9435 | 1.9435 | 1.9435 | 1.9435 | 1.9435 | 1.9435 | 1.9435 | 1.9435 | 1.9435 | 1.9435 | 1.9435 | 1.9435 | 0.0015804 | 0.0016068 | 0.0016226 | 0.0016324 | 0.0016281 | 0.0016209 | 0.0016435 | 0.0016588 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576
| ECA010 | 2259.5 | 8.28 | 8.34 | 8.39 | 8.4 | 8.36 | 8.35 | 8.42 | 8.52 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 7.68 | 7.76 | 7.8 | 7.81 | 7.77 | 7.75 | 7.82 | 7.91 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 3.93 | 3.967 | 3.9885 | 3.9935 | 3.9735 | 3.965 | 4 | 4.0465 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 0.0017393 | 0.0017557 | 0.0017652 | 0.0017674 | 0.0017586 | 0.0017548 | 0.0017703 | 0.0017909 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788
| ECA012 | 2000 | 6.89 | 6.98 | 7.08 | 7.13 | 7.07 | 7.08 | 7.19 | 7.32 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 6.02 | 6.11 | 6.2 | 6.24 | 6.22 | 6.23 | 6.33 | 6.45 | 6.43 | 6.43 | 6.43 | 6.43 | 6.43 | 6.43 | 6.43 | 6.43 | 6.43 | 6.43 | 6.43 | 6.43 | 6.43 | 3.1405 | 3.1855 | 3.232 | 3.2535 | 3.2375 | 3.2425 | 3.294 | 3.3555 | 3.344 | 3.344 | 3.344 | 3.344 | 3.344 | 3.344 | 3.344 | 3.344 | 3.344 | 3.344 | 3.344 | 3.344 | 3.344 | 0.0015702 | 0.0015928 | 0.001616 | 0.0016267 | 0.0016187 | 0.0016212 | 0.001647 | 0.0016777 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672
| EHK021 | 367 | 14.07 | 13.53 | 13.53 | 13.51 | 13.37 | 13.22 | 13.31 | 13.34 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.07 | 12.75 | 12.75 | 12.73 | 12.6 | 12.59 | 12.67 | 12.7 | 12.49 | 12.49 | 12.49 | 12.49 | 12.49 | 12.49 | 12.49 | 12.49 | 12.49 | 12.49 | 12.49 | 12.49 | 12.49 | 6.685 | 6.492 | 6.492 | 6.482 | 6.4155 | 6.3895 | 6.431 | 6.446 | 6.365 | 6.365 | 6.365 | 6.365 | 6.365 | 6.365 | 6.365 | 6.365 | 6.365 | 6.365 | 6.365 | 6.365 | 6.365 | 0.018215 | 0.017689 | 0.017689 | 0.017662 | 0.017481 | 0.01741 | 0.017523 | 0.017564 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343
| EHK022 | 1369.5 | 8.18 | 8.15 | 8.08 | 7.98 | 7.91 | 7.85 | 7.83 | 7.85 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 5.75 | 5.73 | 5.68 | 5.67 | 5.67 | 5.72 | 5.77 | 5.82 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 3.2395 | 3.228 | 3.2 | 3.1815 | 3.171 | 3.1795 | 3.194 | 3.2145 | 3.217 | 3.217 | 3.217 | 3.217 | 3.217 | 3.217 | 3.217 | 3.217 | 3.217 | 3.217 | 3.217 | 3.217 | 3.217 | 0.0023655 | 0.0023571 | 0.0023366 | 0.0023231 | 0.0023154 | 0.0023217 | 0.0023322 | 0.0023472 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349
| EHK023 | 4251 | 9.22 | 9.34 | 9.43 | 9.49 | 9.51 | 9.56 | 9.68 | 9.81 | 9.92 | 9.92 | 9.92 | 9.92 | 9.92 | 9.92 | 9.92 | 9.92 | 9.92 | 9.92 | 9.92 | 9.92 | 9.92 | 8.56 | 8.65 | 8.74 | 8.81 | 8.82 | 8.87 | 9.03 | 9.34 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 4.379 | 4.4285 | 4.4735 | 4.507 | 4.5135 | 4.5385 | 4.6125 | 4.7405 | 4.8375 | 4.8375 | 4.8375 | 4.8375 | 4.8375 | 4.8375 | 4.8375 | 4.8375 | 4.8375 | 4.8375 | 4.8375 | 4.8375 | 4.8375 | 0.0010301 | 0.0010418 | 0.0010523 | 0.0010602 | 0.0010618 | 0.0010676 | 0.001085 | 0.0011151 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138
| EHK024 | 2181 | 10.17 | 10.94 | 10.95 | 10.96 | 10.9 | 10.87 | 10.91 | 11 | 10.98 | 10.98 | 10.98 | 10.98 | 10.98 | 10.98 | 10.98 | 10.98 | 10.98 | 10.98 | 10.98 | 10.98 | 10.98 | 9.14 | 9.95 | 9.98 | 9.98 | 9.92 | 9.91 | 9.95 | 10.03 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 10.01 | 4.7245 | 5.1235 | 5.1355 | 5.137 | 5.107 | 5.099 | 5.119 | 5.1605 | 5.1505 | 5.1505 | 5.1505 | 5.1505 | 5.1505 | 5.1505 | 5.1505 | 5.1505 | 5.1505 | 5.1505 | 5.1505 | 5.1505 | 5.1505 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615
| EHK031 | 2346.5 | 11.07 | 11.46 | 11.72 | 11.95 | 12.14 | 12.39 | 12.71 | 13.04 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 9.88 | 10.23 | 10.48 | 10.69 | 10.86 | 11.07 | 11.56 | 12.09 | 12.48 | 12.48 | 12.48 | 12.48 | 12.48 | 12.48 | 12.48 | 12.48 | 12.48 | 12.48 | 12.48 | 12.48 | 12.48 | 5.1185 | 5.2995 | 5.426 | 5.534 | 5.622 | 5.733 | 5.9525 | 6.1875 | 6.3615 | 6.3615 | 6.3615 | 6.3615 | 6.3615 | 6.3615 | 6.3615 | 6.3615 | 6.3615 | 6.3615 | 6.3615 | 6.3615 | 6.3615 | 0.0021813 | 0.0022585 | 0.0023124 | 0.0023584 | 0.0023959 | 0.0024432 | 0.0025368 | 0.0026369 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111
| EHK032 | 141.5 | 0.92 | 0.91 | 0.91 | 0.91 | 0.91 | 0.92 | 0.93 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.75 | 0.75 | 0.75 | 0.75 | 0.76 | 0.77 | 0.78 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.4005 | 0.399 | 0.399 | 0.399 | 0.4025 | 0.4075 | 0.4125 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.0028304 | 0.0028198 | 0.0028198 | 0.0028198 | 0.0028445 | 0.0028799 | 0.0029152 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505
| EHK033 | 5477.5 | 15.5 | 15.95 | 16.33 | 16.6 | 16.84 | 17.15 | 17.57 | 18.06 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 14.17 | 14.59 | 14.92 | 15.21 | 15.45 | 15.77 | 16.18 | 16.61 | 16.95 | 16.95 | 16.95 | 16.95 | 16.95 | 16.95 | 16.95 | 16.95 | 16.95 | 16.95 | 16.95 | 16.95 | 16.95 | 7.2845 | 7.499 | 7.6715 | 7.8135 | 7.9335 | 8.092 | 8.2985 | 8.5225 | 8.6955 | 8.6955 | 8.6955 | 8.6955 | 8.6955 | 8.6955 | 8.6955 | 8.6955 | 8.6955 | 8.6955 | 8.6955 | 8.6955 | 8.6955 | 0.0013299 | 0.0013691 | 0.0014005 | 0.0014265 | 0.0014484 | 0.0014773 | 0.001515 | 0.0015559 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875
| EHK034 | 888 | 6.69 | 6.64 | 6.57 | 6.5 | 6.4 | 6.33 | 6.29 | 6.26 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.23 | 6.12 | 6.08 | 5.99 | 5.91 | 5.83 | 5.76 | 5.73 | 5.7 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 3.1455 | 3.124 | 3.082 | 3.0435 | 3.0005 | 2.9655 | 2.949 | 2.934 | 2.9225 | 2.9225 | 2.9225 | 2.9225 | 2.9225 | 2.9225 | 2.9225 | 2.9225 | 2.9225 | 2.9225 | 2.9225 | 2.9225 | 2.9225 | 0.0035422 | 0.003518 | 0.0034707 | 0.0034274 | 0.0033789 | 0.0033395 | 0.0033209 | 0.0033041 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911
| ETSA001 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ETSA003 | 45.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FNS011 | 2052 | 9.06 | 9.16 | 9.24 | 9.3 | 9.29 | 9.32 | 9.45 | 9.6 | 9.62 | 9.62 | 9.62 | 9.62 | 9.62 | 9.62 | 9.62 | 9.62 | 9.62 | 9.62 | 9.62 | 9.62 | 9.62 | 8.34 | 8.44 | 8.51 | 8.55 | 8.52 | 8.55 | 8.67 | 8.8 | 8.81 | 8.81 | 8.81 | 8.81 | 8.81 | 8.81 | 8.81 | 8.81 | 8.81 | 8.81 | 8.81 | 8.81 | 8.81 | 4.278 | 4.328 | 4.3645 | 4.3875 | 4.3755 | 4.3905 | 4.452 | 4.52 | 4.5265 | 4.5265 | 4.5265 | 4.5265 | 4.5265 | 4.5265 | 4.5265 | 4.5265 | 4.5265 | 4.5265 | 4.5265 | 4.5265 | 4.5265 | 0.0020848 | 0.0021092 | 0.0021269 | 0.0021382 | 0.0021323 | 0.0021396 | 0.0021696 | 0.0022027 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059
| FNS012 | 3051 | 7.51 | 7.67 | 7.9 | 8.1 | 8.28 | 8.54 | 8.84 | 9.09 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 6.43 | 6.54 | 6.67 | 6.82 | 6.95 | 7.16 | 7.42 | 7.64 | 7.78 | 7.78 | 7.78 | 7.78 | 7.78 | 7.78 | 7.78 | 7.78 | 7.78 | 7.78 | 7.78 | 7.78 | 7.78 | 3.377 | 3.4395 | 3.5195 | 3.602 | 3.6745 | 3.787 | 3.923 | 4.0375 | 4.109 | 4.109 | 4.109 | 4.109 | 4.109 | 4.109 | 4.109 | 4.109 | 4.109 | 4.109 | 4.109 | 4.109 | 4.109 | 0.0011069 | 0.0011273 | 0.0011536 | 0.0011806 | 0.0012044 | 0.0012412 | 0.0012858 | 0.0013233 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468
| FNS013 | 3988.5 | 12.08 | 12.36 | 12.53 | 12.74 | 12.92 | 13.1 | 13.34 | 13.63 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 10.96 | 11.22 | 11.43 | 11.63 | 11.78 | 11.96 | 12.23 | 12.51 | 12.75 | 12.75 | 12.75 | 12.75 | 12.75 | 12.75 | 12.75 | 12.75 | 12.75 | 12.75 | 12.75 | 12.75 | 12.75 | 5.648 | 5.781 | 5.88 | 5.9815 | 6.061 | 6.151 | 6.2815 | 6.423 | 6.5415 | 6.5415 | 6.5415 | 6.5415 | 6.5415 | 6.5415 | 6.5415 | 6.5415 | 6.5415 | 6.5415 | 6.5415 | 6.5415 | 6.5415 | 0.0014161 | 0.0014494 | 0.0014742 | 0.0014997 | 0.0015196 | 0.0015422 | 0.0015749 | 0.0016104 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401
| FNS021 | 1993.5 | 14.85 | 15.11 | 15.49 | 15.77 | 15.99 | 16.35 | 16.81 | 17.23 | 17.41 | 17.41 | 17.41 | 17.41 | 17.41 | 17.41 | 17.41 | 17.41 | 17.41 | 17.41 | 17.41 | 17.41 | 17.41 | 13.17 | 13.44 | 13.54 | 13.64 | 13.65 | 13.8 | 14.2 | 14.55 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 14.72 | 6.837 | 6.9705 | 7.0625 | 7.1395 | 7.176 | 7.2825 | 7.4915 | 7.677 | 7.7635 | 7.7635 | 7.7635 | 7.7635 | 7.7635 | 7.7635 | 7.7635 | 7.7635 | 7.7635 | 7.7635 | 7.7635 | 7.7635 | 7.7635 | 0.0034296 | 0.0034966 | 0.0035428 | 0.0035814 | 0.0035997 | 0.0036531 | 0.003758 | 0.003851 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944
| FNS022 | 972.5 | 7.85 | 8.02 | 8.13 | 8.23 | 8.29 | 8.36 | 8.52 | 8.69 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 8.75 | 6.77 | 6.92 | 7.03 | 7.12 | 7.21 | 7.37 | 7.59 | 7.78 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 3.547 | 3.625 | 3.68 | 3.7265 | 3.767 | 3.8335 | 3.9345 | 4.0265 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 4.06 | 0.0036473 | 0.0037275 | 0.0037841 | 0.0038319 | 0.0038735 | 0.0039419 | 0.0040458 | 0.0041404 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748
| FNS032 | 224 | 6.53 | 6.57 | 6.57 | 6.56 | 6.53 | 6.53 | 6.56 | 6.57 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.01 | 6.05 | 6.05 | 6.03 | 6 | 5.99 | 6.03 | 6.05 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 6.02 | 3.083 | 3.103 | 3.103 | 3.0945 | 3.0795 | 3.076 | 3.0945 | 3.103 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 0.013763 | 0.013853 | 0.013853 | 0.013815 | 0.013748 | 0.013732 | 0.013815 | 0.013853 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792
| GB011 | 2 | 1.45 | 1.45 | 1.44 | 1.45 | 1.48 | 1.51 | 1.52 | 1.51 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.44 | 1.44 | 1.44 | 1.44 | 1.46 | 1.48 | 1.49 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 1.48 | 0.7215 | 0.7215 | 0.72 | 0.7215 | 0.733 | 0.7445 | 0.7495 | 0.7445 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.743 | 0.36075 | 0.36075 | 0.36 | 0.36075 | 0.3665 | 0.37225 | 0.37475 | 0.37225 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715
| GB012 | 27 | 7.63 | 7.68 | 7.67 | 7.64 | 7.6 | 7.57 | 7.58 | 7.59 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 6.86 | 6.91 | 6.89 | 6.87 | 6.83 | 6.81 | 6.81 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 6.82 | 3.5455 | 3.5705 | 3.562 | 3.5505 | 3.5305 | 3.519 | 3.5205 | 3.5255 | 3.524 | 3.524 | 3.524 | 3.524 | 3.524 | 3.524 | 3.524 | 3.524 | 3.524 | 3.524 | 3.524 | 3.524 | 3.524 | 0.13131 | 0.13224 | 0.13193 | 0.1315 | 0.13076 | 0.13033 | 0.13039 | 0.13057 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052
| GB014 | 545.5 | 1.25 | 1.29 | 1.33 | 1.38 | 1.42 | 1.48 | 1.54 | 1.59 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.12 | 1.16 | 1.21 | 1.25 | 1.3 | 1.35 | 1.4 | 1.45 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 0.5795 | 0.5995 | 0.623 | 0.6445 | 0.668 | 0.6945 | 0.721 | 0.746 | 0.766 | 0.766 | 0.766 | 0.766 | 0.766 | 0.766 | 0.766 | 0.766 | 0.766 | 0.766 | 0.766 | 0.766 | 0.766 | 0.0010623 | 0.001099 | 0.0011421 | 0.0011815 | 0.0012246 | 0.0012731 | 0.0013217 | 0.0013676 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042
| GB031 | 631.5 | 5.41 | 5.45 | 5.51 | 5.55 | 5.58 | 5.68 | 5.8 | 5.91 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.94 | 5.14 | 5.17 | 5.22 | 5.26 | 5.3 | 5.37 | 5.49 | 5.6 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 2.6105 | 2.627 | 2.6535 | 2.6735 | 2.692 | 2.7315 | 2.7915 | 2.8465 | 2.8615 | 2.8615 | 2.8615 | 2.8615 | 2.8615 | 2.8615 | 2.8615 | 2.8615 | 2.8615 | 2.8615 | 2.8615 | 2.8615 | 2.8615 | 0.0041338 | 0.0041599 | 0.0042019 | 0.0042336 | 0.0042629 | 0.0043254 | 0.0044204 | 0.0045075 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313
| GB032 | 3 | 6.8 | 6.86 | 6.83 | 6.81 | 6.78 | 6.76 | 6.75 | 6.75 | 6.74 | 6.74 | 6.74 | 6.74 | 6.74 | 6.74 | 6.74 | 6.74 | 6.74 | 6.74 | 6.74 | 6.74 | 6.74 | 6.16 | 6.22 | 6.19 | 6.17 | 6.15 | 6.14 | 6.13 | 6.13 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 3.176 | 3.206 | 3.191 | 3.181 | 3.1695 | 3.163 | 3.158 | 3.158 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 1.0587 | 1.0687 | 1.0637 | 1.0603 | 1.0565 | 1.0543 | 1.0527 | 1.0527 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051
| GCY011 | 4413.5 | 15.15 | 15.3 | 15.37 | 15.46 | 15.43 | 15.46 | 15.62 | 15.79 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 13.3 | 13.45 | 13.51 | 13.55 | 13.52 | 13.57 | 13.68 | 13.86 | 13.95 | 13.95 | 13.95 | 13.95 | 13.95 | 13.95 | 13.95 | 13.95 | 13.95 | 13.95 | 13.95 | 13.95 | 13.95 | 6.9275 | 7.0025 | 7.034 | 7.0615 | 7.0465 | 7.0685 | 7.131 | 7.2195 | 7.266 | 7.266 | 7.266 | 7.266 | 7.266 | 7.266 | 7.266 | 7.266 | 7.266 | 7.266 | 7.266 | 7.266 | 7.266 | 0.0015696 | 0.0015866 | 0.0015937 | 0.0016 | 0.0015966 | 0.0016016 | 0.0016157 | 0.0016358 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463
| GCY012 | 893 | 6.01 | 6 | 5.92 | 5.83 | 5.73 | 5.63 | 5.58 | 5.53 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.65 | 5.63 | 5.56 | 5.47 | 5.38 | 5.3 | 5.25 | 5.2 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 2.879 | 2.8705 | 2.834 | 2.789 | 2.7425 | 2.6995 | 2.6745 | 2.6495 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 2.614 | 0.003224 | 0.0032144 | 0.0031736 | 0.0031232 | 0.0030711 | 0.003023 | 0.002995 | 0.002967 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272
| GCY013 | 346 | 5.29 | 5.29 | 5.24 | 5.19 | 5.13 | 5.08 | 5.05 | 5.04 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 4.67 | 4.67 | 4.63 | 4.59 | 4.54 | 4.5 | 4.47 | 4.45 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 2.428 | 2.428 | 2.4065 | 2.385 | 2.3585 | 2.337 | 2.322 | 2.3135 | 2.302 | 2.302 | 2.302 | 2.302 | 2.302 | 2.302 | 2.302 | 2.302 | 2.302 | 2.302 | 2.302 | 2.302 | 2.302 | 0.0070173 | 0.0070173 | 0.0069552 | 0.0068931 | 0.0068165 | 0.0067543 | 0.006711 | 0.0066864 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532
| GCY014 | 3888 | 12.25 | 12.17 | 12.1 | 12.04 | 11.98 | 12.13 | 12.54 | 12.9 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 10.92 | 10.99 | 11.01 | 11.05 | 11.34 | 11.67 | 12.03 | 12.38 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 12.62 | 5.6595 | 5.672 | 5.6685 | 5.6735 | 5.766 | 5.904 | 6.0915 | 6.268 | 6.3895 | 6.3895 | 6.3895 | 6.3895 | 6.3895 | 6.3895 | 6.3895 | 6.3895 | 6.3895 | 6.3895 | 6.3895 | 6.3895 | 6.3895 | 0.0014556 | 0.0014588 | 0.0014579 | 0.0014592 | 0.001483 | 0.0015185 | 0.0015667 | 0.0016121 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434
| GCY021 | 278 | 2.66 | 2.65 | 2.63 | 2.6 | 2.57 | 2.54 | 2.53 | 2.52 | 2.49 | 2.49 | 2.49 | 2.49 | 2.49 | 2.49 | 2.49 | 2.49 | 2.49 | 2.49 | 2.49 | 2.49 | 2.49 | 2.39 | 2.39 | 2.37 | 2.34 | 2.31 | 2.29 | 2.27 | 2.26 | 2.24 | 2.24 | 2.24 | 2.24 | 2.24 | 2.24 | 2.24 | 2.24 | 2.24 | 2.24 | 2.24 | 2.24 | 2.24 | 1.2355 | 1.234 | 1.224 | 1.209 | 1.194 | 1.1825 | 1.174 | 1.169 | 1.1575 | 1.1575 | 1.1575 | 1.1575 | 1.1575 | 1.1575 | 1.1575 | 1.1575 | 1.1575 | 1.1575 | 1.1575 | 1.1575 | 1.1575 | 0.0044442 | 0.0044388 | 0.0044029 | 0.0043489 | 0.004295 | 0.0042536 | 0.004223 | 0.004205 | 0.0041637 | 0.0041637 | 0.0041637 | 0.0041637 | 0.0041637 | 0.0041637 | 0.0041637 | 0.0041637 | 0.0041637 | 0.0041637 | 0.0041637 | 0.0041637 | 0.0041637
| GCY022 | 522.5 | 6.6 | 6.61 | 6.57 | 6.51 | 6.42 | 6.36 | 6.34 | 6.34 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 5.53 | 5.52 | 5.48 | 5.42 | 5.34 | 5.29 | 5.28 | 5.28 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 5.23 | 2.9255 | 2.9235 | 2.9035 | 2.8735 | 2.832 | 2.8055 | 2.799 | 2.799 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 0.005599 | 0.0055952 | 0.0055569 | 0.0054995 | 0.0054201 | 0.0053694 | 0.0053569 | 0.0053569 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033
| GCY023 | 31 | 1.77 | 1.77 | 1.75 | 1.73 | 1.71 | 1.69 | 1.68 | 1.67 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.61 | 1.61 | 1.59 | 1.57 | 1.55 | 1.54 | 1.52 | 1.51 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 0.829 | 0.829 | 0.819 | 0.809 | 0.799 | 0.7925 | 0.784 | 0.779 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.774 | 0.026742 | 0.026742 | 0.026419 | 0.026097 | 0.025774 | 0.025565 | 0.02529 | 0.025129 | 0.024968 | 0.024968 | 0.024968 | 0.024968 | 0.024968 | 0.024968 | 0.024968 | 0.024968 | 0.024968 | 0.024968 | 0.024968 | 0.024968 | 0.024968
| GCY024 | 2452.5 | 8.16 | 8.18 | 8.17 | 8.15 | 8.12 | 8.09 | 8.12 | 8.24 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 7.6 | 7.61 | 7.57 | 7.55 | 7.5 | 7.48 | 7.48 | 7.59 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 3.884 | 3.8905 | 3.875 | 3.865 | 3.843 | 3.8315 | 3.836 | 3.8925 | 3.9475 | 3.9475 | 3.9475 | 3.9475 | 3.9475 | 3.9475 | 3.9475 | 3.9475 | 3.9475 | 3.9475 | 3.9475 | 3.9475 | 3.9475 | 0.0015837 | 0.0015863 | 0.00158 | 0.0015759 | 0.001567 | 0.0015623 | 0.0015641 | 0.0015872 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096
| GHP011 | 1380 | 10.88 | 11.14 | 11.37 | 11.56 | 11.66 | 11.82 | 12.16 | 12.51 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 12.74 | 9.94 | 10.2 | 10.4 | 10.58 | 10.68 | 10.84 | 11.15 | 11.5 | 11.79 | 11.79 | 11.79 | 11.79 | 11.79 | 11.79 | 11.79 | 11.79 | 11.79 | 11.79 | 11.79 | 11.79 | 11.79 | 5.111 | 5.241 | 5.3455 | 5.437 | 5.487 | 5.567 | 5.7265 | 5.9015 | 6.0375 | 6.0375 | 6.0375 | 6.0375 | 6.0375 | 6.0375 | 6.0375 | 6.0375 | 6.0375 | 6.0375 | 6.0375 | 6.0375 | 6.0375 | 0.0037036 | 0.0037978 | 0.0038736 | 0.0039399 | 0.0039761 | 0.0040341 | 0.0041496 | 0.0042764 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375
| GHP012 | 1800 | 9.76 | 9.95 | 10.08 | 10.19 | 10.24 | 10.34 | 10.51 | 10.66 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 9.05 | 9.2 | 9.34 | 9.44 | 9.51 | 9.57 | 9.73 | 9.92 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 4.6315 | 4.7125 | 4.781 | 4.8325 | 4.8645 | 4.9005 | 4.982 | 5.071 | 5.142 | 5.142 | 5.142 | 5.142 | 5.142 | 5.142 | 5.142 | 5.142 | 5.142 | 5.142 | 5.142 | 5.142 | 5.142 | 0.0025731 | 0.0026181 | 0.0026561 | 0.0026847 | 0.0027025 | 0.0027225 | 0.0027678 | 0.0028172 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567
| GHP021 | 1474 | 9.42 | 9.65 | 9.86 | 10.02 | 10.25 | 10.72 | 11.28 | 11.82 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 8.37 | 8.59 | 8.78 | 9.15 | 9.53 | 9.99 | 10.55 | 11.06 | 11.43 | 11.43 | 11.43 | 11.43 | 11.43 | 11.43 | 11.43 | 11.43 | 11.43 | 11.43 | 11.43 | 11.43 | 11.43 | 4.3425 | 4.454 | 4.552 | 4.7055 | 4.873 | 5.1045 | 5.3845 | 5.644 | 5.8275 | 5.8275 | 5.8275 | 5.8275 | 5.8275 | 5.8275 | 5.8275 | 5.8275 | 5.8275 | 5.8275 | 5.8275 | 5.8275 | 5.8275 | 0.0029461 | 0.0030217 | 0.0030882 | 0.0031923 | 0.003306 | 0.003463 | 0.003653 | 0.003829 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535
| GHP022 | 1056.5 | 6.64 | 6.75 | 6.83 | 6.9 | 6.93 | 6.98 | 7.28 | 7.59 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 6.13 | 6.24 | 6.32 | 6.39 | 6.42 | 6.66 | 7.01 | 7.31 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 3.1415 | 3.1965 | 3.2365 | 3.2715 | 3.2865 | 3.378 | 3.5455 | 3.697 | 3.7935 | 3.7935 | 3.7935 | 3.7935 | 3.7935 | 3.7935 | 3.7935 | 3.7935 | 3.7935 | 3.7935 | 3.7935 | 3.7935 | 3.7935 | 0.0029735 | 0.0030256 | 0.0030634 | 0.0030965 | 0.0031107 | 0.0031973 | 0.0033559 | 0.0034993 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906
| GL011 | 1109 | 7.87 | 8.21 | 8.14 | 8.07 | 8.05 | 8.1 | 8.18 | 8.24 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 8.27 | 7.69 | 7.8 | 7.82 | 7.85 | 7.87 | 7.92 | 7.99 | 8.04 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 3.872 | 3.9615 | 3.958 | 3.958 | 3.962 | 3.987 | 4.0235 | 4.05 | 4.0615 | 4.0615 | 4.0615 | 4.0615 | 4.0615 | 4.0615 | 4.0615 | 4.0615 | 4.0615 | 4.0615 | 4.0615 | 4.0615 | 4.0615 | 0.0034914 | 0.0035721 | 0.003569 | 0.003569 | 0.0035726 | 0.0035951 | 0.003628 | 0.0036519 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623
| GL012 | 2854.5 | 2.53 | 2.56 | 2.57 | 2.57 | 2.56 | 2.56 | 2.59 | 2.62 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.26 | 2.27 | 2.29 | 2.3 | 2.33 | 2.38 | 2.45 | 2.51 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 1.1705 | 1.1785 | 1.187 | 1.1905 | 1.1995 | 1.217 | 1.246 | 1.2715 | 1.288 | 1.288 | 1.288 | 1.288 | 1.288 | 1.288 | 1.288 | 1.288 | 1.288 | 1.288 | 1.288 | 1.288 | 1.288 | 0.00041005 | 0.00041286 | 0.00041583 | 0.00041706 | 0.00042021 | 0.00042634 | 0.0004365 | 0.00044544 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122
| GL013 | 2203 | 4.51 | 4.57 | 4.63 | 4.68 | 4.74 | 4.94 | 5.15 | 5.33 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46 | 4.12 | 4.19 | 4.25 | 4.34 | 4.5 | 4.69 | 4.9 | 5.07 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 2.1185 | 2.152 | 2.182 | 2.221 | 2.286 | 2.3825 | 2.4875 | 2.574 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 0.00096164 | 0.00097685 | 0.00099047 | 0.0010082 | 0.0010377 | 0.0010815 | 0.0011291 | 0.0011684 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979
| GL014 | 2959 | 4.94 | 5.03 | 5.1 | 5.24 | 5.44 | 5.67 | 5.91 | 6.12 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 4.48 | 4.57 | 4.75 | 4.94 | 5.13 | 5.34 | 5.57 | 5.76 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 2.309 | 2.354 | 2.4275 | 2.515 | 2.6115 | 2.7195 | 2.836 | 2.934 | 3.014 | 3.014 | 3.014 | 3.014 | 3.014 | 3.014 | 3.014 | 3.014 | 3.014 | 3.014 | 3.014 | 3.014 | 3.014 | 0.00078033 | 0.00079554 | 0.00082038 | 0.00084995 | 0.00088256 | 0.00091906 | 0.00095843 | 0.00099155 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186
| GL015 | 3591 | 4.82 | 4.92 | 5.13 | 5.3 | 5.46 | 5.66 | 5.89 | 6.1 | 6.22 | 6.22 | 6.22 | 6.22 | 6.22 | 6.22 | 6.22 | 6.22 | 6.22 | 6.22 | 6.22 | 6.22 | 6.22 | 4.38 | 4.48 | 4.57 | 4.64 | 4.7 | 4.91 | 5.13 | 5.33 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 2.256 | 2.306 | 2.369 | 2.419 | 2.464 | 2.5675 | 2.679 | 2.7805 | 2.8405 | 2.8405 | 2.8405 | 2.8405 | 2.8405 | 2.8405 | 2.8405 | 2.8405 | 2.8405 | 2.8405 | 2.8405 | 2.8405 | 2.8405 | 0.00062824 | 0.00064216 | 0.0006597 | 0.00067363 | 0.00068616 | 0.00071498 | 0.00074603 | 0.0007743 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101
| GL021 | 3383.5 | 6.23 | 6.31 | 6.38 | 6.42 | 6.42 | 6.43 | 6.5 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 5.19 | 5.25 | 5.31 | 5.34 | 5.35 | 5.38 | 5.58 | 5.75 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 5.85 | 2.751 | 2.784 | 2.8155 | 2.832 | 2.8355 | 2.8475 | 2.928 | 2.9995 | 3.0345 | 3.0345 | 3.0345 | 3.0345 | 3.0345 | 3.0345 | 3.0345 | 3.0345 | 3.0345 | 3.0345 | 3.0345 | 3.0345 | 3.0345 | 0.00081306 | 0.00082282 | 0.00083213 | 0.000837 | 0.00083804 | 0.00084158 | 0.00086538 | 0.00088651 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685
| GL022 | 3776 | 8.23 | 8.3 | 8.35 | 8.38 | 8.37 | 8.4 | 8.51 | 8.73 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 7.38 | 7.47 | 7.52 | 7.58 | 7.58 | 7.77 | 8.07 | 8.29 | 8.43 | 8.43 | 8.43 | 8.43 | 8.43 | 8.43 | 8.43 | 8.43 | 8.43 | 8.43 | 8.43 | 8.43 | 8.43 | 3.8175 | 3.8595 | 3.8845 | 3.91 | 3.9085 | 3.9795 | 4.101 | 4.211 | 4.2795 | 4.2795 | 4.2795 | 4.2795 | 4.2795 | 4.2795 | 4.2795 | 4.2795 | 4.2795 | 4.2795 | 4.2795 | 4.2795 | 4.2795 | 0.001011 | 0.0010221 | 0.0010287 | 0.0010355 | 0.0010351 | 0.0010539 | 0.0010861 | 0.0011152 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333
| GL023 | 2120.5 | 6.86 | 6.83 | 6.74 | 6.67 | 6.57 | 6.51 | 6.49 | 6.51 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 5.97 | 5.91 | 5.87 | 5.81 | 5.74 | 5.69 | 5.83 | 5.97 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 3.1185 | 3.093 | 3.0655 | 3.034 | 2.9945 | 2.968 | 3.014 | 3.066 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 0.0014706 | 0.0014586 | 0.0014456 | 0.0014308 | 0.0014122 | 0.0013997 | 0.0014214 | 0.0014459 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548
| GL024 | 1767.5 | 6.31 | 6.34 | 6.33 | 6.3 | 6.28 | 6.25 | 6.28 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 5.79 | 5.83 | 5.83 | 5.83 | 5.81 | 5.82 | 5.86 | 5.91 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 5.92 | 2.973 | 2.9915 | 2.99 | 2.9855 | 2.9755 | 2.9745 | 2.993 | 3.015 | 3.0185 | 3.0185 | 3.0185 | 3.0185 | 3.0185 | 3.0185 | 3.0185 | 3.0185 | 3.0185 | 3.0185 | 3.0185 | 3.0185 | 3.0185 | 0.001682 | 0.0016925 | 0.0016917 | 0.0016891 | 0.0016835 | 0.0016829 | 0.0016934 | 0.0017058 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078
| GLE011 | 359 | 3.88 | 3.86 | 3.85 | 3.83 | 3.79 | 3.79 | 3.81 | 3.82 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.77 | 3.53 | 3.51 | 3.51 | 3.49 | 3.45 | 3.45 | 3.47 | 3.48 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 1.8175 | 1.8075 | 1.806 | 1.796 | 1.776 | 1.776 | 1.786 | 1.791 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 0.0050627 | 0.0050348 | 0.0050306 | 0.0050028 | 0.0049471 | 0.0049471 | 0.0049749 | 0.0049889 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387
| GLE012 | 4727 | 10.14 | 10.2 | 10.27 | 10.58 | 10.9 | 11.27 | 11.68 | 12.04 | 12.32 | 12.32 | 12.32 | 12.32 | 12.32 | 12.32 | 12.32 | 12.32 | 12.32 | 12.32 | 12.32 | 12.32 | 12.32 | 9.42 | 9.53 | 9.76 | 10.08 | 10.4 | 10.76 | 11.16 | 11.5 | 11.77 | 11.77 | 11.77 | 11.77 | 11.77 | 11.77 | 11.77 | 11.77 | 11.77 | 11.77 | 11.77 | 11.77 | 11.77 | 4.818 | 4.8655 | 4.9565 | 5.115 | 5.275 | 5.4565 | 5.658 | 5.831 | 5.9675 | 5.9675 | 5.9675 | 5.9675 | 5.9675 | 5.9675 | 5.9675 | 5.9675 | 5.9675 | 5.9675 | 5.9675 | 5.9675 | 5.9675 | 0.0010193 | 0.0010293 | 0.0010486 | 0.0010821 | 0.0011159 | 0.0011543 | 0.001197 | 0.0012336 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624
| GLE013 | 6631.5 | 17.89 | 19.15 | 20.69 | 22.17 | 23.52 | 25.13 | 26.77 | 28.36 | 29.73 | 29.73 | 29.73 | 29.73 | 29.73 | 29.73 | 29.73 | 29.73 | 29.73 | 29.73 | 29.73 | 29.73 | 29.73 | 14.3 | 15.55 | 16.91 | 18.23 | 19.51 | 20.94 | 22.46 | 23.88 | 25.11 | 25.11 | 25.11 | 25.11 | 25.11 | 25.11 | 25.11 | 25.11 | 25.11 | 25.11 | 25.11 | 25.11 | 25.11 | 7.6885 | 8.315 | 9.022 | 9.706 | 10.3565 | 11.0985 | 11.8765 | 12.612 | 13.248 | 13.248 | 13.248 | 13.248 | 13.248 | 13.248 | 13.248 | 13.248 | 13.248 | 13.248 | 13.248 | 13.248 | 13.248 | 0.0011594 | 0.0012539 | 0.0013605 | 0.0014636 | 0.0015617 | 0.0016736 | 0.0017909 | 0.0019018 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977
| GLE021 | 602.5 | 5.77 | 5.84 | 5.87 | 5.88 | 5.82 | 5.88 | 6.02 | 6.13 | 6.06 | 6.06 | 6.06 | 6.06 | 6.06 | 6.06 | 6.06 | 6.06 | 6.06 | 6.06 | 6.06 | 6.06 | 6.06 | 5.53 | 5.57 | 5.66 | 5.68 | 5.66 | 5.72 | 5.86 | 5.97 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 2.801 | 2.8255 | 2.8615 | 2.87 | 2.854 | 2.884 | 2.954 | 3.009 | 2.974 | 2.974 | 2.974 | 2.974 | 2.974 | 2.974 | 2.974 | 2.974 | 2.974 | 2.974 | 2.974 | 2.974 | 2.974 | 0.004649 | 0.0046896 | 0.0047494 | 0.0047635 | 0.0047369 | 0.0047867 | 0.0049029 | 0.0049942 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361
| GLE023 | 1 | 2.44 | 2.45 | 2.43 | 2.41 | 2.39 | 2.36 | 2.35 | 2.34 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.32 | 2.33 | 2.31 | 2.29 | 2.26 | 2.25 | 2.23 | 2.22 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 1.178 | 1.183 | 1.173 | 1.163 | 1.1495 | 1.1415 | 1.133 | 1.128 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.178 | 1.183 | 1.173 | 1.163 | 1.1495 | 1.1415 | 1.133 | 1.128 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123
| GLE024 | 4883.5 | 12.34 | 12.62 | 12.69 | 12.73 | 12.71 | 12.72 | 12.83 | 12.97 | 13.02 | 13.02 | 13.02 | 13.02 | 13.02 | 13.02 | 13.02 | 13.02 | 13.02 | 13.02 | 13.02 | 13.02 | 13.02 | 11.27 | 11.55 | 11.61 | 11.65 | 11.63 | 11.61 | 11.73 | 12.01 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 5.7955 | 5.9355 | 5.967 | 5.987 | 5.977 | 5.9715 | 6.03 | 6.149 | 6.223 | 6.223 | 6.223 | 6.223 | 6.223 | 6.223 | 6.223 | 6.223 | 6.223 | 6.223 | 6.223 | 6.223 | 6.223 | 0.0011868 | 0.0012154 | 0.0012219 | 0.001226 | 0.0012239 | 0.0012228 | 0.0012348 | 0.0012591 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743
| GLE031 | 3592 | 11.01 | 11.48 | 11.41 | 11.34 | 11.33 | 11.44 | 11.62 | 11.77 | 11.83 | 11.83 | 11.83 | 11.83 | 11.83 | 11.83 | 11.83 | 11.83 | 11.83 | 11.83 | 11.83 | 11.83 | 11.83 | 10.39 | 10.55 | 10.63 | 10.69 | 10.73 | 10.84 | 11.02 | 11.17 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 5.288 | 5.4145 | 5.432 | 5.4425 | 5.455 | 5.51 | 5.6 | 5.675 | 5.7085 | 5.7085 | 5.7085 | 5.7085 | 5.7085 | 5.7085 | 5.7085 | 5.7085 | 5.7085 | 5.7085 | 5.7085 | 5.7085 | 5.7085 | 0.0014722 | 0.0015074 | 0.0015122 | 0.0015152 | 0.0015187 | 0.001534 | 0.001559 | 0.0015799 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892
| GLE032 | 2766 | 9.1 | 9.29 | 9.41 | 9.53 | 9.62 | 9.76 | 9.94 | 10.08 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 8.64 | 8.83 | 8.96 | 9.07 | 9.17 | 9.31 | 9.48 | 9.62 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 4.389 | 4.484 | 4.5475 | 4.604 | 4.6525 | 4.7225 | 4.809 | 4.879 | 4.904 | 4.904 | 4.904 | 4.904 | 4.904 | 4.904 | 4.904 | 4.904 | 4.904 | 4.904 | 4.904 | 4.904 | 4.904 | 0.0015868 | 0.0016211 | 0.0016441 | 0.0016645 | 0.001682 | 0.0017073 | 0.0017386 | 0.0017639 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773
| GLE033 | 573.5 | 4.21 | 4.21 | 4.21 | 4.19 | 4.17 | 4.18 | 4.21 | 4.23 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 3.96 | 3.95 | 3.95 | 3.94 | 3.92 | 3.92 | 3.95 | 3.97 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 2.0175 | 2.014 | 2.014 | 2.0075 | 1.9975 | 1.999 | 2.014 | 2.024 | 2.014 | 2.014 | 2.014 | 2.014 | 2.014 | 2.014 | 2.014 | 2.014 | 2.014 | 2.014 | 2.014 | 2.014 | 2.014 | 0.0035179 | 0.0035118 | 0.0035118 | 0.0035004 | 0.003483 | 0.0034856 | 0.0035118 | 0.0035292 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118
| GSB011 | 2553 | 7.39 | 7.5 | 7.61 | 7.8 | 8 | 8.24 | 8.54 | 8.8 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 8.98 | 6.9 | 7.09 | 7.32 | 7.53 | 7.73 | 7.98 | 8.27 | 8.52 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 3.5235 | 3.6065 | 3.7035 | 3.8055 | 3.9055 | 4.029 | 4.1755 | 4.302 | 4.392 | 4.392 | 4.392 | 4.392 | 4.392 | 4.392 | 4.392 | 4.392 | 4.392 | 4.392 | 4.392 | 4.392 | 4.392 | 0.0013801 | 0.0014127 | 0.0014506 | 0.0014906 | 0.0015298 | 0.0015781 | 0.0016355 | 0.0016851 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203
| GSB012 | 2218 | 10.4 | 10.71 | 11.08 | 11.4 | 11.7 | 12.09 | 12.56 | 12.97 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 13.23 | 10 | 10.3 | 10.67 | 10.99 | 11.28 | 11.66 | 12.11 | 12.52 | 12.78 | 12.78 | 12.78 | 12.78 | 12.78 | 12.78 | 12.78 | 12.78 | 12.78 | 12.78 | 12.78 | 12.78 | 12.78 | 5.06 | 5.2115 | 5.3965 | 5.5565 | 5.703 | 5.8945 | 6.1225 | 6.3275 | 6.4575 | 6.4575 | 6.4575 | 6.4575 | 6.4575 | 6.4575 | 6.4575 | 6.4575 | 6.4575 | 6.4575 | 6.4575 | 6.4575 | 6.4575 | 0.0022813 | 0.0023496 | 0.002433 | 0.0025052 | 0.0025712 | 0.0026576 | 0.0027604 | 0.0028528 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114
| GSB013 | 2829.5 | 10.07 | 10.31 | 10.47 | 10.61 | 10.89 | 11.23 | 11.64 | 12 | 12.24 | 12.24 | 12.24 | 12.24 | 12.24 | 12.24 | 12.24 | 12.24 | 12.24 | 12.24 | 12.24 | 12.24 | 12.24 | 8.37 | 8.58 | 8.68 | 8.95 | 9.22 | 9.54 | 9.9 | 10.24 | 10.48 | 10.48 | 10.48 | 10.48 | 10.48 | 10.48 | 10.48 | 10.48 | 10.48 | 10.48 | 10.48 | 10.48 | 10.48 | 4.44 | 4.5495 | 4.6085 | 4.724 | 4.8605 | 5.0235 | 5.211 | 5.384 | 5.504 | 5.504 | 5.504 | 5.504 | 5.504 | 5.504 | 5.504 | 5.504 | 5.504 | 5.504 | 5.504 | 5.504 | 5.504 | 0.0015692 | 0.0016079 | 0.0016287 | 0.0016696 | 0.0017178 | 0.0017754 | 0.0018417 | 0.0019028 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452
| GSB014 | 2108.5 | 5.62 | 5.73 | 5.85 | 5.96 | 6.06 | 6.2 | 6.38 | 6.53 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 5.44 | 5.54 | 5.66 | 5.77 | 5.86 | 5.99 | 6.16 | 6.3 | 6.37 | 6.37 | 6.37 | 6.37 | 6.37 | 6.37 | 6.37 | 6.37 | 6.37 | 6.37 | 6.37 | 6.37 | 6.37 | 2.747 | 2.7985 | 2.8585 | 2.9135 | 2.96 | 3.0265 | 3.113 | 3.1845 | 3.2195 | 3.2195 | 3.2195 | 3.2195 | 3.2195 | 3.2195 | 3.2195 | 3.2195 | 3.2195 | 3.2195 | 3.2195 | 3.2195 | 3.2195 | 0.0013028 | 0.0013272 | 0.0013557 | 0.0013818 | 0.0014038 | 0.0014354 | 0.0014764 | 0.0015103 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269
| HSM001 | 1135 | 4.95 | 4.92 | 4.9 | 4.86 | 4.79 | 4.76 | 4.78 | 4.78 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.71 | 4.24 | 4.21 | 4.2 | 4.17 | 4.12 | 4.1 | 4.1 | 4.1 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 4.03 | 2.2265 | 2.2115 | 2.205 | 2.1885 | 2.1605 | 2.149 | 2.152 | 2.152 | 2.117 | 2.117 | 2.117 | 2.117 | 2.117 | 2.117 | 2.117 | 2.117 | 2.117 | 2.117 | 2.117 | 2.117 | 2.117 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652
| HSM002 | 1394 | 3.47 | 3.47 | 3.48 | 3.47 | 3.43 | 3.4 | 3.41 | 3.42 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.22 | 3.23 | 3.23 | 3.21 | 3.17 | 3.15 | 3.15 | 3.16 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 1.6475 | 1.651 | 1.6525 | 1.644 | 1.624 | 1.6125 | 1.614 | 1.619 | 1.6025 | 1.6025 | 1.6025 | 1.6025 | 1.6025 | 1.6025 | 1.6025 | 1.6025 | 1.6025 | 1.6025 | 1.6025 | 1.6025 | 1.6025 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496
| HSM003 | 1601.5 | 6.22 | 6.37 | 6.38 | 6.37 | 6.31 | 6.27 | 6.29 | 6.33 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 5.54 | 5.66 | 5.68 | 5.67 | 5.62 | 5.59 | 5.62 | 5.66 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 2.872 | 2.9365 | 2.945 | 2.94 | 2.9135 | 2.897 | 2.9105 | 2.9305 | 2.904 | 2.904 | 2.904 | 2.904 | 2.904 | 2.904 | 2.904 | 2.904 | 2.904 | 2.904 | 2.904 | 2.904 | 2.904 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133
| HSM004 | 2062.5 | 5.34 | 5.33 | 5.33 | 5.3 | 5.22 | 5.17 | 5.16 | 5.17 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 4.96 | 4.97 | 4.96 | 4.94 | 4.87 | 4.81 | 4.81 | 4.82 | 4.75 | 4.75 | 4.75 | 4.75 | 4.75 | 4.75 | 4.75 | 4.75 | 4.75 | 4.75 | 4.75 | 4.75 | 4.75 | 2.537 | 2.539 | 2.5355 | 2.524 | 2.4875 | 2.459 | 2.4575 | 2.4625 | 2.4275 | 2.4275 | 2.4275 | 2.4275 | 2.4275 | 2.4275 | 2.4275 | 2.4275 | 2.4275 | 2.4275 | 2.4275 | 2.4275 | 2.4275 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177
| HSM005 | 1665.5 | 5.84 | 5.9 | 5.86 | 5.8 | 5.72 | 5.67 | 5.65 | 5.63 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.49 | 5.56 | 5.54 | 5.5 | 5.43 | 5.38 | 5.36 | 5.34 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 5.29 | 2.7975 | 2.831 | 2.818 | 2.795 | 2.7585 | 2.7335 | 2.7235 | 2.7135 | 2.687 | 2.687 | 2.687 | 2.687 | 2.687 | 2.687 | 2.687 | 2.687 | 2.687 | 2.687 | 2.687 | 2.687 | 2.687 | 0.0016797 | 0.0016998 | 0.001692 | 0.0016782 | 0.0016563 | 0.0016412 | 0.0016352 | 0.0016292 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133
| HSM006 | 2923.5 | 8.92 | 8.93 | 8.9 | 8.82 | 8.71 | 8.63 | 8.63 | 8.65 | 8.58 | 8.58 | 8.58 | 8.58 | 8.58 | 8.58 | 8.58 | 8.58 | 8.58 | 8.58 | 8.58 | 8.58 | 8.58 | 8.19 | 8.18 | 8.14 | 8.08 | 7.98 | 7.91 | 7.9 | 7.91 | 7.84 | 7.84 | 7.84 | 7.84 | 7.84 | 7.84 | 7.84 | 7.84 | 7.84 | 7.84 | 7.84 | 7.84 | 7.84 | 4.2045 | 4.2025 | 4.184 | 4.151 | 4.0995 | 4.063 | 4.0595 | 4.066 | 4.031 | 4.031 | 4.031 | 4.031 | 4.031 | 4.031 | 4.031 | 4.031 | 4.031 | 4.031 | 4.031 | 4.031 | 4.031 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788
| HSM009 | 3347.5 | 7.77 | 7.79 | 7.78 | 7.76 | 7.69 | 7.7 | 7.86 | 8 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 7.25 | 7.25 | 7.25 | 7.21 | 7.15 | 7.12 | 7.14 | 7.21 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 3.703 | 3.706 | 3.7045 | 3.6875 | 3.656 | 3.647 | 3.678 | 3.7235 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 0.0011062 | 0.0011071 | 0.0011066 | 0.0011016 | 0.0010922 | 0.0010895 | 0.0010987 | 0.0011123 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214
| HSM010 | 3229 | 10.11 | 10.02 | 9.9 | 9.68 | 9.51 | 9.36 | 9.46 | 9.52 | 9.48 | 9.48 | 9.48 | 9.48 | 9.48 | 9.48 | 9.48 | 9.48 | 9.48 | 9.48 | 9.48 | 9.48 | 9.48 | 9.03 | 8.98 | 8.99 | 8.97 | 8.94 | 8.98 | 9.08 | 9.15 | 9.11 | 9.11 | 9.11 | 9.11 | 9.11 | 9.11 | 9.11 | 9.11 | 9.11 | 9.11 | 9.11 | 9.11 | 9.11 | 4.677 | 4.646 | 4.6315 | 4.5915 | 4.5555 | 4.547 | 4.597 | 4.6305 | 4.6105 | 4.6105 | 4.6105 | 4.6105 | 4.6105 | 4.6105 | 4.6105 | 4.6105 | 4.6105 | 4.6105 | 4.6105 | 4.6105 | 4.6105 | 0.0014484 | 0.0014388 | 0.0014343 | 0.001422 | 0.0014108 | 0.0014082 | 0.0014237 | 0.001434 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278
| HTN011 | 776 | 1.4 | 1.42 | 1.43 | 1.43 | 1.42 | 1.41 | 1.43 | 1.46 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.31 | 1.32 | 1.33 | 1.33 | 1.32 | 1.33 | 1.36 | 1.37 | 1.35 | 1.35 | 1.35 | 1.35 | 1.35 | 1.35 | 1.35 | 1.35 | 1.35 | 1.35 | 1.35 | 1.35 | 1.35 | 0.6685 | 0.675 | 0.68 | 0.68 | 0.675 | 0.677 | 0.6905 | 0.6985 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918
| HTN012 | 1859 | 3.41 | 3.43 | 3.43 | 3.42 | 3.38 | 3.36 | 3.37 | 3.38 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.35 | 3.05 | 3.06 | 3.08 | 3.08 | 3.06 | 3.08 | 3.11 | 3.14 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 1.579 | 1.5855 | 1.5925 | 1.591 | 1.578 | 1.582 | 1.594 | 1.606 | 1.591 | 1.591 | 1.591 | 1.591 | 1.591 | 1.591 | 1.591 | 1.591 | 1.591 | 1.591 | 1.591 | 1.591 | 1.591 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584
| HTN013 | 2423 | 5.43 | 5.43 | 5.39 | 5.35 | 5.29 | 5.23 | 5.22 | 5.22 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 5.16 | 4.9 | 4.9 | 4.88 | 4.85 | 4.78 | 4.74 | 4.73 | 4.74 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 4.69 | 2.5295 | 2.5295 | 2.5165 | 2.5 | 2.4665 | 2.4435 | 2.4385 | 2.442 | 2.4155 | 2.4155 | 2.4155 | 2.4155 | 2.4155 | 2.4155 | 2.4155 | 2.4155 | 2.4155 | 2.4155 | 2.4155 | 2.4155 | 2.4155 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969
| HTN032 | 3106 | 7.13 | 7.12 | 7.17 | 7.18 | 7.18 | 7.22 | 7.34 | 7.42 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 6.47 | 6.46 | 6.53 | 6.57 | 6.6 | 6.68 | 6.8 | 6.9 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 3.334 | 3.329 | 3.361 | 3.3765 | 3.387 | 3.421 | 3.481 | 3.528 | 3.5185 | 3.5185 | 3.5185 | 3.5185 | 3.5185 | 3.5185 | 3.5185 | 3.5185 | 3.5185 | 3.5185 | 3.5185 | 3.5185 | 3.5185 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328
| HTN033 | 3372.5 | 8.2 | 8.16 | 8.1 | 8.04 | 7.94 | 7.85 | 7.83 | 7.82 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.28 | 7.26 | 7.21 | 7.13 | 7.04 | 7.07 | 7.18 | 7.26 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 3.778 | 3.765 | 3.7385 | 3.7015 | 3.655 | 3.652 | 3.6875 | 3.714 | 3.7105 | 3.7105 | 3.7105 | 3.7105 | 3.7105 | 3.7105 | 3.7105 | 3.7105 | 3.7105 | 3.7105 | 3.7105 | 3.7105 | 3.7105 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002
| HTN034 | 1853 | 3.75 | 3.78 | 3.79 | 3.77 | 3.73 | 3.7 | 3.72 | 3.74 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.25 | 3.26 | 3.27 | 3.26 | 3.22 | 3.2 | 3.21 | 3.23 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 1.7 | 1.708 | 1.713 | 1.7065 | 1.6865 | 1.675 | 1.6815 | 1.6915 | 1.6715 | 1.6715 | 1.6715 | 1.6715 | 1.6715 | 1.6715 | 1.6715 | 1.6715 | 1.6715 | 1.6715 | 1.6715 | 1.6715 | 1.6715 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205
| HYT011 | 164.5 | 2.78 | 2.81 | 2.87 | 2.87 | 2.86 | 2.89 | 2.97 | 3.02 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.41 | 2.44 | 2.49 | 2.5 | 2.48 | 2.51 | 2.58 | 2.63 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 2.56 | 1.2605 | 1.2755 | 1.302 | 1.3055 | 1.297 | 1.312 | 1.3485 | 1.3735 | 1.3445 | 1.3445 | 1.3445 | 1.3445 | 1.3445 | 1.3445 | 1.3445 | 1.3445 | 1.3445 | 1.3445 | 1.3445 | 1.3445 | 1.3445 | 0.0076626 | 0.0077538 | 0.0079149 | 0.0079362 | 0.0078845 | 0.0079757 | 0.0081976 | 0.0083495 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733
| KGT002 | 2268.5 | 6.94 | 6.96 | 6.93 | 6.9 | 6.82 | 6.77 | 6.77 | 6.78 | 6.73 | 6.73 | 6.73 | 6.73 | 6.73 | 6.73 | 6.73 | 6.73 | 6.73 | 6.73 | 6.73 | 6.73 | 6.73 | 6.27 | 6.27 | 6.23 | 6.2 | 6.12 | 6.05 | 6.05 | 6.06 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 3.2355 | 3.2385 | 3.22 | 3.205 | 3.165 | 3.133 | 3.133 | 3.138 | 3.1095 | 3.1095 | 3.1095 | 3.1095 | 3.1095 | 3.1095 | 3.1095 | 3.1095 | 3.1095 | 3.1095 | 3.1095 | 3.1095 | 3.1095 | 0.0014263 | 0.0014276 | 0.0014194 | 0.0014128 | 0.0013952 | 0.0013811 | 0.0013811 | 0.0013833 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707
| KGT003 | 1306 | 4.25 | 4.3 | 4.33 | 4.33 | 4.29 | 4.27 | 4.31 | 4.36 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 4.32 | 3.91 | 3.95 | 3.97 | 3.98 | 3.95 | 3.93 | 3.97 | 4.03 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 3.99 | 2.006 | 2.0275 | 2.039 | 2.0425 | 2.026 | 2.016 | 2.036 | 2.0645 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655
| KGT004 | 1477 | 5.46 | 5.5 | 5.5 | 5.49 | 5.41 | 5.36 | 5.39 | 5.43 | 5.38 | 5.38 | 5.38 | 5.38 | 5.38 | 5.38 | 5.38 | 5.38 | 5.38 | 5.38 | 5.38 | 5.38 | 5.38 | 5.01 | 5.04 | 5.04 | 5.03 | 4.96 | 4.92 | 4.93 | 4.97 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 2.5725 | 2.589 | 2.589 | 2.584 | 2.5475 | 2.526 | 2.534 | 2.554 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123
| KRT012 | 1182.5 | 3.21 | 3.25 | 3.29 | 3.31 | 3.3 | 3.3 | 3.36 | 3.42 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 2.97 | 3 | 3.05 | 3.06 | 3.06 | 3.09 | 3.17 | 3.22 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 1.521 | 1.5375 | 1.561 | 1.5675 | 1.566 | 1.5765 | 1.6135 | 1.64 | 1.623 | 1.623 | 1.623 | 1.623 | 1.623 | 1.623 | 1.623 | 1.623 | 1.623 | 1.623 | 1.623 | 1.623 | 1.623 | 0.0012863 | 0.0013002 | 0.0013201 | 0.0013256 | 0.0013243 | 0.0013332 | 0.0013645 | 0.0013869 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725
| KRT013 | 2512 | 7.05 | 7.08 | 7.1 | 7.09 | 7.03 | 7.01 | 7.07 | 7.24 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 6.6 | 6.64 | 6.66 | 6.65 | 6.59 | 6.59 | 6.77 | 6.93 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 3.3675 | 3.386 | 3.396 | 3.391 | 3.361 | 3.358 | 3.43 | 3.5115 | 3.5215 | 3.5215 | 3.5215 | 3.5215 | 3.5215 | 3.5215 | 3.5215 | 3.5215 | 3.5215 | 3.5215 | 3.5215 | 3.5215 | 3.5215 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019
| KRT022 | 3037 | 10.21 | 10.28 | 10.4 | 10.49 | 10.53 | 10.65 | 10.84 | 11 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 7.08 | 7.16 | 7.3 | 7.44 | 7.55 | 7.72 | 7.93 | 8.11 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 4.0095 | 4.048 | 4.115 | 4.1775 | 4.222 | 4.2995 | 4.4015 | 4.4885 | 4.523 | 4.523 | 4.523 | 4.523 | 4.523 | 4.523 | 4.523 | 4.523 | 4.523 | 4.523 | 4.523 | 4.523 | 4.523 | 0.0013202 | 0.0013329 | 0.001355 | 0.0013755 | 0.0013902 | 0.0014157 | 0.0014493 | 0.0014779 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893
| KRT023 | 1792 | 9.08 | 9.12 | 9.09 | 9.08 | 9.16 | 9.32 | 9.49 | 9.66 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 8.33 | 8.34 | 8.41 | 8.47 | 8.54 | 8.68 | 8.87 | 9.01 | 9.09 | 9.09 | 9.09 | 9.09 | 9.09 | 9.09 | 9.09 | 9.09 | 9.09 | 9.09 | 9.09 | 9.09 | 9.09 | 4.2775 | 4.287 | 4.307 | 4.3265 | 4.363 | 4.436 | 4.528 | 4.6025 | 4.6455 | 4.6455 | 4.6455 | 4.6455 | 4.6455 | 4.6455 | 4.6455 | 4.6455 | 4.6455 | 4.6455 | 4.6455 | 4.6455 | 4.6455 | 0.002387 | 0.0023923 | 0.0024035 | 0.0024143 | 0.0024347 | 0.0024754 | 0.0025268 | 0.0025684 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924
| KRT031 | 166 | 16.82 | 16.98 | 16.82 | 16.65 | 16.49 | 16.35 | 16.25 | 16.17 | 16.07 | 16.07 | 16.07 | 16.07 | 16.07 | 16.07 | 16.07 | 16.07 | 16.07 | 16.07 | 16.07 | 16.07 | 16.07 | 11.44 | 11.57 | 11.44 | 11.33 | 11.22 | 11.13 | 11.07 | 11.02 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 6.527 | 6.5965 | 6.527 | 6.463 | 6.4005 | 6.348 | 6.312 | 6.2825 | 6.243 | 6.243 | 6.243 | 6.243 | 6.243 | 6.243 | 6.243 | 6.243 | 6.243 | 6.243 | 6.243 | 6.243 | 6.243 | 0.039319 | 0.039738 | 0.039319 | 0.038934 | 0.038557 | 0.038241 | 0.038024 | 0.037846 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608
| KYM001 | 593 | 7.67 | 7.71 | 7.65 | 7.6 | 7.5 | 7.41 | 7.39 | 7.41 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 7.38 | 6.49 | 6.56 | 6.52 | 6.47 | 6.39 | 6.32 | 6.3 | 6.31 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 3.422 | 3.4525 | 3.4295 | 3.4045 | 3.3615 | 3.3235 | 3.3135 | 3.32 | 3.3015 | 3.3015 | 3.3015 | 3.3015 | 3.3015 | 3.3015 | 3.3015 | 3.3015 | 3.3015 | 3.3015 | 3.3015 | 3.3015 | 3.3015 | 0.0057707 | 0.0058221 | 0.0057833 | 0.0057411 | 0.0056686 | 0.0056046 | 0.0055877 | 0.0055987 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675
| KYM002 | 1071.5 | 5.28 | 5.21 | 5.09 | 5.01 | 4.9 | 4.82 | 4.76 | 4.72 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.67 | 4.11 | 4.11 | 4.07 | 4.02 | 3.96 | 3.91 | 3.89 | 3.87 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 2.2305 | 2.22 | 2.188 | 2.1585 | 2.121 | 2.0915 | 2.0755 | 2.0625 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 2.0445 | 0.0020817 | 0.0020719 | 0.002042 | 0.0020145 | 0.0019795 | 0.0019519 | 0.001937 | 0.0019249 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081
| KYM003 | 1159 | 4.8 | 4.82 | 4.85 | 4.85 | 4.79 | 4.77 | 4.82 | 4.89 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.48 | 4.51 | 4.54 | 4.55 | 4.5 | 4.48 | 4.53 | 4.59 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 4.55 | 2.288 | 2.3015 | 2.3165 | 2.32 | 2.2935 | 2.2835 | 2.3085 | 2.34 | 2.3185 | 2.3185 | 2.3185 | 2.3185 | 2.3185 | 2.3185 | 2.3185 | 2.3185 | 2.3185 | 2.3185 | 2.3185 | 2.3185 | 2.3185 | 0.0019741 | 0.0019858 | 0.0019987 | 0.0020017 | 0.0019789 | 0.0019702 | 0.0019918 | 0.002019 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004
| KYM004 | 1528 | 6.05 | 6.11 | 6.15 | 6.15 | 6.09 | 6.07 | 6.13 | 6.23 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 6.18 | 5.64 | 5.69 | 5.72 | 5.71 | 5.65 | 5.62 | 5.69 | 5.77 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 5.73 | 2.8815 | 2.908 | 2.9245 | 2.921 | 2.891 | 2.8775 | 2.911 | 2.954 | 2.9325 | 2.9325 | 2.9325 | 2.9325 | 2.9325 | 2.9325 | 2.9325 | 2.9325 | 2.9325 | 2.9325 | 2.9325 | 2.9325 | 2.9325 | 0.0018858 | 0.0019031 | 0.0019139 | 0.0019116 | 0.001892 | 0.0018832 | 0.0019051 | 0.0019332 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192
| KYM005 | 2032.5 | 5.89 | 5.91 | 5.9 | 5.88 | 5.82 | 5.78 | 5.79 | 5.81 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.77 | 5.42 | 5.43 | 5.43 | 5.41 | 5.35 | 5.32 | 5.32 | 5.34 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 2.7805 | 2.787 | 2.7855 | 2.7755 | 2.7455 | 2.729 | 2.7305 | 2.7405 | 2.7205 | 2.7205 | 2.7205 | 2.7205 | 2.7205 | 2.7205 | 2.7205 | 2.7205 | 2.7205 | 2.7205 | 2.7205 | 2.7205 | 2.7205 | 0.001368 | 0.0013712 | 0.0013705 | 0.0013656 | 0.0013508 | 0.0013427 | 0.0013434 | 0.0013483 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385
| KYM006 | 474 | 7.38 | 7.36 | 7.26 | 7.17 | 7.04 | 6.94 | 6.89 | 6.84 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.21 | 6.2 | 6.12 | 6.04 | 5.94 | 5.85 | 5.81 | 5.78 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 3.2805 | 3.274 | 3.231 | 3.1895 | 3.135 | 3.0885 | 3.067 | 3.049 | 3.0145 | 3.0145 | 3.0145 | 3.0145 | 3.0145 | 3.0145 | 3.0145 | 3.0145 | 3.0145 | 3.0145 | 3.0145 | 3.0145 | 3.0145 | 0.0069209 | 0.0069072 | 0.0068165 | 0.0067289 | 0.0066139 | 0.0065158 | 0.0064705 | 0.0064325 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597
| LV001 | 5658 | 14.55 | 10.3 | 10.38 | 10.45 | 10.48 | 10.53 | 10.64 | 10.74 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 12.96 | 9.18 | 9.26 | 9.32 | 9.33 | 9.38 | 9.48 | 9.6 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 9.67 | 6.7185 | 4.758 | 4.798 | 4.8295 | 4.8375 | 4.8625 | 4.914 | 4.971 | 5.0105 | 5.0105 | 5.0105 | 5.0105 | 5.0105 | 5.0105 | 5.0105 | 5.0105 | 5.0105 | 5.0105 | 5.0105 | 5.0105 | 5.0105 | 0.0011874 | 0.00084093 | 0.000848 | 0.00085357 | 0.00085498 | 0.0008594 | 0.0008685 | 0.00087858 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556
| LV002 | 6571.5 | 16.53 | 16.91 | 17.25 | 17.57 | 17.81 | 18.08 | 18.5 | 19 | 19.31 | 19.31 | 19.31 | 19.31 | 19.31 | 19.31 | 19.31 | 19.31 | 19.31 | 19.31 | 19.31 | 19.31 | 19.31 | 14.3 | 14.6 | 14.91 | 15.24 | 15.5 | 15.84 | 16.52 | 17.34 | 18.03 | 18.03 | 18.03 | 18.03 | 18.03 | 18.03 | 18.03 | 18.03 | 18.03 | 18.03 | 18.03 | 18.03 | 18.03 | 7.4845 | 7.6465 | 7.806 | 7.9695 | 8.0965 | 8.256 | 8.557 | 8.919 | 9.207 | 9.207 | 9.207 | 9.207 | 9.207 | 9.207 | 9.207 | 9.207 | 9.207 | 9.207 | 9.207 | 9.207 | 9.207 | 0.0011389 | 0.0011636 | 0.0011879 | 0.0012127 | 0.0012321 | 0.0012563 | 0.0013021 | 0.0013572 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011
| LV003 | 4752 | 14.7 | 12.69 | 13.26 | 13.76 | 14.22 | 14.76 | 15.37 | 16 | 16.39 | 16.39 | 16.39 | 16.39 | 16.39 | 16.39 | 16.39 | 16.39 | 16.39 | 16.39 | 16.39 | 16.39 | 16.39 | 13.34 | 11.79 | 12.2 | 12.55 | 12.86 | 13.21 | 13.65 | 14.14 | 14.47 | 14.47 | 14.47 | 14.47 | 14.47 | 14.47 | 14.47 | 14.47 | 14.47 | 14.47 | 14.47 | 14.47 | 14.47 | 6.874 | 6.03 | 6.259 | 6.4565 | 6.634 | 6.8375 | 7.083 | 7.349 | 7.523 | 7.523 | 7.523 | 7.523 | 7.523 | 7.523 | 7.523 | 7.523 | 7.523 | 7.523 | 7.523 | 7.523 | 7.523 | 0.0014465 | 0.0012689 | 0.0013171 | 0.0013587 | 0.001396 | 0.0014389 | 0.0014905 | 0.0015465 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831
| LV004 | 6072 | 15.84 | 16.27 | 16.64 | 17.04 | 17.37 | 17.74 | 18.22 | 18.71 | 19.13 | 19.13 | 19.13 | 19.13 | 19.13 | 19.13 | 19.13 | 19.13 | 19.13 | 19.13 | 19.13 | 19.13 | 19.13 | 14.28 | 14.69 | 15.08 | 15.43 | 15.75 | 16.08 | 16.52 | 17 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 17.62 | 7.374 | 7.582 | 7.774 | 7.9565 | 8.118 | 8.289 | 8.515 | 8.7565 | 9.0365 | 9.0365 | 9.0365 | 9.0365 | 9.0365 | 9.0365 | 9.0365 | 9.0365 | 9.0365 | 9.0365 | 9.0365 | 9.0365 | 9.0365 | 0.0012144 | 0.0012487 | 0.0012803 | 0.0013104 | 0.001337 | 0.0013651 | 0.0014023 | 0.0014421 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882
| LV005 | 1747.5 | 20.35 | 21.51 | 22.16 | 22.76 | 23.21 | 23.82 | 25.17 | 26.59 | 27.72 | 27.72 | 27.72 | 27.72 | 27.72 | 27.72 | 27.72 | 27.72 | 27.72 | 27.72 | 27.72 | 27.72 | 27.72 | 18.19 | 19.38 | 20 | 20.57 | 21.05 | 22.34 | 23.74 | 25.06 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 9.419 | 10.0095 | 10.324 | 10.6135 | 10.849 | 11.392 | 12.0845 | 12.7595 | 13.2965 | 13.2965 | 13.2965 | 13.2965 | 13.2965 | 13.2965 | 13.2965 | 13.2965 | 13.2965 | 13.2965 | 13.2965 | 13.2965 | 13.2965 | 0.00539 | 0.0057279 | 0.0059079 | 0.0060735 | 0.0062083 | 0.006519 | 0.0069153 | 0.0073016 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089
| LV006 | 5844 | 4.32 | 4.74 | 4.89 | 5.07 | 5.25 | 5.46 | 5.68 | 5.88 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 6.04 | 4.05 | 4.48 | 4.6 | 4.78 | 4.95 | 5.13 | 5.33 | 5.51 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 5.66 | 2.0655 | 2.279 | 2.3435 | 2.4335 | 2.52 | 2.6145 | 2.7175 | 2.8105 | 2.887 | 2.887 | 2.887 | 2.887 | 2.887 | 2.887 | 2.887 | 2.887 | 2.887 | 2.887 | 2.887 | 2.887 | 2.887 | 0.00035344 | 0.00038997 | 0.00040101 | 0.00041641 | 0.00043121 | 0.00044738 | 0.00046501 | 0.00048092 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401
| LV007 | 3474.5 | 11.51 | 12.66 | 13.11 | 13.54 | 13.87 | 14.25 | 14.73 | 15.23 | 15.58 | 15.58 | 15.58 | 15.58 | 15.58 | 15.58 | 15.58 | 15.58 | 15.58 | 15.58 | 15.58 | 15.58 | 15.58 | 9.98 | 11.02 | 11.41 | 11.77 | 12.04 | 12.59 | 13.4 | 14.17 | 14.74 | 14.74 | 14.74 | 14.74 | 14.74 | 14.74 | 14.74 | 14.74 | 14.74 | 14.74 | 14.74 | 14.74 | 14.74 | 5.2195 | 5.756 | 5.96 | 6.1505 | 6.2945 | 6.544 | 6.8995 | 7.244 | 7.496 | 7.496 | 7.496 | 7.496 | 7.496 | 7.496 | 7.496 | 7.496 | 7.496 | 7.496 | 7.496 | 7.496 | 7.496 | 0.0015022 | 0.0016566 | 0.0017154 | 0.0017702 | 0.0018116 | 0.0018834 | 0.0019858 | 0.0020849 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574
| LV008 | 3779 | 16.36 | 16.54 | 16.59 | 16.59 | 16.61 | 16.65 | 16.82 | 17.04 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 17.09 | 14.9 | 14.99 | 15.05 | 15.08 | 15.08 | 15.13 | 15.3 | 15.53 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 7.669 | 7.7275 | 7.756 | 7.7665 | 7.7695 | 7.793 | 7.878 | 7.9915 | 8.0095 | 8.0095 | 8.0095 | 8.0095 | 8.0095 | 8.0095 | 8.0095 | 8.0095 | 8.0095 | 8.0095 | 8.0095 | 8.0095 | 8.0095 | 0.0020294 | 0.0020449 | 0.0020524 | 0.0020552 | 0.002056 | 0.0020622 | 0.0020847 | 0.0021147 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195
| LV009 | 3497 | 7.89 | 7.81 | 7.69 | 7.59 | 7.44 | 7.32 | 7.26 | 7.19 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.18 | 7.1 | 7.01 | 6.92 | 6.8 | 6.69 | 6.64 | 6.57 | 6.48 | 6.48 | 6.48 | 6.48 | 6.48 | 6.48 | 6.48 | 6.48 | 6.48 | 6.48 | 6.48 | 6.48 | 6.48 | 3.6965 | 3.6565 | 3.607 | 3.5605 | 3.496 | 3.4395 | 3.413 | 3.378 | 3.3315 | 3.3315 | 3.3315 | 3.3315 | 3.3315 | 3.3315 | 3.3315 | 3.3315 | 3.3315 | 3.3315 | 3.3315 | 3.3315 | 3.3315 | 0.001057 | 0.0010456 | 0.0010315 | 0.0010182 | 0.00099971 | 0.00098356 | 0.00097598 | 0.00096597 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267
| LV010 | 2697.5 | 7.56 | 7.5 | 7.45 | 7.41 | 7.37 | 7.33 | 7.35 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 6.58 | 6.53 | 6.49 | 6.45 | 6.4 | 6.38 | 6.4 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 3.437 | 3.4105 | 3.389 | 3.369 | 3.3455 | 3.3325 | 3.3425 | 3.364 | 3.364 | 3.364 | 3.364 | 3.364 | 3.364 | 3.364 | 3.364 | 3.364 | 3.364 | 3.364 | 3.364 | 3.364 | 3.364 | 0.0012741 | 0.0012643 | 0.0012563 | 0.0012489 | 0.0012402 | 0.0012354 | 0.0012391 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471
| LVN001 | 2 | 16.74 | 17.11 | 17.43 | 17.72 | 17.97 | 18.23 | 18.53 | 18.83 | 19.11 | 19.11 | 19.11 | 19.11 | 19.11 | 19.11 | 19.11 | 19.11 | 19.11 | 19.11 | 19.11 | 19.11 | 19.11 | 16.43 | 16.76 | 17.07 | 17.35 | 17.59 | 17.86 | 18.15 | 18.44 | 18.71 | 18.71 | 18.71 | 18.71 | 18.71 | 18.71 | 18.71 | 18.71 | 18.71 | 18.71 | 18.71 | 18.71 | 18.71 | 8.2615 | 8.4325 | 8.589 | 8.7305 | 8.852 | 8.9855 | 9.132 | 9.2785 | 9.415 | 9.415 | 9.415 | 9.415 | 9.415 | 9.415 | 9.415 | 9.415 | 9.415 | 9.415 | 9.415 | 9.415 | 9.415 | 4.1308 | 4.2163 | 4.2945 | 4.3653 | 4.426 | 4.4928 | 4.566 | 4.6393 | 4.7075 | 4.7075 | 4.7075 | 4.7075 | 4.7075 | 4.7075 | 4.7075 | 4.7075 | 4.7075 | 4.7075 | 4.7075 | 4.7075 | 4.7075
| LVN021 | 53 | 21.34 | 22.34 | 23.18 | 23.9 | 24.45 | 25.05 | 25.82 | 26.61 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 17.08 | 17.81 | 18.48 | 19.08 | 19.51 | 20 | 20.62 | 21.23 | 21.61 | 21.61 | 21.61 | 21.61 | 21.61 | 21.61 | 21.61 | 21.61 | 21.61 | 21.61 | 21.61 | 21.61 | 21.61 | 9.179 | 9.5845 | 9.945 | 10.263 | 10.496 | 10.7575 | 11.09 | 11.422 | 11.6285 | 11.6285 | 11.6285 | 11.6285 | 11.6285 | 11.6285 | 11.6285 | 11.6285 | 11.6285 | 11.6285 | 11.6285 | 11.6285 | 11.6285 | 0.17319 | 0.18084 | 0.18764 | 0.19364 | 0.19804 | 0.20297 | 0.20925 | 0.21551 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941
| LVN022 | 4725.5 | 13.75 | 13.86 | 13.94 | 13.99 | 13.97 | 14 | 14.15 | 14.33 | 14.36 | 14.36 | 14.36 | 14.36 | 14.36 | 14.36 | 14.36 | 14.36 | 14.36 | 14.36 | 14.36 | 14.36 | 14.36 | 12.97 | 13.1 | 13.18 | 13.21 | 13.16 | 13.17 | 13.31 | 13.52 | 13.57 | 13.57 | 13.57 | 13.57 | 13.57 | 13.57 | 13.57 | 13.57 | 13.57 | 13.57 | 13.57 | 13.57 | 13.57 | 6.602 | 6.664 | 6.704 | 6.722 | 6.7015 | 6.7095 | 6.781 | 6.8815 | 6.9035 | 6.9035 | 6.9035 | 6.9035 | 6.9035 | 6.9035 | 6.9035 | 6.9035 | 6.9035 | 6.9035 | 6.9035 | 6.9035 | 6.9035 | 0.0013971 | 0.0014102 | 0.0014187 | 0.0014225 | 0.0014182 | 0.0014198 | 0.001435 | 0.0014562 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609
| LVN023 | 151 | 13.02 | 13.3 | 13.59 | 13.8 | 13.96 | 14.15 | 14.41 | 14.69 | 14.85 | 14.85 | 14.85 | 14.85 | 14.85 | 14.85 | 14.85 | 14.85 | 14.85 | 14.85 | 14.85 | 14.85 | 14.85 | 12.23 | 12.48 | 12.73 | 12.91 | 13.05 | 13.25 | 13.52 | 13.75 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 13.86 | 6.2335 | 6.363 | 6.494 | 6.5885 | 6.6615 | 6.76 | 6.8935 | 7.016 | 7.0785 | 7.0785 | 7.0785 | 7.0785 | 7.0785 | 7.0785 | 7.0785 | 7.0785 | 7.0785 | 7.0785 | 7.0785 | 7.0785 | 7.0785 | 0.041281 | 0.042139 | 0.043007 | 0.043632 | 0.044116 | 0.044768 | 0.045652 | 0.046464 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877
| LVN024 | 54 | 11.85 | 12.65 | 13.18 | 13.66 | 14.1 | 14.49 | 14.93 | 15.39 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 11.36 | 11.8 | 12.26 | 12.69 | 13.05 | 13.42 | 13.83 | 14.24 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 5.7535 | 6.0275 | 6.268 | 6.4905 | 6.6825 | 6.8705 | 7.08 | 7.2925 | 7.4715 | 7.4715 | 7.4715 | 7.4715 | 7.4715 | 7.4715 | 7.4715 | 7.4715 | 7.4715 | 7.4715 | 7.4715 | 7.4715 | 7.4715 | 0.10655 | 0.11162 | 0.11607 | 0.12019 | 0.12375 | 0.12723 | 0.13111 | 0.13505 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836
| LVN031 | 34.5 | 17.85 | 18.22 | 18.47 | 18.7 | 18.86 | 19.03 | 19.26 | 19.5 | 19.67 | 19.67 | 19.67 | 19.67 | 19.67 | 19.67 | 19.67 | 19.67 | 19.67 | 19.67 | 19.67 | 19.67 | 19.67 | 16.55 | 17.28 | 17.51 | 17.72 | 17.86 | 18.02 | 18.24 | 18.47 | 18.63 | 18.63 | 18.63 | 18.63 | 18.63 | 18.63 | 18.63 | 18.63 | 18.63 | 18.63 | 18.63 | 18.63 | 18.63 | 8.47 | 8.781 | 8.899 | 9.007 | 9.08 | 9.1615 | 9.273 | 9.3895 | 9.471 | 9.471 | 9.471 | 9.471 | 9.471 | 9.471 | 9.471 | 9.471 | 9.471 | 9.471 | 9.471 | 9.471 | 9.471 | 0.24551 | 0.25452 | 0.25794 | 0.26107 | 0.26319 | 0.26555 | 0.26878 | 0.27216 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452
| LVN032 | 248 | 17.71 | 18.37 | 18.63 | 18.88 | 19.09 | 19.31 | 19.62 | 19.95 | 20.21 | 20.21 | 20.21 | 20.21 | 20.21 | 20.21 | 20.21 | 20.21 | 20.21 | 20.21 | 20.21 | 20.21 | 20.21 | 15.47 | 16.05 | 16.28 | 16.49 | 16.68 | 16.88 | 17.14 | 17.43 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 8.071 | 8.373 | 8.4925 | 8.6035 | 8.7015 | 8.8045 | 8.942 | 9.093 | 9.209 | 9.209 | 9.209 | 9.209 | 9.209 | 9.209 | 9.209 | 9.209 | 9.209 | 9.209 | 9.209 | 9.209 | 9.209 | 0.032544 | 0.033762 | 0.034244 | 0.034692 | 0.035087 | 0.035502 | 0.036056 | 0.036665 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133
| LVN033 | 157.5 | 8.83 | 8.98 | 9.16 | 9.24 | 9.25 | 9.41 | 9.66 | 9.84 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 8.52 | 8.66 | 8.85 | 8.93 | 8.95 | 9.09 | 9.33 | 9.51 | 9.46 | 9.46 | 9.46 | 9.46 | 9.46 | 9.46 | 9.46 | 9.46 | 9.46 | 9.46 | 9.46 | 9.46 | 9.46 | 4.3065 | 4.378 | 4.4715 | 4.5115 | 4.52 | 4.593 | 4.7145 | 4.8045 | 4.7825 | 4.7825 | 4.7825 | 4.7825 | 4.7825 | 4.7825 | 4.7825 | 4.7825 | 4.7825 | 4.7825 | 4.7825 | 4.7825 | 4.7825 | 0.027343 | 0.027797 | 0.02839 | 0.028644 | 0.028698 | 0.029162 | 0.029933 | 0.030505 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365
| LVN034 | 108 | 11.9 | 12.09 | 12.24 | 12.35 | 12.41 | 12.51 | 12.68 | 12.86 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 12.93 | 10.54 | 10.66 | 10.79 | 10.87 | 10.92 | 11.02 | 11.17 | 11.31 | 11.37 | 11.37 | 11.37 | 11.37 | 11.37 | 11.37 | 11.37 | 11.37 | 11.37 | 11.37 | 11.37 | 11.37 | 11.37 | 5.474 | 5.5445 | 5.6125 | 5.657 | 5.6835 | 5.7335 | 5.8115 | 5.8875 | 5.919 | 5.919 | 5.919 | 5.919 | 5.919 | 5.919 | 5.919 | 5.919 | 5.919 | 5.919 | 5.919 | 5.919 | 5.919 | 0.050685 | 0.051338 | 0.051968 | 0.05238 | 0.052625 | 0.053088 | 0.05381 | 0.054514 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806
| MBN012 | 2493.5 | 10.9 | 11.05 | 11.19 | 11.28 | 11.3 | 11.34 | 11.49 | 11.65 | 11.73 | 11.73 | 11.73 | 11.73 | 11.73 | 11.73 | 11.73 | 11.73 | 11.73 | 11.73 | 11.73 | 11.73 | 11.73 | 10.12 | 10.28 | 10.39 | 10.48 | 10.52 | 10.57 | 10.7 | 10.85 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 10.92 | 5.177 | 5.2555 | 5.315 | 5.36 | 5.377 | 5.4005 | 5.4685 | 5.545 | 5.5815 | 5.5815 | 5.5815 | 5.5815 | 5.5815 | 5.5815 | 5.5815 | 5.5815 | 5.5815 | 5.5815 | 5.5815 | 5.5815 | 5.5815 | 0.0020762 | 0.0021077 | 0.0021315 | 0.0021496 | 0.0021564 | 0.0021658 | 0.0021931 | 0.0022238 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384
| MBN013 | 870.5 | 4.28 | 4.3 | 4.31 | 4.31 | 4.26 | 4.24 | 4.26 | 4.3 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 4.26 | 3.92 | 3.95 | 3.95 | 3.95 | 3.91 | 3.89 | 3.91 | 3.94 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | 2.014 | 2.0275 | 2.029 | 2.029 | 2.0075 | 1.9975 | 2.0075 | 2.024 | 2.0075 | 2.0075 | 2.0075 | 2.0075 | 2.0075 | 2.0075 | 2.0075 | 2.0075 | 2.0075 | 2.0075 | 2.0075 | 2.0075 | 2.0075 | 0.0023136 | 0.0023291 | 0.0023308 | 0.0023308 | 0.0023061 | 0.0022947 | 0.0023061 | 0.0023251 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061
| MBN014 | 1044 | 6.64 | 6.71 | 6.75 | 6.75 | 6.69 | 6.66 | 6.7 | 6.77 | 6.72 | 6.72 | 6.72 | 6.72 | 6.72 | 6.72 | 6.72 | 6.72 | 6.72 | 6.72 | 6.72 | 6.72 | 6.72 | 5.88 | 5.93 | 5.97 | 5.97 | 5.92 | 5.9 | 5.94 | 6 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 3.054 | 3.082 | 3.102 | 3.102 | 3.0755 | 3.064 | 3.084 | 3.1155 | 3.0905 | 3.0905 | 3.0905 | 3.0905 | 3.0905 | 3.0905 | 3.0905 | 3.0905 | 3.0905 | 3.0905 | 3.0905 | 3.0905 | 3.0905 | 0.0029253 | 0.0029521 | 0.0029713 | 0.0029713 | 0.0029459 | 0.0029349 | 0.002954 | 0.0029842 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602
| MBN023 | 3282.5 | 13.85 | 13.88 | 13.83 | 13.75 | 13.6 | 13.49 | 13.46 | 13.45 | 13.36 | 13.36 | 13.36 | 13.36 | 13.36 | 13.36 | 13.36 | 13.36 | 13.36 | 13.36 | 13.36 | 13.36 | 13.36 | 12.2 | 12.2 | 12.13 | 12.04 | 11.9 | 11.79 | 11.76 | 11.75 | 11.67 | 11.67 | 11.67 | 11.67 | 11.67 | 11.67 | 11.67 | 11.67 | 11.67 | 11.67 | 11.67 | 11.67 | 11.67 | 6.3475 | 6.352 | 6.32 | 6.2765 | 6.205 | 6.15 | 6.135 | 6.13 | 6.0885 | 6.0885 | 6.0885 | 6.0885 | 6.0885 | 6.0885 | 6.0885 | 6.0885 | 6.0885 | 6.0885 | 6.0885 | 6.0885 | 6.0885 | 0.0019337 | 0.0019351 | 0.0019254 | 0.0019121 | 0.0018903 | 0.0018736 | 0.001869 | 0.0018675 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548
| MBN031 | 707.5 | 6.43 | 6.5 | 6.53 | 6.53 | 6.48 | 6.45 | 6.5 | 6.57 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 6.52 | 5.88 | 5.95 | 5.97 | 5.97 | 5.93 | 5.9 | 5.94 | 6 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 3.0225 | 3.0575 | 3.069 | 3.069 | 3.0475 | 3.0325 | 3.054 | 3.0855 | 3.0675 | 3.0675 | 3.0675 | 3.0675 | 3.0675 | 3.0675 | 3.0675 | 3.0675 | 3.0675 | 3.0675 | 3.0675 | 3.0675 | 3.0675 | 0.0042721 | 0.0043216 | 0.0043378 | 0.0043378 | 0.0043074 | 0.0042862 | 0.0043166 | 0.0043611 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357
| MBN032 | 2319 | 11.55 | 11.75 | 11.92 | 12.05 | 12.1 | 12.19 | 12.38 | 12.6 | 12.68 | 12.68 | 12.68 | 12.68 | 12.68 | 12.68 | 12.68 | 12.68 | 12.68 | 12.68 | 12.68 | 12.68 | 12.68 | 10.9 | 11.08 | 11.24 | 11.35 | 11.4 | 11.49 | 11.67 | 11.86 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 5.5475 | 5.6405 | 5.722 | 5.78 | 5.805 | 5.85 | 5.9415 | 6.041 | 6.081 | 6.081 | 6.081 | 6.081 | 6.081 | 6.081 | 6.081 | 6.081 | 6.081 | 6.081 | 6.081 | 6.081 | 6.081 | 0.0023922 | 0.0024323 | 0.0024674 | 0.0024925 | 0.0025032 | 0.0025226 | 0.0025621 | 0.002605 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223
| MDA022 | 1770 | 8.91 | 8.82 | 8.64 | 8.46 | 8.25 | 8.1 | 8.02 | 7.96 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 8.35 | 8.25 | 8.08 | 7.91 | 7.71 | 7.53 | 7.44 | 7.36 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 4.259 | 4.2105 | 4.124 | 4.0375 | 3.936 | 3.8505 | 3.807 | 3.77 | 3.7085 | 3.7085 | 3.7085 | 3.7085 | 3.7085 | 3.7085 | 3.7085 | 3.7085 | 3.7085 | 3.7085 | 3.7085 | 3.7085 | 3.7085 | 0.0024062 | 0.0023788 | 0.0023299 | 0.0022811 | 0.0022237 | 0.0021754 | 0.0021508 | 0.0021299 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952
| MDA023 | 3035 | 17.06 | 17.78 | 17.87 | 17.95 | 17.9 | 17.89 | 18.05 | 18.22 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 15.8 | 16.46 | 16.55 | 16.61 | 16.55 | 16.55 | 16.68 | 16.85 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 16.84 | 8.089 | 8.428 | 8.473 | 8.506 | 8.4775 | 8.476 | 8.5455 | 8.6305 | 8.624 | 8.624 | 8.624 | 8.624 | 8.624 | 8.624 | 8.624 | 8.624 | 8.624 | 8.624 | 8.624 | 8.624 | 8.624 | 0.0026652 | 0.0027769 | 0.0027918 | 0.0028026 | 0.0027932 | 0.0027928 | 0.0028157 | 0.0028437 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415
| MDA024 | 1323 | 8.68 | 8.58 | 8.37 | 8.22 | 8.04 | 7.87 | 7.76 | 7.7 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.59 | 7.73 | 7.62 | 7.44 | 7.32 | 7.2 | 7.12 | 7.11 | 7.08 | 6.98 | 6.98 | 6.98 | 6.98 | 6.98 | 6.98 | 6.98 | 6.98 | 6.98 | 6.98 | 6.98 | 6.98 | 6.98 | 4.0075 | 3.954 | 3.8595 | 3.795 | 3.726 | 3.6725 | 3.6525 | 3.633 | 3.5815 | 3.5815 | 3.5815 | 3.5815 | 3.5815 | 3.5815 | 3.5815 | 3.5815 | 3.5815 | 3.5815 | 3.5815 | 3.5815 | 3.5815 | 0.0030291 | 0.0029887 | 0.0029172 | 0.0028685 | 0.0028163 | 0.0027759 | 0.0027608 | 0.002746 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071
| MDA031 | 1896.5 | 6.17 | 6.13 | 6.09 | 6.02 | 5.95 | 5.89 | 5.86 | 5.87 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.55 | 5.48 | 5.4 | 5.32 | 5.23 | 5.16 | 5.14 | 5.13 | 5.07 | 5.07 | 5.07 | 5.07 | 5.07 | 5.07 | 5.07 | 5.07 | 5.07 | 5.07 | 5.07 | 5.07 | 5.07 | 2.868 | 2.8375 | 2.8035 | 2.765 | 2.723 | 2.6895 | 2.678 | 2.676 | 2.6475 | 2.6475 | 2.6475 | 2.6475 | 2.6475 | 2.6475 | 2.6475 | 2.6475 | 2.6475 | 2.6475 | 2.6475 | 2.6475 | 2.6475 | 0.0015123 | 0.0014962 | 0.0014782 | 0.0014579 | 0.0014358 | 0.0014181 | 0.0014121 | 0.001411 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396
| MDA032 | 2138 | 8.07 | 8.09 | 8.08 | 8.04 | 7.95 | 7.89 | 7.89 | 7.91 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.27 | 7.28 | 7.26 | 7.22 | 7.14 | 7.09 | 7.09 | 7.11 | 7.05 | 7.05 | 7.05 | 7.05 | 7.05 | 7.05 | 7.05 | 7.05 | 7.05 | 7.05 | 7.05 | 7.05 | 7.05 | 3.755 | 3.7615 | 3.753 | 3.733 | 3.6915 | 3.665 | 3.665 | 3.675 | 3.645 | 3.645 | 3.645 | 3.645 | 3.645 | 3.645 | 3.645 | 3.645 | 3.645 | 3.645 | 3.645 | 3.645 | 3.645 | 0.0017563 | 0.0017594 | 0.0017554 | 0.001746 | 0.0017266 | 0.0017142 | 0.0017142 | 0.0017189 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049
| MDA033 | 1245.5 | 4.52 | 4.56 | 4.6 | 4.62 | 4.63 | 4.67 | 4.72 | 4.76 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.05 | 4.09 | 4.13 | 4.15 | 4.16 | 4.19 | 4.24 | 4.28 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 4.29 | 2.0955 | 2.1155 | 2.1355 | 2.1455 | 2.1505 | 2.167 | 2.192 | 2.212 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 0.0016825 | 0.0016985 | 0.0017146 | 0.0017226 | 0.0017266 | 0.0017399 | 0.0017599 | 0.001776 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178
| MDA034 | 1771 | 6.86 | 6.96 | 7.03 | 7.08 | 7.08 | 7.11 | 7.2 | 7.29 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 6.07 | 6.14 | 6.19 | 6.23 | 6.24 | 6.27 | 6.35 | 6.44 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 6.47 | 3.1535 | 3.193 | 3.221 | 3.2425 | 3.246 | 3.261 | 3.3025 | 3.3475 | 3.3625 | 3.3625 | 3.3625 | 3.3625 | 3.3625 | 3.3625 | 3.3625 | 3.3625 | 3.3625 | 3.3625 | 3.3625 | 3.3625 | 3.3625 | 0.0017806 | 0.0018029 | 0.0018187 | 0.0018309 | 0.0018329 | 0.0018413 | 0.0018648 | 0.0018902 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986
| MLN011 | 5616 | 13.44 | 14.34 | 15.35 | 16.28 | 17.19 | 18.24 | 19.39 | 20.47 | 21.32 | 21.32 | 21.32 | 21.32 | 21.32 | 21.32 | 21.32 | 21.32 | 21.32 | 21.32 | 21.32 | 21.32 | 21.32 | 11.78 | 12.34 | 13.22 | 14.1 | 14.94 | 15.91 | 16.99 | 17.98 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 6.139 | 6.47 | 6.9295 | 7.377 | 7.8075 | 8.3045 | 8.855 | 9.3635 | 9.778 | 9.778 | 9.778 | 9.778 | 9.778 | 9.778 | 9.778 | 9.778 | 9.778 | 9.778 | 9.778 | 9.778 | 9.778 | 0.0010931 | 0.0011521 | 0.0012339 | 0.0013136 | 0.0013902 | 0.0014787 | 0.0015767 | 0.0016673 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411
| MLN012 | 2717 | 8.4 | 8.64 | 8.86 | 9.06 | 9.21 | 9.38 | 9.61 | 9.85 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 7.67 | 7.88 | 8.08 | 8.26 | 8.39 | 8.55 | 8.88 | 9.3 | 9.63 | 9.63 | 9.63 | 9.63 | 9.63 | 9.63 | 9.63 | 9.63 | 9.63 | 9.63 | 9.63 | 9.63 | 9.63 | 3.9445 | 4.054 | 4.157 | 4.25 | 4.318 | 4.3995 | 4.5495 | 4.7325 | 4.8735 | 4.8735 | 4.8735 | 4.8735 | 4.8735 | 4.8735 | 4.8735 | 4.8735 | 4.8735 | 4.8735 | 4.8735 | 4.8735 | 4.8735 | 0.0014518 | 0.0014921 | 0.00153 | 0.0015642 | 0.0015893 | 0.0016192 | 0.0016745 | 0.0017418 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937
| MLN013 | 5029 | 14.46 | 14.98 | 15.43 | 15.87 | 16.22 | 16.61 | 17.11 | 17.63 | 18.06 | 18.06 | 18.06 | 18.06 | 18.06 | 18.06 | 18.06 | 18.06 | 18.06 | 18.06 | 18.06 | 18.06 | 18.06 | 13.26 | 13.74 | 14.16 | 14.56 | 14.89 | 15.25 | 15.73 | 16.22 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 6.81 | 7.056 | 7.2705 | 7.4765 | 7.6445 | 7.829 | 8.072 | 8.3215 | 8.519 | 8.519 | 8.519 | 8.519 | 8.519 | 8.519 | 8.519 | 8.519 | 8.519 | 8.519 | 8.519 | 8.519 | 8.519 | 0.0013541 | 0.0014031 | 0.0014457 | 0.0014867 | 0.0015201 | 0.0015568 | 0.0016051 | 0.0016547 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694
| MLN014 | 4642.5 | 11.17 | 11.63 | 12.06 | 12.47 | 12.79 | 13.21 | 14 | 14.72 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 10.34 | 10.75 | 11.13 | 11.49 | 11.81 | 12.15 | 12.8 | 13.52 | 14.13 | 14.13 | 14.13 | 14.13 | 14.13 | 14.13 | 14.13 | 14.13 | 14.13 | 14.13 | 14.13 | 14.13 | 14.13 | 5.2945 | 5.507 | 5.7045 | 5.892 | 6.052 | 6.234 | 6.58 | 6.94 | 7.2435 | 7.2435 | 7.2435 | 7.2435 | 7.2435 | 7.2435 | 7.2435 | 7.2435 | 7.2435 | 7.2435 | 7.2435 | 7.2435 | 7.2435 | 0.0011404 | 0.0011862 | 0.0012288 | 0.0012691 | 0.0013036 | 0.0013428 | 0.0014173 | 0.0014949 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603
| MLN021 | 5237.5 | 22.47 | 23.99 | 25.32 | 26.69 | 28.14 | 29.79 | 31.64 | 33.22 | 34.23 | 34.23 | 34.23 | 34.23 | 34.23 | 34.23 | 34.23 | 34.23 | 34.23 | 34.23 | 34.23 | 34.23 | 34.23 | 20.37 | 21.75 | 22.94 | 24.08 | 25.08 | 26.16 | 27.57 | 29.12 | 30.28 | 30.28 | 30.28 | 30.28 | 30.28 | 30.28 | 30.28 | 30.28 | 30.28 | 30.28 | 30.28 | 30.28 | 30.28 | 10.5 | 11.211 | 11.827 | 12.4315 | 12.999 | 13.6245 | 14.3955 | 15.175 | 15.7325 | 15.7325 | 15.7325 | 15.7325 | 15.7325 | 15.7325 | 15.7325 | 15.7325 | 15.7325 | 15.7325 | 15.7325 | 15.7325 | 15.7325 | 0.0020048 | 0.0021405 | 0.0022581 | 0.0023736 | 0.0024819 | 0.0026013 | 0.0027485 | 0.0028974 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038
| MLN022 | 2140 | 10.61 | 10.97 | 11.27 | 11.52 | 11.72 | 11.95 | 12.29 | 12.67 | 12.86 | 12.86 | 12.86 | 12.86 | 12.86 | 12.86 | 12.86 | 12.86 | 12.86 | 12.86 | 12.86 | 12.86 | 12.86 | 9.5 | 9.8 | 10.07 | 10.32 | 10.49 | 10.68 | 11.01 | 11.42 | 11.78 | 11.78 | 11.78 | 11.78 | 11.78 | 11.78 | 11.78 | 11.78 | 11.78 | 11.78 | 11.78 | 11.78 | 11.78 | 4.9165 | 5.0755 | 5.215 | 5.34 | 5.4295 | 5.5305 | 5.697 | 5.8975 | 6.052 | 6.052 | 6.052 | 6.052 | 6.052 | 6.052 | 6.052 | 6.052 | 6.052 | 6.052 | 6.052 | 6.052 | 6.052 | 0.0022974 | 0.0023717 | 0.0024369 | 0.0024953 | 0.0025371 | 0.0025843 | 0.0026621 | 0.0027558 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828
| MLN023 | 2956.5 | 8.66 | 9.06 | 9.42 | 9.75 | 10.06 | 10.4 | 10.78 | 11.18 | 11.53 | 11.53 | 11.53 | 11.53 | 11.53 | 11.53 | 11.53 | 11.53 | 11.53 | 11.53 | 11.53 | 11.53 | 11.53 | 7.81 | 8.15 | 8.48 | 8.79 | 9.06 | 9.35 | 9.72 | 10.1 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 4.0325 | 4.2115 | 4.381 | 4.539 | 4.68 | 4.8325 | 5.019 | 5.212 | 5.401 | 5.401 | 5.401 | 5.401 | 5.401 | 5.401 | 5.401 | 5.401 | 5.401 | 5.401 | 5.401 | 5.401 | 5.401 | 0.0013639 | 0.0014245 | 0.0014818 | 0.0015353 | 0.001583 | 0.0016345 | 0.0016976 | 0.0017629 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268
| MLN024 | 1703 | 10.06 | 10.31 | 10.52 | 10.66 | 10.8 | 10.96 | 11.18 | 11.42 | 11.62 | 11.62 | 11.62 | 11.62 | 11.62 | 11.62 | 11.62 | 11.62 | 11.62 | 11.62 | 11.62 | 11.62 | 11.62 | 9.31 | 9.58 | 9.73 | 9.89 | 9.99 | 10.11 | 10.31 | 10.53 | 10.71 | 10.71 | 10.71 | 10.71 | 10.71 | 10.71 | 10.71 | 10.71 | 10.71 | 10.71 | 10.71 | 10.71 | 10.71 | 4.7675 | 4.8995 | 4.9835 | 5.0605 | 5.1165 | 5.1825 | 5.2855 | 5.3985 | 5.4915 | 5.4915 | 5.4915 | 5.4915 | 5.4915 | 5.4915 | 5.4915 | 5.4915 | 5.4915 | 5.4915 | 5.4915 | 5.4915 | 5.4915 | 0.0027995 | 0.002877 | 0.0029263 | 0.0029715 | 0.0030044 | 0.0030432 | 0.0031036 | 0.00317 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246
| MLN032 | 3857.5 | 9.63 | 9.96 | 10.26 | 10.54 | 10.79 | 11.06 | 11.43 | 11.8 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 12.08 | 8.81 | 9.11 | 9.41 | 9.68 | 9.92 | 10.18 | 10.51 | 10.86 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 4.528 | 4.6825 | 4.8325 | 4.969 | 5.0905 | 5.222 | 5.393 | 5.571 | 5.732 | 5.732 | 5.732 | 5.732 | 5.732 | 5.732 | 5.732 | 5.732 | 5.732 | 5.732 | 5.732 | 5.732 | 5.732 | 0.0011738 | 0.0012139 | 0.0012528 | 0.0012881 | 0.0013196 | 0.0013537 | 0.0013981 | 0.0014442 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859
| MLN033 | 3400 | 15.53 | 12.6 | 13.58 | 14.53 | 15.44 | 16.81 | 18.24 | 19.6 | 20.82 | 20.82 | 20.82 | 20.82 | 20.82 | 20.82 | 20.82 | 20.82 | 20.82 | 20.82 | 20.82 | 20.82 | 20.82 | 14.12 | 11.49 | 12.39 | 13.56 | 14.78 | 16.1 | 17.48 | 18.81 | 20.02 | 20.02 | 20.02 | 20.02 | 20.02 | 20.02 | 20.02 | 20.02 | 20.02 | 20.02 | 20.02 | 20.02 | 20.02 | 7.2715 | 5.9115 | 6.3735 | 6.9255 | 7.489 | 8.1565 | 8.854 | 9.5235 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 0.0021387 | 0.0017387 | 0.0018746 | 0.0020369 | 0.0022026 | 0.002399 | 0.0026041 | 0.002801 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794
| MNA013 | 651 | 10.5 | 10.56 | 10.46 | 10.35 | 10.21 | 10.09 | 10.03 | 9.98 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.26 | 9.19 | 9.09 | 8.99 | 8.87 | 8.79 | 8.76 | 8.72 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 8.63 | 4.816 | 4.8005 | 4.7505 | 4.699 | 4.636 | 4.59 | 4.5705 | 4.549 | 4.504 | 4.504 | 4.504 | 4.504 | 4.504 | 4.504 | 4.504 | 4.504 | 4.504 | 4.504 | 4.504 | 4.504 | 4.504 | 0.0073978 | 0.007374 | 0.0072972 | 0.0072181 | 0.0071214 | 0.0070507 | 0.0070207 | 0.0069877 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186
| MNA014 | 1638.5 | 11.98 | 12.19 | 12.29 | 12.33 | 12.16 | 12.15 | 12.31 | 12.51 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 12.41 | 10.48 | 10.68 | 10.77 | 10.78 | 10.66 | 10.65 | 10.78 | 10.96 | 10.87 | 10.87 | 10.87 | 10.87 | 10.87 | 10.87 | 10.87 | 10.87 | 10.87 | 10.87 | 10.87 | 10.87 | 10.87 | 5.465 | 5.5665 | 5.613 | 5.6225 | 5.555 | 5.55 | 5.6195 | 5.7125 | 5.666 | 5.666 | 5.666 | 5.666 | 5.666 | 5.666 | 5.666 | 5.666 | 5.666 | 5.666 | 5.666 | 5.666 | 5.666 | 0.0033354 | 0.0033973 | 0.0034257 | 0.0034315 | 0.0033903 | 0.0033872 | 0.0034297 | 0.0034864 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458
| MNA021 | 1826 | 9.84 | 9.79 | 9.72 | 9.63 | 9.53 | 9.45 | 9.44 | 9.42 | 9.31 | 9.31 | 9.31 | 9.31 | 9.31 | 9.31 | 9.31 | 9.31 | 9.31 | 9.31 | 9.31 | 9.31 | 9.31 | 8.35 | 8.32 | 8.25 | 8.09 | 8 | 7.91 | 7.9 | 7.88 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 4.3985 | 4.3805 | 4.3455 | 4.276 | 4.2295 | 4.186 | 4.181 | 4.171 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 0.0024088 | 0.002399 | 0.0023798 | 0.0023417 | 0.0023163 | 0.0022924 | 0.0022897 | 0.0022842 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579
| MNA022 | 2163 | 6.75 | 6.77 | 6.77 | 6.76 | 6.72 | 6.69 | 6.71 | 6.73 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 5.86 | 5.89 | 5.88 | 5.87 | 5.82 | 5.8 | 5.8 | 5.82 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 3.0635 | 3.077 | 3.0735 | 3.0685 | 3.045 | 3.0335 | 3.0365 | 3.0465 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 0.0014163 | 0.0014226 | 0.0014209 | 0.0014186 | 0.0014078 | 0.0014025 | 0.0014038 | 0.0014085 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055
| MNA024 | 2562 | 8.88 | 9 | 9.1 | 9.17 | 9.18 | 9.27 | 9.43 | 9.6 | 9.69 | 9.69 | 9.69 | 9.69 | 9.69 | 9.69 | 9.69 | 9.69 | 9.69 | 9.69 | 9.69 | 9.69 | 9.69 | 8.13 | 8.27 | 8.37 | 8.46 | 8.5 | 8.58 | 8.74 | 8.9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 4.1775 | 4.2445 | 4.2945 | 4.3365 | 4.352 | 4.3935 | 4.4735 | 4.555 | 4.6035 | 4.6035 | 4.6035 | 4.6035 | 4.6035 | 4.6035 | 4.6035 | 4.6035 | 4.6035 | 4.6035 | 4.6035 | 4.6035 | 4.6035 | 0.0016306 | 0.0016567 | 0.0016762 | 0.0016926 | 0.0016987 | 0.0017149 | 0.0017461 | 0.0017779 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968
| MNA034 | 1852 | 6.96 | 7.01 | 7.05 | 7.06 | 7.01 | 7 | 7.05 | 7.13 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 6.33 | 6.39 | 6.41 | 6.41 | 6.37 | 6.35 | 6.4 | 6.47 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 6.44 | 3.2595 | 3.288 | 3.301 | 3.3025 | 3.281 | 3.2725 | 3.2975 | 3.334 | 3.3175 | 3.3175 | 3.3175 | 3.3175 | 3.3175 | 3.3175 | 3.3175 | 3.3175 | 3.3175 | 3.3175 | 3.3175 | 3.3175 | 3.3175 | 0.00176 | 0.0017754 | 0.0017824 | 0.0017832 | 0.0017716 | 0.001767 | 0.0017805 | 0.0018002 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913
| MRO002 | 2 | 1.11 | 1.11 | 1.09 | 1.08 | 1.06 | 1.05 | 1.04 | 1.03 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 0.91 | 0.91 | 0.9 | 0.88 | 0.87 | 0.86 | 0.85 | 0.84 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.485 | 0.485 | 0.4785 | 0.47 | 0.4635 | 0.4585 | 0.4535 | 0.4485 | 0.442 | 0.442 | 0.442 | 0.442 | 0.442 | 0.442 | 0.442 | 0.442 | 0.442 | 0.442 | 0.442 | 0.442 | 0.442 | 0.2425 | 0.2425 | 0.23925 | 0.235 | 0.23175 | 0.22925 | 0.22675 | 0.22425 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221
| MRO004 | 1865 | 4.21 | 4.23 | 4.21 | 4.19 | 4.16 | 4.14 | 4.14 | 4.15 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 4.13 | 3.89 | 3.89 | 3.88 | 3.86 | 3.82 | 3.8 | 3.79 | 3.8 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 1.993 | 1.996 | 1.9895 | 1.9795 | 1.961 | 1.951 | 1.9475 | 1.9525 | 1.9425 | 1.9425 | 1.9425 | 1.9425 | 1.9425 | 1.9425 | 1.9425 | 1.9425 | 1.9425 | 1.9425 | 1.9425 | 1.9425 | 1.9425 | 0.0010686 | 0.0010702 | 0.0010668 | 0.0010614 | 0.0010515 | 0.0010461 | 0.0010442 | 0.0010469 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416
| MRO005 | 2180.5 | 7.21 | 7.22 | 7.2 | 7.14 | 7.07 | 7 | 6.97 | 6.96 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 5.98 | 5.98 | 5.94 | 5.89 | 5.81 | 5.76 | 5.74 | 5.73 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 3.1745 | 3.176 | 3.159 | 3.1325 | 3.094 | 3.066 | 3.0545 | 3.0495 | 3.0195 | 3.0195 | 3.0195 | 3.0195 | 3.0195 | 3.0195 | 3.0195 | 3.0195 | 3.0195 | 3.0195 | 3.0195 | 3.0195 | 3.0195 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848
| MRO006 | 1092.5 | 3.49 | 3.44 | 3.41 | 3.38 | 3.35 | 3.34 | 3.34 | 3.34 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.22 | 3.18 | 3.15 | 3.11 | 3.07 | 3.05 | 3.05 | 3.05 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 1.6505 | 1.629 | 1.614 | 1.5955 | 1.577 | 1.5685 | 1.5685 | 1.5685 | 1.5585 | 1.5585 | 1.5585 | 1.5585 | 1.5585 | 1.5585 | 1.5585 | 1.5585 | 1.5585 | 1.5585 | 1.5585 | 1.5585 | 1.5585 | 0.0015108 | 0.0014911 | 0.0014773 | 0.0014604 | 0.0014435 | 0.0014357 | 0.0014357 | 0.0014357 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265
| MRO007 | 1887.5 | 5.42 | 5.48 | 5.52 | 5.53 | 5.52 | 5.56 | 5.62 | 5.69 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 4.67 | 4.71 | 4.74 | 4.76 | 4.75 | 4.76 | 4.81 | 4.87 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 4.86 | 2.4475 | 2.4705 | 2.487 | 2.4955 | 2.4905 | 2.5 | 2.5265 | 2.558 | 2.553 | 2.553 | 2.553 | 2.553 | 2.553 | 2.553 | 2.553 | 2.553 | 2.553 | 2.553 | 2.553 | 2.553 | 2.553 | 0.0012967 | 0.0013089 | 0.0013176 | 0.0013221 | 0.0013195 | 0.0013245 | 0.0013385 | 0.0013552 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526
| MRO008 | 2858 | 6.65 | 6.68 | 6.66 | 6.66 | 6.6 | 6.58 | 6.61 | 6.65 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 6.63 | 5.98 | 6.02 | 6.03 | 6.02 | 5.99 | 5.97 | 6 | 6.04 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 3.0905 | 3.109 | 3.1095 | 3.106 | 3.0865 | 3.0765 | 3.0915 | 3.1115 | 3.105 | 3.105 | 3.105 | 3.105 | 3.105 | 3.105 | 3.105 | 3.105 | 3.105 | 3.105 | 3.105 | 3.105 | 3.105 | 0.0010814 | 0.0010878 | 0.001088 | 0.0010868 | 0.00108 | 0.0010765 | 0.0010817 | 0.0010887 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864
| NHL015 | 1550.5 | 3.68 | 3.68 | 3.65 | 3.62 | 3.55 | 3.49 | 3.47 | 3.46 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.42 | 3.42 | 3.4 | 3.37 | 3.31 | 3.25 | 3.23 | 3.22 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 1.749 | 1.749 | 1.7375 | 1.7225 | 1.691 | 1.661 | 1.651 | 1.646 | 1.6195 | 1.6195 | 1.6195 | 1.6195 | 1.6195 | 1.6195 | 1.6195 | 1.6195 | 1.6195 | 1.6195 | 1.6195 | 1.6195 | 1.6195 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445
| NHL016 | 1386 | 3.87 | 3.85 | 3.82 | 3.77 | 3.7 | 3.64 | 3.61 | 3.59 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.5 | 3.47 | 3.42 | 3.35 | 3.29 | 3.27 | 3.24 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 1.8125 | 1.8025 | 1.7875 | 1.7625 | 1.7275 | 1.6975 | 1.686 | 1.6725 | 1.641 | 1.641 | 1.641 | 1.641 | 1.641 | 1.641 | 1.641 | 1.641 | 1.641 | 1.641 | 1.641 | 1.641 | 1.641 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184
| NHL031 | 1337.5 | 4.28 | 4.26 | 4.23 | 4.17 | 4.09 | 4.03 | 3.99 | 3.97 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.83 | 3.78 | 3.75 | 3.69 | 3.61 | 3.57 | 3.55 | 3.51 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 3.43 | 1.9825 | 1.962 | 1.947 | 1.917 | 1.877 | 1.854 | 1.841 | 1.824 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335
| NKA001 | 972.5 | 2.74 | 2.77 | 2.79 | 2.8 | 2.78 | 2.78 | 2.81 | 2.85 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.52 | 2.55 | 2.57 | 2.58 | 2.57 | 2.56 | 2.59 | 2.63 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 1.293 | 1.308 | 1.318 | 1.323 | 1.3165 | 1.313 | 1.328 | 1.348 | 1.3415 | 1.3415 | 1.3415 | 1.3415 | 1.3415 | 1.3415 | 1.3415 | 1.3415 | 1.3415 | 1.3415 | 1.3415 | 1.3415 | 1.3415 | 0.0013296 | 0.001345 | 0.0013553 | 0.0013604 | 0.0013537 | 0.0013501 | 0.0013656 | 0.0013861 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794
| NKA002 | 1699 | 6.01 | 6.07 | 6.1 | 6.1 | 6.05 | 6.02 | 6.05 | 6.1 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 5.44 | 5.49 | 5.52 | 5.52 | 5.47 | 5.43 | 5.47 | 5.51 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 5.48 | 2.8055 | 2.832 | 2.847 | 2.847 | 2.822 | 2.8035 | 2.822 | 2.8435 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 0.0016513 | 0.0016669 | 0.0016757 | 0.0016757 | 0.001661 | 0.0016501 | 0.001661 | 0.0016736 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663
| NKA003 | 651 | 4.96 | 4.95 | 4.9 | 4.84 | 4.77 | 4.71 | 4.68 | 4.65 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.43 | 4.43 | 4.38 | 4.33 | 4.26 | 4.21 | 4.18 | 4.15 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 2.2945 | 2.293 | 2.268 | 2.2415 | 2.2065 | 2.18 | 2.165 | 2.15 | 2.125 | 2.125 | 2.125 | 2.125 | 2.125 | 2.125 | 2.125 | 2.125 | 2.125 | 2.125 | 2.125 | 2.125 | 2.125 | 0.0035246 | 0.0035223 | 0.0034839 | 0.0034432 | 0.0033894 | 0.0033487 | 0.0033257 | 0.0033026 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642
| NKA004 | 2486 | 10.76 | 10.91 | 11.03 | 11.08 | 11.01 | 10.99 | 11.14 | 11.34 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 9.64 | 9.78 | 9.9 | 9.94 | 9.88 | 9.87 | 10 | 10.17 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 4.988 | 5.0595 | 5.1195 | 5.141 | 5.1095 | 5.103 | 5.171 | 5.2605 | 5.2255 | 5.2255 | 5.2255 | 5.2255 | 5.2255 | 5.2255 | 5.2255 | 5.2255 | 5.2255 | 5.2255 | 5.2255 | 5.2255 | 5.2255 | 0.0020064 | 0.0020352 | 0.0020593 | 0.002068 | 0.0020553 | 0.0020527 | 0.00208 | 0.002116 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102
| NKA005 | 599.5 | 4.77 | 4.82 | 4.84 | 4.85 | 4.8 | 4.79 | 4.84 | 4.89 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.28 | 4.32 | 4.34 | 4.34 | 4.32 | 4.3 | 4.34 | 4.38 | 4.34 | 4.34 | 4.34 | 4.34 | 4.34 | 4.34 | 4.34 | 4.34 | 4.34 | 4.34 | 4.34 | 4.34 | 4.34 | 2.2135 | 2.235 | 2.245 | 2.2465 | 2.232 | 2.2235 | 2.245 | 2.2665 | 2.245 | 2.245 | 2.245 | 2.245 | 2.245 | 2.245 | 2.245 | 2.245 | 2.245 | 2.245 | 2.245 | 2.245 | 2.245 | 0.0036922 | 0.0037281 | 0.0037448 | 0.0037473 | 0.0037231 | 0.0037089 | 0.0037448 | 0.0037807 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448
| NKA006 | 1364.5 | 9.43 | 9.68 | 9.75 | 9.72 | 9.64 | 9.68 | 9.83 | 9.9 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 9.71 | 8.44 | 8.7 | 8.77 | 8.73 | 8.66 | 8.7 | 8.82 | 8.89 | 8.72 | 8.72 | 8.72 | 8.72 | 8.72 | 8.72 | 8.72 | 8.72 | 8.72 | 8.72 | 8.72 | 8.72 | 8.72 | 4.3685 | 4.497 | 4.532 | 4.5135 | 4.477 | 4.497 | 4.5615 | 4.5965 | 4.5085 | 4.5085 | 4.5085 | 4.5085 | 4.5085 | 4.5085 | 4.5085 | 4.5085 | 4.5085 | 4.5085 | 4.5085 | 4.5085 | 4.5085 | 0.0032015 | 0.0032957 | 0.0033214 | 0.0033078 | 0.0032811 | 0.0032957 | 0.003343 | 0.0033686 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041
| NR022 | 9885.5 | 5.68 | 5.81 | 5.88 | 5.94 | 5.97 | 6.02 | 6.11 | 6.21 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 6.27 | 5.04 | 5.15 | 5.21 | 5.26 | 5.31 | 5.35 | 5.42 | 5.5 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 2.616 | 2.674 | 2.7055 | 2.732 | 2.754 | 2.7755 | 2.8135 | 2.8565 | 2.8795 | 2.8795 | 2.8795 | 2.8795 | 2.8795 | 2.8795 | 2.8795 | 2.8795 | 2.8795 | 2.8795 | 2.8795 | 2.8795 | 2.8795 | 0.00026463 | 0.0002705 | 0.00027368 | 0.00027636 | 0.00027859 | 0.00028076 | 0.00028461 | 0.00028896 | 0.00029129 | 0.00029129 | 0.00029129 | 0.00029129 | 0.00029129 | 0.00029129 | 0.00029129 | 0.00029129 | 0.00029129 | 0.00029129 | 0.00029129 | 0.00029129 | 0.00029129
| OYN001 | 888 | 1.96 | 1.96 | 1.95 | 1.94 | 1.91 | 1.89 | 1.89 | 1.89 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.76 | 1.77 | 1.76 | 1.75 | 1.72 | 1.7 | 1.69 | 1.69 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 0.91 | 0.9135 | 0.9085 | 0.9035 | 0.8885 | 0.8785 | 0.875 | 0.875 | 0.8635 | 0.8635 | 0.8635 | 0.8635 | 0.8635 | 0.8635 | 0.8635 | 0.8635 | 0.8635 | 0.8635 | 0.8635 | 0.8635 | 0.8635 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241
| OYN003 | 350.5 | 0.79 | 0.79 | 0.79 | 0.78 | 0.76 | 0.76 | 0.76 | 0.76 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.7 | 0.7 | 0.7 | 0.69 | 0.68 | 0.67 | 0.68 | 0.68 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.3635 | 0.3635 | 0.3635 | 0.3585 | 0.352 | 0.3485 | 0.352 | 0.352 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.342 | 0.0010371 | 0.0010371 | 0.0010371 | 0.0010228 | 0.0010043 | 0.00099429 | 0.0010043 | 0.0010043 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575
| OYN005 | 1275.5 | 3.43 | 3.44 | 3.42 | 3.39 | 3.33 | 3.29 | 3.27 | 3.26 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.18 | 3.18 | 3.17 | 3.14 | 3.09 | 3.05 | 3.04 | 3.03 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 1.6275 | 1.629 | 1.6225 | 1.6075 | 1.581 | 1.561 | 1.5545 | 1.5495 | 1.526 | 1.526 | 1.526 | 1.526 | 1.526 | 1.526 | 1.526 | 1.526 | 1.526 | 1.526 | 1.526 | 1.526 | 1.526 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964
| OYN007 | 655.5 | 2.43 | 2.39 | 2.37 | 2.33 | 2.28 | 2.25 | 2.23 | 2.21 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.17 | 2.16 | 2.13 | 2.11 | 2.07 | 2.03 | 2 | 1.99 | 1.97 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.1205 | 1.104 | 1.094 | 1.074 | 1.0525 | 1.0375 | 1.031 | 1.021 | 1.001 | 1.001 | 1.001 | 1.001 | 1.001 | 1.001 | 1.001 | 1.001 | 1.001 | 1.001 | 1.001 | 1.001 | 1.001 | 0.0017094 | 0.0016842 | 0.001669 | 0.0016384 | 0.0016056 | 0.0015828 | 0.0015728 | 0.0015576 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271
| PLD001 | 1934.5 | 4.63 | 4.6 | 4.59 | 4.55 | 4.49 | 4.47 | 4.48 | 4.48 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.29 | 4.26 | 4.25 | 4.21 | 4.16 | 4.14 | 4.15 | 4.15 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 2.196 | 2.181 | 2.176 | 2.156 | 2.1295 | 2.1195 | 2.1245 | 2.1245 | 2.096 | 2.096 | 2.096 | 2.096 | 2.096 | 2.096 | 2.096 | 2.096 | 2.096 | 2.096 | 2.096 | 2.096 | 2.096 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835
| PLD002 | 16 | 1.53 | 1.51 | 1.49 | 1.47 | 1.44 | 1.43 | 1.42 | 1.4 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.13 | 1.11 | 1.1 | 1.08 | 1.06 | 1.05 | 1.04 | 1.03 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 0.625 | 0.615 | 0.6085 | 0.5985 | 0.587 | 0.582 | 0.577 | 0.5705 | 0.564 | 0.564 | 0.564 | 0.564 | 0.564 | 0.564 | 0.564 | 0.564 | 0.564 | 0.564 | 0.564 | 0.564 | 0.564 | 0.039062 | 0.038438 | 0.038031 | 0.037406 | 0.036687 | 0.036375 | 0.036062 | 0.035656 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525
| PLD003 | 1113 | 2.37 | 2.36 | 2.37 | 2.35 | 2.32 | 2.32 | 2.33 | 2.34 | 2.29 | 2.29 | 2.29 | 2.29 | 2.29 | 2.29 | 2.29 | 2.29 | 2.29 | 2.29 | 2.29 | 2.29 | 2.29 | 2.22 | 2.21 | 2.22 | 2.2 | 2.17 | 2.17 | 2.18 | 2.19 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 1.1325 | 1.1275 | 1.1325 | 1.1225 | 1.1075 | 1.1075 | 1.1125 | 1.1175 | 1.096 | 1.096 | 1.096 | 1.096 | 1.096 | 1.096 | 1.096 | 1.096 | 1.096 | 1.096 | 1.096 | 1.096 | 1.096 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473
| PLD004 | 2874 | 6.6 | 6.6 | 6.66 | 6.69 | 6.7 | 6.76 | 6.87 | 6.95 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.03 | 6.05 | 6.09 | 6.13 | 6.16 | 6.22 | 6.32 | 6.39 | 6.41 | 6.41 | 6.41 | 6.41 | 6.41 | 6.41 | 6.41 | 6.41 | 6.41 | 6.41 | 6.41 | 6.41 | 6.41 | 3.1005 | 3.1075 | 3.1305 | 3.149 | 3.161 | 3.191 | 3.2425 | 3.279 | 3.289 | 3.289 | 3.289 | 3.289 | 3.289 | 3.289 | 3.289 | 3.289 | 3.289 | 3.289 | 3.289 | 3.289 | 3.289 | 0.0010788 | 0.0010812 | 0.0010892 | 0.0010957 | 0.0010999 | 0.0011103 | 0.0011282 | 0.0011409 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444
| PLD005 | 174.5 | 2.74 | 2.71 | 2.68 | 2.63 | 2.58 | 2.55 | 2.53 | 2.5 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 2.42 | 2.39 | 2.36 | 2.32 | 2.28 | 2.25 | 2.24 | 2.22 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 2.19 | 1.258 | 1.243 | 1.228 | 1.2065 | 1.185 | 1.17 | 1.1635 | 1.152 | 1.137 | 1.137 | 1.137 | 1.137 | 1.137 | 1.137 | 1.137 | 1.137 | 1.137 | 1.137 | 1.137 | 1.137 | 1.137 | 0.0072092 | 0.0071232 | 0.0070372 | 0.006914 | 0.0067908 | 0.0067049 | 0.0066676 | 0.0066017 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158
| PLD006 | 3422.5 | 5.21 | 5.26 | 5.34 | 5.41 | 5.48 | 5.57 | 5.7 | 5.79 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 4.95 | 5 | 5.09 | 5.16 | 5.22 | 5.31 | 5.43 | 5.52 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 5.57 | 2.514 | 2.539 | 2.5825 | 2.6175 | 2.649 | 2.694 | 2.7555 | 2.8005 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 2.8255 | 0.00073455 | 0.00074186 | 0.00075457 | 0.00076479 | 0.000774 | 0.00078714 | 0.00080511 | 0.00081826 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557
| RCT011 | 810.5 | 4.23 | 4.3 | 4.35 | 4.38 | 4.38 | 4.4 | 4.46 | 4.53 | 4.54 | 4.54 | 4.54 | 4.54 | 4.54 | 4.54 | 4.54 | 4.54 | 4.54 | 4.54 | 4.54 | 4.54 | 4.54 | 3.87 | 3.93 | 3.97 | 4 | 4 | 4.02 | 4.07 | 4.13 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 4.14 | 1.989 | 2.0205 | 2.042 | 2.057 | 2.057 | 2.067 | 2.0935 | 2.125 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 2.13 | 0.002454 | 0.0024929 | 0.0025194 | 0.0025379 | 0.0025379 | 0.0025503 | 0.002583 | 0.0026218 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628
| RCT012 | 1 | 2.49 | 2.49 | 2.46 | 2.43 | 2.4 | 2.37 | 2.35 | 2.33 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.31 | 2.26 | 2.26 | 2.23 | 2.2 | 2.18 | 2.15 | 2.13 | 2.11 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 2.09 | 1.1645 | 1.1645 | 1.1495 | 1.1345 | 1.123 | 1.108 | 1.098 | 1.088 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.1645 | 1.1645 | 1.1495 | 1.1345 | 1.123 | 1.108 | 1.098 | 1.088 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078
| RCT013 | 631.5 | 11.43 | 12.02 | 11.97 | 11.88 | 11.69 | 11.56 | 11.6 | 11.68 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 10.88 | 11.49 | 11.43 | 11.35 | 11.17 | 11.05 | 11.09 | 11.16 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 5.5225 | 5.8245 | 5.796 | 5.7545 | 5.663 | 5.6015 | 5.6215 | 5.658 | 5.588 | 5.588 | 5.588 | 5.588 | 5.588 | 5.588 | 5.588 | 5.588 | 5.588 | 5.588 | 5.588 | 5.588 | 5.588 | 0.0087451 | 0.0092233 | 0.0091781 | 0.0091124 | 0.0089675 | 0.0088702 | 0.0089018 | 0.0089596 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488
| RCT014 | 350.5 | 9.82 | 9.88 | 9.83 | 9.76 | 9.65 | 9.57 | 9.58 | 9.62 | 9.53 | 9.53 | 9.53 | 9.53 | 9.53 | 9.53 | 9.53 | 9.53 | 9.53 | 9.53 | 9.53 | 9.53 | 9.53 | 9.08 | 9.18 | 9.13 | 9.07 | 8.97 | 8.9 | 8.91 | 8.94 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 8.86 | 4.651 | 4.695 | 4.67 | 4.6385 | 4.587 | 4.5505 | 4.5555 | 4.572 | 4.5305 | 4.5305 | 4.5305 | 4.5305 | 4.5305 | 4.5305 | 4.5305 | 4.5305 | 4.5305 | 4.5305 | 4.5305 | 4.5305 | 4.5305 | 0.01327 | 0.013395 | 0.013324 | 0.013234 | 0.013087 | 0.012983 | 0.012997 | 0.013044 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926
| RCT015 | 20 | 2.98 | 3 | 2.98 | 2.95 | 2.92 | 2.9 | 2.88 | 2.87 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.49 | 2.51 | 2.49 | 2.47 | 2.44 | 2.42 | 2.41 | 2.4 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 1.3185 | 1.3285 | 1.3185 | 1.307 | 1.292 | 1.282 | 1.2755 | 1.2705 | 1.2605 | 1.2605 | 1.2605 | 1.2605 | 1.2605 | 1.2605 | 1.2605 | 1.2605 | 1.2605 | 1.2605 | 1.2605 | 1.2605 | 1.2605 | 0.065925 | 0.066425 | 0.065925 | 0.06535 | 0.0646 | 0.0641 | 0.063775 | 0.063525 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025
| RCT021 | 654.5 | 6.68 | 6.72 | 6.75 | 6.75 | 6.71 | 6.69 | 6.73 | 6.8 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 6.75 | 5.78 | 5.82 | 5.84 | 5.84 | 5.8 | 5.78 | 5.82 | 5.87 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 3.025 | 3.045 | 3.0565 | 3.0565 | 3.0365 | 3.0265 | 3.0465 | 3.0745 | 3.053 | 3.053 | 3.053 | 3.053 | 3.053 | 3.053 | 3.053 | 3.053 | 3.053 | 3.053 | 3.053 | 3.053 | 3.053 | 0.0046218 | 0.0046524 | 0.00467 | 0.00467 | 0.0046394 | 0.0046241 | 0.0046547 | 0.0046975 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646
| RCT022 | 838 | 10.32 | 10.41 | 10.61 | 10.63 | 10.54 | 10.63 | 10.91 | 11.11 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 7.77 | 7.9 | 8.03 | 8.08 | 8.01 | 8.03 | 8.21 | 8.4 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 4.2675 | 4.3265 | 4.402 | 4.4225 | 4.3845 | 4.405 | 4.51 | 4.6065 | 4.5325 | 4.5325 | 4.5325 | 4.5325 | 4.5325 | 4.5325 | 4.5325 | 4.5325 | 4.5325 | 4.5325 | 4.5325 | 4.5325 | 4.5325 | 0.0050925 | 0.0051629 | 0.005253 | 0.0052774 | 0.0052321 | 0.0052566 | 0.0053819 | 0.005497 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087
| RCT023 | 2208.5 | 9.98 | 10.05 | 10.1 | 10.05 | 9.93 | 9.88 | 10 | 10.13 | 10.05 | 10.05 | 10.05 | 10.05 | 10.05 | 10.05 | 10.05 | 10.05 | 10.05 | 10.05 | 10.05 | 10.05 | 10.05 | 8.65 | 8.74 | 8.8 | 8.81 | 8.73 | 8.69 | 8.79 | 8.91 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 4.5245 | 4.5665 | 4.595 | 4.591 | 4.545 | 4.5235 | 4.5765 | 4.638 | 4.6015 | 4.6015 | 4.6015 | 4.6015 | 4.6015 | 4.6015 | 4.6015 | 4.6015 | 4.6015 | 4.6015 | 4.6015 | 4.6015 | 4.6015 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835
| RVL001 | 858 | 8.6 | 9.13 | 9.17 | 9.16 | 9.13 | 9.12 | 9.18 | 9.26 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 7.87 | 8.36 | 8.4 | 8.41 | 8.37 | 8.37 | 8.43 | 8.5 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 4.0445 | 4.2955 | 4.3155 | 4.3175 | 4.299 | 4.2975 | 4.3275 | 4.364 | 4.346 | 4.346 | 4.346 | 4.346 | 4.346 | 4.346 | 4.346 | 4.346 | 4.346 | 4.346 | 4.346 | 4.346 | 4.346 | 0.0047139 | 0.0050064 | 0.0050297 | 0.0050321 | 0.0050105 | 0.0050087 | 0.0050437 | 0.0050862 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653
| RVL004 | 231 | 13.92 | 14.28 | 14.43 | 14.58 | 14.56 | 14.52 | 14.71 | 14.99 | 15.03 | 15.03 | 15.03 | 15.03 | 15.03 | 15.03 | 15.03 | 15.03 | 15.03 | 15.03 | 15.03 | 15.03 | 15.03 | 10.45 | 10.67 | 10.8 | 10.89 | 10.86 | 10.85 | 11.02 | 11.21 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 5.7455 | 5.8765 | 5.9445 | 5.9985 | 5.985 | 5.9755 | 6.0635 | 6.172 | 6.1745 | 6.1745 | 6.1745 | 6.1745 | 6.1745 | 6.1745 | 6.1745 | 6.1745 | 6.1745 | 6.1745 | 6.1745 | 6.1745 | 6.1745 | 0.024872 | 0.025439 | 0.025734 | 0.025968 | 0.025909 | 0.025868 | 0.026249 | 0.026719 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729
| RVL006 | 584.5 | 7.67 | 7.76 | 7.77 | 7.79 | 7.77 | 7.75 | 7.78 | 7.82 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 7.83 | 6.86 | 6.93 | 6.93 | 6.95 | 6.91 | 6.89 | 6.91 | 6.95 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 6.96 | 3.5515 | 3.5895 | 3.591 | 3.601 | 3.584 | 3.574 | 3.5855 | 3.6055 | 3.6105 | 3.6105 | 3.6105 | 3.6105 | 3.6105 | 3.6105 | 3.6105 | 3.6105 | 3.6105 | 3.6105 | 3.6105 | 3.6105 | 3.6105 | 0.0060761 | 0.0061411 | 0.0061437 | 0.0061608 | 0.0061317 | 0.0061146 | 0.0061343 | 0.0061685 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771
| RVL008 | 215 | 7.82 | 9.24 | 9.38 | 9.46 | 9.43 | 9.43 | 9.58 | 9.78 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 7.08 | 8.36 | 8.49 | 8.55 | 8.52 | 8.52 | 8.67 | 8.84 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 3.651 | 4.312 | 4.3785 | 4.4115 | 4.3965 | 4.3965 | 4.4715 | 4.561 | 4.551 | 4.551 | 4.551 | 4.551 | 4.551 | 4.551 | 4.551 | 4.551 | 4.551 | 4.551 | 4.551 | 4.551 | 4.551 | 0.016981 | 0.020056 | 0.020365 | 0.020519 | 0.020449 | 0.020449 | 0.020798 | 0.021214 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167
| SA001 | 1933 | 4.32 | 4.42 | 4.56 | 4.68 | 4.8 | 4.94 | 5.11 | 5.25 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 5.36 | 3.98 | 4.09 | 4.22 | 4.34 | 4.45 | 4.59 | 4.75 | 4.89 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 2.041 | 2.0945 | 2.161 | 2.221 | 2.2775 | 2.3475 | 2.429 | 2.499 | 2.5505 | 2.5505 | 2.5505 | 2.5505 | 2.5505 | 2.5505 | 2.5505 | 2.5505 | 2.5505 | 2.5505 | 2.5505 | 2.5505 | 2.5505 | 0.0010559 | 0.0010835 | 0.001118 | 0.001149 | 0.0011782 | 0.0012144 | 0.0012566 | 0.0012928 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195
| SA002 | 2669.5 | 8.01 | 8.02 | 8.03 | 8.02 | 7.98 | 7.94 | 7.98 | 8.02 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.4 | 7.43 | 7.45 | 7.44 | 7.39 | 7.37 | 7.39 | 7.43 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 3.7915 | 3.8035 | 3.812 | 3.807 | 3.7835 | 3.7705 | 3.7835 | 3.8035 | 3.792 | 3.792 | 3.792 | 3.792 | 3.792 | 3.792 | 3.792 | 3.792 | 3.792 | 3.792 | 3.792 | 3.792 | 3.792 | 0.0014203 | 0.0014248 | 0.001428 | 0.0014261 | 0.0014173 | 0.0014124 | 0.0014173 | 0.0014248 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205
| SA003 | 3078 | 8.47 | 8.52 | 8.59 | 8.62 | 8.58 | 8.6 | 8.72 | 8.86 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 7.5 | 7.52 | 7.55 | 7.57 | 7.55 | 7.55 | 7.65 | 7.78 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 7.79 | 3.8955 | 3.91 | 3.931 | 3.9425 | 3.9295 | 3.9325 | 3.9855 | 4.052 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 4.0525 | 0.0012656 | 0.0012703 | 0.0012771 | 0.0012809 | 0.0012766 | 0.0012776 | 0.0012948 | 0.0013164 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166
| SA004 | 2655 | 5.37 | 5.44 | 5.49 | 5.53 | 5.57 | 5.62 | 5.7 | 5.8 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 4.83 | 4.88 | 4.92 | 4.98 | 5.03 | 5.16 | 5.32 | 5.46 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 5.56 | 2.496 | 2.524 | 2.5455 | 2.5725 | 2.596 | 2.649 | 2.717 | 2.781 | 2.828 | 2.828 | 2.828 | 2.828 | 2.828 | 2.828 | 2.828 | 2.828 | 2.828 | 2.828 | 2.828 | 2.828 | 2.828 | 0.00094011 | 0.00095066 | 0.00095876 | 0.00096893 | 0.00097778 | 0.00099774 | 0.0010234 | 0.0010475 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652
| SA005 | 3710.5 | 8.31 | 8.42 | 8.48 | 8.47 | 8.5 | 8.55 | 8.65 | 8.76 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 8.95 | 7.61 | 7.7 | 7.75 | 7.81 | 7.83 | 7.86 | 8.12 | 8.37 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 3.91 | 3.958 | 3.9845 | 4.004 | 4.0155 | 4.0335 | 4.1395 | 4.2435 | 4.335 | 4.335 | 4.335 | 4.335 | 4.335 | 4.335 | 4.335 | 4.335 | 4.335 | 4.335 | 4.335 | 4.335 | 4.335 | 0.0010538 | 0.0010667 | 0.0010738 | 0.0010791 | 0.0010822 | 0.0010871 | 0.0011156 | 0.0011436 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683
| SA006 | 2176.5 | 6.74 | 6.76 | 6.73 | 6.71 | 6.65 | 6.61 | 6.61 | 6.62 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.58 | 6.1 | 6.11 | 6.09 | 6.07 | 6.02 | 5.99 | 5.99 | 6 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 5.97 | 3.146 | 3.1525 | 3.141 | 3.131 | 3.1045 | 3.088 | 3.088 | 3.093 | 3.0765 | 3.0765 | 3.0765 | 3.0765 | 3.0765 | 3.0765 | 3.0765 | 3.0765 | 3.0765 | 3.0765 | 3.0765 | 3.0765 | 3.0765 | 0.0014454 | 0.0014484 | 0.0014431 | 0.0014385 | 0.0014264 | 0.0014188 | 0.0014188 | 0.0014211 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135
| SA007 | 7103.5 | 17.34 | 17.69 | 17.99 | 18.24 | 18.47 | 19.6 | 20.78 | 21.86 | 22.75 | 22.75 | 22.75 | 22.75 | 22.75 | 22.75 | 22.75 | 22.75 | 22.75 | 22.75 | 22.75 | 22.75 | 22.75 | 15.79 | 16.08 | 16.38 | 16.7 | 17.67 | 18.74 | 19.87 | 20.89 | 21.73 | 21.73 | 21.73 | 21.73 | 21.73 | 21.73 | 21.73 | 21.73 | 21.73 | 21.73 | 21.73 | 21.73 | 21.73 | 8.1275 | 8.2815 | 8.4315 | 8.581 | 8.955 | 9.499 | 10.0715 | 10.5905 | 11.018 | 11.018 | 11.018 | 11.018 | 11.018 | 11.018 | 11.018 | 11.018 | 11.018 | 11.018 | 11.018 | 11.018 | 11.018 | 0.0011442 | 0.0011658 | 0.001187 | 0.001208 | 0.0012606 | 0.0013372 | 0.0014178 | 0.0014909 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511
| SA009 | 5448 | 12.58 | 12.9 | 13.12 | 13.37 | 13.54 | 13.76 | 14.4 | 15.21 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 15.89 | 11.25 | 11.52 | 11.75 | 11.97 | 12.1 | 12.64 | 13.47 | 14.2 | 14.83 | 14.83 | 14.83 | 14.83 | 14.83 | 14.83 | 14.83 | 14.83 | 14.83 | 14.83 | 14.83 | 14.83 | 14.83 | 5.8245 | 5.967 | 6.0805 | 6.195 | 6.266 | 6.488 | 6.8745 | 7.2515 | 7.574 | 7.574 | 7.574 | 7.574 | 7.574 | 7.574 | 7.574 | 7.574 | 7.574 | 7.574 | 7.574 | 7.574 | 7.574 | 0.0010691 | 0.0010953 | 0.0011161 | 0.0011371 | 0.0011501 | 0.0011909 | 0.0012618 | 0.001331 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902
| SA010 | 2686.5 | 7.34 | 7.38 | 7.36 | 7.34 | 7.27 | 7.24 | 7.28 | 7.34 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 7.32 | 6.69 | 6.72 | 6.71 | 6.7 | 6.64 | 6.62 | 6.66 | 6.72 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 3.4425 | 3.459 | 3.4525 | 3.446 | 3.4145 | 3.403 | 3.423 | 3.453 | 3.4465 | 3.4465 | 3.4465 | 3.4465 | 3.4465 | 3.4465 | 3.4465 | 3.4465 | 3.4465 | 3.4465 | 3.4465 | 3.4465 | 3.4465 | 0.0012814 | 0.0012875 | 0.0012851 | 0.0012827 | 0.001271 | 0.0012667 | 0.0012741 | 0.0012853 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829
| SA011 | 4064.5 | 12.21 | 12.44 | 12.61 | 12.74 | 12.83 | 12.97 | 13.46 | 14.14 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 11.17 | 11.38 | 11.54 | 11.7 | 11.8 | 11.94 | 12.59 | 13.2 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 5.741 | 5.849 | 5.9305 | 6.006 | 6.0545 | 6.1245 | 6.4255 | 6.741 | 7.014 | 7.014 | 7.014 | 7.014 | 7.014 | 7.014 | 7.014 | 7.014 | 7.014 | 7.014 | 7.014 | 7.014 | 7.014 | 0.0014125 | 0.001439 | 0.0014591 | 0.0014777 | 0.0014896 | 0.0015068 | 0.0015809 | 0.0016585 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257
| SA012 | 271.5 | 8.94 | 8.93 | 8.79 | 8.64 | 8.49 | 8.34 | 8.24 | 8.14 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.03 | 8.1 | 8.11 | 7.98 | 7.85 | 7.71 | 7.58 | 7.49 | 7.4 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 7.29 | 4.176 | 4.178 | 4.1115 | 4.0435 | 3.972 | 3.904 | 3.8575 | 3.811 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 3.756 | 0.015381 | 0.015389 | 0.015144 | 0.014893 | 0.01463 | 0.014379 | 0.014208 | 0.014037 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834
| SHL001 | 342 | 2.26 | 2.21 | 2.17 | 2.12 | 2.07 | 2.03 | 2.01 | 1.98 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 2.04 | 2 | 1.96 | 1.91 | 1.87 | 1.83 | 1.81 | 1.78 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.74 | 1.053 | 1.0315 | 1.0115 | 0.9865 | 0.965 | 0.945 | 0.935 | 0.92 | 0.8985 | 0.8985 | 0.8985 | 0.8985 | 0.8985 | 0.8985 | 0.8985 | 0.8985 | 0.8985 | 0.8985 | 0.8985 | 0.8985 | 0.8985 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272
| SHL002 | 1218 | 14.36 | 14.33 | 14.19 | 13.99 | 13.72 | 13.48 | 13.39 | 13.35 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 12.55 | 12.52 | 12.39 | 12.21 | 11.97 | 11.78 | 11.68 | 11.66 | 11.47 | 11.47 | 11.47 | 11.47 | 11.47 | 11.47 | 11.47 | 11.47 | 11.47 | 11.47 | 11.47 | 11.47 | 11.47 | 6.5465 | 6.5315 | 6.465 | 6.372 | 6.2475 | 6.145 | 6.0965 | 6.0835 | 5.987 | 5.987 | 5.987 | 5.987 | 5.987 | 5.987 | 5.987 | 5.987 | 5.987 | 5.987 | 5.987 | 5.987 | 5.987 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154
| SHL004 | 1436.5 | 8.93 | 8.93 | 8.86 | 8.75 | 8.59 | 8.47 | 8.43 | 8.41 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.2 | 8.2 | 8.14 | 8.05 | 7.91 | 7.79 | 7.76 | 7.76 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 7.65 | 4.2095 | 4.2095 | 4.178 | 4.13 | 4.057 | 3.997 | 3.9805 | 3.9775 | 3.9225 | 3.9225 | 3.9225 | 3.9225 | 3.9225 | 3.9225 | 3.9225 | 3.9225 | 3.9225 | 3.9225 | 3.9225 | 3.9225 | 3.9225 | 0.0029304 | 0.0029304 | 0.0029085 | 0.002875 | 0.0028242 | 0.0027825 | 0.002771 | 0.0027689 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306
| SHL005 | 1142 | 4.08 | 4.07 | 4.05 | 4.01 | 3.95 | 3.91 | 3.91 | 3.91 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.78 | 3.78 | 3.76 | 3.74 | 3.68 | 3.64 | 3.63 | 3.64 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 1.935 | 1.9335 | 1.9235 | 1.9105 | 1.8805 | 1.8605 | 1.857 | 1.8605 | 1.8355 | 1.8355 | 1.8355 | 1.8355 | 1.8355 | 1.8355 | 1.8355 | 1.8355 | 1.8355 | 1.8355 | 1.8355 | 1.8355 | 1.8355 | 0.0016944 | 0.0016931 | 0.0016843 | 0.0016729 | 0.0016467 | 0.0016292 | 0.0016261 | 0.0016292 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073
| SHL007 | 2061 | 8.86 | 8.79 | 8.68 | 8.56 | 8.4 | 8.27 | 8.19 | 8.14 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.22 | 8.16 | 8.05 | 7.93 | 7.78 | 7.66 | 7.59 | 7.53 | 7.43 | 7.43 | 7.43 | 7.43 | 7.43 | 7.43 | 7.43 | 7.43 | 7.43 | 7.43 | 7.43 | 7.43 | 7.43 | 4.206 | 4.1745 | 4.1195 | 4.0595 | 3.983 | 3.9215 | 3.885 | 3.8565 | 3.8035 | 3.8035 | 3.8035 | 3.8035 | 3.8035 | 3.8035 | 3.8035 | 3.8035 | 3.8035 | 3.8035 | 3.8035 | 3.8035 | 3.8035 | 0.0020408 | 0.0020255 | 0.0019988 | 0.0019697 | 0.0019326 | 0.0019027 | 0.001885 | 0.0018712 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455
| SHL008 | 2682 | 10.5 | 10.32 | 10.04 | 9.76 | 9.48 | 9.18 | 9.11 | 9.05 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 9.36 | 9.23 | 9.07 | 8.9 | 8.7 | 8.54 | 8.49 | 8.44 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 8.28 | 4.851 | 4.7785 | 4.6805 | 4.579 | 4.467 | 4.366 | 4.338 | 4.3115 | 4.233 | 4.233 | 4.233 | 4.233 | 4.233 | 4.233 | 4.233 | 4.233 | 4.233 | 4.233 | 4.233 | 4.233 | 4.233 | 0.0018087 | 0.0017817 | 0.0017452 | 0.0017073 | 0.0016655 | 0.0016279 | 0.0016174 | 0.0016076 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783
| SHN011 | 1767 | 7.22 | 7.3 | 7.38 | 7.41 | 7.38 | 7.39 | 7.49 | 7.61 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 6.59 | 6.66 | 6.73 | 6.77 | 6.75 | 6.76 | 6.86 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 6.97 | 3.3895 | 3.426 | 3.4625 | 3.481 | 3.4695 | 3.4745 | 3.5245 | 3.581 | 3.5765 | 3.5765 | 3.5765 | 3.5765 | 3.5765 | 3.5765 | 3.5765 | 3.5765 | 3.5765 | 3.5765 | 3.5765 | 3.5765 | 3.5765 | 0.0019182 | 0.0019389 | 0.0019595 | 0.00197 | 0.0019635 | 0.0019663 | 0.0019946 | 0.0020266 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241
| SHN012 | 2575.5 | 8.22 | 8.41 | 8.5 | 8.57 | 8.59 | 8.63 | 8.73 | 8.85 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 8.88 | 7.85 | 8.03 | 8.1 | 8.15 | 8.15 | 8.18 | 8.26 | 8.37 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 3.9805 | 4.072 | 4.11 | 4.138 | 4.141 | 4.1575 | 4.2005 | 4.257 | 4.2685 | 4.2685 | 4.2685 | 4.2685 | 4.2685 | 4.2685 | 4.2685 | 4.2685 | 4.2685 | 4.2685 | 4.2685 | 4.2685 | 4.2685 | 0.0015455 | 0.0015811 | 0.0015958 | 0.0016067 | 0.0016078 | 0.0016142 | 0.0016309 | 0.0016529 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573
| SHN014 | 355 | 5.44 | 5.5 | 5.53 | 5.54 | 5.5 | 5.49 | 5.55 | 5.62 | 5.59 | 5.59 | 5.59 | 5.59 | 5.59 | 5.59 | 5.59 | 5.59 | 5.59 | 5.59 | 5.59 | 5.59 | 5.59 | 4.64 | 4.69 | 4.72 | 4.72 | 4.69 | 4.68 | 4.73 | 4.79 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 4.77 | 2.44 | 2.4665 | 2.4815 | 2.483 | 2.4665 | 2.4615 | 2.488 | 2.5195 | 2.508 | 2.508 | 2.508 | 2.508 | 2.508 | 2.508 | 2.508 | 2.508 | 2.508 | 2.508 | 2.508 | 2.508 | 2.508 | 0.0068732 | 0.0069479 | 0.0069901 | 0.0069944 | 0.0069479 | 0.0069338 | 0.0070085 | 0.0070972 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648
| SHN021 | 2426.5 | 7.56 | 7.69 | 7.76 | 7.82 | 7.83 | 7.87 | 7.97 | 8.09 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 6.81 | 6.92 | 6.99 | 7.05 | 7.06 | 7.1 | 7.2 | 7.29 | 7.33 | 7.33 | 7.33 | 7.33 | 7.33 | 7.33 | 7.33 | 7.33 | 7.33 | 7.33 | 7.33 | 7.33 | 7.33 | 3.5175 | 3.5755 | 3.6105 | 3.6405 | 3.6455 | 3.6655 | 3.7155 | 3.765 | 3.7865 | 3.7865 | 3.7865 | 3.7865 | 3.7865 | 3.7865 | 3.7865 | 3.7865 | 3.7865 | 3.7865 | 3.7865 | 3.7865 | 3.7865 | 0.0014496 | 0.0014735 | 0.0014879 | 0.0015003 | 0.0015024 | 0.0015106 | 0.0015312 | 0.0015516 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605
| SHN022 | 1882.5 | 3.42 | 3.56 | 3.56 | 3.56 | 3.54 | 3.53 | 3.55 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.57 | 3.26 | 3.39 | 3.39 | 3.38 | 3.36 | 3.36 | 3.37 | 3.39 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 1.654 | 1.7205 | 1.7205 | 1.717 | 1.707 | 1.7055 | 1.712 | 1.722 | 1.7185 | 1.7185 | 1.7185 | 1.7185 | 1.7185 | 1.7185 | 1.7185 | 1.7185 | 1.7185 | 1.7185 | 1.7185 | 1.7185 | 1.7185 | 0.00087862 | 0.00091394 | 0.00091394 | 0.00091209 | 0.00090677 | 0.00090598 | 0.00090943 | 0.00091474 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288
| SHN023 | 1002.5 | 4.39 | 4.38 | 4.35 | 4.28 | 4.25 | 4.32 | 4.42 | 4.51 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.53 | 4.03 | 4.02 | 3.97 | 3.92 | 3.94 | 4.01 | 4.11 | 4.19 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 2.069 | 2.064 | 2.042 | 2.014 | 2.0165 | 2.0515 | 2.1015 | 2.143 | 2.153 | 2.153 | 2.153 | 2.153 | 2.153 | 2.153 | 2.153 | 2.153 | 2.153 | 2.153 | 2.153 | 2.153 | 2.153 | 0.0020638 | 0.0020589 | 0.0020369 | 0.002009 | 0.0020115 | 0.0020464 | 0.0020963 | 0.0021377 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476
| SHN024 | 1073 | 7.41 | 7.53 | 7.64 | 7.71 | 7.72 | 7.76 | 7.9 | 8.05 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 5.8 | 5.9 | 5.98 | 6.03 | 6.03 | 6.07 | 6.18 | 6.31 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 6.29 | 3.1415 | 3.1945 | 3.239 | 3.267 | 3.2685 | 3.2885 | 3.348 | 3.416 | 3.403 | 3.403 | 3.403 | 3.403 | 3.403 | 3.403 | 3.403 | 3.403 | 3.403 | 3.403 | 3.403 | 3.403 | 3.403 | 0.0029278 | 0.0029772 | 0.0030186 | 0.0030447 | 0.0030461 | 0.0030648 | 0.0031202 | 0.0031836 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715
| SHP011 | 706 | 8.23 | 8.24 | 8.16 | 8.07 | 7.96 | 7.89 | 7.85 | 7.82 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.55 | 7.55 | 7.47 | 7.4 | 7.32 | 7.25 | 7.22 | 7.18 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 3.877 | 3.8785 | 3.8385 | 3.8005 | 3.756 | 3.721 | 3.7045 | 3.686 | 3.641 | 3.641 | 3.641 | 3.641 | 3.641 | 3.641 | 3.641 | 3.641 | 3.641 | 3.641 | 3.641 | 3.641 | 3.641 | 0.0054915 | 0.0054936 | 0.005437 | 0.0053831 | 0.0053201 | 0.0052705 | 0.0052472 | 0.005221 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572
| SHP012 | 2262 | 7.82 | 7.89 | 7.95 | 7.98 | 7.89 | 7.88 | 7.97 | 8.08 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 7.12 | 7.2 | 7.26 | 7.29 | 7.25 | 7.24 | 7.33 | 7.43 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 3.665 | 3.7035 | 3.7335 | 3.7485 | 3.721 | 3.716 | 3.761 | 3.8125 | 3.796 | 3.796 | 3.796 | 3.796 | 3.796 | 3.796 | 3.796 | 3.796 | 3.796 | 3.796 | 3.796 | 3.796 | 3.796 | 0.0016202 | 0.0016373 | 0.0016505 | 0.0016572 | 0.001645 | 0.0016428 | 0.0016627 | 0.0016855 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782
| SHP014 | 1669 | 5.86 | 5.81 | 5.84 | 5.82 | 5.77 | 5.74 | 5.76 | 5.79 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 5.74 | 4.96 | 4.98 | 4.98 | 4.97 | 4.92 | 4.89 | 4.9 | 4.94 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 4.89 | 2.615 | 2.6145 | 2.619 | 2.6125 | 2.5875 | 2.5725 | 2.579 | 2.5975 | 2.5725 | 2.5725 | 2.5725 | 2.5725 | 2.5725 | 2.5725 | 2.5725 | 2.5725 | 2.5725 | 2.5725 | 2.5725 | 2.5725 | 2.5725 | 0.0015668 | 0.0015665 | 0.0015692 | 0.0015653 | 0.0015503 | 0.0015413 | 0.0015452 | 0.0015563 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413
| SHP021 | 717.5 | 4.98 | 4.77 | 4.75 | 4.65 | 4.53 | 4.4 | 4.39 | 4.41 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 4.43 | 3.55 | 3.57 | 3.58 | 3.57 | 3.54 | 3.52 | 3.53 | 3.55 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 1.9895 | 1.965 | 1.9655 | 1.947 | 1.9185 | 1.892 | 1.894 | 1.904 | 1.8965 | 1.8965 | 1.8965 | 1.8965 | 1.8965 | 1.8965 | 1.8965 | 1.8965 | 1.8965 | 1.8965 | 1.8965 | 1.8965 | 1.8965 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432
| SSE011 | 1135.5 | 12.47 | 12.65 | 12.57 | 12.48 | 12.38 | 12.29 | 12.26 | 12.25 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.21 | 12.09 | 12.24 | 12.17 | 12.1 | 12 | 11.93 | 11.89 | 11.9 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 11.85 | 6.102 | 6.1815 | 6.145 | 6.107 | 6.057 | 6.019 | 6.0005 | 6.0025 | 5.979 | 5.979 | 5.979 | 5.979 | 5.979 | 5.979 | 5.979 | 5.979 | 5.979 | 5.979 | 5.979 | 5.979 | 5.979 | 0.0053738 | 0.0054439 | 0.0054117 | 0.0053782 | 0.0053342 | 0.0053007 | 0.0052845 | 0.0052862 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655
| SSE012 | 3006.5 | 6.23 | 6.33 | 6.49 | 6.6 | 6.72 | 6.86 | 7.09 | 7.27 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 7.31 | 5.87 | 5.98 | 6.12 | 6.24 | 6.33 | 6.5 | 6.71 | 6.88 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 6.95 | 2.989 | 3.0425 | 3.1155 | 3.174 | 3.2235 | 3.304 | 3.412 | 3.4985 | 3.529 | 3.529 | 3.529 | 3.529 | 3.529 | 3.529 | 3.529 | 3.529 | 3.529 | 3.529 | 3.529 | 3.529 | 3.529 | 0.00099418 | 0.001012 | 0.0010363 | 0.0010557 | 0.0010722 | 0.001099 | 0.0011349 | 0.0011636 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738
| SSE013 | 2118.5 | 8.18 | 8.16 | 8.1 | 8.05 | 8.07 | 8.15 | 8.27 | 8.34 | 8.36 | 8.36 | 8.36 | 8.36 | 8.36 | 8.36 | 8.36 | 8.36 | 8.36 | 8.36 | 8.36 | 8.36 | 8.36 | 7.6 | 7.6 | 7.53 | 7.43 | 7.32 | 7.24 | 7.25 | 7.29 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 7.26 | 3.887 | 3.884 | 3.8505 | 3.808 | 3.7725 | 3.7565 | 3.778 | 3.8025 | 3.795 | 3.795 | 3.795 | 3.795 | 3.795 | 3.795 | 3.795 | 3.795 | 3.795 | 3.795 | 3.795 | 3.795 | 3.795 | 0.0018348 | 0.0018334 | 0.0018176 | 0.0017975 | 0.0017807 | 0.0017732 | 0.0017833 | 0.0017949 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914
| SSE014 | 3891 | 11.83 | 11.99 | 12.11 | 12.18 | 12.17 | 12.22 | 12.41 | 12.61 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 10.97 | 11.08 | 11.27 | 11.36 | 11.42 | 11.58 | 11.83 | 12.02 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 11.98 | 5.614 | 5.6765 | 5.761 | 5.803 | 5.8225 | 5.886 | 6.002 | 6.0985 | 6.0755 | 6.0755 | 6.0755 | 6.0755 | 6.0755 | 6.0755 | 6.0755 | 6.0755 | 6.0755 | 6.0755 | 6.0755 | 6.0755 | 6.0755 | 0.0014428 | 0.0014589 | 0.0014806 | 0.0014914 | 0.0014964 | 0.0015127 | 0.0015425 | 0.0015673 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614
| SSE031 | 5874.5 | 11.69 | 11.84 | 11.96 | 12.29 | 12.91 | 13.61 | 14.32 | 14.95 | 15.46 | 15.46 | 15.46 | 15.46 | 15.46 | 15.46 | 15.46 | 15.46 | 15.46 | 15.46 | 15.46 | 15.46 | 15.46 | 10.53 | 10.65 | 10.73 | 11.27 | 11.82 | 12.44 | 13.09 | 13.65 | 14.11 | 14.11 | 14.11 | 14.11 | 14.11 | 14.11 | 14.11 | 14.11 | 14.11 | 14.11 | 14.11 | 14.11 | 14.11 | 5.439 | 5.5035 | 5.5495 | 5.788 | 6.0735 | 6.3955 | 6.7295 | 7.02 | 7.2575 | 7.2575 | 7.2575 | 7.2575 | 7.2575 | 7.2575 | 7.2575 | 7.2575 | 7.2575 | 7.2575 | 7.2575 | 7.2575 | 7.2575 | 0.00092587 | 0.00093685 | 0.00094468 | 0.00098528 | 0.0010339 | 0.0010887 | 0.0011455 | 0.001195 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354
| SSE032 | 2957 | 10.74 | 10.77 | 10.68 | 10.62 | 10.47 | 10.38 | 10.58 | 10.77 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 10.76 | 9.58 | 9.57 | 9.55 | 9.62 | 9.66 | 9.8 | 10.04 | 10.19 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 4.964 | 4.965 | 4.9445 | 4.96 | 4.9515 | 4.987 | 5.101 | 5.182 | 5.177 | 5.177 | 5.177 | 5.177 | 5.177 | 5.177 | 5.177 | 5.177 | 5.177 | 5.177 | 5.177 | 5.177 | 5.177 | 0.0016787 | 0.0016791 | 0.0016721 | 0.0016774 | 0.0016745 | 0.0016865 | 0.0017251 | 0.0017525 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508
| SSE033 | 3919.5 | 10.51 | 10.68 | 10.79 | 10.88 | 10.9 | 10.95 | 11.1 | 11.28 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 9.64 | 9.8 | 9.9 | 9.98 | 10.02 | 10.08 | 10.23 | 10.39 | 10.42 | 10.42 | 10.42 | 10.42 | 10.42 | 10.42 | 10.42 | 10.42 | 10.42 | 10.42 | 10.42 | 10.42 | 10.42 | 4.9505 | 5.032 | 5.0835 | 5.125 | 5.142 | 5.1705 | 5.2455 | 5.3285 | 5.342 | 5.342 | 5.342 | 5.342 | 5.342 | 5.342 | 5.342 | 5.342 | 5.342 | 5.342 | 5.342 | 5.342 | 5.342 | 0.001263 | 0.0012838 | 0.001297 | 0.0013076 | 0.0013119 | 0.0013192 | 0.0013383 | 0.0013595 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629
| SSE034 | 2596.5 | 11.2 | 11.46 | 11.63 | 11.75 | 11.75 | 11.78 | 12.02 | 12.32 | 12.33 | 12.33 | 12.33 | 12.33 | 12.33 | 12.33 | 12.33 | 12.33 | 12.33 | 12.33 | 12.33 | 12.33 | 12.33 | 9.66 | 9.86 | 10.02 | 10.13 | 10.12 | 10.17 | 10.4 | 10.66 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 10.64 | 5.061 | 5.17 | 5.2515 | 5.308 | 5.3045 | 5.3265 | 5.443 | 5.579 | 5.5735 | 5.5735 | 5.5735 | 5.5735 | 5.5735 | 5.5735 | 5.5735 | 5.5735 | 5.5735 | 5.5735 | 5.5735 | 5.5735 | 5.5735 | 0.0019492 | 0.0019911 | 0.0020225 | 0.0020443 | 0.0020429 | 0.0020514 | 0.0020963 | 0.0021487 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465
| STL004 | 1614 | 7.91 | 7.87 | 7.74 | 7.61 | 7.46 | 7.34 | 7.25 | 7.18 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 7.09 | 6.78 | 6.74 | 6.64 | 6.52 | 6.4 | 6.3 | 6.23 | 6.16 | 6.09 | 6.09 | 6.09 | 6.09 | 6.09 | 6.09 | 6.09 | 6.09 | 6.09 | 6.09 | 6.09 | 6.09 | 6.09 | 3.5595 | 3.5395 | 3.485 | 3.4235 | 3.359 | 3.306 | 3.268 | 3.233 | 3.195 | 3.195 | 3.195 | 3.195 | 3.195 | 3.195 | 3.195 | 3.195 | 3.195 | 3.195 | 3.195 | 3.195 | 3.195 | 0.0022054 | 0.002193 | 0.0021592 | 0.0021211 | 0.0020812 | 0.0020483 | 0.0020248 | 0.0020031 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796
| STL005 | 2555 | 7.35 | 7.34 | 7.29 | 7.23 | 7.13 | 7.05 | 7.02 | 7 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.51 | 6.51 | 6.46 | 6.4 | 6.32 | 6.25 | 6.23 | 6.22 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 3.381 | 3.3795 | 3.3545 | 3.3245 | 3.2815 | 3.245 | 3.2335 | 3.227 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 3.1955 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507
| STL006 | 1605 | 6.26 | 6.37 | 6.36 | 6.35 | 6.29 | 6.26 | 6.29 | 6.32 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 5.65 | 5.73 | 5.74 | 5.73 | 5.69 | 5.67 | 5.7 | 5.73 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 2.9165 | 2.961 | 2.963 | 2.958 | 2.935 | 2.9235 | 2.9385 | 2.9535 | 2.922 | 2.922 | 2.922 | 2.922 | 2.922 | 2.922 | 2.922 | 2.922 | 2.922 | 2.922 | 2.922 | 2.922 | 2.922 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206
| STL007 | 821 | 12.11 | 12.2 | 12.07 | 11.98 | 11.86 | 11.8 | 11.72 | 11.63 | 11.51 | 11.51 | 11.51 | 11.51 | 11.51 | 11.51 | 11.51 | 11.51 | 11.51 | 11.51 | 11.51 | 11.51 | 11.51 | 11.49 | 11.47 | 11.37 | 11.26 | 11.13 | 11.05 | 10.99 | 10.92 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 10.84 | 5.838 | 5.8445 | 5.79 | 5.738 | 5.6745 | 5.6375 | 5.6045 | 5.5665 | 5.5205 | 5.5205 | 5.5205 | 5.5205 | 5.5205 | 5.5205 | 5.5205 | 5.5205 | 5.5205 | 5.5205 | 5.5205 | 5.5205 | 5.5205 | 0.0071108 | 0.0071188 | 0.0070524 | 0.006989 | 0.0069117 | 0.0068666 | 0.0068264 | 0.0067801 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241
| STN011 | 1015 | 5.99 | 6.02 | 6.06 | 6.07 | 6.05 | 6.09 | 6.18 | 6.24 | 6.19 | 6.19 | 6.19 | 6.19 | 6.19 | 6.19 | 6.19 | 6.19 | 6.19 | 6.19 | 6.19 | 6.19 | 6.19 | 5.51 | 5.53 | 5.58 | 5.6 | 5.59 | 5.64 | 5.73 | 5.79 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 2.827 | 2.8385 | 2.862 | 2.8705 | 2.864 | 2.8875 | 2.9325 | 2.9625 | 2.9445 | 2.9445 | 2.9445 | 2.9445 | 2.9445 | 2.9445 | 2.9445 | 2.9445 | 2.9445 | 2.9445 | 2.9445 | 2.9445 | 2.9445 | 0.0027852 | 0.0027966 | 0.0028197 | 0.0028281 | 0.0028217 | 0.0028448 | 0.0028892 | 0.0029187 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901
| STN012 | 3409 | 11.8 | 12 | 12.19 | 12.35 | 12.44 | 12.57 | 12.8 | 13.02 | 13.16 | 13.16 | 13.16 | 13.16 | 13.16 | 13.16 | 13.16 | 13.16 | 13.16 | 13.16 | 13.16 | 13.16 | 13.16 | 10.82 | 11.02 | 11.2 | 11.33 | 11.41 | 11.54 | 11.75 | 11.97 | 12.11 | 12.11 | 12.11 | 12.11 | 12.11 | 12.11 | 12.11 | 12.11 | 12.11 | 12.11 | 12.11 | 12.11 | 12.11 | 5.557 | 5.657 | 5.7485 | 5.818 | 5.8595 | 5.9245 | 6.0325 | 6.1425 | 6.2125 | 6.2125 | 6.2125 | 6.2125 | 6.2125 | 6.2125 | 6.2125 | 6.2125 | 6.2125 | 6.2125 | 6.2125 | 6.2125 | 6.2125 | 0.0016301 | 0.0016594 | 0.0016863 | 0.0017067 | 0.0017188 | 0.0017379 | 0.0017696 | 0.0018018 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224
| STN013 | 3 | 6.68 | 6.7 | 6.66 | 6.61 | 6.55 | 6.5 | 6.47 | 6.45 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.42 | 6.29 | 6.29 | 6.25 | 6.2 | 6.14 | 6.1 | 6.07 | 6.05 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 6.03 | 3.2035 | 3.2065 | 3.1865 | 3.1615 | 3.1315 | 3.11 | 3.095 | 3.085 | 3.0735 | 3.0735 | 3.0735 | 3.0735 | 3.0735 | 3.0735 | 3.0735 | 3.0735 | 3.0735 | 3.0735 | 3.0735 | 3.0735 | 3.0735 | 1.0678 | 1.0688 | 1.0622 | 1.0538 | 1.0438 | 1.0367 | 1.0317 | 1.0283 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245
| STN014 | 692 | 7.95 | 8.14 | 8.19 | 8.21 | 8.17 | 8.17 | 8.23 | 8.29 | 8.29 | 8.29 | 8.29 | 8.29 | 8.29 | 8.29 | 8.29 | 8.29 | 8.29 | 8.29 | 8.29 | 8.29 | 8.29 | 7.47 | 7.66 | 7.71 | 7.71 | 7.68 | 7.68 | 7.72 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 7.77 | 3.807 | 3.902 | 3.927 | 3.93 | 3.9135 | 3.9135 | 3.9365 | 3.963 | 3.963 | 3.963 | 3.963 | 3.963 | 3.963 | 3.963 | 3.963 | 3.963 | 3.963 | 3.963 | 3.963 | 3.963 | 3.963 | 0.0055014 | 0.0056387 | 0.0056749 | 0.0056792 | 0.0056553 | 0.0056553 | 0.0056886 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269
| STN021 | 2007.5 | 6.49 | 6.55 | 6.58 | 6.6 | 6.6 | 6.61 | 6.67 | 6.74 | 6.77 | 6.77 | 6.77 | 6.77 | 6.77 | 6.77 | 6.77 | 6.77 | 6.77 | 6.77 | 6.77 | 6.77 | 6.77 | 5.78 | 5.84 | 5.87 | 5.89 | 5.88 | 5.9 | 5.95 | 6.02 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 6.05 | 2.9965 | 3.0265 | 3.0415 | 3.0515 | 3.048 | 3.0565 | 3.083 | 3.118 | 3.133 | 3.133 | 3.133 | 3.133 | 3.133 | 3.133 | 3.133 | 3.133 | 3.133 | 3.133 | 3.133 | 3.133 | 3.133 | 0.0014927 | 0.0015076 | 0.0015151 | 0.00152 | 0.0015183 | 0.0015225 | 0.0015357 | 0.0015532 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606
| STN022 | 2918.5 | 8.11 | 8.17 | 8.13 | 8.12 | 8.07 | 8.03 | 8.05 | 8.08 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 8.06 | 7.34 | 7.38 | 7.37 | 7.35 | 7.3 | 7.27 | 7.29 | 7.31 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 7.28 | 3.7855 | 3.8085 | 3.799 | 3.7905 | 3.7655 | 3.749 | 3.759 | 3.7705 | 3.757 | 3.757 | 3.757 | 3.757 | 3.757 | 3.757 | 3.757 | 3.757 | 3.757 | 3.757 | 3.757 | 3.757 | 3.757 | 0.0012971 | 0.001305 | 0.0013017 | 0.0012988 | 0.0012902 | 0.0012846 | 0.001288 | 0.0012919 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873
| STN023 | 267 | 3.79 | 3.78 | 3.72 | 3.66 | 3.6 | 3.54 | 3.51 | 3.49 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.59 | 3.58 | 3.53 | 3.48 | 3.41 | 3.36 | 3.34 | 3.31 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 1.825 | 1.82 | 1.7935 | 1.767 | 1.7335 | 1.707 | 1.6955 | 1.682 | 1.6655 | 1.6655 | 1.6655 | 1.6655 | 1.6655 | 1.6655 | 1.6655 | 1.6655 | 1.6655 | 1.6655 | 1.6655 | 1.6655 | 1.6655 | 0.0068352 | 0.0068165 | 0.0067172 | 0.006618 | 0.0064925 | 0.0063933 | 0.0063502 | 0.0062996 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378
| STN024 | 1221.5 | 12.25 | 12.34 | 12.39 | 12.35 | 12.22 | 12.17 | 12.33 | 12.53 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 12.37 | 10.91 | 11.03 | 11.08 | 11.06 | 10.95 | 10.94 | 11.2 | 11.4 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 11.24 | 5.656 | 5.7115 | 5.7365 | 5.7235 | 5.6655 | 5.6545 | 5.7695 | 5.8695 | 5.7895 | 5.7895 | 5.7895 | 5.7895 | 5.7895 | 5.7895 | 5.7895 | 5.7895 | 5.7895 | 5.7895 | 5.7895 | 5.7895 | 5.7895 | 0.0046304 | 0.0046758 | 0.0046963 | 0.0046856 | 0.0046381 | 0.0046291 | 0.0047233 | 0.0048052 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397
| STN031 | 329.5 | 9.86 | 9.77 | 9.62 | 9.46 | 9.26 | 9.11 | 9.02 | 8.95 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 6.6 | 6.54 | 6.42 | 6.3 | 6.17 | 6.05 | 5.97 | 5.92 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 5.83 | 3.789 | 3.7545 | 3.69 | 3.624 | 3.5485 | 3.484 | 3.4425 | 3.4145 | 3.365 | 3.365 | 3.365 | 3.365 | 3.365 | 3.365 | 3.365 | 3.365 | 3.365 | 3.365 | 3.365 | 3.365 | 3.365 | 0.011499 | 0.011395 | 0.011199 | 0.010998 | 0.010769 | 0.010574 | 0.010448 | 0.010363 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212
| SU012 | 3551 | 14.25 | 14.38 | 14.6 | 14.76 | 14.9 | 15.14 | 15.42 | 15.69 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 12.54 | 12.54 | 12.52 | 12.53 | 12.51 | 12.51 | 12.62 | 12.76 | 12.81 | 12.81 | 12.81 | 12.81 | 12.81 | 12.81 | 12.81 | 12.81 | 12.81 | 12.81 | 12.81 | 12.81 | 12.81 | 6.5265 | 6.546 | 6.572 | 6.5995 | 6.6135 | 6.6495 | 6.73 | 6.8195 | 6.858 | 6.858 | 6.858 | 6.858 | 6.858 | 6.858 | 6.858 | 6.858 | 6.858 | 6.858 | 6.858 | 6.858 | 6.858 | 0.0018379 | 0.0018434 | 0.0018507 | 0.0018585 | 0.0018624 | 0.0018726 | 0.0018952 | 0.0019204 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313
| SU013 | 100 | 10.41 | 10.56 | 10.61 | 10.64 | 10.64 | 10.65 | 10.73 | 10.84 | 10.89 | 10.89 | 10.89 | 10.89 | 10.89 | 10.89 | 10.89 | 10.89 | 10.89 | 10.89 | 10.89 | 10.89 | 10.89 | 9.59 | 9.73 | 9.78 | 9.8 | 9.8 | 9.81 | 9.88 | 9.98 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 4.918 | 4.9895 | 5.0145 | 5.026 | 5.026 | 5.031 | 5.0675 | 5.119 | 5.1405 | 5.1405 | 5.1405 | 5.1405 | 5.1405 | 5.1405 | 5.1405 | 5.1405 | 5.1405 | 5.1405 | 5.1405 | 5.1405 | 5.1405 | 0.04918 | 0.049895 | 0.050145 | 0.05026 | 0.05026 | 0.05031 | 0.050675 | 0.05119 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405
| SU015 | 4993.5 | 11.84 | 12.05 | 12.31 | 12.52 | 12.57 | 13.12 | 13.9 | 14.5 | 14.97 | 14.97 | 14.97 | 14.97 | 14.97 | 14.97 | 14.97 | 14.97 | 14.97 | 14.97 | 14.97 | 14.97 | 14.97 | 10.58 | 10.82 | 11.05 | 11.26 | 11.68 | 12.29 | 12.98 | 13.62 | 14.09 | 14.09 | 14.09 | 14.09 | 14.09 | 14.09 | 14.09 | 14.09 | 14.09 | 14.09 | 14.09 | 14.09 | 14.09 | 5.479 | 5.5945 | 5.714 | 5.819 | 5.9735 | 6.2695 | 6.628 | 6.942 | 7.177 | 7.177 | 7.177 | 7.177 | 7.177 | 7.177 | 7.177 | 7.177 | 7.177 | 7.177 | 7.177 | 7.177 | 7.177 | 0.0010972 | 0.0011204 | 0.0011443 | 0.0011653 | 0.0011963 | 0.0012555 | 0.0013273 | 0.0013902 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373
| SU021 | 3578.5 | 10.62 | 10.71 | 10.75 | 10.77 | 10.76 | 10.78 | 10.86 | 10.96 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 11.01 | 9.74 | 9.8 | 9.81 | 9.81 | 9.8 | 9.81 | 9.9 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | 10.12 | 10.12 | 10.12 | 10.12 | 10.12 | 10.12 | 10.12 | 10.12 | 10.12 | 5.002 | 5.0365 | 5.046 | 5.049 | 5.044 | 5.0505 | 5.094 | 5.144 | 5.1935 | 5.1935 | 5.1935 | 5.1935 | 5.1935 | 5.1935 | 5.1935 | 5.1935 | 5.1935 | 5.1935 | 5.1935 | 5.1935 | 5.1935 | 0.0013978 | 0.0014074 | 0.0014101 | 0.0014109 | 0.0014095 | 0.0014113 | 0.0014235 | 0.0014375 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513
| SU022 | 5301.5 | 14.12 | 14.28 | 14.51 | 14.67 | 14.84 | 15.02 | 15.86 | 16.74 | 17.48 | 17.48 | 17.48 | 17.48 | 17.48 | 17.48 | 17.48 | 17.48 | 17.48 | 17.48 | 17.48 | 17.48 | 17.48 | 12.73 | 13 | 13.24 | 13.45 | 13.63 | 13.9 | 14.79 | 15.62 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 6.5735 | 6.692 | 6.8105 | 6.908 | 6.9965 | 7.118 | 7.5555 | 7.978 | 8.334 | 8.334 | 8.334 | 8.334 | 8.334 | 8.334 | 8.334 | 8.334 | 8.334 | 8.334 | 8.334 | 8.334 | 8.334 | 0.0012399 | 0.0012623 | 0.0012846 | 0.001303 | 0.0013197 | 0.0013426 | 0.0014252 | 0.0015049 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572
| SU023 | 1533.5 | 11.52 | 11.67 | 11.74 | 11.79 | 11.8 | 11.86 | 12 | 12.16 | 12.22 | 12.22 | 12.22 | 12.22 | 12.22 | 12.22 | 12.22 | 12.22 | 12.22 | 12.22 | 12.22 | 12.22 | 12.22 | 10.86 | 10.96 | 11.08 | 11.16 | 11.22 | 11.35 | 11.57 | 11.74 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 5.529 | 5.5865 | 5.639 | 5.6745 | 5.697 | 5.7515 | 5.8495 | 5.933 | 5.9665 | 5.9665 | 5.9665 | 5.9665 | 5.9665 | 5.9665 | 5.9665 | 5.9665 | 5.9665 | 5.9665 | 5.9665 | 5.9665 | 5.9665 | 0.0036055 | 0.003643 | 0.0036772 | 0.0037004 | 0.003715 | 0.0037506 | 0.0038145 | 0.0038689 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908
| SU024 | 2 | 6.61 | 6.64 | 6.68 | 6.69 | 6.68 | 6.71 | 6.78 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.25 | 6.34 | 6.37 | 6.41 | 6.4 | 6.4 | 6.44 | 6.51 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 3.179 | 3.215 | 3.2315 | 3.247 | 3.242 | 3.2465 | 3.271 | 3.303 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 1.5895 | 1.6075 | 1.6157 | 1.6235 | 1.621 | 1.6233 | 1.6355 | 1.6515 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655
| SU032 | 1 | 6.09 | 7.78 | 7.79 | 7.79 | 7.78 | 7.79 | 7.81 | 7.83 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 7.85 | 5.9 | 7.55 | 7.58 | 7.58 | 7.57 | 7.58 | 7.6 | 7.62 | 7.64 | 7.64 | 7.64 | 7.64 | 7.64 | 7.64 | 7.64 | 7.64 | 7.64 | 7.64 | 7.64 | 7.64 | 7.64 | 2.9785 | 3.8095 | 3.8215 | 3.8215 | 3.8165 | 3.8215 | 3.8315 | 3.8415 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 2.9785 | 3.8095 | 3.8215 | 3.8215 | 3.8165 | 3.8215 | 3.8315 | 3.8415 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 3.8515
| SU034 | 77.5 | 10.19 | 10.47 | 10.61 | 10.74 | 10.83 | 10.92 | 11.07 | 11.24 | 11.34 | 11.34 | 11.34 | 11.34 | 11.34 | 11.34 | 11.34 | 11.34 | 11.34 | 11.34 | 11.34 | 11.34 | 11.34 | 9.52 | 9.76 | 9.89 | 10.01 | 10.09 | 10.18 | 10.31 | 10.47 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 4.8605 | 4.9865 | 5.053 | 5.1145 | 5.156 | 5.201 | 5.269 | 5.3505 | 5.4005 | 5.4005 | 5.4005 | 5.4005 | 5.4005 | 5.4005 | 5.4005 | 5.4005 | 5.4005 | 5.4005 | 5.4005 | 5.4005 | 5.4005 | 0.062716 | 0.064342 | 0.0652 | 0.065994 | 0.066529 | 0.06711 | 0.067987 | 0.069039 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684
| SU035 | 4593.5 | 18.76 | 19.22 | 19.52 | 19.74 | 19.88 | 20.06 | 20.42 | 20.8 | 20.96 | 20.96 | 20.96 | 20.96 | 20.96 | 20.96 | 20.96 | 20.96 | 20.96 | 20.96 | 20.96 | 20.96 | 20.96 | 16.86 | 17.25 | 17.53 | 17.78 | 17.91 | 18.09 | 18.44 | 18.79 | 18.95 | 18.95 | 18.95 | 18.95 | 18.95 | 18.95 | 18.95 | 18.95 | 18.95 | 18.95 | 18.95 | 18.95 | 18.95 | 8.715 | 8.9205 | 9.0635 | 9.184 | 9.2505 | 9.3405 | 9.517 | 9.6965 | 9.7765 | 9.7765 | 9.7765 | 9.7765 | 9.7765 | 9.7765 | 9.7765 | 9.7765 | 9.7765 | 9.7765 | 9.7765 | 9.7765 | 9.7765 | 0.0018972 | 0.001942 | 0.0019731 | 0.0019993 | 0.0020138 | 0.0020334 | 0.0020718 | 0.0021109 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283
| TNA011 | 7297 | 25.81 | 16.4 | 17.19 | 17.94 | 18.58 | 19.25 | 20.12 | 21.02 | 21.69 | 21.69 | 21.69 | 21.69 | 21.69 | 21.69 | 21.69 | 21.69 | 21.69 | 21.69 | 21.69 | 21.69 | 21.69 | 22.59 | 14.33 | 15.03 | 15.66 | 16.22 | 16.84 | 17.62 | 18.42 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 19.03 | 11.778 | 7.4755 | 7.839 | 8.172 | 8.464 | 8.7815 | 9.185 | 9.6 | 9.914 | 9.914 | 9.914 | 9.914 | 9.914 | 9.914 | 9.914 | 9.914 | 9.914 | 9.914 | 9.914 | 9.914 | 9.914 | 0.0016141 | 0.0010245 | 0.0010743 | 0.0011199 | 0.0011599 | 0.0012034 | 0.0012587 | 0.0013156 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586
| TNA012 | 6940.5 | 22.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA013 | 1613.5 | 13.68 | 14.21 | 14.78 | 15.2 | 15.56 | 16.05 | 16.68 | 17.2 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 10.47 | 11.06 | 11.56 | 11.98 | 12.31 | 12.67 | 13.17 | 13.69 | 14.02 | 14.02 | 14.02 | 14.02 | 14.02 | 14.02 | 14.02 | 14.02 | 14.02 | 14.02 | 14.02 | 14.02 | 14.02 | 5.7165 | 6.0025 | 6.263 | 6.473 | 6.6425 | 6.842 | 7.1115 | 7.3715 | 7.517 | 7.517 | 7.517 | 7.517 | 7.517 | 7.517 | 7.517 | 7.517 | 7.517 | 7.517 | 7.517 | 7.517 | 7.517 | 0.0035429 | 0.0037202 | 0.0038816 | 0.0040118 | 0.0041168 | 0.0042405 | 0.0044075 | 0.0045686 | 0.0046588 | 0.0046588 | 0.0046588 | 0.0046588 | 0.0046588 | 0.0046588 | 0.0046588 | 0.0046588 | 0.0046588 | 0.0046588 | 0.0046588 | 0.0046588 | 0.0046588
| TNA014 | 52 | 11.19 | 11.6 | 11.83 | 12.04 | 12.13 | 12.24 | 12.49 | 12.79 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 12.92 | 10.26 | 10.61 | 10.83 | 11.01 | 11.09 | 11.2 | 11.43 | 11.71 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 11.81 | 5.2695 | 5.4535 | 5.565 | 5.6595 | 5.701 | 5.756 | 5.874 | 6.017 | 6.0715 | 6.0715 | 6.0715 | 6.0715 | 6.0715 | 6.0715 | 6.0715 | 6.0715 | 6.0715 | 6.0715 | 6.0715 | 6.0715 | 6.0715 | 0.10134 | 0.10487 | 0.10702 | 0.10884 | 0.10963 | 0.11069 | 0.11296 | 0.11571 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676
| TNA021 | 2494.5 | 18.8 | 19.59 | 19.52 | 19.31 | 19.05 | 18.9 | 19.05 | 19.21 | 19.28 | 19.28 | 19.28 | 19.28 | 19.28 | 19.28 | 19.28 | 19.28 | 19.28 | 19.28 | 19.28 | 19.28 | 19.28 | 15.02 | 15.68 | 15.57 | 15.42 | 15.21 | 15.08 | 15.19 | 15.31 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 15.32 | 8.077 | 8.4265 | 8.3775 | 8.2935 | 8.181 | 8.113 | 8.174 | 8.24 | 8.254 | 8.254 | 8.254 | 8.254 | 8.254 | 8.254 | 8.254 | 8.254 | 8.254 | 8.254 | 8.254 | 8.254 | 8.254 | 0.0032379 | 0.003378 | 0.0033584 | 0.0033247 | 0.0032796 | 0.0032524 | 0.0032768 | 0.0033033 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089
| TNA022 | 7362 | 18.22 | 12.99 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 15.84 | 12.99 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 8.277 | 6.495 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0.0011243 | 0.00088223 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291
| TNA023 | 1654.5 | 22.56 | 22.54 | 24.28 | 26.36 | 28.29 | 30.35 | 32.57 | 34.63 | 36.35 | 36.35 | 36.35 | 36.35 | 36.35 | 36.35 | 36.35 | 36.35 | 36.35 | 36.35 | 36.35 | 36.35 | 36.35 | 18.35 | 18.14 | 19.84 | 21.53 | 23.16 | 24.97 | 26.82 | 28.59 | 30.08 | 30.08 | 30.08 | 30.08 | 30.08 | 30.08 | 30.08 | 30.08 | 30.08 | 30.08 | 30.08 | 30.08 | 30.08 | 9.8065 | 9.73 | 10.586 | 11.4895 | 12.3495 | 13.292 | 14.2725 | 15.201 | 15.9805 | 15.9805 | 15.9805 | 15.9805 | 15.9805 | 15.9805 | 15.9805 | 15.9805 | 15.9805 | 15.9805 | 15.9805 | 15.9805 | 15.9805 | 0.0059272 | 0.0058809 | 0.0063983 | 0.0069444 | 0.0074642 | 0.0080338 | 0.0086265 | 0.0091877 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588
| TNA024 | 493 | 16.78 | 17.26 | 17.6 | 17.88 | 18.2 | 18.71 | 19.39 | 19.97 | 20.22 | 20.22 | 20.22 | 20.22 | 20.22 | 20.22 | 20.22 | 20.22 | 20.22 | 20.22 | 20.22 | 20.22 | 20.22 | 15.81 | 16.23 | 16.73 | 17.12 | 17.44 | 17.93 | 18.58 | 19.16 | 19.39 | 19.39 | 19.39 | 19.39 | 19.39 | 19.39 | 19.39 | 19.39 | 19.39 | 19.39 | 19.39 | 19.39 | 19.39 | 8.0505 | 8.2695 | 8.4955 | 8.674 | 8.834 | 9.082 | 9.4115 | 9.7015 | 9.8195 | 9.8195 | 9.8195 | 9.8195 | 9.8195 | 9.8195 | 9.8195 | 9.8195 | 9.8195 | 9.8195 | 9.8195 | 9.8195 | 9.8195 | 0.01633 | 0.016774 | 0.017232 | 0.017594 | 0.017919 | 0.018422 | 0.01909 | 0.019678 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918
| TNA031 | 2813 | 22.45 | 16.29 | 16.66 | 17.02 | 17.28 | 17.61 | 18.06 | 18.78 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 20.47 | 14.2 | 14.52 | 14.83 | 15.07 | 15.55 | 16.42 | 17.23 | 17.86 | 17.86 | 17.86 | 17.86 | 17.86 | 17.86 | 17.86 | 17.86 | 17.86 | 17.86 | 17.86 | 17.86 | 17.86 | 10.532 | 7.4135 | 7.581 | 7.7435 | 7.8665 | 8.084 | 8.456 | 8.8475 | 9.1625 | 9.1625 | 9.1625 | 9.1625 | 9.1625 | 9.1625 | 9.1625 | 9.1625 | 9.1625 | 9.1625 | 9.1625 | 9.1625 | 9.1625 | 0.003744 | 0.0026354 | 0.002695 | 0.0027528 | 0.0027965 | 0.0028738 | 0.003006 | 0.0031452 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572
| TNA033 | 6922 | 18.17 | 19.42 | 20.87 | 22.43 | 23.99 | 25.74 | 27.58 | 29.2 | 30.56 | 30.56 | 30.56 | 30.56 | 30.56 | 30.56 | 30.56 | 30.56 | 30.56 | 30.56 | 30.56 | 30.56 | 30.56 | 15.96 | 16.59 | 17.19 | 17.89 | 19.31 | 20.82 | 22.4 | 23.81 | 25.01 | 25.01 | 25.01 | 25.01 | 25.01 | 25.01 | 25.01 | 25.01 | 25.01 | 25.01 | 25.01 | 25.01 | 25.01 | 8.3115 | 8.7195 | 9.147 | 9.626 | 10.357 | 11.148 | 11.977 | 12.7135 | 13.3375 | 13.3375 | 13.3375 | 13.3375 | 13.3375 | 13.3375 | 13.3375 | 13.3375 | 13.3375 | 13.3375 | 13.3375 | 13.3375 | 13.3375 | 0.0012007 | 0.0012597 | 0.0013214 | 0.0013906 | 0.0014962 | 0.0016105 | 0.0017303 | 0.0018367 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268
| TQY021 | 2292 | 12.07 | 12.15 | 12.29 | 12.34 | 12.36 | 12.43 | 12.54 | 12.62 | 12.59 | 12.59 | 12.59 | 12.59 | 12.59 | 12.59 | 12.59 | 12.59 | 12.59 | 12.59 | 12.59 | 12.59 | 12.59 | 10.52 | 10.61 | 10.73 | 10.78 | 10.79 | 10.85 | 10.95 | 11.02 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 10.95 | 5.4925 | 5.536 | 5.599 | 5.624 | 5.6305 | 5.662 | 5.7135 | 5.75 | 5.721 | 5.721 | 5.721 | 5.721 | 5.721 | 5.721 | 5.721 | 5.721 | 5.721 | 5.721 | 5.721 | 5.721 | 5.721 | 0.0023964 | 0.0024154 | 0.0024428 | 0.0024538 | 0.0024566 | 0.0024703 | 0.0024928 | 0.0025087 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961
| TQY022 | 2362 | 12.54 | 12.97 | 13.17 | 13.38 | 13.52 | 13.73 | 13.99 | 14.24 | 14.41 | 14.41 | 14.41 | 14.41 | 14.41 | 14.41 | 14.41 | 14.41 | 14.41 | 14.41 | 14.41 | 14.41 | 14.41 | 11.09 | 11.51 | 11.76 | 11.97 | 12.11 | 12.28 | 12.5 | 12.82 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 12.96 | 5.7625 | 5.974 | 6.0915 | 6.1965 | 6.2665 | 6.3575 | 6.4735 | 6.623 | 6.6975 | 6.6975 | 6.6975 | 6.6975 | 6.6975 | 6.6975 | 6.6975 | 6.6975 | 6.6975 | 6.6975 | 6.6975 | 6.6975 | 6.6975 | 0.0024397 | 0.0025292 | 0.002579 | 0.0026234 | 0.002653 | 0.0026916 | 0.0027407 | 0.002804 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355
| TQY031 | 2440 | 14.82 | 15.15 | 15.37 | 15.59 | 15.72 | 15.88 | 16.1 | 16.33 | 16.42 | 16.42 | 16.42 | 16.42 | 16.42 | 16.42 | 16.42 | 16.42 | 16.42 | 16.42 | 16.42 | 16.42 | 16.42 | 12.94 | 13.16 | 13.33 | 13.51 | 13.61 | 13.77 | 13.92 | 14.1 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 6.752 | 6.8785 | 6.971 | 7.067 | 7.1215 | 7.2015 | 7.287 | 7.3845 | 7.433 | 7.433 | 7.433 | 7.433 | 7.433 | 7.433 | 7.433 | 7.433 | 7.433 | 7.433 | 7.433 | 7.433 | 7.433 | 0.0027672 | 0.0028191 | 0.002857 | 0.0028963 | 0.0029186 | 0.0029514 | 0.0029865 | 0.0030264 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463
| TQY032 | 2120 | 14.82 | 15.8 | 15.77 | 15.72 | 15.63 | 15.52 | 15.57 | 15.74 | 15.88 | 15.88 | 15.88 | 15.88 | 15.88 | 15.88 | 15.88 | 15.88 | 15.88 | 15.88 | 15.88 | 15.88 | 15.88 | 13.16 | 14.08 | 13.98 | 13.83 | 13.74 | 13.68 | 13.7 | 13.8 | 13.91 | 13.91 | 13.91 | 13.91 | 13.91 | 13.91 | 13.91 | 13.91 | 13.91 | 13.91 | 13.91 | 13.91 | 13.91 | 6.829 | 7.298 | 7.2585 | 7.1985 | 7.1535 | 7.116 | 7.1305 | 7.191 | 7.2505 | 7.2505 | 7.2505 | 7.2505 | 7.2505 | 7.2505 | 7.2505 | 7.2505 | 7.2505 | 7.2505 | 7.2505 | 7.2505 | 7.2505 | 0.0032212 | 0.0034425 | 0.0034238 | 0.0033955 | 0.0033743 | 0.0033566 | 0.0033634 | 0.003392 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342
| TRG011 | 432.5 | 1.49 | 1.52 | 1.54 | 1.55 | 1.54 | 1.53 | 1.55 | 1.59 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.58 | 1.41 | 1.44 | 1.45 | 1.46 | 1.45 | 1.44 | 1.47 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 1.49 | 0.717 | 0.732 | 0.7385 | 0.7435 | 0.7385 | 0.7335 | 0.747 | 0.76 | 0.7585 | 0.7585 | 0.7585 | 0.7585 | 0.7585 | 0.7585 | 0.7585 | 0.7585 | 0.7585 | 0.7585 | 0.7585 | 0.7585 | 0.7585 | 0.0016578 | 0.0016925 | 0.0017075 | 0.0017191 | 0.0017075 | 0.001696 | 0.0017272 | 0.0017572 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538
| TRG013 | 1717 | 6.52 | 6.54 | 6.53 | 6.49 | 6.4 | 6.33 | 6.37 | 6.41 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 6.33 | 5.87 | 5.86 | 5.88 | 5.83 | 5.76 | 5.76 | 5.82 | 5.84 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 5.72 | 3.0325 | 3.032 | 3.0375 | 3.014 | 2.976 | 2.9655 | 2.9925 | 3.0055 | 2.9515 | 2.9515 | 2.9515 | 2.9515 | 2.9515 | 2.9515 | 2.9515 | 2.9515 | 2.9515 | 2.9515 | 2.9515 | 2.9515 | 2.9515 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719
| TRG014 | 1622.5 | 4.13 | 4.13 | 4.15 | 4.13 | 4.08 | 4.08 | 4.12 | 4.15 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 4.09 | 3.97 | 3.96 | 3.98 | 3.96 | 3.92 | 3.92 | 3.96 | 3.98 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 2.009 | 2.0055 | 2.0155 | 2.0055 | 1.984 | 1.984 | 2.004 | 2.0155 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.0012382 | 0.0012361 | 0.0012422 | 0.0012361 | 0.0012228 | 0.0012228 | 0.0012351 | 0.0012422 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237
| TRG022 | 2004.5 | 5.38 | 5.41 | 5.48 | 5.47 | 5.43 | 5.47 | 5.56 | 5.62 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.52 | 5.19 | 5.22 | 5.29 | 5.28 | 5.25 | 5.27 | 5.37 | 5.43 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 2.6235 | 2.6385 | 2.6735 | 2.6685 | 2.652 | 2.665 | 2.7135 | 2.7435 | 2.6935 | 2.6935 | 2.6935 | 2.6935 | 2.6935 | 2.6935 | 2.6935 | 2.6935 | 2.6935 | 2.6935 | 2.6935 | 2.6935 | 2.6935 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437
| TRG024 | 1107.5 | 10.95 | 11.17 | 11.33 | 11.44 | 11.4 | 11.4 | 11.59 | 11.86 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 5.98 | 6.12 | 6.2 | 6.27 | 6.24 | 6.23 | 6.34 | 6.48 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 6.45 | 3.7355 | 3.8175 | 3.8695 | 3.9105 | 3.894 | 3.8905 | 3.9575 | 4.047 | 4.0275 | 4.0275 | 4.0275 | 4.0275 | 4.0275 | 4.0275 | 4.0275 | 4.0275 | 4.0275 | 4.0275 | 4.0275 | 4.0275 | 4.0275 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366
| WBE011 | 2466 | 7.38 | 7.3 | 7.22 | 7.12 | 6.98 | 7.03 | 7.16 | 7.26 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 7.23 | 6.82 | 6.77 | 6.71 | 6.63 | 6.52 | 6.44 | 6.56 | 6.66 | 6.64 | 6.64 | 6.64 | 6.64 | 6.64 | 6.64 | 6.64 | 6.64 | 6.64 | 6.64 | 6.64 | 6.64 | 6.64 | 3.494 | 3.4645 | 3.4315 | 3.3885 | 3.329 | 3.3085 | 3.37 | 3.42 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 0.0014169 | 0.0014049 | 0.0013915 | 0.0013741 | 0.00135 | 0.0013416 | 0.0013666 | 0.0013869 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822
| WBE012 | 2236.5 | 4.78 | 4.82 | 4.84 | 4.86 | 4.86 | 4.86 | 4.92 | 4.98 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.32 | 4.35 | 4.38 | 4.4 | 4.4 | 4.42 | 4.46 | 4.56 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 2.229 | 2.2455 | 2.259 | 2.269 | 2.269 | 2.276 | 2.299 | 2.343 | 2.3865 | 2.3865 | 2.3865 | 2.3865 | 2.3865 | 2.3865 | 2.3865 | 2.3865 | 2.3865 | 2.3865 | 2.3865 | 2.3865 | 2.3865 | 0.00099665 | 0.001004 | 0.0010101 | 0.0010145 | 0.0010145 | 0.0010177 | 0.0010279 | 0.0010476 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671
| WBE013 | 5164 | 16.19 | 17.21 | 17.64 | 18.05 | 18.4 | 18.81 | 19.35 | 20.14 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 14.45 | 15.35 | 15.81 | 16.21 | 16.55 | 16.98 | 17.7 | 18.59 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 7.486 | 7.954 | 8.1795 | 8.381 | 8.5525 | 8.7645 | 9.0975 | 9.5275 | 9.903 | 9.903 | 9.903 | 9.903 | 9.903 | 9.903 | 9.903 | 9.903 | 9.903 | 9.903 | 9.903 | 9.903 | 9.903 | 0.0014497 | 0.0015403 | 0.0015839 | 0.001623 | 0.0016562 | 0.0016972 | 0.0017617 | 0.001845 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177
| WBE014 | 6472 | 14.8 | 7.78 | 8.13 | 8.47 | 8.78 | 9.11 | 9.5 | 9.9 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 13.34 | 7.03 | 7.36 | 7.67 | 7.94 | 8.25 | 8.61 | 8.97 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 6.889 | 3.6275 | 3.7955 | 3.955 | 4.096 | 4.254 | 4.4385 | 4.6245 | 4.779 | 4.779 | 4.779 | 4.779 | 4.779 | 4.779 | 4.779 | 4.779 | 4.779 | 4.779 | 4.779 | 4.779 | 4.779 | 0.0010644 | 0.00056049 | 0.00058645 | 0.00061109 | 0.00063288 | 0.00065729 | 0.0006858 | 0.00071454 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841
| WBE021 | 2980.5 | 11.45 | 3.39 | 3.31 | 3.26 | 3.19 | 3.13 | 3.09 | 3.07 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 3.03 | 10.49 | 3.09 | 3.01 | 2.93 | 2.86 | 2.8 | 2.77 | 2.73 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 5.389 | 1.59 | 1.55 | 1.5145 | 1.4795 | 1.4495 | 1.433 | 1.416 | 1.3995 | 1.3995 | 1.3995 | 1.3995 | 1.3995 | 1.3995 | 1.3995 | 1.3995 | 1.3995 | 1.3995 | 1.3995 | 1.3995 | 1.3995 | 0.0018081 | 0.00053347 | 0.00052005 | 0.00050814 | 0.00049639 | 0.00048633 | 0.00048079 | 0.00047509 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955
| WBE022 | 1529.5 | 9.06 | 9.87 | 9.77 | 9.67 | 9.51 | 9.37 | 9.31 | 9.31 | 9.38 | 9.38 | 9.38 | 9.38 | 9.38 | 9.38 | 9.38 | 9.38 | 9.38 | 9.38 | 9.38 | 9.38 | 9.38 | 8.29 | 9.06 | 8.98 | 8.87 | 8.72 | 8.58 | 8.51 | 8.5 | 8.57 | 8.57 | 8.57 | 8.57 | 8.57 | 8.57 | 8.57 | 8.57 | 8.57 | 8.57 | 8.57 | 8.57 | 8.57 | 4.2605 | 4.6515 | 4.6085 | 4.555 | 4.4785 | 4.4085 | 4.375 | 4.3715 | 4.4065 | 4.4065 | 4.4065 | 4.4065 | 4.4065 | 4.4065 | 4.4065 | 4.4065 | 4.4065 | 4.4065 | 4.4065 | 4.4065 | 4.4065 | 0.0027856 | 0.0030412 | 0.0030131 | 0.0029781 | 0.0029281 | 0.0028823 | 0.0028604 | 0.0028581 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881
| WBE023 | 6050.5 | 15.44 | 15.77 | 16.07 | 16.4 | 16.64 | 16.99 | 17.41 | 18.07 | 18.61 | 18.61 | 18.61 | 18.61 | 18.61 | 18.61 | 18.61 | 18.61 | 18.61 | 18.61 | 18.61 | 18.61 | 18.61 | 12.93 | 13.21 | 13.53 | 13.79 | 14.05 | 14.35 | 14.86 | 15.57 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 16.13 | 6.8415 | 6.989 | 7.146 | 7.2865 | 7.4135 | 7.571 | 7.8125 | 8.16 | 8.437 | 8.437 | 8.437 | 8.437 | 8.437 | 8.437 | 8.437 | 8.437 | 8.437 | 8.437 | 8.437 | 8.437 | 8.437 | 0.0011307 | 0.0011551 | 0.0011811 | 0.0012043 | 0.0012253 | 0.0012513 | 0.0012912 | 0.0013486 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944
| WBE024 | 3481.5 | 18.23 | 18.57 | 18.97 | 19.35 | 19.62 | 20.08 | 20.62 | 21.13 | 21.47 | 21.47 | 21.47 | 21.47 | 21.47 | 21.47 | 21.47 | 21.47 | 21.47 | 21.47 | 21.47 | 21.47 | 21.47 | 16.24 | 16.51 | 16.65 | 16.81 | 16.89 | 17.06 | 17.54 | 18.03 | 18.32 | 18.32 | 18.32 | 18.32 | 18.32 | 18.32 | 18.32 | 18.32 | 18.32 | 18.32 | 18.32 | 18.32 | 18.32 | 8.4185 | 8.564 | 8.673 | 8.786 | 8.8545 | 8.983 | 9.232 | 9.48 | 9.6325 | 9.6325 | 9.6325 | 9.6325 | 9.6325 | 9.6325 | 9.6325 | 9.6325 | 9.6325 | 9.6325 | 9.6325 | 9.6325 | 9.6325 | 0.0024181 | 0.0024599 | 0.0024912 | 0.0025236 | 0.0025433 | 0.0025802 | 0.0026517 | 0.002723 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668
| WBE031 | 6384.5 | 12.37 | 12.72 | 13.07 | 13.41 | 14.16 | 14.98 | 15.85 | 16.67 | 17.29 | 17.29 | 17.29 | 17.29 | 17.29 | 17.29 | 17.29 | 17.29 | 17.29 | 17.29 | 17.29 | 17.29 | 17.29 | 11.25 | 11.58 | 11.91 | 12.57 | 13.28 | 14.07 | 14.89 | 15.63 | 16.19 | 16.19 | 16.19 | 16.19 | 16.19 | 16.19 | 16.19 | 16.19 | 16.19 | 16.19 | 16.19 | 16.19 | 16.19 | 5.793 | 5.961 | 6.129 | 6.411 | 6.772 | 7.1715 | 7.589 | 7.971 | 8.26 | 8.26 | 8.26 | 8.26 | 8.26 | 8.26 | 8.26 | 8.26 | 8.26 | 8.26 | 8.26 | 8.26 | 8.26 | 0.00090735 | 0.00093367 | 0.00095998 | 0.0010042 | 0.0010607 | 0.0011233 | 0.0011887 | 0.0012485 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938
| WBE032 | 4804.5 | 11.72 | 8.1 | 8.23 | 8.35 | 8.44 | 8.55 | 8.72 | 8.9 | 9.01 | 9.01 | 9.01 | 9.01 | 9.01 | 9.01 | 9.01 | 9.01 | 9.01 | 9.01 | 9.01 | 9.01 | 9.01 | 10.48 | 7.24 | 7.35 | 7.47 | 7.56 | 7.66 | 7.81 | 7.97 | 8.07 | 8.07 | 8.07 | 8.07 | 8.07 | 8.07 | 8.07 | 8.07 | 8.07 | 8.07 | 8.07 | 8.07 | 8.07 | 5.426 | 3.749 | 3.807 | 3.867 | 3.912 | 3.9635 | 4.0415 | 4.1245 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 0.0011294 | 0.00078031 | 0.00079238 | 0.00080487 | 0.00081424 | 0.00082496 | 0.00084119 | 0.00085847 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919
| WBE033 | 5055 | 22.86 | 23.55 | 24.22 | 24.81 | 25.25 | 25.77 | 26.5 | 27.43 | 28.11 | 28.11 | 28.11 | 28.11 | 28.11 | 28.11 | 28.11 | 28.11 | 28.11 | 28.11 | 28.11 | 28.11 | 28.11 | 20.59 | 21.21 | 21.81 | 22.35 | 22.71 | 23.17 | 23.89 | 24.63 | 25.14 | 25.14 | 25.14 | 25.14 | 25.14 | 25.14 | 25.14 | 25.14 | 25.14 | 25.14 | 25.14 | 25.14 | 25.14 | 10.6355 | 10.956 | 11.2665 | 11.544 | 11.736 | 11.975 | 12.3365 | 12.735 | 13.0155 | 13.0155 | 13.0155 | 13.0155 | 13.0155 | 13.0155 | 13.0155 | 13.0155 | 13.0155 | 13.0155 | 13.0155 | 13.0155 | 13.0155 | 0.002104 | 0.0021674 | 0.0022288 | 0.0022837 | 0.0023217 | 0.0023689 | 0.0024405 | 0.0025193 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748
| WBE034 | 3886.5 | 12.81 | 13.32 | 13.78 | 14.2 | 14.53 | 14.92 | 15.41 | 15.93 | 16.29 | 16.29 | 16.29 | 16.29 | 16.29 | 16.29 | 16.29 | 16.29 | 16.29 | 16.29 | 16.29 | 16.29 | 16.29 | 11.77 | 12.24 | 12.67 | 13.06 | 13.39 | 13.75 | 14.18 | 14.66 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 6.041 | 6.282 | 6.5015 | 6.701 | 6.866 | 7.0505 | 7.2745 | 7.5205 | 7.6935 | 7.6935 | 7.6935 | 7.6935 | 7.6935 | 7.6935 | 7.6935 | 7.6935 | 7.6935 | 7.6935 | 7.6935 | 7.6935 | 7.6935 | 0.0015544 | 0.0016164 | 0.0016728 | 0.0017242 | 0.0017666 | 0.0018141 | 0.0018717 | 0.001935 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795
| WBL002 | 1960 | 14.36 | 14.55 | 14.53 | 14.48 | 14.35 | 14.26 | 14.39 | 14.5 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 14.37 | 13.57 | 13.57 | 13.63 | 13.61 | 13.55 | 13.61 | 13.77 | 13.87 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 6.9035 | 6.932 | 6.95 | 6.9355 | 6.895 | 6.9025 | 6.978 | 7.0295 | 6.9645 | 6.9645 | 6.9645 | 6.9645 | 6.9645 | 6.9645 | 6.9645 | 6.9645 | 6.9645 | 6.9645 | 6.9645 | 6.9645 | 6.9645 | 0.0035222 | 0.0035367 | 0.0035459 | 0.0035385 | 0.0035179 | 0.0035217 | 0.0035602 | 0.0035865 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533
| WBL003 | 2031.5 | 6.72 | 6.68 | 6.61 | 6.5 | 6.4 | 6.32 | 6.46 | 6.6 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.67 | 6.02 | 5.99 | 5.91 | 5.83 | 5.88 | 5.97 | 6.11 | 6.23 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 6.28 | 3.115 | 3.0985 | 3.06 | 3.0155 | 3.018 | 3.0375 | 3.1075 | 3.1705 | 3.1985 | 3.1985 | 3.1985 | 3.1985 | 3.1985 | 3.1985 | 3.1985 | 3.1985 | 3.1985 | 3.1985 | 3.1985 | 3.1985 | 3.1985 | 0.0015333 | 0.0015252 | 0.0015063 | 0.0014844 | 0.0014856 | 0.0014952 | 0.0015297 | 0.0015607 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745
| WBL004 | 2114.5 | 12.9 | 12.82 | 12.64 | 12.49 | 12.32 | 12.18 | 12.11 | 12.03 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 10.35 | 10.29 | 10.21 | 10.16 | 10.13 | 10.14 | 10.15 | 10.16 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 10.13 | 5.5575 | 5.5245 | 5.4695 | 5.4295 | 5.3935 | 5.376 | 5.369 | 5.3605 | 5.335 | 5.335 | 5.335 | 5.335 | 5.335 | 5.335 | 5.335 | 5.335 | 5.335 | 5.335 | 5.335 | 5.335 | 5.335 | 0.0026283 | 0.0026127 | 0.0025867 | 0.0025677 | 0.0025507 | 0.0025424 | 0.0025391 | 0.0025351 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231
| WBL005 | 2611.5 | 5.97 | 6.03 | 6.09 | 6.14 | 6.14 | 6.29 | 6.54 | 6.76 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 6.89 | 5.4 | 5.46 | 5.51 | 5.66 | 5.82 | 6.03 | 6.27 | 6.48 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 2.7855 | 2.8155 | 2.842 | 2.902 | 2.958 | 3.054 | 3.1755 | 3.282 | 3.3435 | 3.3435 | 3.3435 | 3.3435 | 3.3435 | 3.3435 | 3.3435 | 3.3435 | 3.3435 | 3.3435 | 3.3435 | 3.3435 | 3.3435 | 0.0010666 | 0.0010781 | 0.0010883 | 0.0011112 | 0.0011327 | 0.0011694 | 0.001216 | 0.0012567 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803
| WBL006 | 2867.5 | 4.86 | 4.93 | 4.98 | 5.08 | 5.24 | 5.45 | 5.67 | 5.86 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4.39 | 4.52 | 4.69 | 4.86 | 5.03 | 5.23 | 5.44 | 5.62 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 2.2655 | 2.3215 | 2.3885 | 2.463 | 2.5465 | 2.648 | 2.7545 | 2.846 | 2.916 | 2.916 | 2.916 | 2.916 | 2.916 | 2.916 | 2.916 | 2.916 | 2.916 | 2.916 | 2.916 | 2.916 | 2.916 | 0.00079006 | 0.00080959 | 0.00083296 | 0.00085894 | 0.00088806 | 0.00092345 | 0.00096059 | 0.0009925 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169
| WBL008 | 2347.5 | 5.58 | 5.49 | 5.37 | 5.28 | 5.17 | 5.12 | 5.23 | 5.33 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 5.37 | 4.87 | 4.84 | 4.76 | 4.67 | 4.73 | 4.82 | 4.94 | 5.04 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 5.09 | 2.5415 | 2.5175 | 2.4715 | 2.4265 | 2.431 | 2.455 | 2.5135 | 2.5635 | 2.587 | 2.587 | 2.587 | 2.587 | 2.587 | 2.587 | 2.587 | 2.587 | 2.587 | 2.587 | 2.587 | 2.587 | 2.587 | 0.0010826 | 0.0010724 | 0.0010528 | 0.0010337 | 0.0010356 | 0.0010458 | 0.0010707 | 0.001092 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102
| WBL010 | 1129.5 | 7.09 | 6.94 | 6.79 | 6.63 | 6.49 | 6.37 | 6.39 | 6.41 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.53 | 6.41 | 6.23 | 6.1 | 6.05 | 6.05 | 6.09 | 6.11 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 6.08 | 3.349 | 3.2845 | 3.199 | 3.1295 | 3.091 | 3.073 | 3.09 | 3.1 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 3.085 | 0.002965 | 0.0029079 | 0.0028322 | 0.0027707 | 0.0027366 | 0.0027207 | 0.0027357 | 0.0027446 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313
| WBL012 | 2829 | 9.59 | 9.67 | 9.77 | 9.79 | 9.71 | 9.71 | 9.86 | 10.02 | 9.97 | 9.97 | 9.97 | 9.97 | 9.97 | 9.97 | 9.97 | 9.97 | 9.97 | 9.97 | 9.97 | 9.97 | 9.97 | 8.92 | 9.02 | 9.06 | 9.07 | 9 | 8.97 | 9.07 | 9.22 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 4.5605 | 4.6075 | 4.6365 | 4.643 | 4.6065 | 4.596 | 4.6535 | 4.73 | 4.7085 | 4.7085 | 4.7085 | 4.7085 | 4.7085 | 4.7085 | 4.7085 | 4.7085 | 4.7085 | 4.7085 | 4.7085 | 4.7085 | 4.7085 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644
| WIN011 | 2316.5 | 5.35 | 5.39 | 5.41 | 5.4 | 5.38 | 5.37 | 5.39 | 5.44 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 5.43 | 4.72 | 4.76 | 4.82 | 4.86 | 4.89 | 4.96 | 5.05 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 2.4545 | 2.4745 | 2.4985 | 2.511 | 2.5185 | 2.5415 | 2.576 | 2.608 | 2.6065 | 2.6065 | 2.6065 | 2.6065 | 2.6065 | 2.6065 | 2.6065 | 2.6065 | 2.6065 | 2.6065 | 2.6065 | 2.6065 | 2.6065 | 0.0010596 | 0.0010682 | 0.0010786 | 0.001084 | 0.0010872 | 0.0010971 | 0.001112 | 0.0011258 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252
| WIN022 | 1083.5 | 2.78 | 2.8 | 2.81 | 2.81 | 2.8 | 2.79 | 2.81 | 2.83 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.55 | 2.56 | 2.58 | 2.59 | 2.58 | 2.59 | 2.62 | 2.64 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 1.3095 | 1.316 | 1.3245 | 1.328 | 1.323 | 1.325 | 1.3385 | 1.3485 | 1.3385 | 1.3385 | 1.3385 | 1.3385 | 1.3385 | 1.3385 | 1.3385 | 1.3385 | 1.3385 | 1.3385 | 1.3385 | 1.3385 | 1.3385 | 0.0012086 | 0.0012146 | 0.0012224 | 0.0012257 | 0.001221 | 0.0012229 | 0.0012353 | 0.0012446 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353
| WIN023 | 851 | 2.8 | 2.83 | 2.88 | 2.91 | 2.92 | 2.95 | 3.01 | 3.08 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 2.51 | 2.55 | 2.58 | 2.62 | 2.63 | 2.65 | 2.71 | 2.79 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 2.84 | 1.2985 | 1.317 | 1.335 | 1.3535 | 1.3585 | 1.37 | 1.4 | 1.4385 | 1.462 | 1.462 | 1.462 | 1.462 | 1.462 | 1.462 | 1.462 | 1.462 | 1.462 | 1.462 | 1.462 | 1.462 | 1.462 | 0.0015259 | 0.0015476 | 0.0015687 | 0.0015905 | 0.0015964 | 0.0016099 | 0.0016451 | 0.0016904 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718
| WMN013 | 108.5 | 7.85 | 7.84 | 7.8 | 7.71 | 7.57 | 7.48 | 7.49 | 7.52 | 7.39 | 7.39 | 7.39 | 7.39 | 7.39 | 7.39 | 7.39 | 7.39 | 7.39 | 7.39 | 7.39 | 7.39 | 7.39 | 6.66 | 6.67 | 6.63 | 6.58 | 6.47 | 6.38 | 6.38 | 6.41 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 3.5085 | 3.5105 | 3.4905 | 3.4595 | 3.4 | 3.355 | 3.3565 | 3.3715 | 3.3205 | 3.3205 | 3.3205 | 3.3205 | 3.3205 | 3.3205 | 3.3205 | 3.3205 | 3.3205 | 3.3205 | 3.3205 | 3.3205 | 3.3205 | 0.032336 | 0.032355 | 0.032171 | 0.031885 | 0.031336 | 0.030922 | 0.030935 | 0.031074 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604
| WMN014 | 190 | 10.55 | 10.83 | 10.95 | 11.06 | 11 | 10.98 | 11.12 | 11.38 | 11.38 | 11.38 | 11.38 | 11.38 | 11.38 | 11.38 | 11.38 | 11.38 | 11.38 | 11.38 | 11.38 | 11.38 | 11.38 | 8.91 | 9.13 | 9.25 | 9.33 | 9.27 | 9.26 | 9.39 | 9.61 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 9.57 | 4.701 | 4.82 | 4.88 | 4.9245 | 4.8945 | 4.888 | 4.9545 | 5.0705 | 5.0565 | 5.0565 | 5.0565 | 5.0565 | 5.0565 | 5.0565 | 5.0565 | 5.0565 | 5.0565 | 5.0565 | 5.0565 | 5.0565 | 5.0565 | 0.024742 | 0.025368 | 0.025684 | 0.025918 | 0.025761 | 0.025726 | 0.026076 | 0.026687 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613
| WMN021 | 78 | 13.45 | 13.58 | 13.54 | 13.47 | 13.28 | 13.11 | 13.14 | 13.24 | 13.13 | 13.13 | 13.13 | 13.13 | 13.13 | 13.13 | 13.13 | 13.13 | 13.13 | 13.13 | 13.13 | 13.13 | 13.13 | 11.88 | 11.98 | 11.93 | 11.86 | 11.68 | 11.54 | 11.56 | 11.66 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 11.54 | 6.1755 | 6.23 | 6.2065 | 6.1715 | 6.08 | 6.0055 | 6.017 | 6.067 | 6.0085 | 6.0085 | 6.0085 | 6.0085 | 6.0085 | 6.0085 | 6.0085 | 6.0085 | 6.0085 | 6.0085 | 6.0085 | 6.0085 | 6.0085 | 0.079173 | 0.079872 | 0.079571 | 0.079122 | 0.077949 | 0.076994 | 0.077141 | 0.077782 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032
| WND011 | 266.5 | 0.86 | 0.87 | 0.89 | 0.91 | 0.92 | 0.93 | 0.96 | 0.98 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.81 | 0.82 | 0.84 | 0.85 | 0.87 | 0.88 | 0.9 | 0.92 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.4125 | 0.4175 | 0.4275 | 0.434 | 0.4425 | 0.4475 | 0.459 | 0.469 | 0.474 | 0.474 | 0.474 | 0.474 | 0.474 | 0.474 | 0.474 | 0.474 | 0.474 | 0.474 | 0.474 | 0.474 | 0.474 | 0.0015478 | 0.0015666 | 0.0016041 | 0.0016285 | 0.0016604 | 0.0016792 | 0.0017223 | 0.0017598 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786
| WND012 | 3569 | 4.34 | 4.4 | 4.46 | 4.51 | 4.55 | 4.65 | 4.79 | 4.89 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 3.88 | 3.92 | 3.98 | 4.02 | 4.05 | 4.13 | 4.26 | 4.35 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 2.009 | 2.032 | 2.062 | 2.0835 | 2.1 | 2.143 | 2.2095 | 2.256 | 2.2775 | 2.2775 | 2.2775 | 2.2775 | 2.2775 | 2.2775 | 2.2775 | 2.2775 | 2.2775 | 2.2775 | 2.2775 | 2.2775 | 2.2775 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813
| WND013 | 2863 | 7.51 | 7.85 | 8.24 | 8.59 | 8.89 | 9.32 | 9.8 | 10.23 | 10.55 | 10.55 | 10.55 | 10.55 | 10.55 | 10.55 | 10.55 | 10.55 | 10.55 | 10.55 | 10.55 | 10.55 | 10.55 | 7.18 | 7.51 | 7.89 | 8.23 | 8.55 | 8.96 | 9.43 | 9.85 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 10.18 | 3.6395 | 3.806 | 3.9975 | 4.169 | 4.326 | 4.534 | 4.7705 | 4.982 | 5.1455 | 5.1455 | 5.1455 | 5.1455 | 5.1455 | 5.1455 | 5.1455 | 5.1455 | 5.1455 | 5.1455 | 5.1455 | 5.1455 | 5.1455 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972
| WND014 | 2973 | 7.25 | 7.32 | 7.46 | 7.56 | 7.65 | 7.82 | 8.07 | 8.26 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 8.34 | 6.89 | 6.97 | 7.11 | 7.22 | 7.31 | 7.48 | 7.72 | 7.92 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 8.02 | 3.499 | 3.5375 | 3.6075 | 3.661 | 3.706 | 3.791 | 3.9125 | 4.011 | 4.058 | 4.058 | 4.058 | 4.058 | 4.058 | 4.058 | 4.058 | 4.058 | 4.058 | 4.058 | 4.058 | 4.058 | 4.058 | 0.0011769 | 0.0011899 | 0.0012134 | 0.0012314 | 0.0012466 | 0.0012751 | 0.001316 | 0.0013491 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365
| WND021 | 828 | 2.1 | 2.16 | 2.24 | 2.3 | 2.36 | 2.43 | 2.53 | 2.61 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.03 | 2.09 | 2.17 | 2.23 | 2.28 | 2.36 | 2.45 | 2.53 | 2.57 | 2.57 | 2.57 | 2.57 | 2.57 | 2.57 | 2.57 | 2.57 | 2.57 | 2.57 | 2.57 | 2.57 | 2.57 | 1.0255 | 1.0555 | 1.0955 | 1.1255 | 1.152 | 1.1905 | 1.237 | 1.277 | 1.297 | 1.297 | 1.297 | 1.297 | 1.297 | 1.297 | 1.297 | 1.297 | 1.297 | 1.297 | 1.297 | 1.297 | 1.297 | 0.0012385 | 0.0012748 | 0.0013231 | 0.0013593 | 0.0013913 | 0.0014378 | 0.001494 | 0.0015423 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664
| WND022 | 688 | 1.39 | 1.44 | 1.51 | 1.57 | 1.63 | 1.7 | 1.78 | 1.86 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.32 | 1.38 | 1.44 | 1.5 | 1.56 | 1.63 | 1.71 | 1.78 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 0.6705 | 0.699 | 0.7305 | 0.7605 | 0.7905 | 0.8255 | 0.8655 | 0.902 | 0.927 | 0.927 | 0.927 | 0.927 | 0.927 | 0.927 | 0.927 | 0.927 | 0.927 | 0.927 | 0.927 | 0.927 | 0.927 | 0.00097456 | 0.001016 | 0.0010618 | 0.0011054 | 0.001149 | 0.0011999 | 0.001258 | 0.001311 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474
| WND023 | 1516 | 7.63 | 7.75 | 7.92 | 8.02 | 8.05 | 8.16 | 8.41 | 8.61 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 6.92 | 7.02 | 7.2 | 7.27 | 7.29 | 7.4 | 7.62 | 7.81 | 7.76 | 7.76 | 7.76 | 7.76 | 7.76 | 7.76 | 7.76 | 7.76 | 7.76 | 7.76 | 7.76 | 7.76 | 7.76 | 3.5665 | 3.6195 | 3.708 | 3.7475 | 3.759 | 3.814 | 3.9285 | 4.025 | 3.9985 | 3.9985 | 3.9985 | 3.9985 | 3.9985 | 3.9985 | 3.9985 | 3.9985 | 3.9985 | 3.9985 | 3.9985 | 3.9985 | 3.9985 | 0.0023526 | 0.0023875 | 0.0024459 | 0.002472 | 0.0024796 | 0.0025158 | 0.0025914 | 0.002655 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375
| WND024 | 2045 | 6.2 | 6.6 | 6.68 | 6.73 | 6.76 | 6.83 | 6.95 | 7.04 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 6.01 | 6.42 | 6.5 | 6.54 | 6.58 | 6.65 | 6.76 | 6.85 | 6.88 | 6.88 | 6.88 | 6.88 | 6.88 | 6.88 | 6.88 | 6.88 | 6.88 | 6.88 | 6.88 | 6.88 | 6.88 | 3.0335 | 3.237 | 3.277 | 3.2985 | 3.317 | 3.352 | 3.4085 | 3.4535 | 3.4685 | 3.4685 | 3.4685 | 3.4685 | 3.4685 | 3.4685 | 3.4685 | 3.4685 | 3.4685 | 3.4685 | 3.4685 | 3.4685 | 3.4685 | 0.0014834 | 0.0015829 | 0.0016024 | 0.001613 | 0.001622 | 0.0016391 | 0.0016667 | 0.0016888 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961
| WPD012 | 4690 | 16.14 | 16.64 | 17.06 | 17.55 | 17.86 | 18.27 | 18.79 | 19.31 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 14.17 | 14.64 | 15.04 | 15.46 | 15.77 | 16.13 | 16.92 | 17.77 | 18.49 | 18.49 | 18.49 | 18.49 | 18.49 | 18.49 | 18.49 | 18.49 | 18.49 | 18.49 | 18.49 | 18.49 | 18.49 | 7.3805 | 7.62 | 7.823 | 8.0435 | 8.1985 | 8.386 | 8.7405 | 9.116 | 9.4325 | 9.4325 | 9.4325 | 9.4325 | 9.4325 | 9.4325 | 9.4325 | 9.4325 | 9.4325 | 9.4325 | 9.4325 | 9.4325 | 9.4325 | 0.0015737 | 0.0016247 | 0.001668 | 0.001715 | 0.0017481 | 0.0017881 | 0.0018636 | 0.0019437 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112
| WPD013 | 55 | 10.07 | 10.09 | 10.1 | 10.1 | 10.1 | 10.11 | 10.16 | 10.2 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 10.23 | 6.66 | 6.74 | 6.75 | 6.75 | 6.75 | 6.75 | 6.77 | 6.8 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 3.8415 | 3.8725 | 3.8775 | 3.8775 | 3.8775 | 3.879 | 3.8935 | 3.91 | 3.925 | 3.925 | 3.925 | 3.925 | 3.925 | 3.925 | 3.925 | 3.925 | 3.925 | 3.925 | 3.925 | 3.925 | 3.925 | 0.069845 | 0.070409 | 0.0705 | 0.0705 | 0.0705 | 0.070527 | 0.070791 | 0.071091 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364
| WPD014 | 1633.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.0465 | 0.0465 | 0.0465 | 0.0465 | 0.0465 | 0.048 | 0.048 | 0.0515 | 0.0515 | 0.0515 | 0.0515 | 0.0515 | 0.0515 | 0.0515 | 0.0515 | 0.0515 | 0.0515 | 0.0515 | 0.0515 | 0.0515 | 0.0515 | 2.8466e-05 | 2.8466e-05 | 2.8466e-05 | 2.8466e-05 | 2.8466e-05 | 2.9385e-05 | 2.9385e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05
| WPD022 | 5190.5 | 13.75 | 14.48 | 15.09 | 15.69 | 16.21 | 16.78 | 17.45 | 18.47 | 19.34 | 19.34 | 19.34 | 19.34 | 19.34 | 19.34 | 19.34 | 19.34 | 19.34 | 19.34 | 19.34 | 19.34 | 19.34 | 12.4 | 13.03 | 13.58 | 14.12 | 14.6 | 15.27 | 16.3 | 17.26 | 18.09 | 18.09 | 18.09 | 18.09 | 18.09 | 18.09 | 18.09 | 18.09 | 18.09 | 18.09 | 18.09 | 18.09 | 18.09 | 6.4025 | 6.7325 | 7.0165 | 7.2955 | 7.5415 | 7.8615 | 8.3225 | 8.8115 | 9.2325 | 9.2325 | 9.2325 | 9.2325 | 9.2325 | 9.2325 | 9.2325 | 9.2325 | 9.2325 | 9.2325 | 9.2325 | 9.2325 | 9.2325 | 0.0012335 | 0.0012971 | 0.0013518 | 0.0014055 | 0.0014529 | 0.0015146 | 0.0016034 | 0.0016976 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787
| WPD024 | 5439 | 7.13 | 7.31 | 7.46 | 7.64 | 7.8 | 7.99 | 8.22 | 8.47 | 8.64 | 8.64 | 8.64 | 8.64 | 8.64 | 8.64 | 8.64 | 8.64 | 8.64 | 8.64 | 8.64 | 8.64 | 8.64 | 6.29 | 6.46 | 6.6 | 6.74 | 6.89 | 7.08 | 7.3 | 7.55 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74 | 7.74 | 3.271 | 3.3575 | 3.429 | 3.505 | 3.5815 | 3.6765 | 3.788 | 3.913 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 0.0006014 | 0.0006173 | 0.00063045 | 0.00064442 | 0.00065849 | 0.00067595 | 0.00069645 | 0.00071943 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635
| WPD031 | 3692 | 6.2 | 6.44 | 6.65 | 6.88 | 7.1 | 7.54 | 7.99 | 8.4 | 8.74 | 8.74 | 8.74 | 8.74 | 8.74 | 8.74 | 8.74 | 8.74 | 8.74 | 8.74 | 8.74 | 8.74 | 8.74 | 5.43 | 5.64 | 5.83 | 6.02 | 6.17 | 6.48 | 6.88 | 7.26 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 7.58 | 2.8305 | 2.94 | 3.038 | 3.139 | 3.2245 | 3.399 | 3.6065 | 3.801 | 3.964 | 3.964 | 3.964 | 3.964 | 3.964 | 3.964 | 3.964 | 3.964 | 3.964 | 3.964 | 3.964 | 3.964 | 3.964 | 0.00076666 | 0.00079632 | 0.00082286 | 0.00085022 | 0.00087337 | 0.00092064 | 0.00097684 | 0.0010295 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737
| WPD033 | 3691.5 | 9.46 | 9.64 | 9.82 | 9.99 | 10.29 | 10.91 | 11.56 | 12.13 | 12.61 | 12.61 | 12.61 | 12.61 | 12.61 | 12.61 | 12.61 | 12.61 | 12.61 | 12.61 | 12.61 | 12.61 | 12.61 | 8.71 | 8.92 | 9.09 | 9.3 | 9.84 | 10.43 | 11.05 | 11.6 | 12.05 | 12.05 | 12.05 | 12.05 | 12.05 | 12.05 | 12.05 | 12.05 | 12.05 | 12.05 | 12.05 | 12.05 | 12.05 | 4.4675 | 4.568 | 4.6545 | 4.7535 | 4.9875 | 5.287 | 5.6015 | 5.8795 | 6.109 | 6.109 | 6.109 | 6.109 | 6.109 | 6.109 | 6.109 | 6.109 | 6.109 | 6.109 | 6.109 | 6.109 | 6.109 | 0.0012102 | 0.0012374 | 0.0012609 | 0.0012877 | 0.0013511 | 0.0014322 | 0.0015174 | 0.0015927 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549

## Combined LOS
Powercor
Pole bushfire resilience program
Combined LOS0_per_year, LOS1_per_year, CUSTO and CUST1
| Equipment | Feeder | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
| AC024-200218081 | AC024 | 0.00022523 | 0.00022778 | 0.00023033 | 0.00023289 | 0.00023544 | 0.00023449 | 0.00023354 | 0.0002326 | 0.00023165 | 0.0002307 | 0.00022976 | 0.00022881 | 0.00022786 | 0.00022691 | 0.00022597 | 0.00022502 | 0.00022407 | 0.00022313 | 0.00022218 | 0.00022123
| AC024-200218767 | AC024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AC024-200218825 | AC024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AC025-200218004 | AC025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AC026-200217919 | AC026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AC031-200217854 | AC031 | 0.054341 | 0.054629 | 0.054918 | 0.055207 | 0.055495 | 0.055465 | 0.055435 | 0.055405 | 0.055375 | 0.055344 | 0.055314 | 0.055284 | 0.055254 | 0.055224 | 0.055193 | 0.055163 | 0.055133 | 0.055103 | 0.055072 | 0.055042
| AC032-200217768 | AC032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL002-15404158 | AL002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL002-200779408 | AL002 | 0.56202 | 0.56826 | 0.57451 | 0.58076 | 0.58701 | 0.585 | 0.58299 | 0.58098 | 0.57897 | 0.57696 | 0.57496 | 0.57295 | 0.57094 | 0.56893 | 0.56692 | 0.56491 | 0.5629 | 0.56089 | 0.55888 | 0.55688
| AL006-200403372 | AL006 | 12.8578 | 12.9604 | 13.063 | 13.1656 | 13.2682 | 13.2278 | 13.1874 | 13.147 | 13.1066 | 13.0661 | 13.0257 | 12.9853 | 12.9449 | 12.9045 | 12.864 | 12.8236 | 12.7832 | 12.7428 | 12.7024 | 12.6619
| AL007-200403464 | AL007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL007-200403526 | AL007 | 0.0063708 | 0.006432 | 0.0064931 | 0.0065543 | 0.0066155 | 0.0065842 | 0.0065529 | 0.0065216 | 0.0064903 | 0.0064589 | 0.0064276 | 0.0063963 | 0.006365 | 0.0063337 | 0.0063024 | 0.0062711 | 0.0062398 | 0.0062085 | 0.0061772 | 0.0061458
| AL011-200635544 | AL011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL012-200635470 | AL012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AL014-200635260 | AL014 | 14.1317 | 14.2259 | 14.32 | 14.4141 | 14.5082 | 14.4853 | 14.4623 | 14.4393 | 14.4163 | 14.3933 | 14.3704 | 14.3474 | 14.3244 | 14.3014 | 14.2784 | 14.2555 | 14.2325 | 14.2095 | 14.1865 | 14.1636
| ART023-15411707 | ART023 | 21.4474 | 21.6185 | 21.7897 | 21.9608 | 22.132 | 22.1509 | 22.1699 | 22.1888 | 22.2078 | 22.2267 | 22.2457 | 22.2646 | 22.2835 | 22.3025 | 22.3214 | 22.3404 | 22.3593 | 22.3783 | 22.3972 | 22.4162
| ART023-15411718 | ART023 | 7.5157e-07 | 7.6143e-07 | 7.7129e-07 | 7.8114e-07 | 7.91e-07 | 7.927e-07 | 7.944e-07 | 7.961e-07 | 7.978e-07 | 7.995e-07 | 8.012e-07 | 8.029e-07 | 8.046e-07 | 8.063e-07 | 8.08e-07 | 8.097e-07 | 8.114e-07 | 8.131e-07 | 8.148e-07 | 8.165e-07
| ART023-154832740 | ART023 | 0.007115 | 0.007181 | 0.007247 | 0.0073131 | 0.0073791 | 0.0073805 | 0.0073818 | 0.0073832 | 0.0073846 | 0.007386 | 0.0073874 | 0.0073887 | 0.0073901 | 0.0073915 | 0.0073929 | 0.0073943 | 0.0073956 | 0.007397 | 0.0073984 | 0.0073998
| ART023-154832902 | ART023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART023-24601770 | ART023 | 2.9303 | 2.9573 | 2.9842 | 3.0112 | 3.0381 | 3.0392 | 3.0403 | 3.0413 | 3.0424 | 3.0435 | 3.0445 | 3.0456 | 3.0467 | 3.0477 | 3.0488 | 3.0499 | 3.0509 | 3.052 | 3.0531 | 3.0541
| ART023-63832300 | ART023 | 4.3302 | 4.3623 | 4.3944 | 4.4265 | 4.4585 | 4.4592 | 4.4598 | 4.4605 | 4.4611 | 4.4617 | 4.4624 | 4.463 | 4.4636 | 4.4643 | 4.4649 | 4.4656 | 4.4662 | 4.4668 | 4.4675 | 4.4681
| ART023-76359967 | ART023 | 0.78702 | 0.79408 | 0.80114 | 0.8082 | 0.81526 | 0.81457 | 0.81389 | 0.8132 | 0.81251 | 0.81183 | 0.81114 | 0.81046 | 0.80977 | 0.80909 | 0.8084 | 0.80772 | 0.80703 | 0.80634 | 0.80566 | 0.80497
| ART031-140150600 | ART031 | 0.23627 | 0.23791 | 0.23955 | 0.24119 | 0.24283 | 0.24268 | 0.24253 | 0.24239 | 0.24224 | 0.24209 | 0.24194 | 0.2418 | 0.24165 | 0.2415 | 0.24135 | 0.2412 | 0.24106 | 0.24091 | 0.24076 | 0.24061
| ART031-15411744 | ART031 | 17.3122 | 17.4365 | 17.5607 | 17.6849 | 17.8091 | 17.8257 | 17.8423 | 17.8588 | 17.8754 | 17.892 | 17.9086 | 17.9252 | 17.9418 | 17.9583 | 17.9749 | 17.9915 | 18.0081 | 18.0247 | 18.0413 | 18.0578
| ART031-155164001 | ART031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART031-155164103 | ART031 | 0.00025449 | 0.00025731 | 0.00026014 | 0.00026297 | 0.0002658 | 0.00026604 | 0.00026628 | 0.00026652 | 0.00026676 | 0.000267 | 0.00026724 | 0.00026748 | 0.00026772 | 0.00026796 | 0.0002682 | 0.00026844 | 0.00026868 | 0.00026892 | 0.00026916 | 0.0002694
| ART031-76359985 | ART031 | 0.072704 | 0.073352 | 0.074001 | 0.074649 | 0.075297 | 0.075361 | 0.075425 | 0.075488 | 0.075552 | 0.075616 | 0.07568 | 0.075744 | 0.075807 | 0.075871 | 0.075935 | 0.075999 | 0.076062 | 0.076126 | 0.07619 | 0.076254
| ART031-76433910 | ART031 | 9.2195 | 9.2838 | 9.3481 | 9.4124 | 9.4767 | 9.4773 | 9.4779 | 9.4785 | 9.4791 | 9.4797 | 9.4803 | 9.4809 | 9.4815 | 9.4821 | 9.4827 | 9.4833 | 9.4839 | 9.4845 | 9.4851 | 9.4857
| ART031-78747678 | ART031 | 0.10355 | 0.1043 | 0.10505 | 0.1058 | 0.10655 | 0.10669 | 0.10683 | 0.10697 | 0.10711 | 0.10726 | 0.1074 | 0.10754 | 0.10768 | 0.10782 | 0.10797 | 0.10811 | 0.10825 | 0.10839 | 0.10853 | 0.10868
| ART031-78747795 | ART031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-15411794 | ART033 | 35.31 | 35.5532 | 35.7963 | 36.0395 | 36.2826 | 36.1971 | 36.1116 | 36.0261 | 35.9406 | 35.8551 | 35.7696 | 35.6841 | 35.5986 | 35.5131 | 35.4276 | 35.342 | 35.2565 | 35.171 | 35.0855 | 35
| ART033-154972245 | ART033 | 0.046632 | 0.046991 | 0.047349 | 0.047707 | 0.048065 | 0.048118 | 0.04817 | 0.048222 | 0.048275 | 0.048327 | 0.04838 | 0.048432 | 0.048485 | 0.048537 | 0.048589 | 0.048642 | 0.048694 | 0.048747 | 0.048799 | 0.048852
| ART033-154972416 | ART033 | 0.023887 | 0.024101 | 0.024315 | 0.024529 | 0.024743 | 0.024691 | 0.02464 | 0.024588 | 0.024537 | 0.024485 | 0.024434 | 0.024382 | 0.024331 | 0.024279 | 0.024228 | 0.024176 | 0.024125 | 0.024073 | 0.024022 | 0.02397
| ART033-154972520 | ART033 | 0.0096584 | 0.0097545 | 0.0098506 | 0.0099467 | 0.010043 | 0.010053 | 0.010064 | 0.010075 | 0.010085 | 0.010096 | 0.010106 | 0.010117 | 0.010127 | 0.010138 | 0.010149 | 0.010159 | 0.01017 | 0.01018 | 0.010191 | 0.010202
| ART033-154972637 | ART033 | 0.00016853 | 0.00017039 | 0.00017226 | 0.00017413 | 0.000176 | 0.00017508 | 0.00017416 | 0.00017324 | 0.00017232 | 0.0001714 | 0.00017048 | 0.00016956 | 0.00016864 | 0.00016772 | 0.0001668 | 0.00016588 | 0.00016496 | 0.00016404 | 0.00016312 | 0.0001622
| ART033-155019358 | ART033 | 0.010548 | 0.010652 | 0.010757 | 0.010862 | 0.010967 | 0.010933 | 0.010899 | 0.010866 | 0.010832 | 0.010798 | 0.010765 | 0.010731 | 0.010697 | 0.010664 | 0.01063 | 0.010596 | 0.010563 | 0.010529 | 0.010495 | 0.010462
| ART033-155019455 | ART033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ART033-155019644 | ART033 | 0.096525 | 0.097303 | 0.098082 | 0.098861 | 0.099639 | 0.099956 | 0.10027 | 0.10059 | 0.10091 | 0.10122 | 0.10154 | 0.10186 | 0.10217 | 0.10249 | 0.10281 | 0.10312 | 0.10344 | 0.10376 | 0.10408 | 0.10439
| ART033-155019780 | ART033 | 0.0031438 | 0.0031661 | 0.0031883 | 0.0032105 | 0.0032328 | 0.0032281 | 0.0032233 | 0.0032186 | 0.0032139 | 0.0032092 | 0.0032045 | 0.0031998 | 0.0031951 | 0.0031904 | 0.0031857 | 0.003181 | 0.0031763 | 0.0031716 | 0.0031669 | 0.0031622
| ART033-155019881 | ART033 | 0.012499 | 0.012564 | 0.01263 | 0.012696 | 0.012762 | 0.012734 | 0.012706 | 0.012679 | 0.012651 | 0.012623 | 0.012596 | 0.012568 | 0.01254 | 0.012512 | 0.012485 | 0.012457 | 0.012429 | 0.012401 | 0.012374 | 0.012346
| ART033-155025562 | ART033 | 0.033218 | 0.033541 | 0.033864 | 0.034187 | 0.03451 | 0.034345 | 0.03418 | 0.034015 | 0.03385 | 0.033685 | 0.03352 | 0.033355 | 0.033191 | 0.033026 | 0.032861 | 0.032696 | 0.032531 | 0.032366 | 0.032201 | 0.032036
| ART033-155025764 | ART033 | 6.4336e-05 | 6.5152e-05 | 6.5968e-05 | 6.6784e-05 | 6.76e-05 | 6.778e-05 | 6.796e-05 | 6.814e-05 | 6.832e-05 | 6.85e-05 | 6.868e-05 | 6.886e-05 | 6.904e-05 | 6.922e-05 | 6.94e-05 | 6.958e-05 | 6.976e-05 | 6.994e-05 | 7.012e-05 | 7.03e-05
| ART033-155025850 | ART033 | 0.00056881 | 0.00057575 | 0.0005827 | 0.00058965 | 0.0005966 | 0.00059812 | 0.00059964 | 0.00060116 | 0.00060268 | 0.0006042 | 0.00060572 | 0.00060724 | 0.00060876 | 0.00061028 | 0.0006118 | 0.00061332 | 0.00061484 | 0.00061636 | 0.00061788 | 0.0006194
| ART033-155026277 | ART033 | 0.0041639 | 0.0042062 | 0.0042486 | 0.0042909 | 0.0043332 | 0.0043339 | 0.0043346 | 0.0043353 | 0.004336 | 0.0043367 | 0.0043373 | 0.004338 | 0.0043387 | 0.0043394 | 0.0043401 | 0.0043408 | 0.0043415 | 0.0043422 | 0.0043429 | 0.0043436
| ART033-155052342 | ART033 | 0.28445 | 0.28678 | 0.28911 | 0.29144 | 0.29378 | 0.29399 | 0.29421 | 0.29443 | 0.29464 | 0.29486 | 0.29507 | 0.29529 | 0.29551 | 0.29572 | 0.29594 | 0.29616 | 0.29637 | 0.29659 | 0.29681 | 0.29702
| ART033-155052479 | ART033 | 0.002807 | 0.0028326 | 0.0028583 | 0.0028839 | 0.0029096 | 0.0029026 | 0.0028956 | 0.0028887 | 0.0028817 | 0.0028748 | 0.0028678 | 0.0028608 | 0.0028539 | 0.0028469 | 0.00284 | 0.002833 | 0.002826 | 0.0028191 | 0.0028121 | 0.0028052
| ART033-155052606 | ART033 | 2.5971e-05 | 2.6379e-05 | 2.6786e-05 | 2.7193e-05 | 2.76e-05 | 2.7398e-05 | 2.7195e-05 | 2.6993e-05 | 2.679e-05 | 2.6588e-05 | 2.6385e-05 | 2.6183e-05 | 2.598e-05 | 2.5778e-05 | 2.5575e-05 | 2.5373e-05 | 2.517e-05 | 2.4968e-05 | 2.4765e-05 | 2.4563e-05
| ART033-155052720 | ART033 | 2.3326e-05 | 2.363e-05 | 2.3933e-05 | 2.4237e-05 | 2.454e-05 | 2.4447e-05 | 2.4354e-05 | 2.4261e-05 | 2.4168e-05 | 2.4075e-05 | 2.3982e-05 | 2.3889e-05 | 2.3796e-05 | 2.3703e-05 | 2.361e-05 | 2.3517e-05 | 2.3424e-05 | 2.3331e-05 | 2.3238e-05 | 2.3145e-05
| ART033-155062161 | ART033 | 2.0734e-05 | 2.1026e-05 | 2.1317e-05 | 2.1609e-05 | 2.19e-05 | 2.1816e-05 | 2.1732e-05 | 2.1648e-05 | 2.1564e-05 | 2.148e-05 | 2.1396e-05 | 2.1312e-05 | 2.1228e-05 | 2.1144e-05 | 2.106e-05 | 2.0976e-05 | 2.0892e-05 | 2.0808e-05 | 2.0724e-05 | 2.064e-05
| ART033-155062324 | ART033 | 2.2585e-06 | 2.2901e-06 | 2.3217e-06 | 2.3534e-06 | 2.385e-06 | 2.3733e-06 | 2.3616e-06 | 2.3499e-06 | 2.3382e-06 | 2.3265e-06 | 2.3148e-06 | 2.3031e-06 | 2.2914e-06 | 2.2797e-06 | 2.268e-06 | 2.2563e-06 | 2.2446e-06 | 2.2329e-06 | 2.2212e-06 | 2.2095e-06
| ART033-155062418 | ART033 | 0.037352 | 0.037738 | 0.038123 | 0.038508 | 0.038893 | 0.038682 | 0.038471 | 0.03826 | 0.038049 | 0.037838 | 0.037627 | 0.037416 | 0.037206 | 0.036995 | 0.036784 | 0.036573 | 0.036362 | 0.036151 | 0.03594 | 0.035729
| ART033-155079125 | ART033 | 0.013329 | 0.013439 | 0.013548 | 0.013657 | 0.013767 | 0.013706 | 0.013644 | 0.013583 | 0.013522 | 0.013461 | 0.013399 | 0.013338 | 0.013277 | 0.013215 | 0.013154 | 0.013093 | 0.013032 | 0.01297 | 0.012909 | 0.012848
| ART033-155091128 | ART033 | 0.029759 | 0.029934 | 0.030109 | 0.030283 | 0.030458 | 0.030372 | 0.030287 | 0.030201 | 0.030116 | 0.03003 | 0.029945 | 0.029859 | 0.029774 | 0.029688 | 0.029603 | 0.029517 | 0.029432 | 0.029346 | 0.029261 | 0.029175
| ART033-155155386 | ART033 | 0.0031176 | 0.0031392 | 0.0031608 | 0.0031824 | 0.003204 | 0.0031983 | 0.0031925 | 0.0031868 | 0.003181 | 0.0031752 | 0.0031695 | 0.0031637 | 0.003158 | 0.0031522 | 0.0031464 | 0.0031407 | 0.0031349 | 0.0031291 | 0.0031234 | 0.0031176
| ART033-162913151 | ART033 | 1.4224 | 1.4333 | 1.4441 | 1.455 | 1.4659 | 1.4617 | 1.4575 | 1.4533 | 1.449 | 1.4448 | 1.4406 | 1.4364 | 1.4322 | 1.428 | 1.4238 | 1.4196 | 1.4153 | 1.4111 | 1.4069 | 1.4027
| ART033-183308941 | ART033 | 6.3363e-06 | 6.4173e-06 | 6.4982e-06 | 6.5791e-06 | 6.66e-06 | 6.6261e-06 | 6.5922e-06 | 6.5583e-06 | 6.5244e-06 | 6.4905e-06 | 6.4566e-06 | 6.4227e-06 | 6.3888e-06 | 6.3549e-06 | 6.321e-06 | 6.2871e-06 | 6.2532e-06 | 6.2193e-06 | 6.1854e-06 | 6.1515e-06
| ART033-24601322 | ART033 | 4.0046 | 4.0406 | 4.0766 | 4.1126 | 4.1486 | 4.139 | 4.1294 | 4.1197 | 4.1101 | 4.1004 | 4.0908 | 4.0812 | 4.0715 | 4.0619 | 4.0523 | 4.0426 | 4.033 | 4.0234 | 4.0137 | 4.0041
| ART033-80719107 | ART033 | 0.063922 | 0.06446 | 0.064998 | 0.065537 | 0.066075 | 0.06609 | 0.066105 | 0.06612 | 0.066135 | 0.066149 | 0.066164 | 0.066179 | 0.066194 | 0.066209 | 0.066224 | 0.066239 | 0.066254 | 0.066269 | 0.066283 | 0.066298
| ART034-15411844 | ART034 | 63.5463 | 64.0829 | 64.6195 | 65.1561 | 65.6927 | 65.7465 | 65.8002 | 65.854 | 65.9078 | 65.9616 | 66.0154 | 66.0692 | 66.123 | 66.1768 | 66.2306 | 66.2844 | 66.3382 | 66.392 | 66.4458 | 66.4996
| ART034-15411868 | ART034 | 3.7579e-06 | 3.8071e-06 | 3.8564e-06 | 3.9057e-06 | 3.955e-06 | 3.9635e-06 | 3.972e-06 | 3.9805e-06 | 3.989e-06 | 3.9975e-06 | 4.006e-06 | 4.0145e-06 | 4.023e-06 | 4.0315e-06 | 4.04e-06 | 4.0485e-06 | 4.057e-06 | 4.0655e-06 | 4.074e-06 | 4.0825e-06
| BAN001-15414753 | BAN001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN001-15414766 | BAN001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN002-15414829 | BAN002 | 17.8322 | 17.9557 | 18.0793 | 18.2029 | 18.3265 | 18.365 | 18.4035 | 18.442 | 18.4805 | 18.519 | 18.5575 | 18.5961 | 18.6346 | 18.6731 | 18.7116 | 18.7501 | 18.7886 | 18.8271 | 18.8656 | 18.9042
| BAN003-141839634 | BAN003 | 0.039486 | 0.039823 | 0.040161 | 0.040498 | 0.040835 | 0.041 | 0.041165 | 0.04133 | 0.041495 | 0.04166 | 0.041825 | 0.04199 | 0.042155 | 0.04232 | 0.042485 | 0.04265 | 0.042815 | 0.04298 | 0.043145 | 0.04331
| BAN003-141839757 | BAN003 | 0.42045 | 0.42272 | 0.42499 | 0.42726 | 0.42953 | 0.43045 | 0.43136 | 0.43228 | 0.4332 | 0.43411 | 0.43503 | 0.43594 | 0.43686 | 0.43777 | 0.43869 | 0.43961 | 0.44052 | 0.44144 | 0.44235 | 0.44327
| BAN003-141839920 | BAN003 | 0.023229 | 0.023398 | 0.023568 | 0.023738 | 0.023908 | 0.023993 | 0.024078 | 0.024163 | 0.024248 | 0.024333 | 0.024418 | 0.024503 | 0.024588 | 0.024673 | 0.024758 | 0.024843 | 0.024928 | 0.025013 | 0.025099 | 0.025184
| BAN003-141840240 | BAN003 | 0.73646 | 0.74123 | 0.74601 | 0.75078 | 0.75556 | 0.75919 | 0.76281 | 0.76644 | 0.77006 | 0.77369 | 0.77732 | 0.78094 | 0.78457 | 0.7882 | 0.79182 | 0.79545 | 0.79907 | 0.8027 | 0.80633 | 0.80995
| BAN003-154067153 | BAN003 | 139.2057 | 139.8514 | 140.4971 | 141.1427 | 141.7884 | 142.5332 | 143.2779 | 144.0226 | 144.7674 | 145.5121 | 146.2568 | 147.0015 | 147.7463 | 148.491 | 149.2357 | 149.9804 | 150.7252 | 151.4699 | 152.2146 | 152.9594
| BAN003-15414742 | BAN003 | 320.5546 | 320.8195 | 321.0844 | 321.3493 | 321.6142 | 321.3859 | 321.1576 | 320.9293 | 320.701 | 320.4727 | 320.2444 | 320.0161 | 319.7878 | 319.5595 | 319.3312 | 319.1029 | 318.8746 | 318.6463 | 318.418 | 318.1897
| BAN003-159380665 | BAN003 | 0.36564 | 0.36928 | 0.37293 | 0.37658 | 0.38023 | 0.38174 | 0.38326 | 0.38477 | 0.38628 | 0.38779 | 0.3893 | 0.39081 | 0.39233 | 0.39384 | 0.39535 | 0.39686 | 0.39837 | 0.39989 | 0.4014 | 0.40291
| BAN003-159380816 | BAN003 | 0.78119 | 0.78654 | 0.79189 | 0.79723 | 0.80258 | 0.80477 | 0.80695 | 0.80914 | 0.81133 | 0.81352 | 0.81571 | 0.81789 | 0.82008 | 0.82227 | 0.82446 | 0.82665 | 0.82883 | 0.83102 | 0.83321 | 0.8354
| BAN003-163842570 | BAN003 | 0.06279 | 0.063328 | 0.063866 | 0.064404 | 0.064942 | 0.065526 | 0.066111 | 0.066695 | 0.067279 | 0.067863 | 0.068448 | 0.069032 | 0.069616 | 0.070201 | 0.070785 | 0.071369 | 0.071953 | 0.072538 | 0.073122 | 0.073706
| BAN003-164488210 | BAN003 | 0.065261 | 0.065853 | 0.066444 | 0.067035 | 0.067626 | 0.068164 | 0.068702 | 0.06924 | 0.069777 | 0.070315 | 0.070853 | 0.071391 | 0.071929 | 0.072467 | 0.073005 | 0.073543 | 0.07408 | 0.074618 | 0.075156 | 0.075694
| BAN003-171330864 | BAN003 | 0.29354 | 0.29594 | 0.29835 | 0.30076 | 0.30317 | 0.30515 | 0.30712 | 0.3091 | 0.31107 | 0.31305 | 0.31503 | 0.317 | 0.31898 | 0.32095 | 0.32293 | 0.32491 | 0.32688 | 0.32886 | 0.33083 | 0.33281
| BAN003-193118819 | BAN003 | 137.8172 | 138.4752 | 139.1333 | 139.7913 | 140.4494 | 141.3116 | 142.1739 | 143.0361 | 143.8984 | 144.7606 | 145.6229 | 146.4852 | 147.3474 | 148.2097 | 149.0719 | 149.9342 | 150.7964 | 151.6587 | 152.5209 | 153.3832
| BAN003-193396210 | BAN003 | 4.2825 | 4.3122 | 4.342 | 4.3717 | 4.4015 | 4.4372 | 4.473 | 4.5087 | 4.5444 | 4.5802 | 4.6159 | 4.6517 | 4.6874 | 4.7231 | 4.7589 | 4.7946 | 4.8304 | 4.8661 | 4.9018 | 4.9376
| BAN003-193396225 | BAN003 | 11.4508 | 11.5375 | 11.6242 | 11.7109 | 11.7976 | 11.8655 | 11.9334 | 12.0012 | 12.0691 | 12.137 | 12.2048 | 12.2727 | 12.3406 | 12.4085 | 12.4763 | 12.5442 | 12.6121 | 12.68 | 12.7478 | 12.8157
| BAN003-193396423 | BAN003 | 50.716 | 50.9504 | 51.1848 | 51.4193 | 51.6537 | 51.8774 | 52.1011 | 52.3248 | 52.5485 | 52.7722 | 52.9959 | 53.2196 | 53.4433 | 53.667 | 53.8907 | 54.1144 | 54.3381 | 54.5617 | 54.7854 | 55.0091
| BAN003-24598678 | BAN003 | 0.040082 | 0.040428 | 0.040774 | 0.04112 | 0.041465 | 0.041689 | 0.041912 | 0.042136 | 0.04236 | 0.042583 | 0.042807 | 0.043031 | 0.043254 | 0.043478 | 0.043702 | 0.043925 | 0.044149 | 0.044372 | 0.044596 | 0.04482
| BAN003-24598720 | BAN003 | 1.2278 | 1.2286 | 1.2294 | 1.2302 | 1.2309 | 1.2303 | 1.2297 | 1.229 | 1.2284 | 1.2278 | 1.2271 | 1.2265 | 1.2259 | 1.2252 | 1.2246 | 1.2239 | 1.2233 | 1.2227 | 1.222 | 1.2214
| BAN003-24598790 | BAN003 | 15.5207 | 15.5928 | 15.6649 | 15.7369 | 15.809 | 15.8467 | 15.8844 | 15.9221 | 15.9598 | 15.9974 | 16.0351 | 16.0728 | 16.1105 | 16.1482 | 16.1858 | 16.2235 | 16.2612 | 16.2989 | 16.3366 | 16.3742
| BAN003-24610965 | BAN003 | 0.10312 | 0.10387 | 0.10462 | 0.10537 | 0.10612 | 0.10755 | 0.10898 | 0.11042 | 0.11185 | 0.11328 | 0.11471 | 0.11614 | 0.11758 | 0.11901 | 0.12044 | 0.12187 | 0.1233 | 0.12474 | 0.12617 | 0.1276
| BAN003-79423703 | BAN003 | 0.066188 | 0.066658 | 0.067128 | 0.067598 | 0.068067 | 0.068418 | 0.068769 | 0.06912 | 0.069471 | 0.069822 | 0.070173 | 0.070524 | 0.070875 | 0.071226 | 0.071577 | 0.071928 | 0.072279 | 0.07263 | 0.072981 | 0.073332
| BAN003-79424004 | BAN003 | 0.39892 | 0.40166 | 0.4044 | 0.40713 | 0.40987 | 0.41218 | 0.41448 | 0.41679 | 0.41909 | 0.4214 | 0.42371 | 0.42601 | 0.42832 | 0.43063 | 0.43293 | 0.43524 | 0.43754 | 0.43985 | 0.44216 | 0.44446
| BAN003-79424224 | BAN003 | 0.38782 | 0.39078 | 0.39374 | 0.3967 | 0.39966 | 0.40205 | 0.40443 | 0.40681 | 0.40919 | 0.41157 | 0.41395 | 0.41633 | 0.41871 | 0.42109 | 0.42347 | 0.42585 | 0.42824 | 0.43062 | 0.433 | 0.43538
| BAN003-79424313 | BAN003 | 0.26298 | 0.26544 | 0.26791 | 0.27037 | 0.27283 | 0.27443 | 0.27603 | 0.27763 | 0.27923 | 0.28083 | 0.28243 | 0.28403 | 0.28564 | 0.28724 | 0.28884 | 0.29044 | 0.29204 | 0.29364 | 0.29524 | 0.29684
| BAN003-79424384 | BAN003 | 0.81402 | 0.8201 | 0.82619 | 0.83227 | 0.83836 | 0.84294 | 0.84753 | 0.85211 | 0.8567 | 0.86129 | 0.86587 | 0.87046 | 0.87504 | 0.87963 | 0.88421 | 0.8888 | 0.89338 | 0.89797 | 0.90256 | 0.90714
| BAN003-79424629 | BAN003 | 0.5117 | 0.51491 | 0.51813 | 0.52135 | 0.52456 | 0.5279 | 0.53123 | 0.53457 | 0.5379 | 0.54123 | 0.54457 | 0.5479 | 0.55123 | 0.55457 | 0.5579 | 0.56124 | 0.56457 | 0.5679 | 0.57124 | 0.57457
| BAN003-79424820 | BAN003 | 0.17995 | 0.18176 | 0.18357 | 0.18539 | 0.1872 | 0.18798 | 0.18877 | 0.18955 | 0.19034 | 0.19113 | 0.19191 | 0.1927 | 0.19348 | 0.19427 | 0.19505 | 0.19584 | 0.19662 | 0.19741 | 0.19819 | 0.19898
| BAN004-15414853 | BAN004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN004-15414866 | BAN004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN004-15414892 | BAN004 | 2.9688 | 2.9935 | 3.0182 | 3.0429 | 3.0676 | 3.0788 | 3.0901 | 3.1014 | 3.1126 | 3.1239 | 3.1351 | 3.1464 | 3.1576 | 3.1689 | 3.1801 | 3.1914 | 3.2026 | 3.2139 | 3.2252 | 3.2364
| BAN005-15414666 | BAN005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN006-15414916 | BAN006 | 31.9385 | 32.1947 | 32.4509 | 32.7071 | 32.9632 | 33.1131 | 33.263 | 33.4129 | 33.5628 | 33.7127 | 33.8626 | 34.0125 | 34.1624 | 34.3122 | 34.4621 | 34.612 | 34.7619 | 34.9118 | 35.0617 | 35.2116
| BAN006-157281583 | BAN006 | 0.0024723 | 0.0024958 | 0.0025193 | 0.0025429 | 0.0025664 | 0.0025691 | 0.0025717 | 0.0025744 | 0.002577 | 0.0025796 | 0.0025823 | 0.0025849 | 0.0025876 | 0.0025902 | 0.0025929 | 0.0025955 | 0.0025982 | 0.0026008 | 0.0026034 | 0.0026061
| BAN006-161068079 | BAN006 | 0.010241 | 0.010329 | 0.010417 | 0.010504 | 0.010592 | 0.010612 | 0.010632 | 0.010652 | 0.010671 | 0.010691 | 0.010711 | 0.010731 | 0.01075 | 0.01077 | 0.01079 | 0.01081 | 0.010829 | 0.010849 | 0.010869 | 0.010889
| BAN006-193339101 | BAN006 | 4.6388 | 4.6678 | 4.6968 | 4.7258 | 4.7548 | 4.7673 | 4.7799 | 4.7924 | 4.805 | 4.8176 | 4.8301 | 4.8427 | 4.8552 | 4.8678 | 4.8804 | 4.8929 | 4.9055 | 4.918 | 4.9306 | 4.9432
| BAN006-193339124 | BAN006 | 12.0895 | 12.1423 | 12.1952 | 12.2481 | 12.301 | 12.301 | 12.301 | 12.301 | 12.301 | 12.301 | 12.301 | 12.301 | 12.301 | 12.3011 | 12.3011 | 12.3011 | 12.3011 | 12.3011 | 12.3011 | 12.3011
| BAN006-193339156 | BAN006 | 5.7285 | 5.7834 | 5.8382 | 5.8931 | 5.9479 | 5.9577 | 5.9676 | 5.9774 | 5.9872 | 5.997 | 6.0069 | 6.0167 | 6.0265 | 6.0363 | 6.0462 | 6.056 | 6.0658 | 6.0756 | 6.0855 | 6.0953
| BAN006-193339179 | BAN006 | 19.6147 | 19.664 | 19.7134 | 19.7628 | 19.8121 | 19.8745 | 19.9368 | 19.9992 | 20.0616 | 20.1239 | 20.1863 | 20.2487 | 20.311 | 20.3734 | 20.4358 | 20.4981 | 20.5605 | 20.6228 | 20.6852 | 20.7476
| BAN006-72501199 | BAN006 | 0.20126 | 0.20248 | 0.2037 | 0.20492 | 0.20614 | 0.20602 | 0.20591 | 0.20579 | 0.20568 | 0.20557 | 0.20545 | 0.20534 | 0.20522 | 0.20511 | 0.205 | 0.20488 | 0.20477 | 0.20465 | 0.20454 | 0.20443
| BAN006-72501281 | BAN006 | 0.38162 | 0.3846 | 0.38758 | 0.39055 | 0.39353 | 0.39497 | 0.3964 | 0.39783 | 0.39927 | 0.4007 | 0.40214 | 0.40357 | 0.405 | 0.40644 | 0.40787 | 0.4093 | 0.41074 | 0.41217 | 0.41361 | 0.41504
| BAN006-84647249 | BAN006 | 0.11931 | 0.12038 | 0.12145 | 0.12253 | 0.1236 | 0.12369 | 0.12377 | 0.12385 | 0.12394 | 0.12402 | 0.1241 | 0.12419 | 0.12427 | 0.12436 | 0.12444 | 0.12452 | 0.12461 | 0.12469 | 0.12478 | 0.12486
| BAN006-85222599 | BAN006 | 0.10666 | 0.10764 | 0.10862 | 0.10961 | 0.11059 | 0.11093 | 0.11127 | 0.1116 | 0.11194 | 0.11228 | 0.11262 | 0.11296 | 0.1133 | 0.11364 | 0.11398 | 0.11432 | 0.11466 | 0.115 | 0.11534 | 0.11568
| BAN007-15414603 | BAN007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN007-156954231 | BAN007 | 8.7836 | 8.8379 | 8.8923 | 8.9466 | 9.001 | 9.0294 | 9.0578 | 9.0862 | 9.1146 | 9.143 | 9.1714 | 9.1998 | 9.2282 | 9.2566 | 9.285 | 9.3134 | 9.3419 | 9.3703 | 9.3987 | 9.4271
| BAN007-24598874 | BAN007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN007-24598888 | BAN007 | 1.3454 | 1.3481 | 1.3508 | 1.3536 | 1.3563 | 1.3571 | 1.3579 | 1.3587 | 1.3595 | 1.3603 | 1.3612 | 1.362 | 1.3628 | 1.3636 | 1.3644 | 1.3653 | 1.3661 | 1.3669 | 1.3677 | 1.3685
| BAN008-15414979 | BAN008 | 80.3681 | 80.8096 | 81.2512 | 81.6927 | 82.1342 | 82.3457 | 82.5572 | 82.7687 | 82.9802 | 83.1917 | 83.4032 | 83.6147 | 83.8262 | 84.0377 | 84.2492 | 84.4607 | 84.6722 | 84.8837 | 85.0952 | 85.3067
| BAN008-193386449 | BAN008 | 22.3475 | 22.5221 | 22.6968 | 22.8714 | 23.046 | 23.1748 | 23.3036 | 23.4324 | 23.5613 | 23.6901 | 23.8189 | 23.9477 | 24.0765 | 24.2053 | 24.3342 | 24.463 | 24.5918 | 24.7206 | 24.8494 | 24.9782
| BAN008-193386491 | BAN008 | 235.0751 | 236.1877 | 237.3002 | 238.4127 | 239.5253 | 240.5491 | 241.5729 | 242.5967 | 243.6205 | 244.6442 | 245.668 | 246.6918 | 247.7156 | 248.7394 | 249.7632 | 250.787 | 251.8108 | 252.8346 | 253.8584 | 254.8822
| BAN008-193386514 | BAN008 | 46.2465 | 46.4957 | 46.7449 | 46.994 | 47.2432 | 47.445 | 47.6469 | 47.8488 | 48.0506 | 48.2525 | 48.4543 | 48.6562 | 48.8581 | 49.0599 | 49.2618 | 49.4637 | 49.6655 | 49.8674 | 50.0692 | 50.2711
| BAN008-193386533 | BAN008 | 0.78678 | 0.79247 | 0.79817 | 0.80386 | 0.80956 | 0.81357 | 0.81757 | 0.82158 | 0.82559 | 0.82959 | 0.8336 | 0.83761 | 0.84161 | 0.84562 | 0.84963 | 0.85363 | 0.85764 | 0.86165 | 0.86565 | 0.86966
| BAN009-15414553 | BAN009 | 113.0541 | 113.7627 | 114.4714 | 115.1801 | 115.8888 | 116.2705 | 116.6523 | 117.0341 | 117.4158 | 117.7976 | 118.1793 | 118.5611 | 118.9429 | 119.3246 | 119.7064 | 120.0882 | 120.4699 | 120.8517 | 121.2335 | 121.6152
| BAN009-199768607 | BAN009 | 46.5187 | 46.8357 | 47.1527 | 47.4697 | 47.7867 | 48.1382 | 48.4898 | 48.8413 | 49.1928 | 49.5444 | 49.8959 | 50.2474 | 50.599 | 50.9505 | 51.302 | 51.6536 | 52.0051 | 52.3566 | 52.7082 | 53.0597
| BAN009-201078585 | BAN009 | 23.8434 | 24.0302 | 24.2169 | 24.4037 | 24.5905 | 24.6961 | 24.8017 | 24.9074 | 25.013 | 25.1187 | 25.2243 | 25.3299 | 25.4356 | 25.5412 | 25.6468 | 25.7525 | 25.8581 | 25.9638 | 26.0694 | 26.175
| BAN009-77240394 | BAN009 | 1.8133 | 1.8242 | 1.8351 | 1.846 | 1.8569 | 1.8667 | 1.8765 | 1.8864 | 1.8962 | 1.906 | 1.9158 | 1.9256 | 1.9354 | 1.9452 | 1.9551 | 1.9649 | 1.9747 | 1.9845 | 1.9943 | 2.0041
| BAN009-77240588 | BAN009 | 0.23784 | 0.23971 | 0.24159 | 0.24346 | 0.24534 | 0.24691 | 0.24849 | 0.25006 | 0.25164 | 0.25321 | 0.25479 | 0.25636 | 0.25793 | 0.25951 | 0.26108 | 0.26266 | 0.26423 | 0.26581 | 0.26738 | 0.26896
| BAN009-78742110 | BAN009 | 0.063224 | 0.063798 | 0.064373 | 0.064948 | 0.065522 | 0.065702 | 0.065881 | 0.066061 | 0.06624 | 0.06642 | 0.066599 | 0.066779 | 0.066958 | 0.067138 | 0.067317 | 0.067497 | 0.067676 | 0.067856 | 0.068035 | 0.068215
| BAN009-78742394 | BAN009 | 0.021284 | 0.021491 | 0.021697 | 0.021904 | 0.022111 | 0.022307 | 0.022503 | 0.0227 | 0.022896 | 0.023092 | 0.023288 | 0.023485 | 0.023681 | 0.023877 | 0.024074 | 0.02427 | 0.024466 | 0.024662 | 0.024859 | 0.025055
| BAN011-15414529 | BAN011 | 7.7984 | 7.835 | 7.8715 | 7.9081 | 7.9447 | 7.9465 | 7.9483 | 7.9501 | 7.9518 | 7.9536 | 7.9554 | 7.9572 | 7.959 | 7.9607 | 7.9625 | 7.9643 | 7.9661 | 7.9678 | 7.9696 | 7.9714
| BAN011-171348706 | BAN011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN013-15414453 | BAN013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN015-15414416 | BAN015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAN015-24611936 | BAN015 | 75.7295 | 76.0765 | 76.4234 | 76.7704 | 77.1173 | 77.3713 | 77.6253 | 77.8793 | 78.1333 | 78.3873 | 78.6413 | 78.8953 | 79.1492 | 79.4032 | 79.6572 | 79.9112 | 80.1652 | 80.4192 | 80.6732 | 80.9272
| BAS011-111131839 | BAS011 | 0.007553 | 0.00761 | 0.007667 | 0.0077239 | 0.0077809 | 0.00782 | 0.0078591 | 0.0078982 | 0.0079373 | 0.0079764 | 0.0080155 | 0.0080546 | 0.0080937 | 0.0081328 | 0.0081719 | 0.008211 | 0.0082501 | 0.0082892 | 0.0083283 | 0.0083674
| BAS011-134530801 | BAS011 | 0.10131 | 0.1018 | 0.10228 | 0.10277 | 0.10326 | 0.10347 | 0.10367 | 0.10388 | 0.10409 | 0.1043 | 0.10451 | 0.10472 | 0.10493 | 0.10514 | 0.10535 | 0.10555 | 0.10576 | 0.10597 | 0.10618 | 0.10639
| BAS011-140236715 | BAS011 | 0.037571 | 0.037768 | 0.037965 | 0.038162 | 0.038359 | 0.038243 | 0.038128 | 0.038012 | 0.037897 | 0.037781 | 0.037666 | 0.03755 | 0.037435 | 0.037319 | 0.037204 | 0.037088 | 0.036973 | 0.036857 | 0.036742 | 0.036626
| BAS011-140237055 | BAS011 | 0.022156 | 0.022333 | 0.022511 | 0.022688 | 0.022865 | 0.022794 | 0.022722 | 0.02265 | 0.022579 | 0.022507 | 0.022435 | 0.022363 | 0.022292 | 0.02222 | 0.022148 | 0.022076 | 0.022005 | 0.021933 | 0.021861 | 0.021789
| BAS011-15414096 | BAS011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS011-15414109 | BAS011 | 61.1409 | 61.4579 | 61.7749 | 62.0918 | 62.4088 | 62.5276 | 62.6464 | 62.7651 | 62.8839 | 63.0027 | 63.1215 | 63.2403 | 63.359 | 63.4778 | 63.5966 | 63.7154 | 63.8342 | 63.9529 | 64.0717 | 64.1905
| BAS011-158128939 | BAS011 | 0.08157 | 0.082247 | 0.082925 | 0.083602 | 0.08428 | 0.084501 | 0.084723 | 0.084944 | 0.085166 | 0.085387 | 0.085608 | 0.08583 | 0.086051 | 0.086273 | 0.086494 | 0.086716 | 0.086937 | 0.087158 | 0.08738 | 0.087601
| BAS011-158493706 | BAS011 | 0.013058 | 0.013152 | 0.013247 | 0.013341 | 0.013436 | 0.013501 | 0.013566 | 0.013632 | 0.013697 | 0.013763 | 0.013828 | 0.013894 | 0.013959 | 0.014025 | 0.01409 | 0.014156 | 0.014221 | 0.014286 | 0.014352 | 0.014417
| BAS011-158493822 | BAS011 | 1.9702e-05 | 1.9952e-05 | 2.0201e-05 | 2.0451e-05 | 2.07e-05 | 2.0691e-05 | 2.0682e-05 | 2.0673e-05 | 2.0664e-05 | 2.0655e-05 | 2.0646e-05 | 2.0637e-05 | 2.0628e-05 | 2.0619e-05 | 2.061e-05 | 2.0601e-05 | 2.0592e-05 | 2.0583e-05 | 2.0574e-05 | 2.0565e-05
| BAS011-163842929 | BAS011 | 0.035168 | 0.035393 | 0.035619 | 0.035844 | 0.03607 | 0.036209 | 0.036348 | 0.036488 | 0.036627 | 0.036766 | 0.036906 | 0.037045 | 0.037184 | 0.037324 | 0.037463 | 0.037602 | 0.037742 | 0.037881 | 0.03802 | 0.03816
| BAS011-163930345 | BAS011 | 0.0033179 | 0.0033442 | 0.0033704 | 0.0033967 | 0.0034229 | 0.0034112 | 0.0033994 | 0.0033876 | 0.0033758 | 0.003364 | 0.0033522 | 0.0033405 | 0.0033287 | 0.0033169 | 0.0033051 | 0.0032933 | 0.0032815 | 0.0032697 | 0.003258 | 0.0032462
| BAS011-163930441 | BAS011 | 8.9358e-06 | 9.0418e-06 | 9.1479e-06 | 9.2539e-06 | 9.36e-06 | 9.324e-06 | 9.288e-06 | 9.252e-06 | 9.216e-06 | 9.18e-06 | 9.144e-06 | 9.108e-06 | 9.072e-06 | 9.036e-06 | 9e-06 | 8.964e-06 | 8.928e-06 | 8.892e-06 | 8.856e-06 | 8.82e-06
| BAS011-164206932 | BAS011 | 8.095 | 8.1513 | 8.2076 | 8.264 | 8.3203 | 8.3452 | 8.37 | 8.3949 | 8.4198 | 8.4447 | 8.4695 | 8.4944 | 8.5193 | 8.5442 | 8.569 | 8.5939 | 8.6188 | 8.6437 | 8.6685 | 8.6934
| BAS011-164206954 | BAS011 | 23.2991 | 23.4765 | 23.654 | 23.8315 | 24.009 | 24.0612 | 24.1135 | 24.1657 | 24.218 | 24.2702 | 24.3225 | 24.3747 | 24.427 | 24.4792 | 24.5315 | 24.5837 | 24.636 | 24.6883 | 24.7405 | 24.7928
| BAS011-164206976 | BAS011 | 15.7714 | 15.8763 | 15.9811 | 16.086 | 16.1909 | 16.2107 | 16.2305 | 16.2504 | 16.2702 | 16.29 | 16.3099 | 16.3297 | 16.3496 | 16.3694 | 16.3892 | 16.4091 | 16.4289 | 16.4487 | 16.4686 | 16.4884
| BAS011-164287379 | BAS011 | 0.40582 | 0.40946 | 0.41309 | 0.41673 | 0.42037 | 0.42164 | 0.42292 | 0.4242 | 0.42547 | 0.42675 | 0.42803 | 0.42931 | 0.43058 | 0.43186 | 0.43314 | 0.43441 | 0.43569 | 0.43697 | 0.43824 | 0.43952
| BAS011-172348924 | BAS011 | 0.48513 | 0.48758 | 0.49002 | 0.49247 | 0.49491 | 0.49547 | 0.49603 | 0.49659 | 0.49715 | 0.49771 | 0.49827 | 0.49883 | 0.49939 | 0.49995 | 0.50051 | 0.50107 | 0.50162 | 0.50218 | 0.50274 | 0.5033
| BAS011-182896771 | BAS011 | 0.0077573 | 0.0078274 | 0.0078974 | 0.0079675 | 0.0080376 | 0.0080399 | 0.0080422 | 0.0080445 | 0.0080467 | 0.008049 | 0.0080513 | 0.0080536 | 0.0080559 | 0.0080581 | 0.0080604 | 0.0080627 | 0.008065 | 0.0080673 | 0.0080695 | 0.0080718
| BAS011-24598608 | BAS011 | 4.0788 | 4.1036 | 4.1284 | 4.1533 | 4.1781 | 4.1885 | 4.1988 | 4.2091 | 4.2195 | 4.2298 | 4.2401 | 4.2505 | 4.2608 | 4.2711 | 4.2815 | 4.2918 | 4.3021 | 4.3125 | 4.3228 | 4.3331
| BAS011-24602396 | BAS011 | 0.07593 | 0.07614 | 0.076351 | 0.076562 | 0.076772 | 0.076722 | 0.076671 | 0.076621 | 0.07657 | 0.07652 | 0.076469 | 0.076418 | 0.076368 | 0.076317 | 0.076267 | 0.076216 | 0.076166 | 0.076115 | 0.076065 | 0.076014
| BAS011-24608723 | BAS011 | 0.01372 | 0.013804 | 0.013888 | 0.013973 | 0.014057 | 0.014121 | 0.014185 | 0.014249 | 0.014313 | 0.014377 | 0.014441 | 0.014505 | 0.014569 | 0.014633 | 0.014697 | 0.014761 | 0.014825 | 0.014889 | 0.014953 | 0.015017
| BAS011-76148984 | BAS011 | 0.0042882 | 0.0043198 | 0.0043513 | 0.0043829 | 0.0044144 | 0.0044175 | 0.0044206 | 0.0044236 | 0.0044267 | 0.0044297 | 0.0044328 | 0.0044359 | 0.0044389 | 0.004442 | 0.004445 | 0.0044481 | 0.0044512 | 0.0044542 | 0.0044573 | 0.0044603
| BAS011-76149624 | BAS011 | 0.016055 | 0.016166 | 0.016278 | 0.016389 | 0.0165 | 0.016512 | 0.016524 | 0.016536 | 0.016548 | 0.01656 | 0.016572 | 0.016584 | 0.016596 | 0.016608 | 0.01662 | 0.016632 | 0.016644 | 0.016656 | 0.016667 | 0.016679
| BAS011-76150176 | BAS011 | 0.064196 | 0.064744 | 0.065291 | 0.065838 | 0.066386 | 0.066433 | 0.06648 | 0.066527 | 0.066575 | 0.066622 | 0.066669 | 0.066716 | 0.066764 | 0.066811 | 0.066858 | 0.066905 | 0.066953 | 0.067 | 0.067047 | 0.067095
| BAS011-76150520 | BAS011 | 0.083564 | 0.084202 | 0.08484 | 0.085478 | 0.086116 | 0.086096 | 0.086077 | 0.086057 | 0.086037 | 0.086017 | 0.085997 | 0.085977 | 0.085958 | 0.085938 | 0.085918 | 0.085898 | 0.085878 | 0.085858 | 0.085839 | 0.085819
| BAS011-76150666 | BAS011 | 0.15309 | 0.15429 | 0.15549 | 0.15669 | 0.15789 | 0.15815 | 0.15841 | 0.15868 | 0.15894 | 0.1592 | 0.15946 | 0.15972 | 0.15999 | 0.16025 | 0.16051 | 0.16077 | 0.16104 | 0.1613 | 0.16156 | 0.16182
| BAS011-79244341 | BAS011 | 0.021814 | 0.021971 | 0.022127 | 0.022284 | 0.02244 | 0.022561 | 0.022682 | 0.022803 | 0.022924 | 0.023044 | 0.023165 | 0.023286 | 0.023407 | 0.023528 | 0.023648 | 0.023769 | 0.02389 | 0.024011 | 0.024132 | 0.024252
| BAS011-79244394 | BAS011 | 0.064481 | 0.064996 | 0.065511 | 0.066025 | 0.06654 | 0.066734 | 0.066927 | 0.067121 | 0.067315 | 0.067508 | 0.067702 | 0.067895 | 0.068089 | 0.068283 | 0.068476 | 0.06867 | 0.068864 | 0.069057 | 0.069251 | 0.069445
| BAS011-79244446 | BAS011 | 0.88669 | 0.89263 | 0.89858 | 0.90452 | 0.91047 | 0.91161 | 0.91275 | 0.91389 | 0.91503 | 0.91617 | 0.91731 | 0.91845 | 0.91958 | 0.92072 | 0.92186 | 0.923 | 0.92414 | 0.92528 | 0.92642 | 0.92756
| BAS011-79244508 | BAS011 | 0.0013723 | 0.0013835 | 0.0013948 | 0.001406 | 0.0014172 | 0.0014214 | 0.0014255 | 0.0014296 | 0.0014337 | 0.0014378 | 0.0014419 | 0.001446 | 0.0014501 | 0.0014542 | 0.0014583 | 0.0014624 | 0.0014665 | 0.0014706 | 0.0014747 | 0.0014788
| BAS011-79244589 | BAS011 | 0.033077 | 0.033396 | 0.033716 | 0.034035 | 0.034354 | 0.034375 | 0.034395 | 0.034416 | 0.034437 | 0.034458 | 0.034479 | 0.034499 | 0.03452 | 0.034541 | 0.034562 | 0.034583 | 0.034603 | 0.034624 | 0.034645 | 0.034666
| BAS011-79245218 | BAS011 | 0.0022017 | 0.0022069 | 0.0022121 | 0.0022173 | 0.0022225 | 0.0022213 | 0.00222 | 0.0022188 | 0.0022176 | 0.0022164 | 0.0022152 | 0.0022139 | 0.0022127 | 0.0022115 | 0.0022103 | 0.002209 | 0.0022078 | 0.0022066 | 0.0022054 | 0.0022041
| BAS011-84427318 | BAS011 | 0.048637 | 0.04905 | 0.049463 | 0.049876 | 0.050288 | 0.050382 | 0.050476 | 0.05057 | 0.050664 | 0.050758 | 0.050852 | 0.050946 | 0.05104 | 0.051134 | 0.051228 | 0.051322 | 0.051416 | 0.051509 | 0.051603 | 0.051697
| BAS011-84621962 | BAS011 | 0.7527 | 0.7565 | 0.76029 | 0.76409 | 0.76788 | 0.76888 | 0.76987 | 0.77087 | 0.77187 | 0.77286 | 0.77386 | 0.77486 | 0.77585 | 0.77685 | 0.77785 | 0.77884 | 0.77984 | 0.78083 | 0.78183 | 0.78283
| BAS011-84622282 | BAS011 | 0.21739 | 0.2187 | 0.22001 | 0.22132 | 0.22263 | 0.22338 | 0.22413 | 0.22488 | 0.22563 | 0.22638 | 0.22713 | 0.22788 | 0.22863 | 0.22938 | 0.23013 | 0.23088 | 0.23163 | 0.23238 | 0.23313 | 0.23388
| BAS011-84732066 | BAS011 | 0.0004941 | 0.0004995 | 0.0005049 | 0.0005103 | 0.0005157 | 0.000518 | 0.00052029 | 0.00052259 | 0.00052488 | 0.00052718 | 0.00052947 | 0.00053177 | 0.00053406 | 0.00053636 | 0.00053865 | 0.00054095 | 0.00054324 | 0.00054554 | 0.00054783 | 0.00055013
| BAS011-85028212 | BAS011 | 0.15036 | 0.15129 | 0.15222 | 0.15315 | 0.15409 | 0.15408 | 0.15407 | 0.15406 | 0.15405 | 0.15405 | 0.15404 | 0.15403 | 0.15402 | 0.15402 | 0.15401 | 0.154 | 0.15399 | 0.15399 | 0.15398 | 0.15397
| BAS011-85028323 | BAS011 | 1.8359e-05 | 1.8489e-05 | 1.8619e-05 | 1.875e-05 | 1.888e-05 | 1.9048e-05 | 1.9216e-05 | 1.9384e-05 | 1.9552e-05 | 1.972e-05 | 1.9888e-05 | 2.0056e-05 | 2.0224e-05 | 2.0392e-05 | 2.056e-05 | 2.0728e-05 | 2.0896e-05 | 2.1064e-05 | 2.1232e-05 | 2.14e-05
| BAS011-85029671 | BAS011 | 0.035171 | 0.03543 | 0.035688 | 0.035946 | 0.036205 | 0.03633 | 0.036455 | 0.03658 | 0.036705 | 0.036831 | 0.036956 | 0.037081 | 0.037206 | 0.037332 | 0.037457 | 0.037582 | 0.037707 | 0.037833 | 0.037958 | 0.038083
| BAS011-85030316 | BAS011 | 0.017843 | 0.017976 | 0.018109 | 0.018243 | 0.018376 | 0.018431 | 0.018486 | 0.018541 | 0.018596 | 0.018652 | 0.018707 | 0.018762 | 0.018817 | 0.018872 | 0.018927 | 0.018982 | 0.019037 | 0.019093 | 0.019148 | 0.019203
| BAS011-85421065 | BAS011 | 0.08516 | 0.08565 | 0.08614 | 0.08663 | 0.08712 | 0.087211 | 0.087302 | 0.087393 | 0.087484 | 0.087576 | 0.087667 | 0.087758 | 0.087849 | 0.08794 | 0.088031 | 0.088122 | 0.088213 | 0.088305 | 0.088396 | 0.088487
| BAS011-85421256 | BAS011 | 0.036771 | 0.037058 | 0.037345 | 0.037632 | 0.037919 | 0.03804 | 0.038161 | 0.038281 | 0.038402 | 0.038523 | 0.038643 | 0.038764 | 0.038885 | 0.039006 | 0.039126 | 0.039247 | 0.039368 | 0.039489 | 0.039609 | 0.03973
| BAS011-85724039 | BAS011 | 0.41901 | 0.42151 | 0.424 | 0.4265 | 0.42899 | 0.42996 | 0.43092 | 0.43188 | 0.43284 | 0.43381 | 0.43477 | 0.43573 | 0.43669 | 0.43765 | 0.43862 | 0.43958 | 0.44054 | 0.4415 | 0.44246 | 0.44343
| BAS011-89021568 | BAS011 | 0.11226 | 0.11301 | 0.11376 | 0.11452 | 0.11527 | 0.11547 | 0.11566 | 0.11586 | 0.11606 | 0.11626 | 0.11645 | 0.11665 | 0.11685 | 0.11704 | 0.11724 | 0.11744 | 0.11764 | 0.11783 | 0.11803 | 0.11823
| BAS011-99529198 | BAS011 | 0.0085738 | 0.0086544 | 0.008735 | 0.0088156 | 0.0088962 | 0.0089452 | 0.0089942 | 0.0090431 | 0.0090921 | 0.0091411 | 0.00919 | 0.009239 | 0.009288 | 0.0093369 | 0.0093859 | 0.0094349 | 0.0094839 | 0.0095328 | 0.0095818 | 0.0096308
| BAS012-15414133 | BAS012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS012-187042122 | BAS012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS013-15414170 | BAS013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS014-15414207 | BAS014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS014-74639994 | BAS014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS021-15414366 | BAS021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-130430211 | BAS022 | 0.086221 | 0.086799 | 0.087377 | 0.087954 | 0.088532 | 0.088642 | 0.088753 | 0.088863 | 0.088974 | 0.089084 | 0.089195 | 0.089306 | 0.089416 | 0.089527 | 0.089637 | 0.089748 | 0.089858 | 0.089969 | 0.090079 | 0.09019
| BAS022-131562724 | BAS022 | 37.8166 | 38.0083 | 38.2 | 38.3917 | 38.5834 | 38.763 | 38.9426 | 39.1223 | 39.3019 | 39.4815 | 39.6611 | 39.8407 | 40.0203 | 40.1999 | 40.3795 | 40.5591 | 40.7387 | 40.9183 | 41.0979 | 41.2775
| BAS022-139345117 | BAS022 | 0.48903 | 0.49177 | 0.4945 | 0.49724 | 0.49997 | 0.49945 | 0.49893 | 0.4984 | 0.49788 | 0.49735 | 0.49683 | 0.49631 | 0.49578 | 0.49526 | 0.49473 | 0.49421 | 0.49369 | 0.49316 | 0.49264 | 0.49211
| BAS022-139345255 | BAS022 | 0.39214 | 0.39267 | 0.39319 | 0.39372 | 0.39424 | 0.39344 | 0.39263 | 0.39182 | 0.39102 | 0.39021 | 0.38941 | 0.3886 | 0.38779 | 0.38699 | 0.38618 | 0.38538 | 0.38457 | 0.38376 | 0.38296 | 0.38215
| BAS022-139345594 | BAS022 | 0.2343 | 0.2357 | 0.2371 | 0.2385 | 0.23989 | 0.24055 | 0.24121 | 0.24187 | 0.24253 | 0.24318 | 0.24384 | 0.2445 | 0.24516 | 0.24582 | 0.24647 | 0.24713 | 0.24779 | 0.24845 | 0.24911 | 0.24976
| BAS022-142437045 | BAS022 | 1.2552 | 1.2621 | 1.2689 | 1.2758 | 1.2826 | 1.283 | 1.2833 | 1.2836 | 1.2839 | 1.2842 | 1.2846 | 1.2849 | 1.2852 | 1.2855 | 1.2858 | 1.2862 | 1.2865 | 1.2868 | 1.2871 | 1.2875
| BAS022-142437276 | BAS022 | 0.032508 | 0.032693 | 0.032877 | 0.033062 | 0.033246 | 0.033257 | 0.033267 | 0.033277 | 0.033288 | 0.033298 | 0.033308 | 0.033318 | 0.033329 | 0.033339 | 0.033349 | 0.03336 | 0.03337 | 0.03338 | 0.033391 | 0.033401
| BAS022-142437414 | BAS022 | 0.34457 | 0.34641 | 0.34825 | 0.35009 | 0.35193 | 0.35219 | 0.35246 | 0.35272 | 0.35298 | 0.35325 | 0.35351 | 0.35377 | 0.35404 | 0.3543 | 0.35456 | 0.35483 | 0.35509 | 0.35535 | 0.35562 | 0.35588
| BAS022-144337084 | BAS022 | 0.2427 | 0.244 | 0.2453 | 0.2466 | 0.2479 | 0.24882 | 0.24975 | 0.25067 | 0.2516 | 0.25252 | 0.25344 | 0.25437 | 0.25529 | 0.25621 | 0.25714 | 0.25806 | 0.25899 | 0.25991 | 0.26083 | 0.26176
| BAS022-15416117 | BAS022 | 58.1743 | 58.4589 | 58.7436 | 59.0283 | 59.3129 | 59.509 | 59.7051 | 59.9012 | 60.0972 | 60.2933 | 60.4894 | 60.6855 | 60.8816 | 61.0776 | 61.2737 | 61.4698 | 61.6659 | 61.8619 | 62.058 | 62.2541
| BAS022-155392787 | BAS022 | 0.16968 | 0.17026 | 0.17083 | 0.17141 | 0.17199 | 0.17238 | 0.17278 | 0.17318 | 0.17358 | 0.17398 | 0.17438 | 0.17477 | 0.17517 | 0.17557 | 0.17597 | 0.17637 | 0.17676 | 0.17716 | 0.17756 | 0.17796
| BAS022-155392904 | BAS022 | 0.041878 | 0.042137 | 0.042397 | 0.042656 | 0.042915 | 0.043049 | 0.043183 | 0.043317 | 0.043451 | 0.043585 | 0.043719 | 0.043853 | 0.043987 | 0.044121 | 0.044255 | 0.044389 | 0.044523 | 0.044657 | 0.044791 | 0.044925
| BAS022-155393076 | BAS022 | 0.14938 | 0.15047 | 0.15156 | 0.15264 | 0.15373 | 0.1542 | 0.15467 | 0.15514 | 0.15561 | 0.15608 | 0.15655 | 0.15702 | 0.15749 | 0.15795 | 0.15842 | 0.15889 | 0.15936 | 0.15983 | 0.1603 | 0.16077
| BAS022-163916141 | BAS022 | 0.22234 | 0.22369 | 0.22504 | 0.22639 | 0.22773 | 0.22832 | 0.22891 | 0.2295 | 0.23009 | 0.23068 | 0.23127 | 0.23186 | 0.23245 | 0.23304 | 0.23363 | 0.23422 | 0.23481 | 0.2354 | 0.23599 | 0.23658
| BAS022-164206998 | BAS022 | 25.3354 | 25.4455 | 25.5556 | 25.6657 | 25.7758 | 25.8228 | 25.8698 | 25.9168 | 25.9638 | 26.0108 | 26.0578 | 26.1048 | 26.1518 | 26.1988 | 26.2458 | 26.2928 | 26.3398 | 26.3868 | 26.4338 | 26.4808
| BAS022-171331284 | BAS022 | 0.39051 | 0.39243 | 0.39434 | 0.39626 | 0.39818 | 0.39914 | 0.40009 | 0.40105 | 0.402 | 0.40296 | 0.40392 | 0.40487 | 0.40583 | 0.40679 | 0.40774 | 0.4087 | 0.40966 | 0.41061 | 0.41157 | 0.41253
| BAS022-172349144 | BAS022 | 0.00011409 | 0.00011475 | 0.0001154 | 0.00011605 | 0.0001167 | 0.00011731 | 0.00011793 | 0.00011855 | 0.00011916 | 0.00011978 | 0.00012039 | 0.00012101 | 0.00012162 | 0.00012224 | 0.00012285 | 0.00012347 | 0.00012408 | 0.0001247 | 0.00012531 | 0.00012593
| BAS022-193385657 | BAS022 | 8.908 | 8.9362 | 8.9643 | 8.9925 | 9.0207 | 9.0294 | 9.038 | 9.0467 | 9.0554 | 9.064 | 9.0727 | 9.0814 | 9.09 | 9.0987 | 9.1074 | 9.1161 | 9.1247 | 9.1334 | 9.1421 | 9.1507
| BAS022-193385775 | BAS022 | 250.1655 | 251.3558 | 252.546 | 253.7362 | 254.9265 | 255.4082 | 255.8899 | 256.3716 | 256.8533 | 257.335 | 257.8167 | 258.2984 | 258.7801 | 259.2618 | 259.7436 | 260.2253 | 260.707 | 261.1887 | 261.6704 | 262.1521
| BAS022-24598930 | BAS022 | 10.3979 | 10.4529 | 10.5078 | 10.5628 | 10.6177 | 10.645 | 10.6723 | 10.6996 | 10.7269 | 10.7542 | 10.7815 | 10.8088 | 10.8361 | 10.8634 | 10.8908 | 10.9181 | 10.9454 | 10.9727 | 11 | 11.0273
| BAS022-72697775 | BAS022 | 0.028052 | 0.028221 | 0.028391 | 0.02856 | 0.02873 | 0.028774 | 0.028817 | 0.028861 | 0.028905 | 0.028948 | 0.028992 | 0.029036 | 0.029079 | 0.029123 | 0.029167 | 0.029211 | 0.029254 | 0.029298 | 0.029342 | 0.029385
| BAS022-72698236 | BAS022 | 0.062501 | 0.062874 | 0.063248 | 0.063621 | 0.063994 | 0.064204 | 0.064414 | 0.064624 | 0.064834 | 0.065044 | 0.065255 | 0.065465 | 0.065675 | 0.065885 | 0.066095 | 0.066305 | 0.066515 | 0.066725 | 0.066935 | 0.067145
| BAS022-72698508 | BAS022 | 0.035106 | 0.035283 | 0.035461 | 0.035638 | 0.035816 | 0.035898 | 0.03598 | 0.036062 | 0.036144 | 0.036226 | 0.036308 | 0.03639 | 0.036472 | 0.036554 | 0.036636 | 0.036718 | 0.0368 | 0.036882 | 0.036964 | 0.037046
| BAS022-88324187 | BAS022 | 0.26623 | 0.2677 | 0.26917 | 0.27064 | 0.27211 | 0.273 | 0.27389 | 0.27478 | 0.27567 | 0.27656 | 0.27745 | 0.27834 | 0.27923 | 0.28013 | 0.28102 | 0.28191 | 0.2828 | 0.28369 | 0.28458 | 0.28547
| BAS022-88324452 | BAS022 | 0.28175 | 0.2835 | 0.28525 | 0.287 | 0.28875 | 0.28935 | 0.28994 | 0.29054 | 0.29113 | 0.29172 | 0.29232 | 0.29291 | 0.2935 | 0.2941 | 0.29469 | 0.29528 | 0.29588 | 0.29647 | 0.29706 | 0.29766
| BAS023-141849160 | BAS023 | 0.33121 | 0.33299 | 0.33477 | 0.33656 | 0.33834 | 0.33899 | 0.33964 | 0.34028 | 0.34093 | 0.34158 | 0.34223 | 0.34287 | 0.34352 | 0.34417 | 0.34482 | 0.34546 | 0.34611 | 0.34676 | 0.34741 | 0.34805
| BAS023-141849179 | BAS023 | 0.041025 | 0.041309 | 0.041592 | 0.041876 | 0.04216 | 0.042352 | 0.042545 | 0.042738 | 0.04293 | 0.043123 | 0.043316 | 0.043508 | 0.043701 | 0.043894 | 0.044087 | 0.044279 | 0.044472 | 0.044665 | 0.044857 | 0.04505
| BAS023-15416141 | BAS023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS023-155325011 | BAS023 | 0.41844 | 0.42089 | 0.42333 | 0.42577 | 0.42822 | 0.42914 | 0.43006 | 0.43099 | 0.43191 | 0.43283 | 0.43376 | 0.43468 | 0.43561 | 0.43653 | 0.43745 | 0.43838 | 0.4393 | 0.44022 | 0.44115 | 0.44207
| BAS023-24612761 | BAS023 | 83.3881 | 83.7491 | 84.1101 | 84.4711 | 84.8321 | 84.9517 | 85.0713 | 85.1909 | 85.3105 | 85.4301 | 85.5497 | 85.6693 | 85.7889 | 85.9085 | 86.0281 | 86.1477 | 86.2673 | 86.3869 | 86.5065 | 86.6261
| BAS023-41628847 | BAS023 | 10.5007 | 10.5658 | 10.6308 | 10.6958 | 10.7608 | 10.7952 | 10.8297 | 10.8641 | 10.8985 | 10.9329 | 10.9673 | 11.0017 | 11.0362 | 11.0706 | 11.105 | 11.1394 | 11.1738 | 11.2083 | 11.2427 | 11.2771
| BAS024-15416191 | BAS024 | 1.8323 | 1.8451 | 1.858 | 1.8708 | 1.8837 | 1.8942 | 1.9048 | 1.9153 | 1.9259 | 1.9365 | 1.947 | 1.9576 | 1.9681 | 1.9787 | 1.9892 | 1.9998 | 2.0104 | 2.0209 | 2.0315 | 2.042
| BAS032-155216556 | BAS032 | 118.5393 | 118.9448 | 119.3502 | 119.7557 | 120.1612 | 120.2915 | 120.4218 | 120.5521 | 120.6823 | 120.8126 | 120.9429 | 121.0732 | 121.2035 | 121.3338 | 121.4641 | 121.5944 | 121.7247 | 121.855 | 121.9853 | 122.1156
| BAS032-177751012 | BAS032 | 55.9949 | 56.1603 | 56.3258 | 56.4912 | 56.6566 | 56.7307 | 56.8048 | 56.8789 | 56.953 | 57.027 | 57.1011 | 57.1752 | 57.2493 | 57.3234 | 57.3975 | 57.4716 | 57.5457 | 57.6198 | 57.6939 | 57.768
| BAS033-139662053 | BAS033 | 1.0822 | 1.0899 | 1.0975 | 1.1052 | 1.1128 | 1.1105 | 1.1082 | 1.1059 | 1.1036 | 1.1013 | 1.099 | 1.0967 | 1.0944 | 1.0921 | 1.0898 | 1.0875 | 1.0851 | 1.0828 | 1.0805 | 1.0782
| BAS033-139662229 | BAS033 | 1.6162 | 1.6267 | 1.6373 | 1.6479 | 1.6585 | 1.6588 | 1.6591 | 1.6594 | 1.6597 | 1.66 | 1.6603 | 1.6606 | 1.6609 | 1.6612 | 1.6615 | 1.6618 | 1.6621 | 1.6624 | 1.6626 | 1.6629
| BAS033-140150122 | BAS033 | 0.099675 | 0.10043 | 0.10118 | 0.10193 | 0.10268 | 0.10246 | 0.10224 | 0.10202 | 0.10181 | 0.10159 | 0.10137 | 0.10115 | 0.10093 | 0.10072 | 0.1005 | 0.10028 | 0.10006 | 0.099845 | 0.099627 | 0.099409
| BAS033-142953276 | BAS033 | 0.69213 | 0.6951 | 0.69806 | 0.70103 | 0.70399 | 0.70685 | 0.70971 | 0.71257 | 0.71543 | 0.71829 | 0.72116 | 0.72402 | 0.72688 | 0.72974 | 0.7326 | 0.73546 | 0.73832 | 0.74118 | 0.74404 | 0.74691
| BAS033-155164312 | BAS033 | 0.0021946 | 0.0022147 | 0.0022349 | 0.002255 | 0.0022752 | 0.0022738 | 0.0022723 | 0.0022709 | 0.0022694 | 0.002268 | 0.0022666 | 0.0022651 | 0.0022637 | 0.0022622 | 0.0022608 | 0.0022594 | 0.0022579 | 0.0022565 | 0.002255 | 0.0022536
| BAS033-155176923 | BAS033 | 0.7472 | 0.75266 | 0.75812 | 0.76357 | 0.76903 | 0.76766 | 0.76629 | 0.76493 | 0.76356 | 0.76219 | 0.76082 | 0.75945 | 0.75808 | 0.75671 | 0.75535 | 0.75398 | 0.75261 | 0.75124 | 0.74987 | 0.7485
| BAS033-155190238 | BAS033 | 0.071439 | 0.071954 | 0.072469 | 0.072983 | 0.073498 | 0.073135 | 0.072771 | 0.072408 | 0.072044 | 0.071681 | 0.071317 | 0.070954 | 0.07059 | 0.070227 | 0.069863 | 0.0695 | 0.069137 | 0.068773 | 0.06841 | 0.068046
| BAS033-155190444 | BAS033 | 0.010934 | 0.011031 | 0.011127 | 0.011223 | 0.011319 | 0.01131 | 0.0113 | 0.01129 | 0.011281 | 0.011271 | 0.011262 | 0.011252 | 0.011242 | 0.011233 | 0.011223 | 0.011214 | 0.011204 | 0.011194 | 0.011185 | 0.011175
| BAS033-155190566 | BAS033 | 0.021402 | 0.021601 | 0.021801 | 0.022001 | 0.0222 | 0.022142 | 0.022083 | 0.022024 | 0.021965 | 0.021906 | 0.021847 | 0.021788 | 0.021729 | 0.021671 | 0.021612 | 0.021553 | 0.021494 | 0.021435 | 0.021376 | 0.021317
| BAS033-155190689 | BAS033 | 0.0016421 | 0.0016556 | 0.001669 | 0.0016824 | 0.0016959 | 0.0016939 | 0.001692 | 0.0016901 | 0.0016881 | 0.0016862 | 0.0016843 | 0.0016823 | 0.0016804 | 0.0016785 | 0.0016765 | 0.0016746 | 0.0016727 | 0.0016707 | 0.0016688 | 0.0016669
| BAS033-155190801 | BAS033 | 0.00017854 | 0.00018026 | 0.00018197 | 0.00018369 | 0.0001854 | 0.00018501 | 0.00018462 | 0.00018423 | 0.00018384 | 0.00018345 | 0.00018306 | 0.00018267 | 0.00018228 | 0.00018189 | 0.0001815 | 0.00018111 | 0.00018072 | 0.00018033 | 0.00017994 | 0.00017955
| BAS033-155250207 | BAS033 | 0.054334 | 0.054787 | 0.05524 | 0.055693 | 0.056145 | 0.056028 | 0.05591 | 0.055793 | 0.055675 | 0.055558 | 0.05544 | 0.055323 | 0.055205 | 0.055087 | 0.05497 | 0.054852 | 0.054735 | 0.054617 | 0.0545 | 0.054382
| BAS033-155250324 | BAS033 | 4.2545e-05 | 4.2979e-05 | 4.3413e-05 | 4.3846e-05 | 4.428e-05 | 4.4259e-05 | 4.4238e-05 | 4.4217e-05 | 4.4196e-05 | 4.4175e-05 | 4.4154e-05 | 4.4133e-05 | 4.4112e-05 | 4.4091e-05 | 4.407e-05 | 4.4049e-05 | 4.4028e-05 | 4.4007e-05 | 4.3986e-05 | 4.3965e-05
| BAS033-177750890 | BAS033 | 39.7469 | 39.9269 | 40.1068 | 40.2868 | 40.4668 | 40.5414 | 40.6161 | 40.6907 | 40.7654 | 40.8401 | 40.9147 | 40.9894 | 41.064 | 41.1387 | 41.2134 | 41.288 | 41.3627 | 41.4373 | 41.512 | 41.5867
| BAS033-193428051 | BAS033 | 332.2525 | 333.8779 | 335.5033 | 337.1287 | 338.7541 | 339.1172 | 339.4802 | 339.8432 | 340.2062 | 340.5693 | 340.9323 | 341.2953 | 341.6583 | 342.0213 | 342.3844 | 342.7474 | 343.1104 | 343.4734 | 343.8364 | 344.1995
| BAS033-193428083 | BAS033 | 2.7082 | 2.7279 | 2.7477 | 2.7675 | 2.7873 | 2.7784 | 2.7696 | 2.7608 | 2.7519 | 2.7431 | 2.7342 | 2.7254 | 2.7165 | 2.7077 | 2.6989 | 2.69 | 2.6812 | 2.6723 | 2.6635 | 2.6546
| BAS033-193428108 | BAS033 | 5.8177 | 5.8651 | 5.9125 | 5.9599 | 6.0073 | 6.0015 | 5.9957 | 5.9898 | 5.984 | 5.9782 | 5.9724 | 5.9665 | 5.9607 | 5.9549 | 5.9491 | 5.9433 | 5.9374 | 5.9316 | 5.9258 | 5.92
| BAS033-193428622 | BAS033 | 197.1821 | 198.1483 | 199.1144 | 200.0806 | 201.0467 | 201.3966 | 201.7465 | 202.0964 | 202.4463 | 202.7962 | 203.1461 | 203.4961 | 203.846 | 204.1959 | 204.5458 | 204.8957 | 205.2456 | 205.5955 | 205.9454 | 206.2953
| BAS033-78747898 | BAS033 | 0.00092916 | 0.00093452 | 0.00093988 | 0.00094524 | 0.0009506 | 0.00095564 | 0.00096068 | 0.00096572 | 0.00097076 | 0.0009758 | 0.00098084 | 0.00098588 | 0.00099092 | 0.00099596 | 0.001001 | 0.001006 | 0.0010111 | 0.0010161 | 0.0010212 | 0.0010262
| BAS033-78747960 | BAS033 | 0.0030851 | 0.0031008 | 0.0031165 | 0.0031323 | 0.003148 | 0.0031585 | 0.003169 | 0.0031796 | 0.0031901 | 0.0032007 | 0.0032112 | 0.0032218 | 0.0032323 | 0.0032429 | 0.0032534 | 0.0032639 | 0.0032745 | 0.003285 | 0.0032956 | 0.0033061
| BAS033-78748025 | BAS033 | 1.4289 | 1.4349 | 1.4408 | 1.4468 | 1.4528 | 1.4552 | 1.4576 | 1.46 | 1.4624 | 1.4648 | 1.4672 | 1.4696 | 1.472 | 1.4744 | 1.4768 | 1.4792 | 1.4816 | 1.484 | 1.4864 | 1.4888
| BAS033-78748089 | BAS033 | 0.16494 | 0.16577 | 0.16659 | 0.16742 | 0.16825 | 0.16867 | 0.16908 | 0.1695 | 0.16991 | 0.17033 | 0.17075 | 0.17116 | 0.17158 | 0.17199 | 0.17241 | 0.17282 | 0.17324 | 0.17366 | 0.17407 | 0.17449
| BAS033-95730010 | BAS033 | 0.0071446 | 0.0071964 | 0.0072483 | 0.0073001 | 0.007352 | 0.0073274 | 0.0073027 | 0.0072781 | 0.0072534 | 0.0072288 | 0.0072041 | 0.0071795 | 0.0071549 | 0.0071302 | 0.0071056 | 0.0070809 | 0.0070563 | 0.0070317 | 0.007007 | 0.0069824
| BAS033-96330036 | BAS033 | 0.34419 | 0.34694 | 0.3497 | 0.35245 | 0.3552 | 0.35444 | 0.35368 | 0.35292 | 0.35217 | 0.35141 | 0.35065 | 0.34989 | 0.34913 | 0.34837 | 0.34761 | 0.34686 | 0.3461 | 0.34534 | 0.34458 | 0.34382
| BAS034-15416250 | BAS034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS034-199849971 | BAS034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BBD013-15437974 | BBD013 | 1.7781 | 1.7946 | 1.811 | 1.8275 | 1.8439 | 1.8415 | 1.839 | 1.8365 | 1.8341 | 1.8316 | 1.8292 | 1.8267 | 1.8242 | 1.8218 | 1.8193 | 1.8169 | 1.8144 | 1.8119 | 1.8095 | 1.807
| BBD013-24614080 | BBD013 | 0.64313 | 0.6481 | 0.65307 | 0.65804 | 0.66302 | 0.66289 | 0.66277 | 0.66265 | 0.66252 | 0.6624 | 0.66228 | 0.66215 | 0.66203 | 0.6619 | 0.66178 | 0.66166 | 0.66153 | 0.66141 | 0.66129 | 0.66116
| BBD014-15437952 | BBD014 | 0.1366 | 0.13793 | 0.13925 | 0.14057 | 0.14189 | 0.14172 | 0.14155 | 0.14138 | 0.14121 | 0.14104 | 0.14087 | 0.14069 | 0.14052 | 0.14035 | 0.14018 | 0.14001 | 0.13984 | 0.13967 | 0.13949 | 0.13932
| BBD014-160682204 | BBD014 | 0.0014089 | 0.0014093 | 0.0014096 | 0.00141 | 0.0014103 | 0.0014101 | 0.0014098 | 0.0014095 | 0.0014092 | 0.0014089 | 0.0014086 | 0.0014084 | 0.0014081 | 0.0014078 | 0.0014075 | 0.0014072 | 0.001407 | 0.0014067 | 0.0014064 | 0.0014061
| BBD014-162435599 | BBD014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BBD014-96325732 | BBD014 | 0.24633 | 0.24896 | 0.25159 | 0.25422 | 0.25685 | 0.25585 | 0.25484 | 0.25384 | 0.25283 | 0.25183 | 0.25082 | 0.24982 | 0.24881 | 0.24781 | 0.2468 | 0.2458 | 0.24479 | 0.24379 | 0.24278 | 0.24178
| BBD014-96325958 | BBD014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BBD014-97325263 | BBD014 | 1.7128 | 1.7284 | 1.7441 | 1.7598 | 1.7755 | 1.7727 | 1.7698 | 1.7669 | 1.764 | 1.7612 | 1.7583 | 1.7554 | 1.7525 | 1.7497 | 1.7468 | 1.7439 | 1.741 | 1.7382 | 1.7353 | 1.7324
| BBD021-15437930 | BBD021 | 0.0015363 | 0.0015511 | 0.001566 | 0.0015809 | 0.0015958 | 0.0015938 | 0.0015919 | 0.00159 | 0.0015881 | 0.0015862 | 0.0015842 | 0.0015823 | 0.0015804 | 0.0015785 | 0.0015765 | 0.0015746 | 0.0015727 | 0.0015708 | 0.0015688 | 0.0015669
| BBD021-24611491 | BBD021 | 1.2433 | 1.2548 | 1.2663 | 1.2777 | 1.2892 | 1.2869 | 1.2845 | 1.2822 | 1.2798 | 1.2775 | 1.2752 | 1.2728 | 1.2705 | 1.2681 | 1.2658 | 1.2635 | 1.2611 | 1.2588 | 1.2564 | 1.2541
| BBD021-24613487 | BBD021 | 7.0207 | 7.0782 | 7.1357 | 7.1932 | 7.2508 | 7.2353 | 7.2198 | 7.2043 | 7.1888 | 7.1733 | 7.1579 | 7.1424 | 7.1269 | 7.1114 | 7.0959 | 7.0804 | 7.065 | 7.0495 | 7.034 | 7.0185
| BBD021-40480035 | BBD021 | 1.6453 | 1.6582 | 1.6712 | 1.6841 | 1.6971 | 1.6933 | 1.6895 | 1.6857 | 1.6819 | 1.6781 | 1.6743 | 1.6705 | 1.6667 | 1.6629 | 1.6591 | 1.6553 | 1.6515 | 1.6478 | 1.644 | 1.6402
| BBD022-15437908 | BBD022 | 0.049911 | 0.050383 | 0.050855 | 0.051327 | 0.051799 | 0.051682 | 0.051565 | 0.051447 | 0.05133 | 0.051213 | 0.051096 | 0.050979 | 0.050861 | 0.050744 | 0.050627 | 0.05051 | 0.050393 | 0.050275 | 0.050158 | 0.050041
| BET001-143534818 | BET001 | 0.19697 | 0.19826 | 0.19956 | 0.20085 | 0.20215 | 0.20245 | 0.20275 | 0.20306 | 0.20336 | 0.20366 | 0.20396 | 0.20427 | 0.20457 | 0.20487 | 0.20517 | 0.20548 | 0.20578 | 0.20608 | 0.20638 | 0.20669
| BET001-15424260 | BET001 | 134.5314 | 135.441 | 136.3505 | 137.2601 | 138.1697 | 138.5685 | 138.9673 | 139.3662 | 139.765 | 140.1639 | 140.5627 | 140.9615 | 141.3604 | 141.7592 | 142.1581 | 142.5569 | 142.9557 | 143.3546 | 143.7534 | 144.1523
| BET001-163510183 | BET001 | 4.9007 | 4.9311 | 4.9615 | 4.9919 | 5.0222 | 5.0353 | 5.0483 | 5.0613 | 5.0743 | 5.0874 | 5.1004 | 5.1134 | 5.1264 | 5.1395 | 5.1525 | 5.1655 | 5.1785 | 5.1916 | 5.2046 | 5.2176
| BET001-163510254 | BET001 | 6.8985 | 6.9502 | 7.0019 | 7.0536 | 7.1053 | 7.1293 | 7.1532 | 7.1771 | 7.201 | 7.2249 | 7.2488 | 7.2727 | 7.2967 | 7.3206 | 7.3445 | 7.3684 | 7.3923 | 7.4162 | 7.4401 | 7.4641
| BET001-163979859 | BET001 | 0.37104 | 0.37386 | 0.37669 | 0.37951 | 0.38234 | 0.38333 | 0.38432 | 0.38531 | 0.3863 | 0.3873 | 0.38829 | 0.38928 | 0.39027 | 0.39126 | 0.39225 | 0.39325 | 0.39424 | 0.39523 | 0.39622 | 0.39721
| BET002-147836095 | BET002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET002-15424310 | BET002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET003-15424094 | BET003 | 0.76827 | 0.7723 | 0.77634 | 0.78037 | 0.78441 | 0.78574 | 0.78708 | 0.78841 | 0.78974 | 0.79108 | 0.79241 | 0.79374 | 0.79508 | 0.79641 | 0.79774 | 0.79908 | 0.80041 | 0.80174 | 0.80308 | 0.80441
| BET004-112026510 | BET004 | 0.61176 | 0.6161 | 0.62043 | 0.62477 | 0.62911 | 0.63094 | 0.63276 | 0.63459 | 0.63642 | 0.63824 | 0.64007 | 0.6419 | 0.64373 | 0.64555 | 0.64738 | 0.64921 | 0.65103 | 0.65286 | 0.65469 | 0.65651
| BET004-15424334 | BET004 | 65.9867 | 66.3652 | 66.7436 | 67.1221 | 67.5006 | 67.8313 | 68.162 | 68.4927 | 68.8234 | 69.1541 | 69.4848 | 69.8156 | 70.1463 | 70.477 | 70.8077 | 71.1384 | 71.4691 | 71.7998 | 72.1305 | 72.4612
| BET004-163616866 | BET004 | 0.35139 | 0.3539 | 0.35642 | 0.35894 | 0.36145 | 0.36232 | 0.3632 | 0.36407 | 0.36494 | 0.36581 | 0.36668 | 0.36755 | 0.36843 | 0.3693 | 0.37017 | 0.37104 | 0.37191 | 0.37278 | 0.37366 | 0.37453
| BET004-164487583 | BET004 | 0.035575 | 0.035782 | 0.035989 | 0.036196 | 0.036403 | 0.036471 | 0.036539 | 0.036607 | 0.036675 | 0.036743 | 0.036811 | 0.036879 | 0.036947 | 0.037015 | 0.037082 | 0.03715 | 0.037218 | 0.037286 | 0.037354 | 0.037422
| BET004-164487758 | BET004 | 0.046905 | 0.047242 | 0.047579 | 0.047916 | 0.048253 | 0.04837 | 0.048487 | 0.048603 | 0.04872 | 0.048837 | 0.048954 | 0.049071 | 0.049188 | 0.049305 | 0.049422 | 0.049539 | 0.049656 | 0.049773 | 0.04989 | 0.050007
| BET004-24611449 | BET004 | 47.3211 | 47.5879 | 47.8548 | 48.1216 | 48.3885 | 48.4588 | 48.529 | 48.5993 | 48.6695 | 48.7398 | 48.81 | 48.8803 | 48.9505 | 49.0208 | 49.091 | 49.1613 | 49.2315 | 49.3018 | 49.372 | 49.4423
| BET004-72499638 | BET004 | 0.88516 | 0.89069 | 0.89622 | 0.90176 | 0.90729 | 0.90856 | 0.90983 | 0.9111 | 0.91237 | 0.91364 | 0.91491 | 0.91618 | 0.91745 | 0.91872 | 0.91999 | 0.92126 | 0.92253 | 0.9238 | 0.92507 | 0.92634
| BET004-72499720 | BET004 | 0.13681 | 0.1377 | 0.13858 | 0.13947 | 0.14036 | 0.14071 | 0.14107 | 0.14142 | 0.14177 | 0.14212 | 0.14248 | 0.14283 | 0.14318 | 0.14353 | 0.14389 | 0.14424 | 0.14459 | 0.14494 | 0.1453 | 0.14565
| BET004-72499790 | BET004 | 0.10551 | 0.10637 | 0.10723 | 0.10808 | 0.10894 | 0.10931 | 0.10968 | 0.11005 | 0.11041 | 0.11078 | 0.11115 | 0.11152 | 0.11189 | 0.11226 | 0.11263 | 0.113 | 0.11336 | 0.11373 | 0.1141 | 0.11447
| BET004-72500100 | BET004 | 0.48857 | 0.49138 | 0.49418 | 0.49698 | 0.49978 | 0.50089 | 0.502 | 0.50311 | 0.50421 | 0.50532 | 0.50643 | 0.50754 | 0.50865 | 0.50975 | 0.51086 | 0.51197 | 0.51308 | 0.51419 | 0.5153 | 0.5164
| BET004-72500230 | BET004 | 0.10541 | 0.10612 | 0.10684 | 0.10756 | 0.10828 | 0.10845 | 0.10863 | 0.10881 | 0.10899 | 0.10916 | 0.10934 | 0.10952 | 0.1097 | 0.10987 | 0.11005 | 0.11023 | 0.11041 | 0.11058 | 0.11076 | 0.11094
| BET004-72500251 | BET004 | 0.58889 | 0.59363 | 0.59836 | 0.6031 | 0.60783 | 0.60951 | 0.61119 | 0.61287 | 0.61455 | 0.61623 | 0.6179 | 0.61958 | 0.62126 | 0.62294 | 0.62462 | 0.6263 | 0.62798 | 0.62966 | 0.63133 | 0.63301
| BET004-72500469 | BET004 | 0.40919 | 0.4109 | 0.41261 | 0.41432 | 0.41602 | 0.41655 | 0.41707 | 0.41759 | 0.41812 | 0.41864 | 0.41916 | 0.41969 | 0.42021 | 0.42074 | 0.42126 | 0.42178 | 0.42231 | 0.42283 | 0.42335 | 0.42388
| BET005-110828671 | BET005 | 0.85224 | 0.85793 | 0.86362 | 0.86931 | 0.87501 | 0.8767 | 0.87839 | 0.88009 | 0.88178 | 0.88348 | 0.88517 | 0.88686 | 0.88856 | 0.89025 | 0.89195 | 0.89364 | 0.89534 | 0.89703 | 0.89872 | 0.90042
| BET005-117327746 | BET005 | 0.063892 | 0.064441 | 0.06499 | 0.065539 | 0.066087 | 0.066418 | 0.066748 | 0.067079 | 0.067409 | 0.067739 | 0.06807 | 0.0684 | 0.06873 | 0.069061 | 0.069391 | 0.069722 | 0.070052 | 0.070382 | 0.070713 | 0.071043
| BET005-142631975 | BET005 | 0.0045161 | 0.0045538 | 0.0045916 | 0.0046293 | 0.004667 | 0.0046861 | 0.0047052 | 0.0047242 | 0.0047433 | 0.0047624 | 0.0047815 | 0.0048005 | 0.0048196 | 0.0048387 | 0.0048577 | 0.0048768 | 0.0048959 | 0.0049149 | 0.004934 | 0.0049531
| BET005-142632215 | BET005 | 0.11939 | 0.12032 | 0.12125 | 0.12219 | 0.12312 | 0.12353 | 0.12394 | 0.12434 | 0.12475 | 0.12516 | 0.12557 | 0.12598 | 0.12639 | 0.12679 | 0.1272 | 0.12761 | 0.12802 | 0.12843 | 0.12883 | 0.12924
| BET005-143035133 | BET005 | 0.21801 | 0.21966 | 0.22131 | 0.22297 | 0.22462 | 0.22509 | 0.22555 | 0.22602 | 0.22649 | 0.22695 | 0.22742 | 0.22788 | 0.22835 | 0.22882 | 0.22928 | 0.22975 | 0.23022 | 0.23068 | 0.23115 | 0.23162
| BET005-143035406 | BET005 | 0.54983 | 0.55342 | 0.55701 | 0.5606 | 0.56418 | 0.56525 | 0.56631 | 0.56737 | 0.56844 | 0.5695 | 0.57056 | 0.57162 | 0.57269 | 0.57375 | 0.57481 | 0.57587 | 0.57694 | 0.578 | 0.57906 | 0.58013
| BET005-143035691 | BET005 | 0.082696 | 0.083266 | 0.083837 | 0.084408 | 0.084978 | 0.085245 | 0.085512 | 0.085779 | 0.086046 | 0.086313 | 0.08658 | 0.086848 | 0.087115 | 0.087382 | 0.087649 | 0.087916 | 0.088183 | 0.08845 | 0.088717 | 0.088984
| BET005-15436909 | BET005 | 98.4039 | 98.7623 | 99.1208 | 99.4792 | 99.8377 | 99.948 | 100.0583 | 100.1686 | 100.279 | 100.3893 | 100.4996 | 100.6099 | 100.7202 | 100.8305 | 100.9409 | 101.0512 | 101.1615 | 101.2718 | 101.3821 | 101.4925
| BET005-162764936 | BET005 | 0.016774 | 0.016892 | 0.017011 | 0.017129 | 0.017248 | 0.017286 | 0.017324 | 0.017362 | 0.0174 | 0.017438 | 0.017476 | 0.017514 | 0.017553 | 0.017591 | 0.017629 | 0.017667 | 0.017705 | 0.017743 | 0.017781 | 0.017819
| BET005-24614354 | BET005 | 76.2416 | 76.6578 | 77.0739 | 77.49 | 77.9062 | 78.0886 | 78.271 | 78.4534 | 78.6358 | 78.8183 | 79.0007 | 79.1831 | 79.3655 | 79.548 | 79.7304 | 79.9128 | 80.0952 | 80.2776 | 80.4601 | 80.6425
| BET005-54520179 | BET005 | 24.6429 | 24.8316 | 25.0204 | 25.2091 | 25.3979 | 25.4969 | 25.5959 | 25.6948 | 25.7938 | 25.8928 | 25.9918 | 26.0908 | 26.1897 | 26.2887 | 26.3877 | 26.4867 | 26.5857 | 26.6846 | 26.7836 | 26.8826
| BET005-76446461 | BET005 | 0.38988 | 0.39302 | 0.39616 | 0.3993 | 0.40244 | 0.40372 | 0.405 | 0.40629 | 0.40757 | 0.40885 | 0.41013 | 0.41141 | 0.41269 | 0.41397 | 0.41525 | 0.41653 | 0.41781 | 0.41909 | 0.42038 | 0.42166
| BET005-76446537 | BET005 | 0.20555 | 0.20731 | 0.20907 | 0.21083 | 0.21259 | 0.21331 | 0.21404 | 0.21477 | 0.21549 | 0.21622 | 0.21695 | 0.21767 | 0.2184 | 0.21913 | 0.21985 | 0.22058 | 0.22131 | 0.22203 | 0.22276 | 0.22349
| BET006-122234049 | BET006 | 0.12515 | 0.12591 | 0.12666 | 0.12742 | 0.12818 | 0.12848 | 0.12877 | 0.12907 | 0.12936 | 0.12966 | 0.12996 | 0.13025 | 0.13055 | 0.13085 | 0.13114 | 0.13144 | 0.13173 | 0.13203 | 0.13233 | 0.13262
| BET006-123629680 | BET006 | 1.3452 | 1.3542 | 1.3632 | 1.3722 | 1.3812 | 1.3832 | 1.3852 | 1.3872 | 1.3892 | 1.3912 | 1.3932 | 1.3952 | 1.3972 | 1.3992 | 1.4012 | 1.4032 | 1.4053 | 1.4073 | 1.4093 | 1.4113
| BET006-130742783 | BET006 | 0.29992 | 0.30183 | 0.30373 | 0.30564 | 0.30754 | 0.30823 | 0.30891 | 0.3096 | 0.31028 | 0.31097 | 0.31165 | 0.31234 | 0.31303 | 0.31371 | 0.3144 | 0.31508 | 0.31577 | 0.31645 | 0.31714 | 0.31782
| BET006-143535036 | BET006 | 0.088357 | 0.088988 | 0.089618 | 0.090248 | 0.090878 | 0.091066 | 0.091253 | 0.091441 | 0.091629 | 0.091816 | 0.092004 | 0.092192 | 0.092379 | 0.092567 | 0.092754 | 0.092942 | 0.09313 | 0.093317 | 0.093505 | 0.093692
| BET006-143535310 | BET006 | 0.11701 | 0.1178 | 0.11859 | 0.11938 | 0.12018 | 0.1207 | 0.12121 | 0.12173 | 0.12225 | 0.12277 | 0.12329 | 0.12381 | 0.12433 | 0.12485 | 0.12537 | 0.12589 | 0.1264 | 0.12692 | 0.12744 | 0.12796
| BET006-143535450 | BET006 | 0.47627 | 0.47997 | 0.48367 | 0.48737 | 0.49107 | 0.49235 | 0.49363 | 0.49491 | 0.49619 | 0.49747 | 0.49875 | 0.50003 | 0.50131 | 0.50259 | 0.50387 | 0.50515 | 0.50643 | 0.50771 | 0.50899 | 0.51027
| BET006-15436859 | BET006 | 152.2601 | 152.4453 | 152.6304 | 152.8155 | 153.0006 | 153.0476 | 153.0946 | 153.1416 | 153.1886 | 153.2356 | 153.2826 | 153.3296 | 153.3766 | 153.4236 | 153.4706 | 153.5176 | 153.5646 | 153.6116 | 153.6586 | 153.7056
| BET006-160813078 | BET006 | 0.36216 | 0.3649 | 0.36764 | 0.37038 | 0.37312 | 0.3746 | 0.37607 | 0.37755 | 0.37902 | 0.3805 | 0.38197 | 0.38344 | 0.38492 | 0.38639 | 0.38787 | 0.38934 | 0.39082 | 0.39229 | 0.39376 | 0.39524
| BET006-163864001 | BET006 | 0.65787 | 0.66185 | 0.66582 | 0.66979 | 0.67377 | 0.67545 | 0.67713 | 0.67881 | 0.6805 | 0.68218 | 0.68386 | 0.68554 | 0.68723 | 0.68891 | 0.69059 | 0.69227 | 0.69395 | 0.69564 | 0.69732 | 0.699
| BET006-195895491 | BET006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET006-195895635 | BET006 | 15.1492 | 15.247 | 15.3448 | 15.4426 | 15.5404 | 15.5844 | 15.6283 | 15.6723 | 15.7162 | 15.7602 | 15.8041 | 15.848 | 15.892 | 15.9359 | 15.9799 | 16.0238 | 16.0678 | 16.1117 | 16.1557 | 16.1996
| BET006-195895661 | BET006 | 37.987 | 38.1367 | 38.2863 | 38.436 | 38.5857 | 38.6631 | 38.7405 | 38.8179 | 38.8952 | 38.9726 | 39.05 | 39.1274 | 39.2047 | 39.2821 | 39.3595 | 39.4369 | 39.5142 | 39.5916 | 39.669 | 39.7464
| BET006-195895699 | BET006 | 110.878 | 111.6448 | 112.4117 | 113.1785 | 113.9454 | 114.1407 | 114.336 | 114.5313 | 114.7266 | 114.9219 | 115.1172 | 115.3126 | 115.5079 | 115.7032 | 115.8985 | 116.0938 | 116.2891 | 116.4844 | 116.6797 | 116.8751
| BET006-74053669 | BET006 | 0.11125 | 0.11209 | 0.11294 | 0.11378 | 0.11462 | 0.11493 | 0.11523 | 0.11554 | 0.11585 | 0.11615 | 0.11646 | 0.11677 | 0.11708 | 0.11738 | 0.11769 | 0.118 | 0.11831 | 0.11861 | 0.11892 | 0.11923
| BET006-74053924 | BET006 | 0.3223 | 0.32457 | 0.32685 | 0.32912 | 0.33139 | 0.33233 | 0.33327 | 0.33421 | 0.33515 | 0.33609 | 0.33704 | 0.33798 | 0.33892 | 0.33986 | 0.3408 | 0.34174 | 0.34268 | 0.34362 | 0.34456 | 0.3455
| BET007-110330821 | BET007 | 0.33479 | 0.336 | 0.33722 | 0.33843 | 0.33965 | 0.34049 | 0.34134 | 0.34219 | 0.34303 | 0.34388 | 0.34473 | 0.34557 | 0.34642 | 0.34727 | 0.34811 | 0.34896 | 0.3498 | 0.35065 | 0.3515 | 0.35234
| BET007-129159691 | BET007 | 0.070833 | 0.071264 | 0.071695 | 0.072126 | 0.072558 | 0.072791 | 0.073024 | 0.073257 | 0.073491 | 0.073724 | 0.073957 | 0.074191 | 0.074424 | 0.074657 | 0.074891 | 0.075124 | 0.075357 | 0.07559 | 0.075824 | 0.076057
| BET007-132469306 | BET007 | 2.3718 | 2.3812 | 2.3907 | 2.4001 | 2.4096 | 2.4167 | 2.4239 | 2.431 | 2.4382 | 2.4454 | 2.4525 | 2.4597 | 2.4669 | 2.474 | 2.4812 | 2.4884 | 2.4955 | 2.5027 | 2.5098 | 2.517
| BET007-132750977 | BET007 | 0.24928 | 0.25052 | 0.25176 | 0.253 | 0.25423 | 0.25528 | 0.25633 | 0.25738 | 0.25843 | 0.25948 | 0.26053 | 0.26157 | 0.26262 | 0.26367 | 0.26472 | 0.26577 | 0.26682 | 0.26787 | 0.26891 | 0.26996
| BET007-132751049 | BET007 | 0.019648 | 0.019752 | 0.019857 | 0.019961 | 0.020066 | 0.020162 | 0.020258 | 0.020354 | 0.02045 | 0.020546 | 0.020642 | 0.020738 | 0.020834 | 0.02093 | 0.021026 | 0.021122 | 0.021218 | 0.021314 | 0.02141 | 0.021506
| BET007-134953366 | BET007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BET007-154907496 | BET007 | 0.20526 | 0.20639 | 0.20752 | 0.20865 | 0.20978 | 0.21068 | 0.21158 | 0.21248 | 0.21338 | 0.21428 | 0.21518 | 0.21608 | 0.21698 | 0.21788 | 0.21878 | 0.21968 | 0.22058 | 0.22148 | 0.22238 | 0.22328
| BET007-154907629 | BET007 | 0.1546 | 0.15538 | 0.15616 | 0.15694 | 0.15772 | 0.15833 | 0.15893 | 0.15954 | 0.16015 | 0.16075 | 0.16136 | 0.16197 | 0.16258 | 0.16318 | 0.16379 | 0.1644 | 0.16501 | 0.16561 | 0.16622 | 0.16683
| BET007-154907735 | BET007 | 0.13021 | 0.13111 | 0.13201 | 0.13291 | 0.13381 | 0.13415 | 0.1345 | 0.13485 | 0.1352 | 0.13555 | 0.1359 | 0.13625 | 0.13659 | 0.13694 | 0.13729 | 0.13764 | 0.13799 | 0.13834 | 0.13868 | 0.13903
| BET007-154907875 | BET007 | 0.09875 | 0.099381 | 0.10001 | 0.10064 | 0.10127 | 0.10151 | 0.10175 | 0.10199 | 0.10223 | 0.10247 | 0.10271 | 0.10294 | 0.10318 | 0.10342 | 0.10366 | 0.1039 | 0.10414 | 0.10438 | 0.10462 | 0.10485
| BET007-155326877 | BET007 | 187.0313 | 187.846 | 188.6607 | 189.4755 | 190.2902 | 190.5293 | 190.7685 | 191.0076 | 191.2467 | 191.4859 | 191.725 | 191.9642 | 192.2033 | 192.4424 | 192.6816 | 192.9207 | 193.1598 | 193.399 | 193.6381 | 193.8773
| BET007-159943710 | BET007 | 7.7422 | 7.7826 | 7.8229 | 7.8633 | 7.9036 | 7.9333 | 7.963 | 7.9927 | 8.0224 | 8.052 | 8.0817 | 8.1114 | 8.1411 | 8.1707 | 8.2004 | 8.2301 | 8.2598 | 8.2894 | 8.3191 | 8.3488
| BET007-162663688 | BET007 | 5.762 | 5.7971 | 5.8322 | 5.8674 | 5.9025 | 5.9156 | 5.9287 | 5.9418 | 5.9549 | 5.9681 | 5.9812 | 5.9943 | 6.0074 | 6.0205 | 6.0336 | 6.0468 | 6.0599 | 6.073 | 6.0861 | 6.0992
| BET007-24613316 | BET007 | 28.64 | 28.8127 | 28.9855 | 29.1582 | 29.3309 | 29.3912 | 29.4515 | 29.5117 | 29.572 | 29.6322 | 29.6925 | 29.7527 | 29.813 | 29.8733 | 29.9335 | 29.9938 | 30.054 | 30.1143 | 30.1745 | 30.2348
| BET007-63637518 | BET007 | 16.2803 | 16.3583 | 16.4363 | 16.5142 | 16.5922 | 16.6173 | 16.6424 | 16.6675 | 16.6925 | 16.7176 | 16.7427 | 16.7678 | 16.7929 | 16.818 | 16.8431 | 16.8682 | 16.8932 | 16.9183 | 16.9434 | 16.9685
| BET008-94648877 | BET008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO011-197684068 | BGO011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO012-197683994 | BGO012 | 22.8589 | 22.9678 | 23.0768 | 23.1857 | 23.2947 | 23.3291 | 23.3635 | 23.3979 | 23.4323 | 23.4667 | 23.5011 | 23.5355 | 23.5699 | 23.6043 | 23.6387 | 23.6731 | 23.7075 | 23.7419 | 23.7763 | 23.8107
| BGO013-163795489 | BGO013 | 4.1943 | 4.2201 | 4.2458 | 4.2715 | 4.2973 | 4.3053 | 4.3133 | 4.3213 | 4.3293 | 4.3373 | 4.3453 | 4.3533 | 4.3613 | 4.3693 | 4.3773 | 4.3853 | 4.3933 | 4.4013 | 4.4093 | 4.4173
| BGO013-197650863 | BGO013 | 69.4433 | 69.8061 | 70.1689 | 70.5317 | 70.8945 | 71.1757 | 71.4569 | 71.7381 | 72.0192 | 72.3004 | 72.5816 | 72.8628 | 73.144 | 73.4252 | 73.7063 | 73.9875 | 74.2687 | 74.5499 | 74.8311 | 75.1123
| BGO013-24606216 | BGO013 | 14.6847 | 14.7752 | 14.8657 | 14.9563 | 15.0468 | 15.091 | 15.1353 | 15.1795 | 15.2238 | 15.268 | 15.3122 | 15.3565 | 15.4007 | 15.4449 | 15.4892 | 15.5334 | 15.5777 | 15.6219 | 15.6661 | 15.7104
| BGO014-197650786 | BGO014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO022-164367964 | BGO022 | 4.3165 | 4.346 | 4.3754 | 4.4049 | 4.4344 | 4.45 | 4.4655 | 4.4811 | 4.4967 | 4.5123 | 4.5279 | 4.5434 | 4.559 | 4.5746 | 4.5902 | 4.6057 | 4.6213 | 4.6369 | 4.6525 | 4.668
| BGO022-164368050 | BGO022 | 2.7706 | 2.7822 | 2.7938 | 2.8054 | 2.817 | 2.8214 | 2.8258 | 2.8301 | 2.8345 | 2.8389 | 2.8432 | 2.8476 | 2.852 | 2.8564 | 2.8607 | 2.8651 | 2.8695 | 2.8738 | 2.8782 | 2.8826
| BGO022-197683907 | BGO022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BGO023-143335276 | BGO023 | 2.6784 | 2.695 | 2.7116 | 2.7282 | 2.7448 | 2.7604 | 2.776 | 2.7916 | 2.8072 | 2.8228 | 2.8384 | 2.854 | 2.8697 | 2.8853 | 2.9009 | 2.9165 | 2.9321 | 2.9477 | 2.9633 | 2.9789
| BGO023-143335516 | BGO023 | 0.13793 | 0.139 | 0.14007 | 0.14114 | 0.14222 | 0.14283 | 0.14345 | 0.14407 | 0.14469 | 0.14531 | 0.14593 | 0.14655 | 0.14717 | 0.14779 | 0.14841 | 0.14903 | 0.14965 | 0.15027 | 0.15088 | 0.1515
| BGO023-154908179 | BGO023 | 0.078383 | 0.07897 | 0.079558 | 0.080145 | 0.080732 | 0.081004 | 0.081276 | 0.081548 | 0.081819 | 0.082091 | 0.082363 | 0.082635 | 0.082907 | 0.083178 | 0.08345 | 0.083722 | 0.083994 | 0.084266 | 0.084538 | 0.084809
| BGO023-154971813 | BGO023 | 0.028101 | 0.028336 | 0.028571 | 0.028806 | 0.029041 | 0.029179 | 0.029316 | 0.029454 | 0.029591 | 0.029729 | 0.029866 | 0.030004 | 0.030141 | 0.030279 | 0.030416 | 0.030554 | 0.030691 | 0.030829 | 0.030966 | 0.031104
| BGO023-154971917 | BGO023 | 0.036499 | 0.03676 | 0.037021 | 0.037282 | 0.037543 | 0.037715 | 0.037888 | 0.03806 | 0.038233 | 0.038405 | 0.038578 | 0.03875 | 0.038923 | 0.039095 | 0.039268 | 0.03944 | 0.039613 | 0.039785 | 0.039958 | 0.04013
| BGO023-154972040 | BGO023 | 0.030847 | 0.031097 | 0.031348 | 0.031598 | 0.031848 | 0.032037 | 0.032225 | 0.032413 | 0.032602 | 0.03279 | 0.032978 | 0.033166 | 0.033355 | 0.033543 | 0.033731 | 0.03392 | 0.034108 | 0.034296 | 0.034484 | 0.034673
| BGO023-155521549 | BGO023 | 0.19528 | 0.19654 | 0.1978 | 0.19906 | 0.20032 | 0.20217 | 0.20401 | 0.20585 | 0.2077 | 0.20954 | 0.21138 | 0.21323 | 0.21507 | 0.21691 | 0.21876 | 0.2206 | 0.22244 | 0.22429 | 0.22613 | 0.22797
| BGO023-159428721 | BGO023 | 135.5157 | 136.1163 | 136.717 | 137.3176 | 137.9182 | 138.2889 | 138.6596 | 139.0303 | 139.4009 | 139.7716 | 140.1423 | 140.513 | 140.8836 | 141.2543 | 141.625 | 141.9957 | 142.3664 | 142.737 | 143.1077 | 143.4784
| BGO023-159428755 | BGO023 | 25.3004 | 25.4753 | 25.6502 | 25.825 | 25.9999 | 26.1212 | 26.2425 | 26.3638 | 26.4851 | 26.6064 | 26.7277 | 26.8489 | 26.9702 | 27.0915 | 27.2128 | 27.3341 | 27.4554 | 27.5767 | 27.698 | 27.8193
| BGO023-197650699 | BGO023 | 97.3517 | 97.7793 | 98.2069 | 98.6346 | 99.0622 | 99.2393 | 99.4165 | 99.5937 | 99.7708 | 99.948 | 100.1251 | 100.3023 | 100.4794 | 100.6566 | 100.8337 | 101.0109 | 101.1881 | 101.3652 | 101.5424 | 101.7195
| BGO023-24604124 | BGO023 | 25.4924 | 25.651 | 25.8095 | 25.9681 | 26.1267 | 26.3159 | 26.5051 | 26.6942 | 26.8834 | 27.0726 | 27.2618 | 27.451 | 27.6401 | 27.8293 | 28.0185 | 28.2077 | 28.3969 | 28.5861 | 28.7752 | 28.9644
| BGO023-24614382 | BGO023 | 7.9729 | 8.0232 | 8.0735 | 8.1238 | 8.174 | 8.2301 | 8.2862 | 8.3423 | 8.3984 | 8.4545 | 8.5106 | 8.5666 | 8.6227 | 8.6788 | 8.7349 | 8.791 | 8.8471 | 8.9031 | 8.9592 | 9.0153
| BGO023-76446934 | BGO023 | 0.25047 | 0.25266 | 0.25486 | 0.25705 | 0.25924 | 0.26018 | 0.26112 | 0.26207 | 0.26301 | 0.26395 | 0.26489 | 0.26583 | 0.26678 | 0.26772 | 0.26866 | 0.2696 | 0.27054 | 0.27148 | 0.27243 | 0.27337
| BGO023-76447847 | BGO023 | 0.18654 | 0.18825 | 0.18997 | 0.19168 | 0.1934 | 0.19471 | 0.19603 | 0.19734 | 0.19866 | 0.19997 | 0.20129 | 0.2026 | 0.20392 | 0.20523 | 0.20655 | 0.20786 | 0.20918 | 0.21049 | 0.21181 | 0.21313
| BGO023-76448158 | BGO023 | 0.20772 | 0.2095 | 0.21127 | 0.21304 | 0.21481 | 0.21649 | 0.21817 | 0.21985 | 0.22154 | 0.22322 | 0.2249 | 0.22658 | 0.22826 | 0.22994 | 0.23162 | 0.23331 | 0.23499 | 0.23667 | 0.23835 | 0.24003
| BGO023-76448224 | BGO023 | 0.34007 | 0.34189 | 0.34371 | 0.34553 | 0.34735 | 0.34915 | 0.35095 | 0.35274 | 0.35454 | 0.35634 | 0.35813 | 0.35993 | 0.36173 | 0.36352 | 0.36532 | 0.36712 | 0.36891 | 0.37071 | 0.37251 | 0.3743
| BGO023-95132601 | BGO023 | 0.12362 | 0.12466 | 0.1257 | 0.12674 | 0.12778 | 0.12823 | 0.12867 | 0.12911 | 0.12956 | 0.13 | 0.13044 | 0.13089 | 0.13133 | 0.13177 | 0.13222 | 0.13266 | 0.1331 | 0.13355 | 0.13399 | 0.13443
| BGO023-95621561 | BGO023 | 0.0058159 | 0.0058599 | 0.0059038 | 0.0059477 | 0.0059916 | 0.0060465 | 0.0061015 | 0.0061564 | 0.0062114 | 0.0062663 | 0.0063212 | 0.0063762 | 0.0064311 | 0.0064861 | 0.006541 | 0.0065959 | 0.0066509 | 0.0067058 | 0.0067608 | 0.0068157
| BLT016-15429893 | BLT016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT017-15429856 | BLT017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT019-15429808 | BLT019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT020-15429758 | BLT020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT021-15429734 | BLT021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT022-15429547 | BLT022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT022-164443534 | BLT022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT030-15429658 | BLT030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT031-15429682 | BLT031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH003-137632826 | BMH003 | 0.25682 | 0.25834 | 0.25985 | 0.26136 | 0.26288 | 0.26375 | 0.26462 | 0.26549 | 0.26636 | 0.26723 | 0.2681 | 0.26898 | 0.26985 | 0.27072 | 0.27159 | 0.27246 | 0.27333 | 0.2742 | 0.27507 | 0.27594
| BMH003-137632841 | BMH003 | 0.065099 | 0.065659 | 0.066218 | 0.066778 | 0.067337 | 0.067715 | 0.068094 | 0.068472 | 0.06885 | 0.069228 | 0.069606 | 0.069985 | 0.070363 | 0.070741 | 0.071119 | 0.071497 | 0.071876 | 0.072254 | 0.072632 | 0.07301
| BMH003-137632864 | BMH003 | 0.033894 | 0.034136 | 0.034378 | 0.034621 | 0.034863 | 0.035002 | 0.03514 | 0.035279 | 0.035418 | 0.035556 | 0.035695 | 0.035834 | 0.035972 | 0.036111 | 0.03625 | 0.036388 | 0.036527 | 0.036665 | 0.036804 | 0.036943
| BMH003-137632887 | BMH003 | 0.024734 | 0.024874 | 0.025013 | 0.025152 | 0.025291 | 0.025396 | 0.025501 | 0.025606 | 0.025711 | 0.025816 | 0.025921 | 0.026026 | 0.026131 | 0.026236 | 0.026341 | 0.026446 | 0.026551 | 0.026656 | 0.026761 | 0.026866
| BMH003-140036206 | BMH003 | 23.4572 | 23.6124 | 23.7675 | 23.9227 | 24.0778 | 24.1446 | 24.2114 | 24.2782 | 24.3449 | 24.4117 | 24.4785 | 24.5453 | 24.6121 | 24.6788 | 24.7456 | 24.8124 | 24.8792 | 24.946 | 25.0128 | 25.0795
| BMH003-15408256 | BMH003 | 1.2481 | 1.2494 | 1.2506 | 1.2519 | 1.2531 | 1.2512 | 1.2493 | 1.2474 | 1.2455 | 1.2436 | 1.2417 | 1.2398 | 1.2379 | 1.236 | 1.2341 | 1.2322 | 1.2303 | 1.2284 | 1.2265 | 1.2246
| BMH003-155324907 | BMH003 | 1.1816 | 1.1905 | 1.1995 | 1.2085 | 1.2174 | 1.2214 | 1.2254 | 1.2293 | 1.2333 | 1.2372 | 1.2412 | 1.2451 | 1.2491 | 1.2531 | 1.257 | 1.261 | 1.2649 | 1.2689 | 1.2728 | 1.2768
| BMH003-24599924 | BMH003 | 0.0078922 | 0.0079662 | 0.0080402 | 0.0081142 | 0.0081882 | 0.0082431 | 0.008298 | 0.0083529 | 0.0084078 | 0.0084627 | 0.0085176 | 0.0085725 | 0.0086274 | 0.0086823 | 0.0087372 | 0.0087921 | 0.008847 | 0.0089019 | 0.0089568 | 0.0090117
| BMH003-24599938 | BMH003 | 21.0606 | 21.281 | 21.5013 | 21.7217 | 21.9421 | 21.9776 | 22.0132 | 22.0488 | 22.0844 | 22.12 | 22.1556 | 22.1912 | 22.2268 | 22.2623 | 22.2979 | 22.3335 | 22.3691 | 22.4047 | 22.4403 | 22.4759
| BMH003-54311761 | BMH003 | 1.4092 | 1.4189 | 1.4286 | 1.4384 | 1.4481 | 1.4525 | 1.457 | 1.4614 | 1.4658 | 1.4703 | 1.4747 | 1.4791 | 1.4835 | 1.488 | 1.4924 | 1.4968 | 1.5013 | 1.5057 | 1.5101 | 1.5146
| BMH003-84023922 | BMH003 | 0.0083375 | 0.0084072 | 0.0084769 | 0.0085466 | 0.0086163 | 0.0086585 | 0.0087006 | 0.0087428 | 0.0087849 | 0.008827 | 0.0088692 | 0.0089113 | 0.0089534 | 0.0089956 | 0.0090377 | 0.0090798 | 0.009122 | 0.0091641 | 0.0092062 | 0.0092484
| BMH003-84426167 | BMH003 | 0.063914 | 0.064491 | 0.065068 | 0.065645 | 0.066223 | 0.066749 | 0.067275 | 0.067802 | 0.068328 | 0.068855 | 0.069381 | 0.069907 | 0.070434 | 0.07096 | 0.071486 | 0.072013 | 0.072539 | 0.073066 | 0.073592 | 0.074118
| BMH004-15408343 | BMH004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH004-15408369 | BMH004 | 77.2219 | 77.9612 | 78.7005 | 79.4398 | 80.1791 | 80.2395 | 80.3 | 80.3604 | 80.4208 | 80.4812 | 80.5416 | 80.602 | 80.6624 | 80.7229 | 80.7833 | 80.8437 | 80.9041 | 80.9645 | 81.0249 | 81.0853
| BMH005-15408219 | BMH005 | 65.8663 | 66.4328 | 66.9992 | 67.5657 | 68.1322 | 68.0751 | 68.018 | 67.9609 | 67.9038 | 67.8468 | 67.7897 | 67.7326 | 67.6755 | 67.6184 | 67.5613 | 67.5042 | 67.4471 | 67.3901 | 67.333 | 67.2759
| BMH005-15408230 | BMH005 | 0.40214 | 0.40578 | 0.40942 | 0.41307 | 0.41671 | 0.41759 | 0.41846 | 0.41934 | 0.42021 | 0.42109 | 0.42196 | 0.42284 | 0.42371 | 0.42459 | 0.42546 | 0.42634 | 0.42721 | 0.42809 | 0.42896 | 0.42984
| BMH005-65434147 | BMH005 | 8.4955 | 8.5973 | 8.6992 | 8.801 | 8.9029 | 8.9212 | 8.9395 | 8.9578 | 8.9761 | 8.9944 | 9.0127 | 9.031 | 9.0492 | 9.0675 | 9.0858 | 9.1041 | 9.1224 | 9.1407 | 9.159 | 9.1773
| BMH006-15408306 | BMH006 | 10.6533 | 10.7347 | 10.8161 | 10.8976 | 10.979 | 11.0123 | 11.0456 | 11.0789 | 11.1123 | 11.1456 | 11.1789 | 11.2122 | 11.2455 | 11.2789 | 11.3122 | 11.3455 | 11.3788 | 11.4122 | 11.4455 | 11.4788
| BMH006-201878277 | BMH006 | 2.5645 | 2.5844 | 2.6043 | 2.6243 | 2.6442 | 2.6527 | 2.6613 | 2.6699 | 2.6784 | 2.687 | 2.6956 | 2.7042 | 2.7127 | 2.7213 | 2.7299 | 2.7385 | 2.747 | 2.7556 | 2.7642 | 2.7727
| BMH006-24602242 | BMH006 | 0.0034569 | 0.0034883 | 0.0035196 | 0.003551 | 0.0035823 | 0.0035906 | 0.0035989 | 0.0036072 | 0.0036155 | 0.0036237 | 0.003632 | 0.0036403 | 0.0036486 | 0.0036569 | 0.0036652 | 0.0036735 | 0.0036818 | 0.0036901 | 0.0036984 | 0.0037066
| BMH006-74239819 | BMH006 | 0.020735 | 0.02091 | 0.021084 | 0.021259 | 0.021434 | 0.021504 | 0.021575 | 0.021646 | 0.021716 | 0.021787 | 0.021858 | 0.021929 | 0.021999 | 0.02207 | 0.022141 | 0.022211 | 0.022282 | 0.022353 | 0.022423 | 0.022494
| BMH006-84024816 | BMH006 | 0.023689 | 0.023895 | 0.024102 | 0.024308 | 0.024515 | 0.024602 | 0.024689 | 0.024776 | 0.024863 | 0.02495 | 0.025037 | 0.025124 | 0.025211 | 0.025298 | 0.025385 | 0.025472 | 0.025559 | 0.025646 | 0.025733 | 0.025821
| BMH006-85029171 | BMH006 | 0.04975 | 0.050172 | 0.050595 | 0.051017 | 0.051439 | 0.051553 | 0.051667 | 0.051781 | 0.051895 | 0.052009 | 0.052123 | 0.052237 | 0.052351 | 0.052465 | 0.052579 | 0.052693 | 0.052807 | 0.052921 | 0.053035 | 0.053149
| BMH006-85031037 | BMH006 | 0.020241 | 0.020413 | 0.020584 | 0.020756 | 0.020928 | 0.020969 | 0.02101 | 0.021051 | 0.021092 | 0.021133 | 0.021174 | 0.021215 | 0.021256 | 0.021297 | 0.021338 | 0.021379 | 0.02142 | 0.021461 | 0.021502 | 0.021543
| CDN001-144336613 | CDN001 | 0.0045509 | 0.0045572 | 0.0045636 | 0.00457 | 0.0045763 | 0.0045697 | 0.004563 | 0.0045564 | 0.0045498 | 0.0045431 | 0.0045365 | 0.0045298 | 0.0045232 | 0.0045165 | 0.0045099 | 0.0045033 | 0.0044966 | 0.00449 | 0.0044833 | 0.0044767
| CDN001-147732702 | CDN001 | 0.0030979 | 0.0031356 | 0.0031733 | 0.0032109 | 0.0032486 | 0.0031819 | 0.0031153 | 0.0030487 | 0.0029821 | 0.0029154 | 0.0028488 | 0.0027822 | 0.0027156 | 0.0026489 | 0.0025823 | 0.0025157 | 0.0024491 | 0.0023824 | 0.0023158 | 0.0022492
| CDN001-147732747 | CDN001 | 0.0062139 | 0.0062767 | 0.0063396 | 0.0064025 | 0.0064654 | 0.0063869 | 0.0063085 | 0.00623 | 0.0061516 | 0.0060731 | 0.0059947 | 0.0059162 | 0.0058378 | 0.0057593 | 0.0056809 | 0.0056024 | 0.005524 | 0.0054455 | 0.0053671 | 0.0052886
| CDN001-15400083 | CDN001 | 7.0535 | 7.1147 | 7.1759 | 7.2371 | 7.2983 | 7.2268 | 7.1553 | 7.0839 | 7.0124 | 6.9409 | 6.8694 | 6.798 | 6.7265 | 6.655 | 6.5835 | 6.5121 | 6.4406 | 6.3691 | 6.2976 | 6.2262
| CDN001-15400094 | CDN001 | 0.4951 | 0.50037 | 0.50564 | 0.5109 | 0.51617 | 0.50989 | 0.50361 | 0.49733 | 0.49105 | 0.48478 | 0.4785 | 0.47222 | 0.46594 | 0.45966 | 0.45338 | 0.4471 | 0.44083 | 0.43455 | 0.42827 | 0.42199
| CDN001-154719434 | CDN001 | 0.0028577 | 0.002887 | 0.0029164 | 0.0029457 | 0.0029751 | 0.0029363 | 0.0028974 | 0.0028586 | 0.0028198 | 0.002781 | 0.0027421 | 0.0027033 | 0.0026645 | 0.0026257 | 0.0025868 | 0.002548 | 0.0025092 | 0.0024704 | 0.0024316 | 0.0023927
| CDN001-156321963 | CDN001 | 1.4408 | 1.4563 | 1.4718 | 1.4873 | 1.5028 | 1.4829 | 1.4631 | 1.4432 | 1.4234 | 1.4036 | 1.3837 | 1.3639 | 1.344 | 1.3242 | 1.3044 | 1.2845 | 1.2647 | 1.2448 | 1.225 | 1.2052
| CDN001-158379454 | CDN001 | 0.019597 | 0.019627 | 0.019657 | 0.019687 | 0.019718 | 0.019686 | 0.019655 | 0.019623 | 0.019591 | 0.01956 | 0.019528 | 0.019497 | 0.019465 | 0.019434 | 0.019402 | 0.019371 | 0.019339 | 0.019308 | 0.019276 | 0.019244
| CDN001-160252941 | CDN001 | 0.000962 | 0.00097372 | 0.00098545 | 0.00099717 | 0.0010089 | 0.00099493 | 0.00098097 | 0.000967 | 0.00095304 | 0.00093907 | 0.00092511 | 0.00091114 | 0.00089718 | 0.00088322 | 0.00086925 | 0.00085529 | 0.00084132 | 0.00082736 | 0.00081339 | 0.00079943
| CDN001-162435420 | CDN001 | 0.00053254 | 0.0005405 | 0.00054847 | 0.00055643 | 0.0005644 | 0.00055318 | 0.00054196 | 0.00053074 | 0.00051952 | 0.0005083 | 0.00049708 | 0.00048586 | 0.00047464 | 0.00046342 | 0.0004522 | 0.00044098 | 0.00042976 | 0.00041854 | 0.00040732 | 0.0003961
| CDN001-162435922 | CDN001 | 0.004864 | 0.0049105 | 0.0049569 | 0.0050034 | 0.0050498 | 0.0049908 | 0.0049318 | 0.0048728 | 0.0048138 | 0.0047547 | 0.0046957 | 0.0046367 | 0.0045777 | 0.0045186 | 0.0044596 | 0.0044006 | 0.0043416 | 0.0042826 | 0.0042235 | 0.0041645
| CDN001-164044162 | CDN001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-164044516 | CDN001 | 0.056501 | 0.056955 | 0.057409 | 0.057863 | 0.058317 | 0.057492 | 0.056667 | 0.055843 | 0.055018 | 0.054193 | 0.053369 | 0.052544 | 0.05172 | 0.050895 | 0.05007 | 0.049246 | 0.048421 | 0.047596 | 0.046772 | 0.045947
| CDN001-171348505 | CDN001 | 0.0026855 | 0.0027006 | 0.0027157 | 0.0027309 | 0.002746 | 0.0027189 | 0.0026919 | 0.0026648 | 0.0026378 | 0.0026107 | 0.0025836 | 0.0025566 | 0.0025295 | 0.0025024 | 0.0024754 | 0.0024483 | 0.0024213 | 0.0023942 | 0.0023671 | 0.0023401
| CDN001-177002783 | CDN001 | 0.011224 | 0.011346 | 0.011468 | 0.01159 | 0.011713 | 0.011556 | 0.011398 | 0.011241 | 0.011084 | 0.010927 | 0.01077 | 0.010613 | 0.010455 | 0.010298 | 0.010141 | 0.009984 | 0.0098268 | 0.0096696 | 0.0095125 | 0.0093553
| CDN001-178141597 | CDN001 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06
| CDN001-202076817 | CDN001 | 0.43317 | 0.43721 | 0.44125 | 0.44529 | 0.44933 | 0.44333 | 0.43734 | 0.43135 | 0.42536 | 0.41936 | 0.41337 | 0.40738 | 0.40138 | 0.39539 | 0.3894 | 0.3834 | 0.37741 | 0.37142 | 0.36543 | 0.35943
| CDN002-15400020 | CDN002 | 2.8324 | 2.8603 | 2.8882 | 2.9161 | 2.944 | 2.9156 | 2.8871 | 2.8586 | 2.8301 | 2.8017 | 2.7732 | 2.7447 | 2.7163 | 2.6878 | 2.6593 | 2.6309 | 2.6024 | 2.5739 | 2.5455 | 2.517
| CDN002-15400044 | CDN002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN002-162961049 | CDN002 | 0.003308 | 0.0033491 | 0.0033901 | 0.0034312 | 0.0034722 | 0.0034231 | 0.0033739 | 0.0033248 | 0.0032756 | 0.0032264 | 0.0031773 | 0.0031281 | 0.003079 | 0.0030298 | 0.0029806 | 0.0029315 | 0.0028823 | 0.0028332 | 0.002784 | 0.0027348
| CDN002-162961261 | CDN002 | 0.00014585 | 0.00014779 | 0.00014973 | 0.00015166 | 0.0001536 | 0.00015207 | 0.00015054 | 0.00014901 | 0.00014748 | 0.00014595 | 0.00014442 | 0.00014289 | 0.00014136 | 0.00013983 | 0.0001383 | 0.00013677 | 0.00013524 | 0.00013371 | 0.00013218 | 0.00013065
| CDN002-162961458 | CDN002 | 0.000914 | 0.00092526 | 0.00093652 | 0.00094778 | 0.00095904 | 0.00094989 | 0.00094073 | 0.00093158 | 0.00092243 | 0.00091327 | 0.00090412 | 0.00089497 | 0.00088581 | 0.00087666 | 0.00086751 | 0.00085835 | 0.0008492 | 0.00084005 | 0.00083089 | 0.00082174
| CDN002-163179235 | CDN002 | 0.017873 | 0.01803 | 0.018188 | 0.018345 | 0.018503 | 0.0183 | 0.018098 | 0.017895 | 0.017693 | 0.01749 | 0.017288 | 0.017085 | 0.016882 | 0.01668 | 0.016477 | 0.016275 | 0.016072 | 0.01587 | 0.015667 | 0.015465
| CDN002-163194789 | CDN002 | 1.7509e-05 | 1.7731e-05 | 1.7954e-05 | 1.8177e-05 | 1.84e-05 | 1.8135e-05 | 1.787e-05 | 1.7605e-05 | 1.734e-05 | 1.7075e-05 | 1.681e-05 | 1.6545e-05 | 1.628e-05 | 1.6015e-05 | 1.575e-05 | 1.5485e-05 | 1.522e-05 | 1.4955e-05 | 1.469e-05 | 1.4425e-05
| CDN002-163309826 | CDN002 | 0.017983 | 0.018204 | 0.018424 | 0.018644 | 0.018865 | 0.018665 | 0.018465 | 0.018265 | 0.018066 | 0.017866 | 0.017666 | 0.017466 | 0.017266 | 0.017067 | 0.016867 | 0.016667 | 0.016467 | 0.016268 | 0.016068 | 0.015868
| CDN002-85030215 | CDN002 | 0.40168 | 0.40652 | 0.41135 | 0.41619 | 0.42103 | 0.41544 | 0.40986 | 0.40428 | 0.39869 | 0.39311 | 0.38753 | 0.38195 | 0.37636 | 0.37078 | 0.3652 | 0.35961 | 0.35403 | 0.34845 | 0.34286 | 0.33728
| CDN003-15400133 | CDN003 | 1.1794 | 1.1883 | 1.1971 | 1.206 | 1.2149 | 1.2037 | 1.1926 | 1.1815 | 1.1703 | 1.1592 | 1.1481 | 1.137 | 1.1258 | 1.1147 | 1.1036 | 1.0924 | 1.0813 | 1.0702 | 1.0591 | 1.0479
| CDN004-139244393 | CDN004 | 0.0019911 | 0.0020167 | 0.0020422 | 0.0020677 | 0.0020932 | 0.0020913 | 0.0020893 | 0.0020874 | 0.0020854 | 0.0020835 | 0.0020815 | 0.0020795 | 0.0020776 | 0.0020756 | 0.0020737 | 0.0020717 | 0.0020698 | 0.0020678 | 0.0020659 | 0.0020639
| CDN004-139244670 | CDN004 | 0.099924 | 0.10096 | 0.102 | 0.10304 | 0.10408 | 0.10346 | 0.10284 | 0.10222 | 0.1016 | 0.10098 | 0.10036 | 0.099744 | 0.099124 | 0.098505 | 0.097885 | 0.097266 | 0.096646 | 0.096027 | 0.095407 | 0.094788
| CDN004-139351301 | CDN004 | 0.0031208 | 0.0031556 | 0.0031904 | 0.0032252 | 0.0032601 | 0.0032444 | 0.0032287 | 0.003213 | 0.0031973 | 0.0031816 | 0.0031659 | 0.0031502 | 0.0031345 | 0.0031188 | 0.0031031 | 0.0030874 | 0.0030717 | 0.003056 | 0.0030403 | 0.0030246
| CDN004-142953493 | CDN004 | 0.0094316 | 0.009516 | 0.0096004 | 0.0096848 | 0.0097692 | 0.0096967 | 0.0096242 | 0.0095517 | 0.0094792 | 0.0094066 | 0.0093341 | 0.0092616 | 0.0091891 | 0.0091166 | 0.009044 | 0.0089715 | 0.008899 | 0.0088265 | 0.008754 | 0.0086815
| CDN004-15399970 | CDN004 | 2.0391 | 2.0555 | 2.0718 | 2.0882 | 2.1045 | 2.0828 | 2.061 | 2.0393 | 2.0175 | 1.9957 | 1.974 | 1.9522 | 1.9305 | 1.9087 | 1.887 | 1.8652 | 1.8435 | 1.8217 | 1.8 | 1.7782
| CDN004-159428859 | CDN004 | 0.0017646 | 0.0017801 | 0.0017956 | 0.001811 | 0.0018265 | 0.0018194 | 0.0018123 | 0.0018053 | 0.0017982 | 0.0017911 | 0.001784 | 0.0017769 | 0.0017699 | 0.0017628 | 0.0017557 | 0.0017486 | 0.0017415 | 0.0017345 | 0.0017274 | 0.0017203
| CDN004-159428956 | CDN004 | 0.0067627 | 0.0068217 | 0.0068806 | 0.0069396 | 0.0069986 | 0.0069652 | 0.0069319 | 0.0068985 | 0.0068651 | 0.0068318 | 0.0067984 | 0.0067651 | 0.0067317 | 0.0066984 | 0.006665 | 0.0066317 | 0.0065983 | 0.0065649 | 0.0065316 | 0.0064982
| CDN004-159429052 | CDN004 | 0.00055189 | 0.00055211 | 0.00055234 | 0.00055257 | 0.0005528 | 0.00055256 | 0.00055232 | 0.00055208 | 0.00055184 | 0.0005516 | 0.00055136 | 0.00055112 | 0.00055088 | 0.00055064 | 0.0005504 | 0.00055016 | 0.00054992 | 0.00054968 | 0.00054944 | 0.0005492
| CDN004-162436765 | CDN004 | 0.0039939 | 0.0040351 | 0.0040763 | 0.0041175 | 0.0041587 | 0.0041355 | 0.0041122 | 0.0040889 | 0.0040657 | 0.0040424 | 0.0040191 | 0.0039958 | 0.0039726 | 0.0039493 | 0.003926 | 0.0039028 | 0.0038795 | 0.0038562 | 0.003833 | 0.0038097
| CDN004-202037935 | CDN004 | 0.51743 | 0.52082 | 0.52421 | 0.52761 | 0.531 | 0.53173 | 0.53247 | 0.5332 | 0.53393 | 0.53467 | 0.5354 | 0.53613 | 0.53687 | 0.5376 | 0.53833 | 0.53907 | 0.5398 | 0.54053 | 0.54127 | 0.542
| CDN004-202768387 | CDN004 | 1.6599 | 1.6752 | 1.6905 | 1.7059 | 1.7212 | 1.7154 | 1.7096 | 1.7039 | 1.6981 | 1.6923 | 1.6866 | 1.6808 | 1.675 | 1.6693 | 1.6635 | 1.6577 | 1.652 | 1.6462 | 1.6404 | 1.6347
| CDN006-143338433 | CDN006 | 0.018719 | 0.018885 | 0.019051 | 0.019217 | 0.019382 | 0.019318 | 0.019254 | 0.01919 | 0.019126 | 0.019062 | 0.018998 | 0.018934 | 0.01887 | 0.018805 | 0.018741 | 0.018677 | 0.018613 | 0.018549 | 0.018485 | 0.018421
| CDN006-143338709 | CDN006 | 0.0039237 | 0.0039617 | 0.0039996 | 0.0040376 | 0.0040756 | 0.0040634 | 0.0040512 | 0.004039 | 0.0040268 | 0.0040146 | 0.0040025 | 0.0039903 | 0.0039781 | 0.0039659 | 0.0039537 | 0.0039415 | 0.0039293 | 0.0039171 | 0.0039049 | 0.0038928
| CDN006-143338924 | CDN006 | 0.00027981 | 0.00028275 | 0.0002857 | 0.00028865 | 0.0002916 | 0.00029016 | 0.00028872 | 0.00028728 | 0.00028584 | 0.0002844 | 0.00028296 | 0.00028152 | 0.00028008 | 0.00027864 | 0.0002772 | 0.00027576 | 0.00027432 | 0.00027288 | 0.00027144 | 0.00027
| CDN006-143339149 | CDN006 | 0.0045544 | 0.0045868 | 0.0046191 | 0.0046514 | 0.0046838 | 0.004654 | 0.0046242 | 0.0045945 | 0.0045647 | 0.004535 | 0.0045052 | 0.0044754 | 0.0044457 | 0.0044159 | 0.0043862 | 0.0043564 | 0.0043266 | 0.0042969 | 0.0042671 | 0.0042374
| CDN006-15399920 | CDN006 | 1.7556 | 1.7714 | 1.7872 | 1.8029 | 1.8187 | 1.7974 | 1.7761 | 1.7548 | 1.7335 | 1.7122 | 1.6909 | 1.6696 | 1.6482 | 1.6269 | 1.6056 | 1.5843 | 1.563 | 1.5417 | 1.5204 | 1.4991
| CDN006-158379713 | CDN006 | 0.015389 | 0.015538 | 0.015686 | 0.015835 | 0.015983 | 0.015933 | 0.015882 | 0.015831 | 0.01578 | 0.015729 | 0.015678 | 0.015627 | 0.015576 | 0.015526 | 0.015475 | 0.015424 | 0.015373 | 0.015322 | 0.015271 | 0.01522
| CDN006-158379840 | CDN006 | 0.0042044 | 0.0042493 | 0.0042943 | 0.0043392 | 0.0043842 | 0.0043689 | 0.0043535 | 0.0043382 | 0.0043228 | 0.0043075 | 0.0042921 | 0.0042768 | 0.0042614 | 0.0042461 | 0.0042308 | 0.0042154 | 0.0042001 | 0.0041847 | 0.0041694 | 0.004154
| CDN006-160451043 | CDN006 | 0.013821 | 0.013967 | 0.014114 | 0.01426 | 0.014406 | 0.014361 | 0.014315 | 0.014269 | 0.014223 | 0.014177 | 0.014132 | 0.014086 | 0.01404 | 0.013994 | 0.013948 | 0.013902 | 0.013857 | 0.013811 | 0.013765 | 0.013719
| CDN006-162450281 | CDN006 | 1.9716e-05 | 1.9992e-05 | 2.0268e-05 | 2.0544e-05 | 2.082e-05 | 2.0757e-05 | 2.0694e-05 | 2.0631e-05 | 2.0568e-05 | 2.0505e-05 | 2.0442e-05 | 2.0379e-05 | 2.0316e-05 | 2.0253e-05 | 2.019e-05 | 2.0127e-05 | 2.0064e-05 | 2.0001e-05 | 1.9938e-05 | 1.9875e-05
| CDN006-162451240 | CDN006 | 0.00062951 | 0.00063537 | 0.00064122 | 0.00064708 | 0.00065294 | 0.00064859 | 0.00064425 | 0.0006399 | 0.00063556 | 0.00063121 | 0.00062687 | 0.00062252 | 0.00061818 | 0.00061383 | 0.00060949 | 0.00060514 | 0.0006008 | 0.00059645 | 0.00059211 | 0.00058776
| CDN006-162572514 | CDN006 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05
| CDN006-162572817 | CDN006 | 5.8661e-05 | 5.9395e-05 | 6.013e-05 | 6.0865e-05 | 6.16e-05 | 6.078e-05 | 5.996e-05 | 5.914e-05 | 5.832e-05 | 5.75e-05 | 5.668e-05 | 5.586e-05 | 5.504e-05 | 5.422e-05 | 5.34e-05 | 5.258e-05 | 5.176e-05 | 5.094e-05 | 5.012e-05 | 4.93e-05
| CDN006-162588679 | CDN006 | 0.0035757 | 0.0036155 | 0.0036554 | 0.0036952 | 0.003735 | 0.0036795 | 0.003624 | 0.0035685 | 0.003513 | 0.0034575 | 0.003402 | 0.0033465 | 0.003291 | 0.0032355 | 0.00318 | 0.0031245 | 0.003069 | 0.0030135 | 0.002958 | 0.0029025
| CDN006-162675220 | CDN006 | 1.5637e-05 | 1.5803e-05 | 1.5969e-05 | 1.6134e-05 | 1.63e-05 | 1.6145e-05 | 1.599e-05 | 1.5835e-05 | 1.568e-05 | 1.5525e-05 | 1.537e-05 | 1.5215e-05 | 1.506e-05 | 1.4905e-05 | 1.475e-05 | 1.4595e-05 | 1.444e-05 | 1.4285e-05 | 1.413e-05 | 1.3975e-05
| CDN006-162675596 | CDN006 | 4.48e-06 | 4.54e-06 | 4.6e-06 | 4.66e-06 | 4.72e-06 | 4.701e-06 | 4.682e-06 | 4.663e-06 | 4.644e-06 | 4.625e-06 | 4.606e-06 | 4.587e-06 | 4.568e-06 | 4.549e-06 | 4.53e-06 | 4.511e-06 | 4.492e-06 | 4.473e-06 | 4.454e-06 | 4.435e-06
| CDN006-183157401 | CDN006 | 0.00016962 | 0.00017182 | 0.00017401 | 0.00017621 | 0.0001784 | 0.00017544 | 0.00017248 | 0.00016952 | 0.00016656 | 0.0001636 | 0.00016064 | 0.00015768 | 0.00015472 | 0.00015176 | 0.0001488 | 0.00014584 | 0.00014288 | 0.00013992 | 0.00013696 | 0.000134
| CDN006-202038054 | CDN006 | 1.1756 | 1.1842 | 1.1928 | 1.2014 | 1.2101 | 1.2067 | 1.2033 | 1.2 | 1.1966 | 1.1932 | 1.1898 | 1.1865 | 1.1831 | 1.1797 | 1.1764 | 1.173 | 1.1696 | 1.1662 | 1.1629 | 1.1595
| CDN006-202248649 | CDN006 | 1.3847 | 1.3968 | 1.4089 | 1.4209 | 1.433 | 1.4256 | 1.4182 | 1.4108 | 1.4034 | 1.396 | 1.3887 | 1.3813 | 1.3739 | 1.3665 | 1.3591 | 1.3517 | 1.3443 | 1.3369 | 1.3295 | 1.3221
| CHA003-15429144 | CHA003 | 3.6025 | 3.6298 | 3.657 | 3.6843 | 3.7116 | 3.7498 | 3.788 | 3.8262 | 3.8644 | 3.9027 | 3.9409 | 3.9791 | 4.0173 | 4.0555 | 4.0938 | 4.132 | 4.1702 | 4.2084 | 4.2466 | 4.2849
| CHA003-155052833 | CHA003 | 0.00028677 | 0.00028907 | 0.00029138 | 0.00029369 | 0.000296 | 0.00029956 | 0.00030312 | 0.00030668 | 0.00031024 | 0.0003138 | 0.00031736 | 0.00032092 | 0.00032448 | 0.00032804 | 0.0003316 | 0.00033516 | 0.00033872 | 0.00034228 | 0.00034584 | 0.0003494
| CHA003-155052965 | CHA003 | 0.00087787 | 0.00088455 | 0.00089124 | 0.00089793 | 0.00090461 | 0.00091569 | 0.00092676 | 0.00093784 | 0.00094891 | 0.00095999 | 0.00097106 | 0.00098214 | 0.00099321 | 0.0010043 | 0.0010154 | 0.0010264 | 0.0010375 | 0.0010486 | 0.0010597 | 0.0010707
| CHA003-24606706 | CHA003 | 2.541 | 2.5565 | 2.572 | 2.5875 | 2.6029 | 2.6236 | 2.6443 | 2.6649 | 2.6856 | 2.7063 | 2.7269 | 2.7476 | 2.7682 | 2.7889 | 2.8096 | 2.8302 | 2.8509 | 2.8715 | 2.8922 | 2.9129
| CHA005-15429107 | CHA005 | 6.0766 | 6.121 | 6.1654 | 6.2098 | 6.2542 | 6.3147 | 6.3753 | 6.4359 | 6.4964 | 6.557 | 6.6175 | 6.6781 | 6.7387 | 6.7992 | 6.8598 | 6.9203 | 6.9809 | 7.0415 | 7.102 | 7.1626
| CHA005-155053189 | CHA005 | 0.00035367 | 0.00035661 | 0.00035954 | 0.00036247 | 0.0003654 | 0.00036999 | 0.00037458 | 0.00037917 | 0.00038376 | 0.00038835 | 0.00039294 | 0.00039753 | 0.00040212 | 0.00040671 | 0.0004113 | 0.00041589 | 0.00042048 | 0.00042507 | 0.00042966 | 0.00043425
| CHA005-24606076 | CHA005 | 28.8313 | 29.0034 | 29.1755 | 29.3476 | 29.5197 | 29.701 | 29.8824 | 30.0637 | 30.245 | 30.4263 | 30.6077 | 30.789 | 30.9703 | 31.1516 | 31.333 | 31.5143 | 31.6956 | 31.8769 | 32.0583 | 32.2396
| CHA005-24606160 | CHA005 | 0.84994 | 0.85577 | 0.8616 | 0.86743 | 0.87326 | 0.87992 | 0.88659 | 0.89326 | 0.89992 | 0.90659 | 0.91326 | 0.91992 | 0.92659 | 0.93326 | 0.93992 | 0.94659 | 0.95326 | 0.95993 | 0.96659 | 0.97326
| CHA005-53118475 | CHA005 | 0.68623 | 0.69058 | 0.69494 | 0.69929 | 0.70365 | 0.70797 | 0.7123 | 0.71663 | 0.72096 | 0.72529 | 0.72961 | 0.73394 | 0.73827 | 0.7426 | 0.74693 | 0.75125 | 0.75558 | 0.75991 | 0.76424 | 0.76856
| CHA005-56709738 | CHA005 | 0.16167 | 0.16299 | 0.16432 | 0.16564 | 0.16697 | 0.16861 | 0.17024 | 0.17188 | 0.17352 | 0.17515 | 0.17679 | 0.17843 | 0.18007 | 0.1817 | 0.18334 | 0.18498 | 0.18661 | 0.18825 | 0.18989 | 0.19152
| CHA005-56710238 | CHA005 | 18.3502 | 18.4628 | 18.5755 | 18.6881 | 18.8007 | 18.8928 | 18.9849 | 19.077 | 19.1691 | 19.2612 | 19.3533 | 19.4454 | 19.5375 | 19.6296 | 19.7217 | 19.8138 | 19.9058 | 19.9979 | 20.09 | 20.1821
| CHA006-120251163 | CHA006 | 0.11141 | 0.11212 | 0.11282 | 0.11353 | 0.11423 | 0.11502 | 0.1158 | 0.11659 | 0.11737 | 0.11816 | 0.11895 | 0.11973 | 0.12052 | 0.1213 | 0.12209 | 0.12287 | 0.12366 | 0.12444 | 0.12523 | 0.12601
| CHA006-130745345 | CHA006 | 0.00054069 | 0.00054421 | 0.00054774 | 0.00055127 | 0.0005548 | 0.00056031 | 0.00056582 | 0.00057133 | 0.00057684 | 0.00058235 | 0.00058786 | 0.00059337 | 0.00059888 | 0.00060439 | 0.0006099 | 0.00061541 | 0.00062092 | 0.00062643 | 0.00063194 | 0.00063745
| CHA006-138134893 | CHA006 | 0.00021287 | 0.00021475 | 0.00021663 | 0.00021852 | 0.0002204 | 0.00022163 | 0.00022287 | 0.0002241 | 0.00022534 | 0.00022657 | 0.00022781 | 0.00022905 | 0.00023028 | 0.00023152 | 0.00023275 | 0.00023399 | 0.00023522 | 0.00023646 | 0.00023769 | 0.00023893
| CHA006-15429283 | CHA006 | 8.7738 | 8.8328 | 8.8919 | 8.951 | 9.0101 | 9.0862 | 9.1624 | 9.2385 | 9.3146 | 9.3907 | 9.4669 | 9.543 | 9.6191 | 9.6953 | 9.7714 | 9.8475 | 9.9236 | 9.9998 | 10.0759 | 10.152
| CHA006-155505830 | CHA006 | 0.0082267 | 0.0082901 | 0.0083535 | 0.0084169 | 0.0084804 | 0.008524 | 0.0085677 | 0.0086114 | 0.008655 | 0.0086987 | 0.0087424 | 0.008786 | 0.0088297 | 0.0088733 | 0.008917 | 0.0089607 | 0.0090043 | 0.009048 | 0.0090917 | 0.0091353
| CHA006-155506079 | CHA006 | 0.099325 | 0.099816 | 0.10031 | 0.1008 | 0.10129 | 0.10164 | 0.10198 | 0.10233 | 0.10267 | 0.10302 | 0.10337 | 0.10371 | 0.10406 | 0.1044 | 0.10475 | 0.1051 | 0.10544 | 0.10579 | 0.10614 | 0.10648
| CHA006-155506186 | CHA006 | 0.0098412 | 0.0099007 | 0.0099601 | 0.01002 | 0.010079 | 0.010116 | 0.010152 | 0.010189 | 0.010225 | 0.010262 | 0.010298 | 0.010335 | 0.010372 | 0.010408 | 0.010445 | 0.010481 | 0.010518 | 0.010554 | 0.010591 | 0.010628
| CHA006-155506347 | CHA006 | 0.011962 | 0.012031 | 0.012099 | 0.012167 | 0.012235 | 0.012281 | 0.012326 | 0.012372 | 0.012417 | 0.012462 | 0.012508 | 0.012553 | 0.012599 | 0.012644 | 0.01269 | 0.012735 | 0.012781 | 0.012826 | 0.012871 | 0.012917
| CHA006-155506472 | CHA006 | 0.019381 | 0.019478 | 0.019575 | 0.019671 | 0.019768 | 0.019832 | 0.019897 | 0.019961 | 0.020025 | 0.020089 | 0.020154 | 0.020218 | 0.020282 | 0.020346 | 0.02041 | 0.020475 | 0.020539 | 0.020603 | 0.020667 | 0.020732
| CHA006-155506614 | CHA006 | 0.00016294 | 0.00016446 | 0.00016597 | 0.00016749 | 0.000169 | 0.0001702 | 0.0001714 | 0.0001726 | 0.0001738 | 0.000175 | 0.0001762 | 0.0001774 | 0.0001786 | 0.0001798 | 0.000181 | 0.0001822 | 0.0001834 | 0.0001846 | 0.0001858 | 0.000187
| CHA006-155618024 | CHA006 | 0.00045352 | 0.00045704 | 0.00046056 | 0.00046408 | 0.0004676 | 0.00047215 | 0.0004767 | 0.00048125 | 0.0004858 | 0.00049035 | 0.0004949 | 0.00049945 | 0.000504 | 0.00050855 | 0.0005131 | 0.00051765 | 0.0005222 | 0.00052675 | 0.0005313 | 0.00053585
| CHA006-155618140 | CHA006 | 0.11383 | 0.1139 | 0.11398 | 0.11405 | 0.11412 | 0.11407 | 0.11401 | 0.11395 | 0.1139 | 0.11384 | 0.11379 | 0.11373 | 0.11367 | 0.11362 | 0.11356 | 0.1135 | 0.11345 | 0.11339 | 0.11334 | 0.11328
| CHA006-155618314 | CHA006 | 0.020321 | 0.020416 | 0.020511 | 0.020606 | 0.020701 | 0.020774 | 0.020847 | 0.020919 | 0.020992 | 0.021065 | 0.021137 | 0.02121 | 0.021282 | 0.021355 | 0.021428 | 0.0215 | 0.021573 | 0.021646 | 0.021718 | 0.021791
| CHA006-155621164 | CHA006 | 0.045638 | 0.045852 | 0.046066 | 0.046279 | 0.046493 | 0.046583 | 0.046674 | 0.046764 | 0.046854 | 0.046944 | 0.047034 | 0.047124 | 0.047215 | 0.047305 | 0.047395 | 0.047485 | 0.047575 | 0.047666 | 0.047756 | 0.047846
| CHA006-155668372 | CHA006 | 0.0026839 | 0.0027067 | 0.0027294 | 0.0027522 | 0.0027749 | 0.0028038 | 0.0028327 | 0.0028616 | 0.0028904 | 0.0029193 | 0.0029482 | 0.0029771 | 0.003006 | 0.0030349 | 0.0030637 | 0.0030926 | 0.0031215 | 0.0031504 | 0.0031793 | 0.0032081
| CHA006-155668704 | CHA006 | 0.0030997 | 0.0031238 | 0.0031478 | 0.0031719 | 0.003196 | 0.0032294 | 0.0032627 | 0.0032961 | 0.0033295 | 0.0033629 | 0.0033963 | 0.0034297 | 0.0034631 | 0.0034965 | 0.0035298 | 0.0035632 | 0.0035966 | 0.00363 | 0.0036634 | 0.0036968
| CHA006-155668831 | CHA006 | 0.017441 | 0.017579 | 0.017717 | 0.017854 | 0.017992 | 0.018123 | 0.018253 | 0.018384 | 0.018514 | 0.018644 | 0.018775 | 0.018905 | 0.019036 | 0.019166 | 0.019296 | 0.019427 | 0.019557 | 0.019688 | 0.019818 | 0.019948
| CHA006-155727138 | CHA006 | 0.0019791 | 0.0019943 | 0.0020095 | 0.0020248 | 0.00204 | 0.0020634 | 0.0020869 | 0.0021103 | 0.0021337 | 0.0021572 | 0.0021806 | 0.002204 | 0.0022274 | 0.0022509 | 0.0022743 | 0.0022977 | 0.0023212 | 0.0023446 | 0.002368 | 0.0023915
| CHA006-155747849 | CHA006 | 0.11696 | 0.11765 | 0.11834 | 0.11903 | 0.11973 | 0.12009 | 0.12044 | 0.1208 | 0.12116 | 0.12152 | 0.12188 | 0.12224 | 0.1226 | 0.12296 | 0.12332 | 0.12368 | 0.12404 | 0.12439 | 0.12475 | 0.12511
| CHA006-156354256 | CHA006 | 0.0038565 | 0.0038821 | 0.0039078 | 0.0039334 | 0.003959 | 0.004013 | 0.004067 | 0.004121 | 0.0041751 | 0.0042291 | 0.0042831 | 0.0043371 | 0.0043911 | 0.0044451 | 0.0044991 | 0.0045531 | 0.0046072 | 0.0046612 | 0.0047152 | 0.0047692
| CHA006-164004018 | CHA006 | 0.018701 | 0.018851 | 0.019001 | 0.019151 | 0.019301 | 0.019507 | 0.019713 | 0.01992 | 0.020126 | 0.020332 | 0.020539 | 0.020745 | 0.020952 | 0.021158 | 0.021364 | 0.021571 | 0.021777 | 0.021983 | 0.02219 | 0.022396
| CHA006-164004212 | CHA006 | 0.0016069 | 0.0016193 | 0.0016316 | 0.001644 | 0.0016564 | 0.0016754 | 0.0016944 | 0.0017134 | 0.0017325 | 0.0017515 | 0.0017705 | 0.0017896 | 0.0018086 | 0.0018276 | 0.0018466 | 0.0018657 | 0.0018847 | 0.0019037 | 0.0019227 | 0.0019418
| CHA006-164004465 | CHA006 | 0.00057641 | 0.00058071 | 0.00058501 | 0.0005893 | 0.0005936 | 0.000602 | 0.0006104 | 0.0006188 | 0.0006272 | 0.0006356 | 0.000644 | 0.0006524 | 0.0006608 | 0.0006692 | 0.0006776 | 0.000686 | 0.0006944 | 0.0007028 | 0.0007112 | 0.0007196
| CHA006-164281123 | CHA006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-181783097 | CHA006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA006-185820630 | CHA006 | 3.0018 | 3.0176 | 3.0333 | 3.049 | 3.0647 | 3.0744 | 3.0842 | 3.0939 | 3.1036 | 3.1133 | 3.123 | 3.1327 | 3.1424 | 3.1522 | 3.1619 | 3.1716 | 3.1813 | 3.191 | 3.2007 | 3.2104
| CHA006-202038162 | CHA006 | 1.8645 | 1.8744 | 1.8843 | 1.8941 | 1.904 | 1.9103 | 1.9167 | 1.923 | 1.9293 | 1.9356 | 1.9419 | 1.9482 | 1.9545 | 1.9608 | 1.9671 | 1.9735 | 1.9798 | 1.9861 | 1.9924 | 1.9987
| CHA006-24606426 | CHA006 | 4.3522 | 4.3635 | 4.3748 | 4.3862 | 4.3975 | 4.4052 | 4.4129 | 4.4207 | 4.4284 | 4.4361 | 4.4438 | 4.4516 | 4.4593 | 4.467 | 4.4747 | 4.4824 | 4.4902 | 4.4979 | 4.5056 | 4.5133
| CHA006-56709766 | CHA006 | 0.022845 | 0.023016 | 0.023186 | 0.023357 | 0.023527 | 0.023859 | 0.024191 | 0.024523 | 0.024854 | 0.025186 | 0.025518 | 0.02585 | 0.026182 | 0.026513 | 0.026845 | 0.027177 | 0.027509 | 0.027841 | 0.028172 | 0.028504
| CHA006-95436119 | CHA006 | 3.739 | 3.7628 | 3.7865 | 3.8103 | 3.8341 | 3.8715 | 3.9088 | 3.9462 | 3.9835 | 4.0209 | 4.0583 | 4.0956 | 4.133 | 4.1704 | 4.2077 | 4.2451 | 4.2824 | 4.3198 | 4.3572 | 4.3945
| CHA007-162618256 | CHA007 | 1.4454e-05 | 1.4566e-05 | 1.4677e-05 | 1.4789e-05 | 1.49e-05 | 1.509e-05 | 1.528e-05 | 1.547e-05 | 1.566e-05 | 1.585e-05 | 1.604e-05 | 1.623e-05 | 1.642e-05 | 1.661e-05 | 1.68e-05 | 1.699e-05 | 1.718e-05 | 1.737e-05 | 1.756e-05 | 1.775e-05
| CHA008-162618131 | CHA008 | 1.1642e-05 | 1.1732e-05 | 1.1821e-05 | 1.1911e-05 | 1.2e-05 | 1.215e-05 | 1.23e-05 | 1.245e-05 | 1.26e-05 | 1.275e-05 | 1.29e-05 | 1.305e-05 | 1.32e-05 | 1.335e-05 | 1.35e-05 | 1.365e-05 | 1.38e-05 | 1.395e-05 | 1.41e-05 | 1.425e-05
| CHM011-15436218 | CHM011 | 7.7143e-06 | 7.7657e-06 | 7.8171e-06 | 7.8686e-06 | 7.92e-06 | 7.914e-06 | 7.908e-06 | 7.902e-06 | 7.896e-06 | 7.89e-06 | 7.884e-06 | 7.878e-06 | 7.872e-06 | 7.866e-06 | 7.86e-06 | 7.854e-06 | 7.848e-06 | 7.842e-06 | 7.836e-06 | 7.83e-06
| CHM011-159371854 | CHM011 | 0.035807 | 0.036022 | 0.036238 | 0.036453 | 0.036669 | 0.036444 | 0.03622 | 0.035995 | 0.035771 | 0.035546 | 0.035322 | 0.035097 | 0.034873 | 0.034648 | 0.034424 | 0.034199 | 0.033975 | 0.03375 | 0.033526 | 0.033301
| CHM011-159371937 | CHM011 | 0.0049465 | 0.0049794 | 0.0050124 | 0.0050453 | 0.0050783 | 0.0050456 | 0.0050128 | 0.0049801 | 0.0049474 | 0.0049147 | 0.0048819 | 0.0048492 | 0.0048165 | 0.0047838 | 0.0047511 | 0.0047183 | 0.0046856 | 0.0046529 | 0.0046202 | 0.0045874
| CHM011-159372020 | CHM011 | 0.1102 | 0.11083 | 0.11146 | 0.11209 | 0.11272 | 0.11205 | 0.11139 | 0.11073 | 0.11006 | 0.1094 | 0.10874 | 0.10808 | 0.10741 | 0.10675 | 0.10609 | 0.10542 | 0.10476 | 0.1041 | 0.10344 | 0.10277
| CHM011-159372116 | CHM011 | 0.0117 | 0.011772 | 0.011844 | 0.011916 | 0.011988 | 0.011914 | 0.011839 | 0.011764 | 0.01169 | 0.011615 | 0.01154 | 0.011466 | 0.011391 | 0.011316 | 0.011242 | 0.011167 | 0.011092 | 0.011017 | 0.010943 | 0.010868
| CHM011-159372219 | CHM011 | 0.088855 | 0.089313 | 0.089771 | 0.09023 | 0.090688 | 0.090193 | 0.089697 | 0.089202 | 0.088706 | 0.088211 | 0.087715 | 0.08722 | 0.086724 | 0.086229 | 0.085734 | 0.085238 | 0.084743 | 0.084247 | 0.083752 | 0.083256
| CHM011-159372384 | CHM011 | 0.01258 | 0.012651 | 0.012723 | 0.012794 | 0.012865 | 0.012803 | 0.012741 | 0.01268 | 0.012618 | 0.012556 | 0.012494 | 0.012432 | 0.01237 | 0.012308 | 0.012247 | 0.012185 | 0.012123 | 0.012061 | 0.011999 | 0.011937
| CHM011-159372472 | CHM011 | 0.0038911 | 0.0039106 | 0.0039302 | 0.0039498 | 0.0039693 | 0.0039494 | 0.0039294 | 0.0039095 | 0.0038895 | 0.0038695 | 0.0038496 | 0.0038296 | 0.0038097 | 0.0037897 | 0.0037697 | 0.0037498 | 0.0037298 | 0.0037099 | 0.0036899 | 0.0036699
| CHM011-159372576 | CHM011 | 0.030201 | 0.030376 | 0.030551 | 0.030726 | 0.030902 | 0.030718 | 0.030534 | 0.03035 | 0.030166 | 0.029982 | 0.029798 | 0.029614 | 0.02943 | 0.029246 | 0.029063 | 0.028879 | 0.028695 | 0.028511 | 0.028327 | 0.028143
| CHM011-159372815 | CHM011 | 0.00033572 | 0.00033814 | 0.00034056 | 0.00034298 | 0.0003454 | 0.00034276 | 0.00034012 | 0.00033748 | 0.00033484 | 0.0003322 | 0.00032956 | 0.00032692 | 0.00032428 | 0.00032164 | 0.000319 | 0.00031636 | 0.00031372 | 0.00031108 | 0.00030844 | 0.0003058
| CHM011-159372981 | CHM011 | 0.017015 | 0.0171 | 0.017185 | 0.01727 | 0.017355 | 0.017251 | 0.017147 | 0.017043 | 0.016938 | 0.016834 | 0.01673 | 0.016625 | 0.016521 | 0.016417 | 0.016313 | 0.016208 | 0.016104 | 0.016 | 0.015896 | 0.015791
| CHM011-159373200 | CHM011 | 0.076187 | 0.076622 | 0.077058 | 0.077494 | 0.077929 | 0.07742 | 0.076911 | 0.076402 | 0.075892 | 0.075383 | 0.074874 | 0.074364 | 0.073855 | 0.073346 | 0.072837 | 0.072327 | 0.071818 | 0.071309 | 0.070799 | 0.07029
| CHM011-159373315 | CHM011 | 0.0041733 | 0.0041953 | 0.0042172 | 0.0042392 | 0.0042612 | 0.0042341 | 0.004207 | 0.00418 | 0.0041529 | 0.0041258 | 0.0040988 | 0.0040717 | 0.0040446 | 0.0040176 | 0.0039905 | 0.0039634 | 0.0039364 | 0.0039093 | 0.0038822 | 0.0038552
| CHM011-159373411 | CHM011 | 0.0067318 | 0.006772 | 0.0068122 | 0.0068524 | 0.0068926 | 0.0068564 | 0.0068202 | 0.0067841 | 0.0067479 | 0.0067118 | 0.0066756 | 0.0066395 | 0.0066033 | 0.0065671 | 0.006531 | 0.0064948 | 0.0064587 | 0.0064225 | 0.0063863 | 0.0063502
| CHM011-160317885 | CHM011 | 0.03315 | 0.033322 | 0.033494 | 0.033666 | 0.033839 | 0.033667 | 0.033496 | 0.033324 | 0.033153 | 0.032982 | 0.03281 | 0.032639 | 0.032467 | 0.032296 | 0.032125 | 0.031953 | 0.031782 | 0.031611 | 0.031439 | 0.031268
| CHM011-160318163 | CHM011 | 0.00012646 | 0.00012735 | 0.00012825 | 0.00012915 | 0.00013005 | 0.00012917 | 0.0001283 | 0.00012742 | 0.00012655 | 0.00012567 | 0.0001248 | 0.00012392 | 0.00012305 | 0.00012217 | 0.00012129 | 0.00012042 | 0.00011954 | 0.00011867 | 0.00011779 | 0.00011692
| CHM011-160318338 | CHM011 | 0.0027712 | 0.0027887 | 0.0028063 | 0.0028239 | 0.0028415 | 0.0028221 | 0.0028027 | 0.0027832 | 0.0027638 | 0.0027444 | 0.002725 | 0.0027056 | 0.0026862 | 0.0026667 | 0.0026473 | 0.0026279 | 0.0026085 | 0.0025891 | 0.0025697 | 0.0025503
| CHM011-160677964 | CHM011 | 0.046749 | 0.047033 | 0.047317 | 0.047601 | 0.047885 | 0.04763 | 0.047375 | 0.04712 | 0.046865 | 0.046611 | 0.046356 | 0.046101 | 0.045846 | 0.045591 | 0.045336 | 0.045081 | 0.044826 | 0.044571 | 0.044316 | 0.044062
| CHM011-160678238 | CHM011 | 0.041363 | 0.041578 | 0.041793 | 0.042008 | 0.042223 | 0.041985 | 0.041747 | 0.041508 | 0.04127 | 0.041031 | 0.040793 | 0.040554 | 0.040316 | 0.040078 | 0.039839 | 0.039601 | 0.039362 | 0.039124 | 0.038885 | 0.038647
| CHM011-160721783 | CHM011 | 0.00023411 | 0.00023571 | 0.00023731 | 0.0002389 | 0.0002405 | 0.00023887 | 0.00023725 | 0.00023562 | 0.000234 | 0.00023237 | 0.00023075 | 0.00022912 | 0.0002275 | 0.00022587 | 0.00022425 | 0.00022263 | 0.000221 | 0.00021938 | 0.00021775 | 0.00021613
| CHM011-163177271 | CHM011 | 0.0064558 | 0.0065036 | 0.0065514 | 0.0065992 | 0.006647 | 0.0065942 | 0.0065415 | 0.0064887 | 0.0064359 | 0.0063831 | 0.0063303 | 0.0062776 | 0.0062248 | 0.006172 | 0.0061192 | 0.0060664 | 0.0060137 | 0.0059609 | 0.0059081 | 0.0058553
| CHM011-163198394 | CHM011 | 0.018797 | 0.018897 | 0.018997 | 0.019097 | 0.019197 | 0.019061 | 0.018924 | 0.018788 | 0.018652 | 0.018516 | 0.018379 | 0.018243 | 0.018107 | 0.017971 | 0.017834 | 0.017698 | 0.017562 | 0.017426 | 0.017289 | 0.017153
| CHM011-163198509 | CHM011 | 0.2988 | 0.30054 | 0.30228 | 0.30402 | 0.30576 | 0.30413 | 0.30249 | 0.30085 | 0.29922 | 0.29758 | 0.29594 | 0.2943 | 0.29267 | 0.29103 | 0.28939 | 0.28776 | 0.28612 | 0.28448 | 0.28285 | 0.28121
| CHM011-163310655 | CHM011 | 0.14162 | 0.14252 | 0.14342 | 0.14432 | 0.14522 | 0.14426 | 0.1433 | 0.14235 | 0.14139 | 0.14044 | 0.13948 | 0.13853 | 0.13757 | 0.13661 | 0.13566 | 0.1347 | 0.13375 | 0.13279 | 0.13184 | 0.13088
| CHM011-164238923 | CHM011 | 0.00022194 | 0.00022346 | 0.00022497 | 0.00022649 | 0.000228 | 0.00022615 | 0.0002243 | 0.00022245 | 0.0002206 | 0.00021875 | 0.0002169 | 0.00021505 | 0.0002132 | 0.00021135 | 0.0002095 | 0.00020765 | 0.0002058 | 0.00020395 | 0.0002021 | 0.00020025
| CHM011-164366730 | CHM011 | 0.0084031 | 0.008452 | 0.0085008 | 0.0085497 | 0.0085986 | 0.0085467 | 0.0084949 | 0.008443 | 0.0083912 | 0.0083393 | 0.0082875 | 0.0082356 | 0.0081837 | 0.0081319 | 0.00808 | 0.0080282 | 0.0079763 | 0.0079245 | 0.0078726 | 0.0078208
| CHM011-187119686 | CHM011 | 21.0675 | 21.1724 | 21.2772 | 21.3821 | 21.487 | 21.3851 | 21.2832 | 21.1814 | 21.0795 | 20.9776 | 20.8758 | 20.7739 | 20.672 | 20.5701 | 20.4683 | 20.3664 | 20.2645 | 20.1627 | 20.0608 | 19.9589
| CHM011-24600428 | CHM011 | 1.5518 | 1.5595 | 1.5673 | 1.575 | 1.5827 | 1.5744 | 1.5661 | 1.5578 | 1.5495 | 1.5411 | 1.5328 | 1.5245 | 1.5162 | 1.5079 | 1.4996 | 1.4913 | 1.483 | 1.4746 | 1.4663 | 1.458
| CHM011-24600540 | CHM011 | 4.2593 | 4.2838 | 4.3083 | 4.3327 | 4.3572 | 4.3332 | 4.3091 | 4.2851 | 4.261 | 4.2369 | 4.2129 | 4.1888 | 4.1648 | 4.1407 | 4.1166 | 4.0926 | 4.0685 | 4.0444 | 4.0204 | 3.9963
| CLC001-15400682 | CLC001 | 0.97255 | 0.97398 | 0.97542 | 0.97686 | 0.97829 | 0.97645 | 0.97461 | 0.97277 | 0.97093 | 0.96909 | 0.96725 | 0.96541 | 0.96357 | 0.96174 | 0.9599 | 0.95806 | 0.95622 | 0.95438 | 0.95254 | 0.9507
| CLC001-15400693 | CLC001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC002-15400645 | CLC002 | 7.0767 | 7.0845 | 7.0923 | 7.1001 | 7.1079 | 7.0955 | 7.0831 | 7.0706 | 7.0582 | 7.0458 | 7.0333 | 7.0209 | 7.0085 | 6.996 | 6.9836 | 6.9711 | 6.9587 | 6.9463 | 6.9338 | 6.9214
| CLC003-119149948 | CLC003 | 0.0046904 | 0.0047501 | 0.0048097 | 0.0048693 | 0.0049289 | 0.0048507 | 0.0047724 | 0.0046941 | 0.0046159 | 0.0045376 | 0.0044593 | 0.004381 | 0.0043028 | 0.0042245 | 0.0041462 | 0.004068 | 0.0039897 | 0.0039114 | 0.0038331 | 0.0037549
| CLC003-123633044 | CLC003 | 0.013955 | 0.014072 | 0.014189 | 0.014307 | 0.014424 | 0.014256 | 0.014089 | 0.013921 | 0.013754 | 0.013587 | 0.013419 | 0.013252 | 0.013084 | 0.012917 | 0.012749 | 0.012582 | 0.012414 | 0.012247 | 0.01208 | 0.011912
| CLC003-130014430 | CLC003 | 0.0001463 | 0.00014842 | 0.00015055 | 0.00015267 | 0.0001548 | 0.00015294 | 0.00015108 | 0.00014922 | 0.00014736 | 0.0001455 | 0.00014364 | 0.00014178 | 0.00013992 | 0.00013806 | 0.0001362 | 0.00013434 | 0.00013248 | 0.00013062 | 0.00012876 | 0.0001269
| CLC003-130014725 | CLC003 | 0.0012008 | 0.0012236 | 0.0012464 | 0.0012692 | 0.001292 | 0.0012627 | 0.0012335 | 0.0012042 | 0.001175 | 0.0011457 | 0.0011164 | 0.0010872 | 0.0010579 | 0.0010287 | 0.0009994 | 0.00097014 | 0.00094088 | 0.00091162 | 0.00088236 | 0.0008531
| CLC003-130014949 | CLC003 | 0.0037333 | 0.0037837 | 0.0038341 | 0.0038845 | 0.0039349 | 0.00389 | 0.0038452 | 0.0038003 | 0.0037555 | 0.0037106 | 0.0036658 | 0.0036209 | 0.0035761 | 0.0035312 | 0.0034864 | 0.0034415 | 0.0033967 | 0.0033518 | 0.0033069 | 0.0032621
| CLC003-130747301 | CLC003 | 0.0058191 | 0.0059032 | 0.0059872 | 0.0060712 | 0.0061553 | 0.0060805 | 0.0060058 | 0.005931 | 0.0058562 | 0.0057815 | 0.0057067 | 0.005632 | 0.0055572 | 0.0054824 | 0.0054077 | 0.0053329 | 0.0052582 | 0.0051834 | 0.0051086 | 0.0050339
| CLC003-130748256 | CLC003 | 0.0062733 | 0.0063381 | 0.0064028 | 0.0064676 | 0.0065323 | 0.0064514 | 0.0063704 | 0.0062895 | 0.0062086 | 0.0061276 | 0.0060467 | 0.0059657 | 0.0058848 | 0.0058039 | 0.0057229 | 0.005642 | 0.0055611 | 0.0054801 | 0.0053992 | 0.0053183
| CLC003-152030196 | CLC003 | 0.024238 | 0.024304 | 0.024371 | 0.024437 | 0.024504 | 0.024361 | 0.024219 | 0.024076 | 0.023934 | 0.023791 | 0.023648 | 0.023506 | 0.023363 | 0.02322 | 0.023078 | 0.022935 | 0.022792 | 0.02265 | 0.022507 | 0.022365
| CLC003-15400758 | CLC003 | 31.1319 | 31.3438 | 31.5558 | 31.7677 | 31.9797 | 31.7309 | 31.4822 | 31.2335 | 30.9848 | 30.7361 | 30.4873 | 30.2386 | 29.9899 | 29.7412 | 29.4925 | 29.2437 | 28.995 | 28.7463 | 28.4976 | 28.2489
| CLC003-154876479 | CLC003 | 0.0019078 | 0.0019209 | 0.001934 | 0.001947 | 0.0019601 | 0.0019544 | 0.0019487 | 0.001943 | 0.0019372 | 0.0019315 | 0.0019258 | 0.0019201 | 0.0019143 | 0.0019086 | 0.0019029 | 0.0018972 | 0.0018914 | 0.0018857 | 0.00188 | 0.0018743
| CLC003-154908324 | CLC003 | 0.070032 | 0.070206 | 0.070381 | 0.070555 | 0.070729 | 0.070354 | 0.069978 | 0.069603 | 0.069227 | 0.068851 | 0.068476 | 0.0681 | 0.067725 | 0.067349 | 0.066973 | 0.066598 | 0.066222 | 0.065847 | 0.065471 | 0.065095
| CLC003-154908634 | CLC003 | 0.00052533 | 0.00053019 | 0.00053506 | 0.00053993 | 0.0005448 | 0.00054344 | 0.00054208 | 0.00054072 | 0.00053936 | 0.000538 | 0.00053664 | 0.00053528 | 0.00053392 | 0.00053256 | 0.0005312 | 0.00052984 | 0.00052848 | 0.00052712 | 0.00052576 | 0.0005244
| CLC003-154908755 | CLC003 | 0.00023512 | 0.00023794 | 0.00024076 | 0.00024358 | 0.0002464 | 0.00024318 | 0.00023996 | 0.00023674 | 0.00023352 | 0.0002303 | 0.00022708 | 0.00022386 | 0.00022064 | 0.00021742 | 0.0002142 | 0.00021098 | 0.00020776 | 0.00020454 | 0.00020132 | 0.0001981
| CLC003-154908853 | CLC003 | 0.0016691 | 0.0016838 | 0.0016985 | 0.0017131 | 0.0017278 | 0.0017183 | 0.0017088 | 0.0016993 | 0.0016898 | 0.0016802 | 0.0016707 | 0.0016612 | 0.0016517 | 0.0016422 | 0.0016327 | 0.0016232 | 0.0016137 | 0.0016042 | 0.0015947 | 0.0015851
| CLC003-154908977 | CLC003 | 0.042845 | 0.043207 | 0.043569 | 0.04393 | 0.044292 | 0.043994 | 0.043696 | 0.043399 | 0.043101 | 0.042803 | 0.042505 | 0.042208 | 0.04191 | 0.041612 | 0.041314 | 0.041017 | 0.040719 | 0.040421 | 0.040123 | 0.039826
| CLC003-193886326 | CLC003 | 0.41101 | 0.41531 | 0.41961 | 0.42391 | 0.4282 | 0.42262 | 0.41703 | 0.41144 | 0.40585 | 0.40026 | 0.39467 | 0.38908 | 0.38349 | 0.3779 | 0.37231 | 0.36672 | 0.36113 | 0.35555 | 0.34996 | 0.34437
| CLC003-198593463 | CLC003 | 0.23982 | 0.24171 | 0.24359 | 0.24548 | 0.24736 | 0.24392 | 0.24048 | 0.23705 | 0.23361 | 0.23017 | 0.22673 | 0.2233 | 0.21986 | 0.21642 | 0.21298 | 0.20955 | 0.20611 | 0.20267 | 0.19923 | 0.19579
| CLC003-24597492 | CLC003 | 3.746 | 3.7814 | 3.8168 | 3.8522 | 3.8875 | 3.8348 | 3.7821 | 3.7293 | 3.6766 | 3.6238 | 3.5711 | 3.5183 | 3.4656 | 3.4129 | 3.3601 | 3.3074 | 3.2546 | 3.2019 | 3.1491 | 3.0964
| CLC003-24597520 | CLC003 | 0.86668 | 0.87281 | 0.87895 | 0.88509 | 0.89123 | 0.87961 | 0.868 | 0.85638 | 0.84477 | 0.83315 | 0.82154 | 0.80992 | 0.79831 | 0.78669 | 0.77508 | 0.76347 | 0.75185 | 0.74024 | 0.72862 | 0.71701
| CLC003-24597576 | CLC003 | 1.2633 | 1.277 | 1.2906 | 1.3043 | 1.318 | 1.2974 | 1.2769 | 1.2564 | 1.2359 | 1.2154 | 1.1948 | 1.1743 | 1.1538 | 1.1333 | 1.1128 | 1.0922 | 1.0717 | 1.0512 | 1.0307 | 1.0101
| CLC003-24607110 | CLC003 | 3.6858 | 3.6954 | 3.705 | 3.7146 | 3.7243 | 3.7036 | 3.6828 | 3.6621 | 3.6414 | 3.6206 | 3.5999 | 3.5792 | 3.5584 | 3.5377 | 3.517 | 3.4963 | 3.4755 | 3.4548 | 3.4341 | 3.4133
| CLC003-24607264 | CLC003 | 1.5684 | 1.5847 | 1.601 | 1.6173 | 1.6336 | 1.6142 | 1.5947 | 1.5753 | 1.5559 | 1.5365 | 1.517 | 1.4976 | 1.4782 | 1.4587 | 1.4393 | 1.4199 | 1.4004 | 1.381 | 1.3616 | 1.3421
| CLC003-24613704 | CLC003 | 0.2442 | 0.24633 | 0.24846 | 0.2506 | 0.25273 | 0.24979 | 0.24685 | 0.24391 | 0.24098 | 0.23804 | 0.2351 | 0.23216 | 0.22922 | 0.22629 | 0.22335 | 0.22041 | 0.21747 | 0.21453 | 0.21159 | 0.20866
| CLC003-78545961 | CLC003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC003-80120806 | CLC003 | 0.0088237 | 0.0089036 | 0.0089835 | 0.0090633 | 0.0091432 | 0.0090697 | 0.0089962 | 0.0089227 | 0.0088492 | 0.0087757 | 0.0087022 | 0.0086287 | 0.0085552 | 0.0084817 | 0.0084082 | 0.0083347 | 0.0082612 | 0.0081877 | 0.0081142 | 0.0080407
| CLC003-80121007 | CLC003 | 0.00031174 | 0.00031518 | 0.00031862 | 0.00032206 | 0.0003255 | 0.00032287 | 0.00032025 | 0.00031762 | 0.000315 | 0.00031237 | 0.00030975 | 0.00030712 | 0.0003045 | 0.00030187 | 0.00029925 | 0.00029662 | 0.000294 | 0.00029137 | 0.00028875 | 0.00028612
| CLC003-80919181 | CLC003 | 0.27795 | 0.28076 | 0.28357 | 0.28638 | 0.28919 | 0.28642 | 0.28365 | 0.28087 | 0.2781 | 0.27533 | 0.27255 | 0.26978 | 0.26701 | 0.26423 | 0.26146 | 0.25869 | 0.25591 | 0.25314 | 0.25037 | 0.2476
| CLC004-15400582 | CLC004 | 16.3219 | 16.4455 | 16.5691 | 16.6927 | 16.8164 | 16.7428 | 16.6693 | 16.5958 | 16.5223 | 16.4488 | 16.3753 | 16.3018 | 16.2283 | 16.1548 | 16.0813 | 16.0078 | 15.9343 | 15.8608 | 15.7873 | 15.7138
| CLC004-176886107 | CLC004 | 0.0010129 | 0.0010229 | 0.0010329 | 0.001043 | 0.001053 | 0.0010504 | 0.0010479 | 0.0010453 | 0.0010427 | 0.0010402 | 0.0010376 | 0.001035 | 0.0010325 | 0.0010299 | 0.0010274 | 0.0010248 | 0.0010222 | 0.0010197 | 0.0010171 | 0.0010145
| CLC004-201015049 | CLC004 | 1.2637 | 1.2744 | 1.2851 | 1.2959 | 1.3066 | 1.2993 | 1.292 | 1.2847 | 1.2774 | 1.2702 | 1.2629 | 1.2556 | 1.2483 | 1.241 | 1.2337 | 1.2264 | 1.2191 | 1.2118 | 1.2045 | 1.1972
| CLC004-24597506 | CLC004 | 3.7056 | 3.7296 | 3.7537 | 3.7778 | 3.8019 | 3.784 | 3.766 | 3.7481 | 3.7302 | 3.7123 | 3.6944 | 3.6765 | 3.6586 | 3.6406 | 3.6227 | 3.6048 | 3.5869 | 3.569 | 3.5511 | 3.5331
| CLC006-142438034 | CLC006 | 0.0028372 | 0.002873 | 0.0029087 | 0.0029445 | 0.0029803 | 0.0029803 | 0.0029803 | 0.0029803 | 0.0029803 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029801 | 0.0029801
| CLC006-142438492 | CLC006 | 0.030719 | 0.030892 | 0.031065 | 0.031238 | 0.031411 | 0.031367 | 0.031323 | 0.031279 | 0.031235 | 0.031191 | 0.031147 | 0.031103 | 0.031059 | 0.031015 | 0.030971 | 0.030927 | 0.030884 | 0.03084 | 0.030796 | 0.030752
| CLC006-144337956 | CLC006 | 0.068388 | 0.068967 | 0.069545 | 0.070123 | 0.070702 | 0.070356 | 0.07001 | 0.069664 | 0.069319 | 0.068973 | 0.068627 | 0.068281 | 0.067935 | 0.067589 | 0.067243 | 0.066898 | 0.066552 | 0.066206 | 0.06586 | 0.065514
| CLC006-144337978 | CLC006 | 0.017387 | 0.017526 | 0.017665 | 0.017804 | 0.017944 | 0.017914 | 0.017885 | 0.017855 | 0.017826 | 0.017797 | 0.017767 | 0.017738 | 0.017709 | 0.017679 | 0.01765 | 0.01762 | 0.017591 | 0.017562 | 0.017532 | 0.017503
| CLC006-15400532 | CLC006 | 11.4739 | 11.5145 | 11.5551 | 11.5958 | 11.6364 | 11.6037 | 11.5711 | 11.5384 | 11.5057 | 11.4731 | 11.4404 | 11.4078 | 11.3751 | 11.3425 | 11.3098 | 11.2771 | 11.2445 | 11.2118 | 11.1792 | 11.1465
| CLC006-154827505 | CLC006 | 0.00034365 | 0.00034803 | 0.00035242 | 0.00035681 | 0.0003612 | 0.00036102 | 0.00036084 | 0.00036066 | 0.00036048 | 0.0003603 | 0.00036012 | 0.00035994 | 0.00035976 | 0.00035958 | 0.0003594 | 0.00035922 | 0.00035904 | 0.00035886 | 0.00035868 | 0.0003585
| CLC006-154827674 | CLC006 | 0.022834 | 0.023058 | 0.023281 | 0.023505 | 0.023728 | 0.023591 | 0.023454 | 0.023317 | 0.02318 | 0.023043 | 0.022906 | 0.022769 | 0.022632 | 0.022495 | 0.022359 | 0.022222 | 0.022085 | 0.021948 | 0.021811 | 0.021674
| CLC006-154827847 | CLC006 | 0.0050121 | 0.0050126 | 0.0050132 | 0.0050137 | 0.0050142 | 0.005013 | 0.0050119 | 0.0050107 | 0.0050095 | 0.0050083 | 0.0050071 | 0.0050059 | 0.0050047 | 0.0050035 | 0.0050023 | 0.0050011 | 0.005 | 0.0049988 | 0.0049976 | 0.0049964
| CLC006-154828072 | CLC006 | 0.037031 | 0.037367 | 0.037703 | 0.038039 | 0.038375 | 0.038218 | 0.038062 | 0.037906 | 0.037749 | 0.037593 | 0.037437 | 0.03728 | 0.037124 | 0.036968 | 0.036811 | 0.036655 | 0.036499 | 0.036343 | 0.036186 | 0.03603
| CLC006-154828287 | CLC006 | 0.028491 | 0.028849 | 0.029207 | 0.029564 | 0.029922 | 0.029802 | 0.029683 | 0.029563 | 0.029443 | 0.029324 | 0.029204 | 0.029084 | 0.028965 | 0.028845 | 0.028725 | 0.028606 | 0.028486 | 0.028366 | 0.028246 | 0.028127
| CLC006-154828396 | CLC006 | 0.098675 | 0.099885 | 0.1011 | 0.10231 | 0.10352 | 0.10311 | 0.10271 | 0.10231 | 0.10191 | 0.10151 | 0.10111 | 0.10071 | 0.10031 | 0.099908 | 0.099508 | 0.099107 | 0.098706 | 0.098305 | 0.097905 | 0.097504
| CLC006-154907356 | CLC006 | 0.0081171 | 0.0082026 | 0.0082881 | 0.0083736 | 0.008459 | 0.0084374 | 0.0084158 | 0.0083942 | 0.0083725 | 0.0083509 | 0.0083293 | 0.0083077 | 0.008286 | 0.0082644 | 0.0082428 | 0.0082212 | 0.0081996 | 0.0081779 | 0.0081563 | 0.0081347
| CLC006-156831394 | CLC006 | 4.1972 | 4.2411 | 4.2849 | 4.3288 | 4.3726 | 4.3622 | 4.3519 | 4.3415 | 4.3311 | 4.3208 | 4.3104 | 4.3 | 4.2897 | 4.2793 | 4.2689 | 4.2586 | 4.2482 | 4.2378 | 4.2275 | 4.2171
| CLC006-44811375 | CLC006 | 1.4763 | 1.4909 | 1.5055 | 1.52 | 1.5346 | 1.5306 | 1.5266 | 1.5226 | 1.5186 | 1.5146 | 1.5106 | 1.5065 | 1.5025 | 1.4985 | 1.4945 | 1.4905 | 1.4865 | 1.4825 | 1.4785 | 1.4745
| CLC006-80819775 | CLC006 | 0.17815 | 0.18015 | 0.18216 | 0.18416 | 0.18617 | 0.18551 | 0.18485 | 0.18419 | 0.18352 | 0.18286 | 0.1822 | 0.18154 | 0.18088 | 0.18022 | 0.17955 | 0.17889 | 0.17823 | 0.17757 | 0.17691 | 0.17624
| CLC006-80819849 | CLC006 | 0.04054 | 0.041086 | 0.041633 | 0.042179 | 0.042725 | 0.042555 | 0.042385 | 0.042215 | 0.042045 | 0.041874 | 0.041704 | 0.041534 | 0.041364 | 0.041194 | 0.041024 | 0.040854 | 0.040684 | 0.040513 | 0.040343 | 0.040173
| CLC013-120141536 | CLC013 | 0.066737 | 0.067457 | 0.068176 | 0.068896 | 0.069616 | 0.068892 | 0.068168 | 0.067445 | 0.066721 | 0.065997 | 0.065273 | 0.064549 | 0.063826 | 0.063102 | 0.062378 | 0.061654 | 0.060931 | 0.060207 | 0.059483 | 0.058759
| CLC013-155048935 | CLC013 | 0.00095362 | 0.0009613 | 0.00096899 | 0.00097667 | 0.00098435 | 0.00098184 | 0.00097933 | 0.00097683 | 0.00097432 | 0.00097181 | 0.00096931 | 0.0009668 | 0.00096429 | 0.00096179 | 0.00095928 | 0.00095677 | 0.00095426 | 0.00095176 | 0.00094925 | 0.00094674
| CLC013-155049125 | CLC013 | 0.1077 | 0.10837 | 0.10904 | 0.10972 | 0.11039 | 0.10993 | 0.10947 | 0.10901 | 0.10855 | 0.10809 | 0.10762 | 0.10716 | 0.1067 | 0.10624 | 0.10578 | 0.10532 | 0.10486 | 0.1044 | 0.10394 | 0.10348
| CLC013-155049446 | CLC013 | 0.033904 | 0.034267 | 0.03463 | 0.034992 | 0.035355 | 0.0351 | 0.034845 | 0.034589 | 0.034334 | 0.034079 | 0.033824 | 0.033569 | 0.033313 | 0.033058 | 0.032803 | 0.032548 | 0.032292 | 0.032037 | 0.031782 | 0.031527
| CLC013-155049582 | CLC013 | 0.012793 | 0.013011 | 0.013229 | 0.013447 | 0.013665 | 0.013364 | 0.013063 | 0.012761 | 0.01246 | 0.012159 | 0.011858 | 0.011556 | 0.011255 | 0.010954 | 0.010653 | 0.010352 | 0.01005 | 0.0097491 | 0.0094479 | 0.0091467
| CLC013-155079387 | CLC013 | 0.0031291 | 0.0031653 | 0.0032015 | 0.0032376 | 0.0032738 | 0.0032281 | 0.0031823 | 0.0031366 | 0.0030909 | 0.0030452 | 0.0029995 | 0.0029538 | 0.0029081 | 0.0028624 | 0.0028167 | 0.0027709 | 0.0027252 | 0.0026795 | 0.0026338 | 0.0025881
| CLC013-155079659 | CLC013 | 0.029883 | 0.030177 | 0.030471 | 0.030765 | 0.031058 | 0.030875 | 0.030691 | 0.030508 | 0.030324 | 0.030141 | 0.029957 | 0.029774 | 0.02959 | 0.029406 | 0.029223 | 0.029039 | 0.028856 | 0.028672 | 0.028489 | 0.028305
| CLC013-161744857 | CLC013 | 35.7129 | 35.9291 | 36.1453 | 36.3615 | 36.5777 | 36.3942 | 36.2107 | 36.0273 | 35.8438 | 35.6603 | 35.4768 | 35.2933 | 35.1098 | 34.9263 | 34.7429 | 34.5594 | 34.3759 | 34.1924 | 34.0089 | 33.8254
| CLC013-24598538 | CLC013 | 0.08382 | 0.08453 | 0.085239 | 0.085949 | 0.086658 | 0.086158 | 0.085658 | 0.085158 | 0.084657 | 0.084157 | 0.083657 | 0.083157 | 0.082657 | 0.082157 | 0.081657 | 0.081156 | 0.080656 | 0.080156 | 0.079656 | 0.079156
| CLC013-24598566 | CLC013 | 0.17758 | 0.17869 | 0.17979 | 0.1809 | 0.182 | 0.18122 | 0.18043 | 0.17964 | 0.17885 | 0.17807 | 0.17728 | 0.17649 | 0.1757 | 0.17491 | 0.17413 | 0.17334 | 0.17255 | 0.17176 | 0.17097 | 0.17019
| CLC013-24602770 | CLC013 | 5.8443 | 5.9141 | 5.9839 | 6.0536 | 6.1234 | 6.0294 | 5.9355 | 5.8415 | 5.7475 | 5.6536 | 5.5596 | 5.4656 | 5.3716 | 5.2777 | 5.1837 | 5.0897 | 4.9958 | 4.9018 | 4.8078 | 4.7139
| CLC013-24602784 | CLC013 | 6.5474 | 6.6089 | 6.6704 | 6.7319 | 6.7933 | 6.7053 | 6.6172 | 6.5292 | 6.4411 | 6.353 | 6.265 | 6.1769 | 6.0889 | 6.0008 | 5.9127 | 5.8247 | 5.7366 | 5.6486 | 5.5605 | 5.4725
| CLC013-40996443 | CLC013 | 14.4298 | 14.4617 | 14.4936 | 14.5255 | 14.5574 | 14.489 | 14.4206 | 14.3523 | 14.2839 | 14.2156 | 14.1472 | 14.0788 | 14.0105 | 13.9421 | 13.8738 | 13.8054 | 13.737 | 13.6687 | 13.6003 | 13.5319
| CLC013-77737876 | CLC013 | 0.0017487 | 0.0017571 | 0.0017655 | 0.0017738 | 0.0017822 | 0.0017764 | 0.0017706 | 0.0017647 | 0.0017589 | 0.0017531 | 0.0017472 | 0.0017414 | 0.0017356 | 0.0017298 | 0.0017239 | 0.0017181 | 0.0017123 | 0.0017065 | 0.0017006 | 0.0016948
| CLC013-77738225 | CLC013 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395
| CLC014-119350337 | CLC014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC014-161744928 | CLC014 | 21.6312 | 21.8019 | 21.9726 | 22.1433 | 22.3139 | 22.1925 | 22.0711 | 21.9496 | 21.8282 | 21.7067 | 21.5853 | 21.4638 | 21.3424 | 21.221 | 21.0995 | 20.9781 | 20.8566 | 20.7352 | 20.6137 | 20.4923
| CME014-15423823 | CME014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME014-15423849 | CME014 | 169.8191 | 170.6824 | 171.5457 | 172.4091 | 173.2724 | 174.0323 | 174.7921 | 175.552 | 176.3119 | 177.0717 | 177.8316 | 178.5914 | 179.3513 | 180.1112 | 180.871 | 181.6309 | 182.3908 | 183.1506 | 183.9105 | 184.6704
| CME014-24612269 | CME014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME015-15423773 | CME015 | 5.1516 | 5.1895 | 5.2275 | 5.2655 | 5.3034 | 5.3348 | 5.3661 | 5.3975 | 5.4289 | 5.4602 | 5.4916 | 5.523 | 5.5543 | 5.5857 | 5.6171 | 5.6484 | 5.6798 | 5.7112 | 5.7425 | 5.7739
| CME015-182988165 | CME015 | 9.7716 | 9.8314 | 9.8913 | 9.9512 | 10.0111 | 10.0632 | 10.1153 | 10.1674 | 10.2195 | 10.2716 | 10.3237 | 10.3758 | 10.4279 | 10.48 | 10.5321 | 10.5843 | 10.6364 | 10.6885 | 10.7406 | 10.7927
| CME016-142932211 | CME016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME016-142932557 | CME016 | 0.050781 | 0.051092 | 0.051403 | 0.051715 | 0.052026 | 0.052422 | 0.052819 | 0.053216 | 0.053612 | 0.054009 | 0.054406 | 0.054802 | 0.055199 | 0.055595 | 0.055992 | 0.056389 | 0.056785 | 0.057182 | 0.057578 | 0.057975
| CME016-142932825 | CME016 | 0.03518 | 0.035414 | 0.035647 | 0.03588 | 0.036113 | 0.036299 | 0.036486 | 0.036672 | 0.036858 | 0.037044 | 0.03723 | 0.037416 | 0.037602 | 0.037788 | 0.037974 | 0.03816 | 0.038346 | 0.038532 | 0.038718 | 0.038904
| CME016-142933135 | CME016 | 0.085005 | 0.085505 | 0.086004 | 0.086504 | 0.087003 | 0.087807 | 0.08861 | 0.089414 | 0.090217 | 0.091021 | 0.091824 | 0.092628 | 0.093431 | 0.094235 | 0.095038 | 0.095842 | 0.096645 | 0.097449 | 0.098252 | 0.099056
| CME016-154143626 | CME016 | 3.1758 | 3.1899 | 3.204 | 3.2181 | 3.2322 | 3.2675 | 3.3029 | 3.3383 | 3.3737 | 3.409 | 3.4444 | 3.4798 | 3.5151 | 3.5505 | 3.5859 | 3.6213 | 3.6566 | 3.692 | 3.7274 | 3.7627
| CME016-15423749 | CME016 | 122.858 | 123.4715 | 124.085 | 124.6985 | 125.312 | 125.8108 | 126.3095 | 126.8083 | 127.3071 | 127.8059 | 128.3046 | 128.8034 | 129.3022 | 129.801 | 130.2997 | 130.7985 | 131.2973 | 131.7961 | 132.2948 | 132.7936
| CME016-163066872 | CME016 | 0.0012425 | 0.0012535 | 0.0012645 | 0.0012754 | 0.0012864 | 0.001303 | 0.0013195 | 0.0013361 | 0.0013526 | 0.0013692 | 0.0013858 | 0.0014023 | 0.0014189 | 0.0014354 | 0.001452 | 0.0014686 | 0.0014851 | 0.0015017 | 0.0015182 | 0.0015348
| CME016-171344649 | CME016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME016-24605950 | CME016 | 0.055418 | 0.055792 | 0.056167 | 0.056541 | 0.056915 | 0.057432 | 0.057949 | 0.058466 | 0.058982 | 0.059499 | 0.060016 | 0.060533 | 0.06105 | 0.061567 | 0.062084 | 0.062601 | 0.063118 | 0.063635 | 0.064151 | 0.064668
| CME016-68675557 | CME016 | 0.76698 | 0.77192 | 0.77686 | 0.78179 | 0.78673 | 0.79413 | 0.80153 | 0.80892 | 0.81632 | 0.82372 | 0.83112 | 0.83852 | 0.84592 | 0.85331 | 0.86071 | 0.86811 | 0.87551 | 0.88291 | 0.89031 | 0.8977
| CME021-15423551 | CME021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CME021-15423564 | CME021 | 9.8524 | 9.902 | 9.9517 | 10.0013 | 10.051 | 10.0771 | 10.1033 | 10.1294 | 10.1556 | 10.1817 | 10.2078 | 10.234 | 10.2601 | 10.2863 | 10.3124 | 10.3386 | 10.3647 | 10.3909 | 10.417 | 10.4432
| CME021-184455628 | CME021 | 7.6129 | 7.6623 | 7.7117 | 7.7611 | 7.8105 | 7.8573 | 7.9041 | 7.9509 | 7.9977 | 8.0446 | 8.0914 | 8.1382 | 8.185 | 8.2318 | 8.2786 | 8.3254 | 8.3722 | 8.4191 | 8.4659 | 8.5127
| CME022-15423527 | CME022 | 0.058211 | 0.058679 | 0.059147 | 0.059616 | 0.060084 | 0.060667 | 0.061249 | 0.061832 | 0.062415 | 0.062997 | 0.06358 | 0.064162 | 0.064745 | 0.065328 | 0.06591 | 0.066493 | 0.067076 | 0.067658 | 0.068241 | 0.068824
| CMN001-124828418 | CMN001 | 62.606 | 63.0895 | 63.573 | 64.0565 | 64.54 | 64.7141 | 64.8882 | 65.0624 | 65.2365 | 65.4107 | 65.5848 | 65.759 | 65.9331 | 66.1073 | 66.2814 | 66.4556 | 66.6297 | 66.8039 | 66.978 | 67.1522
| CMN001-132430534 | CMN001 | 24.8324 | 24.9976 | 25.1629 | 25.3281 | 25.4934 | 25.5564 | 25.6194 | 25.6825 | 25.7455 | 25.8085 | 25.8715 | 25.9345 | 25.9976 | 26.0606 | 26.1236 | 26.1866 | 26.2496 | 26.3127 | 26.3757 | 26.4387
| CMN001-15420462 | CMN001 | 157.9234 | 158.6808 | 159.4382 | 160.1956 | 160.9529 | 161.121 | 161.289 | 161.457 | 161.625 | 161.793 | 161.9611 | 162.1291 | 162.2971 | 162.4651 | 162.6331 | 162.8012 | 162.9692 | 163.1372 | 163.3052 | 163.4733
| CMN001-156820944 | CMN001 | 142.2185 | 142.9385 | 143.6586 | 144.3786 | 145.0986 | 145.4969 | 145.8952 | 146.2935 | 146.6918 | 147.0901 | 147.4885 | 147.8868 | 148.2851 | 148.6834 | 149.0817 | 149.48 | 149.8783 | 150.2767 | 150.675 | 151.0733
| CMN001-163864096 | CMN001 | 0.24895 | 0.25053 | 0.25211 | 0.25369 | 0.25527 | 0.25583 | 0.25639 | 0.25696 | 0.25752 | 0.25808 | 0.25865 | 0.25921 | 0.25977 | 0.26034 | 0.2609 | 0.26146 | 0.26203 | 0.26259 | 0.26315 | 0.26372
| CMN001-182014538 | CMN001 | 7.1016 | 7.1631 | 7.2246 | 7.2861 | 7.3476 | 7.3473 | 7.3471 | 7.3468 | 7.3466 | 7.3463 | 7.3461 | 7.3458 | 7.3456 | 7.3453 | 7.3451 | 7.3448 | 7.3446 | 7.3443 | 7.344 | 7.3438
| CMN001-73767965 | CMN001 | 0.1574 | 0.1587 | 0.16001 | 0.16132 | 0.16263 | 0.16276 | 0.16289 | 0.16301 | 0.16314 | 0.16327 | 0.1634 | 0.16353 | 0.16366 | 0.16379 | 0.16391 | 0.16404 | 0.16417 | 0.1643 | 0.16443 | 0.16456
| CMN001-73948224 | CMN001 | 0.24432 | 0.24608 | 0.24784 | 0.24959 | 0.25135 | 0.25221 | 0.25307 | 0.25393 | 0.25479 | 0.25565 | 0.25651 | 0.25737 | 0.25823 | 0.25909 | 0.25995 | 0.26081 | 0.26167 | 0.26253 | 0.26339 | 0.26425
| CMN001-73948442 | CMN001 | 0.01881 | 0.01901 | 0.01921 | 0.019411 | 0.019611 | 0.019768 | 0.019924 | 0.020081 | 0.020238 | 0.020395 | 0.020551 | 0.020708 | 0.020865 | 0.021022 | 0.021179 | 0.021335 | 0.021492 | 0.021649 | 0.021806 | 0.021962
| CMN001-74644085 | CMN001 | 0.70799 | 0.71354 | 0.71908 | 0.72462 | 0.73017 | 0.73325 | 0.73633 | 0.73941 | 0.74249 | 0.74557 | 0.74865 | 0.75173 | 0.75481 | 0.7579 | 0.76098 | 0.76406 | 0.76714 | 0.77022 | 0.7733 | 0.77638
| CMN001-74644167 | CMN001 | 0.508 | 0.51177 | 0.51555 | 0.51933 | 0.5231 | 0.52367 | 0.52424 | 0.52481 | 0.52539 | 0.52596 | 0.52653 | 0.5271 | 0.52767 | 0.52824 | 0.52881 | 0.52938 | 0.52995 | 0.53052 | 0.5311 | 0.53167
| CMN001-74644242 | CMN001 | 0.91052 | 0.91796 | 0.9254 | 0.93284 | 0.94028 | 0.9416 | 0.94291 | 0.94423 | 0.94554 | 0.94686 | 0.94817 | 0.94949 | 0.9508 | 0.95212 | 0.95343 | 0.95474 | 0.95606 | 0.95737 | 0.95869 | 0.96
| CMN001-74644428 | CMN001 | 0.058883 | 0.059349 | 0.059814 | 0.06028 | 0.060746 | 0.060903 | 0.061061 | 0.061218 | 0.061375 | 0.061533 | 0.06169 | 0.061848 | 0.062005 | 0.062162 | 0.06232 | 0.062477 | 0.062635 | 0.062792 | 0.062949 | 0.063107
| CMN002-138133472 | CMN002 | 0.06312 | 0.063538 | 0.063957 | 0.064376 | 0.064794 | 0.064932 | 0.065069 | 0.065207 | 0.065344 | 0.065482 | 0.065619 | 0.065757 | 0.065894 | 0.066032 | 0.066169 | 0.066307 | 0.066444 | 0.066581 | 0.066719 | 0.066856
| CMN002-15420512 | CMN002 | 121.8083 | 122.4279 | 123.0475 | 123.6671 | 124.2867 | 124.6614 | 125.036 | 125.4106 | 125.7852 | 126.1599 | 126.5345 | 126.9091 | 127.2837 | 127.6584 | 128.033 | 128.4076 | 128.7822 | 129.1569 | 129.5315 | 129.9061
| CMN002-15420523 | CMN002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN002-78928402 | CMN002 | 0.084371 | 0.084945 | 0.085519 | 0.086093 | 0.086667 | 0.086828 | 0.08699 | 0.087152 | 0.087314 | 0.087476 | 0.087638 | 0.0878 | 0.087961 | 0.088123 | 0.088285 | 0.088447 | 0.088609 | 0.088771 | 0.088933 | 0.089094
| CMN002-78928472 | CMN002 | 0.22412 | 0.22546 | 0.22679 | 0.22813 | 0.22946 | 0.22982 | 0.23018 | 0.23054 | 0.2309 | 0.23126 | 0.23163 | 0.23199 | 0.23235 | 0.23271 | 0.23307 | 0.23343 | 0.23379 | 0.23415 | 0.23451 | 0.23487
| CMN002-87920200 | CMN002 | 0.066253 | 0.066737 | 0.06722 | 0.067704 | 0.068188 | 0.068508 | 0.068829 | 0.069149 | 0.069469 | 0.06979 | 0.07011 | 0.070431 | 0.070751 | 0.071072 | 0.071392 | 0.071712 | 0.072033 | 0.072353 | 0.072674 | 0.072994
| CMN003-123737154 | CMN003 | 73.9419 | 74.3863 | 74.8306 | 75.275 | 75.7194 | 75.8163 | 75.9133 | 76.0102 | 76.1071 | 76.204 | 76.301 | 76.3979 | 76.4948 | 76.5918 | 76.6887 | 76.7856 | 76.8825 | 76.9795 | 77.0764 | 77.1733
| CMN003-15420636 | CMN003 | 0.0077718 | 0.007827 | 0.0078821 | 0.0079373 | 0.0079924 | 0.008015 | 0.0080376 | 0.0080603 | 0.0080829 | 0.0081055 | 0.0081281 | 0.0081507 | 0.0081734 | 0.008196 | 0.0082186 | 0.0082412 | 0.0082638 | 0.0082865 | 0.0083091 | 0.0083317
| CMN003-15420649 | CMN003 | 95.8677 | 96.4251 | 96.9825 | 97.5399 | 98.0973 | 98.2743 | 98.4512 | 98.6281 | 98.805 | 98.9819 | 99.1588 | 99.3358 | 99.5127 | 99.6896 | 99.8665 | 100.0434 | 100.2203 | 100.3972 | 100.5742 | 100.7511
| CMN003-164373106 | CMN003 | 11.976 | 12.0462 | 12.1164 | 12.1866 | 12.2568 | 12.2693 | 12.2818 | 12.2943 | 12.3068 | 12.3193 | 12.3318 | 12.3443 | 12.3568 | 12.3693 | 12.3818 | 12.3943 | 12.4068 | 12.4193 | 12.4318 | 12.4443
| CMN003-164373173 | CMN003 | 1.1097 | 1.1165 | 1.1234 | 1.1302 | 1.137 | 1.1418 | 1.1467 | 1.1515 | 1.1563 | 1.1611 | 1.1659 | 1.1708 | 1.1756 | 1.1804 | 1.1852 | 1.1901 | 1.1949 | 1.1997 | 1.2045 | 1.2093
| CMN003-75645317 | CMN003 | 0.014047 | 0.014118 | 0.014189 | 0.014261 | 0.014332 | 0.014404 | 0.014477 | 0.01455 | 0.014622 | 0.014695 | 0.014768 | 0.01484 | 0.014913 | 0.014985 | 0.015058 | 0.015131 | 0.015203 | 0.015276 | 0.015349 | 0.015421
| CMN003-75645537 | CMN003 | 0.01839 | 0.018521 | 0.018652 | 0.018783 | 0.018914 | 0.018992 | 0.01907 | 0.019148 | 0.019227 | 0.019305 | 0.019383 | 0.019461 | 0.019539 | 0.019617 | 0.019695 | 0.019773 | 0.019851 | 0.019929 | 0.020007 | 0.020086
| CMN003-76447191 | CMN003 | 0.11901 | 0.12 | 0.12099 | 0.12197 | 0.12296 | 0.12302 | 0.12309 | 0.12315 | 0.12322 | 0.12328 | 0.12334 | 0.12341 | 0.12347 | 0.12353 | 0.1236 | 0.12366 | 0.12372 | 0.12379 | 0.12385 | 0.12392
| CMN003-76447226 | CMN003 | 0.026998 | 0.027181 | 0.027363 | 0.027546 | 0.027729 | 0.027819 | 0.027909 | 0.028 | 0.02809 | 0.02818 | 0.02827 | 0.028361 | 0.028451 | 0.028541 | 0.028631 | 0.028721 | 0.028812 | 0.028902 | 0.028992 | 0.029082
| CMN004-15420549 | CMN004 | 83.7897 | 84.4001 | 85.0106 | 85.621 | 86.2314 | 86.2938 | 86.3562 | 86.4186 | 86.481 | 86.5434 | 86.6058 | 86.6682 | 86.7306 | 86.7931 | 86.8555 | 86.9179 | 86.9803 | 87.0427 | 87.1051 | 87.1675
| CMN004-24614626 | CMN004 | 11.589 | 11.6816 | 11.7742 | 11.8668 | 11.9593 | 11.9693 | 11.9792 | 11.9891 | 11.999 | 12.009 | 12.0189 | 12.0288 | 12.0387 | 12.0486 | 12.0586 | 12.0685 | 12.0784 | 12.0883 | 12.0982 | 12.1082
| CMN004-74052344 | CMN004 | 0.16083 | 0.16176 | 0.1627 | 0.16363 | 0.16456 | 0.16485 | 0.16513 | 0.16542 | 0.1657 | 0.16598 | 0.16627 | 0.16655 | 0.16684 | 0.16712 | 0.16741 | 0.16769 | 0.16798 | 0.16826 | 0.16854 | 0.16883
| CMN004-76446391 | CMN004 | 0.084324 | 0.08507 | 0.085816 | 0.086562 | 0.087308 | 0.087392 | 0.087477 | 0.087562 | 0.087646 | 0.087731 | 0.087815 | 0.0879 | 0.087984 | 0.088069 | 0.088153 | 0.088238 | 0.088323 | 0.088407 | 0.088492 | 0.088576
| CMN004-76547682 | CMN004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CMN005-15420597 | CMN005 | 40.6654 | 40.9175 | 41.1695 | 41.4216 | 41.6737 | 41.7627 | 41.8517 | 41.9408 | 42.0298 | 42.1188 | 42.2079 | 42.2969 | 42.3859 | 42.475 | 42.564 | 42.653 | 42.742 | 42.8311 | 42.9201 | 43.0091
| COB011-15431802 | COB011 | 7.5611e-05 | 7.6467e-05 | 7.7323e-05 | 7.818e-05 | 7.9036e-05 | 7.8016e-05 | 7.6995e-05 | 7.5974e-05 | 7.4954e-05 | 7.3933e-05 | 7.2913e-05 | 7.1892e-05 | 7.0872e-05 | 6.9851e-05 | 6.8831e-05 | 6.781e-05 | 6.679e-05 | 6.5769e-05 | 6.4749e-05 | 6.3728e-05
| COB011-15431815 | COB011 | 3.4888 | 3.5134 | 3.538 | 3.5626 | 3.5872 | 3.558 | 3.5288 | 3.4996 | 3.4705 | 3.4413 | 3.4121 | 3.383 | 3.3538 | 3.3246 | 3.2955 | 3.2663 | 3.2371 | 3.208 | 3.1788 | 3.1496
| COB011-162571445 | COB011 | 3.7841e-05 | 3.8371e-05 | 3.8901e-05 | 3.943e-05 | 3.996e-05 | 3.9342e-05 | 3.8724e-05 | 3.8106e-05 | 3.7488e-05 | 3.687e-05 | 3.6252e-05 | 3.5634e-05 | 3.5016e-05 | 3.4398e-05 | 3.378e-05 | 3.3162e-05 | 3.2544e-05 | 3.1926e-05 | 3.1308e-05 | 3.069e-05
| COB011-162571831 | COB011 | 9.0569e-07 | 9.1751e-07 | 9.2934e-07 | 9.4117e-07 | 9.53e-07 | 9.3745e-07 | 9.219e-07 | 9.0635e-07 | 8.908e-07 | 8.7525e-07 | 8.597e-07 | 8.4415e-07 | 8.286e-07 | 8.1305e-07 | 7.975e-07 | 7.8195e-07 | 7.664e-07 | 7.5085e-07 | 7.353e-07 | 7.1975e-07
| COB011-162572039 | COB011 | 0.0010207 | 0.0010298 | 0.0010388 | 0.0010479 | 0.001057 | 0.0010466 | 0.0010362 | 0.0010257 | 0.0010153 | 0.0010049 | 0.00099445 | 0.00098402 | 0.00097359 | 0.00096316 | 0.00095273 | 0.0009423 | 0.00093187 | 0.00092144 | 0.00091101 | 0.00090059
| COB011-162572240 | COB011 | 0.00088051 | 0.00089089 | 0.00090126 | 0.00091163 | 0.000922 | 0.00090765 | 0.0008933 | 0.00087895 | 0.0008646 | 0.00085025 | 0.0008359 | 0.00082155 | 0.0008072 | 0.00079285 | 0.0007785 | 0.00076415 | 0.0007498 | 0.00073545 | 0.0007211 | 0.00070675
| COB011-162572975 | COB011 | 1.3598e-05 | 1.3843e-05 | 1.4089e-05 | 1.4334e-05 | 1.458e-05 | 1.4281e-05 | 1.3982e-05 | 1.3684e-05 | 1.3385e-05 | 1.3086e-05 | 1.2787e-05 | 1.2488e-05 | 1.219e-05 | 1.1891e-05 | 1.1592e-05 | 1.1293e-05 | 1.0994e-05 | 1.0696e-05 | 1.0397e-05 | 1.0098e-05
| COB011-162661437 | COB011 | 0.00066191 | 0.00066969 | 0.00067746 | 0.00068523 | 0.000693 | 0.00068255 | 0.0006721 | 0.00066165 | 0.0006512 | 0.00064075 | 0.0006303 | 0.00061985 | 0.0006094 | 0.00059895 | 0.0005885 | 0.00057805 | 0.0005676 | 0.00055715 | 0.0005467 | 0.00053625
| COB011-162661589 | COB011 | 0.021741 | 0.021965 | 0.022189 | 0.022414 | 0.022638 | 0.0223 | 0.021962 | 0.021624 | 0.021286 | 0.020948 | 0.02061 | 0.020272 | 0.019934 | 0.019596 | 0.019258 | 0.01892 | 0.018582 | 0.018244 | 0.017906 | 0.017568
| COB011-162661811 | COB011 | 8.7588e-05 | 8.9316e-05 | 9.1044e-05 | 9.2772e-05 | 9.45e-05 | 9.261e-05 | 9.072e-05 | 8.883e-05 | 8.694e-05 | 8.505e-05 | 8.316e-05 | 8.127e-05 | 7.938e-05 | 7.749e-05 | 7.56e-05 | 7.371e-05 | 7.182e-05 | 6.993e-05 | 6.804e-05 | 6.615e-05
| COB011-162798633 | COB011 | 0.003334 | 0.0033592 | 0.0033844 | 0.0034096 | 0.0034348 | 0.0033954 | 0.0033561 | 0.0033167 | 0.0032774 | 0.003238 | 0.0031987 | 0.0031593 | 0.00312 | 0.0030806 | 0.0030413 | 0.0030019 | 0.0029626 | 0.0029232 | 0.0028839 | 0.0028445
| COB011-163103340 | COB011 | 0.0060328 | 0.0061095 | 0.0061862 | 0.0062629 | 0.0063396 | 0.0062477 | 0.0061558 | 0.0060639 | 0.005972 | 0.0058801 | 0.0057882 | 0.0056964 | 0.0056045 | 0.0055126 | 0.0054207 | 0.0053288 | 0.0052369 | 0.005145 | 0.0050531 | 0.0049613
| COB011-164044294 | COB011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-201141604 | COB011 | 0.25379 | 0.25556 | 0.25733 | 0.25909 | 0.26086 | 0.25821 | 0.25555 | 0.2529 | 0.25025 | 0.24759 | 0.24494 | 0.24229 | 0.23964 | 0.23698 | 0.23433 | 0.23168 | 0.22902 | 0.22637 | 0.22372 | 0.22107
| COB011-202349052 | COB011 | 0.85506 | 0.86083 | 0.86659 | 0.87236 | 0.87813 | 0.86919 | 0.86025 | 0.85131 | 0.84237 | 0.83342 | 0.82448 | 0.81554 | 0.8066 | 0.79766 | 0.78872 | 0.77978 | 0.77084 | 0.76189 | 0.75295 | 0.74401
| COB012-15431852 | COB012 | 0.023437 | 0.023639 | 0.02384 | 0.024042 | 0.024243 | 0.024008 | 0.023774 | 0.02354 | 0.023305 | 0.023071 | 0.022836 | 0.022602 | 0.022367 | 0.022133 | 0.021898 | 0.021664 | 0.021429 | 0.021195 | 0.02096 | 0.020726
| COB021-15436290 | COB021 | 0.028752 | 0.028993 | 0.029234 | 0.029475 | 0.029716 | 0.029429 | 0.029143 | 0.028856 | 0.02857 | 0.028283 | 0.027996 | 0.02771 | 0.027423 | 0.027137 | 0.02685 | 0.026563 | 0.026277 | 0.02599 | 0.025704 | 0.025417
| COB021-24613718 | COB021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COB022-160576265 | COB022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO013-15404871 | CRO013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO013-15404884 | CRO013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO014-15404821 | CRO014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO021-153844129 | CRO021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO021-15404447 | CRO021 | 0.44132 | 0.44336 | 0.4454 | 0.44743 | 0.44947 | 0.44925 | 0.44902 | 0.4488 | 0.44857 | 0.44835 | 0.44812 | 0.4479 | 0.44767 | 0.44745 | 0.44722 | 0.447 | 0.44677 | 0.44654 | 0.44632 | 0.44609
| CRO022-15404471 | CRO022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO022-24612421 | CRO022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO023-15404521 | CRO023 | 0.0046798 | 0.0047208 | 0.0047618 | 0.0048028 | 0.0048438 | 0.0048632 | 0.0048827 | 0.0049021 | 0.0049215 | 0.004941 | 0.0049604 | 0.0049798 | 0.0049993 | 0.0050187 | 0.0050382 | 0.0050576 | 0.005077 | 0.0050965 | 0.0051159 | 0.0051353
| CRO031-15404634 | CRO031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO031-15404660 | CRO031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO032-15404697 | CRO032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRO033-15404721 | CRO033 | 0.034285 | 0.034573 | 0.03486 | 0.035148 | 0.035436 | 0.035561 | 0.035687 | 0.035812 | 0.035938 | 0.036064 | 0.036189 | 0.036315 | 0.036441 | 0.036566 | 0.036692 | 0.036818 | 0.036943 | 0.037069 | 0.037194 | 0.03732
| CRO034-15404810 | CRO034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN001-129145544 | CTN001 | 4.5716 | 4.5953 | 4.6189 | 4.6426 | 4.6662 | 4.6703 | 4.6744 | 4.6785 | 4.6827 | 4.6868 | 4.6909 | 4.695 | 4.6991 | 4.7032 | 4.7073 | 4.7115 | 4.7156 | 4.7197 | 4.7238 | 4.7279
| CTN001-15418475 | CTN001 | 3.7046 | 3.7178 | 3.731 | 3.7443 | 3.7575 | 3.7559 | 3.7544 | 3.7529 | 3.7513 | 3.7498 | 3.7482 | 3.7467 | 3.7451 | 3.7436 | 3.742 | 3.7405 | 3.739 | 3.7374 | 3.7359 | 3.7343
| CTN001-155143379 | CTN001 | 0.08267 | 0.083459 | 0.084247 | 0.085036 | 0.085824 | 0.085744 | 0.085665 | 0.085585 | 0.085505 | 0.085425 | 0.085345 | 0.085265 | 0.085185 | 0.085106 | 0.085026 | 0.084946 | 0.084866 | 0.084786 | 0.084706 | 0.084626
| CTN001-155143591 | CTN001 | 0.15881 | 0.16048 | 0.16215 | 0.16382 | 0.16549 | 0.16502 | 0.16456 | 0.16409 | 0.16363 | 0.16316 | 0.16269 | 0.16223 | 0.16176 | 0.1613 | 0.16083 | 0.16036 | 0.1599 | 0.15943 | 0.15897 | 0.1585
| CTN001-155143776 | CTN001 | 0.14406 | 0.14515 | 0.14624 | 0.14733 | 0.14843 | 0.14874 | 0.14905 | 0.14936 | 0.14966 | 0.14997 | 0.15028 | 0.15059 | 0.1509 | 0.15121 | 0.15152 | 0.15183 | 0.15214 | 0.15245 | 0.15276 | 0.15307
| CTN001-155143905 | CTN001 | 0.00056092 | 0.00056684 | 0.00057276 | 0.00057868 | 0.0005846 | 0.00058589 | 0.00058719 | 0.00058848 | 0.00058978 | 0.00059107 | 0.00059237 | 0.00059366 | 0.00059496 | 0.00059625 | 0.00059755 | 0.00059884 | 0.00060014 | 0.00060143 | 0.00060273 | 0.00060402
| CTN001-155145203 | CTN001 | 0.0069808 | 0.007057 | 0.0071332 | 0.0072094 | 0.0072856 | 0.0072754 | 0.0072651 | 0.0072549 | 0.0072446 | 0.0072344 | 0.0072241 | 0.0072139 | 0.0072036 | 0.0071933 | 0.0071831 | 0.0071728 | 0.0071626 | 0.0071523 | 0.0071421 | 0.0071318
| CTN001-155179699 | CTN001 | 0.0069178 | 0.0070025 | 0.0070872 | 0.007172 | 0.0072567 | 0.0072449 | 0.0072332 | 0.0072214 | 0.0072097 | 0.0071979 | 0.0071862 | 0.0071744 | 0.0071627 | 0.0071509 | 0.0071392 | 0.0071274 | 0.0071157 | 0.0071039 | 0.0070922 | 0.0070804
| CTN001-155179789 | CTN001 | 0.014282 | 0.01446 | 0.014637 | 0.014815 | 0.014992 | 0.014963 | 0.014934 | 0.014905 | 0.014875 | 0.014846 | 0.014817 | 0.014788 | 0.014758 | 0.014729 | 0.0147 | 0.014671 | 0.014641 | 0.014612 | 0.014583 | 0.014554
| CTN001-155190934 | CTN001 | 0.0013431 | 0.0013572 | 0.0013714 | 0.0013855 | 0.0013996 | 0.0013969 | 0.0013942 | 0.0013915 | 0.0013887 | 0.001386 | 0.0013833 | 0.0013806 | 0.0013779 | 0.0013752 | 0.0013725 | 0.0013698 | 0.0013671 | 0.0013644 | 0.0013617 | 0.001359
| CTN001-155191080 | CTN001 | 7.8811e-06 | 7.9709e-06 | 8.0606e-06 | 8.1503e-06 | 8.24e-06 | 8.257e-06 | 8.274e-06 | 8.291e-06 | 8.308e-06 | 8.325e-06 | 8.342e-06 | 8.359e-06 | 8.376e-06 | 8.393e-06 | 8.41e-06 | 8.427e-06 | 8.444e-06 | 8.461e-06 | 8.478e-06 | 8.495e-06
| CTN001-155191213 | CTN001 | 0.0093863 | 0.009498 | 0.0096096 | 0.0097213 | 0.009833 | 0.0098069 | 0.0097809 | 0.0097548 | 0.0097288 | 0.0097027 | 0.0096767 | 0.0096506 | 0.0096246 | 0.0095985 | 0.0095725 | 0.0095464 | 0.0095204 | 0.0094943 | 0.0094683 | 0.0094422
| CTN001-155191322 | CTN001 | 0.23946 | 0.24208 | 0.2447 | 0.24731 | 0.24993 | 0.24965 | 0.24937 | 0.24909 | 0.2488 | 0.24852 | 0.24824 | 0.24796 | 0.24768 | 0.2474 | 0.24712 | 0.24683 | 0.24655 | 0.24627 | 0.24599 | 0.24571
| CTN001-155250725 | CTN001 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05
| CTN001-155250997 | CTN001 | 0.34403 | 0.34665 | 0.34926 | 0.35188 | 0.35449 | 0.35498 | 0.35548 | 0.35597 | 0.35646 | 0.35696 | 0.35745 | 0.35794 | 0.35844 | 0.35893 | 0.35943 | 0.35992 | 0.36041 | 0.36091 | 0.3614 | 0.36189
| CTN001-155668176 | CTN001 | 0.05758 | 0.058236 | 0.058891 | 0.059547 | 0.060202 | 0.06013 | 0.060059 | 0.059987 | 0.059915 | 0.059843 | 0.059772 | 0.0597 | 0.059628 | 0.059556 | 0.059485 | 0.059413 | 0.059341 | 0.059269 | 0.059197 | 0.059126
| CTN001-155668272 | CTN001 | 0.014831 | 0.015004 | 0.015177 | 0.015349 | 0.015522 | 0.015514 | 0.015505 | 0.015497 | 0.015488 | 0.01548 | 0.015471 | 0.015463 | 0.015454 | 0.015446 | 0.015437 | 0.015429 | 0.015421 | 0.015412 | 0.015404 | 0.015395
| CTN001-155821745 | CTN001 | 0.084583 | 0.085536 | 0.086489 | 0.087442 | 0.088395 | 0.088242 | 0.088089 | 0.087936 | 0.087783 | 0.08763 | 0.087477 | 0.087324 | 0.08717 | 0.087017 | 0.086864 | 0.086711 | 0.086558 | 0.086405 | 0.086252 | 0.086099
| CTN001-155821947 | CTN001 | 0.019895 | 0.019902 | 0.019909 | 0.019915 | 0.019922 | 0.019916 | 0.019909 | 0.019903 | 0.019897 | 0.019891 | 0.019884 | 0.019878 | 0.019872 | 0.019866 | 0.01986 | 0.019853 | 0.019847 | 0.019841 | 0.019835 | 0.019828
| CTN001-155822474 | CTN001 | 0.019703 | 0.019921 | 0.020139 | 0.020356 | 0.020574 | 0.020564 | 0.020555 | 0.020545 | 0.020535 | 0.020526 | 0.020516 | 0.020507 | 0.020497 | 0.020487 | 0.020478 | 0.020468 | 0.020459 | 0.020449 | 0.020439 | 0.02043
| CTN001-155822565 | CTN001 | 0.078603 | 0.079448 | 0.080293 | 0.081138 | 0.081983 | 0.081983 | 0.081982 | 0.081982 | 0.081981 | 0.081981 | 0.081981 | 0.08198 | 0.08198 | 0.08198 | 0.081979 | 0.081979 | 0.081979 | 0.081978 | 0.081978 | 0.081978
| CTN001-156780450 | CTN001 | 0.076742 | 0.077276 | 0.07781 | 0.078343 | 0.078877 | 0.079063 | 0.079249 | 0.079435 | 0.079621 | 0.079807 | 0.079993 | 0.080179 | 0.080366 | 0.080552 | 0.080738 | 0.080924 | 0.08111 | 0.081296 | 0.081482 | 0.081668
| CTN001-158006395 | CTN001 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07
| CTN001-161785823 | CTN001 | 0.12639 | 0.12733 | 0.12828 | 0.12923 | 0.13018 | 0.13035 | 0.13052 | 0.13069 | 0.13087 | 0.13104 | 0.13121 | 0.13138 | 0.13155 | 0.13172 | 0.13189 | 0.13206 | 0.13223 | 0.1324 | 0.13257 | 0.13275
| CTN001-163126863 | CTN001 | 0.0083989 | 0.0084534 | 0.0085078 | 0.0085623 | 0.0086168 | 0.0086245 | 0.0086323 | 0.0086401 | 0.0086478 | 0.0086556 | 0.0086634 | 0.0086711 | 0.0086789 | 0.0086867 | 0.0086944 | 0.0087022 | 0.00871 | 0.0087177 | 0.0087255 | 0.0087333
| CTN001-163266702 | CTN001 | 0.0077005 | 0.0077876 | 0.0078747 | 0.0079618 | 0.0080489 | 0.0080529 | 0.0080568 | 0.0080607 | 0.0080647 | 0.0080686 | 0.0080726 | 0.0080765 | 0.0080804 | 0.0080844 | 0.0080883 | 0.0080923 | 0.0080962 | 0.0081002 | 0.0081041 | 0.008108
| CTN001-24604306 | CTN001 | 13.1559 | 13.2784 | 13.4009 | 13.5235 | 13.646 | 13.6249 | 13.6038 | 13.5827 | 13.5616 | 13.5405 | 13.5194 | 13.4983 | 13.4772 | 13.4561 | 13.435 | 13.4139 | 13.3928 | 13.3717 | 13.3505 | 13.3294
| CTN001-24604862 | CTN001 | 0.44669 | 0.44705 | 0.4474 | 0.44776 | 0.44812 | 0.44769 | 0.44725 | 0.44682 | 0.44639 | 0.44595 | 0.44552 | 0.44509 | 0.44466 | 0.44422 | 0.44379 | 0.44336 | 0.44292 | 0.44249 | 0.44206 | 0.44162
| CTN001-24611782 | CTN001 | 1.2303 | 1.2398 | 1.2493 | 1.2588 | 1.2682 | 1.2689 | 1.2695 | 1.2701 | 1.2708 | 1.2714 | 1.272 | 1.2727 | 1.2733 | 1.2739 | 1.2746 | 1.2752 | 1.2758 | 1.2765 | 1.2771 | 1.2777
| CTN001-24611950 | CTN001 | 0.58397 | 0.58899 | 0.59401 | 0.59903 | 0.60405 | 0.60302 | 0.60199 | 0.60096 | 0.59993 | 0.5989 | 0.59787 | 0.59684 | 0.59581 | 0.59479 | 0.59376 | 0.59273 | 0.5917 | 0.59067 | 0.58964 | 0.58861
| CTN002-15418512 | CTN002 | 64.892 | 65.2263 | 65.5607 | 65.8951 | 66.2294 | 66.2768 | 66.3242 | 66.3716 | 66.419 | 66.4664 | 66.5139 | 66.5613 | 66.6087 | 66.6561 | 66.7035 | 66.7509 | 66.7983 | 66.8457 | 66.8931 | 66.9405
| CTN002-154876793 | CTN002 | 0.18591 | 0.18712 | 0.18832 | 0.18953 | 0.19074 | 0.19101 | 0.19128 | 0.19154 | 0.19181 | 0.19208 | 0.19234 | 0.19261 | 0.19288 | 0.19314 | 0.19341 | 0.19368 | 0.19394 | 0.19421 | 0.19448 | 0.19474
| CTN002-154876923 | CTN002 | 0.28079 | 0.28271 | 0.28463 | 0.28655 | 0.28847 | 0.29042 | 0.29237 | 0.29432 | 0.29627 | 0.29822 | 0.30017 | 0.30212 | 0.30407 | 0.30602 | 0.30798 | 0.30993 | 0.31188 | 0.31383 | 0.31578 | 0.31773
| CTN002-154877191 | CTN002 | 0.14997 | 0.15087 | 0.15177 | 0.15267 | 0.15357 | 0.15381 | 0.15404 | 0.15427 | 0.15451 | 0.15474 | 0.15497 | 0.1552 | 0.15544 | 0.15567 | 0.1559 | 0.15614 | 0.15637 | 0.1566 | 0.15684 | 0.15707
| CTN002-154877287 | CTN002 | 0.011246 | 0.011265 | 0.011283 | 0.011301 | 0.011319 | 0.011313 | 0.011307 | 0.011301 | 0.011295 | 0.011289 | 0.011283 | 0.011277 | 0.011271 | 0.011265 | 0.011259 | 0.011253 | 0.011247 | 0.011242 | 0.011236 | 0.01123
| CTN002-154877444 | CTN002 | 0.00072291 | 0.00073069 | 0.00073846 | 0.00074623 | 0.000754 | 0.0007572 | 0.0007604 | 0.0007636 | 0.0007668 | 0.00077 | 0.0007732 | 0.0007764 | 0.0007796 | 0.0007828 | 0.000786 | 0.0007892 | 0.0007924 | 0.0007956 | 0.0007988 | 0.000802
| CTN002-155259126 | CTN002 | 0.059317 | 0.059685 | 0.060052 | 0.06042 | 0.060787 | 0.060923 | 0.061059 | 0.061195 | 0.061331 | 0.061467 | 0.061603 | 0.061739 | 0.061875 | 0.062011 | 0.062146 | 0.062282 | 0.062418 | 0.062554 | 0.06269 | 0.062826
| CTN002-155504946 | CTN002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN002-155616870 | CTN002 | 0.011773 | 0.011862 | 0.011951 | 0.01204 | 0.012129 | 0.012157 | 0.012186 | 0.012215 | 0.012244 | 0.012273 | 0.012302 | 0.012331 | 0.01236 | 0.012389 | 0.012417 | 0.012446 | 0.012475 | 0.012504 | 0.012533 | 0.012562
| CTN002-155622465 | CTN002 | 0.006673 | 0.0067262 | 0.0067795 | 0.0068327 | 0.006886 | 0.006902 | 0.006918 | 0.006934 | 0.00695 | 0.0069661 | 0.0069821 | 0.0069981 | 0.0070141 | 0.0070301 | 0.0070461 | 0.0070621 | 0.0070781 | 0.0070941 | 0.0071101 | 0.0071261
| CTN002-155683683 | CTN002 | 0.10318 | 0.10387 | 0.10456 | 0.10525 | 0.10594 | 0.10641 | 0.10689 | 0.10737 | 0.10785 | 0.10832 | 0.1088 | 0.10928 | 0.10975 | 0.11023 | 0.11071 | 0.11119 | 0.11166 | 0.11214 | 0.11262 | 0.1131
| CTN002-155683893 | CTN002 | 0.051801 | 0.052229 | 0.052657 | 0.053085 | 0.053514 | 0.053704 | 0.053895 | 0.054086 | 0.054277 | 0.054468 | 0.054658 | 0.054849 | 0.05504 | 0.055231 | 0.055422 | 0.055612 | 0.055803 | 0.055994 | 0.056185 | 0.056376
| CTN002-158379241 | CTN002 | 0.34853 | 0.35033 | 0.35214 | 0.35394 | 0.35574 | 0.35605 | 0.35636 | 0.35667 | 0.35697 | 0.35728 | 0.35759 | 0.35789 | 0.3582 | 0.35851 | 0.35881 | 0.35912 | 0.35943 | 0.35974 | 0.36004 | 0.36035
| CTN002-182897070 | CTN002 | 6.1326e-06 | 6.1994e-06 | 6.2663e-06 | 6.3331e-06 | 6.4e-06 | 6.42e-06 | 6.44e-06 | 6.46e-06 | 6.48e-06 | 6.5e-06 | 6.52e-06 | 6.54e-06 | 6.56e-06 | 6.58e-06 | 6.6e-06 | 6.62e-06 | 6.64e-06 | 6.66e-06 | 6.68e-06 | 6.7e-06
| CTN002-24605474 | CTN002 | 9.2548 | 9.2994 | 9.3441 | 9.3888 | 9.4334 | 9.4374 | 9.4414 | 9.4455 | 9.4495 | 9.4535 | 9.4575 | 9.4615 | 9.4655 | 9.4695 | 9.4735 | 9.4775 | 9.4815 | 9.4855 | 9.4895 | 9.4935
| CTN003-15418451 | CTN003 | 17.8975 | 18.0088 | 18.1201 | 18.2314 | 18.3427 | 18.3541 | 18.3655 | 18.3769 | 18.3883 | 18.3997 | 18.4111 | 18.4225 | 18.4339 | 18.4453 | 18.4568 | 18.4682 | 18.4796 | 18.491 | 18.5024 | 18.5138
| CTN003-155024326 | CTN003 | 0.021345 | 0.02157 | 0.021794 | 0.022019 | 0.022244 | 0.022288 | 0.022332 | 0.022376 | 0.02242 | 0.022464 | 0.022508 | 0.022552 | 0.022596 | 0.02264 | 0.022684 | 0.022728 | 0.022772 | 0.022816 | 0.02286 | 0.022904
| CTN003-155024531 | CTN003 | 0.033178 | 0.033517 | 0.033856 | 0.034196 | 0.034535 | 0.034585 | 0.034636 | 0.034686 | 0.034736 | 0.034787 | 0.034837 | 0.034887 | 0.034937 | 0.034988 | 0.035038 | 0.035088 | 0.035139 | 0.035189 | 0.035239 | 0.035289
| CTN003-155024643 | CTN003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-155024758 | CTN003 | 0.090938 | 0.091841 | 0.092743 | 0.093646 | 0.094549 | 0.094799 | 0.095049 | 0.095298 | 0.095548 | 0.095798 | 0.096048 | 0.096298 | 0.096548 | 0.096798 | 0.097048 | 0.097298 | 0.097548 | 0.097798 | 0.098048 | 0.098298
| CTN003-155024899 | CTN003 | 0.095547 | 0.096331 | 0.097114 | 0.097897 | 0.09868 | 0.099095 | 0.09951 | 0.099926 | 0.10034 | 0.10076 | 0.10117 | 0.10159 | 0.102 | 0.10242 | 0.10283 | 0.10325 | 0.10366 | 0.10408 | 0.10449 | 0.10491
| CTN003-155024988 | CTN003 | 0.028229 | 0.028456 | 0.028683 | 0.02891 | 0.029137 | 0.029323 | 0.029509 | 0.029694 | 0.02988 | 0.030066 | 0.030252 | 0.030438 | 0.030623 | 0.030809 | 0.030995 | 0.031181 | 0.031367 | 0.031553 | 0.031738 | 0.031924
| CTN003-155025108 | CTN003 | 0.009166 | 0.0092468 | 0.0093275 | 0.0094083 | 0.0094891 | 0.0095239 | 0.0095587 | 0.0095935 | 0.0096283 | 0.0096632 | 0.009698 | 0.0097328 | 0.0097676 | 0.0098024 | 0.0098373 | 0.0098721 | 0.0099069 | 0.0099417 | 0.0099765 | 0.010011
| CTN003-155025214 | CTN003 | 0.01894 | 0.019127 | 0.019315 | 0.019502 | 0.019689 | 0.019726 | 0.019763 | 0.0198 | 0.019836 | 0.019873 | 0.01991 | 0.019946 | 0.019983 | 0.02002 | 0.020056 | 0.020093 | 0.02013 | 0.020166 | 0.020203 | 0.02024
| CTN003-155025401 | CTN003 | 0.13884 | 0.14 | 0.14116 | 0.14232 | 0.14348 | 0.14339 | 0.1433 | 0.1432 | 0.14311 | 0.14302 | 0.14293 | 0.14283 | 0.14274 | 0.14265 | 0.14255 | 0.14246 | 0.14237 | 0.14228 | 0.14218 | 0.14209
| CTN003-155052230 | CTN003 | 0.031302 | 0.031622 | 0.031943 | 0.032263 | 0.032583 | 0.032649 | 0.032715 | 0.032781 | 0.032846 | 0.032912 | 0.032978 | 0.033044 | 0.03311 | 0.033176 | 0.033242 | 0.033308 | 0.033374 | 0.03344 | 0.033506 | 0.033572
| CTN003-155063034 | CTN003 | 0.073846 | 0.074596 | 0.075347 | 0.076098 | 0.076848 | 0.077025 | 0.077202 | 0.077379 | 0.077556 | 0.077733 | 0.077909 | 0.078086 | 0.078263 | 0.07844 | 0.078617 | 0.078794 | 0.07897 | 0.079147 | 0.079324 | 0.079501
| CTN003-155063181 | CTN003 | 0.0042747 | 0.0043198 | 0.0043649 | 0.00441 | 0.0044551 | 0.0044671 | 0.004479 | 0.004491 | 0.0045029 | 0.0045149 | 0.0045269 | 0.0045388 | 0.0045508 | 0.0045627 | 0.0045747 | 0.0045866 | 0.0045986 | 0.0046105 | 0.0046225 | 0.0046345
| CTN003-155063369 | CTN003 | 0.023883 | 0.024101 | 0.024319 | 0.024537 | 0.024755 | 0.024872 | 0.024989 | 0.025106 | 0.025223 | 0.02534 | 0.025457 | 0.025574 | 0.025691 | 0.025808 | 0.025925 | 0.026042 | 0.026159 | 0.026276 | 0.026393 | 0.02651
| CTN003-155063514 | CTN003 | 0.002458 | 0.0024788 | 0.0024995 | 0.0025203 | 0.002541 | 0.0025518 | 0.0025626 | 0.0025734 | 0.0025842 | 0.0025949 | 0.0026057 | 0.0026165 | 0.0026273 | 0.0026381 | 0.0026489 | 0.0026597 | 0.0026705 | 0.0026813 | 0.0026921 | 0.0027028
| CTN003-155063645 | CTN003 | 0.0043109 | 0.0043513 | 0.0043917 | 0.0044322 | 0.0044726 | 0.004488 | 0.0045035 | 0.0045189 | 0.0045344 | 0.0045498 | 0.0045653 | 0.0045807 | 0.0045962 | 0.0046116 | 0.0046271 | 0.0046425 | 0.004658 | 0.0046734 | 0.0046889 | 0.0047043
| CTN003-155063885 | CTN003 | 0.23106 | 0.23339 | 0.23572 | 0.23804 | 0.24037 | 0.24128 | 0.2422 | 0.24311 | 0.24402 | 0.24493 | 0.24584 | 0.24676 | 0.24767 | 0.24858 | 0.24949 | 0.2504 | 0.25131 | 0.25223 | 0.25314 | 0.25405
| CTN003-155155512 | CTN003 | 0.061841 | 0.0623 | 0.06276 | 0.063219 | 0.063679 | 0.063965 | 0.064251 | 0.064536 | 0.064822 | 0.065108 | 0.065394 | 0.06568 | 0.065966 | 0.066251 | 0.066537 | 0.066823 | 0.067109 | 0.067395 | 0.067681 | 0.067966
| CTN003-155155602 | CTN003 | 2.0439e-05 | 2.0625e-05 | 2.081e-05 | 2.0995e-05 | 2.118e-05 | 2.1301e-05 | 2.1423e-05 | 2.1545e-05 | 2.1666e-05 | 2.1787e-05 | 2.1909e-05 | 2.203e-05 | 2.2152e-05 | 2.2273e-05 | 2.2395e-05 | 2.2516e-05 | 2.2638e-05 | 2.2759e-05 | 2.2881e-05 | 2.3002e-05
| CTN003-155176630 | CTN003 | 0.040313 | 0.040698 | 0.041082 | 0.041467 | 0.041851 | 0.041896 | 0.041941 | 0.041986 | 0.04203 | 0.042075 | 0.04212 | 0.042164 | 0.042209 | 0.042254 | 0.042299 | 0.042343 | 0.042388 | 0.042433 | 0.042477 | 0.042522
| CTN003-155177865 | CTN003 | 0.0027739 | 0.0028017 | 0.0028295 | 0.0028573 | 0.0028851 | 0.0028893 | 0.0028934 | 0.0028976 | 0.0029017 | 0.0029058 | 0.00291 | 0.0029141 | 0.0029183 | 0.0029224 | 0.0029266 | 0.0029307 | 0.0029349 | 0.002939 | 0.0029431 | 0.0029473
| CTN003-155392598 | CTN003 | 0.014055 | 0.014207 | 0.01436 | 0.014512 | 0.014665 | 0.014661 | 0.014657 | 0.014653 | 0.014649 | 0.014645 | 0.014641 | 0.014637 | 0.014633 | 0.014629 | 0.014625 | 0.014621 | 0.014617 | 0.014613 | 0.014609 | 0.014605
| CTN003-155422079 | CTN003 | 0.10946 | 0.11051 | 0.11157 | 0.11262 | 0.11368 | 0.11401 | 0.11434 | 0.11467 | 0.115 | 0.11532 | 0.11565 | 0.11598 | 0.11631 | 0.11664 | 0.11697 | 0.1173 | 0.11763 | 0.11796 | 0.11829 | 0.11861
| CTN003-158006357 | CTN003 | 0.95132 | 0.96147 | 0.97161 | 0.98176 | 0.99191 | 0.99395 | 0.99599 | 0.99804 | 1.0001 | 1.0021 | 1.0042 | 1.0062 | 1.0083 | 1.0103 | 1.0123 | 1.0144 | 1.0164 | 1.0185 | 1.0205 | 1.0226
| CTN003-182897268 | CTN003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN003-24603160 | CTN003 | 5.5397 | 5.574 | 5.6083 | 5.6426 | 5.6769 | 5.6777 | 5.6786 | 5.6795 | 5.6804 | 5.6813 | 5.6821 | 5.683 | 5.6839 | 5.6848 | 5.6857 | 5.6865 | 5.6874 | 5.6883 | 5.6892 | 5.6901
| CTN003-47810169 | CTN003 | 6.9307 | 6.9867 | 7.0428 | 7.0988 | 7.1549 | 7.1677 | 7.1805 | 7.1933 | 7.2061 | 7.2189 | 7.2317 | 7.2445 | 7.2572 | 7.27 | 7.2828 | 7.2956 | 7.3084 | 7.3212 | 7.334 | 7.3468
| CTN003-88138723 | CTN003 | 0.055552 | 0.056103 | 0.056654 | 0.057205 | 0.057757 | 0.057926 | 0.058096 | 0.058266 | 0.058436 | 0.058605 | 0.058775 | 0.058945 | 0.059115 | 0.059284 | 0.059454 | 0.059624 | 0.059794 | 0.059963 | 0.060133 | 0.060303
| CTN004-134372186 | CTN004 | 0.16436 | 0.16567 | 0.16699 | 0.1683 | 0.16961 | 0.16985 | 0.1701 | 0.17034 | 0.17059 | 0.17084 | 0.17108 | 0.17133 | 0.17157 | 0.17182 | 0.17207 | 0.17231 | 0.17256 | 0.1728 | 0.17305 | 0.1733
| CTN004-134372435 | CTN004 | 0.10518 | 0.10606 | 0.10693 | 0.1078 | 0.10867 | 0.10877 | 0.10887 | 0.10897 | 0.10907 | 0.10917 | 0.10927 | 0.10937 | 0.10947 | 0.10957 | 0.10967 | 0.10977 | 0.10987 | 0.10997 | 0.11007 | 0.11017
| CTN004-15418536 | CTN004 | 71.1466 | 71.5681 | 71.9897 | 72.4112 | 72.8328 | 72.8872 | 72.9416 | 72.996 | 73.0504 | 73.1048 | 73.1592 | 73.2136 | 73.2681 | 73.3225 | 73.3769 | 73.4313 | 73.4857 | 73.5401 | 73.5945 | 73.649
| CTN004-15418547 | CTN004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN004-155091767 | CTN004 | 0.036433 | 0.036706 | 0.036979 | 0.037252 | 0.037525 | 0.037599 | 0.037673 | 0.037748 | 0.037822 | 0.037896 | 0.037971 | 0.038045 | 0.038119 | 0.038193 | 0.038268 | 0.038342 | 0.038416 | 0.038491 | 0.038565 | 0.038639
| CTN004-155091935 | CTN004 | 0.059629 | 0.060133 | 0.060637 | 0.061142 | 0.061646 | 0.061716 | 0.061786 | 0.061856 | 0.061926 | 0.061996 | 0.062066 | 0.062136 | 0.062206 | 0.062277 | 0.062347 | 0.062417 | 0.062487 | 0.062557 | 0.062627 | 0.062697
| CTN004-155092023 | CTN004 | 0.036735 | 0.037026 | 0.037317 | 0.037608 | 0.037899 | 0.03795 | 0.038002 | 0.038054 | 0.038105 | 0.038157 | 0.038209 | 0.03826 | 0.038312 | 0.038364 | 0.038416 | 0.038467 | 0.038519 | 0.038571 | 0.038622 | 0.038674
| CTN004-155092123 | CTN004 | 0.18212 | 0.18343 | 0.18474 | 0.18605 | 0.18736 | 0.18737 | 0.18737 | 0.18738 | 0.18738 | 0.18739 | 0.1874 | 0.1874 | 0.18741 | 0.18741 | 0.18742 | 0.18742 | 0.18743 | 0.18744 | 0.18744 | 0.18745
| CTN004-160370806 | CTN004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CTN005-15418323 | CTN005 | 4.5515 | 4.5748 | 4.598 | 4.6212 | 4.6445 | 4.6466 | 4.6487 | 4.6508 | 4.653 | 4.6551 | 4.6572 | 4.6593 | 4.6615 | 4.6636 | 4.6657 | 4.6678 | 4.67 | 4.6721 | 4.6742 | 4.6764
| CTN006-100525030 | CTN006 | 0.11302 | 0.11378 | 0.11453 | 0.11529 | 0.11604 | 0.11606 | 0.11608 | 0.1161 | 0.11612 | 0.11614 | 0.11615 | 0.11617 | 0.11619 | 0.11621 | 0.11623 | 0.11625 | 0.11627 | 0.11629 | 0.1163 | 0.11632
| CTN006-123737136 | CTN006 | 0.17358 | 0.1747 | 0.17583 | 0.17695 | 0.17807 | 0.17814 | 0.17821 | 0.17827 | 0.17834 | 0.17841 | 0.17848 | 0.17854 | 0.17861 | 0.17868 | 0.17875 | 0.17881 | 0.17888 | 0.17895 | 0.17901 | 0.17908
| CTN006-138230928 | CTN006 | 0.084043 | 0.084675 | 0.085308 | 0.085941 | 0.086574 | 0.086668 | 0.086763 | 0.086858 | 0.086953 | 0.087048 | 0.087143 | 0.087238 | 0.087333 | 0.087428 | 0.087523 | 0.087618 | 0.087713 | 0.087808 | 0.087903 | 0.087998
| CTN006-15418599 | CTN006 | 0.0012676 | 0.001281 | 0.0012944 | 0.0013078 | 0.0013213 | 0.0013253 | 0.0013294 | 0.0013334 | 0.0013375 | 0.0013415 | 0.0013456 | 0.0013496 | 0.0013537 | 0.0013577 | 0.0013618 | 0.0013658 | 0.0013699 | 0.0013739 | 0.001378 | 0.001382
| CTN006-154972740 | CTN006 | 0.051395 | 0.051809 | 0.052222 | 0.052636 | 0.05305 | 0.053028 | 0.053005 | 0.052983 | 0.052961 | 0.052939 | 0.052917 | 0.052895 | 0.052872 | 0.05285 | 0.052828 | 0.052806 | 0.052784 | 0.052762 | 0.052739 | 0.052717
| CTN006-154972844 | CTN006 | 1.1106e-05 | 1.123e-05 | 1.1353e-05 | 1.1477e-05 | 1.16e-05 | 1.1612e-05 | 1.1624e-05 | 1.1636e-05 | 1.1648e-05 | 1.166e-05 | 1.1672e-05 | 1.1684e-05 | 1.1696e-05 | 1.1708e-05 | 1.172e-05 | 1.1732e-05 | 1.1744e-05 | 1.1756e-05 | 1.1768e-05 | 1.178e-05
| CTN006-154972931 | CTN006 | 0.1336 | 0.13485 | 0.1361 | 0.13736 | 0.13861 | 0.13874 | 0.13887 | 0.139 | 0.13913 | 0.13925 | 0.13938 | 0.13951 | 0.13964 | 0.13977 | 0.1399 | 0.14003 | 0.14016 | 0.14029 | 0.14042 | 0.14055
| CTN006-154973045 | CTN006 | 0.042373 | 0.042829 | 0.043286 | 0.043742 | 0.044199 | 0.044192 | 0.044185 | 0.044178 | 0.044171 | 0.044164 | 0.044157 | 0.04415 | 0.044143 | 0.044136 | 0.044129 | 0.044122 | 0.044115 | 0.044108 | 0.044101 | 0.044094
| CTN006-155015964 | CTN006 | 0.024775 | 0.024948 | 0.025121 | 0.025294 | 0.025467 | 0.025479 | 0.02549 | 0.025502 | 0.025514 | 0.025525 | 0.025537 | 0.025549 | 0.02556 | 0.025572 | 0.025584 | 0.025595 | 0.025607 | 0.025619 | 0.02563 | 0.025642
| CTN006-155016184 | CTN006 | 0.00074391 | 0.00074551 | 0.00074711 | 0.0007487 | 0.0007503 | 0.00074977 | 0.00074924 | 0.00074872 | 0.00074819 | 0.00074766 | 0.00074713 | 0.0007466 | 0.00074607 | 0.00074554 | 0.00074501 | 0.00074448 | 0.00074396 | 0.00074343 | 0.0007429 | 0.00074237
| CTN006-155016351 | CTN006 | 0.00011128 | 0.00011246 | 0.00011364 | 0.00011482 | 0.000116 | 0.00011636 | 0.00011672 | 0.00011708 | 0.00011744 | 0.0001178 | 0.00011816 | 0.00011852 | 0.00011888 | 0.00011924 | 0.0001196 | 0.00011996 | 0.00012032 | 0.00012068 | 0.00012104 | 0.0001214
| CTN006-155016482 | CTN006 | 0.23799 | 0.24 | 0.242 | 0.24401 | 0.24601 | 0.24615 | 0.2463 | 0.24644 | 0.24659 | 0.24673 | 0.24687 | 0.24702 | 0.24716 | 0.2473 | 0.24745 | 0.24759 | 0.24773 | 0.24788 | 0.24802 | 0.24816
| CTN006-155018538 | CTN006 | 0.052714 | 0.053174 | 0.053634 | 0.054094 | 0.054555 | 0.054655 | 0.054756 | 0.054856 | 0.054957 | 0.055057 | 0.055158 | 0.055259 | 0.055359 | 0.05546 | 0.05556 | 0.055661 | 0.055762 | 0.055862 | 0.055963 | 0.056063
| CTN006-155018674 | CTN006 | 0.059745 | 0.060129 | 0.060514 | 0.060898 | 0.061283 | 0.061308 | 0.061333 | 0.061359 | 0.061384 | 0.061409 | 0.061434 | 0.061459 | 0.061485 | 0.06151 | 0.061535 | 0.06156 | 0.061585 | 0.06161 | 0.061636 | 0.061661
| CTN006-155018773 | CTN006 | 0.069789 | 0.070424 | 0.071059 | 0.071694 | 0.072329 | 0.072355 | 0.072381 | 0.072407 | 0.072432 | 0.072458 | 0.072484 | 0.07251 | 0.072535 | 0.072561 | 0.072587 | 0.072613 | 0.072639 | 0.072664 | 0.07269 | 0.072716
| CTN006-155018968 | CTN006 | 0.0001329 | 0.0001345 | 0.0001361 | 0.0001377 | 0.0001393 | 0.00013944 | 0.00013958 | 0.00013972 | 0.00013986 | 0.00014 | 0.00014014 | 0.00014028 | 0.00014042 | 0.00014056 | 0.0001407 | 0.00014084 | 0.00014098 | 0.00014112 | 0.00014126 | 0.0001414
| CTN006-155019123 | CTN006 | 0.067699 | 0.068222 | 0.068745 | 0.069269 | 0.069792 | 0.06986 | 0.069928 | 0.069996 | 0.070063 | 0.070131 | 0.070199 | 0.070267 | 0.070335 | 0.070402 | 0.07047 | 0.070538 | 0.070606 | 0.070673 | 0.070741 | 0.070809
| CTN006-155062010 | CTN006 | 0.048869 | 0.04931 | 0.049751 | 0.050191 | 0.050632 | 0.05066 | 0.050688 | 0.050715 | 0.050743 | 0.050771 | 0.050799 | 0.050826 | 0.050854 | 0.050882 | 0.05091 | 0.050937 | 0.050965 | 0.050993 | 0.051021 | 0.051048
| CTN006-155062651 | CTN006 | 0.16123 | 0.16266 | 0.16408 | 0.16551 | 0.16693 | 0.16694 | 0.16695 | 0.16696 | 0.16697 | 0.16698 | 0.16699 | 0.167 | 0.16701 | 0.16702 | 0.16703 | 0.16704 | 0.16705 | 0.16706 | 0.16706 | 0.16707
| CTN006-155077957 | CTN006 | 0.092645 | 0.093409 | 0.094172 | 0.094936 | 0.095699 | 0.095852 | 0.096004 | 0.096156 | 0.096309 | 0.096461 | 0.096614 | 0.096766 | 0.096919 | 0.097071 | 0.097223 | 0.097376 | 0.097528 | 0.097681 | 0.097833 | 0.097986
| CTN006-155078265 | CTN006 | 0.00034018 | 0.00034424 | 0.00034829 | 0.00035235 | 0.0003564 | 0.00035651 | 0.00035662 | 0.00035673 | 0.00035684 | 0.00035695 | 0.00035706 | 0.00035717 | 0.00035728 | 0.00035739 | 0.0003575 | 0.00035761 | 0.00035772 | 0.00035783 | 0.00035794 | 0.00035805
| CTN006-155078364 | CTN006 | 0.061014 | 0.061667 | 0.06232 | 0.062973 | 0.063626 | 0.063665 | 0.063704 | 0.063743 | 0.063782 | 0.063821 | 0.06386 | 0.063899 | 0.063938 | 0.063978 | 0.064017 | 0.064056 | 0.064095 | 0.064134 | 0.064173 | 0.064212
| CTN006-155078558 | CTN006 | 0.082003 | 0.082737 | 0.083471 | 0.084205 | 0.08494 | 0.084941 | 0.084942 | 0.084943 | 0.084945 | 0.084946 | 0.084947 | 0.084948 | 0.084949 | 0.084951 | 0.084952 | 0.084953 | 0.084954 | 0.084955 | 0.084957 | 0.084958
| CTN006-155078784 | CTN006 | 0.00045454 | 0.00045866 | 0.00046277 | 0.00046689 | 0.000471 | 0.00047165 | 0.0004723 | 0.00047295 | 0.0004736 | 0.00047425 | 0.0004749 | 0.00047555 | 0.0004762 | 0.00047685 | 0.0004775 | 0.00047815 | 0.0004788 | 0.00047945 | 0.0004801 | 0.00048075
| CTN006-155078876 | CTN006 | 4.5906e-05 | 4.643e-05 | 4.6953e-05 | 4.7477e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05
| CTN006-155392437 | CTN006 | 0.050011 | 0.050466 | 0.050921 | 0.051376 | 0.051831 | 0.051856 | 0.051882 | 0.051907 | 0.051933 | 0.051958 | 0.051984 | 0.05201 | 0.052035 | 0.052061 | 0.052086 | 0.052112 | 0.052137 | 0.052163 | 0.052188 | 0.052214
| CTN006-157466480 | CTN006 | 0.1882 | 0.18949 | 0.19078 | 0.19207 | 0.19336 | 0.19367 | 0.19397 | 0.19428 | 0.19458 | 0.19489 | 0.19519 | 0.1955 | 0.1958 | 0.1961 | 0.19641 | 0.19671 | 0.19702 | 0.19732 | 0.19763 | 0.19793
| CTN006-157466735 | CTN006 | 0.26692 | 0.26881 | 0.2707 | 0.27259 | 0.27448 | 0.27465 | 0.27481 | 0.27498 | 0.27515 | 0.27532 | 0.27548 | 0.27565 | 0.27582 | 0.27599 | 0.27615 | 0.27632 | 0.27649 | 0.27666 | 0.27682 | 0.27699
| CTN006-157466858 | CTN006 | 8.9099 | 8.9762 | 9.0425 | 9.1088 | 9.1751 | 9.1873 | 9.1994 | 9.2115 | 9.2236 | 9.2357 | 9.2478 | 9.2599 | 9.2721 | 9.2842 | 9.2963 | 9.3084 | 9.3205 | 9.3326 | 9.3448 | 9.3569
| CTN006-158006328 | CTN006 | 6.4093 | 6.4551 | 6.5008 | 6.5466 | 6.5923 | 6.5918 | 6.5913 | 6.5909 | 6.5904 | 6.5899 | 6.5894 | 6.5889 | 6.5884 | 6.5879 | 6.5875 | 6.587 | 6.5865 | 6.586 | 6.5855 | 6.585
| CTN006-163924253 | CTN006 | 0.05831 | 0.058655 | 0.059 | 0.059345 | 0.059691 | 0.059716 | 0.059742 | 0.059767 | 0.059793 | 0.059818 | 0.059844 | 0.059869 | 0.059895 | 0.05992 | 0.059946 | 0.059971 | 0.059997 | 0.060022 | 0.060048 | 0.060073
| CTN006-24603272 | CTN006 | 3.7314 | 3.7558 | 3.7801 | 3.8045 | 3.8288 | 3.8312 | 3.8336 | 3.836 | 3.8384 | 3.8408 | 3.8432 | 3.8457 | 3.8481 | 3.8505 | 3.8529 | 3.8553 | 3.8577 | 3.8601 | 3.8625 | 3.8649
| CTN006-24605098 | CTN006 | 0.45888 | 0.46295 | 0.46702 | 0.47109 | 0.47516 | 0.47574 | 0.47633 | 0.47691 | 0.4775 | 0.47808 | 0.47867 | 0.47926 | 0.47984 | 0.48043 | 0.48101 | 0.4816 | 0.48218 | 0.48277 | 0.48335 | 0.48394
| CTN006-24605334 | CTN006 | 8.0592 | 8.1065 | 8.1538 | 8.2011 | 8.2484 | 8.2531 | 8.2577 | 8.2624 | 8.2671 | 8.2718 | 8.2764 | 8.2811 | 8.2858 | 8.2905 | 8.2951 | 8.2998 | 8.3045 | 8.3092 | 8.3138 | 8.3185
| CTN006-88333121 | CTN006 | 0.011353 | 0.011452 | 0.01155 | 0.011649 | 0.011748 | 0.011763 | 0.011778 | 0.011793 | 0.011808 | 0.011823 | 0.011838 | 0.011854 | 0.011869 | 0.011884 | 0.011899 | 0.011914 | 0.011929 | 0.011944 | 0.01196 | 0.011975
| DDL011-193014102 | DDL011 | 35.4528 | 35.5094 | 35.5661 | 35.6228 | 35.6795 | 35.5566 | 35.4337 | 35.3109 | 35.188 | 35.0651 | 34.9422 | 34.8194 | 34.6965 | 34.5736 | 34.4508 | 34.3279 | 34.205 | 34.0822 | 33.9593 | 33.8364
| DDL011-24612671 | DDL011 | 1.0641 | 1.0658 | 1.0674 | 1.0691 | 1.0708 | 1.0672 | 1.0635 | 1.0599 | 1.0563 | 1.0527 | 1.0491 | 1.0455 | 1.0419 | 1.0383 | 1.0347 | 1.031 | 1.0274 | 1.0238 | 1.0202 | 1.0166
| DDL012-193014212 | DDL012 | 15.3062 | 15.3964 | 15.4866 | 15.5768 | 15.667 | 15.7719 | 15.8768 | 15.9817 | 16.0866 | 16.1915 | 16.2964 | 16.4013 | 16.5062 | 16.6111 | 16.716 | 16.8209 | 16.9258 | 17.0307 | 17.1356 | 17.2405
| DDL012-24612381 | DDL012 | 0.91166 | 0.91338 | 0.91511 | 0.91683 | 0.91856 | 0.91486 | 0.91116 | 0.90746 | 0.90376 | 0.90007 | 0.89637 | 0.89267 | 0.88897 | 0.88527 | 0.88157 | 0.87787 | 0.87417 | 0.87048 | 0.86678 | 0.86308
| DDL012-24612395 | DDL012 | 1.3631 | 1.3662 | 1.3692 | 1.3723 | 1.3754 | 1.3689 | 1.3624 | 1.3559 | 1.3494 | 1.3429 | 1.3364 | 1.3299 | 1.3234 | 1.3169 | 1.3104 | 1.3039 | 1.2974 | 1.2909 | 1.2844 | 1.2779
| DDL013-197602097 | DDL013 | 15.3931 | 15.4032 | 15.4134 | 15.4236 | 15.4337 | 15.4198 | 15.4058 | 15.3918 | 15.3778 | 15.3638 | 15.3498 | 15.3359 | 15.3219 | 15.3079 | 15.2939 | 15.2799 | 15.266 | 15.252 | 15.238 | 15.224
| DDL013-24612353 | DDL013 | 7.9163 | 7.9233 | 7.9302 | 7.9371 | 7.944 | 7.9349 | 7.9258 | 7.9167 | 7.9077 | 7.8986 | 7.8895 | 7.8804 | 7.8713 | 7.8622 | 7.8531 | 7.844 | 7.8349 | 7.8258 | 7.8167 | 7.8076
| DDL013-24612367 | DDL013 | 0.4084 | 0.40922 | 0.41004 | 0.41086 | 0.41168 | 0.41069 | 0.4097 | 0.40871 | 0.40771 | 0.40672 | 0.40573 | 0.40474 | 0.40375 | 0.40275 | 0.40176 | 0.40077 | 0.39978 | 0.39879 | 0.39779 | 0.3968
| DDL014-197602155 | DDL014 | 48.6184 | 48.6696 | 48.7209 | 48.7722 | 48.8234 | 48.7139 | 48.6044 | 48.4949 | 48.3854 | 48.2759 | 48.1664 | 48.0569 | 47.9474 | 47.8379 | 47.7284 | 47.6189 | 47.5093 | 47.3998 | 47.2903 | 47.1808
| DDL021-193014245 | DDL021 | 16.3757 | 16.4101 | 16.4445 | 16.4789 | 16.5133 | 16.44 | 16.3667 | 16.2934 | 16.2201 | 16.1469 | 16.0736 | 16.0003 | 15.927 | 15.8537 | 15.7804 | 15.7072 | 15.6339 | 15.5606 | 15.4873 | 15.414
| DDL021-24613592 | DDL021 | 10.3361 | 10.3446 | 10.3531 | 10.3616 | 10.3701 | 10.3589 | 10.3476 | 10.3363 | 10.325 | 10.3137 | 10.3025 | 10.2912 | 10.2799 | 10.2686 | 10.2574 | 10.2461 | 10.2348 | 10.2235 | 10.2123 | 10.201
| DDL022-197602273 | DDL022 | 20.3786 | 20.3983 | 20.4181 | 20.4378 | 20.4576 | 20.4127 | 20.3679 | 20.3231 | 20.2783 | 20.2334 | 20.1886 | 20.1438 | 20.099 | 20.0542 | 20.0093 | 19.9645 | 19.9197 | 19.8749 | 19.83 | 19.7852
| DDL022-24596878 | DDL022 | 1.2108 | 1.2106 | 1.2105 | 1.2103 | 1.2102 | 1.2102 | 1.2101 | 1.2101 | 1.2101 | 1.21 | 1.21 | 1.21 | 1.2099 | 1.2099 | 1.2099 | 1.2098 | 1.2098 | 1.2098 | 1.2097 | 1.2097
| DDL023-197602323 | DDL023 | 16.1692 | 16.1973 | 16.2254 | 16.2535 | 16.2816 | 16.221 | 16.1604 | 16.0998 | 16.0393 | 15.9787 | 15.9181 | 15.8575 | 15.7969 | 15.7363 | 15.6758 | 15.6152 | 15.5546 | 15.494 | 15.4334 | 15.3729
| DDL023-24612657 | DDL023 | 0.86161 | 0.8637 | 0.86578 | 0.86786 | 0.86995 | 0.86554 | 0.86113 | 0.85673 | 0.85232 | 0.84792 | 0.84351 | 0.8391 | 0.8347 | 0.83029 | 0.82588 | 0.82148 | 0.81707 | 0.81266 | 0.80826 | 0.80385
| DDL023-72495872 | DDL023 | 1.2211 | 1.2253 | 1.2294 | 1.2336 | 1.2378 | 1.2269 | 1.216 | 1.2052 | 1.1943 | 1.1834 | 1.1725 | 1.1617 | 1.1508 | 1.1399 | 1.1291 | 1.1182 | 1.1073 | 1.0965 | 1.0856 | 1.0747
| DDL024-203514186 | DDL024 | 37.5461 | 37.5875 | 37.6289 | 37.6702 | 37.7116 | 37.623 | 37.5343 | 37.4456 | 37.357 | 37.2683 | 37.1797 | 37.091 | 37.0023 | 36.9137 | 36.825 | 36.7363 | 36.6477 | 36.559 | 36.4704 | 36.3817
| DDL024-73759432 | DDL024 | 1.9883 | 1.9918 | 1.9953 | 1.9988 | 2.0023 | 1.9947 | 1.9872 | 1.9797 | 1.9721 | 1.9646 | 1.957 | 1.9495 | 1.942 | 1.9344 | 1.9269 | 1.9193 | 1.9118 | 1.9043 | 1.8967 | 1.8892
| ECA001-15422792 | ECA001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA001-15422805 | ECA001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA001-15422818 | ECA001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA001-24613400 | ECA001 | 62.1998 | 62.5587 | 62.9175 | 63.2764 | 63.6353 | 63.9183 | 64.2012 | 64.4841 | 64.7671 | 65.05 | 65.3329 | 65.6159 | 65.8988 | 66.1817 | 66.4647 | 66.7476 | 67.0305 | 67.3135 | 67.5964 | 67.8794
| ECA001-24613414 | ECA001 | 2.2579 | 2.2671 | 2.2764 | 2.2856 | 2.2948 | 2.2993 | 2.3037 | 2.3082 | 2.3126 | 2.317 | 2.3215 | 2.3259 | 2.3304 | 2.3348 | 2.3392 | 2.3437 | 2.3481 | 2.3526 | 2.357 | 2.3614
| ECA003-15422755 | ECA003 | 119.6296 | 120.2278 | 120.826 | 121.4242 | 122.0223 | 122.6099 | 123.1974 | 123.7849 | 124.3724 | 124.9599 | 125.5475 | 126.135 | 126.7225 | 127.31 | 127.8975 | 128.4851 | 129.0726 | 129.6601 | 130.2476 | 130.8352
| ECA005-15422679 | ECA005 | 4.4524 | 4.4649 | 4.4774 | 4.4899 | 4.5023 | 4.5027 | 4.5031 | 4.5035 | 4.5039 | 4.5042 | 4.5046 | 4.505 | 4.5054 | 4.5058 | 4.5062 | 4.5065 | 4.5069 | 4.5073 | 4.5077 | 4.5081
| ECA005-24596794 | ECA005 | 0.0049422 | 0.0049786 | 0.0050149 | 0.0050513 | 0.0050876 | 0.0051496 | 0.0052116 | 0.0052736 | 0.0053355 | 0.0053975 | 0.0054595 | 0.0055215 | 0.0055835 | 0.0056455 | 0.0057074 | 0.0057694 | 0.0058314 | 0.0058934 | 0.0059554 | 0.0060174
| ECA005-88419875 | ECA005 | 4.6405 | 4.6684 | 4.6962 | 4.724 | 4.7519 | 4.7824 | 4.813 | 4.8435 | 4.874 | 4.9046 | 4.9351 | 4.9657 | 4.9962 | 5.0268 | 5.0573 | 5.0879 | 5.1184 | 5.149 | 5.1795 | 5.21
| ECA007-111138070 | ECA007 | 12.0424 | 12.1126 | 12.1828 | 12.253 | 12.3232 | 12.3534 | 12.3836 | 12.4138 | 12.444 | 12.4742 | 12.5044 | 12.5346 | 12.5648 | 12.595 | 12.6252 | 12.6554 | 12.6856 | 12.7158 | 12.746 | 12.7762
| ECA007-139030671 | ECA007 | 0.0080024 | 0.0080609 | 0.0081193 | 0.0081777 | 0.0082361 | 0.0082773 | 0.0083186 | 0.0083598 | 0.0084011 | 0.0084423 | 0.0084835 | 0.0085248 | 0.008566 | 0.0086073 | 0.0086485 | 0.0086897 | 0.008731 | 0.0087722 | 0.0088134 | 0.0088547
| ECA007-139030700 | ECA007 | 0.12276 | 0.12365 | 0.12455 | 0.12544 | 0.12634 | 0.12683 | 0.12732 | 0.12781 | 0.1283 | 0.12879 | 0.12928 | 0.12977 | 0.13026 | 0.13075 | 0.13124 | 0.13173 | 0.13222 | 0.13271 | 0.1332 | 0.13369
| ECA007-15422655 | ECA007 | 11.7645 | 11.8231 | 11.8817 | 11.9404 | 11.999 | 12.0965 | 12.1939 | 12.2914 | 12.3889 | 12.4863 | 12.5838 | 12.6813 | 12.7787 | 12.8762 | 12.9737 | 13.0712 | 13.1686 | 13.2661 | 13.3636 | 13.461
| ECA007-155422337 | ECA007 | 0.073194 | 0.073651 | 0.074108 | 0.074564 | 0.075021 | 0.075572 | 0.076123 | 0.076674 | 0.077225 | 0.077776 | 0.078327 | 0.078878 | 0.079429 | 0.07998 | 0.080531 | 0.081082 | 0.081633 | 0.082184 | 0.082735 | 0.083286
| ECA007-155422427 | ECA007 | 0.011223 | 0.011293 | 0.011364 | 0.011434 | 0.011505 | 0.011592 | 0.011679 | 0.011766 | 0.011853 | 0.011939 | 0.012026 | 0.012113 | 0.0122 | 0.012287 | 0.012374 | 0.012461 | 0.012548 | 0.012634 | 0.012721 | 0.012808
| ECA007-155422573 | ECA007 | 0.070463 | 0.071016 | 0.071569 | 0.072121 | 0.072674 | 0.073157 | 0.073639 | 0.074122 | 0.074604 | 0.075087 | 0.07557 | 0.076052 | 0.076535 | 0.077017 | 0.0775 | 0.077983 | 0.078465 | 0.078948 | 0.07943 | 0.079913
| ECA007-175612541 | ECA007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ECA007-24611056 | ECA007 | 4.2362 | 4.2573 | 4.2784 | 4.2995 | 4.3205 | 4.3511 | 4.3817 | 4.4123 | 4.4429 | 4.4734 | 4.504 | 4.5346 | 4.5652 | 4.5958 | 4.6263 | 4.6569 | 4.6875 | 4.7181 | 4.7487 | 4.7792
| ECA010-15423016 | ECA010 | 101.9039 | 102.5708 | 103.2378 | 103.9048 | 104.5718 | 105.1378 | 105.7039 | 106.27 | 106.8361 | 107.4021 | 107.9682 | 108.5343 | 109.1003 | 109.6664 | 110.2325 | 110.7985 | 111.3646 | 111.9307 | 112.4968 | 113.0628
| ECA012-15423053 | ECA012 | 26.4164 | 26.5888 | 26.7612 | 26.9336 | 27.106 | 27.277 | 27.448 | 27.619 | 27.79 | 27.9609 | 28.1319 | 28.3029 | 28.4739 | 28.6449 | 28.8158 | 28.9868 | 29.1578 | 29.3288 | 29.4998 | 29.6707
| ECA012-160768254 | ECA012 | 0.038762 | 0.03902 | 0.039279 | 0.039537 | 0.039796 | 0.040059 | 0.040323 | 0.040587 | 0.040851 | 0.041114 | 0.041378 | 0.041642 | 0.041906 | 0.04217 | 0.042433 | 0.042697 | 0.042961 | 0.043225 | 0.043489 | 0.043752
| ECA012-164487948 | ECA012 | 0.0022192 | 0.0022327 | 0.0022461 | 0.0022596 | 0.0022731 | 0.0022922 | 0.0023114 | 0.0023305 | 0.0023496 | 0.0023687 | 0.0023878 | 0.002407 | 0.0024261 | 0.0024452 | 0.0024643 | 0.0024835 | 0.0025026 | 0.0025217 | 0.0025408 | 0.0025599
| ECA012-202230762 | ECA012 | 5.3036 | 5.3201 | 5.3366 | 5.3531 | 5.3695 | 5.3708 | 5.3721 | 5.3733 | 5.3746 | 5.3759 | 5.3771 | 5.3784 | 5.3797 | 5.3809 | 5.3822 | 5.3835 | 5.3847 | 5.386 | 5.3873 | 5.3885
| EHK021-15417698 | EHK021 | 2.3457 | 2.3578 | 2.37 | 2.3822 | 2.3943 | 2.3984 | 2.4024 | 2.4065 | 2.4105 | 2.4146 | 2.4186 | 2.4226 | 2.4267 | 2.4307 | 2.4348 | 2.4388 | 2.4429 | 2.4469 | 2.4509 | 2.455
| EHK022-15417761 | EHK022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK023-15417824 | EHK023 | 439.3042 | 441.9157 | 444.5271 | 447.1386 | 449.7501 | 450.6294 | 451.5086 | 452.3879 | 453.2672 | 454.1465 | 455.0258 | 455.905 | 456.7843 | 457.6636 | 458.5429 | 459.4222 | 460.3014 | 461.1807 | 462.06 | 462.9393
| EHK024-109924737 | EHK024 | 0.0042357 | 0.0042699 | 0.0043041 | 0.0043383 | 0.0043725 | 0.0043955 | 0.0044185 | 0.0044415 | 0.0044645 | 0.0044876 | 0.0045106 | 0.0045336 | 0.0045566 | 0.0045796 | 0.0046026 | 0.0046256 | 0.0046486 | 0.0046716 | 0.0046946 | 0.0047176
| EHK024-119636484 | EHK024 | 3.7642 | 3.7728 | 3.7814 | 3.7901 | 3.7987 | 3.7958 | 3.7929 | 3.79 | 3.7871 | 3.7843 | 3.7814 | 3.7785 | 3.7756 | 3.7727 | 3.7698 | 3.767 | 3.7641 | 3.7612 | 3.7583 | 3.7554
| EHK024-130742429 | EHK024 | 0.42343 | 0.42641 | 0.42939 | 0.43237 | 0.43534 | 0.43745 | 0.43955 | 0.44165 | 0.44375 | 0.44585 | 0.44795 | 0.45005 | 0.45215 | 0.45425 | 0.45635 | 0.45845 | 0.46055 | 0.46265 | 0.46475 | 0.46685
| EHK024-15417874 | EHK024 | 73.2482 | 73.7302 | 74.2121 | 74.6941 | 75.1761 | 75.2989 | 75.4216 | 75.5444 | 75.6672 | 75.79 | 75.9127 | 76.0355 | 76.1583 | 76.2811 | 76.4038 | 76.5266 | 76.6494 | 76.7722 | 76.8949 | 77.0177
| EHK024-155053117 | EHK024 | 0.037591 | 0.037851 | 0.03811 | 0.038369 | 0.038629 | 0.038832 | 0.039036 | 0.03924 | 0.039444 | 0.039647 | 0.039851 | 0.040055 | 0.040259 | 0.040462 | 0.040666 | 0.04087 | 0.041074 | 0.041277 | 0.041481 | 0.041685
| EHK024-155155262 | EHK024 | 0.0042697 | 0.0043054 | 0.0043411 | 0.0043768 | 0.0044124 | 0.0044241 | 0.0044359 | 0.0044476 | 0.0044593 | 0.004471 | 0.0044827 | 0.0044944 | 0.0045062 | 0.0045179 | 0.0045296 | 0.0045413 | 0.004553 | 0.0045647 | 0.0045764 | 0.0045882
| EHK024-155423299 | EHK024 | 0.047156 | 0.047484 | 0.047812 | 0.04814 | 0.048468 | 0.048738 | 0.049009 | 0.049279 | 0.049549 | 0.04982 | 0.05009 | 0.050361 | 0.050631 | 0.050901 | 0.051172 | 0.051442 | 0.051712 | 0.051983 | 0.052253 | 0.052523
| EHK024-155616704 | EHK024 | 0.0055486 | 0.0055628 | 0.0055771 | 0.0055913 | 0.0056056 | 0.0056093 | 0.005613 | 0.0056167 | 0.0056204 | 0.0056241 | 0.0056278 | 0.0056315 | 0.0056352 | 0.0056389 | 0.0056426 | 0.0056463 | 0.00565 | 0.0056537 | 0.0056574 | 0.0056611
| EHK024-155621039 | EHK024 | 0.11862 | 0.11942 | 0.12022 | 0.12102 | 0.12182 | 0.12217 | 0.12252 | 0.12286 | 0.12321 | 0.12356 | 0.1239 | 0.12425 | 0.12459 | 0.12494 | 0.12529 | 0.12563 | 0.12598 | 0.12633 | 0.12667 | 0.12702
| EHK024-161138740 | EHK024 | 12.8621 | 12.922 | 12.982 | 13.0419 | 13.1019 | 13.1424 | 13.183 | 13.2236 | 13.2641 | 13.3047 | 13.3453 | 13.3858 | 13.4264 | 13.467 | 13.5075 | 13.5481 | 13.5887 | 13.6292 | 13.6698 | 13.7104
| EHK024-162768321 | EHK024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-162802004 | EHK024 | 0.00015391 | 0.00015533 | 0.00015675 | 0.00015818 | 0.0001596 | 0.00016053 | 0.00016146 | 0.00016239 | 0.00016332 | 0.00016425 | 0.00016518 | 0.00016611 | 0.00016704 | 0.00016797 | 0.0001689 | 0.00016983 | 0.00017076 | 0.00017169 | 0.00017262 | 0.00017355
| EHK024-162802163 | EHK024 | 0.00021429 | 0.00021611 | 0.00021794 | 0.00021977 | 0.0002216 | 0.00022272 | 0.00022384 | 0.00022496 | 0.00022608 | 0.0002272 | 0.00022832 | 0.00022944 | 0.00023056 | 0.00023168 | 0.0002328 | 0.00023392 | 0.00023504 | 0.00023616 | 0.00023728 | 0.0002384
| EHK024-171210602 | EHK024 | 5.9349e-05 | 5.9811e-05 | 6.0274e-05 | 6.0737e-05 | 6.12e-05 | 6.165e-05 | 6.21e-05 | 6.255e-05 | 6.3e-05 | 6.345e-05 | 6.39e-05 | 6.435e-05 | 6.48e-05 | 6.525e-05 | 6.57e-05 | 6.615e-05 | 6.66e-05 | 6.705e-05 | 6.75e-05 | 6.795e-05
| EHK024-63048145 | EHK024 | 1.7752 | 1.7871 | 1.799 | 1.8109 | 1.8227 | 1.8315 | 1.8402 | 1.8489 | 1.8577 | 1.8664 | 1.8752 | 1.8839 | 1.8926 | 1.9014 | 1.9101 | 1.9189 | 1.9276 | 1.9363 | 1.9451 | 1.9538
| EHK024-63048164 | EHK024 | 9.2358 | 9.2913 | 9.3468 | 9.4023 | 9.4579 | 9.4838 | 9.5098 | 9.5358 | 9.5618 | 9.5877 | 9.6137 | 9.6397 | 9.6657 | 9.6917 | 9.7176 | 9.7436 | 9.7696 | 9.7956 | 9.8215 | 9.8475
| EHK024-73766693 | EHK024 | 0.33003 | 0.33234 | 0.33465 | 0.33697 | 0.33928 | 0.34004 | 0.34079 | 0.34155 | 0.3423 | 0.34306 | 0.34381 | 0.34457 | 0.34532 | 0.34608 | 0.34683 | 0.34759 | 0.34834 | 0.3491 | 0.34985 | 0.35061
| EHK024-73766943 | EHK024 | 0.066905 | 0.067275 | 0.067644 | 0.068014 | 0.068384 | 0.068677 | 0.068971 | 0.069265 | 0.069558 | 0.069852 | 0.070145 | 0.070439 | 0.070733 | 0.071026 | 0.07132 | 0.071614 | 0.071907 | 0.072201 | 0.072495 | 0.072788
| EHK031-134953753 | EHK031 | 0.5385 | 0.54188 | 0.54526 | 0.54864 | 0.55202 | 0.55314 | 0.55426 | 0.55538 | 0.5565 | 0.55762 | 0.55874 | 0.55986 | 0.56098 | 0.5621 | 0.56322 | 0.56433 | 0.56545 | 0.56657 | 0.56769 | 0.56881
| EHK031-134953882 | EHK031 | 0.21184 | 0.21336 | 0.21487 | 0.21639 | 0.2179 | 0.2182 | 0.2185 | 0.2188 | 0.2191 | 0.2194 | 0.2197 | 0.22 | 0.2203 | 0.22059 | 0.22089 | 0.22119 | 0.22149 | 0.22179 | 0.22209 | 0.22239
| EHK031-134954057 | EHK031 | 0.083922 | 0.084504 | 0.085087 | 0.085669 | 0.086252 | 0.086462 | 0.086672 | 0.086882 | 0.087092 | 0.087302 | 0.087513 | 0.087723 | 0.087933 | 0.088143 | 0.088353 | 0.088563 | 0.088773 | 0.088984 | 0.089194 | 0.089404
| EHK031-15417885 | EHK031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK031-15417924 | EHK031 | 183.8058 | 184.9938 | 186.1818 | 187.3699 | 188.5579 | 188.9632 | 189.3685 | 189.7737 | 190.179 | 190.5843 | 190.9896 | 191.3949 | 191.8002 | 192.2054 | 192.6107 | 193.016 | 193.4213 | 193.8266 | 194.2318 | 194.6371
| EHK031-156804503 | EHK031 | 2.6683 | 2.6824 | 2.6966 | 2.7107 | 2.7248 | 2.7253 | 2.7258 | 2.7263 | 2.7267 | 2.7272 | 2.7277 | 2.7282 | 2.7286 | 2.7291 | 2.7296 | 2.73 | 2.7305 | 2.731 | 2.7315 | 2.7319
| EHK031-156804528 | EHK031 | 2.7263 | 2.7437 | 2.7611 | 2.7785 | 2.7958 | 2.8012 | 2.8066 | 2.812 | 2.8174 | 2.8228 | 2.8282 | 2.8336 | 2.839 | 2.8444 | 2.8498 | 2.8552 | 2.8606 | 2.866 | 2.8714 | 2.8768
| EHK032-15417935 | EHK032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK032-15417948 | EHK032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHK033-15418024 | EHK033 | 763.7168 | 767.9218 | 772.1267 | 776.3317 | 780.5366 | 781.3918 | 782.2469 | 783.102 | 783.9571 | 784.8122 | 785.6673 | 786.5225 | 787.3776 | 788.2327 | 789.0878 | 789.9429 | 790.798 | 791.6532 | 792.5083 | 793.3634
| EHK034-15431419 | EHK034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FNS011-15405543 | FNS011 | 56.7662 | 57.1043 | 57.4423 | 57.7803 | 58.1183 | 58.3839 | 58.6494 | 58.9149 | 59.1804 | 59.4459 | 59.7114 | 59.9769 | 60.2425 | 60.508 | 60.7735 | 61.039 | 61.3045 | 61.57 | 61.8355 | 62.1011
| FNS011-24604152 | FNS011 | 1.4319 | 1.4417 | 1.4515 | 1.4613 | 1.4711 | 1.4788 | 1.4865 | 1.4942 | 1.5019 | 1.5097 | 1.5174 | 1.5251 | 1.5328 | 1.5405 | 1.5482 | 1.556 | 1.5637 | 1.5714 | 1.5791 | 1.5868
| FNS012-15405393 | FNS012 | 60.3646 | 60.8608 | 61.357 | 61.8532 | 62.3494 | 62.5812 | 62.813 | 63.0448 | 63.2766 | 63.5084 | 63.7402 | 63.972 | 64.2038 | 64.4356 | 64.6674 | 64.8992 | 65.131 | 65.3628 | 65.5946 | 65.8264
| FNS012-76065032 | FNS012 | 5.6676 | 5.7098 | 5.752 | 5.7942 | 5.8364 | 5.8724 | 5.9084 | 5.9445 | 5.9805 | 6.0165 | 6.0526 | 6.0886 | 6.1246 | 6.1607 | 6.1967 | 6.2327 | 6.2688 | 6.3048 | 6.3408 | 6.3769
| FNS013-15405406 | FNS013 | 72.5472 | 73.1578 | 73.7683 | 74.3789 | 74.9894 | 74.8302 | 74.671 | 74.5118 | 74.3526 | 74.1934 | 74.0342 | 73.875 | 73.7158 | 73.5566 | 73.3974 | 73.2382 | 73.079 | 72.9198 | 72.7606 | 72.6014
| FNS013-73561266 | FNS013 | 1.6144 | 1.6261 | 1.6378 | 1.6495 | 1.6612 | 1.6673 | 1.6734 | 1.6795 | 1.6855 | 1.6916 | 1.6977 | 1.7038 | 1.7099 | 1.7159 | 1.722 | 1.7281 | 1.7342 | 1.7402 | 1.7463 | 1.7524
| FNS021-15405600 | FNS021 | 55.9815 | 56.2057 | 56.4298 | 56.6539 | 56.878 | 56.9604 | 57.0427 | 57.125 | 57.2073 | 57.2897 | 57.372 | 57.4543 | 57.5366 | 57.619 | 57.7013 | 57.7836 | 57.866 | 57.9483 | 58.0306 | 58.1129
| FNS021-24604138 | FNS021 | 2.8211 | 2.8427 | 2.8642 | 2.8858 | 2.9073 | 2.9259 | 2.9445 | 2.963 | 2.9816 | 3.0002 | 3.0187 | 3.0373 | 3.0559 | 3.0744 | 3.093 | 3.1115 | 3.1301 | 3.1487 | 3.1672 | 3.1858
| FNS022-15405419 | FNS022 | 56.3293 | 56.6996 | 57.07 | 57.4404 | 57.8107 | 57.7765 | 57.7423 | 57.7081 | 57.6738 | 57.6396 | 57.6054 | 57.5711 | 57.5369 | 57.5027 | 57.4684 | 57.4342 | 57.4 | 57.3658 | 57.3315 | 57.2973
| FNS022-24604096 | FNS022 | 13.5807 | 13.6935 | 13.8063 | 13.9191 | 14.0319 | 14.0615 | 14.0911 | 14.1206 | 14.1502 | 14.1798 | 14.2094 | 14.239 | 14.2686 | 14.2982 | 14.3278 | 14.3574 | 14.387 | 14.4166 | 14.4462 | 14.4757
| FNS032-15405445 | FNS032 | 4.0131 | 4.0397 | 4.0664 | 4.0931 | 4.1197 | 4.1238 | 4.1278 | 4.1319 | 4.136 | 4.14 | 4.1441 | 4.1481 | 4.1522 | 4.1563 | 4.1603 | 4.1644 | 4.1684 | 4.1725 | 4.1766 | 4.1806
| FNS032-156356596 | FNS032 | 0.00030031 | 0.00030349 | 0.00030666 | 0.00030983 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313
| FNS032-24606816 | FNS032 | 2.0816 | 2.0945 | 2.1073 | 2.1201 | 2.133 | 2.129 | 2.125 | 2.1211 | 2.1171 | 2.1131 | 2.1092 | 2.1052 | 2.1012 | 2.0973 | 2.0933 | 2.0893 | 2.0853 | 2.0814 | 2.0774 | 2.0734
| GB011-15403523 | GB011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GB011-15403536 | GB011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GB012-15403573 | GB012 | 0.4944 | 0.4955 | 0.4966 | 0.49771 | 0.49881 | 0.49648 | 0.49416 | 0.49184 | 0.48952 | 0.48719 | 0.48487 | 0.48255 | 0.48023 | 0.4779 | 0.47558 | 0.47326 | 0.47093 | 0.46861 | 0.46629 | 0.46397
| GB014-15403449 | GB014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GB014-15403475 | GB014 | 0.0073396 | 0.0073643 | 0.0073889 | 0.0074136 | 0.0074382 | 0.007422 | 0.0074059 | 0.0073897 | 0.0073735 | 0.0073574 | 0.0073412 | 0.007325 | 0.0073088 | 0.0072927 | 0.0072765 | 0.0072603 | 0.0072442 | 0.007228 | 0.0072118 | 0.0071957
| GB031-15403499 | GB031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GB032-15403425 | GB032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GB032-15403438 | GB032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY011-153967160 | GCY011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY011-15403919 | GCY011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY012-15403889 | GCY012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY013-15403874 | GCY013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY014-116530590 | GCY014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY014-15403904 | GCY014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY022-15403949 | GCY022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY024-15403979 | GCY024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GCY024-77737752 | GCY024 | 0.17782 | 0.17861 | 0.17939 | 0.18018 | 0.18096 | 0.18061 | 0.18025 | 0.17989 | 0.17954 | 0.17918 | 0.17882 | 0.17847 | 0.17811 | 0.17775 | 0.1774 | 0.17704 | 0.17668 | 0.17633 | 0.17597 | 0.17561
| GHP011-123128913 | GHP011 | 0.00015493 | 0.00015659 | 0.00015826 | 0.00015993 | 0.0001616 | 0.00016188 | 0.00016216 | 0.00016244 | 0.00016272 | 0.000163 | 0.00016328 | 0.00016356 | 0.00016384 | 0.00016412 | 0.0001644 | 0.00016468 | 0.00016496 | 0.00016524 | 0.00016552 | 0.0001658
| GHP011-124927621 | GHP011 | 0.053218 | 0.053669 | 0.05412 | 0.054571 | 0.055022 | 0.054978 | 0.054934 | 0.054889 | 0.054845 | 0.054801 | 0.054756 | 0.054712 | 0.054668 | 0.054624 | 0.054579 | 0.054535 | 0.054491 | 0.054446 | 0.054402 | 0.054358
| GHP011-144337307 | GHP011 | 0.050245 | 0.050647 | 0.05105 | 0.051452 | 0.051854 | 0.052086 | 0.052317 | 0.052548 | 0.05278 | 0.053011 | 0.053242 | 0.053473 | 0.053705 | 0.053936 | 0.054167 | 0.054399 | 0.05463 | 0.054861 | 0.055093 | 0.055324
| GHP011-144337672 | GHP011 | 0.063153 | 0.063554 | 0.063956 | 0.064357 | 0.064759 | 0.064934 | 0.065109 | 0.065285 | 0.06546 | 0.065635 | 0.065811 | 0.065986 | 0.066161 | 0.066337 | 0.066512 | 0.066687 | 0.066863 | 0.067038 | 0.067213 | 0.067389
| GHP011-187048453 | GHP011 | 25.5075 | 25.6981 | 25.8886 | 26.0792 | 26.2697 | 26.3121 | 26.3545 | 26.3969 | 26.4393 | 26.4817 | 26.5241 | 26.5665 | 26.6089 | 26.6513 | 26.6937 | 26.7361 | 26.7785 | 26.8209 | 26.8633 | 26.9057
| GHP011-190579532 | GHP011 | 4.7079 | 4.7465 | 4.785 | 4.8235 | 4.8621 | 4.8607 | 4.8593 | 4.8579 | 4.8565 | 4.8552 | 4.8538 | 4.8524 | 4.851 | 4.8496 | 4.8482 | 4.8468 | 4.8455 | 4.8441 | 4.8427 | 4.8413
| GHP011-62939475 | GHP011 | 4.8219 | 4.8516 | 4.8814 | 4.9111 | 4.9408 | 4.9582 | 4.9755 | 4.9928 | 5.0102 | 5.0275 | 5.0448 | 5.0621 | 5.0795 | 5.0968 | 5.1141 | 5.1315 | 5.1488 | 5.1661 | 5.1835 | 5.2008
| GHP011-72503866 | GHP011 | 0.1152 | 0.11621 | 0.11722 | 0.11823 | 0.11924 | 0.11915 | 0.11905 | 0.11896 | 0.11887 | 0.11878 | 0.11868 | 0.11859 | 0.1185 | 0.11841 | 0.11831 | 0.11822 | 0.11813 | 0.11804 | 0.11794 | 0.11785
| GHP012-190579518 | GHP012 | 30.9983 | 31.2185 | 31.4386 | 31.6587 | 31.8789 | 31.9829 | 32.0869 | 32.1909 | 32.295 | 32.399 | 32.503 | 32.607 | 32.7111 | 32.8151 | 32.9191 | 33.0231 | 33.1271 | 33.2312 | 33.3352 | 33.4392
| GHP012-77546539 | GHP012 | 6.9486 | 6.9848 | 7.021 | 7.0572 | 7.0935 | 7.0937 | 7.0939 | 7.0941 | 7.0943 | 7.0946 | 7.0948 | 7.095 | 7.0952 | 7.0954 | 7.0957 | 7.0959 | 7.0961 | 7.0963 | 7.0965 | 7.0968
| GHP021-130746528 | GHP021 | 10.2125 | 10.2919 | 10.3713 | 10.4506 | 10.53 | 10.5912 | 10.6524 | 10.7136 | 10.7747 | 10.8359 | 10.8971 | 10.9583 | 11.0195 | 11.0807 | 11.1419 | 11.2031 | 11.2642 | 11.3254 | 11.3866 | 11.4478
| GHP021-140732642 | GHP021 | 0.04709 | 0.047392 | 0.047694 | 0.047996 | 0.048298 | 0.048354 | 0.048411 | 0.048468 | 0.048524 | 0.048581 | 0.048637 | 0.048694 | 0.048751 | 0.048807 | 0.048864 | 0.04892 | 0.048977 | 0.049034 | 0.04909 | 0.049147
| GHP021-141034135 | GHP021 | 0.023146 | 0.0233 | 0.023454 | 0.023608 | 0.023762 | 0.023751 | 0.023741 | 0.02373 | 0.023719 | 0.023709 | 0.023698 | 0.023687 | 0.023677 | 0.023666 | 0.023655 | 0.023645 | 0.023634 | 0.023623 | 0.023612 | 0.023602
| GHP021-187048221 | GHP021 | 20.3151 | 20.4474 | 20.5798 | 20.7121 | 20.8444 | 20.839 | 20.8335 | 20.8281 | 20.8226 | 20.8172 | 20.8117 | 20.8063 | 20.8008 | 20.7954 | 20.7899 | 20.7845 | 20.779 | 20.7736 | 20.7681 | 20.7627
| GHP021-190579468 | GHP021 | 7.2513 | 7.3107 | 7.3701 | 7.4294 | 7.4888 | 7.4998 | 7.5109 | 7.5219 | 7.533 | 7.544 | 7.5551 | 7.5661 | 7.5772 | 7.5882 | 7.5993 | 7.6103 | 7.6214 | 7.6324 | 7.6435 | 7.6545
| GHP021-24614163 | GHP021 | 5.269 | 5.2746 | 5.2802 | 5.2857 | 5.2913 | 5.2793 | 5.2673 | 5.2553 | 5.2434 | 5.2314 | 5.2194 | 5.2074 | 5.1954 | 5.1834 | 5.1714 | 5.1594 | 5.1474 | 5.1354 | 5.1234 | 5.1114
| GHP022-141431252 | GHP022 | 0.085461 | 0.086196 | 0.086931 | 0.087666 | 0.088401 | 0.088696 | 0.088992 | 0.089287 | 0.089582 | 0.089878 | 0.090173 | 0.090468 | 0.090764 | 0.091059 | 0.091354 | 0.09165 | 0.091945 | 0.09224 | 0.092536 | 0.092831
| GHP022-141431280 | GHP022 | 0.013485 | 0.013583 | 0.013681 | 0.013778 | 0.013876 | 0.013889 | 0.013902 | 0.013914 | 0.013927 | 0.01394 | 0.013952 | 0.013965 | 0.013978 | 0.01399 | 0.014003 | 0.014016 | 0.014029 | 0.014041 | 0.014054 | 0.014067
| GHP022-188587433 | GHP022 | 10.4682 | 10.5319 | 10.5957 | 10.6594 | 10.7232 | 10.7538 | 10.7844 | 10.8151 | 10.8457 | 10.8763 | 10.9069 | 10.9376 | 10.9682 | 10.9988 | 11.0295 | 11.0601 | 11.0907 | 11.1214 | 11.152 | 11.1826
| GHP022-190579440 | GHP022 | 5.0881 | 5.1261 | 5.164 | 5.202 | 5.2399 | 5.26 | 5.2802 | 5.3003 | 5.3204 | 5.3405 | 5.3607 | 5.3808 | 5.4009 | 5.421 | 5.4412 | 5.4613 | 5.4814 | 5.5016 | 5.5217 | 5.5418
| GHP022-72503462 | GHP022 | 0.17888 | 0.18049 | 0.1821 | 0.1837 | 0.18531 | 0.18592 | 0.18652 | 0.18713 | 0.18773 | 0.18834 | 0.18895 | 0.18955 | 0.19016 | 0.19076 | 0.19137 | 0.19197 | 0.19258 | 0.19319 | 0.19379 | 0.1944
| GL011-15402625 | GL011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL012-15402649 | GL012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL013-15402686 | GL013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL014-15402723 | GL014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL015-15402771 | GL015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL021-15402795 | GL021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL021-24612685 | GL021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL022-15402832 | GL022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL022-24612699 | GL022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL023-15402869 | GL023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GL024-15402919 | GL024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE011-15406891 | GLE011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE012-15406954 | GLE012 | 0.097214 | 0.0982 | 0.099186 | 0.10017 | 0.10116 | 0.10139 | 0.10163 | 0.10187 | 0.1021 | 0.10234 | 0.10258 | 0.10281 | 0.10305 | 0.10328 | 0.10352 | 0.10376 | 0.10399 | 0.10423 | 0.10447 | 0.1047
| GLE012-77546340 | GLE012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE013-15407017 | GLE013 | 100.8882 | 101.6641 | 102.44 | 103.2159 | 103.9918 | 104.0612 | 104.1306 | 104.1999 | 104.2693 | 104.3387 | 104.4081 | 104.4774 | 104.5468 | 104.6162 | 104.6856 | 104.7549 | 104.8243 | 104.8937 | 104.9631 | 105.0324
| GLE021-15407054 | GLE021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE023-15407104 | GLE023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE024-15407167 | GLE024 | 26.9534 | 26.9705 | 26.9875 | 27.0046 | 27.0216 | 26.9806 | 26.9395 | 26.8984 | 26.8573 | 26.8163 | 26.7752 | 26.7341 | 26.693 | 26.652 | 26.6109 | 26.5698 | 26.5287 | 26.4877 | 26.4466 | 26.4055
| GLE024-24612325 | GLE024 | 3.159 | 3.1649 | 3.1707 | 3.1765 | 3.1824 | 3.1698 | 3.1573 | 3.1448 | 3.1323 | 3.1198 | 3.1073 | 3.0947 | 3.0822 | 3.0697 | 3.0572 | 3.0447 | 3.0322 | 3.0196 | 3.0071 | 2.9946
| GLE031-15407178 | GLE031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE031-24612339 | GLE031 | 2.2104 | 2.2148 | 2.2191 | 2.2235 | 2.2278 | 2.2185 | 2.2092 | 2.1999 | 2.1906 | 2.1814 | 2.1721 | 2.1628 | 2.1535 | 2.1442 | 2.1349 | 2.1256 | 2.1163 | 2.1071 | 2.0978 | 2.0885
| GLE032-15407241 | GLE032 | 2.202 | 2.2092 | 2.2165 | 2.2238 | 2.2311 | 2.229 | 2.227 | 2.2249 | 2.2229 | 2.2208 | 2.2188 | 2.2167 | 2.2146 | 2.2126 | 2.2105 | 2.2085 | 2.2064 | 2.2044 | 2.2023 | 2.2003
| GLE032-24612713 | GLE032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLE033-15407304 | GLE033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB011-24597032 | GSB011 | 16.5144 | 16.6367 | 16.7589 | 16.8812 | 17.0034 | 17.1171 | 17.2308 | 17.3445 | 17.4582 | 17.5718 | 17.6855 | 17.7992 | 17.9129 | 18.0266 | 18.1402 | 18.2539 | 18.3676 | 18.4813 | 18.595 | 18.7086
| GSB011-24613746 | GSB011 | 42.2699 | 42.6493 | 43.0287 | 43.4081 | 43.7875 | 44.1582 | 44.5289 | 44.8996 | 45.2703 | 45.641 | 46.0117 | 46.3824 | 46.7531 | 47.1237 | 47.4944 | 47.8651 | 48.2358 | 48.6065 | 48.9772 | 49.3479
| GSB011-74623144 | GSB011 | 14.6589 | 14.7379 | 14.8169 | 14.896 | 14.975 | 15.042 | 15.109 | 15.1759 | 15.2429 | 15.3099 | 15.3769 | 15.4438 | 15.5108 | 15.5778 | 15.6447 | 15.7117 | 15.7787 | 15.8457 | 15.9126 | 15.9796
| GSB011-74623154 | GSB011 | 49.4531 | 49.8845 | 50.3159 | 50.7474 | 51.1788 | 51.617 | 52.0553 | 52.4935 | 52.9317 | 53.37 | 53.8082 | 54.2465 | 54.6847 | 55.123 | 55.5612 | 55.9994 | 56.4377 | 56.8759 | 57.3142 | 57.7524
| GSB012-181419068 | GSB012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSB012-24607348 | GSB012 | 215.4672 | 216.967 | 218.4668 | 219.9666 | 221.4664 | 221.6852 | 221.9041 | 222.1229 | 222.3417 | 222.5606 | 222.7794 | 222.9983 | 223.2171 | 223.436 | 223.6548 | 223.8737 | 224.0925 | 224.3114 | 224.5302 | 224.749
| GSB012-24607362 | GSB012 | 2.5537 | 2.5762 | 2.5988 | 2.6213 | 2.6438 | 2.6433 | 2.6427 | 2.6421 | 2.6416 | 2.641 | 2.6404 | 2.6399 | 2.6393 | 2.6387 | 2.6382 | 2.6376 | 2.637 | 2.6365 | 2.6359 | 2.6353
| GSB012-72499030 | GSB012 | 0.062535 | 0.06311 | 0.063685 | 0.06426 | 0.064835 | 0.065088 | 0.065341 | 0.065593 | 0.065846 | 0.066099 | 0.066351 | 0.066604 | 0.066857 | 0.067109 | 0.067362 | 0.067615 | 0.067867 | 0.06812 | 0.068372 | 0.068625
| GSB012-72499395 | GSB012 | 0.14122 | 0.1425 | 0.14378 | 0.14506 | 0.14634 | 0.1463 | 0.14627 | 0.14624 | 0.1462 | 0.14617 | 0.14613 | 0.1461 | 0.14607 | 0.14603 | 0.146 | 0.14597 | 0.14593 | 0.1459 | 0.14586 | 0.14583
| GSB012-74623277 | GSB012 | 101.9962 | 102.6794 | 103.3626 | 104.0457 | 104.7289 | 105.0405 | 105.3521 | 105.6638 | 105.9754 | 106.2871 | 106.5987 | 106.9104 | 107.222 | 107.5336 | 107.8453 | 108.1569 | 108.4686 | 108.7802 | 109.0919 | 109.4035
| GSB012-77736949 | GSB012 | 0.33165 | 0.33424 | 0.33682 | 0.33941 | 0.342 | 0.34465 | 0.3473 | 0.34995 | 0.3526 | 0.35525 | 0.3579 | 0.36055 | 0.3632 | 0.36586 | 0.36851 | 0.37116 | 0.37381 | 0.37646 | 0.37911 | 0.38176
| GSB012-85320967 | GSB012 | 0.0012194 | 0.0012327 | 0.001246 | 0.0012594 | 0.0012727 | 0.0012775 | 0.0012824 | 0.0012872 | 0.001292 | 0.0012969 | 0.0013017 | 0.0013065 | 0.0013114 | 0.0013162 | 0.001321 | 0.0013259 | 0.0013307 | 0.0013355 | 0.0013403 | 0.0013452
| GSB013-74623435 | GSB013 | 192.0134 | 193.3737 | 194.734 | 196.0943 | 197.4546 | 198.0889 | 198.7231 | 199.3574 | 199.9917 | 200.626 | 201.2603 | 201.8946 | 202.5289 | 203.1631 | 203.7974 | 204.4317 | 205.066 | 205.7003 | 206.3346 | 206.9688
| GSB014-163179564 | GSB014 | 0.0038196 | 0.0038622 | 0.0039049 | 0.0039476 | 0.0039902 | 0.0040148 | 0.0040393 | 0.0040638 | 0.0040884 | 0.0041129 | 0.0041374 | 0.004162 | 0.0041865 | 0.004211 | 0.0042356 | 0.0042601 | 0.0042846 | 0.0043091 | 0.0043337 | 0.0043582
| GSB014-194965507 | GSB014 | 71.116 | 71.6541 | 72.1922 | 72.7303 | 73.2684 | 73.8213 | 74.3742 | 74.9271 | 75.48 | 76.0329 | 76.5858 | 77.1387 | 77.6915 | 78.2444 | 78.7973 | 79.3502 | 79.9031 | 80.456 | 81.0089 | 81.5618
| GSB014-194965541 | GSB014 | 41.1881 | 41.4392 | 41.6904 | 41.9416 | 42.1927 | 42.3956 | 42.5984 | 42.8012 | 43.004 | 43.2068 | 43.4097 | 43.6125 | 43.8153 | 44.0181 | 44.2209 | 44.4238 | 44.6266 | 44.8294 | 45.0322 | 45.235
| GSB014-194965599 | GSB014 | 18.7011 | 18.8541 | 19.0071 | 19.1601 | 19.3131 | 19.4706 | 19.628 | 19.7854 | 19.9429 | 20.1003 | 20.2577 | 20.4152 | 20.5726 | 20.73 | 20.8875 | 21.0449 | 21.2023 | 21.3597 | 21.5172 | 21.6746
| GSB014-73768594 | GSB014 | 0.21609 | 0.21843 | 0.22077 | 0.22312 | 0.22546 | 0.22671 | 0.22795 | 0.2292 | 0.23045 | 0.2317 | 0.23295 | 0.2342 | 0.23545 | 0.23669 | 0.23794 | 0.23919 | 0.24044 | 0.24169 | 0.24294 | 0.24419
| GSB014-74623507 | GSB014 | 24.1771 | 24.329 | 24.4809 | 24.6329 | 24.7848 | 24.902 | 25.0192 | 25.1365 | 25.2537 | 25.3709 | 25.4881 | 25.6054 | 25.7226 | 25.8398 | 25.957 | 26.0742 | 26.1915 | 26.3087 | 26.4259 | 26.5431
| HSM001-108341890 | HSM001 | 0.31045 | 0.31252 | 0.31458 | 0.31665 | 0.31871 | 0.31896 | 0.31922 | 0.31947 | 0.31972 | 0.31998 | 0.32023 | 0.32048 | 0.32074 | 0.32099 | 0.32124 | 0.3215 | 0.32175 | 0.322 | 0.32226 | 0.32251
| HSM001-15416529 | HSM001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-15416542 | HSM001 | 21.2253 | 21.2718 | 21.3182 | 21.3647 | 21.4112 | 21.3833 | 21.3554 | 21.3275 | 21.2996 | 21.2717 | 21.2438 | 21.2158 | 21.1879 | 21.16 | 21.1321 | 21.1042 | 21.0763 | 21.0484 | 21.0205 | 20.9926
| HSM001-157535060 | HSM001 | 0.18575 | 0.18757 | 0.1894 | 0.19122 | 0.19305 | 0.19327 | 0.1935 | 0.19373 | 0.19396 | 0.19419 | 0.19442 | 0.19465 | 0.19488 | 0.19511 | 0.19533 | 0.19556 | 0.19579 | 0.19602 | 0.19625 | 0.19648
| HSM001-157535228 | HSM001 | 0.21744 | 0.21922 | 0.221 | 0.22278 | 0.22457 | 0.22511 | 0.22566 | 0.2262 | 0.22675 | 0.22729 | 0.22784 | 0.22838 | 0.22893 | 0.22948 | 0.23002 | 0.23057 | 0.23111 | 0.23166 | 0.2322 | 0.23275
| HSM001-157577413 | HSM001 | 0.13277 | 0.13377 | 0.13476 | 0.13576 | 0.13675 | 0.13699 | 0.13723 | 0.13747 | 0.13771 | 0.13795 | 0.13819 | 0.13843 | 0.13867 | 0.1389 | 0.13914 | 0.13938 | 0.13962 | 0.13986 | 0.1401 | 0.14034
| HSM001-157577658 | HSM001 | 0.17247 | 0.1737 | 0.17492 | 0.17615 | 0.17738 | 0.17738 | 0.17739 | 0.17739 | 0.17739 | 0.17739 | 0.1774 | 0.1774 | 0.1774 | 0.17741 | 0.17741 | 0.17741 | 0.17741 | 0.17742 | 0.17742 | 0.17742
| HSM001-157598665 | HSM001 | 0.037278 | 0.037648 | 0.038018 | 0.038388 | 0.038758 | 0.038793 | 0.038827 | 0.038862 | 0.038896 | 0.03893 | 0.038965 | 0.038999 | 0.039034 | 0.039068 | 0.039102 | 0.039137 | 0.039171 | 0.039206 | 0.03924 | 0.039275
| HSM001-157598865 | HSM001 | 0.054295 | 0.054859 | 0.055424 | 0.055989 | 0.056554 | 0.056535 | 0.056516 | 0.056497 | 0.056478 | 0.056459 | 0.05644 | 0.056421 | 0.056402 | 0.056382 | 0.056363 | 0.056344 | 0.056325 | 0.056306 | 0.056287 | 0.056268
| HSM001-157598965 | HSM001 | 0.13598 | 0.13725 | 0.13851 | 0.13978 | 0.14104 | 0.14119 | 0.14134 | 0.14149 | 0.14163 | 0.14178 | 0.14193 | 0.14207 | 0.14222 | 0.14237 | 0.14251 | 0.14266 | 0.14281 | 0.14295 | 0.1431 | 0.14325
| HSM001-163581806 | HSM001 | 0.0036009 | 0.0036321 | 0.0036632 | 0.0036943 | 0.0037255 | 0.003736 | 0.0037464 | 0.0037569 | 0.0037673 | 0.0037778 | 0.0037883 | 0.0037987 | 0.0038092 | 0.0038196 | 0.0038301 | 0.0038406 | 0.003851 | 0.0038615 | 0.0038719 | 0.0038824
| HSM001-163582048 | HSM001 | 0.011908 | 0.012011 | 0.012115 | 0.012219 | 0.012322 | 0.012341 | 0.012359 | 0.012377 | 0.012396 | 0.012414 | 0.012432 | 0.01245 | 0.012469 | 0.012487 | 0.012505 | 0.012524 | 0.012542 | 0.01256 | 0.012579 | 0.012597
| HSM001-167869770 | HSM001 | 0.049673 | 0.050014 | 0.050354 | 0.050695 | 0.051035 | 0.051204 | 0.051373 | 0.051543 | 0.051712 | 0.051881 | 0.05205 | 0.052219 | 0.052388 | 0.052557 | 0.052726 | 0.052895 | 0.053064 | 0.053234 | 0.053403 | 0.053572
| HSM001-167869862 | HSM001 | 0.098679 | 0.099477 | 0.10028 | 0.10108 | 0.10187 | 0.1019 | 0.10193 | 0.10196 | 0.10199 | 0.10202 | 0.10205 | 0.10208 | 0.10211 | 0.10214 | 0.10217 | 0.1022 | 0.10223 | 0.10226 | 0.10229 | 0.10232
| HSM001-192496053 | HSM001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-24613473 | HSM001 | 6.4463 | 6.5044 | 6.5625 | 6.6206 | 6.6786 | 6.6806 | 6.6826 | 6.6846 | 6.6866 | 6.6886 | 6.6906 | 6.6926 | 6.6946 | 6.6966 | 6.6986 | 6.7006 | 6.7026 | 6.7046 | 6.7066 | 6.7086
| HSM001-41021978 | HSM001 | 11.0669 | 11.1603 | 11.2538 | 11.3472 | 11.4407 | 11.4484 | 11.4562 | 11.4639 | 11.4717 | 11.4794 | 11.4872 | 11.4949 | 11.5027 | 11.5104 | 11.5182 | 11.5259 | 11.5337 | 11.5414 | 11.5492 | 11.5569
| HSM002-15416605 | HSM002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-15416618 | HSM002 | 48.9981 | 49.2854 | 49.5728 | 49.8602 | 50.1475 | 50.0862 | 50.0249 | 49.9635 | 49.9022 | 49.8408 | 49.7795 | 49.7182 | 49.6568 | 49.5955 | 49.5341 | 49.4728 | 49.4115 | 49.3501 | 49.2888 | 49.2274
| HSM002-155422817 | HSM002 | 0.06223 | 0.06256 | 0.062889 | 0.063219 | 0.063548 | 0.063182 | 0.062816 | 0.06245 | 0.062084 | 0.061719 | 0.061353 | 0.060987 | 0.060621 | 0.060255 | 0.059889 | 0.059523 | 0.059157 | 0.058791 | 0.058425 | 0.058059
| HSM002-157400246 | HSM002 | 0.0066118 | 0.0066567 | 0.0067015 | 0.0067464 | 0.0067912 | 0.006791 | 0.0067908 | 0.0067906 | 0.0067904 | 0.0067902 | 0.00679 | 0.0067898 | 0.0067896 | 0.0067894 | 0.0067892 | 0.006789 | 0.0067888 | 0.0067886 | 0.0067884 | 0.0067882
| HSM002-157400607 | HSM002 | 0.0073592 | 0.0073953 | 0.0074314 | 0.0074674 | 0.0075035 | 0.0074948 | 0.0074861 | 0.0074775 | 0.0074688 | 0.0074601 | 0.0074515 | 0.0074428 | 0.0074341 | 0.0074255 | 0.0074168 | 0.0074081 | 0.0073995 | 0.0073908 | 0.0073821 | 0.0073735
| HSM002-157400755 | HSM002 | 0.083523 | 0.084154 | 0.084785 | 0.085416 | 0.086047 | 0.085929 | 0.085812 | 0.085694 | 0.085577 | 0.085459 | 0.085342 | 0.085224 | 0.085107 | 0.084989 | 0.084872 | 0.084754 | 0.084637 | 0.084519 | 0.084402 | 0.084284
| HSM002-157998943 | HSM002 | 0.0045916 | 0.004615 | 0.0046383 | 0.0046617 | 0.0046851 | 0.0046599 | 0.0046346 | 0.0046094 | 0.0045841 | 0.0045589 | 0.0045336 | 0.0045084 | 0.0044831 | 0.0044578 | 0.0044326 | 0.0044073 | 0.0043821 | 0.0043568 | 0.0043316 | 0.0043063
| HSM002-157999372 | HSM002 | 0.025115 | 0.025264 | 0.025414 | 0.025563 | 0.025713 | 0.025652 | 0.025591 | 0.02553 | 0.025469 | 0.025408 | 0.025347 | 0.025286 | 0.025225 | 0.025165 | 0.025104 | 0.025043 | 0.024982 | 0.024921 | 0.02486 | 0.024799
| HSM002-157999534 | HSM002 | 0.002863 | 0.00288 | 0.0028971 | 0.0029141 | 0.0029311 | 0.0029279 | 0.0029247 | 0.0029214 | 0.0029182 | 0.002915 | 0.0029117 | 0.0029085 | 0.0029053 | 0.0029021 | 0.0028988 | 0.0028956 | 0.0028924 | 0.0028891 | 0.0028859 | 0.0028827
| HSM002-158058496 | HSM002 | 0.0010209 | 0.0010233 | 0.0010257 | 0.001028 | 0.0010304 | 0.0010276 | 0.0010249 | 0.0010221 | 0.0010194 | 0.0010166 | 0.0010138 | 0.0010111 | 0.0010083 | 0.0010056 | 0.0010028 | 0.001 | 0.00099728 | 0.00099452 | 0.00099176 | 0.000989
| HSM002-158058597 | HSM002 | 0.0079667 | 0.0080069 | 0.0080471 | 0.0080873 | 0.0081275 | 0.0081079 | 0.0080882 | 0.0080685 | 0.0080489 | 0.0080292 | 0.0080095 | 0.0079898 | 0.0079702 | 0.0079505 | 0.0079308 | 0.0079111 | 0.0078915 | 0.0078718 | 0.0078521 | 0.0078324
| HSM002-158110114 | HSM002 | 0.025669 | 0.025805 | 0.02594 | 0.026076 | 0.026212 | 0.026094 | 0.025976 | 0.025858 | 0.02574 | 0.025622 | 0.025504 | 0.025386 | 0.025268 | 0.02515 | 0.025032 | 0.024914 | 0.024796 | 0.024677 | 0.024559 | 0.024441
| HSM002-158110202 | HSM002 | 0.0023122 | 0.002324 | 0.0023358 | 0.0023477 | 0.0023595 | 0.0023478 | 0.0023361 | 0.0023245 | 0.0023128 | 0.0023011 | 0.0022894 | 0.0022777 | 0.0022661 | 0.0022544 | 0.0022427 | 0.002231 | 0.0022194 | 0.0022077 | 0.002196 | 0.0021843
| HSM002-158110374 | HSM002 | 0.010632 | 0.010689 | 0.010745 | 0.010801 | 0.010858 | 0.010801 | 0.010743 | 0.010686 | 0.010629 | 0.010572 | 0.010515 | 0.010457 | 0.0104 | 0.010343 | 0.010286 | 0.010229 | 0.010171 | 0.010114 | 0.010057 | 0.0099999
| HSM002-158110591 | HSM002 | 0.0048068 | 0.0048342 | 0.0048616 | 0.004889 | 0.0049163 | 0.0048899 | 0.0048635 | 0.0048371 | 0.0048107 | 0.0047843 | 0.0047578 | 0.0047314 | 0.004705 | 0.0046786 | 0.0046522 | 0.0046257 | 0.0045993 | 0.0045729 | 0.0045465 | 0.0045201
| HSM002-158110691 | HSM002 | 0.17495 | 0.17591 | 0.17687 | 0.17784 | 0.1788 | 0.17881 | 0.17883 | 0.17884 | 0.17886 | 0.17887 | 0.17889 | 0.1789 | 0.17892 | 0.17893 | 0.17895 | 0.17896 | 0.17897 | 0.17899 | 0.179 | 0.17902
| HSM002-158126654 | HSM002 | 0.035665 | 0.035916 | 0.036167 | 0.036418 | 0.036669 | 0.036671 | 0.036672 | 0.036674 | 0.036675 | 0.036677 | 0.036678 | 0.03668 | 0.036681 | 0.036682 | 0.036684 | 0.036685 | 0.036687 | 0.036688 | 0.03669 | 0.036691
| HSM002-158165458 | HSM002 | 0.63914 | 0.64201 | 0.64488 | 0.64775 | 0.65062 | 0.65007 | 0.64952 | 0.64897 | 0.64843 | 0.64788 | 0.64733 | 0.64678 | 0.64623 | 0.64568 | 0.64513 | 0.64459 | 0.64404 | 0.64349 | 0.64294 | 0.64239
| HSM002-158165593 | HSM002 | 0.00014512 | 0.00014608 | 0.00014704 | 0.000148 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896
| HSM002-163503065 | HSM002 | 0.0044879 | 0.0045136 | 0.0045392 | 0.0045649 | 0.0045906 | 0.0045722 | 0.0045538 | 0.0045354 | 0.004517 | 0.0044986 | 0.0044802 | 0.0044618 | 0.0044435 | 0.0044251 | 0.0044067 | 0.0043883 | 0.0043699 | 0.0043515 | 0.0043331 | 0.0043147
| HSM002-163560034 | HSM002 | 0.27182 | 0.27324 | 0.27465 | 0.27607 | 0.27748 | 0.27606 | 0.27464 | 0.27323 | 0.27181 | 0.27039 | 0.26897 | 0.26755 | 0.26614 | 0.26472 | 0.2633 | 0.26188 | 0.26046 | 0.25905 | 0.25763 | 0.25621
| HSM002-24600694 | HSM002 | 9.2604 | 9.3085 | 9.3566 | 9.4047 | 9.4528 | 9.4295 | 9.4063 | 9.3831 | 9.3598 | 9.3366 | 9.3134 | 9.2901 | 9.2669 | 9.2437 | 9.2204 | 9.1972 | 9.1739 | 9.1507 | 9.1275 | 9.1042
| HSM002-24601420 | HSM002 | 17.6816 | 17.7643 | 17.8471 | 17.9298 | 18.0125 | 17.994 | 17.9754 | 17.9568 | 17.9382 | 17.9197 | 17.9011 | 17.8825 | 17.8639 | 17.8454 | 17.8268 | 17.8082 | 17.7896 | 17.771 | 17.7525 | 17.7339
| HSM003-15416492 | HSM003 | 41.2835 | 41.6346 | 41.9858 | 42.337 | 42.6882 | 42.7631 | 42.838 | 42.9129 | 42.9878 | 43.0626 | 43.1375 | 43.2124 | 43.2873 | 43.3622 | 43.4371 | 43.512 | 43.5868 | 43.6617 | 43.7366 | 43.8115
| HSM003-160653285 | HSM003 | 0.19408 | 0.19591 | 0.19774 | 0.19957 | 0.2014 | 0.20082 | 0.20023 | 0.19965 | 0.19906 | 0.19847 | 0.19789 | 0.1973 | 0.19671 | 0.19613 | 0.19554 | 0.19496 | 0.19437 | 0.19378 | 0.1932 | 0.19261
| HSM003-160653643 | HSM003 | 0.10268 | 0.10364 | 0.1046 | 0.10555 | 0.10651 | 0.10626 | 0.10602 | 0.10577 | 0.10552 | 0.10528 | 0.10503 | 0.10478 | 0.10454 | 0.10429 | 0.10404 | 0.1038 | 0.10355 | 0.1033 | 0.10306 | 0.10281
| HSM003-160677450 | HSM003 | 0.1715 | 0.17325 | 0.17501 | 0.17676 | 0.17851 | 0.17787 | 0.17723 | 0.17659 | 0.17595 | 0.17531 | 0.17467 | 0.17403 | 0.17339 | 0.17275 | 0.17211 | 0.17147 | 0.17083 | 0.17019 | 0.16955 | 0.16891
| HSM003-160677580 | HSM003 | 0.074835 | 0.075761 | 0.076687 | 0.077613 | 0.078538 | 0.078349 | 0.07816 | 0.077971 | 0.077782 | 0.077593 | 0.077404 | 0.077215 | 0.077026 | 0.076836 | 0.076647 | 0.076458 | 0.076269 | 0.07608 | 0.075891 | 0.075702
| HSM003-160677831 | HSM003 | 0.1195 | 0.12069 | 0.12187 | 0.12306 | 0.12425 | 0.12432 | 0.1244 | 0.12447 | 0.12455 | 0.12463 | 0.1247 | 0.12478 | 0.12486 | 0.12493 | 0.12501 | 0.12509 | 0.12516 | 0.12524 | 0.12532 | 0.12539
| HSM003-160683184 | HSM003 | 0.10618 | 0.10733 | 0.10848 | 0.10963 | 0.11078 | 0.11034 | 0.1099 | 0.10946 | 0.10902 | 0.10858 | 0.10814 | 0.10771 | 0.10727 | 0.10683 | 0.10639 | 0.10595 | 0.10551 | 0.10508 | 0.10464 | 0.1042
| HSM003-160683337 | HSM003 | 0.11561 | 0.1167 | 0.11779 | 0.11888 | 0.11998 | 0.11975 | 0.11953 | 0.11931 | 0.11908 | 0.11886 | 0.11864 | 0.11841 | 0.11819 | 0.11797 | 0.11774 | 0.11752 | 0.1173 | 0.11707 | 0.11685 | 0.11663
| HSM003-160683747 | HSM003 | 0.17274 | 0.17464 | 0.17654 | 0.17845 | 0.18035 | 0.17981 | 0.17926 | 0.17872 | 0.17818 | 0.17764 | 0.1771 | 0.17655 | 0.17601 | 0.17547 | 0.17493 | 0.17439 | 0.17384 | 0.1733 | 0.17276 | 0.17222
| HSM003-160720939 | HSM003 | 0.22693 | 0.22888 | 0.23084 | 0.23279 | 0.23475 | 0.23423 | 0.23372 | 0.2332 | 0.23268 | 0.23217 | 0.23165 | 0.23114 | 0.23062 | 0.2301 | 0.22959 | 0.22907 | 0.22855 | 0.22804 | 0.22752 | 0.22701
| HSM003-160721106 | HSM003 | 0.10868 | 0.10976 | 0.11084 | 0.11192 | 0.113 | 0.11264 | 0.11227 | 0.1119 | 0.11153 | 0.11116 | 0.11079 | 0.11042 | 0.11005 | 0.10968 | 0.10931 | 0.10894 | 0.10857 | 0.1082 | 0.10783 | 0.10746
| HSM003-160828901 | HSM003 | 0.033292 | 0.03368 | 0.034069 | 0.034457 | 0.034845 | 0.034772 | 0.0347 | 0.034627 | 0.034554 | 0.034481 | 0.034409 | 0.034336 | 0.034263 | 0.034191 | 0.034118 | 0.034045 | 0.033972 | 0.0339 | 0.033827 | 0.033754
| HSM003-160875785 | HSM003 | 0.097049 | 0.097828 | 0.098607 | 0.099387 | 0.10017 | 0.10016 | 0.10015 | 0.10014 | 0.10013 | 0.10012 | 0.10011 | 0.10009 | 0.10008 | 0.10007 | 0.10006 | 0.10005 | 0.10004 | 0.10003 | 0.10002 | 0.10001
| HSM003-160931238 | HSM003 | 0.16934 | 0.17118 | 0.17302 | 0.17486 | 0.17671 | 0.17605 | 0.17539 | 0.17474 | 0.17408 | 0.17342 | 0.17276 | 0.17211 | 0.17145 | 0.17079 | 0.17013 | 0.16948 | 0.16882 | 0.16816 | 0.16751 | 0.16685
| HSM003-161008360 | HSM003 | 0.1509 | 0.15229 | 0.15367 | 0.15506 | 0.15645 | 0.1563 | 0.15615 | 0.156 | 0.15585 | 0.1557 | 0.15555 | 0.1554 | 0.15525 | 0.1551 | 0.15495 | 0.1548 | 0.15465 | 0.1545 | 0.15435 | 0.1542
| HSM003-161008735 | HSM003 | 0.069161 | 0.07002 | 0.07088 | 0.07174 | 0.0726 | 0.072426 | 0.072253 | 0.07208 | 0.071907 | 0.071734 | 0.071561 | 0.071388 | 0.071215 | 0.071041 | 0.070868 | 0.070695 | 0.070522 | 0.070349 | 0.070176 | 0.070003
| HSM003-161094121 | HSM003 | 3.1274e-05 | 3.163e-05 | 3.1987e-05 | 3.2343e-05 | 3.27e-05 | 3.261e-05 | 3.252e-05 | 3.243e-05 | 3.234e-05 | 3.225e-05 | 3.216e-05 | 3.207e-05 | 3.198e-05 | 3.189e-05 | 3.18e-05 | 3.171e-05 | 3.162e-05 | 3.153e-05 | 3.144e-05 | 3.135e-05
| HSM003-161094233 | HSM003 | 0.017985 | 0.01817 | 0.018355 | 0.018539 | 0.018724 | 0.018663 | 0.018602 | 0.018541 | 0.018479 | 0.018418 | 0.018357 | 0.018296 | 0.018235 | 0.018173 | 0.018112 | 0.018051 | 0.01799 | 0.017929 | 0.017867 | 0.017806
| HSM003-163378469 | HSM003 | 0.12136 | 0.12282 | 0.12429 | 0.12575 | 0.12721 | 0.12694 | 0.12668 | 0.12641 | 0.12615 | 0.12588 | 0.12562 | 0.12536 | 0.12509 | 0.12483 | 0.12456 | 0.1243 | 0.12403 | 0.12377 | 0.1235 | 0.12324
| HSM003-163378579 | HSM003 | 0.064971 | 0.065665 | 0.066359 | 0.067053 | 0.067747 | 0.067641 | 0.067534 | 0.067427 | 0.06732 | 0.067214 | 0.067107 | 0.067 | 0.066894 | 0.066787 | 0.06668 | 0.066573 | 0.066467 | 0.06636 | 0.066253 | 0.066146
| HSM003-164469812 | HSM003 | 0.0073203 | 0.007399 | 0.0074777 | 0.0075564 | 0.0076352 | 0.0076139 | 0.0075927 | 0.0075715 | 0.0075503 | 0.0075291 | 0.0075079 | 0.0074867 | 0.0074655 | 0.0074443 | 0.0074231 | 0.0074019 | 0.0073806 | 0.0073594 | 0.0073382 | 0.007317
| HSM003-164470113 | HSM003 | 0.0051342 | 0.0051881 | 0.005242 | 0.0052958 | 0.0053497 | 0.0053294 | 0.0053091 | 0.0052888 | 0.0052685 | 0.0052482 | 0.0052279 | 0.0052076 | 0.0051873 | 0.005167 | 0.0051467 | 0.0051264 | 0.0051061 | 0.0050858 | 0.0050655 | 0.0050451
| HSM003-24600316 | HSM003 | 4.7606 | 4.8023 | 4.844 | 4.8857 | 4.9273 | 4.9211 | 4.9148 | 4.9085 | 4.9022 | 4.896 | 4.8897 | 4.8834 | 4.8772 | 4.8709 | 4.8646 | 4.8583 | 4.8521 | 4.8458 | 4.8395 | 4.8332
| HSM003-24601084 | HSM003 | 22.2997 | 22.4692 | 22.6387 | 22.8082 | 22.9777 | 22.901 | 22.8244 | 22.7477 | 22.6711 | 22.5944 | 22.5178 | 22.4411 | 22.3644 | 22.2878 | 22.2111 | 22.1345 | 22.0578 | 21.9812 | 21.9045 | 21.8279
| HSM003-24601658 | HSM003 | 0.67565 | 0.68212 | 0.68859 | 0.69506 | 0.70154 | 0.69905 | 0.69656 | 0.69407 | 0.69159 | 0.6891 | 0.68661 | 0.68413 | 0.68164 | 0.67915 | 0.67667 | 0.67418 | 0.67169 | 0.66921 | 0.66672 | 0.66423
| HSM003-24601840 | HSM003 | 4.0773 | 4.1085 | 4.1398 | 4.1711 | 4.2023 | 4.1866 | 4.1709 | 4.1551 | 4.1394 | 4.1236 | 4.1079 | 4.0921 | 4.0764 | 4.0606 | 4.0449 | 4.0291 | 4.0134 | 3.9976 | 3.9819 | 3.9661
| HSM004-15416655 | HSM004 | 71.0275 | 71.5909 | 72.1543 | 72.7178 | 73.2812 | 73.1893 | 73.0974 | 73.0054 | 72.9135 | 72.8215 | 72.7296 | 72.6377 | 72.5457 | 72.4538 | 72.3619 | 72.2699 | 72.178 | 72.0861 | 71.9941 | 71.9022
| HSM004-155422230 | HSM004 | 0.0078584 | 0.0079034 | 0.0079483 | 0.0079932 | 0.0080382 | 0.0079912 | 0.0079442 | 0.0078971 | 0.0078501 | 0.0078031 | 0.0077561 | 0.0077091 | 0.0076621 | 0.007615 | 0.007568 | 0.007521 | 0.007474 | 0.007427 | 0.00738 | 0.007333
| HSM004-159429141 | HSM004 | 0.096835 | 0.097572 | 0.098308 | 0.099045 | 0.099782 | 0.09991 | 0.10004 | 0.10017 | 0.10029 | 0.10042 | 0.10055 | 0.10068 | 0.10081 | 0.10094 | 0.10106 | 0.10119 | 0.10132 | 0.10145 | 0.10158 | 0.1017
| HSM004-159429252 | HSM004 | 0.12528 | 0.12594 | 0.1266 | 0.12726 | 0.12791 | 0.1274 | 0.1269 | 0.12639 | 0.12588 | 0.12537 | 0.12487 | 0.12436 | 0.12385 | 0.12334 | 0.12283 | 0.12233 | 0.12182 | 0.12131 | 0.1208 | 0.1203
| HSM004-159452345 | HSM004 | 0.22264 | 0.22403 | 0.22542 | 0.22682 | 0.22821 | 0.22805 | 0.22789 | 0.22773 | 0.22757 | 0.2274 | 0.22724 | 0.22708 | 0.22692 | 0.22676 | 0.2266 | 0.22644 | 0.22627 | 0.22611 | 0.22595 | 0.22579
| HSM004-159452484 | HSM004 | 0.0089201 | 0.0089901 | 0.0090601 | 0.0091301 | 0.0092001 | 0.0092042 | 0.0092082 | 0.0092123 | 0.0092164 | 0.0092205 | 0.0092246 | 0.0092287 | 0.0092328 | 0.0092369 | 0.009241 | 0.009245 | 0.0092491 | 0.0092532 | 0.0092573 | 0.0092614
| HSM004-159452607 | HSM004 | 0.027067 | 0.02716 | 0.027252 | 0.027345 | 0.027438 | 0.027327 | 0.027216 | 0.027105 | 0.026994 | 0.026882 | 0.026771 | 0.02666 | 0.026549 | 0.026438 | 0.026327 | 0.026216 | 0.026105 | 0.025994 | 0.025883 | 0.025772
| HSM004-159452714 | HSM004 | 0.0066399 | 0.0066812 | 0.0067226 | 0.0067639 | 0.0068053 | 0.006812 | 0.0068188 | 0.0068256 | 0.0068323 | 0.0068391 | 0.0068458 | 0.0068526 | 0.0068593 | 0.0068661 | 0.0068729 | 0.0068796 | 0.0068864 | 0.0068931 | 0.0068999 | 0.0069067
| HSM004-160294257 | HSM004 | 0.36802 | 0.37019 | 0.37236 | 0.37453 | 0.3767 | 0.37672 | 0.37674 | 0.37675 | 0.37677 | 0.37679 | 0.37681 | 0.37682 | 0.37684 | 0.37686 | 0.37687 | 0.37689 | 0.37691 | 0.37692 | 0.37694 | 0.37696
| HSM004-160411068 | HSM004 | 0.062204 | 0.06259 | 0.062976 | 0.063362 | 0.063748 | 0.063743 | 0.063739 | 0.063735 | 0.063731 | 0.063726 | 0.063722 | 0.063718 | 0.063714 | 0.06371 | 0.063705 | 0.063701 | 0.063697 | 0.063693 | 0.063688 | 0.063684
| HSM004-160411194 | HSM004 | 0.074037 | 0.074633 | 0.07523 | 0.075827 | 0.076424 | 0.075798 | 0.075173 | 0.074548 | 0.073922 | 0.073297 | 0.072672 | 0.072046 | 0.071421 | 0.070796 | 0.07017 | 0.069545 | 0.06892 | 0.068294 | 0.067669 | 0.067044
| HSM004-160424470 | HSM004 | 0.59478 | 0.59843 | 0.60208 | 0.60572 | 0.60937 | 0.60946 | 0.60955 | 0.60964 | 0.60972 | 0.60981 | 0.6099 | 0.60999 | 0.61008 | 0.61017 | 0.61026 | 0.61035 | 0.61043 | 0.61052 | 0.61061 | 0.6107
| HSM004-160437576 | HSM004 | 0.057415 | 0.057822 | 0.058229 | 0.058635 | 0.059042 | 0.058731 | 0.05842 | 0.058109 | 0.057798 | 0.057487 | 0.057176 | 0.056865 | 0.056554 | 0.056243 | 0.055932 | 0.055621 | 0.05531 | 0.054999 | 0.054688 | 0.054377
| HSM004-160437658 | HSM004 | 0.11257 | 0.11324 | 0.11392 | 0.1146 | 0.11528 | 0.11467 | 0.11407 | 0.11347 | 0.11286 | 0.11226 | 0.11166 | 0.11105 | 0.11045 | 0.10985 | 0.10924 | 0.10864 | 0.10804 | 0.10743 | 0.10683 | 0.10623
| HSM004-160438050 | HSM004 | 0.39154 | 0.39436 | 0.39717 | 0.39999 | 0.40281 | 0.40326 | 0.4037 | 0.40415 | 0.4046 | 0.40505 | 0.4055 | 0.40594 | 0.40639 | 0.40684 | 0.40729 | 0.40774 | 0.40818 | 0.40863 | 0.40908 | 0.40953
| HSM004-160438389 | HSM004 | 0.13854 | 0.13943 | 0.14033 | 0.14122 | 0.14212 | 0.14155 | 0.14098 | 0.14041 | 0.13984 | 0.13928 | 0.13871 | 0.13814 | 0.13757 | 0.137 | 0.13644 | 0.13587 | 0.1353 | 0.13473 | 0.13416 | 0.1336
| HSM004-160438554 | HSM004 | 0.19436 | 0.19551 | 0.19666 | 0.19781 | 0.19896 | 0.19765 | 0.19635 | 0.19505 | 0.19375 | 0.19245 | 0.19114 | 0.18984 | 0.18854 | 0.18724 | 0.18594 | 0.18464 | 0.18333 | 0.18203 | 0.18073 | 0.17943
| HSM004-160438797 | HSM004 | 0.00037173 | 0.00037419 | 0.00037666 | 0.00037913 | 0.0003816 | 0.0003792 | 0.0003768 | 0.0003744 | 0.000372 | 0.0003696 | 0.0003672 | 0.0003648 | 0.0003624 | 0.00036 | 0.0003576 | 0.0003552 | 0.0003528 | 0.0003504 | 0.000348 | 0.0003456
| HSM004-160439137 | HSM004 | 0.00047096 | 0.00047404 | 0.00047713 | 0.00048021 | 0.0004833 | 0.00048209 | 0.00048087 | 0.00047966 | 0.00047844 | 0.00047723 | 0.00047601 | 0.0004748 | 0.00047358 | 0.00047237 | 0.00047115 | 0.00046994 | 0.00046872 | 0.00046751 | 0.00046629 | 0.00046508
| HSM004-163582339 | HSM004 | 0.49402 | 0.49769 | 0.50135 | 0.50501 | 0.50868 | 0.50591 | 0.50314 | 0.50038 | 0.49761 | 0.49485 | 0.49208 | 0.48931 | 0.48655 | 0.48378 | 0.48101 | 0.47825 | 0.47548 | 0.47272 | 0.46995 | 0.46718
| HSM004-163582585 | HSM004 | 3.7176e-05 | 3.7452e-05 | 3.7728e-05 | 3.8004e-05 | 3.828e-05 | 3.8046e-05 | 3.7812e-05 | 3.7578e-05 | 3.7344e-05 | 3.711e-05 | 3.6876e-05 | 3.6642e-05 | 3.6408e-05 | 3.6174e-05 | 3.594e-05 | 3.5706e-05 | 3.5472e-05 | 3.5238e-05 | 3.5004e-05 | 3.477e-05
| HSM004-163582753 | HSM004 | 5.9206e-05 | 5.9654e-05 | 6.0103e-05 | 6.0551e-05 | 6.1e-05 | 6.09e-05 | 6.08e-05 | 6.07e-05 | 6.06e-05 | 6.05e-05 | 6.04e-05 | 6.03e-05 | 6.02e-05 | 6.01e-05 | 6e-05 | 5.99e-05 | 5.98e-05 | 5.97e-05 | 5.96e-05 | 5.95e-05
| HSM004-163606098 | HSM004 | 0.73464 | 0.73963 | 0.74462 | 0.74961 | 0.7546 | 0.75431 | 0.75402 | 0.75373 | 0.75345 | 0.75316 | 0.75287 | 0.75258 | 0.75229 | 0.75201 | 0.75172 | 0.75143 | 0.75114 | 0.75085 | 0.75057 | 0.75028
| HSM004-163606269 | HSM004 | 0.0037363 | 0.003764 | 0.0037917 | 0.0038194 | 0.003847 | 0.0038496 | 0.0038522 | 0.0038547 | 0.0038573 | 0.0038598 | 0.0038624 | 0.003865 | 0.0038675 | 0.0038701 | 0.0038727 | 0.0038752 | 0.0038778 | 0.0038804 | 0.0038829 | 0.0038855
| HSM004-163794865 | HSM004 | 0.059069 | 0.059499 | 0.059928 | 0.060358 | 0.060787 | 0.060417 | 0.060046 | 0.059675 | 0.059305 | 0.058934 | 0.058563 | 0.058193 | 0.057822 | 0.057451 | 0.057081 | 0.05671 | 0.056339 | 0.055968 | 0.055598 | 0.055227
| HSM004-163794980 | HSM004 | 0.00060007 | 0.00060443 | 0.00060879 | 0.00061314 | 0.0006175 | 0.00061338 | 0.00060925 | 0.00060513 | 0.000601 | 0.00059688 | 0.00059275 | 0.00058863 | 0.0005845 | 0.00058038 | 0.00057625 | 0.00057213 | 0.000568 | 0.00056388 | 0.00055975 | 0.00055563
| HSM004-163795111 | HSM004 | 0.00018214 | 0.00018334 | 0.00018455 | 0.00018575 | 0.00018696 | 0.0001862 | 0.00018544 | 0.00018468 | 0.00018392 | 0.00018316 | 0.0001824 | 0.00018164 | 0.00018088 | 0.00018012 | 0.00017936 | 0.0001786 | 0.00017784 | 0.00017708 | 0.00017632 | 0.00017556
| HSM004-163795268 | HSM004 | 0.0011363 | 0.0011443 | 0.0011522 | 0.0011602 | 0.0011682 | 0.0011661 | 0.001164 | 0.0011619 | 0.0011598 | 0.0011577 | 0.0011557 | 0.0011536 | 0.0011515 | 0.0011494 | 0.0011473 | 0.0011452 | 0.0011431 | 0.001141 | 0.0011389 | 0.0011369
| HSM004-24599744 | HSM004 | 1.9493 | 1.9623 | 1.9753 | 1.9883 | 2.0013 | 1.9873 | 1.9732 | 1.9591 | 1.945 | 1.931 | 1.9169 | 1.9028 | 1.8887 | 1.8747 | 1.8606 | 1.8465 | 1.8324 | 1.8184 | 1.8043 | 1.7902
| HSM004-24599758 | HSM004 | 3.2515 | 3.2682 | 3.2848 | 3.3015 | 3.3182 | 3.3001 | 3.2821 | 3.264 | 3.246 | 3.2279 | 3.2099 | 3.1918 | 3.1738 | 3.1557 | 3.1377 | 3.1196 | 3.1016 | 3.0835 | 3.0655 | 3.0474
| HSM004-24604904 | HSM004 | 31.2547 | 31.4601 | 31.6656 | 31.871 | 32.0765 | 32.1019 | 32.1274 | 32.1528 | 32.1783 | 32.2037 | 32.2292 | 32.2546 | 32.28 | 32.3055 | 32.3309 | 32.3564 | 32.3818 | 32.4073 | 32.4327 | 32.4581
| HSM004-76359867 | HSM004 | 0.06271 | 0.063083 | 0.063455 | 0.063828 | 0.0642 | 0.063864 | 0.063527 | 0.06319 | 0.062853 | 0.062516 | 0.062179 | 0.061842 | 0.061505 | 0.061168 | 0.060831 | 0.060494 | 0.060157 | 0.05982 | 0.059483 | 0.059147
| HSM004-96221391 | HSM004 | 0.43622 | 0.43888 | 0.44155 | 0.44421 | 0.44688 | 0.44657 | 0.44625 | 0.44594 | 0.44562 | 0.44531 | 0.445 | 0.44468 | 0.44437 | 0.44406 | 0.44374 | 0.44343 | 0.44312 | 0.4428 | 0.44249 | 0.44218
| HSM005-121050437 | HSM005 | 17.245 | 17.3921 | 17.5391 | 17.6861 | 17.8332 | 17.8554 | 17.8777 | 17.8999 | 17.9222 | 17.9445 | 17.9667 | 17.989 | 18.0112 | 18.0335 | 18.0557 | 18.078 | 18.1003 | 18.1225 | 18.1448 | 18.167
| HSM005-15416442 | HSM005 | 65.8701 | 66.3359 | 66.8016 | 67.2673 | 67.7331 | 67.7236 | 67.7142 | 67.7048 | 67.6954 | 67.6859 | 67.6765 | 67.6671 | 67.6577 | 67.6482 | 67.6388 | 67.6294 | 67.62 | 67.6105 | 67.6011 | 67.5917
| HSM005-159947157 | HSM005 | 0.22153 | 0.22332 | 0.22511 | 0.22691 | 0.2287 | 0.22829 | 0.22789 | 0.22748 | 0.22708 | 0.22667 | 0.22627 | 0.22586 | 0.22546 | 0.22505 | 0.22465 | 0.22424 | 0.22383 | 0.22343 | 0.22302 | 0.22262
| HSM005-160318639 | HSM005 | 0.1619 | 0.16347 | 0.16503 | 0.1666 | 0.16817 | 0.16775 | 0.16732 | 0.1669 | 0.16647 | 0.16605 | 0.16562 | 0.1652 | 0.16477 | 0.16435 | 0.16392 | 0.1635 | 0.16307 | 0.16265 | 0.16222 | 0.1618
| HSM005-160319214 | HSM005 | 0.1429 | 0.14407 | 0.14524 | 0.14641 | 0.14757 | 0.14742 | 0.14726 | 0.14711 | 0.14695 | 0.1468 | 0.14664 | 0.14648 | 0.14633 | 0.14617 | 0.14602 | 0.14586 | 0.14571 | 0.14555 | 0.14539 | 0.14524
| HSM005-160415406 | HSM005 | 0.23499 | 0.23703 | 0.23907 | 0.24111 | 0.24315 | 0.24294 | 0.24273 | 0.24252 | 0.24231 | 0.2421 | 0.24189 | 0.24168 | 0.24147 | 0.24126 | 0.24105 | 0.24084 | 0.24063 | 0.24042 | 0.24021 | 0.24
| HSM005-160415504 | HSM005 | 0.039394 | 0.03976 | 0.040126 | 0.040492 | 0.040858 | 0.040826 | 0.040794 | 0.040762 | 0.04073 | 0.040698 | 0.040666 | 0.040634 | 0.040601 | 0.040569 | 0.040537 | 0.040505 | 0.040473 | 0.040441 | 0.040409 | 0.040377
| HSM005-160419737 | HSM005 | 0.10056 | 0.10148 | 0.10239 | 0.10331 | 0.10422 | 0.10425 | 0.10427 | 0.1043 | 0.10432 | 0.10435 | 0.10437 | 0.1044 | 0.10442 | 0.10445 | 0.10447 | 0.1045 | 0.10453 | 0.10455 | 0.10458 | 0.1046
| HSM005-160419880 | HSM005 | 0.075223 | 0.075882 | 0.076541 | 0.077199 | 0.077858 | 0.077933 | 0.078007 | 0.078082 | 0.078156 | 0.078231 | 0.078305 | 0.07838 | 0.078455 | 0.078529 | 0.078604 | 0.078678 | 0.078753 | 0.078828 | 0.078902 | 0.078977
| HSM005-160419993 | HSM005 | 0.041687 | 0.042073 | 0.042458 | 0.042843 | 0.043228 | 0.043308 | 0.043388 | 0.043469 | 0.043549 | 0.043629 | 0.043709 | 0.04379 | 0.04387 | 0.04395 | 0.04403 | 0.044111 | 0.044191 | 0.044271 | 0.044351 | 0.044431
| HSM005-160647192 | HSM005 | 0.27996 | 0.28238 | 0.2848 | 0.28722 | 0.28964 | 0.28926 | 0.28888 | 0.2885 | 0.28812 | 0.28774 | 0.28735 | 0.28697 | 0.28659 | 0.28621 | 0.28583 | 0.28545 | 0.28507 | 0.28468 | 0.2843 | 0.28392
| HSM006-153767042 | HSM006 | 0.15441 | 0.15566 | 0.15692 | 0.15818 | 0.15943 | 0.15907 | 0.15872 | 0.15836 | 0.158 | 0.15764 | 0.15728 | 0.15692 | 0.15656 | 0.1562 | 0.15584 | 0.15548 | 0.15513 | 0.15477 | 0.15441 | 0.15405
| HSM006-15416692 | HSM006 | 4.8174 | 4.8604 | 4.9034 | 4.9464 | 4.9895 | 4.987 | 4.9846 | 4.9821 | 4.9797 | 4.9773 | 4.9748 | 4.9724 | 4.9699 | 4.9675 | 4.9651 | 4.9626 | 4.9602 | 4.9577 | 4.9553 | 4.9529
| HSM006-15416703 | HSM006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM006-160434642 | HSM006 | 0.10495 | 0.1059 | 0.10684 | 0.10778 | 0.10872 | 0.10876 | 0.1088 | 0.10884 | 0.10887 | 0.10891 | 0.10895 | 0.10899 | 0.10902 | 0.10906 | 0.1091 | 0.10914 | 0.10918 | 0.10921 | 0.10925 | 0.10929
| HSM006-160439280 | HSM006 | 0.018696 | 0.018878 | 0.019061 | 0.019244 | 0.019427 | 0.019409 | 0.019391 | 0.019373 | 0.019355 | 0.019337 | 0.019319 | 0.019301 | 0.019283 | 0.019265 | 0.019247 | 0.019229 | 0.019211 | 0.019193 | 0.019175 | 0.019158
| HSM006-160439382 | HSM006 | 0.00036391 | 0.00036743 | 0.00037095 | 0.00037448 | 0.000378 | 0.00037868 | 0.00037935 | 0.00038003 | 0.0003807 | 0.00038138 | 0.00038205 | 0.00038273 | 0.0003834 | 0.00038408 | 0.00038475 | 0.00038543 | 0.0003861 | 0.00038678 | 0.00038745 | 0.00038813
| HSM006-160439464 | HSM006 | 0.10833 | 0.10924 | 0.11015 | 0.11107 | 0.11198 | 0.11181 | 0.11164 | 0.11147 | 0.1113 | 0.11113 | 0.11096 | 0.11079 | 0.11062 | 0.11045 | 0.11028 | 0.11011 | 0.10994 | 0.10977 | 0.1096 | 0.10943
| HSM006-160439562 | HSM006 | 0.57445 | 0.57929 | 0.58414 | 0.58898 | 0.59382 | 0.59307 | 0.59232 | 0.59157 | 0.59082 | 0.59007 | 0.58933 | 0.58858 | 0.58783 | 0.58708 | 0.58633 | 0.58558 | 0.58483 | 0.58408 | 0.58333 | 0.58258
| HSM006-160439782 | HSM006 | 0.009322 | 0.0094129 | 0.0095039 | 0.0095949 | 0.0096858 | 0.009688 | 0.0096902 | 0.0096924 | 0.0096946 | 0.0096968 | 0.0096989 | 0.0097011 | 0.0097033 | 0.0097055 | 0.0097077 | 0.0097099 | 0.0097121 | 0.0097143 | 0.0097164 | 0.0097186
| HSM006-163605855 | HSM006 | 0.00016085 | 0.00016219 | 0.00016353 | 0.00016486 | 0.0001662 | 0.00016626 | 0.00016632 | 0.00016638 | 0.00016644 | 0.0001665 | 0.00016656 | 0.00016662 | 0.00016668 | 0.00016674 | 0.0001668 | 0.00016686 | 0.00016692 | 0.00016698 | 0.00016704 | 0.0001671
| HSM006-201967868 | HSM006 | 32.9146 | 33.1817 | 33.4489 | 33.716 | 33.9832 | 33.9366 | 33.89 | 33.8434 | 33.7968 | 33.7502 | 33.7036 | 33.657 | 33.6104 | 33.5638 | 33.5172 | 33.4706 | 33.4241 | 33.3775 | 33.3309 | 33.2843
| HSM006-24597826 | HSM006 | 5.2381 | 5.2886 | 5.3391 | 5.3896 | 5.4401 | 5.4424 | 5.4448 | 5.4471 | 5.4495 | 5.4518 | 5.4542 | 5.4565 | 5.4589 | 5.4612 | 5.4636 | 5.4659 | 5.4683 | 5.4706 | 5.473 | 5.4753
| HSM009-15416366 | HSM009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HSM009-15416379 | HSM009 | 74.476 | 74.9296 | 75.3833 | 75.8369 | 76.2905 | 76.1503 | 76.0101 | 75.8699 | 75.7297 | 75.5895 | 75.4493 | 75.3091 | 75.1688 | 75.0286 | 74.8884 | 74.7482 | 74.608 | 74.4678 | 74.3276 | 74.1874
| HSM010-15416755 | HSM010 | 148.0226 | 148.956 | 149.8895 | 150.8229 | 151.7564 | 151.6045 | 151.4527 | 151.3008 | 151.149 | 150.9971 | 150.8452 | 150.6934 | 150.5415 | 150.3897 | 150.2378 | 150.086 | 149.9341 | 149.7822 | 149.6304 | 149.4785
| HTN011-155712659 | HTN011 | 0.025267 | 0.025386 | 0.025506 | 0.025626 | 0.025746 | 0.025295 | 0.024844 | 0.024394 | 0.023943 | 0.023492 | 0.023042 | 0.022591 | 0.02214 | 0.02169 | 0.021239 | 0.020788 | 0.020337 | 0.019887 | 0.019436 | 0.018985
| HTN011-156981207 | HTN011 | 0.069435 | 0.070117 | 0.070799 | 0.071481 | 0.072164 | 0.071127 | 0.070091 | 0.069054 | 0.068018 | 0.066981 | 0.065945 | 0.064908 | 0.063872 | 0.062835 | 0.061799 | 0.060762 | 0.059726 | 0.058689 | 0.057653 | 0.056616
| HTN011-157405209 | HTN011 | 0.0016481 | 0.0016619 | 0.0016757 | 0.0016894 | 0.0017032 | 0.0016832 | 0.0016632 | 0.0016433 | 0.0016233 | 0.0016033 | 0.0015833 | 0.0015633 | 0.0015433 | 0.0015233 | 0.0015034 | 0.0014834 | 0.0014634 | 0.0014434 | 0.0014234 | 0.0014034
| HTN011-157405424 | HTN011 | 0.0012188 | 0.0012296 | 0.0012403 | 0.0012511 | 0.0012618 | 0.0012486 | 0.0012353 | 0.0012221 | 0.0012089 | 0.0011956 | 0.0011824 | 0.0011692 | 0.001156 | 0.0011427 | 0.0011295 | 0.0011163 | 0.001103 | 0.0010898 | 0.0010766 | 0.0010634
| HTN011-157405677 | HTN011 | 0.17743 | 0.1787 | 0.17998 | 0.18126 | 0.18253 | 0.18012 | 0.17771 | 0.1753 | 0.17288 | 0.17047 | 0.16806 | 0.16565 | 0.16323 | 0.16082 | 0.15841 | 0.156 | 0.15358 | 0.15117 | 0.14876 | 0.14635
| HTN011-157406255 | HTN011 | 0.062759 | 0.063303 | 0.063846 | 0.06439 | 0.064933 | 0.064327 | 0.063721 | 0.063115 | 0.062509 | 0.061903 | 0.061297 | 0.060691 | 0.060085 | 0.059479 | 0.058873 | 0.058267 | 0.057661 | 0.057055 | 0.056449 | 0.055843
| HTN011-157406464 | HTN011 | 0.034678 | 0.035013 | 0.035349 | 0.035684 | 0.036019 | 0.035652 | 0.035284 | 0.034916 | 0.034549 | 0.034181 | 0.033813 | 0.033446 | 0.033078 | 0.032711 | 0.032343 | 0.031975 | 0.031608 | 0.03124 | 0.030872 | 0.030505
| HTN011-157406612 | HTN011 | 0.032481 | 0.032793 | 0.033105 | 0.033417 | 0.033729 | 0.033256 | 0.032783 | 0.032309 | 0.031836 | 0.031363 | 0.03089 | 0.030416 | 0.029943 | 0.02947 | 0.028997 | 0.028523 | 0.02805 | 0.027577 | 0.027104 | 0.02663
| HTN011-162645268 | HTN011 | 3.6818e-05 | 3.7138e-05 | 3.7459e-05 | 3.7779e-05 | 3.81e-05 | 3.7662e-05 | 3.7224e-05 | 3.6786e-05 | 3.6348e-05 | 3.591e-05 | 3.5472e-05 | 3.5034e-05 | 3.4596e-05 | 3.4158e-05 | 3.372e-05 | 3.3282e-05 | 3.2844e-05 | 3.2406e-05 | 3.1968e-05 | 3.153e-05
| HTN011-162645611 | HTN011 | 0.00066202 | 0.00066714 | 0.00067226 | 0.00067738 | 0.0006825 | 0.00067375 | 0.000665 | 0.00065625 | 0.0006475 | 0.00063875 | 0.00063 | 0.00062125 | 0.0006125 | 0.00060375 | 0.000595 | 0.00058625 | 0.0005775 | 0.00056875 | 0.00056 | 0.00055125
| HTN011-190418895 | HTN011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-190418905 | HTN011 | 7.2476 | 7.2886 | 7.3297 | 7.3707 | 7.4117 | 7.3635 | 7.3153 | 7.2671 | 7.2189 | 7.1707 | 7.1225 | 7.0743 | 7.0261 | 6.9779 | 6.9296 | 6.8814 | 6.8332 | 6.785 | 6.7368 | 6.6886
| HTN011-24613192 | HTN011 | 9.6938 | 9.7547 | 9.8156 | 9.8765 | 9.9374 | 9.8259 | 9.7143 | 9.6028 | 9.4912 | 9.3797 | 9.2681 | 9.1566 | 9.045 | 8.9335 | 8.8219 | 8.7104 | 8.5988 | 8.4873 | 8.3757 | 8.2642
| HTN012-140933454 | HTN012 | 0.083297 | 0.083984 | 0.084672 | 0.085359 | 0.086047 | 0.085064 | 0.084081 | 0.083099 | 0.082116 | 0.081134 | 0.080151 | 0.079168 | 0.078186 | 0.077203 | 0.07622 | 0.075238 | 0.074255 | 0.073272 | 0.07229 | 0.071307
| HTN012-140933685 | HTN012 | 0.028279 | 0.028589 | 0.028899 | 0.029209 | 0.029519 | 0.028899 | 0.028279 | 0.027659 | 0.027039 | 0.026418 | 0.025798 | 0.025178 | 0.024558 | 0.023938 | 0.023318 | 0.022698 | 0.022078 | 0.021458 | 0.020838 | 0.020218
| HTN012-140933990 | HTN012 | 0.00085731 | 0.00086799 | 0.00087866 | 0.00088933 | 0.0009 | 0.0008832 | 0.0008664 | 0.0008496 | 0.0008328 | 0.000816 | 0.0007992 | 0.0007824 | 0.0007656 | 0.0007488 | 0.000732 | 0.0007152 | 0.0006984 | 0.0006816 | 0.0006648 | 0.000648
| HTN012-160319327 | HTN012 | 0.17875 | 0.17946 | 0.18018 | 0.18089 | 0.18161 | 0.18077 | 0.17993 | 0.17909 | 0.17825 | 0.17742 | 0.17658 | 0.17574 | 0.1749 | 0.17406 | 0.17322 | 0.17239 | 0.17155 | 0.17071 | 0.16987 | 0.16903
| HTN012-160319432 | HTN012 | 0.020516 | 0.020696 | 0.020877 | 0.021057 | 0.021238 | 0.021045 | 0.020852 | 0.020659 | 0.020465 | 0.020272 | 0.020079 | 0.019886 | 0.019693 | 0.0195 | 0.019307 | 0.019114 | 0.018921 | 0.018727 | 0.018534 | 0.018341
| HTN012-160319528 | HTN012 | 0.0058903 | 0.0059438 | 0.0059972 | 0.0060507 | 0.0061042 | 0.0060553 | 0.0060064 | 0.0059575 | 0.0059086 | 0.0058597 | 0.0058108 | 0.0057619 | 0.005713 | 0.0056642 | 0.0056153 | 0.0055664 | 0.0055175 | 0.0054686 | 0.0054197 | 0.0053708
| HTN012-160338385 | HTN012 | 0.10083 | 0.10179 | 0.10275 | 0.10371 | 0.10467 | 0.1031 | 0.10152 | 0.099943 | 0.098366 | 0.096789 | 0.095212 | 0.093635 | 0.092058 | 0.090481 | 0.088904 | 0.087327 | 0.085751 | 0.084174 | 0.082597 | 0.08102
| HTN012-160338483 | HTN012 | 0.093538 | 0.094519 | 0.095501 | 0.096483 | 0.097464 | 0.096425 | 0.095386 | 0.094347 | 0.093307 | 0.092268 | 0.091229 | 0.09019 | 0.08915 | 0.088111 | 0.087072 | 0.086033 | 0.084994 | 0.083954 | 0.082915 | 0.081876
| HTN012-160338601 | HTN012 | 0.093287 | 0.094322 | 0.095357 | 0.096392 | 0.097427 | 0.09574 | 0.094054 | 0.092368 | 0.090681 | 0.088995 | 0.087309 | 0.085622 | 0.083936 | 0.08225 | 0.080563 | 0.078877 | 0.077191 | 0.075504 | 0.073818 | 0.072131
| HTN012-160411348 | HTN012 | 0.0089633 | 0.0090569 | 0.0091505 | 0.0092441 | 0.0093378 | 0.0091916 | 0.0090455 | 0.0088994 | 0.0087533 | 0.0086072 | 0.008461 | 0.0083149 | 0.0081688 | 0.0080227 | 0.0078766 | 0.0077304 | 0.0075843 | 0.0074382 | 0.0072921 | 0.007146
| HTN012-160437866 | HTN012 | 0.0081706 | 0.0082594 | 0.0083482 | 0.008437 | 0.0085258 | 0.0084252 | 0.0083246 | 0.008224 | 0.0081234 | 0.0080229 | 0.0079223 | 0.0078217 | 0.0077211 | 0.0076205 | 0.00752 | 0.0074194 | 0.0073188 | 0.0072182 | 0.0071176 | 0.0070171
| HTN012-162615153 | HTN012 | 5.7751e-06 | 5.8389e-06 | 5.9026e-06 | 5.9663e-06 | 6.03e-06 | 5.9185e-06 | 5.807e-06 | 5.6955e-06 | 5.584e-06 | 5.4725e-06 | 5.361e-06 | 5.2495e-06 | 5.138e-06 | 5.0265e-06 | 4.915e-06 | 4.8035e-06 | 4.692e-06 | 4.5805e-06 | 4.469e-06 | 4.3575e-06
| HTN012-162615767 | HTN012 | 0.0063188 | 0.0063759 | 0.006433 | 0.0064901 | 0.0065472 | 0.0064828 | 0.0064184 | 0.006354 | 0.0062896 | 0.0062252 | 0.0061608 | 0.0060963 | 0.0060319 | 0.0059675 | 0.0059031 | 0.0058387 | 0.0057743 | 0.0057099 | 0.0056455 | 0.0055811
| HTN012-162670168 | HTN012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HTN012-190418858 | HTN012 | 1.2523 | 1.2598 | 1.2673 | 1.2748 | 1.2823 | 1.2735 | 1.2647 | 1.256 | 1.2472 | 1.2384 | 1.2296 | 1.2209 | 1.2121 | 1.2033 | 1.1946 | 1.1858 | 1.177 | 1.1683 | 1.1595 | 1.1507
| HTN012-24597770 | HTN012 | 25.5559 | 25.7846 | 26.0134 | 26.2422 | 26.471 | 26.105 | 25.739 | 25.373 | 25.007 | 24.641 | 24.2751 | 23.9091 | 23.5431 | 23.1771 | 22.8111 | 22.4451 | 22.0791 | 21.7132 | 21.3472 | 20.9812
| HTN013-100723362 | HTN013 | 6.4193 | 6.4637 | 6.5081 | 6.5525 | 6.5969 | 6.5655 | 6.5341 | 6.5027 | 6.4713 | 6.4399 | 6.4085 | 6.3771 | 6.3457 | 6.3143 | 6.2829 | 6.2515 | 6.2201 | 6.1887 | 6.1573 | 6.1259
| HTN013-142439156 | HTN013 | 0.20068 | 0.20176 | 0.20285 | 0.20394 | 0.20503 | 0.2039 | 0.20277 | 0.20164 | 0.20051 | 0.19938 | 0.19824 | 0.19711 | 0.19598 | 0.19485 | 0.19372 | 0.19259 | 0.19146 | 0.19033 | 0.1892 | 0.18807
| HTN013-142439579 | HTN013 | 0.031189 | 0.031377 | 0.031566 | 0.031755 | 0.031943 | 0.031814 | 0.031685 | 0.031556 | 0.031426 | 0.031297 | 0.031168 | 0.031038 | 0.030909 | 0.03078 | 0.030651 | 0.030521 | 0.030392 | 0.030263 | 0.030134 | 0.030004
| HTN013-142439718 | HTN013 | 0.01803 | 0.018121 | 0.018212 | 0.018303 | 0.018395 | 0.018306 | 0.018217 | 0.018128 | 0.018039 | 0.01795 | 0.017861 | 0.017772 | 0.017683 | 0.017594 | 0.017505 | 0.017416 | 0.017327 | 0.017238 | 0.017149 | 0.01706
| HTN013-142440041 | HTN013 | 0.11303 | 0.11385 | 0.11467 | 0.11549 | 0.11631 | 0.11578 | 0.11524 | 0.11471 | 0.11417 | 0.11364 | 0.1131 | 0.11257 | 0.11203 | 0.1115 | 0.11097 | 0.11043 | 0.1099 | 0.10936 | 0.10883 | 0.10829
| HTN013-153173736 | HTN013 | 3.374 | 3.3945 | 3.4151 | 3.4356 | 3.4561 | 3.4392 | 3.4222 | 3.4052 | 3.3883 | 3.3713 | 3.3543 | 3.3374 | 3.3204 | 3.3034 | 3.2865 | 3.2695 | 3.2525 | 3.2356 | 3.2186 | 3.2016
| HTN013-158639235 | HTN013 | 0.027194 | 0.02733 | 0.027466 | 0.027601 | 0.027737 | 0.027593 | 0.02745 | 0.027306 | 0.027162 | 0.027018 | 0.026875 | 0.026731 | 0.026587 | 0.026443 | 0.0263 | 0.026156 | 0.026012 | 0.025868 | 0.025725 | 0.025581
| HTN013-158639340 | HTN013 | 0.02341 | 0.023577 | 0.023744 | 0.023911 | 0.024078 | 0.023966 | 0.023855 | 0.023744 | 0.023632 | 0.023521 | 0.023409 | 0.023298 | 0.023187 | 0.023075 | 0.022964 | 0.022853 | 0.022741 | 0.02263 | 0.022519 | 0.022407
| HTN013-159365790 | HTN013 | 0.0093106 | 0.0093553 | 0.0094 | 0.0094447 | 0.0094894 | 0.009429 | 0.0093686 | 0.0093082 | 0.0092478 | 0.0091874 | 0.009127 | 0.0090666 | 0.0090062 | 0.0089458 | 0.0088854 | 0.008825 | 0.0087646 | 0.0087042 | 0.0086437 | 0.0085833
| HTN013-159366167 | HTN013 | 0.0066222 | 0.0066533 | 0.0066843 | 0.0067153 | 0.0067463 | 0.0067094 | 0.0066724 | 0.0066354 | 0.0065985 | 0.0065615 | 0.0065245 | 0.0064875 | 0.0064506 | 0.0064136 | 0.0063766 | 0.0063396 | 0.0063027 | 0.0062657 | 0.0062287 | 0.0061918
| HTN013-159381071 | HTN013 | 0.039245 | 0.039422 | 0.0396 | 0.039777 | 0.039955 | 0.039738 | 0.039521 | 0.039305 | 0.039088 | 0.038871 | 0.038654 | 0.038437 | 0.03822 | 0.038004 | 0.037787 | 0.03757 | 0.037353 | 0.037136 | 0.03692 | 0.036703
| HTN013-159381283 | HTN013 | 0.029744 | 0.029876 | 0.030009 | 0.030142 | 0.030275 | 0.030095 | 0.029916 | 0.029736 | 0.029557 | 0.029378 | 0.029198 | 0.029019 | 0.02884 | 0.02866 | 0.028481 | 0.028302 | 0.028122 | 0.027943 | 0.027764 | 0.027584
| HTN013-160286800 | HTN013 | 0.10987 | 0.11047 | 0.11106 | 0.11165 | 0.11225 | 0.11167 | 0.1111 | 0.11052 | 0.10994 | 0.10937 | 0.10879 | 0.10822 | 0.10764 | 0.10707 | 0.10649 | 0.10592 | 0.10534 | 0.10477 | 0.10419 | 0.10362
| HTN013-160451212 | HTN013 | 0.021526 | 0.021693 | 0.02186 | 0.022027 | 0.022194 | 0.022105 | 0.022016 | 0.021928 | 0.021839 | 0.021751 | 0.021662 | 0.021573 | 0.021485 | 0.021396 | 0.021307 | 0.021219 | 0.02113 | 0.021042 | 0.020953 | 0.020864
| HTN013-160451319 | HTN013 | 0.00011254 | 0.00011325 | 0.00011395 | 0.00011466 | 0.00011536 | 0.00011463 | 0.0001139 | 0.00011318 | 0.00011245 | 0.00011172 | 0.00011099 | 0.00011026 | 0.00010954 | 0.00010881 | 0.00010808 | 0.00010735 | 0.00010662 | 0.0001059 | 0.00010517 | 0.00010444
| HTN013-160451462 | HTN013 | 0.028471 | 0.028663 | 0.028856 | 0.029049 | 0.029241 | 0.029066 | 0.02889 | 0.028714 | 0.028539 | 0.028363 | 0.028187 | 0.028012 | 0.027836 | 0.02766 | 0.027485 | 0.027309 | 0.027133 | 0.026958 | 0.026782 | 0.026606
| HTN013-160772532 | HTN013 | 0.020762 | 0.020863 | 0.020963 | 0.021064 | 0.021164 | 0.021053 | 0.020942 | 0.020831 | 0.02072 | 0.020609 | 0.020499 | 0.020388 | 0.020277 | 0.020166 | 0.020055 | 0.019944 | 0.019833 | 0.019722 | 0.019611 | 0.0195
| HTN013-162802647 | HTN013 | 0.00050392 | 0.00050619 | 0.00050846 | 0.00051072 | 0.00051299 | 0.00051026 | 0.00050754 | 0.00050481 | 0.00050208 | 0.00049935 | 0.00049662 | 0.00049389 | 0.00049117 | 0.00048844 | 0.00048571 | 0.00048298 | 0.00048025 | 0.00047752 | 0.0004748 | 0.00047207
| HTN013-162821734 | HTN013 | 0.23015 | 0.23231 | 0.23447 | 0.23663 | 0.23879 | 0.23738 | 0.23596 | 0.23455 | 0.23313 | 0.23171 | 0.2303 | 0.22888 | 0.22747 | 0.22605 | 0.22464 | 0.22322 | 0.22181 | 0.22039 | 0.21898 | 0.21756
| HTN013-162978763 | HTN013 | 6.0768e-05 | 6.1176e-05 | 6.1584e-05 | 6.1992e-05 | 6.24e-05 | 6.2091e-05 | 6.1782e-05 | 6.1473e-05 | 6.1164e-05 | 6.0855e-05 | 6.0546e-05 | 6.0237e-05 | 5.9928e-05 | 5.9619e-05 | 5.931e-05 | 5.9001e-05 | 5.8692e-05 | 5.8383e-05 | 5.8074e-05 | 5.7765e-05
| HTN013-163073376 | HTN013 | 0.093578 | 0.094013 | 0.094447 | 0.094882 | 0.095317 | 0.094852 | 0.094387 | 0.093922 | 0.093457 | 0.092992 | 0.092527 | 0.092063 | 0.091598 | 0.091133 | 0.090668 | 0.090203 | 0.089738 | 0.089273 | 0.088809 | 0.088344
| HTN013-163073497 | HTN013 | 1.9526e-05 | 1.9682e-05 | 1.9838e-05 | 1.9994e-05 | 2.015e-05 | 1.9994e-05 | 1.9838e-05 | 1.9682e-05 | 1.9526e-05 | 1.937e-05 | 1.9214e-05 | 1.9058e-05 | 1.8902e-05 | 1.8746e-05 | 1.859e-05 | 1.8434e-05 | 1.8278e-05 | 1.8122e-05 | 1.7966e-05 | 1.781e-05
| HTN013-163073657 | HTN013 | 0.00026888 | 0.00027096 | 0.00027304 | 0.00027512 | 0.0002772 | 0.00027538 | 0.00027356 | 0.00027174 | 0.00026992 | 0.0002681 | 0.00026628 | 0.00026446 | 0.00026264 | 0.00026082 | 0.000259 | 0.00025718 | 0.00025536 | 0.00025354 | 0.00025172 | 0.0002499
| HTN013-163073840 | HTN013 | 0.098441 | 0.09897 | 0.099499 | 0.10003 | 0.10056 | 0.099908 | 0.099258 | 0.098609 | 0.09796 | 0.097311 | 0.096661 | 0.096012 | 0.095363 | 0.094714 | 0.094065 | 0.093415 | 0.092766 | 0.092117 | 0.091468 | 0.090818
| HTN013-163074070 | HTN013 | 0.0013908 | 0.001399 | 0.0014073 | 0.0014156 | 0.0014239 | 0.0014183 | 0.0014127 | 0.0014071 | 0.0014016 | 0.001396 | 0.0013904 | 0.0013849 | 0.0013793 | 0.0013737 | 0.0013681 | 0.0013626 | 0.001357 | 0.0013514 | 0.0013459 | 0.0013403
| HTN013-171202197 | HTN013 | 0.13694 | 0.13761 | 0.13828 | 0.13896 | 0.13963 | 0.13906 | 0.13849 | 0.13792 | 0.13735 | 0.13678 | 0.13621 | 0.13564 | 0.13507 | 0.1345 | 0.13393 | 0.13336 | 0.13279 | 0.13222 | 0.13165 | 0.13108
| HTN013-182145838 | HTN013 | 2.2895 | 2.3036 | 2.3177 | 2.3319 | 2.346 | 2.3356 | 2.3253 | 2.315 | 2.3046 | 2.2943 | 2.2839 | 2.2736 | 2.2633 | 2.2529 | 2.2426 | 2.2322 | 2.2219 | 2.2116 | 2.2012 | 2.1909
| HTN013-190418811 | HTN013 | 12.6042 | 12.7203 | 12.8364 | 12.9525 | 13.0685 | 12.9911 | 12.9136 | 12.8361 | 12.7586 | 12.6812 | 12.6037 | 12.5262 | 12.4488 | 12.3713 | 12.2938 | 12.2163 | 12.1389 | 12.0614 | 11.9839 | 11.9064
| HTN013-192570901 | HTN013 | 0.11169 | 0.11258 | 0.11348 | 0.11437 | 0.11527 | 0.11461 | 0.11395 | 0.11329 | 0.11263 | 0.11197 | 0.11131 | 0.11065 | 0.10999 | 0.10934 | 0.10868 | 0.10802 | 0.10736 | 0.1067 | 0.10604 | 0.10538
| HTN013-201063848 | HTN013 | 4.4674 | 4.4901 | 4.5127 | 4.5354 | 4.5581 | 4.5311 | 4.5041 | 4.4771 | 4.4502 | 4.4232 | 4.3962 | 4.3692 | 4.3422 | 4.3152 | 4.2882 | 4.2612 | 4.2342 | 4.2072 | 4.1802 | 4.1533
| HTN032-159373067 | HTN032 | 0.09582 | 0.096825 | 0.09783 | 0.098836 | 0.099841 | 0.098977 | 0.098113 | 0.097249 | 0.096385 | 0.095521 | 0.094657 | 0.093793 | 0.092929 | 0.092065 | 0.091201 | 0.090337 | 0.089473 | 0.088609 | 0.087745 | 0.086881
| HTN032-159377664 | HTN032 | 0.096848 | 0.097602 | 0.098357 | 0.099112 | 0.099866 | 0.09926 | 0.098653 | 0.098047 | 0.09744 | 0.096834 | 0.096227 | 0.09562 | 0.095014 | 0.094407 | 0.093801 | 0.093194 | 0.092588 | 0.091981 | 0.091374 | 0.090768
| HTN032-159377774 | HTN032 | 0.11256 | 0.11308 | 0.1136 | 0.11412 | 0.11464 | 0.11432 | 0.114 | 0.11369 | 0.11337 | 0.11305 | 0.11274 | 0.11242 | 0.1121 | 0.11179 | 0.11147 | 0.11116 | 0.11084 | 0.11052 | 0.11021 | 0.10989
| HTN032-159443241 | HTN032 | 0.0049219 | 0.0049283 | 0.0049348 | 0.0049413 | 0.0049477 | 0.0049395 | 0.0049312 | 0.004923 | 0.0049148 | 0.0049065 | 0.0048983 | 0.00489 | 0.0048818 | 0.0048735 | 0.0048653 | 0.004857 | 0.0048488 | 0.0048405 | 0.0048323 | 0.0048241
| HTN032-159443483 | HTN032 | 0.28707 | 0.28847 | 0.28988 | 0.29128 | 0.29269 | 0.29152 | 0.29036 | 0.28919 | 0.28803 | 0.28686 | 0.2857 | 0.28453 | 0.28337 | 0.2822 | 0.28103 | 0.27987 | 0.2787 | 0.27754 | 0.27637 | 0.27521
| HTN032-159944977 | HTN032 | 0.15947 | 0.1608 | 0.16213 | 0.16346 | 0.16479 | 0.16408 | 0.16336 | 0.16265 | 0.16194 | 0.16123 | 0.16052 | 0.1598 | 0.15909 | 0.15838 | 0.15767 | 0.15695 | 0.15624 | 0.15553 | 0.15482 | 0.1541
| HTN032-160369507 | HTN032 | 0.035622 | 0.035948 | 0.036273 | 0.036598 | 0.036924 | 0.036589 | 0.036255 | 0.03592 | 0.035586 | 0.035252 | 0.034917 | 0.034583 | 0.034248 | 0.033914 | 0.033579 | 0.033245 | 0.032911 | 0.032576 | 0.032242 | 0.031907
| HTN032-160369615 | HTN032 | 0.047715 | 0.048161 | 0.048606 | 0.049052 | 0.049498 | 0.04919 | 0.048882 | 0.048575 | 0.048267 | 0.047959 | 0.047652 | 0.047344 | 0.047036 | 0.046729 | 0.046421 | 0.046113 | 0.045806 | 0.045498 | 0.04519 | 0.044883
| HTN032-160369738 | HTN032 | 0.089588 | 0.090305 | 0.091023 | 0.091741 | 0.092458 | 0.091765 | 0.091071 | 0.090377 | 0.089683 | 0.08899 | 0.088296 | 0.087602 | 0.086908 | 0.086215 | 0.085521 | 0.084827 | 0.084133 | 0.08344 | 0.082746 | 0.082052
| HTN032-162635166 | HTN032 | 9.1771e-05 | 9.2829e-05 | 9.3886e-05 | 9.4943e-05 | 9.6e-05 | 9.555e-05 | 9.51e-05 | 9.465e-05 | 9.42e-05 | 9.375e-05 | 9.33e-05 | 9.285e-05 | 9.24e-05 | 9.195e-05 | 9.15e-05 | 9.105e-05 | 9.06e-05 | 9.015e-05 | 8.97e-05 | 8.925e-05
| HTN032-162645765 | HTN032 | 0.037144 | 0.037408 | 0.037671 | 0.037934 | 0.038198 | 0.037987 | 0.037777 | 0.037566 | 0.037356 | 0.037146 | 0.036935 | 0.036725 | 0.036514 | 0.036304 | 0.036094 | 0.035883 | 0.035673 | 0.035462 | 0.035252 | 0.035042
| HTN032-162671033 | HTN032 | 0.042211 | 0.042564 | 0.042918 | 0.043271 | 0.043625 | 0.043233 | 0.04284 | 0.042447 | 0.042055 | 0.041662 | 0.04127 | 0.040877 | 0.040485 | 0.040092 | 0.0397 | 0.039307 | 0.038914 | 0.038522 | 0.038129 | 0.037737
| HTN032-162671207 | HTN032 | 0.0012124 | 0.0012234 | 0.0012344 | 0.0012454 | 0.0012563 | 0.0012504 | 0.0012445 | 0.0012386 | 0.0012327 | 0.0012268 | 0.0012208 | 0.0012149 | 0.001209 | 0.0012031 | 0.0011972 | 0.0011913 | 0.0011853 | 0.0011794 | 0.0011735 | 0.0011676
| HTN032-162798482 | HTN032 | 0.11531 | 0.116 | 0.11669 | 0.11739 | 0.11808 | 0.11767 | 0.11726 | 0.11686 | 0.11645 | 0.11604 | 0.11563 | 0.11523 | 0.11482 | 0.11441 | 0.114 | 0.1136 | 0.11319 | 0.11278 | 0.11238 | 0.11197
| HTN032-187419014 | HTN032 | 24.1124 | 24.2972 | 24.4819 | 24.6667 | 24.8515 | 24.7216 | 24.5918 | 24.4619 | 24.3321 | 24.2022 | 24.0724 | 23.9425 | 23.8127 | 23.6828 | 23.553 | 23.4231 | 23.2933 | 23.1634 | 23.0335 | 22.9037
| HTN032-190418526 | HTN032 | 113.7442 | 114.3876 | 115.031 | 115.6744 | 116.3178 | 115.5806 | 114.8433 | 114.1061 | 113.3689 | 112.6317 | 111.8944 | 111.1572 | 110.42 | 109.6827 | 108.9455 | 108.2083 | 107.4711 | 106.7338 | 105.9966 | 105.2594
| HTN033-107035043 | HTN033 | 0.066178 | 0.066589 | 0.067 | 0.067411 | 0.067822 | 0.067674 | 0.067526 | 0.067378 | 0.06723 | 0.067082 | 0.066934 | 0.066787 | 0.066639 | 0.066491 | 0.066343 | 0.066195 | 0.066047 | 0.0659 | 0.065752 | 0.065604
| HTN033-142434533 | HTN033 | 0.097649 | 0.098338 | 0.099026 | 0.099714 | 0.1004 | 0.1001 | 0.0998 | 0.099498 | 0.099197 | 0.098895 | 0.098594 | 0.098292 | 0.097991 | 0.097689 | 0.097388 | 0.097086 | 0.096785 | 0.096483 | 0.096182 | 0.09588
| HTN033-159363700 | HTN033 | 0.035201 | 0.035481 | 0.035761 | 0.03604 | 0.03632 | 0.036067 | 0.035813 | 0.035559 | 0.035306 | 0.035052 | 0.034798 | 0.034545 | 0.034291 | 0.034037 | 0.033784 | 0.03353 | 0.033277 | 0.033023 | 0.032769 | 0.032516
| HTN033-159373503 | HTN033 | 0.074138 | 0.074655 | 0.075171 | 0.075688 | 0.076204 | 0.075846 | 0.075487 | 0.075129 | 0.07477 | 0.074412 | 0.074053 | 0.073695 | 0.073336 | 0.072978 | 0.072619 | 0.072261 | 0.071902 | 0.071544 | 0.071185 | 0.070827
| HTN033-159373599 | HTN033 | 0.20431 | 0.2055 | 0.2067 | 0.20789 | 0.20908 | 0.20802 | 0.20695 | 0.20588 | 0.20481 | 0.20374 | 0.20267 | 0.20161 | 0.20054 | 0.19947 | 0.1984 | 0.19733 | 0.19626 | 0.1952 | 0.19413 | 0.19306
| HTN033-159944283 | HTN033 | 0.11995 | 0.12084 | 0.12173 | 0.12262 | 0.12351 | 0.12301 | 0.12251 | 0.12201 | 0.12152 | 0.12102 | 0.12052 | 0.12003 | 0.11953 | 0.11903 | 0.11853 | 0.11804 | 0.11754 | 0.11704 | 0.11655 | 0.11605
| HTN033-159944367 | HTN033 | 0.044374 | 0.044784 | 0.045193 | 0.045603 | 0.046012 | 0.045648 | 0.045284 | 0.044919 | 0.044555 | 0.04419 | 0.043826 | 0.043462 | 0.043097 | 0.042733 | 0.042368 | 0.042004 | 0.04164 | 0.041275 | 0.040911 | 0.040546
| HTN033-159944491 | HTN033 | 0.076408 | 0.076942 | 0.077476 | 0.07801 | 0.078545 | 0.078133 | 0.077721 | 0.077309 | 0.076896 | 0.076484 | 0.076072 | 0.07566 | 0.075248 | 0.074836 | 0.074424 | 0.074012 | 0.0736 | 0.073188 | 0.072776 | 0.072364
| HTN033-159944618 | HTN033 | 0.045899 | 0.046233 | 0.046567 | 0.046901 | 0.047235 | 0.046933 | 0.04663 | 0.046327 | 0.046024 | 0.045721 | 0.045419 | 0.045116 | 0.044813 | 0.04451 | 0.044208 | 0.043905 | 0.043602 | 0.043299 | 0.042996 | 0.042694
| HTN033-162626258 | HTN033 | 0.0061631 | 0.0062155 | 0.0062678 | 0.0063202 | 0.0063726 | 0.0063289 | 0.0062852 | 0.0062415 | 0.0061978 | 0.0061542 | 0.0061105 | 0.0060668 | 0.0060231 | 0.0059794 | 0.0059358 | 0.0058921 | 0.0058484 | 0.0058047 | 0.0057611 | 0.0057174
| HTN033-162670429 | HTN033 | 1.0899e-05 | 1.0975e-05 | 1.105e-05 | 1.1125e-05 | 1.12e-05 | 1.116e-05 | 1.112e-05 | 1.108e-05 | 1.104e-05 | 1.1e-05 | 1.096e-05 | 1.092e-05 | 1.088e-05 | 1.084e-05 | 1.08e-05 | 1.076e-05 | 1.072e-05 | 1.068e-05 | 1.064e-05 | 1.06e-05
| HTN033-162670652 | HTN033 | 0.00012382 | 0.00012386 | 0.00012391 | 0.00012395 | 0.000124 | 0.00012394 | 0.00012388 | 0.00012382 | 0.00012376 | 0.0001237 | 0.00012364 | 0.00012358 | 0.00012352 | 0.00012346 | 0.0001234 | 0.00012334 | 0.00012328 | 0.00012322 | 0.00012316 | 0.0001231
| HTN033-182145786 | HTN033 | 5.0374 | 5.046 | 5.0547 | 5.0633 | 5.072 | 5.0609 | 5.0498 | 5.0387 | 5.0276 | 5.0166 | 5.0055 | 4.9944 | 4.9833 | 4.9722 | 4.9611 | 4.95 | 4.939 | 4.9279 | 4.9168 | 4.9057
| HTN033-190418479 | HTN033 | 31.612 | 31.9027 | 32.1935 | 32.4842 | 32.7749 | 32.4605 | 32.1461 | 31.8317 | 31.5173 | 31.2029 | 30.8885 | 30.5741 | 30.2597 | 29.9453 | 29.6309 | 29.3165 | 29.0021 | 28.6877 | 28.3733 | 28.0589
| HTN034-100723274 | HTN034 | 0.34382 | 0.3456 | 0.34738 | 0.34916 | 0.35094 | 0.34881 | 0.34667 | 0.34453 | 0.3424 | 0.34026 | 0.33813 | 0.33599 | 0.33386 | 0.33172 | 0.32959 | 0.32745 | 0.32532 | 0.32318 | 0.32105 | 0.31891
| HTN034-108340859 | HTN034 | 11.7966 | 11.8667 | 11.9367 | 12.0068 | 12.0769 | 12.0051 | 11.9333 | 11.8616 | 11.7898 | 11.7181 | 11.6463 | 11.5745 | 11.5028 | 11.431 | 11.3593 | 11.2875 | 11.2157 | 11.144 | 11.0722 | 11.0004
| HTN034-142233453 | HTN034 | 0.18237 | 0.18375 | 0.18512 | 0.18649 | 0.18786 | 0.1851 | 0.18233 | 0.17956 | 0.17679 | 0.17402 | 0.17126 | 0.16849 | 0.16572 | 0.16295 | 0.16019 | 0.15742 | 0.15465 | 0.15188 | 0.14911 | 0.14635
| HTN034-142233590 | HTN034 | 0.090139 | 0.090945 | 0.091751 | 0.092558 | 0.093364 | 0.092341 | 0.091318 | 0.090295 | 0.089273 | 0.08825 | 0.087227 | 0.086205 | 0.085182 | 0.084159 | 0.083137 | 0.082114 | 0.081091 | 0.080068 | 0.079046 | 0.078023
| HTN034-142234012 | HTN034 | 0.14392 | 0.14462 | 0.14531 | 0.146 | 0.1467 | 0.14581 | 0.14492 | 0.14403 | 0.14314 | 0.14226 | 0.14137 | 0.14048 | 0.13959 | 0.1387 | 0.13782 | 0.13693 | 0.13604 | 0.13515 | 0.13426 | 0.13338
| HTN034-157456094 | HTN034 | 0.0067868 | 0.0068253 | 0.0068637 | 0.0069022 | 0.0069407 | 0.0069013 | 0.0068619 | 0.0068225 | 0.0067831 | 0.0067438 | 0.0067044 | 0.006665 | 0.0066256 | 0.0065863 | 0.0065469 | 0.0065075 | 0.0064681 | 0.0064288 | 0.0063894 | 0.00635
| HTN034-157599634 | HTN034 | 0.06419 | 0.064491 | 0.064791 | 0.065092 | 0.065393 | 0.065047 | 0.064701 | 0.064355 | 0.064009 | 0.063663 | 0.063317 | 0.062971 | 0.062625 | 0.062279 | 0.061933 | 0.061587 | 0.061241 | 0.060895 | 0.06055 | 0.060204
| HTN034-157998388 | HTN034 | 0.043926 | 0.044171 | 0.044417 | 0.044662 | 0.044907 | 0.044595 | 0.044284 | 0.043972 | 0.04366 | 0.043349 | 0.043037 | 0.042726 | 0.042414 | 0.042102 | 0.041791 | 0.041479 | 0.041168 | 0.040856 | 0.040545 | 0.040233
| HTN034-157998738 | HTN034 | 0.012093 | 0.012164 | 0.012235 | 0.012305 | 0.012376 | 0.012259 | 0.012142 | 0.012026 | 0.011909 | 0.011792 | 0.011675 | 0.011559 | 0.011442 | 0.011325 | 0.011208 | 0.011092 | 0.010975 | 0.010858 | 0.010741 | 0.010625
| HTN034-157999069 | HTN034 | 0.061654 | 0.061987 | 0.062321 | 0.062655 | 0.062989 | 0.062576 | 0.062163 | 0.06175 | 0.061337 | 0.060924 | 0.060511 | 0.060098 | 0.059685 | 0.059272 | 0.058859 | 0.058446 | 0.058033 | 0.05762 | 0.057208 | 0.056795
| HTN034-158085792 | HTN034 | 0.023577 | 0.023777 | 0.023977 | 0.024177 | 0.024377 | 0.024128 | 0.02388 | 0.023631 | 0.023383 | 0.023134 | 0.022885 | 0.022637 | 0.022388 | 0.02214 | 0.021891 | 0.021643 | 0.021394 | 0.021146 | 0.020897 | 0.020649
| HTN034-158085879 | HTN034 | 0.22967 | 0.23155 | 0.23343 | 0.2353 | 0.23718 | 0.23533 | 0.23348 | 0.23162 | 0.22977 | 0.22792 | 0.22606 | 0.22421 | 0.22236 | 0.22051 | 0.21865 | 0.2168 | 0.21495 | 0.21309 | 0.21124 | 0.20939
| HTN034-158086014 | HTN034 | 3.2173e-05 | 3.2515e-05 | 3.2857e-05 | 3.3198e-05 | 3.354e-05 | 3.3221e-05 | 3.2903e-05 | 3.2584e-05 | 3.2266e-05 | 3.1947e-05 | 3.1629e-05 | 3.131e-05 | 3.0992e-05 | 3.0673e-05 | 3.0355e-05 | 3.0036e-05 | 2.9718e-05 | 2.9399e-05 | 2.9081e-05 | 2.8763e-05
| HTN034-158095163 | HTN034 | 0.043597 | 0.043796 | 0.043995 | 0.044194 | 0.044393 | 0.044197 | 0.044 | 0.043803 | 0.043607 | 0.04341 | 0.043213 | 0.043017 | 0.04282 | 0.042623 | 0.042427 | 0.04223 | 0.042033 | 0.041837 | 0.04164 | 0.041443
| HTN034-158103724 | HTN034 | 0.070113 | 0.070556 | 0.070998 | 0.07144 | 0.071883 | 0.071332 | 0.07078 | 0.070229 | 0.069677 | 0.069126 | 0.068575 | 0.068023 | 0.067472 | 0.066921 | 0.066369 | 0.065818 | 0.065266 | 0.064715 | 0.064164 | 0.063612
| HTN034-158130464 | HTN034 | 0.04311 | 0.043362 | 0.043613 | 0.043864 | 0.044115 | 0.04379 | 0.043465 | 0.04314 | 0.042815 | 0.04249 | 0.042166 | 0.041841 | 0.041516 | 0.041191 | 0.040866 | 0.040541 | 0.040216 | 0.039891 | 0.039566 | 0.039241
| HTN034-158139663 | HTN034 | 0.010281 | 0.010334 | 0.010387 | 0.010441 | 0.010494 | 0.010432 | 0.010369 | 0.010307 | 0.010245 | 0.010182 | 0.01012 | 0.010057 | 0.009995 | 0.0099326 | 0.0098702 | 0.0098078 | 0.0097454 | 0.009683 | 0.0096206 | 0.0095582
| HTN034-158494823 | HTN034 | 0.41291 | 0.4162 | 0.41948 | 0.42277 | 0.42605 | 0.42082 | 0.41559 | 0.41036 | 0.40512 | 0.39989 | 0.39466 | 0.38943 | 0.38419 | 0.37896 | 0.37373 | 0.3685 | 0.36327 | 0.35803 | 0.3528 | 0.34757
| HTN034-158495102 | HTN034 | 0.008979 | 0.0090744 | 0.0091698 | 0.0092653 | 0.0093607 | 0.0092754 | 0.00919 | 0.0091047 | 0.0090194 | 0.008934 | 0.0088487 | 0.0087633 | 0.008678 | 0.0085926 | 0.0085073 | 0.008422 | 0.0083366 | 0.0082513 | 0.0081659 | 0.0080806
| HTN034-158495212 | HTN034 | 0.012514 | 0.012619 | 0.012724 | 0.012828 | 0.012933 | 0.0128 | 0.012666 | 0.012533 | 0.0124 | 0.012267 | 0.012134 | 0.012001 | 0.011868 | 0.011735 | 0.011602 | 0.011469 | 0.011336 | 0.011203 | 0.011069 | 0.010936
| HTN034-158638369 | HTN034 | 0.033658 | 0.033921 | 0.034185 | 0.034449 | 0.034713 | 0.034377 | 0.034041 | 0.033705 | 0.033369 | 0.033033 | 0.032697 | 0.032361 | 0.032025 | 0.031689 | 0.031353 | 0.031017 | 0.030681 | 0.030345 | 0.030009 | 0.029673
| HTN034-158638445 | HTN034 | 0.02186 | 0.022048 | 0.022237 | 0.022426 | 0.022615 | 0.022279 | 0.021943 | 0.021607 | 0.021271 | 0.020935 | 0.020598 | 0.020262 | 0.019926 | 0.01959 | 0.019254 | 0.018918 | 0.018582 | 0.018246 | 0.01791 | 0.017574
| HTN034-158638542 | HTN034 | 0.064722 | 0.065128 | 0.065533 | 0.065938 | 0.066343 | 0.065569 | 0.064795 | 0.064021 | 0.063247 | 0.062473 | 0.061699 | 0.060925 | 0.060151 | 0.059377 | 0.058603 | 0.057829 | 0.057055 | 0.056281 | 0.055507 | 0.054733
| HTN034-158638725 | HTN034 | 0.027389 | 0.027638 | 0.027887 | 0.028137 | 0.028386 | 0.028143 | 0.0279 | 0.027656 | 0.027413 | 0.02717 | 0.026927 | 0.026684 | 0.02644 | 0.026197 | 0.025954 | 0.025711 | 0.025468 | 0.025224 | 0.024981 | 0.024738
| HTN034-158639522 | HTN034 | 6.2395e-05 | 6.2719e-05 | 6.3043e-05 | 6.3366e-05 | 6.369e-05 | 6.3354e-05 | 6.3019e-05 | 6.2683e-05 | 6.2348e-05 | 6.2012e-05 | 6.1677e-05 | 6.1341e-05 | 6.1006e-05 | 6.067e-05 | 6.0335e-05 | 5.9999e-05 | 5.9664e-05 | 5.9328e-05 | 5.8993e-05 | 5.8657e-05
| HTN034-158639644 | HTN034 | 0.037034 | 0.037368 | 0.037702 | 0.038036 | 0.03837 | 0.037988 | 0.037606 | 0.037225 | 0.036843 | 0.036461 | 0.036079 | 0.035697 | 0.035315 | 0.034933 | 0.034551 | 0.034169 | 0.033787 | 0.033405 | 0.033023 | 0.032641
| HTN034-158639828 | HTN034 | 0.018278 | 0.018385 | 0.018493 | 0.0186 | 0.018707 | 0.018537 | 0.018366 | 0.018196 | 0.018026 | 0.017855 | 0.017685 | 0.017514 | 0.017344 | 0.017174 | 0.017003 | 0.016833 | 0.016662 | 0.016492 | 0.016322 | 0.016151
| HTN034-158639936 | HTN034 | 0.0047218 | 0.0047491 | 0.0047763 | 0.0048035 | 0.0048308 | 0.004778 | 0.0047253 | 0.0046725 | 0.0046198 | 0.004567 | 0.0045143 | 0.0044615 | 0.0044088 | 0.004356 | 0.0043033 | 0.0042505 | 0.0041978 | 0.004145 | 0.0040923 | 0.0040395
| HTN034-158640079 | HTN034 | 0.00025262 | 0.00025426 | 0.00025591 | 0.00025755 | 0.0002592 | 0.00025776 | 0.00025632 | 0.00025488 | 0.00025344 | 0.000252 | 0.00025056 | 0.00024912 | 0.00024768 | 0.00024624 | 0.0002448 | 0.00024336 | 0.00024192 | 0.00024048 | 0.00023904 | 0.0002376
| HTN034-158770728 | HTN034 | 0.037099 | 0.037182 | 0.037264 | 0.037347 | 0.037429 | 0.037306 | 0.037182 | 0.037058 | 0.036935 | 0.036811 | 0.036688 | 0.036564 | 0.03644 | 0.036317 | 0.036193 | 0.036069 | 0.035946 | 0.035822 | 0.035698 | 0.035575
| HTN034-158770892 | HTN034 | 0.37099 | 0.37448 | 0.37797 | 0.38146 | 0.38495 | 0.37866 | 0.37237 | 0.36608 | 0.3598 | 0.35351 | 0.34722 | 0.34093 | 0.33464 | 0.32835 | 0.32207 | 0.31578 | 0.30949 | 0.3032 | 0.29691 | 0.29063
| HTN034-160807148 | HTN034 | 0.049932 | 0.050413 | 0.050894 | 0.051375 | 0.051856 | 0.051171 | 0.050486 | 0.049801 | 0.049117 | 0.048432 | 0.047747 | 0.047062 | 0.046378 | 0.045693 | 0.045008 | 0.044323 | 0.043638 | 0.042954 | 0.042269 | 0.041584
| HTN034-161079325 | HTN034 | 0.25807 | 0.25986 | 0.26166 | 0.26345 | 0.26525 | 0.26274 | 0.26024 | 0.25774 | 0.25524 | 0.25273 | 0.25023 | 0.24773 | 0.24522 | 0.24272 | 0.24022 | 0.23772 | 0.23521 | 0.23271 | 0.23021 | 0.2277
| HTN034-161093808 | HTN034 | 0.21548 | 0.21691 | 0.21834 | 0.21977 | 0.22119 | 0.21982 | 0.21845 | 0.21707 | 0.2157 | 0.21432 | 0.21295 | 0.21157 | 0.2102 | 0.20882 | 0.20745 | 0.20607 | 0.2047 | 0.20332 | 0.20195 | 0.20057
| HTN034-162616477 | HTN034 | 0.0035 | 0.0035256 | 0.0035513 | 0.003577 | 0.0036026 | 0.0035746 | 0.0035467 | 0.0035187 | 0.0034907 | 0.0034627 | 0.0034348 | 0.0034068 | 0.0033788 | 0.0033508 | 0.0033229 | 0.0032949 | 0.0032669 | 0.0032389 | 0.003211 | 0.003183
| HTN034-162616681 | HTN034 | 0.0018983 | 0.0019087 | 0.0019191 | 0.0019296 | 0.00194 | 0.0019281 | 0.0019163 | 0.0019045 | 0.0018926 | 0.0018808 | 0.0018689 | 0.0018571 | 0.0018452 | 0.0018334 | 0.0018216 | 0.0018097 | 0.0017979 | 0.001786 | 0.0017742 | 0.0017623
| HTN034-162616888 | HTN034 | 0.0029626 | 0.0029768 | 0.002991 | 0.0030053 | 0.0030195 | 0.0030046 | 0.0029897 | 0.0029748 | 0.0029599 | 0.002945 | 0.0029301 | 0.0029152 | 0.0029003 | 0.0028854 | 0.0028705 | 0.0028556 | 0.0028407 | 0.0028258 | 0.0028109 | 0.002796
| HTN034-162617230 | HTN034 | 0.0054866 | 0.0055227 | 0.0055588 | 0.0055949 | 0.005631 | 0.0055912 | 0.0055515 | 0.0055117 | 0.0054719 | 0.0054322 | 0.0053924 | 0.0053527 | 0.0053129 | 0.0052731 | 0.0052334 | 0.0051936 | 0.0051539 | 0.0051141 | 0.0050743 | 0.0050346
| HTN034-162626507 | HTN034 | 0.0078586 | 0.0079518 | 0.008045 | 0.0081383 | 0.0082315 | 0.0080704 | 0.0079094 | 0.0077483 | 0.0075873 | 0.0074262 | 0.0072652 | 0.0071041 | 0.0069431 | 0.006782 | 0.0066209 | 0.0064599 | 0.0062988 | 0.0061378 | 0.0059767 | 0.0058157
| HTN034-162646056 | HTN034 | 0.024438 | 0.024577 | 0.024716 | 0.024854 | 0.024993 | 0.02482 | 0.024647 | 0.024474 | 0.024301 | 0.024128 | 0.023955 | 0.023782 | 0.023608 | 0.023435 | 0.023262 | 0.023089 | 0.022916 | 0.022743 | 0.02257 | 0.022397
| HTN034-162671356 | HTN034 | 0.011841 | 0.011962 | 0.012084 | 0.012205 | 0.012327 | 0.012094 | 0.011861 | 0.011628 | 0.011396 | 0.011163 | 0.01093 | 0.010697 | 0.010465 | 0.010232 | 0.009999 | 0.0097662 | 0.0095335 | 0.0093007 | 0.009068 | 0.0088352
| HTN034-162794244 | HTN034 | 0.00043283 | 0.00043573 | 0.00043862 | 0.00044151 | 0.0004444 | 0.00044264 | 0.00044088 | 0.00043912 | 0.00043736 | 0.0004356 | 0.00043384 | 0.00043208 | 0.00043032 | 0.00042856 | 0.0004268 | 0.00042504 | 0.00042328 | 0.00042152 | 0.00041976 | 0.000418
| HTN034-162794768 | HTN034 | 0.010591 | 0.010648 | 0.010705 | 0.010763 | 0.01082 | 0.010753 | 0.010686 | 0.010619 | 0.010552 | 0.010485 | 0.010418 | 0.010351 | 0.010285 | 0.010218 | 0.010151 | 0.010084 | 0.010017 | 0.0099498 | 0.0098828 | 0.0098159
| HTN034-167870005 | HTN034 | 0.04585 | 0.046211 | 0.046571 | 0.046932 | 0.047293 | 0.046957 | 0.046621 | 0.046285 | 0.045949 | 0.045613 | 0.045277 | 0.044942 | 0.044606 | 0.04427 | 0.043934 | 0.043598 | 0.043262 | 0.042926 | 0.04259 | 0.042254
| HTN034-172348553 | HTN034 | 0.00014568 | 0.00014636 | 0.00014704 | 0.00014772 | 0.0001484 | 0.00014756 | 0.00014672 | 0.00014588 | 0.00014504 | 0.0001442 | 0.00014336 | 0.00014252 | 0.00014168 | 0.00014084 | 0.00014 | 0.00013916 | 0.00013832 | 0.00013748 | 0.00013664 | 0.0001358
| HTN034-182145724 | HTN034 | 36.1574 | 36.3833 | 36.6091 | 36.835 | 37.0608 | 36.7024 | 36.3439 | 35.9855 | 35.627 | 35.2686 | 34.9101 | 34.5517 | 34.1932 | 33.8348 | 33.4763 | 33.1179 | 32.7595 | 32.401 | 32.0426 | 31.6841
| HTN034-182145744 | HTN034 | 3.8509 | 3.8765 | 3.9021 | 3.9276 | 3.9532 | 3.921 | 3.8889 | 3.8567 | 3.8246 | 3.7924 | 3.7602 | 3.7281 | 3.6959 | 3.6637 | 3.6316 | 3.5994 | 3.5672 | 3.5351 | 3.5029 | 3.4707
| HTN034-182145765 | HTN034 | 2.2378 | 2.251 | 2.2642 | 2.2773 | 2.2905 | 2.28 | 2.2696 | 2.2592 | 2.2487 | 2.2383 | 2.2279 | 2.2174 | 2.207 | 2.1966 | 2.1861 | 2.1757 | 2.1652 | 2.1548 | 2.1444 | 2.1339
| HTN034-190418432 | HTN034 | 2.6455 | 2.6687 | 2.692 | 2.7152 | 2.7384 | 2.7122 | 2.6859 | 2.6597 | 2.6334 | 2.6072 | 2.5809 | 2.5547 | 2.5285 | 2.5022 | 2.476 | 2.4497 | 2.4235 | 2.3972 | 2.371 | 2.3447
| HTN034-84443403 | HTN034 | 2.5479 | 2.5602 | 2.5725 | 2.5847 | 2.597 | 2.582 | 2.5671 | 2.5521 | 2.5372 | 2.5222 | 2.5073 | 2.4923 | 2.4774 | 2.4625 | 2.4475 | 2.4326 | 2.4176 | 2.4027 | 2.3877 | 2.3728
| HYT011-157370486 | HYT011 | 0.011504 | 0.011577 | 0.011649 | 0.011722 | 0.011795 | 0.011538 | 0.01128 | 0.011023 | 0.010766 | 0.010508 | 0.010251 | 0.0099934 | 0.009736 | 0.0094786 | 0.0092212 | 0.0089638 | 0.0087064 | 0.008449 | 0.0081916 | 0.0079342
| HYT011-157370579 | HYT011 | 0.016975 | 0.017082 | 0.017189 | 0.017296 | 0.017404 | 0.017064 | 0.016724 | 0.016384 | 0.016043 | 0.015703 | 0.015363 | 0.015023 | 0.014683 | 0.014343 | 0.014003 | 0.013663 | 0.013323 | 0.012983 | 0.012643 | 0.012303
| HYT011-162212996 | HYT011 | 0.0030107 | 0.0030318 | 0.0030529 | 0.0030741 | 0.0030952 | 0.003031 | 0.0029668 | 0.0029026 | 0.0028384 | 0.0027742 | 0.00271 | 0.0026458 | 0.0025816 | 0.0025175 | 0.0024533 | 0.0023891 | 0.0023249 | 0.0022607 | 0.0021965 | 0.0021323
| HYT011-162213233 | HYT011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HYT011-41829518 | HYT011 | 2.3929 | 2.4069 | 2.4209 | 2.4349 | 2.4489 | 2.4237 | 2.3985 | 2.3733 | 2.3481 | 2.3228 | 2.2976 | 2.2724 | 2.2472 | 2.222 | 2.1968 | 2.1716 | 2.1463 | 2.1211 | 2.0959 | 2.0707
| HYT011-82429866 | HYT011 | 0.018752 | 0.018876 | 0.019001 | 0.019125 | 0.019249 | 0.018995 | 0.01874 | 0.018486 | 0.018231 | 0.017976 | 0.017722 | 0.017467 | 0.017213 | 0.016958 | 0.016703 | 0.016449 | 0.016194 | 0.01594 | 0.015685 | 0.01543
| KGT002-15430186 | KGT002 | 31.7503 | 31.9587 | 32.1672 | 32.3757 | 32.5842 | 32.7733 | 32.9624 | 33.1515 | 33.3406 | 33.5298 | 33.7189 | 33.908 | 34.0971 | 34.2862 | 34.4753 | 34.6644 | 34.8535 | 35.0426 | 35.2317 | 35.4208
| KGT002-24605712 | KGT002 | 0.29438 | 0.29603 | 0.29767 | 0.29931 | 0.30096 | 0.30226 | 0.30355 | 0.30485 | 0.30615 | 0.30745 | 0.30875 | 0.31005 | 0.31135 | 0.31265 | 0.31395 | 0.31525 | 0.31655 | 0.31785 | 0.31915 | 0.32045
| KGT003-119555477 | KGT003 | 10.2407 | 10.2512 | 10.2616 | 10.2721 | 10.2826 | 10.2742 | 10.2658 | 10.2575 | 10.2491 | 10.2408 | 10.2324 | 10.2241 | 10.2157 | 10.2073 | 10.199 | 10.1906 | 10.1823 | 10.1739 | 10.1656 | 10.1572
| KGT003-15424502 | KGT003 | 4.234 | 4.2626 | 4.2912 | 4.3198 | 4.3485 | 4.3781 | 4.4076 | 4.4372 | 4.4668 | 4.4964 | 4.526 | 4.5556 | 4.5852 | 4.6147 | 4.6443 | 4.6739 | 4.7035 | 4.7331 | 4.7627 | 4.7922
| KGT003-155046250 | KGT003 | 0.05669 | 0.057146 | 0.057602 | 0.058057 | 0.058513 | 0.058846 | 0.059178 | 0.059511 | 0.059844 | 0.060176 | 0.060509 | 0.060842 | 0.061175 | 0.061507 | 0.06184 | 0.062173 | 0.062505 | 0.062838 | 0.063171 | 0.063503
| KGT003-155046371 | KGT003 | 0.00022454 | 0.0002265 | 0.00022847 | 0.00023043 | 0.0002324 | 0.00023432 | 0.00023624 | 0.00023816 | 0.00024008 | 0.000242 | 0.00024392 | 0.00024584 | 0.00024776 | 0.00024968 | 0.0002516 | 0.00025352 | 0.00025544 | 0.00025736 | 0.00025928 | 0.0002612
| KGT003-155131479 | KGT003 | 0.013484 | 0.013587 | 0.013689 | 0.013791 | 0.013893 | 0.014024 | 0.014155 | 0.014286 | 0.014417 | 0.014548 | 0.01468 | 0.014811 | 0.014942 | 0.015073 | 0.015204 | 0.015335 | 0.015466 | 0.015597 | 0.015728 | 0.015859
| KGT003-155165277 | KGT003 | 0.012505 | 0.012587 | 0.01267 | 0.012752 | 0.012834 | 0.012956 | 0.013077 | 0.013198 | 0.013319 | 0.013441 | 0.013562 | 0.013683 | 0.013804 | 0.013925 | 0.014047 | 0.014168 | 0.014289 | 0.01441 | 0.014532 | 0.014653
| KGT003-155165426 | KGT003 | 0.089874 | 0.090476 | 0.091077 | 0.091678 | 0.092279 | 0.092963 | 0.093647 | 0.094331 | 0.095016 | 0.0957 | 0.096384 | 0.097068 | 0.097752 | 0.098436 | 0.09912 | 0.099804 | 0.10049 | 0.10117 | 0.10186 | 0.10254
| KGT003-155165521 | KGT003 | 0.11391 | 0.11469 | 0.11548 | 0.11626 | 0.11705 | 0.11769 | 0.11834 | 0.11898 | 0.11963 | 0.12028 | 0.12092 | 0.12157 | 0.12221 | 0.12286 | 0.12351 | 0.12415 | 0.1248 | 0.12544 | 0.12609 | 0.12674
| KGT003-155165638 | KGT003 | 0.10593 | 0.10653 | 0.10714 | 0.10774 | 0.10834 | 0.10933 | 0.11032 | 0.11131 | 0.1123 | 0.11329 | 0.11428 | 0.11527 | 0.11625 | 0.11724 | 0.11823 | 0.11922 | 0.12021 | 0.1212 | 0.12219 | 0.12318
| KGT003-155165904 | KGT003 | 0.092594 | 0.093269 | 0.093944 | 0.094619 | 0.095294 | 0.095858 | 0.096421 | 0.096985 | 0.097549 | 0.098113 | 0.098677 | 0.099241 | 0.099804 | 0.10037 | 0.10093 | 0.1015 | 0.10206 | 0.10262 | 0.10319 | 0.10375
| KGT003-155166011 | KGT003 | 0.011155 | 0.011237 | 0.011318 | 0.011399 | 0.01148 | 0.011575 | 0.011671 | 0.011766 | 0.011861 | 0.011956 | 0.012051 | 0.012146 | 0.012241 | 0.012336 | 0.012431 | 0.012526 | 0.012621 | 0.012716 | 0.012811 | 0.012906
| KGT003-155166153 | KGT003 | 0.046158 | 0.046489 | 0.04682 | 0.047151 | 0.047482 | 0.047742 | 0.048002 | 0.048261 | 0.048521 | 0.048781 | 0.04904 | 0.0493 | 0.04956 | 0.04982 | 0.050079 | 0.050339 | 0.050599 | 0.050858 | 0.051118 | 0.051378
| KGT003-155166380 | KGT003 | 0.044679 | 0.044954 | 0.04523 | 0.045506 | 0.045782 | 0.046233 | 0.046684 | 0.047136 | 0.047587 | 0.048038 | 0.048489 | 0.04894 | 0.049391 | 0.049842 | 0.050293 | 0.050744 | 0.051195 | 0.051646 | 0.052097 | 0.052548
| KGT003-155177979 | KGT003 | 0.21811 | 0.21988 | 0.22165 | 0.22342 | 0.2252 | 0.22589 | 0.22659 | 0.22729 | 0.22798 | 0.22868 | 0.22937 | 0.23007 | 0.23077 | 0.23146 | 0.23216 | 0.23285 | 0.23355 | 0.23425 | 0.23494 | 0.23564
| KGT003-155178122 | KGT003 | 0.00044494 | 0.00044786 | 0.00045077 | 0.00045369 | 0.0004566 | 0.00046122 | 0.00046584 | 0.00047046 | 0.00047508 | 0.0004797 | 0.00048432 | 0.00048894 | 0.00049356 | 0.00049818 | 0.0005028 | 0.00050742 | 0.00051204 | 0.00051666 | 0.00052128 | 0.0005259
| KGT003-155178538 | KGT003 | 0.00032884 | 0.00033098 | 0.00033312 | 0.00033526 | 0.0003374 | 0.00034083 | 0.00034426 | 0.00034769 | 0.00035112 | 0.00035455 | 0.00035798 | 0.00036141 | 0.00036484 | 0.00036827 | 0.0003717 | 0.00037513 | 0.00037856 | 0.00038199 | 0.00038542 | 0.00038885
| KGT003-84636133 | KGT003 | 31.7614 | 31.967 | 32.1726 | 32.3781 | 32.5837 | 32.6763 | 32.7689 | 32.8615 | 32.9541 | 33.0467 | 33.1394 | 33.232 | 33.3246 | 33.4172 | 33.5098 | 33.6024 | 33.6951 | 33.7877 | 33.8803 | 33.9729
| KGT004-15430149 | KGT004 | 2.4107 | 2.4277 | 2.4447 | 2.4617 | 2.4786 | 2.499 | 2.5193 | 2.5397 | 2.56 | 2.5804 | 2.6008 | 2.6211 | 2.6415 | 2.6618 | 2.6822 | 2.7025 | 2.7229 | 2.7433 | 2.7636 | 2.784
| KGT004-154877585 | KGT004 | 0.0005124 | 0.0005166 | 0.0005208 | 0.000525 | 0.0005292 | 0.00053498 | 0.00054075 | 0.00054653 | 0.0005523 | 0.00055808 | 0.00056385 | 0.00056963 | 0.0005754 | 0.00058118 | 0.00058695 | 0.00059273 | 0.0005985 | 0.00060428 | 0.00061005 | 0.00061583
| KGT004-154878038 | KGT004 | 0.043159 | 0.043475 | 0.04379 | 0.044106 | 0.044421 | 0.044865 | 0.045309 | 0.045753 | 0.046196 | 0.04664 | 0.047084 | 0.047527 | 0.047971 | 0.048415 | 0.048859 | 0.049302 | 0.049746 | 0.05019 | 0.050633 | 0.051077
| KGT004-154878151 | KGT004 | 0.12555 | 0.12625 | 0.12695 | 0.12765 | 0.12835 | 0.129 | 0.12966 | 0.13032 | 0.13098 | 0.13163 | 0.13229 | 0.13295 | 0.1336 | 0.13426 | 0.13492 | 0.13558 | 0.13623 | 0.13689 | 0.13755 | 0.1382
| KGT004-154878281 | KGT004 | 0.068274 | 0.068787 | 0.069299 | 0.069811 | 0.070323 | 0.07098 | 0.071636 | 0.072293 | 0.072949 | 0.073606 | 0.074262 | 0.074919 | 0.075575 | 0.076232 | 0.076888 | 0.077545 | 0.078201 | 0.078858 | 0.079514 | 0.080171
| KGT004-154878429 | KGT004 | 0.35261 | 0.35498 | 0.35734 | 0.3597 | 0.36206 | 0.36576 | 0.36945 | 0.37315 | 0.37684 | 0.38053 | 0.38423 | 0.38792 | 0.39162 | 0.39531 | 0.39901 | 0.4027 | 0.4064 | 0.41009 | 0.41378 | 0.41748
| KGT004-154971301 | KGT004 | 0.0014143 | 0.0014249 | 0.0014356 | 0.0014462 | 0.0014568 | 0.0014719 | 0.001487 | 0.0015021 | 0.0015171 | 0.0015322 | 0.0015473 | 0.0015624 | 0.0015775 | 0.0015926 | 0.0016076 | 0.0016227 | 0.0016378 | 0.0016529 | 0.001668 | 0.0016831
| KGT004-154971445 | KGT004 | 5.332e-05 | 5.374e-05 | 5.416e-05 | 5.458e-05 | 5.5e-05 | 5.5635e-05 | 5.627e-05 | 5.6905e-05 | 5.754e-05 | 5.8175e-05 | 5.881e-05 | 5.9445e-05 | 6.008e-05 | 6.0715e-05 | 6.135e-05 | 6.1985e-05 | 6.262e-05 | 6.3255e-05 | 6.389e-05 | 6.4525e-05
| KGT004-154971580 | KGT004 | 0.0089672 | 0.0090361 | 0.009105 | 0.0091739 | 0.0092428 | 0.0093101 | 0.0093774 | 0.0094447 | 0.009512 | 0.0095793 | 0.0096466 | 0.0097139 | 0.0097812 | 0.0098485 | 0.0099158 | 0.009983 | 0.01005 | 0.010118 | 0.010185 | 0.010252
| KGT004-154971674 | KGT004 | 0.0021714 | 0.0021877 | 0.0022039 | 0.0022202 | 0.0022364 | 0.0022644 | 0.0022923 | 0.0023203 | 0.0023483 | 0.0023762 | 0.0024042 | 0.0024321 | 0.0024601 | 0.002488 | 0.002516 | 0.0025439 | 0.0025719 | 0.0025999 | 0.0026278 | 0.0026558
| KGT004-160450903 | KGT004 | 0.047562 | 0.04797 | 0.048377 | 0.048785 | 0.049192 | 0.049501 | 0.04981 | 0.050119 | 0.050428 | 0.050737 | 0.051046 | 0.051355 | 0.051664 | 0.051973 | 0.052282 | 0.052591 | 0.0529 | 0.053209 | 0.053518 | 0.053827
| KGT004-24604166 | KGT004 | 0.41322 | 0.4166 | 0.41999 | 0.42338 | 0.42677 | 0.42844 | 0.43012 | 0.43179 | 0.43347 | 0.43514 | 0.43682 | 0.4385 | 0.44017 | 0.44185 | 0.44352 | 0.4452 | 0.44688 | 0.44855 | 0.45023 | 0.4519
| KGT004-24604180 | KGT004 | 1.0059 | 1.013 | 1.0202 | 1.0273 | 1.0345 | 1.0431 | 1.0517 | 1.0603 | 1.0689 | 1.0775 | 1.0861 | 1.0947 | 1.1033 | 1.112 | 1.1206 | 1.1292 | 1.1378 | 1.1464 | 1.155 | 1.1636
| KGT004-24605698 | KGT004 | 17.4823 | 17.5929 | 17.7035 | 17.8141 | 17.9248 | 18.0651 | 18.2055 | 18.3458 | 18.4862 | 18.6265 | 18.7669 | 18.9072 | 19.0475 | 19.1879 | 19.3282 | 19.4686 | 19.6089 | 19.7493 | 19.8896 | 20.03
| KGT004-24605978 | KGT004 | 2.0057 | 2.0081 | 2.0105 | 2.0129 | 2.0153 | 2.0134 | 2.0116 | 2.0097 | 2.0078 | 2.006 | 2.0041 | 2.0022 | 2.0004 | 1.9985 | 1.9967 | 1.9948 | 1.9929 | 1.9911 | 1.9892 | 1.9873
| KGT004-55202181 | KGT004 | 12.4087 | 12.5094 | 12.6102 | 12.7109 | 12.8116 | 12.8767 | 12.9419 | 13.007 | 13.0721 | 13.1373 | 13.2024 | 13.2676 | 13.3327 | 13.3978 | 13.463 | 13.5281 | 13.5933 | 13.6584 | 13.7235 | 13.7887
| KRT012-118960990 | KRT012 | 0.031438 | 0.031716 | 0.031995 | 0.032273 | 0.032552 | 0.031921 | 0.03129 | 0.03066 | 0.030029 | 0.029399 | 0.028768 | 0.028137 | 0.027507 | 0.026876 | 0.026246 | 0.025615 | 0.024984 | 0.024354 | 0.023723 | 0.023093
| KRT012-141850121 | KRT012 | 0.045473 | 0.045917 | 0.04636 | 0.046803 | 0.047246 | 0.046504 | 0.045762 | 0.04502 | 0.044277 | 0.043535 | 0.042793 | 0.04205 | 0.041308 | 0.040566 | 0.039824 | 0.039081 | 0.038339 | 0.037597 | 0.036854 | 0.036112
| KRT012-141850552 | KRT012 | 0.078113 | 0.078887 | 0.079662 | 0.080436 | 0.081211 | 0.079912 | 0.078613 | 0.077315 | 0.076016 | 0.074717 | 0.073419 | 0.07212 | 0.070822 | 0.069523 | 0.068224 | 0.066926 | 0.065627 | 0.064328 | 0.06303 | 0.061731
| KRT012-141850665 | KRT012 | 0.052121 | 0.052242 | 0.052364 | 0.052485 | 0.052606 | 0.052455 | 0.052303 | 0.052152 | 0.052 | 0.051848 | 0.051697 | 0.051545 | 0.051393 | 0.051242 | 0.05109 | 0.050939 | 0.050787 | 0.050635 | 0.050484 | 0.050332
| KRT012-15397067 | KRT012 | 2.6486 | 2.6667 | 2.6848 | 2.7029 | 2.721 | 2.6778 | 2.6346 | 2.5914 | 2.5483 | 2.5051 | 2.4619 | 2.4187 | 2.3755 | 2.3323 | 2.2891 | 2.2459 | 2.2027 | 2.1595 | 2.1163 | 2.0731
| KRT012-160501273 | KRT012 | 0.013441 | 0.013561 | 0.013681 | 0.013801 | 0.013921 | 0.013638 | 0.013356 | 0.013073 | 0.012791 | 0.012508 | 0.012225 | 0.011943 | 0.01166 | 0.011378 | 0.011095 | 0.010812 | 0.01053 | 0.010247 | 0.0099645 | 0.0096819
| KRT012-163206103 | KRT012 | 0.00021974 | 0.0002221 | 0.00022447 | 0.00022683 | 0.0002292 | 0.00022278 | 0.00021636 | 0.00020994 | 0.00020352 | 0.0001971 | 0.00019068 | 0.00018426 | 0.00017784 | 0.00017142 | 0.000165 | 0.00015858 | 0.00015216 | 0.00014574 | 0.00013932 | 0.0001329
| KRT012-163310215 | KRT012 | 0.0033365 | 0.0033736 | 0.0034108 | 0.003448 | 0.0034851 | 0.0034237 | 0.0033622 | 0.0033007 | 0.0032392 | 0.0031777 | 0.0031162 | 0.0030547 | 0.0029932 | 0.0029317 | 0.0028702 | 0.0028087 | 0.0027472 | 0.0026857 | 0.0026242 | 0.0025627
| KRT012-163310404 | KRT012 | 0.00048903 | 0.00049413 | 0.00049922 | 0.00050431 | 0.0005094 | 0.00050009 | 0.00049077 | 0.00048146 | 0.00047214 | 0.00046283 | 0.00045351 | 0.0004442 | 0.00043488 | 0.00042557 | 0.00041625 | 0.00040694 | 0.00039762 | 0.00038831 | 0.00037899 | 0.00036968
| KRT012-163313957 | KRT012 | 0.00014878 | 0.00015026 | 0.00015174 | 0.00015322 | 0.0001547 | 0.00015116 | 0.00014763 | 0.0001441 | 0.00014056 | 0.00013703 | 0.00013349 | 0.00012996 | 0.00012642 | 0.00012289 | 0.00011935 | 0.00011582 | 0.00011228 | 0.00010875 | 0.00010521 | 0.00010168
| KRT012-24598034 | KRT012 | 1.1403 | 1.151 | 1.1617 | 1.1725 | 1.1832 | 1.16 | 1.1368 | 1.1135 | 1.0903 | 1.0671 | 1.0438 | 1.0206 | 0.99738 | 0.97415 | 0.95092 | 0.9277 | 0.90447 | 0.88124 | 0.85801 | 0.83478
| KRT013-146237675 | KRT013 | 0.015024 | 0.015184 | 0.015344 | 0.015504 | 0.015664 | 0.015405 | 0.015146 | 0.014888 | 0.014629 | 0.01437 | 0.014112 | 0.013853 | 0.013594 | 0.013336 | 0.013077 | 0.012818 | 0.01256 | 0.012301 | 0.012042 | 0.011784
| KRT013-15397117 | KRT013 | 6.3035 | 6.3548 | 6.4061 | 6.4573 | 6.5086 | 6.4131 | 6.3176 | 6.222 | 6.1265 | 6.0309 | 5.9354 | 5.8399 | 5.7443 | 5.6488 | 5.5533 | 5.4577 | 5.3622 | 5.2666 | 5.1711 | 5.0756
| KRT013-15397128 | KRT013 | 1.6237e-06 | 1.6363e-06 | 1.6489e-06 | 1.6614e-06 | 1.674e-06 | 1.6413e-06 | 1.6086e-06 | 1.5759e-06 | 1.5432e-06 | 1.5105e-06 | 1.4778e-06 | 1.4451e-06 | 1.4124e-06 | 1.3797e-06 | 1.347e-06 | 1.3143e-06 | 1.2816e-06 | 1.2489e-06 | 1.2162e-06 | 1.1835e-06
| KRT013-157932507 | KRT013 | 0.011486 | 0.011579 | 0.011673 | 0.011767 | 0.01186 | 0.01168 | 0.011499 | 0.011318 | 0.011137 | 0.010956 | 0.010775 | 0.010595 | 0.010414 | 0.010233 | 0.010052 | 0.0098714 | 0.0096906 | 0.0095098 | 0.009329 | 0.0091482
| KRT013-159317752 | KRT013 | 0.0092225 | 0.0092961 | 0.0093697 | 0.0094433 | 0.0095168 | 0.0093753 | 0.0092338 | 0.0090923 | 0.0089508 | 0.0088093 | 0.0086678 | 0.0085263 | 0.0083848 | 0.0082433 | 0.0081018 | 0.0079603 | 0.0078188 | 0.0076773 | 0.0075358 | 0.0073943
| KRT013-159427901 | KRT013 | 0.012703 | 0.012777 | 0.012851 | 0.012925 | 0.012999 | 0.012766 | 0.012532 | 0.012298 | 0.012064 | 0.011831 | 0.011597 | 0.011363 | 0.01113 | 0.010896 | 0.010662 | 0.010429 | 0.010195 | 0.0099612 | 0.0097275 | 0.0094938
| KRT013-161097284 | KRT013 | 0.078744 | 0.079341 | 0.079938 | 0.080535 | 0.081132 | 0.080209 | 0.079286 | 0.078363 | 0.07744 | 0.076517 | 0.075593 | 0.07467 | 0.073747 | 0.072824 | 0.071901 | 0.070978 | 0.070054 | 0.069131 | 0.068208 | 0.067285
| KRT013-161918444 | KRT013 | 0.0038297 | 0.0038607 | 0.0038917 | 0.0039227 | 0.0039537 | 0.0039037 | 0.0038537 | 0.0038038 | 0.0037538 | 0.0037038 | 0.0036539 | 0.0036039 | 0.0035539 | 0.0035039 | 0.003454 | 0.003404 | 0.003354 | 0.003304 | 0.0032541 | 0.0032041
| KRT013-163312849 | KRT013 | 0.0019939 | 0.002009 | 0.0020241 | 0.0020392 | 0.0020542 | 0.0020301 | 0.0020059 | 0.0019818 | 0.0019576 | 0.0019335 | 0.0019093 | 0.0018852 | 0.001861 | 0.0018369 | 0.0018127 | 0.0017886 | 0.0017644 | 0.0017403 | 0.0017161 | 0.0016919
| KRT013-163376810 | KRT013 | 0.015279 | 0.015414 | 0.015548 | 0.015683 | 0.015818 | 0.015624 | 0.01543 | 0.015236 | 0.015041 | 0.014847 | 0.014653 | 0.014459 | 0.014265 | 0.01407 | 0.013876 | 0.013682 | 0.013488 | 0.013294 | 0.013099 | 0.012905
| KRT013-163377041 | KRT013 | 0.00020126 | 0.00020314 | 0.00020503 | 0.00020691 | 0.0002088 | 0.00020496 | 0.00020112 | 0.00019728 | 0.00019344 | 0.0001896 | 0.00018576 | 0.00018192 | 0.00017808 | 0.00017424 | 0.0001704 | 0.00016656 | 0.00016272 | 0.00015888 | 0.00015504 | 0.0001512
| KRT013-163377167 | KRT013 | 0.014374 | 0.014516 | 0.014658 | 0.0148 | 0.014942 | 0.014742 | 0.014542 | 0.014342 | 0.014142 | 0.013942 | 0.013742 | 0.013542 | 0.013342 | 0.013142 | 0.012942 | 0.012742 | 0.012542 | 0.012342 | 0.012142 | 0.011942
| KRT013-163377432 | KRT013 | 0.0029747 | 0.0029983 | 0.0030218 | 0.0030453 | 0.0030689 | 0.0030237 | 0.0029786 | 0.0029334 | 0.0028883 | 0.0028431 | 0.002798 | 0.0027528 | 0.0027077 | 0.0026625 | 0.0026174 | 0.0025722 | 0.002527 | 0.0024819 | 0.0024367 | 0.0023916
| KRT013-163377643 | KRT013 | 0.00023749 | 0.00023987 | 0.00024225 | 0.00024462 | 0.000247 | 0.00024134 | 0.00023569 | 0.00023003 | 0.00022438 | 0.00021873 | 0.00021307 | 0.00020742 | 0.00020176 | 0.00019611 | 0.00019045 | 0.0001848 | 0.00017914 | 0.00017349 | 0.00016783 | 0.00016218
| KRT013-163377831 | KRT013 | 0.0052015 | 0.0052415 | 0.0052815 | 0.0053216 | 0.0053616 | 0.0052735 | 0.0051854 | 0.0050974 | 0.0050093 | 0.0049212 | 0.0048332 | 0.0047451 | 0.004657 | 0.0045689 | 0.0044809 | 0.0043928 | 0.0043047 | 0.0042167 | 0.0041286 | 0.0040405
| KRT013-24611768 | KRT013 | 0.076167 | 0.076734 | 0.077301 | 0.077868 | 0.078434 | 0.077853 | 0.077271 | 0.076689 | 0.076107 | 0.075526 | 0.074944 | 0.074362 | 0.07378 | 0.073198 | 0.072617 | 0.072035 | 0.071453 | 0.070871 | 0.07029 | 0.069708
| KRT013-79724634 | KRT013 | 0.29084 | 0.29339 | 0.29595 | 0.2985 | 0.30105 | 0.29842 | 0.2958 | 0.29318 | 0.29055 | 0.28793 | 0.28531 | 0.28268 | 0.28006 | 0.27743 | 0.27481 | 0.27219 | 0.26956 | 0.26694 | 0.26431 | 0.26169
| KRT013-79724804 | KRT013 | 5.251 | 5.2849 | 5.3189 | 5.3528 | 5.3867 | 5.2957 | 5.2047 | 5.1137 | 5.0227 | 4.9317 | 4.8407 | 4.7497 | 4.6587 | 4.5677 | 4.4767 | 4.3857 | 4.2947 | 4.2037 | 4.1127 | 4.0217
| KRT022-15396980 | KRT022 | 4.2357 | 4.2825 | 4.3292 | 4.3759 | 4.4227 | 4.3288 | 4.2348 | 4.1409 | 4.047 | 3.953 | 3.8591 | 3.7652 | 3.6713 | 3.5773 | 3.4834 | 3.3895 | 3.2956 | 3.2016 | 3.1077 | 3.0138
| KRT022-72389353 | KRT022 | 7.5883 | 7.6381 | 7.688 | 7.7378 | 7.7877 | 7.7366 | 7.6855 | 7.6344 | 7.5833 | 7.5322 | 7.4811 | 7.43 | 7.3789 | 7.3279 | 7.2768 | 7.2257 | 7.1746 | 7.1235 | 7.0724 | 7.0213
| KRT023-15396956 | KRT023 | 0.032666 | 0.032922 | 0.033178 | 0.033434 | 0.03369 | 0.033376 | 0.033062 | 0.032749 | 0.032435 | 0.032122 | 0.031808 | 0.031494 | 0.031181 | 0.030867 | 0.030554 | 0.03024 | 0.029926 | 0.029613 | 0.029299 | 0.028986
| KRT031-15433128 | KRT031 | 0.063374 | 0.064031 | 0.064688 | 0.065344 | 0.066001 | 0.064305 | 0.062609 | 0.060912 | 0.059216 | 0.05752 | 0.055824 | 0.054127 | 0.052431 | 0.050735 | 0.049039 | 0.047342 | 0.045646 | 0.04395 | 0.042254 | 0.040557
| KRT031-163356648 | KRT031 | 0.0029829 | 0.0030138 | 0.0030448 | 0.0030757 | 0.0031066 | 0.0030269 | 0.0029472 | 0.0028675 | 0.0027878 | 0.0027081 | 0.0026283 | 0.0025486 | 0.0024689 | 0.0023892 | 0.0023095 | 0.0022298 | 0.00215 | 0.0020703 | 0.0019906 | 0.0019109
| KYM001-15421949 | KYM001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM001-15421988 | KYM001 | 8.9784 | 9.0405 | 9.1026 | 9.1646 | 9.2267 | 9.2785 | 9.3303 | 9.382 | 9.4338 | 9.4855 | 9.5373 | 9.5891 | 9.6408 | 9.6926 | 9.7443 | 9.7961 | 9.8479 | 9.8996 | 9.9514 | 10.0032
| KYM001-155421580 | KYM001 | 5.3237e-05 | 5.3623e-05 | 5.4009e-05 | 5.4394e-05 | 5.478e-05 | 5.5371e-05 | 5.5962e-05 | 5.6553e-05 | 5.7144e-05 | 5.7735e-05 | 5.8326e-05 | 5.8917e-05 | 5.9508e-05 | 6.0099e-05 | 6.069e-05 | 6.1281e-05 | 6.1872e-05 | 6.2463e-05 | 6.3054e-05 | 6.3645e-05
| KYM001-155421922 | KYM001 | 0.0036123 | 0.0036386 | 0.0036648 | 0.0036911 | 0.0037173 | 0.0037536 | 0.0037898 | 0.003826 | 0.0038623 | 0.0038985 | 0.0039347 | 0.0039709 | 0.0040072 | 0.0040434 | 0.0040796 | 0.0041158 | 0.0041521 | 0.0041883 | 0.0042245 | 0.0042607
| KYM002-15422060 | KYM002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM002-15422073 | KYM002 | 1.2015 | 1.2047 | 1.2079 | 1.211 | 1.2142 | 1.2144 | 1.2146 | 1.2148 | 1.2149 | 1.2151 | 1.2153 | 1.2155 | 1.2157 | 1.2159 | 1.2161 | 1.2162 | 1.2164 | 1.2166 | 1.2168 | 1.217
| KYM002-182106953 | KYM002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM003-15421938 | KYM003 | 6.2094 | 6.2471 | 6.2847 | 6.3223 | 6.3599 | 6.4122 | 6.4645 | 6.5167 | 6.569 | 6.6213 | 6.6736 | 6.7258 | 6.7781 | 6.8304 | 6.8827 | 6.9349 | 6.9872 | 7.0395 | 7.0917 | 7.144
| KYM003-155504708 | KYM003 | 0.046156 | 0.046461 | 0.046765 | 0.04707 | 0.047375 | 0.047814 | 0.048252 | 0.048691 | 0.049129 | 0.049568 | 0.050007 | 0.050445 | 0.050884 | 0.051323 | 0.051761 | 0.0522 | 0.052639 | 0.053077 | 0.053516 | 0.053955
| KYM003-163531836 | KYM003 | 0.0049822 | 0.0050132 | 0.0050443 | 0.0050753 | 0.0051064 | 0.0051683 | 0.0052303 | 0.0052922 | 0.0053541 | 0.0054161 | 0.005478 | 0.0055399 | 0.0056018 | 0.0056638 | 0.0057257 | 0.0057876 | 0.0058496 | 0.0059115 | 0.0059734 | 0.0060354
| KYM003-24602826 | KYM003 | 3.9436 | 3.963 | 3.9825 | 4.0019 | 4.0214 | 4.0557 | 4.09 | 4.1244 | 4.1587 | 4.1931 | 4.2274 | 4.2617 | 4.2961 | 4.3304 | 4.3647 | 4.3991 | 4.4334 | 4.4678 | 4.5021 | 4.5364
| KYM004-15422136 | KYM004 | 2.6636 | 2.6795 | 2.6954 | 2.7113 | 2.7271 | 2.7393 | 2.7515 | 2.7636 | 2.7758 | 2.7879 | 2.8001 | 2.8123 | 2.8244 | 2.8366 | 2.8487 | 2.8609 | 2.8731 | 2.8852 | 2.8974 | 2.9096
| KYM004-24596780 | KYM004 | 1.3715 | 1.379 | 1.3864 | 1.3938 | 1.4013 | 1.411 | 1.4207 | 1.4304 | 1.4401 | 1.4498 | 1.4595 | 1.4692 | 1.479 | 1.4887 | 1.4984 | 1.5081 | 1.5178 | 1.5275 | 1.5372 | 1.5469
| KYM004-24596836 | KYM004 | 2.0932 | 2.1058 | 2.1183 | 2.1308 | 2.1434 | 2.1553 | 2.1673 | 2.1793 | 2.1912 | 2.2032 | 2.2152 | 2.2271 | 2.2391 | 2.2511 | 2.263 | 2.275 | 2.2869 | 2.2989 | 2.3109 | 2.3228
| KYM005-15421849 | KYM005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM006-15422186 | KYM006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KYM006-15422212 | KYM006 | 1.0713 | 1.079 | 1.0866 | 1.0943 | 1.1019 | 1.1118 | 1.1216 | 1.1315 | 1.1414 | 1.1512 | 1.1611 | 1.1709 | 1.1808 | 1.1906 | 1.2005 | 1.2104 | 1.2202 | 1.2301 | 1.2399 | 1.2498
| LV001-15406542 | LV001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV001-15406555 | LV001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV001-24613045 | LV001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV002-15406265 | LV002 | 1.0447 | 1.053 | 1.0614 | 1.0697 | 1.078 | 1.0831 | 1.0882 | 1.0933 | 1.0983 | 1.1034 | 1.1085 | 1.1135 | 1.1186 | 1.1237 | 1.1288 | 1.1338 | 1.1389 | 1.144 | 1.1491 | 1.1541
| LV003-15406616 | LV003 | 2.872 | 2.8945 | 2.9171 | 2.9397 | 2.9622 | 2.9705 | 2.9787 | 2.9869 | 2.9952 | 3.0034 | 3.0116 | 3.0198 | 3.0281 | 3.0363 | 3.0445 | 3.0528 | 3.061 | 3.0692 | 3.0774 | 3.0857
| LV004-15406315 | LV004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV004-24612407 | LV004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV005-15406664 | LV005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV005-15406790 | LV005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV006-15406376 | LV006 | 188.8733 | 190.6241 | 192.3748 | 194.1255 | 195.8763 | 195.7902 | 195.7041 | 195.618 | 195.532 | 195.4459 | 195.3598 | 195.2737 | 195.1876 | 195.1016 | 195.0155 | 194.9294 | 194.8433 | 194.7572 | 194.6712 | 194.5851
| LV006-160301671 | LV006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV007-15406690 | LV007 | 1.0054 | 1.0134 | 1.0214 | 1.0294 | 1.0375 | 1.0423 | 1.0472 | 1.0521 | 1.057 | 1.0619 | 1.0668 | 1.0716 | 1.0765 | 1.0814 | 1.0863 | 1.0912 | 1.096 | 1.1009 | 1.1058 | 1.1107
| LV008-15406413 | LV008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV008-24612803 | LV008 | 0.025564 | 0.025864 | 0.026164 | 0.026465 | 0.026765 | 0.026731 | 0.026696 | 0.026662 | 0.026628 | 0.026593 | 0.026559 | 0.026525 | 0.02649 | 0.026456 | 0.026422 | 0.026387 | 0.026353 | 0.026319 | 0.026285 | 0.02625
| LV008-24612817 | LV008 | 0.0099925 | 0.010055 | 0.010117 | 0.010179 | 0.010242 | 0.01028 | 0.010318 | 0.010356 | 0.010394 | 0.010432 | 0.01047 | 0.010508 | 0.010546 | 0.010584 | 0.010622 | 0.01066 | 0.010698 | 0.010736 | 0.010774 | 0.010812
| LV009-15406766 | LV009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV009-155428316 | LV009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV009-24611519 | LV009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV010-15437621 | LV010 | 0.020837 | 0.021004 | 0.02117 | 0.021337 | 0.021503 | 0.021604 | 0.021705 | 0.021807 | 0.021908 | 0.022009 | 0.02211 | 0.022211 | 0.022312 | 0.022414 | 0.022515 | 0.022616 | 0.022717 | 0.022818 | 0.02292 | 0.023021
| LVN021-15436461 | LVN021 | 0.00066029 | 0.00066747 | 0.00067464 | 0.00068182 | 0.000689 | 0.00068847 | 0.00068794 | 0.00068741 | 0.00068688 | 0.00068635 | 0.00068582 | 0.00068529 | 0.00068476 | 0.00068423 | 0.0006837 | 0.00068317 | 0.00068264 | 0.00068211 | 0.00068158 | 0.00068105
| LVN022-131932324 | LVN022 | 0.067567 | 0.068297 | 0.069026 | 0.069756 | 0.070485 | 0.070115 | 0.069745 | 0.069375 | 0.069005 | 0.068635 | 0.068265 | 0.067895 | 0.067525 | 0.067155 | 0.066785 | 0.066415 | 0.066045 | 0.065675 | 0.065305 | 0.064935
| LVN022-15436485 | LVN022 | 0.43606 | 0.44118 | 0.4463 | 0.45141 | 0.45653 | 0.45594 | 0.45535 | 0.45476 | 0.45417 | 0.45358 | 0.45299 | 0.4524 | 0.45181 | 0.45121 | 0.45062 | 0.45003 | 0.44944 | 0.44885 | 0.44826 | 0.44767
| LVN022-155325443 | LVN022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN023-15436448 | LVN023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN024-15436435 | LVN024 | 0.0042597 | 0.0043058 | 0.0043519 | 0.0043981 | 0.0044442 | 0.0044418 | 0.0044393 | 0.0044369 | 0.0044345 | 0.004432 | 0.0044296 | 0.0044272 | 0.0044248 | 0.0044223 | 0.0044199 | 0.0044175 | 0.004415 | 0.0044126 | 0.0044102 | 0.0044077
| LVN031-15432398 | LVN031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN032-15432411 | LVN032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN033-15432424 | LVN033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LVN034-15432437 | LVN034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN012-15419426 | MBN012 | 40.9228 | 41.1687 | 41.4146 | 41.6606 | 41.9065 | 41.8939 | 41.8813 | 41.8687 | 41.8561 | 41.8434 | 41.8308 | 41.8182 | 41.8056 | 41.793 | 41.7804 | 41.7678 | 41.7552 | 41.7426 | 41.73 | 41.7174
| MBN012-15419437 | MBN012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN013-15419363 | MBN013 | 1.226 | 1.2341 | 1.2422 | 1.2503 | 1.2584 | 1.2597 | 1.261 | 1.2623 | 1.2636 | 1.2649 | 1.2661 | 1.2674 | 1.2687 | 1.27 | 1.2713 | 1.2726 | 1.2739 | 1.2752 | 1.2764 | 1.2777
| MBN013-182964938 | MBN013 | 0.45244 | 0.45567 | 0.4589 | 0.46213 | 0.46537 | 0.46483 | 0.4643 | 0.46377 | 0.46324 | 0.4627 | 0.46217 | 0.46164 | 0.46111 | 0.46058 | 0.46004 | 0.45951 | 0.45898 | 0.45845 | 0.45791 | 0.45738
| MBN013-24605754 | MBN013 | 3.7178 | 3.7423 | 3.7668 | 3.7913 | 3.8158 | 3.8107 | 3.8056 | 3.8005 | 3.7954 | 3.7902 | 3.7851 | 3.78 | 3.7749 | 3.7698 | 3.7647 | 3.7596 | 3.7545 | 3.7494 | 3.7443 | 3.7392
| MBN014-15419313 | MBN014 | 2.0916 | 2.1058 | 2.1199 | 2.1341 | 2.1483 | 2.1497 | 2.1511 | 2.1525 | 2.154 | 2.1554 | 2.1568 | 2.1583 | 2.1597 | 2.1611 | 2.1625 | 2.164 | 2.1654 | 2.1668 | 2.1683 | 2.1697
| MBN014-160652409 | MBN014 | 0.0018281 | 0.001841 | 0.0018539 | 0.0018668 | 0.0018797 | 0.0018766 | 0.0018735 | 0.0018703 | 0.0018672 | 0.0018641 | 0.0018609 | 0.0018578 | 0.0018546 | 0.0018515 | 0.0018484 | 0.0018452 | 0.0018421 | 0.001839 | 0.0018358 | 0.0018327
| MBN014-24605768 | MBN014 | 0.3354 | 0.33777 | 0.34015 | 0.34253 | 0.3449 | 0.34448 | 0.34405 | 0.34362 | 0.34319 | 0.34276 | 0.34233 | 0.3419 | 0.34148 | 0.34105 | 0.34062 | 0.34019 | 0.33976 | 0.33933 | 0.3389 | 0.33848
| MBN023-94547225 | MBN023 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042
| MBN023-94547273 | MBN023 | 143.1799 | 144.1634 | 145.1469 | 146.1303 | 147.1138 | 147.0112 | 146.9087 | 146.8061 | 146.7035 | 146.6009 | 146.4984 | 146.3958 | 146.2932 | 146.1907 | 146.0881 | 145.9855 | 145.8829 | 145.7804 | 145.6778 | 145.5752
| MBN031-140147987 | MBN031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN031-140148011 | MBN031 | 0.60027 | 0.60461 | 0.60895 | 0.61328 | 0.61762 | 0.61694 | 0.61626 | 0.61558 | 0.61491 | 0.61423 | 0.61355 | 0.61287 | 0.6122 | 0.61152 | 0.61084 | 0.61016 | 0.60949 | 0.60881 | 0.60813 | 0.60745
| MBN031-162765180 | MBN031 | 1.37e-07 | 1.38e-07 | 1.39e-07 | 1.4e-07 | 1.41e-07 | 1.4105e-07 | 1.411e-07 | 1.4115e-07 | 1.412e-07 | 1.4125e-07 | 1.413e-07 | 1.4135e-07 | 1.414e-07 | 1.4145e-07 | 1.415e-07 | 1.4155e-07 | 1.416e-07 | 1.4165e-07 | 1.417e-07 | 1.4175e-07
| MBN031-24605740 | MBN031 | 0.30136 | 0.30338 | 0.3054 | 0.30742 | 0.30944 | 0.30913 | 0.30882 | 0.30851 | 0.3082 | 0.30789 | 0.30758 | 0.30727 | 0.30696 | 0.30665 | 0.30634 | 0.30603 | 0.30572 | 0.30541 | 0.3051 | 0.30479
| MBN031-52301620 | MBN031 | 0.35891 | 0.36093 | 0.36296 | 0.36498 | 0.36701 | 0.36618 | 0.36535 | 0.36453 | 0.3637 | 0.36287 | 0.36204 | 0.36122 | 0.36039 | 0.35956 | 0.35873 | 0.3579 | 0.35708 | 0.35625 | 0.35542 | 0.35459
| MBN032-140148075 | MBN032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBN032-140148099 | MBN032 | 5.0923 | 5.1281 | 5.1639 | 5.1998 | 5.2356 | 5.2417 | 5.2479 | 5.254 | 5.2602 | 5.2663 | 5.2724 | 5.2786 | 5.2847 | 5.2909 | 5.297 | 5.3032 | 5.3093 | 5.3154 | 5.3216 | 5.3277
| MDA022-15412339 | MDA022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA022-15412350 | MDA022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA022-24605196 | MDA022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA023-15412302 | MDA023 | 21.2679 | 21.3972 | 21.5264 | 21.6557 | 21.7849 | 21.7944 | 21.8038 | 21.8132 | 21.8226 | 21.832 | 21.8414 | 21.8508 | 21.8602 | 21.8696 | 21.8791 | 21.8885 | 21.8979 | 21.9073 | 21.9167 | 21.9261
| MDA023-24605266 | MDA023 | 2.4921 | 2.5084 | 2.5247 | 2.5411 | 2.5574 | 2.5587 | 2.5599 | 2.5612 | 2.5625 | 2.5638 | 2.5651 | 2.5663 | 2.5676 | 2.5689 | 2.5702 | 2.5715 | 2.5727 | 2.574 | 2.5753 | 2.5766
| MDA024-15412265 | MDA024 | 16.2463 | 16.3351 | 16.4238 | 16.5126 | 16.6013 | 16.6012 | 16.6011 | 16.601 | 16.6009 | 16.6008 | 16.6007 | 16.6006 | 16.6005 | 16.6004 | 16.6003 | 16.6002 | 16.6001 | 16.6 | 16.5999 | 16.5998
| MDA031-15412215 | MDA031 | 0.0087658 | 0.008827 | 0.0088883 | 0.0089495 | 0.0090108 | 0.0090079 | 0.0090051 | 0.0090022 | 0.0089994 | 0.0089965 | 0.0089937 | 0.0089908 | 0.008988 | 0.0089851 | 0.0089823 | 0.0089794 | 0.0089766 | 0.0089738 | 0.0089709 | 0.0089681
| MDA032-15412191 | MDA032 | 0.97221 | 0.97554 | 0.97886 | 0.98219 | 0.98552 | 0.98269 | 0.97987 | 0.97705 | 0.97423 | 0.97141 | 0.96859 | 0.96576 | 0.96294 | 0.96012 | 0.9573 | 0.95448 | 0.95166 | 0.94883 | 0.94601 | 0.94319
| MDA033-15412154 | MDA033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDA034-15433030 | MDA034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN011-196478975 | MLN011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN011-24613386 | MLN011 | 2.6492 | 2.6722 | 2.6952 | 2.7181 | 2.7411 | 2.7496 | 2.758 | 2.7665 | 2.775 | 2.7835 | 2.7919 | 2.8004 | 2.8089 | 2.8173 | 2.8258 | 2.8343 | 2.8427 | 2.8512 | 2.8597 | 2.8681
| MLN012-196479104 | MLN012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN012-24607519 | MLN012 | 1.8353 | 1.8513 | 1.8672 | 1.8831 | 1.8991 | 1.8983 | 1.8976 | 1.8969 | 1.8962 | 1.8955 | 1.8947 | 1.894 | 1.8933 | 1.8926 | 1.8919 | 1.8912 | 1.8904 | 1.8897 | 1.889 | 1.8883
| MLN012-76356455 | MLN012 | 0.084954 | 0.085574 | 0.086194 | 0.086814 | 0.087434 | 0.08792 | 0.088406 | 0.088891 | 0.089377 | 0.089863 | 0.090349 | 0.090834 | 0.09132 | 0.091806 | 0.092292 | 0.092777 | 0.093263 | 0.093749 | 0.094235 | 0.09472
| MLN012-84731779 | MLN012 | 6.637 | 6.693 | 6.7491 | 6.8051 | 6.8612 | 6.8796 | 6.898 | 6.9164 | 6.9348 | 6.9533 | 6.9717 | 6.9901 | 7.0085 | 7.0269 | 7.0454 | 7.0638 | 7.0822 | 7.1006 | 7.119 | 7.1374
| MLN013-196479162 | MLN013 | 81.1172 | 81.8503 | 82.5833 | 83.3164 | 84.0495 | 84.3238 | 84.598 | 84.8723 | 85.1465 | 85.4208 | 85.695 | 85.9693 | 86.2436 | 86.5178 | 86.7921 | 87.0663 | 87.3406 | 87.6148 | 87.8891 | 88.1634
| MLN014-196479219 | MLN014 | 35.3664 | 35.606 | 35.8457 | 36.0853 | 36.3249 | 36.504 | 36.683 | 36.862 | 37.0411 | 37.2201 | 37.3991 | 37.5782 | 37.7572 | 37.9362 | 38.1153 | 38.2943 | 38.4733 | 38.6524 | 38.8314 | 39.0104
| MLN021-196479276 | MLN021 | 39.6412 | 39.0339 | 38.4265 | 37.8192 | 37.2118 | 37.3722 | 37.5326 | 37.693 | 37.8534 | 38.0138 | 38.1742 | 38.3346 | 38.495 | 38.6554 | 38.8158 | 38.9762 | 39.1366 | 39.297 | 39.4574 | 39.6178
| MLN021-24600176 | MLN021 | 46.7863 | 47.1098 | 47.4332 | 47.7566 | 48.08 | 48.1754 | 48.2707 | 48.3661 | 48.4614 | 48.5568 | 48.6521 | 48.7474 | 48.8428 | 48.9381 | 49.0335 | 49.1288 | 49.2241 | 49.3195 | 49.4148 | 49.5102
| MLN022-160532221 | MLN022 | 92.3378 | 93.0814 | 93.8251 | 94.5687 | 95.3123 | 95.5441 | 95.7758 | 96.0076 | 96.2394 | 96.4712 | 96.7029 | 96.9347 | 97.1665 | 97.3983 | 97.63 | 97.8618 | 98.0936 | 98.3254 | 98.5572 | 98.7889
| MLN022-196479342 | MLN022 | 31.6552 | 31.864 | 32.0728 | 32.2815 | 32.4903 | 32.6458 | 32.8013 | 32.9567 | 33.1122 | 33.2677 | 33.4231 | 33.5786 | 33.7341 | 33.8895 | 34.045 | 34.2005 | 34.3559 | 34.5114 | 34.6668 | 34.8223
| MLN022-83935111 | MLN022 | 25.706 | 25.9277 | 26.1495 | 26.3712 | 26.5929 | 26.6625 | 26.7322 | 26.8018 | 26.8715 | 26.9411 | 27.0108 | 27.0804 | 27.1501 | 27.2198 | 27.2894 | 27.3591 | 27.4287 | 27.4984 | 27.568 | 27.6377
| MLN022-84622495 | MLN022 | 0.25778 | 0.25965 | 0.26151 | 0.26338 | 0.26524 | 0.2657 | 0.26617 | 0.26663 | 0.2671 | 0.26756 | 0.26803 | 0.26849 | 0.26895 | 0.26942 | 0.26988 | 0.27035 | 0.27081 | 0.27128 | 0.27174 | 0.2722
| MLN023-196479399 | MLN023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN024-196479455 | MLN024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLN032-196479760 | MLN032 | 40.087 | 40.3623 | 40.6375 | 40.9128 | 41.1881 | 41.397 | 41.6059 | 41.8147 | 42.0236 | 42.2324 | 42.4413 | 42.6502 | 42.859 | 43.0679 | 43.2768 | 43.4856 | 43.6945 | 43.9034 | 44.1122 | 44.3211
| MLN033-196479827 | MLN033 | 82.3312 | 82.9077 | 83.4841 | 84.0606 | 84.6371 | 84.8953 | 85.1534 | 85.4116 | 85.6698 | 85.928 | 86.1861 | 86.4443 | 86.7025 | 86.9606 | 87.2188 | 87.477 | 87.7352 | 87.9933 | 88.2515 | 88.5097
| MNA013-15432110 | MNA013 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06
| MNA013-15432136 | MNA013 | 2.3066 | 2.3189 | 2.3311 | 2.3434 | 2.3556 | 2.378 | 2.4003 | 2.4227 | 2.445 | 2.4674 | 2.4897 | 2.5121 | 2.5344 | 2.5568 | 2.5791 | 2.6015 | 2.6238 | 2.6462 | 2.6685 | 2.6909
| MNA014-138630585 | MNA014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MNA014-15420920 | MNA014 | 17.8755 | 17.9843 | 18.093 | 18.2018 | 18.3105 | 18.4496 | 18.5887 | 18.7278 | 18.8669 | 19.006 | 19.1451 | 19.2842 | 19.4232 | 19.5623 | 19.7014 | 19.8405 | 19.9796 | 20.1187 | 20.2578 | 20.3968
| MNA014-157238172 | MNA014 | 6.1903e-05 | 6.2177e-05 | 6.2451e-05 | 6.2726e-05 | 6.3e-05 | 6.396e-05 | 6.492e-05 | 6.588e-05 | 6.684e-05 | 6.78e-05 | 6.876e-05 | 6.972e-05 | 7.068e-05 | 7.164e-05 | 7.26e-05 | 7.356e-05 | 7.452e-05 | 7.548e-05 | 7.644e-05 | 7.74e-05
| MNA014-157238287 | MNA014 | 0.00026347 | 0.00026465 | 0.00026583 | 0.00026702 | 0.0002682 | 0.00027225 | 0.0002763 | 0.00028035 | 0.0002844 | 0.00028845 | 0.0002925 | 0.00029655 | 0.0003006 | 0.00030465 | 0.0003087 | 0.00031275 | 0.0003168 | 0.00032085 | 0.0003249 | 0.00032895
| MNA014-157238460 | MNA014 | 0.0046686 | 0.0046919 | 0.0047152 | 0.0047386 | 0.0047619 | 0.0048091 | 0.0048562 | 0.0049034 | 0.0049505 | 0.0049976 | 0.0050448 | 0.0050919 | 0.0051391 | 0.0051862 | 0.0052334 | 0.0052805 | 0.0053277 | 0.0053748 | 0.005422 | 0.0054691
| MNA014-163873875 | MNA014 | 0.00059657 | 0.00060103 | 0.00060549 | 0.00060994 | 0.0006144 | 0.00062184 | 0.00062928 | 0.00063672 | 0.00064416 | 0.0006516 | 0.00065904 | 0.00066648 | 0.00067392 | 0.00068136 | 0.0006888 | 0.00069624 | 0.00070368 | 0.00071112 | 0.00071856 | 0.000726
| MNA014-164469721 | MNA014 | 1.9863e-05 | 1.9953e-05 | 2.0042e-05 | 2.0131e-05 | 2.022e-05 | 2.0526e-05 | 2.0832e-05 | 2.1138e-05 | 2.1444e-05 | 2.175e-05 | 2.2056e-05 | 2.2362e-05 | 2.2668e-05 | 2.2974e-05 | 2.328e-05 | 2.3586e-05 | 2.3892e-05 | 2.4198e-05 | 2.4504e-05 | 2.481e-05
| MNA014-167870808 | MNA014 | 0.00015557 | 0.00015673 | 0.00015789 | 0.00015904 | 0.0001602 | 0.00016218 | 0.00016416 | 0.00016614 | 0.00016812 | 0.0001701 | 0.00017208 | 0.00017406 | 0.00017604 | 0.00017802 | 0.00018 | 0.00018198 | 0.00018396 | 0.00018594 | 0.00018792 | 0.0001899
| MNA014-184029858 | MNA014 | 8.4319 | 8.4722 | 8.5126 | 8.5529 | 8.5933 | 8.6674 | 8.7415 | 8.8157 | 8.8898 | 8.964 | 9.0381 | 9.1123 | 9.1864 | 9.2606 | 9.3347 | 9.4089 | 9.483 | 9.5572 | 9.6313 | 9.7055
| MNA014-187105725 | MNA014 | 0.003947 | 0.0039702 | 0.0039935 | 0.0040167 | 0.00404 | 0.0040859 | 0.0041319 | 0.0041778 | 0.0042238 | 0.0042697 | 0.0043157 | 0.0043616 | 0.0044076 | 0.0044535 | 0.0044995 | 0.0045454 | 0.0045914 | 0.0046373 | 0.0046832 | 0.0047292
| MNA014-203082790 | MNA014 | 0.62421 | 0.62787 | 0.63154 | 0.6352 | 0.63886 | 0.64452 | 0.65018 | 0.65583 | 0.66149 | 0.66715 | 0.6728 | 0.67846 | 0.68411 | 0.68977 | 0.69543 | 0.70108 | 0.70674 | 0.7124 | 0.71805 | 0.72371
| MNA021-15421016 | MNA021 | 30.6782 | 30.8556 | 31.0329 | 31.2103 | 31.3877 | 31.524 | 31.6604 | 31.7968 | 31.9332 | 32.0696 | 32.206 | 32.3424 | 32.4788 | 32.6152 | 32.7516 | 32.8879 | 33.0243 | 33.1607 | 33.2971 | 33.4335
| MNA021-164301884 | MNA021 | 25.1118 | 25.2452 | 25.3786 | 25.5119 | 25.6453 | 25.8505 | 26.0557 | 26.2609 | 26.4661 | 26.6713 | 26.8765 | 27.0817 | 27.2869 | 27.4921 | 27.6973 | 27.9025 | 28.1077 | 28.3129 | 28.5181 | 28.7233
| MNA022-15421040 | MNA022 | 0.97304 | 0.97828 | 0.98352 | 0.98876 | 0.994 | 1.0066 | 1.0192 | 1.0318 | 1.0444 | 1.057 | 1.0696 | 1.0822 | 1.0948 | 1.1074 | 1.12 | 1.1326 | 1.1452 | 1.1578 | 1.1704 | 1.183
| MNA024-15421140 | MNA024 | 51.7764 | 52.0283 | 52.2801 | 52.5319 | 52.7837 | 53.14 | 53.4962 | 53.8524 | 54.2087 | 54.5649 | 54.9212 | 55.2774 | 55.6337 | 55.9899 | 56.3461 | 56.7024 | 57.0586 | 57.4149 | 57.7711 | 58.1273
| MNA024-15421151 | MNA024 | 2.5076e-05 | 2.5212e-05 | 2.5348e-05 | 2.5484e-05 | 2.562e-05 | 2.5959e-05 | 2.6299e-05 | 2.6638e-05 | 2.6978e-05 | 2.7317e-05 | 2.7657e-05 | 2.7996e-05 | 2.8336e-05 | 2.8675e-05 | 2.9015e-05 | 2.9354e-05 | 2.9694e-05 | 3.0033e-05 | 3.0373e-05 | 3.0712e-05
| MNA034-15421279 | MNA034 | 37.0543 | 37.2243 | 37.3943 | 37.5644 | 37.7344 | 37.9741 | 38.2138 | 38.4535 | 38.6931 | 38.9328 | 39.1725 | 39.4122 | 39.6518 | 39.8915 | 40.1312 | 40.3709 | 40.6105 | 40.8502 | 41.0899 | 41.3296
| MNA034-157168509 | MNA034 | 0.12237 | 0.1232 | 0.12403 | 0.12487 | 0.1257 | 0.12672 | 0.12775 | 0.12878 | 0.1298 | 0.13083 | 0.13186 | 0.13288 | 0.13391 | 0.13494 | 0.13596 | 0.13699 | 0.13802 | 0.13904 | 0.14007 | 0.1411
| MNA034-157168656 | MNA034 | 0.14559 | 0.14664 | 0.14769 | 0.14875 | 0.1498 | 0.15088 | 0.15196 | 0.15305 | 0.15413 | 0.15521 | 0.15629 | 0.15737 | 0.15846 | 0.15954 | 0.16062 | 0.1617 | 0.16279 | 0.16387 | 0.16495 | 0.16603
| MNA034-157168875 | MNA034 | 0.012151 | 0.012238 | 0.012324 | 0.012411 | 0.012498 | 0.012558 | 0.012618 | 0.012678 | 0.012738 | 0.012799 | 0.012859 | 0.012919 | 0.012979 | 0.013039 | 0.013099 | 0.013159 | 0.013219 | 0.013279 | 0.013339 | 0.013399
| MNA034-175612351 | MNA034 | 9.1351e-05 | 9.1913e-05 | 9.2475e-05 | 9.3038e-05 | 9.36e-05 | 9.476e-05 | 9.592e-05 | 9.708e-05 | 9.824e-05 | 9.94e-05 | 0.00010056 | 0.00010172 | 0.00010288 | 0.00010404 | 0.0001052 | 0.00010636 | 0.00010752 | 0.00010868 | 0.00010984 | 0.000111
| MNA034-181657157 | MNA034 | 25.755 | 25.8934 | 26.0318 | 26.1703 | 26.3087 | 26.4047 | 26.5007 | 26.5966 | 26.6926 | 26.7886 | 26.8846 | 26.9806 | 27.0766 | 27.1726 | 27.2686 | 27.3645 | 27.4605 | 27.5565 | 27.6525 | 27.7485
| MNA034-24605112 | MNA034 | 35.4134 | 35.6322 | 35.851 | 36.0698 | 36.2887 | 36.4881 | 36.6876 | 36.8871 | 37.0865 | 37.286 | 37.4855 | 37.6849 | 37.8844 | 38.0838 | 38.2833 | 38.4828 | 38.6822 | 38.8817 | 39.0812 | 39.2806
| MRO002-15420142 | MRO002 | 0.00031106 | 0.00031137 | 0.00031168 | 0.00031199 | 0.0003123 | 0.00031203 | 0.00031176 | 0.00031148 | 0.00031121 | 0.00031093 | 0.00031066 | 0.00031039 | 0.00031011 | 0.00030984 | 0.00030956 | 0.00030929 | 0.00030902 | 0.00030874 | 0.00030847 | 0.00030819
| MRO002-15420153 | MRO002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO002-15420179 | MRO002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO004-15420205 | MRO004 | 69.4817 | 70.0373 | 70.5928 | 71.1483 | 71.7039 | 71.7394 | 71.775 | 71.8106 | 71.8462 | 71.8818 | 71.9174 | 71.953 | 71.9886 | 72.0242 | 72.0597 | 72.0953 | 72.1309 | 72.1665 | 72.2021 | 72.2377
| MRO005-144335638 | MRO005 | 0.16408 | 0.16568 | 0.16728 | 0.16887 | 0.17047 | 0.17017 | 0.16987 | 0.16957 | 0.16927 | 0.16897 | 0.16866 | 0.16836 | 0.16806 | 0.16776 | 0.16746 | 0.16716 | 0.16686 | 0.16656 | 0.16626 | 0.16596
| MRO005-144335959 | MRO005 | 0.0058938 | 0.0059616 | 0.0060293 | 0.0060971 | 0.0061649 | 0.0061784 | 0.006192 | 0.0062055 | 0.0062191 | 0.0062326 | 0.0062461 | 0.0062597 | 0.0062732 | 0.0062868 | 0.0063003 | 0.0063139 | 0.0063274 | 0.0063409 | 0.0063545 | 0.006368
| MRO005-144336040 | MRO005 | 0.047919 | 0.048243 | 0.048567 | 0.048891 | 0.049215 | 0.049336 | 0.049456 | 0.049577 | 0.049697 | 0.049818 | 0.049938 | 0.050059 | 0.050179 | 0.050299 | 0.05042 | 0.05054 | 0.050661 | 0.050781 | 0.050902 | 0.051022
| MRO005-144336270 | MRO005 | 0.011928 | 0.012024 | 0.01212 | 0.012216 | 0.012312 | 0.012316 | 0.01232 | 0.012324 | 0.012328 | 0.012332 | 0.012335 | 0.012339 | 0.012343 | 0.012347 | 0.012351 | 0.012355 | 0.012359 | 0.012363 | 0.012366 | 0.01237
| MRO005-15420092 | MRO005 | 72.0374 | 72.6041 | 73.1707 | 73.7373 | 74.3039 | 74.3473 | 74.3907 | 74.4342 | 74.4776 | 74.521 | 74.5644 | 74.6078 | 74.6512 | 74.6946 | 74.7381 | 74.7815 | 74.8249 | 74.8683 | 74.9117 | 74.9551
| MRO005-155391758 | MRO005 | 0.16409 | 0.16549 | 0.16688 | 0.16828 | 0.16968 | 0.17008 | 0.17047 | 0.17087 | 0.17126 | 0.17166 | 0.17206 | 0.17245 | 0.17285 | 0.17325 | 0.17364 | 0.17404 | 0.17444 | 0.17483 | 0.17523 | 0.17563
| MRO005-155391898 | MRO005 | 0.12837 | 0.12954 | 0.1307 | 0.13186 | 0.13302 | 0.13323 | 0.13343 | 0.13364 | 0.13385 | 0.13405 | 0.13426 | 0.13446 | 0.13467 | 0.13488 | 0.13508 | 0.13529 | 0.1355 | 0.1357 | 0.13591 | 0.13611
| MRO005-155391999 | MRO005 | 0.33731 | 0.34003 | 0.34275 | 0.34548 | 0.3482 | 0.34905 | 0.3499 | 0.35075 | 0.35161 | 0.35246 | 0.35331 | 0.35416 | 0.35501 | 0.35586 | 0.35672 | 0.35757 | 0.35842 | 0.35927 | 0.36012 | 0.36097
| MRO005-155423773 | MRO005 | 0.37866 | 0.38116 | 0.38367 | 0.38617 | 0.38867 | 0.38932 | 0.38997 | 0.39062 | 0.39128 | 0.39193 | 0.39258 | 0.39323 | 0.39388 | 0.39453 | 0.39518 | 0.39583 | 0.39648 | 0.39713 | 0.39778 | 0.39844
| MRO005-155505168 | MRO005 | 0.16994 | 0.17161 | 0.17327 | 0.17494 | 0.1766 | 0.17675 | 0.1769 | 0.17704 | 0.17719 | 0.17734 | 0.17748 | 0.17763 | 0.17778 | 0.17793 | 0.17807 | 0.17822 | 0.17837 | 0.17851 | 0.17866 | 0.17881
| MRO005-155838268 | MRO005 | 0.056527 | 0.057085 | 0.057644 | 0.058202 | 0.05876 | 0.058875 | 0.05899 | 0.059106 | 0.059221 | 0.059336 | 0.059451 | 0.059567 | 0.059682 | 0.059797 | 0.059912 | 0.060028 | 0.060143 | 0.060258 | 0.060373 | 0.060489
| MRO005-163160444 | MRO005 | 0.026665 | 0.026939 | 0.027213 | 0.027487 | 0.027761 | 0.027739 | 0.027717 | 0.027695 | 0.027673 | 0.027651 | 0.027629 | 0.027607 | 0.027585 | 0.027563 | 0.02754 | 0.027518 | 0.027496 | 0.027474 | 0.027452 | 0.02743
| MRO005-163160605 | MRO005 | 0.043621 | 0.044019 | 0.044417 | 0.044816 | 0.045214 | 0.045334 | 0.045454 | 0.045574 | 0.045694 | 0.045814 | 0.045934 | 0.046054 | 0.046174 | 0.046294 | 0.046414 | 0.046534 | 0.046654 | 0.046773 | 0.046893 | 0.047013
| MRO005-163160879 | MRO005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO005-163161051 | MRO005 | 0.017503 | 0.017674 | 0.017845 | 0.018016 | 0.018188 | 0.018246 | 0.018304 | 0.018362 | 0.01842 | 0.018478 | 0.018536 | 0.018594 | 0.018652 | 0.018711 | 0.018769 | 0.018827 | 0.018885 | 0.018943 | 0.019001 | 0.019059
| MRO005-172349913 | MRO005 | 0.033897 | 0.03418 | 0.034463 | 0.034746 | 0.035029 | 0.035193 | 0.035357 | 0.035522 | 0.035686 | 0.03585 | 0.036014 | 0.036178 | 0.036342 | 0.036506 | 0.03667 | 0.036835 | 0.036999 | 0.037163 | 0.037327 | 0.037491
| MRO005-24606286 | MRO005 | 10.4463 | 10.5185 | 10.5908 | 10.6631 | 10.7354 | 10.7517 | 10.768 | 10.7843 | 10.8006 | 10.8169 | 10.8332 | 10.8495 | 10.8659 | 10.8822 | 10.8985 | 10.9148 | 10.9311 | 10.9474 | 10.9637 | 10.98
| MRO005-24606314 | MRO005 | 17.481 | 17.6137 | 17.7464 | 17.8792 | 18.0119 | 18.0436 | 18.0753 | 18.1069 | 18.1386 | 18.1703 | 18.202 | 18.2336 | 18.2653 | 18.297 | 18.3287 | 18.3603 | 18.392 | 18.4237 | 18.4554 | 18.487
| MRO005-24606328 | MRO005 | 5.6964 | 5.7397 | 5.7831 | 5.8264 | 5.8698 | 5.8899 | 5.9101 | 5.9302 | 5.9503 | 5.9705 | 5.9906 | 6.0107 | 6.0309 | 6.051 | 6.0712 | 6.0913 | 6.1114 | 6.1316 | 6.1517 | 6.1718
| MRO005-24606858 | MRO005 | 14.0051 | 14.1234 | 14.2417 | 14.3599 | 14.4782 | 14.4989 | 14.5196 | 14.5403 | 14.561 | 14.5817 | 14.6023 | 14.623 | 14.6437 | 14.6644 | 14.6851 | 14.7058 | 14.7265 | 14.7472 | 14.7678 | 14.7885
| MRO005-73766637 | MRO005 | 0.34412 | 0.34688 | 0.34964 | 0.35241 | 0.35517 | 0.35599 | 0.3568 | 0.35762 | 0.35843 | 0.35925 | 0.36006 | 0.36088 | 0.36169 | 0.36251 | 0.36332 | 0.36414 | 0.36495 | 0.36577 | 0.36658 | 0.3674
| MRO006-15420268 | MRO006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MRO007-122640081 | MRO007 | 18.4105 | 18.5307 | 18.6509 | 18.7711 | 18.8913 | 18.9431 | 18.9949 | 19.0467 | 19.0984 | 19.1502 | 19.202 | 19.2538 | 19.3056 | 19.3574 | 19.4092 | 19.461 | 19.5128 | 19.5645 | 19.6163 | 19.6681
| MRO007-129258735 | MRO007 | 0.31673 | 0.31935 | 0.32197 | 0.32459 | 0.32721 | 0.32858 | 0.32994 | 0.33131 | 0.33268 | 0.33404 | 0.33541 | 0.33678 | 0.33814 | 0.33951 | 0.34088 | 0.34224 | 0.34361 | 0.34498 | 0.34634 | 0.34771
| MRO007-15420070 | MRO007 | 35.9995 | 36.2758 | 36.5521 | 36.8284 | 37.1047 | 37.0865 | 37.0683 | 37.0501 | 37.0319 | 37.0137 | 36.9955 | 36.9773 | 36.9592 | 36.941 | 36.9228 | 36.9046 | 36.8864 | 36.8682 | 36.85 | 36.8318
| MRO007-161151299 | MRO007 | 0.12276 | 0.12388 | 0.12501 | 0.12613 | 0.12726 | 0.12727 | 0.12729 | 0.12731 | 0.12733 | 0.12734 | 0.12736 | 0.12738 | 0.12739 | 0.12741 | 0.12743 | 0.12744 | 0.12746 | 0.12748 | 0.12749 | 0.12751
| MRO007-24610986 | MRO007 | 13.9572 | 14.092 | 14.2268 | 14.3616 | 14.4964 | 14.4883 | 14.4802 | 14.4722 | 14.4641 | 14.456 | 14.4479 | 14.4398 | 14.4317 | 14.4237 | 14.4156 | 14.4075 | 14.3994 | 14.3913 | 14.3833 | 14.3752
| MRO007-76446321 | MRO007 | 0.46437 | 0.46837 | 0.47237 | 0.47638 | 0.48038 | 0.48062 | 0.48087 | 0.48111 | 0.48136 | 0.4816 | 0.48185 | 0.48209 | 0.48233 | 0.48258 | 0.48282 | 0.48307 | 0.48331 | 0.48356 | 0.4838 | 0.48405
| MRO007-76446588 | MRO007 | 0.15827 | 0.15981 | 0.16135 | 0.16289 | 0.16443 | 0.16445 | 0.16448 | 0.16451 | 0.16453 | 0.16456 | 0.16458 | 0.16461 | 0.16464 | 0.16466 | 0.16469 | 0.16472 | 0.16474 | 0.16477 | 0.1648 | 0.16482
| MRO007-76547638 | MRO007 | 0.20937 | 0.21065 | 0.21193 | 0.21321 | 0.21449 | 0.21504 | 0.2156 | 0.21615 | 0.2167 | 0.21725 | 0.2178 | 0.21835 | 0.21891 | 0.21946 | 0.22001 | 0.22056 | 0.22111 | 0.22167 | 0.22222 | 0.22277
| MRO007-76547903 | MRO007 | 0.0012963 | 0.0013108 | 0.0013252 | 0.0013397 | 0.0013542 | 0.0013555 | 0.0013568 | 0.0013581 | 0.0013594 | 0.0013607 | 0.001362 | 0.0013633 | 0.0013646 | 0.0013659 | 0.0013672 | 0.0013684 | 0.0013697 | 0.001371 | 0.0013723 | 0.0013736
| MRO007-76548012 | MRO007 | 0.20285 | 0.20471 | 0.20657 | 0.20843 | 0.21028 | 0.21038 | 0.21047 | 0.21057 | 0.21066 | 0.21076 | 0.21086 | 0.21095 | 0.21105 | 0.21114 | 0.21124 | 0.21133 | 0.21143 | 0.21152 | 0.21162 | 0.21171
| MRO008-129258570 | MRO008 | 0.12701 | 0.12812 | 0.12922 | 0.13033 | 0.13143 | 0.1315 | 0.13157 | 0.13165 | 0.13172 | 0.13179 | 0.13186 | 0.13193 | 0.132 | 0.13207 | 0.13214 | 0.13221 | 0.13228 | 0.13235 | 0.13242 | 0.13249
| MRO008-137134221 | MRO008 | 0.022179 | 0.022353 | 0.022527 | 0.022701 | 0.022874 | 0.022872 | 0.02287 | 0.022867 | 0.022865 | 0.022863 | 0.02286 | 0.022858 | 0.022855 | 0.022853 | 0.022851 | 0.022848 | 0.022846 | 0.022843 | 0.022841 | 0.022839
| MRO008-15411648 | MRO008 | 93.9911 | 94.5572 | 95.1232 | 95.6893 | 96.2553 | 96.2655 | 96.2756 | 96.2857 | 96.2958 | 96.306 | 96.3161 | 96.3262 | 96.3364 | 96.3465 | 96.3566 | 96.3667 | 96.3769 | 96.387 | 96.3971 | 96.4073
| MRO008-156506029 | MRO008 | 53.4673 | 53.8964 | 54.3255 | 54.7547 | 55.1838 | 55.1509 | 55.118 | 55.0852 | 55.0523 | 55.0194 | 54.9865 | 54.9536 | 54.9208 | 54.8879 | 54.855 | 54.8221 | 54.7892 | 54.7563 | 54.7235 | 54.6906
| MRO008-161918307 | MRO008 | 0.13682 | 0.13807 | 0.13932 | 0.14058 | 0.14183 | 0.14186 | 0.1419 | 0.14193 | 0.14196 | 0.14199 | 0.14202 | 0.14205 | 0.14208 | 0.14211 | 0.14214 | 0.14217 | 0.14221 | 0.14224 | 0.14227 | 0.1423
| MRO008-24606830 | MRO008 | 3.4696 | 3.5006 | 3.5316 | 3.5626 | 3.5936 | 3.5913 | 3.5889 | 3.5865 | 3.5842 | 3.5818 | 3.5795 | 3.5771 | 3.5748 | 3.5724 | 3.5701 | 3.5677 | 3.5654 | 3.563 | 3.5607 | 3.5583
| MRO008-24606844 | MRO008 | 1.355 | 1.368 | 1.3809 | 1.3939 | 1.4068 | 1.4094 | 1.412 | 1.4146 | 1.4171 | 1.4197 | 1.4223 | 1.4249 | 1.4275 | 1.43 | 1.4326 | 1.4352 | 1.4378 | 1.4403 | 1.4429 | 1.4455
| MRO008-77241441 | MRO008 | 3.124e-05 | 3.158e-05 | 3.192e-05 | 3.226e-05 | 3.26e-05 | 3.253e-05 | 3.246e-05 | 3.239e-05 | 3.232e-05 | 3.225e-05 | 3.218e-05 | 3.211e-05 | 3.204e-05 | 3.197e-05 | 3.19e-05 | 3.183e-05 | 3.176e-05 | 3.169e-05 | 3.162e-05 | 3.155e-05
| MRO008-77241511 | MRO008 | 0.26709 | 0.26928 | 0.27147 | 0.27366 | 0.27584 | 0.27546 | 0.27508 | 0.27469 | 0.27431 | 0.27392 | 0.27354 | 0.27315 | 0.27277 | 0.27238 | 0.272 | 0.27162 | 0.27123 | 0.27085 | 0.27046 | 0.27008
| NHL015-115332434 | NHL015 | 22.2739 | 22.4491 | 22.6243 | 22.7995 | 22.9747 | 22.9249 | 22.8751 | 22.8253 | 22.7755 | 22.7257 | 22.6759 | 22.6261 | 22.5763 | 22.5265 | 22.4766 | 22.4268 | 22.377 | 22.3272 | 22.2774 | 22.2276
| NHL015-154154899 | NHL015 | 0.95657 | 0.96546 | 0.97436 | 0.98326 | 0.99216 | 0.98749 | 0.98283 | 0.97816 | 0.9735 | 0.96883 | 0.96417 | 0.9595 | 0.95483 | 0.95017 | 0.9455 | 0.94084 | 0.93617 | 0.93151 | 0.92684 | 0.92218
| NHL015-15417078 | NHL015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-15417104 | NHL015 | 4.7196 | 4.7597 | 4.7999 | 4.8401 | 4.8803 | 4.8609 | 4.8416 | 4.8222 | 4.8028 | 4.7834 | 4.764 | 4.7447 | 4.7253 | 4.7059 | 4.6865 | 4.6671 | 4.6478 | 4.6284 | 4.609 | 4.5896
| NHL015-157413262 | NHL015 | 0.090797 | 0.091794 | 0.092791 | 0.093788 | 0.094785 | 0.094443 | 0.094102 | 0.093761 | 0.093419 | 0.093078 | 0.092736 | 0.092395 | 0.092054 | 0.091712 | 0.091371 | 0.091029 | 0.090688 | 0.090347 | 0.090005 | 0.089664
| NHL015-157443574 | NHL015 | 0.017682 | 0.017868 | 0.018054 | 0.018239 | 0.018425 | 0.018362 | 0.018299 | 0.018236 | 0.018172 | 0.018109 | 0.018046 | 0.017983 | 0.01792 | 0.017856 | 0.017793 | 0.01773 | 0.017667 | 0.017604 | 0.017541 | 0.017477
| NHL015-157455075 | NHL015 | 0.08564 | 0.086409 | 0.087177 | 0.087946 | 0.088714 | 0.08854 | 0.088367 | 0.088193 | 0.088019 | 0.087846 | 0.087672 | 0.087498 | 0.087324 | 0.087151 | 0.086977 | 0.086803 | 0.08663 | 0.086456 | 0.086282 | 0.086108
| NHL015-157999738 | NHL015 | 0.26574 | 0.26828 | 0.27081 | 0.27335 | 0.27589 | 0.27474 | 0.27359 | 0.27243 | 0.27128 | 0.27013 | 0.26898 | 0.26783 | 0.26668 | 0.26553 | 0.26438 | 0.26323 | 0.26207 | 0.26092 | 0.25977 | 0.25862
| NHL015-157999871 | NHL015 | 0.066259 | 0.066949 | 0.067639 | 0.06833 | 0.06902 | 0.068718 | 0.068416 | 0.068114 | 0.067813 | 0.067511 | 0.067209 | 0.066907 | 0.066605 | 0.066303 | 0.066002 | 0.0657 | 0.065398 | 0.065096 | 0.064794 | 0.064492
| NHL015-158004096 | NHL015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-158004251 | NHL015 | 0.040403 | 0.040781 | 0.041159 | 0.041537 | 0.041915 | 0.041767 | 0.041619 | 0.041471 | 0.041324 | 0.041176 | 0.041028 | 0.04088 | 0.040732 | 0.040585 | 0.040437 | 0.040289 | 0.040141 | 0.039993 | 0.039845 | 0.039698
| NHL015-158004482 | NHL015 | 0.038235 | 0.038525 | 0.038815 | 0.039105 | 0.039396 | 0.039287 | 0.039179 | 0.03907 | 0.038962 | 0.038854 | 0.038745 | 0.038637 | 0.038529 | 0.03842 | 0.038312 | 0.038204 | 0.038095 | 0.037987 | 0.037879 | 0.03777
| NHL015-158005276 | NHL015 | 0.030814 | 0.03112 | 0.031426 | 0.031733 | 0.032039 | 0.031933 | 0.031826 | 0.03172 | 0.031613 | 0.031507 | 0.0314 | 0.031294 | 0.031187 | 0.031081 | 0.030975 | 0.030868 | 0.030762 | 0.030655 | 0.030549 | 0.030442
| NHL015-158007892 | NHL015 | 0.035949 | 0.036256 | 0.036562 | 0.036868 | 0.037174 | 0.037082 | 0.03699 | 0.036898 | 0.036806 | 0.036714 | 0.036621 | 0.036529 | 0.036437 | 0.036345 | 0.036253 | 0.036161 | 0.036068 | 0.035976 | 0.035884 | 0.035792
| NHL015-158008058 | NHL015 | 0.35255 | 0.35534 | 0.35812 | 0.3609 | 0.36368 | 0.3629 | 0.36212 | 0.36134 | 0.36056 | 0.35978 | 0.359 | 0.35823 | 0.35745 | 0.35667 | 0.35589 | 0.35511 | 0.35433 | 0.35355 | 0.35277 | 0.35199
| NHL015-158050824 | NHL015 | 0.11419 | 0.11515 | 0.11612 | 0.11708 | 0.11804 | 0.11789 | 0.11774 | 0.11759 | 0.11744 | 0.1173 | 0.11715 | 0.117 | 0.11685 | 0.1167 | 0.11655 | 0.1164 | 0.11625 | 0.1161 | 0.11596 | 0.11581
| NHL015-158051013 | NHL015 | 0.00056168 | 0.00056756 | 0.00057344 | 0.00057932 | 0.0005852 | 0.0005838 | 0.0005824 | 0.000581 | 0.0005796 | 0.0005782 | 0.0005768 | 0.0005754 | 0.000574 | 0.0005726 | 0.0005712 | 0.0005698 | 0.0005684 | 0.000567 | 0.0005656 | 0.0005642
| NHL015-158071333 | NHL015 | 0.14499 | 0.14625 | 0.14751 | 0.14878 | 0.15004 | 0.14965 | 0.14926 | 0.14888 | 0.14849 | 0.1481 | 0.14772 | 0.14733 | 0.14694 | 0.14655 | 0.14617 | 0.14578 | 0.14539 | 0.14501 | 0.14462 | 0.14423
| NHL015-158071498 | NHL015 | 0.030586 | 0.03068 | 0.030774 | 0.030868 | 0.030962 | 0.030855 | 0.030749 | 0.030642 | 0.030535 | 0.030428 | 0.030321 | 0.030215 | 0.030108 | 0.030001 | 0.029894 | 0.029787 | 0.029681 | 0.029574 | 0.029467 | 0.02936
| NHL015-158071668 | NHL015 | 0.044599 | 0.045022 | 0.045444 | 0.045867 | 0.046289 | 0.046206 | 0.046122 | 0.046039 | 0.045956 | 0.045873 | 0.045789 | 0.045706 | 0.045623 | 0.045539 | 0.045456 | 0.045373 | 0.045289 | 0.045206 | 0.045123 | 0.045039
| NHL015-158092505 | NHL015 | 0.022575 | 0.022788 | 0.023002 | 0.023215 | 0.023429 | 0.023369 | 0.023309 | 0.02325 | 0.02319 | 0.023131 | 0.023071 | 0.023011 | 0.022952 | 0.022892 | 0.022832 | 0.022773 | 0.022713 | 0.022653 | 0.022594 | 0.022534
| NHL015-158092654 | NHL015 | 0.15155 | 0.15304 | 0.15454 | 0.15603 | 0.15753 | 0.15691 | 0.15629 | 0.15567 | 0.15505 | 0.15443 | 0.15381 | 0.15319 | 0.15257 | 0.15195 | 0.15132 | 0.1507 | 0.15008 | 0.14946 | 0.14884 | 0.14822
| NHL015-158130266 | NHL015 | 0.01385 | 0.013978 | 0.014105 | 0.014233 | 0.01436 | 0.014313 | 0.014266 | 0.014218 | 0.014171 | 0.014123 | 0.014076 | 0.014028 | 0.013981 | 0.013934 | 0.013886 | 0.013839 | 0.013791 | 0.013744 | 0.013696 | 0.013649
| NHL015-158130348 | NHL015 | 0.015015 | 0.015136 | 0.015258 | 0.015379 | 0.015501 | 0.015454 | 0.015408 | 0.015362 | 0.015316 | 0.01527 | 0.015224 | 0.015178 | 0.015132 | 0.015086 | 0.01504 | 0.014994 | 0.014948 | 0.014902 | 0.014856 | 0.01481
| NHL015-158145995 | NHL015 | 0.28969 | 0.29231 | 0.29492 | 0.29754 | 0.30016 | 0.29895 | 0.29775 | 0.29654 | 0.29534 | 0.29413 | 0.29292 | 0.29172 | 0.29051 | 0.28931 | 0.2881 | 0.2869 | 0.28569 | 0.28448 | 0.28328 | 0.28207
| NHL015-158146107 | NHL015 | 0.1887 | 0.19055 | 0.19239 | 0.19423 | 0.19608 | 0.1955 | 0.19493 | 0.19436 | 0.19379 | 0.19321 | 0.19264 | 0.19207 | 0.19149 | 0.19092 | 0.19035 | 0.18978 | 0.1892 | 0.18863 | 0.18806 | 0.18748
| NHL015-158377999 | NHL015 | 0.078943 | 0.079691 | 0.08044 | 0.081188 | 0.081936 | 0.081779 | 0.081623 | 0.081467 | 0.08131 | 0.081154 | 0.080998 | 0.080841 | 0.080685 | 0.080529 | 0.080372 | 0.080216 | 0.08006 | 0.079903 | 0.079747 | 0.079591
| NHL015-164675628 | NHL015 | 0.027137 | 0.027374 | 0.027611 | 0.027848 | 0.028085 | 0.028018 | 0.027951 | 0.027884 | 0.027817 | 0.027751 | 0.027684 | 0.027617 | 0.02755 | 0.027483 | 0.027417 | 0.02735 | 0.027283 | 0.027216 | 0.027149 | 0.027083
| NHL015-24600722 | NHL015 | 26.289 | 26.4891 | 26.6893 | 26.8894 | 27.0895 | 26.9846 | 26.8798 | 26.7749 | 26.6701 | 26.5652 | 26.4604 | 26.3555 | 26.2507 | 26.1458 | 26.041 | 25.9361 | 25.8313 | 25.7264 | 25.6216 | 25.5167
| NHL015-24600904 | NHL015 | 6.7627 | 6.8253 | 6.8878 | 6.9504 | 7.013 | 6.9837 | 6.9544 | 6.9252 | 6.8959 | 6.8666 | 6.8373 | 6.8081 | 6.7788 | 6.7495 | 6.7202 | 6.691 | 6.6617 | 6.6324 | 6.6032 | 6.5739
| NHL016-15417067 | NHL016 | 15.9967 | 16.1199 | 16.2431 | 16.3664 | 16.4896 | 16.4415 | 16.3935 | 16.3454 | 16.2974 | 16.2493 | 16.2013 | 16.1532 | 16.1052 | 16.0571 | 16.0091 | 15.961 | 15.913 | 15.8649 | 15.8169 | 15.7688
| NHL016-157284541 | NHL016 | 0.063415 | 0.064001 | 0.064587 | 0.065172 | 0.065758 | 0.065563 | 0.065367 | 0.065171 | 0.064976 | 0.06478 | 0.064585 | 0.064389 | 0.064193 | 0.063998 | 0.063802 | 0.063606 | 0.063411 | 0.063215 | 0.06302 | 0.062824
| NHL016-157284640 | NHL016 | 0.049511 | 0.049958 | 0.050405 | 0.050853 | 0.0513 | 0.051157 | 0.051015 | 0.050872 | 0.05073 | 0.050587 | 0.050445 | 0.050303 | 0.05016 | 0.050018 | 0.049875 | 0.049733 | 0.04959 | 0.049448 | 0.049305 | 0.049163
| NHL016-157284729 | NHL016 | 0.020893 | 0.02109 | 0.021288 | 0.021486 | 0.021683 | 0.02159 | 0.021496 | 0.021403 | 0.021309 | 0.021215 | 0.021122 | 0.021028 | 0.020935 | 0.020841 | 0.020748 | 0.020654 | 0.020561 | 0.020467 | 0.020373 | 0.02028
| NHL016-157284831 | NHL016 | 0.083328 | 0.084191 | 0.085053 | 0.085916 | 0.086779 | 0.086456 | 0.086133 | 0.08581 | 0.085487 | 0.085165 | 0.084842 | 0.084519 | 0.084196 | 0.083874 | 0.083551 | 0.083228 | 0.082905 | 0.082582 | 0.08226 | 0.081937
| NHL016-157328241 | NHL016 | 0.030281 | 0.030596 | 0.03091 | 0.031225 | 0.03154 | 0.031362 | 0.031185 | 0.031007 | 0.030829 | 0.030651 | 0.030474 | 0.030296 | 0.030118 | 0.02994 | 0.029763 | 0.029585 | 0.029407 | 0.029229 | 0.029052 | 0.028874
| NHL016-157328461 | NHL016 | 0.080587 | 0.081408 | 0.082228 | 0.083048 | 0.083869 | 0.083598 | 0.083328 | 0.083057 | 0.082787 | 0.082517 | 0.082246 | 0.081976 | 0.081705 | 0.081435 | 0.081164 | 0.080894 | 0.080623 | 0.080353 | 0.080082 | 0.079812
| NHL016-157328563 | NHL016 | 0.025074 | 0.025328 | 0.025581 | 0.025835 | 0.026089 | 0.025973 | 0.025856 | 0.02574 | 0.025624 | 0.025508 | 0.025391 | 0.025275 | 0.025159 | 0.025043 | 0.024926 | 0.02481 | 0.024694 | 0.024577 | 0.024461 | 0.024345
| NHL016-162991101 | NHL016 | 0.022069 | 0.022297 | 0.022526 | 0.022754 | 0.022982 | 0.022865 | 0.022747 | 0.02263 | 0.022512 | 0.022395 | 0.022277 | 0.02216 | 0.022042 | 0.021925 | 0.021808 | 0.02169 | 0.021573 | 0.021455 | 0.021338 | 0.02122
| NHL016-163161231 | NHL016 | 0.097223 | 0.098248 | 0.099272 | 0.1003 | 0.10132 | 0.10117 | 0.10103 | 0.10088 | 0.10073 | 0.10058 | 0.10044 | 0.10029 | 0.10014 | 0.099995 | 0.099847 | 0.0997 | 0.099553 | 0.099406 | 0.099258 | 0.099111
| NHL016-163161483 | NHL016 | 0.00033322 | 0.00033654 | 0.00033986 | 0.00034318 | 0.0003465 | 0.00034566 | 0.00034482 | 0.00034398 | 0.00034314 | 0.0003423 | 0.00034146 | 0.00034062 | 0.00033978 | 0.00033894 | 0.0003381 | 0.00033726 | 0.00033642 | 0.00033558 | 0.00033474 | 0.0003339
| NHL016-24601854 | NHL016 | 3.1142 | 3.1433 | 3.1725 | 3.2016 | 3.2307 | 3.2193 | 3.2079 | 3.1965 | 3.185 | 3.1736 | 3.1622 | 3.1507 | 3.1393 | 3.1279 | 3.1165 | 3.105 | 3.0936 | 3.0822 | 3.0708 | 3.0593
| NHL031-111738437 | NHL031 | 4.4608 | 4.4945 | 4.5281 | 4.5618 | 4.5954 | 4.5671 | 4.5388 | 4.5105 | 4.4821 | 4.4538 | 4.4255 | 4.3972 | 4.3688 | 4.3405 | 4.3122 | 4.2839 | 4.2555 | 4.2272 | 4.1989 | 4.1706
| NHL031-15417259 | NHL031 | 13.3092 | 13.4217 | 13.5343 | 13.6468 | 13.7594 | 13.7057 | 13.652 | 13.5982 | 13.5445 | 13.4908 | 13.4371 | 13.3834 | 13.3297 | 13.276 | 13.2222 | 13.1685 | 13.1148 | 13.0611 | 13.0074 | 12.9537
| NHL031-158072303 | NHL031 | 0.068217 | 0.068732 | 0.069247 | 0.069761 | 0.070276 | 0.070019 | 0.069761 | 0.069504 | 0.069246 | 0.068989 | 0.068731 | 0.068474 | 0.068216 | 0.067959 | 0.067701 | 0.067443 | 0.067186 | 0.066928 | 0.066671 | 0.066413
| NHL031-158072703 | NHL031 | 0.082801 | 0.083483 | 0.084165 | 0.084847 | 0.085529 | 0.084974 | 0.08442 | 0.083865 | 0.083311 | 0.082756 | 0.082202 | 0.081647 | 0.081092 | 0.080538 | 0.079983 | 0.079429 | 0.078874 | 0.078319 | 0.077765 | 0.07721
| NHL031-158073136 | NHL031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158078362 | NHL031 | 0.088575 | 0.089344 | 0.090112 | 0.090881 | 0.09165 | 0.091066 | 0.090482 | 0.089898 | 0.089315 | 0.088731 | 0.088147 | 0.087563 | 0.086979 | 0.086395 | 0.085811 | 0.085227 | 0.084644 | 0.08406 | 0.083476 | 0.082892
| NHL031-158078443 | NHL031 | 0.0083404 | 0.0084204 | 0.0085005 | 0.0085806 | 0.0086607 | 0.0086135 | 0.0085663 | 0.0085191 | 0.008472 | 0.0084248 | 0.0083776 | 0.0083304 | 0.0082832 | 0.008236 | 0.0081889 | 0.0081417 | 0.0080945 | 0.0080473 | 0.0080001 | 0.0079529
| NHL031-158078533 | NHL031 | 0.057494 | 0.058035 | 0.058575 | 0.059115 | 0.059656 | 0.059338 | 0.059019 | 0.058701 | 0.058383 | 0.058064 | 0.057746 | 0.057428 | 0.05711 | 0.056791 | 0.056473 | 0.056155 | 0.055837 | 0.055518 | 0.0552 | 0.054882
| NHL031-158078653 | NHL031 | 0.0014732 | 0.0014865 | 0.0014998 | 0.0015131 | 0.0015264 | 0.0015179 | 0.0015094 | 0.0015008 | 0.0014923 | 0.0014838 | 0.0014753 | 0.0014668 | 0.0014582 | 0.0014497 | 0.0014412 | 0.0014327 | 0.0014242 | 0.0014156 | 0.0014071 | 0.0013986
| NHL031-158092744 | NHL031 | 0.023626 | 0.02385 | 0.024074 | 0.024299 | 0.024523 | 0.024433 | 0.024343 | 0.024253 | 0.024163 | 0.024073 | 0.023983 | 0.023893 | 0.023803 | 0.023713 | 0.023623 | 0.023533 | 0.023443 | 0.023353 | 0.023263 | 0.023173
| NHL031-158092870 | NHL031 | 0.019487 | 0.019654 | 0.019821 | 0.019988 | 0.020155 | 0.020028 | 0.019902 | 0.019775 | 0.019648 | 0.019521 | 0.019395 | 0.019268 | 0.019141 | 0.019015 | 0.018888 | 0.018761 | 0.018635 | 0.018508 | 0.018381 | 0.018254
| NHL031-158093033 | NHL031 | 0.46747 | 0.47172 | 0.47597 | 0.48022 | 0.48446 | 0.48249 | 0.48051 | 0.47853 | 0.47655 | 0.47457 | 0.47259 | 0.47062 | 0.46864 | 0.46666 | 0.46468 | 0.4627 | 0.46072 | 0.45875 | 0.45677 | 0.45479
| NHL031-158103926 | NHL031 | 0.078452 | 0.079131 | 0.079811 | 0.080491 | 0.081171 | 0.080865 | 0.080559 | 0.080253 | 0.079947 | 0.079641 | 0.079335 | 0.079029 | 0.078723 | 0.078417 | 0.078111 | 0.077805 | 0.077499 | 0.077193 | 0.076888 | 0.076582
| NHL031-158104228 | NHL031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-158104320 | NHL031 | 0.00061975 | 0.00062601 | 0.00063227 | 0.00063854 | 0.0006448 | 0.00064032 | 0.00063584 | 0.00063136 | 0.00062688 | 0.0006224 | 0.00061792 | 0.00061344 | 0.00060896 | 0.00060448 | 0.0006 | 0.00059552 | 0.00059104 | 0.00058656 | 0.00058208 | 0.0005776
| NHL031-158104465 | NHL031 | 0.033559 | 0.033889 | 0.034219 | 0.034549 | 0.034879 | 0.034745 | 0.034611 | 0.034477 | 0.034343 | 0.034209 | 0.034075 | 0.03394 | 0.033806 | 0.033672 | 0.033538 | 0.033404 | 0.03327 | 0.033136 | 0.033001 | 0.032867
| NHL031-158118521 | NHL031 | 0.04034 | 0.040707 | 0.041075 | 0.041443 | 0.04181 | 0.041681 | 0.041552 | 0.041423 | 0.041294 | 0.041165 | 0.041036 | 0.040907 | 0.040777 | 0.040648 | 0.040519 | 0.04039 | 0.040261 | 0.040132 | 0.040003 | 0.039874
| NHL031-158118640 | NHL031 | 0.025968 | 0.026174 | 0.026381 | 0.026587 | 0.026793 | 0.02662 | 0.026448 | 0.026275 | 0.026102 | 0.025929 | 0.025756 | 0.025584 | 0.025411 | 0.025238 | 0.025065 | 0.024892 | 0.02472 | 0.024547 | 0.024374 | 0.024201
| NHL031-159317140 | NHL031 | 0.1982 | 0.20012 | 0.20203 | 0.20395 | 0.20586 | 0.20508 | 0.2043 | 0.20352 | 0.20274 | 0.20196 | 0.20118 | 0.2004 | 0.19962 | 0.19884 | 0.19806 | 0.19727 | 0.19649 | 0.19571 | 0.19493 | 0.19415
| NHL031-159317397 | NHL031 | 0.022088 | 0.022315 | 0.022543 | 0.02277 | 0.022997 | 0.022859 | 0.02272 | 0.022582 | 0.022443 | 0.022305 | 0.022166 | 0.022028 | 0.02189 | 0.021751 | 0.021613 | 0.021474 | 0.021336 | 0.021197 | 0.021059 | 0.02092
| NHL031-159338407 | NHL031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-159449178 | NHL031 | 0.070116 | 0.070658 | 0.071199 | 0.07174 | 0.072282 | 0.071985 | 0.071688 | 0.071391 | 0.071094 | 0.070798 | 0.070501 | 0.070204 | 0.069907 | 0.06961 | 0.069313 | 0.069017 | 0.06872 | 0.068423 | 0.068126 | 0.067829
| NHL031-163378374 | NHL031 | 0.017963 | 0.018128 | 0.018294 | 0.018459 | 0.018624 | 0.01851 | 0.018396 | 0.018281 | 0.018167 | 0.018052 | 0.017938 | 0.017824 | 0.017709 | 0.017595 | 0.017481 | 0.017366 | 0.017252 | 0.017137 | 0.017023 | 0.016909
| NHL031-171331453 | NHL031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NHL031-187102650 | NHL031 | 2.7649 | 2.7874 | 2.8099 | 2.8323 | 2.8548 | 2.8377 | 2.8207 | 2.8036 | 2.7865 | 2.7694 | 2.7524 | 2.7353 | 2.7182 | 2.7012 | 2.6841 | 2.667 | 2.6499 | 2.6329 | 2.6158 | 2.5987
| NHL031-202230824 | NHL031 | 10.1395 | 10.23 | 10.3206 | 10.4111 | 10.5017 | 10.4248 | 10.348 | 10.2711 | 10.1942 | 10.1173 | 10.0405 | 9.9636 | 9.8867 | 9.8099 | 9.733 | 9.6561 | 9.5792 | 9.5024 | 9.4255 | 9.3486
| NHL031-44808373 | NHL031 | 0.53284 | 0.53738 | 0.54191 | 0.54645 | 0.55098 | 0.54712 | 0.54325 | 0.53938 | 0.53551 | 0.53164 | 0.52778 | 0.52391 | 0.52004 | 0.51617 | 0.51231 | 0.50844 | 0.50457 | 0.5007 | 0.49683 | 0.49297
| NHL031-47809173 | NHL031 | 0.201 | 0.20281 | 0.20462 | 0.20643 | 0.20824 | 0.20697 | 0.2057 | 0.20442 | 0.20315 | 0.20188 | 0.20061 | 0.19933 | 0.19806 | 0.19679 | 0.19552 | 0.19424 | 0.19297 | 0.1917 | 0.19043 | 0.18916
| NKA001-111726711 | NKA001 | 0.00022565 | 0.00022731 | 0.00022897 | 0.00023064 | 0.0002323 | 0.00023472 | 0.00023713 | 0.00023955 | 0.00024196 | 0.00024438 | 0.00024679 | 0.00024921 | 0.00025162 | 0.00025404 | 0.00025645 | 0.00025887 | 0.00026128 | 0.0002637 | 0.00026611 | 0.00026853
| NKA001-138135636 | NKA001 | 0.0031414 | 0.0031441 | 0.0031469 | 0.0031496 | 0.0031523 | 0.0031524 | 0.0031524 | 0.0031525 | 0.0031526 | 0.0031527 | 0.0031527 | 0.0031528 | 0.0031529 | 0.003153 | 0.003153 | 0.0031531 | 0.0031532 | 0.0031533 | 0.0031533 | 0.0031534
| NKA001-15424552 | NKA001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA001-15424578 | NKA001 | 1.6522 | 1.6626 | 1.6729 | 1.6833 | 1.6936 | 1.7016 | 1.7096 | 1.7176 | 1.7256 | 1.7336 | 1.7416 | 1.7496 | 1.7576 | 1.7655 | 1.7735 | 1.7815 | 1.7895 | 1.7975 | 1.8055 | 1.8135
| NKA001-161093990 | NKA001 | 0.00035781 | 0.00036075 | 0.0003637 | 0.00036665 | 0.0003696 | 0.00037272 | 0.00037584 | 0.00037896 | 0.00038208 | 0.0003852 | 0.00038832 | 0.00039144 | 0.00039456 | 0.00039768 | 0.0004008 | 0.00040392 | 0.00040704 | 0.00041016 | 0.00041328 | 0.0004164
| NKA001-24606104 | NKA001 | 2.867 | 2.8823 | 2.8977 | 2.9131 | 2.9285 | 2.9398 | 2.9511 | 2.9625 | 2.9738 | 2.9851 | 2.9964 | 3.0077 | 3.019 | 3.0304 | 3.0417 | 3.053 | 3.0643 | 3.0756 | 3.0869 | 3.0982
| NKA001-24606118 | NKA001 | 0.50612 | 0.50989 | 0.51366 | 0.51743 | 0.5212 | 0.52477 | 0.52834 | 0.53192 | 0.53549 | 0.53906 | 0.54263 | 0.5462 | 0.54977 | 0.55334 | 0.55691 | 0.56048 | 0.56405 | 0.56763 | 0.5712 | 0.57477
| NKA001-96630054 | NKA001 | 0.90659 | 0.91281 | 0.91902 | 0.92524 | 0.93145 | 0.93675 | 0.94204 | 0.94733 | 0.95263 | 0.95792 | 0.96321 | 0.96851 | 0.9738 | 0.97909 | 0.98439 | 0.98968 | 0.99497 | 1.0003 | 1.0056 | 1.0109
| NKA002-15424741 | NKA002 | 29.2387 | 29.3974 | 29.5561 | 29.7148 | 29.8735 | 30.0326 | 30.1916 | 30.3507 | 30.5098 | 30.6688 | 30.8279 | 30.987 | 31.146 | 31.3051 | 31.4642 | 31.6233 | 31.7823 | 31.9414 | 32.1005 | 32.2595
| NKA002-15424752 | NKA002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA002-157269526 | NKA002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA002-160426606 | NKA002 | 9.7436e-06 | 9.8172e-06 | 9.8908e-06 | 9.9644e-06 | 1.0038e-05 | 1.0141e-05 | 1.0244e-05 | 1.0347e-05 | 1.045e-05 | 1.0553e-05 | 1.0655e-05 | 1.0758e-05 | 1.0861e-05 | 1.0964e-05 | 1.1067e-05 | 1.117e-05 | 1.1273e-05 | 1.1376e-05 | 1.1479e-05 | 1.1582e-05
| NKA002-176883603 | NKA002 | 0.010129 | 0.010193 | 0.010257 | 0.010321 | 0.010385 | 0.010439 | 0.010493 | 0.010547 | 0.010601 | 0.010655 | 0.010709 | 0.010763 | 0.010817 | 0.010871 | 0.010925 | 0.010979 | 0.011033 | 0.011087 | 0.011141 | 0.011195
| NKA002-24606230 | NKA002 | 1.2452 | 1.2531 | 1.261 | 1.2689 | 1.2768 | 1.284 | 1.2911 | 1.2982 | 1.3053 | 1.3125 | 1.3196 | 1.3267 | 1.3338 | 1.341 | 1.3481 | 1.3552 | 1.3623 | 1.3695 | 1.3766 | 1.3837
| NKA002-24606244 | NKA002 | 6.4387 | 6.4721 | 6.5054 | 6.5388 | 6.5722 | 6.6244 | 6.6767 | 6.7289 | 6.7812 | 6.8334 | 6.8857 | 6.9379 | 6.9902 | 7.0424 | 7.0947 | 7.1469 | 7.1992 | 7.2514 | 7.3037 | 7.3559
| NKA003-15422579 | NKA003 | 7.0563 | 7.1002 | 7.1441 | 7.188 | 7.232 | 7.2765 | 7.321 | 7.3655 | 7.41 | 7.4545 | 7.4991 | 7.5436 | 7.5881 | 7.6326 | 7.6771 | 7.7217 | 7.7662 | 7.8107 | 7.8552 | 7.8997
| NKA003-161248298 | NKA003 | 0.00041166 | 0.00041474 | 0.00041783 | 0.00042091 | 0.000424 | 0.0004281 | 0.0004322 | 0.0004363 | 0.0004404 | 0.0004445 | 0.0004486 | 0.0004527 | 0.0004568 | 0.0004609 | 0.000465 | 0.0004691 | 0.0004732 | 0.0004773 | 0.0004814 | 0.0004855
| NKA004-15424817 | NKA004 | 48.998 | 49.2152 | 49.4324 | 49.6497 | 49.8669 | 50.0079 | 50.149 | 50.2901 | 50.4311 | 50.5722 | 50.7133 | 50.8543 | 50.9954 | 51.1364 | 51.2775 | 51.4186 | 51.5596 | 51.7007 | 51.8418 | 51.9828
| NKA004-162977911 | NKA004 | 0.00021864 | 0.00022023 | 0.00022182 | 0.00022341 | 0.000225 | 0.00022743 | 0.00022986 | 0.00023229 | 0.00023472 | 0.00023715 | 0.00023958 | 0.00024201 | 0.00024444 | 0.00024687 | 0.0002493 | 0.00025173 | 0.00025416 | 0.00025659 | 0.00025902 | 0.00026145
| NKA005-154156915 | NKA005 | 1.6792 | 1.692 | 1.7048 | 1.7176 | 1.7304 | 1.7452 | 1.7601 | 1.7749 | 1.7898 | 1.8046 | 1.8195 | 1.8343 | 1.8492 | 1.864 | 1.8789 | 1.8937 | 1.9086 | 1.9234 | 1.9383 | 1.9531
| NKA005-15422555 | NKA005 | 2.1044 | 2.1186 | 2.1329 | 2.1471 | 2.1614 | 2.1748 | 2.1882 | 2.2016 | 2.215 | 2.2284 | 2.2418 | 2.2552 | 2.2686 | 2.282 | 2.2954 | 2.3088 | 2.3222 | 2.3356 | 2.349 | 2.3624
| NKA005-24606900 | NKA005 | 3.9638 | 3.9885 | 4.0131 | 4.0377 | 4.0623 | 4.0912 | 4.12 | 4.1489 | 4.1777 | 4.2066 | 4.2355 | 4.2643 | 4.2932 | 4.322 | 4.3509 | 4.3797 | 4.4086 | 4.4374 | 4.4663 | 4.4951
| NKA006-152812929 | NKA006 | 9.0155 | 9.0762 | 9.1369 | 9.1976 | 9.2582 | 9.2963 | 9.3343 | 9.3723 | 9.4104 | 9.4484 | 9.4865 | 9.5245 | 9.5625 | 9.6006 | 9.6386 | 9.6767 | 9.7147 | 9.7527 | 9.7908 | 9.8288
| NKA006-15424841 | NKA006 | 17.6018 | 17.7174 | 17.8331 | 17.9488 | 18.0645 | 18.1853 | 18.3062 | 18.4271 | 18.548 | 18.6688 | 18.7897 | 18.9106 | 19.0314 | 19.1523 | 19.2732 | 19.3941 | 19.5149 | 19.6358 | 19.7567 | 19.8776
| NKA006-15424865 | NKA006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-160426703 | NKA006 | 0.0017716 | 0.0017855 | 0.0017994 | 0.0018133 | 0.0018272 | 0.0018475 | 0.0018678 | 0.0018882 | 0.0019085 | 0.0019288 | 0.0019491 | 0.0019694 | 0.0019898 | 0.0020101 | 0.0020304 | 0.0020507 | 0.002071 | 0.0020914 | 0.0021117 | 0.002132
| NKA006-160426816 | NKA006 | 0.015711 | 0.015768 | 0.015824 | 0.015881 | 0.015938 | 0.015943 | 0.015948 | 0.015953 | 0.015958 | 0.015963 | 0.015968 | 0.015973 | 0.015978 | 0.015983 | 0.015988 | 0.015993 | 0.015998 | 0.016003 | 0.016008 | 0.016013
| NKA006-162978025 | NKA006 | 0.033555 | 0.033777 | 0.034 | 0.034223 | 0.034445 | 0.034638 | 0.034831 | 0.035024 | 0.035217 | 0.035411 | 0.035604 | 0.035797 | 0.03599 | 0.036183 | 0.036376 | 0.036569 | 0.036762 | 0.036955 | 0.037148 | 0.037341
| NKA006-163615273 | NKA006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-181987048 | NKA006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-192419289 | NKA006 | 0.31983 | 0.32173 | 0.32363 | 0.32554 | 0.32744 | 0.32981 | 0.33218 | 0.33456 | 0.33693 | 0.33931 | 0.34168 | 0.34405 | 0.34643 | 0.3488 | 0.35117 | 0.35355 | 0.35592 | 0.35829 | 0.36067 | 0.36304
| NKA006-24605964 | NKA006 | 0.44741 | 0.45036 | 0.45331 | 0.45626 | 0.45921 | 0.46209 | 0.46497 | 0.46785 | 0.47073 | 0.47361 | 0.47649 | 0.47938 | 0.48226 | 0.48514 | 0.48802 | 0.4909 | 0.49378 | 0.49666 | 0.49954 | 0.50242
| OYN001-15412732 | OYN001 | 0.86746 | 0.8739 | 0.88033 | 0.88677 | 0.89321 | 0.8919 | 0.89059 | 0.88929 | 0.88798 | 0.88667 | 0.88537 | 0.88406 | 0.88275 | 0.88145 | 0.88014 | 0.87883 | 0.87753 | 0.87622 | 0.87491 | 0.87361
| OYN001-15412756 | OYN001 | 0.0033287 | 0.0033582 | 0.0033877 | 0.0034172 | 0.0034468 | 0.0034463 | 0.0034459 | 0.0034454 | 0.003445 | 0.0034445 | 0.0034441 | 0.0034436 | 0.0034432 | 0.0034427 | 0.0034423 | 0.0034418 | 0.0034414 | 0.0034409 | 0.0034405 | 0.00344
| OYN001-157370670 | OYN001 | 0.015004 | 0.015111 | 0.015218 | 0.015326 | 0.015433 | 0.015394 | 0.015355 | 0.015316 | 0.015277 | 0.015238 | 0.015199 | 0.01516 | 0.015121 | 0.015083 | 0.015044 | 0.015005 | 0.014966 | 0.014927 | 0.014888 | 0.014849
| OYN001-157370765 | OYN001 | 0.00040535 | 0.00040829 | 0.00041122 | 0.00041416 | 0.0004171 | 0.00041586 | 0.00041463 | 0.0004134 | 0.00041217 | 0.00041094 | 0.0004097 | 0.00040847 | 0.00040724 | 0.00040601 | 0.00040477 | 0.00040354 | 0.00040231 | 0.00040108 | 0.00039985 | 0.00039861
| OYN001-157425399 | OYN001 | 0.003873 | 0.0038968 | 0.0039207 | 0.0039445 | 0.0039683 | 0.0039563 | 0.0039443 | 0.0039323 | 0.0039203 | 0.0039082 | 0.0038962 | 0.0038842 | 0.0038722 | 0.0038602 | 0.0038482 | 0.0038362 | 0.0038241 | 0.0038121 | 0.0038001 | 0.0037881
| OYN001-157599093 | OYN001 | 4.6641e-05 | 4.6995e-05 | 4.735e-05 | 4.7705e-05 | 4.806e-05 | 4.8045e-05 | 4.803e-05 | 4.8015e-05 | 4.8e-05 | 4.7985e-05 | 4.797e-05 | 4.7955e-05 | 4.794e-05 | 4.7925e-05 | 4.791e-05 | 4.7895e-05 | 4.788e-05 | 4.7865e-05 | 4.785e-05 | 4.7835e-05
| OYN001-157599241 | OYN001 | 0.0063088 | 0.0063605 | 0.0064123 | 0.006464 | 0.0065157 | 0.0065099 | 0.0065041 | 0.0064984 | 0.0064926 | 0.0064868 | 0.006481 | 0.0064752 | 0.0064694 | 0.0064636 | 0.0064578 | 0.006452 | 0.0064462 | 0.0064404 | 0.0064346 | 0.0064288
| OYN001-157599335 | OYN001 | 0.042468 | 0.042776 | 0.043083 | 0.043391 | 0.043698 | 0.043618 | 0.043537 | 0.043456 | 0.043376 | 0.043295 | 0.043215 | 0.043134 | 0.043053 | 0.042973 | 0.042892 | 0.042812 | 0.042731 | 0.04265 | 0.04257 | 0.042489
| OYN001-157997774 | OYN001 | 0.016964 | 0.017091 | 0.017217 | 0.017344 | 0.017471 | 0.01744 | 0.017409 | 0.017378 | 0.017347 | 0.017316 | 0.017285 | 0.017254 | 0.017223 | 0.017192 | 0.017161 | 0.01713 | 0.0171 | 0.017069 | 0.017038 | 0.017007
| OYN001-157997885 | OYN001 | 0.064678 | 0.065132 | 0.065586 | 0.066041 | 0.066495 | 0.066373 | 0.066252 | 0.06613 | 0.066008 | 0.065886 | 0.065765 | 0.065643 | 0.065521 | 0.065399 | 0.065278 | 0.065156 | 0.065034 | 0.064913 | 0.064791 | 0.064669
| OYN001-157997976 | OYN001 | 0.0014223 | 0.0014329 | 0.0014435 | 0.0014541 | 0.0014647 | 0.001464 | 0.0014633 | 0.0014626 | 0.0014619 | 0.0014612 | 0.0014605 | 0.0014598 | 0.0014591 | 0.0014584 | 0.0014577 | 0.001457 | 0.0014563 | 0.0014556 | 0.0014549 | 0.0014542
| OYN001-157998086 | OYN001 | 0.0054214 | 0.0054664 | 0.0055115 | 0.0055566 | 0.0056016 | 0.005604 | 0.0056063 | 0.0056087 | 0.005611 | 0.0056134 | 0.0056157 | 0.0056181 | 0.0056204 | 0.0056228 | 0.0056251 | 0.0056275 | 0.0056298 | 0.0056322 | 0.0056345 | 0.0056369
| OYN001-157998203 | OYN001 | 0.012721 | 0.012823 | 0.012925 | 0.013026 | 0.013128 | 0.013123 | 0.013119 | 0.013114 | 0.013109 | 0.013104 | 0.013099 | 0.013094 | 0.01309 | 0.013085 | 0.01308 | 0.013075 | 0.01307 | 0.013066 | 0.013061 | 0.013056
| OYN001-157998251 | OYN001 | 0.0072511 | 0.0073071 | 0.007363 | 0.0074189 | 0.0074749 | 0.0074757 | 0.0074766 | 0.0074774 | 0.0074783 | 0.0074791 | 0.00748 | 0.0074808 | 0.0074817 | 0.0074825 | 0.0074834 | 0.0074842 | 0.0074851 | 0.0074859 | 0.0074868 | 0.0074876
| OYN001-157998623 | OYN001 | 0.011559 | 0.011657 | 0.011755 | 0.011853 | 0.011951 | 0.011944 | 0.011937 | 0.01193 | 0.011924 | 0.011917 | 0.01191 | 0.011903 | 0.011896 | 0.011889 | 0.011882 | 0.011876 | 0.011869 | 0.011862 | 0.011855 | 0.011848
| OYN001-159943098 | OYN001 | 0.02945 | 0.029741 | 0.030033 | 0.030325 | 0.030616 | 0.030498 | 0.03038 | 0.030263 | 0.030145 | 0.030027 | 0.029909 | 0.029791 | 0.029673 | 0.029555 | 0.029437 | 0.029319 | 0.029202 | 0.029084 | 0.028966 | 0.028848
| OYN001-159943284 | OYN001 | 0.0044465 | 0.0044703 | 0.0044941 | 0.004518 | 0.0045418 | 0.0045302 | 0.0045186 | 0.0045071 | 0.0044955 | 0.0044839 | 0.0044724 | 0.0044608 | 0.0044492 | 0.0044376 | 0.0044261 | 0.0044145 | 0.0044029 | 0.0043914 | 0.0043798 | 0.0043682
| OYN001-161991346 | OYN001 | 0.063837 | 0.064297 | 0.064758 | 0.065218 | 0.065678 | 0.065562 | 0.065446 | 0.06533 | 0.065214 | 0.065098 | 0.064981 | 0.064865 | 0.064749 | 0.064633 | 0.064517 | 0.064401 | 0.064284 | 0.064168 | 0.064052 | 0.063936
| OYN001-161991484 | OYN001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-161991742 | OYN001 | 0.00087929 | 0.00088671 | 0.00089414 | 0.00090157 | 0.000909 | 0.00090864 | 0.00090828 | 0.00090792 | 0.00090757 | 0.00090721 | 0.00090685 | 0.00090649 | 0.00090613 | 0.00090577 | 0.00090541 | 0.00090506 | 0.0009047 | 0.00090434 | 0.00090398 | 0.00090362
| OYN001-161991880 | OYN001 | 0.0039547 | 0.0039905 | 0.0040263 | 0.0040621 | 0.004098 | 0.0040887 | 0.0040795 | 0.0040702 | 0.004061 | 0.0040517 | 0.0040425 | 0.0040332 | 0.004024 | 0.0040147 | 0.0040055 | 0.0039962 | 0.003987 | 0.0039777 | 0.0039685 | 0.0039592
| OYN001-161991949 | OYN001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-24603328 | OYN001 | 0.67701 | 0.68396 | 0.6909 | 0.69785 | 0.7048 | 0.70304 | 0.70128 | 0.69953 | 0.69777 | 0.69601 | 0.69426 | 0.6925 | 0.69074 | 0.68899 | 0.68723 | 0.68547 | 0.68372 | 0.68196 | 0.6802 | 0.67845
| OYN001-24604668 | OYN001 | 3.229 | 3.2492 | 3.2694 | 3.2896 | 3.3098 | 3.301 | 3.2921 | 3.2832 | 3.2743 | 3.2654 | 3.2565 | 3.2477 | 3.2388 | 3.2299 | 3.221 | 3.2121 | 3.2032 | 3.1944 | 3.1855 | 3.1766
| OYN001-41898846 | OYN001 | 0.26591 | 0.26785 | 0.26979 | 0.27174 | 0.27368 | 0.27312 | 0.27255 | 0.27199 | 0.27142 | 0.27086 | 0.2703 | 0.26973 | 0.26917 | 0.26861 | 0.26804 | 0.26748 | 0.26692 | 0.26635 | 0.26579 | 0.26523
| OYN003-15412682 | OYN003 | 0.33787 | 0.34084 | 0.34381 | 0.34678 | 0.34976 | 0.3499 | 0.35003 | 0.35017 | 0.35031 | 0.35045 | 0.35059 | 0.35073 | 0.35086 | 0.351 | 0.35114 | 0.35128 | 0.35142 | 0.35156 | 0.3517 | 0.35183
| OYN003-157425942 | OYN003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN003-158041159 | OYN003 | 0.022465 | 0.022672 | 0.022879 | 0.023087 | 0.023294 | 0.023313 | 0.023332 | 0.023351 | 0.023369 | 0.023388 | 0.023407 | 0.023426 | 0.023444 | 0.023463 | 0.023482 | 0.023501 | 0.023519 | 0.023538 | 0.023557 | 0.023576
| OYN003-158109405 | OYN003 | 0.020846 | 0.021039 | 0.021233 | 0.021426 | 0.02162 | 0.021631 | 0.021642 | 0.021653 | 0.021664 | 0.021675 | 0.021685 | 0.021696 | 0.021707 | 0.021718 | 0.021729 | 0.02174 | 0.021751 | 0.021762 | 0.021773 | 0.021784
| OYN003-158109515 | OYN003 | 0.00010769 | 0.00010867 | 0.00010965 | 0.00011062 | 0.0001116 | 0.00011168 | 0.00011176 | 0.00011184 | 0.00011192 | 0.000112 | 0.00011208 | 0.00011216 | 0.00011224 | 0.00011232 | 0.0001124 | 0.00011248 | 0.00011256 | 0.00011264 | 0.00011272 | 0.0001128
| OYN003-158109598 | OYN003 | 0.01308 | 0.013197 | 0.013314 | 0.013432 | 0.013549 | 0.013566 | 0.013582 | 0.013599 | 0.013616 | 0.013632 | 0.013649 | 0.013666 | 0.013682 | 0.013699 | 0.013716 | 0.013733 | 0.013749 | 0.013766 | 0.013783 | 0.013799
| OYN003-158109716 | OYN003 | 0.0082236 | 0.0082927 | 0.0083617 | 0.0084308 | 0.0084998 | 0.0084923 | 0.0084847 | 0.0084772 | 0.0084696 | 0.0084621 | 0.0084545 | 0.0084469 | 0.0084394 | 0.0084318 | 0.0084243 | 0.0084167 | 0.0084092 | 0.0084016 | 0.0083941 | 0.0083865
| OYN003-158109850 | OYN003 | 0.0069146 | 0.0069709 | 0.0070272 | 0.0070836 | 0.0071399 | 0.0071403 | 0.0071407 | 0.007141 | 0.0071414 | 0.0071418 | 0.0071422 | 0.0071425 | 0.0071429 | 0.0071433 | 0.0071437 | 0.0071441 | 0.0071444 | 0.0071448 | 0.0071452 | 0.0071456
| OYN003-158110054 | OYN003 | 0.026781 | 0.027029 | 0.027276 | 0.027524 | 0.027771 | 0.027785 | 0.027798 | 0.027811 | 0.027824 | 0.027837 | 0.02785 | 0.027863 | 0.027876 | 0.027889 | 0.027902 | 0.027915 | 0.027928 | 0.027941 | 0.027954 | 0.027967
| OYN003-161992042 | OYN003 | 4.892e-05 | 4.936e-05 | 4.98e-05 | 5.024e-05 | 5.068e-05 | 5.0645e-05 | 5.061e-05 | 5.0575e-05 | 5.054e-05 | 5.0505e-05 | 5.047e-05 | 5.0435e-05 | 5.04e-05 | 5.0365e-05 | 5.033e-05 | 5.0295e-05 | 5.026e-05 | 5.0225e-05 | 5.019e-05 | 5.0155e-05
| OYN005-15412808 | OYN005 | 3.7139 | 3.7412 | 3.7684 | 3.7956 | 3.8228 | 3.8181 | 3.8134 | 3.8087 | 3.804 | 3.7992 | 3.7945 | 3.7898 | 3.7851 | 3.7804 | 3.7756 | 3.7709 | 3.7662 | 3.7615 | 3.7568 | 3.752
| OYN005-159372302 | OYN005 | 0.10332 | 0.10437 | 0.10543 | 0.10648 | 0.10754 | 0.10791 | 0.10829 | 0.10867 | 0.10904 | 0.10942 | 0.1098 | 0.11018 | 0.11055 | 0.11093 | 0.11131 | 0.11169 | 0.11206 | 0.11244 | 0.11282 | 0.1132
| OYN005-159377479 | OYN005 | 0.0082295 | 0.0083045 | 0.0083796 | 0.0084547 | 0.0085297 | 0.008553 | 0.0085762 | 0.0085994 | 0.0086226 | 0.0086459 | 0.0086691 | 0.0086923 | 0.0087156 | 0.0087388 | 0.008762 | 0.0087852 | 0.0088085 | 0.0088317 | 0.0088549 | 0.0088781
| OYN005-160435471 | OYN005 | 0.028558 | 0.028822 | 0.029085 | 0.029349 | 0.029613 | 0.029718 | 0.029823 | 0.029928 | 0.030033 | 0.030138 | 0.030243 | 0.030348 | 0.030452 | 0.030557 | 0.030662 | 0.030767 | 0.030872 | 0.030977 | 0.031082 | 0.031187
| OYN005-160491322 | OYN005 | 0.01547 | 0.015592 | 0.015714 | 0.015836 | 0.015958 | 0.016007 | 0.016055 | 0.016104 | 0.016153 | 0.016202 | 0.01625 | 0.016299 | 0.016348 | 0.016397 | 0.016446 | 0.016494 | 0.016543 | 0.016592 | 0.016641 | 0.016689
| OYN005-160578653 | OYN005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-160637132 | OYN005 | 0.001495 | 0.0015104 | 0.0015258 | 0.0015413 | 0.0015567 | 0.0015584 | 0.0015601 | 0.0015618 | 0.0015635 | 0.0015652 | 0.0015669 | 0.0015686 | 0.0015703 | 0.001572 | 0.0015737 | 0.0015754 | 0.0015772 | 0.0015789 | 0.0015806 | 0.0015823
| OYN005-160827931 | OYN005 | 0.092317 | 0.093114 | 0.09391 | 0.094707 | 0.095504 | 0.095509 | 0.095515 | 0.09552 | 0.095526 | 0.095531 | 0.095537 | 0.095542 | 0.095548 | 0.095553 | 0.095558 | 0.095564 | 0.095569 | 0.095575 | 0.09558 | 0.095586
| OYN005-160828059 | OYN005 | 0.027127 | 0.02735 | 0.027574 | 0.027797 | 0.028021 | 0.02804 | 0.02806 | 0.02808 | 0.028099 | 0.028119 | 0.028138 | 0.028158 | 0.028178 | 0.028197 | 0.028217 | 0.028236 | 0.028256 | 0.028276 | 0.028295 | 0.028315
| OYN005-160828223 | OYN005 | 5.4137e-05 | 5.4603e-05 | 5.5069e-05 | 5.5534e-05 | 5.6e-05 | 5.59e-05 | 5.58e-05 | 5.57e-05 | 5.56e-05 | 5.55e-05 | 5.54e-05 | 5.53e-05 | 5.52e-05 | 5.51e-05 | 5.5e-05 | 5.49e-05 | 5.48e-05 | 5.47e-05 | 5.46e-05 | 5.45e-05
| OYN005-160829369 | OYN005 | 0.074525 | 0.075067 | 0.075608 | 0.07615 | 0.076692 | 0.076632 | 0.076572 | 0.076511 | 0.076451 | 0.076391 | 0.076331 | 0.07627 | 0.07621 | 0.07615 | 0.07609 | 0.07603 | 0.075969 | 0.075909 | 0.075849 | 0.075789
| OYN005-160829541 | OYN005 | 0.022692 | 0.022885 | 0.023078 | 0.023271 | 0.023465 | 0.023479 | 0.023494 | 0.023509 | 0.023524 | 0.023539 | 0.023554 | 0.023568 | 0.023583 | 0.023598 | 0.023613 | 0.023628 | 0.023642 | 0.023657 | 0.023672 | 0.023687
| OYN005-160930811 | OYN005 | 0.0211 | 0.021298 | 0.021496 | 0.021694 | 0.021892 | 0.021926 | 0.021961 | 0.021995 | 0.02203 | 0.022064 | 0.022099 | 0.022133 | 0.022168 | 0.022203 | 0.022237 | 0.022272 | 0.022306 | 0.022341 | 0.022375 | 0.02241
| OYN005-160930950 | OYN005 | 0.11732 | 0.11849 | 0.11966 | 0.12083 | 0.122 | 0.1224 | 0.12281 | 0.12321 | 0.12362 | 0.12402 | 0.12443 | 0.12484 | 0.12524 | 0.12565 | 0.12605 | 0.12646 | 0.12686 | 0.12727 | 0.12768 | 0.12808
| OYN005-160931147 | OYN005 | 0.013047 | 0.01314 | 0.013232 | 0.013325 | 0.013418 | 0.01342 | 0.013422 | 0.013424 | 0.013426 | 0.013428 | 0.01343 | 0.013432 | 0.013434 | 0.013436 | 0.013438 | 0.01344 | 0.013442 | 0.013445 | 0.013447 | 0.013449
| OYN005-160960634 | OYN005 | 0.11589 | 0.11701 | 0.11812 | 0.11924 | 0.12035 | 0.12053 | 0.1207 | 0.12087 | 0.12105 | 0.12122 | 0.12139 | 0.12157 | 0.12174 | 0.12191 | 0.12209 | 0.12226 | 0.12243 | 0.12261 | 0.12278 | 0.12295
| OYN005-160960891 | OYN005 | 0.0091114 | 0.0091927 | 0.0092741 | 0.0093554 | 0.0094368 | 0.009457 | 0.0094772 | 0.0094973 | 0.0095175 | 0.0095377 | 0.0095579 | 0.0095781 | 0.0095983 | 0.0096185 | 0.0096387 | 0.0096589 | 0.0096791 | 0.0096993 | 0.0097195 | 0.0097397
| OYN005-161887259 | OYN005 | 1.9234 | 1.9405 | 1.9577 | 1.9748 | 1.992 | 1.9966 | 2.0012 | 2.0058 | 2.0104 | 2.015 | 2.0197 | 2.0243 | 2.0289 | 2.0335 | 2.0381 | 2.0427 | 2.0474 | 2.052 | 2.0566 | 2.0612
| OYN005-162206992 | OYN005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-162260630 | OYN005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-162551906 | OYN005 | 0.023357 | 0.023558 | 0.023759 | 0.02396 | 0.024161 | 0.024255 | 0.024349 | 0.024443 | 0.024537 | 0.024631 | 0.024725 | 0.024819 | 0.024914 | 0.025008 | 0.025102 | 0.025196 | 0.02529 | 0.025384 | 0.025478 | 0.025572
| OYN005-162690111 | OYN005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-162952933 | OYN005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OYN005-164254226 | OYN005 | 0.013119 | 0.013251 | 0.013382 | 0.013514 | 0.013645 | 0.01366 | 0.013674 | 0.013688 | 0.013702 | 0.013717 | 0.013731 | 0.013745 | 0.013759 | 0.013774 | 0.013788 | 0.013802 | 0.013817 | 0.013831 | 0.013845 | 0.013859
| OYN005-164254377 | OYN005 | 0.051799 | 0.052237 | 0.052674 | 0.053112 | 0.053549 | 0.05365 | 0.053751 | 0.053852 | 0.053953 | 0.054054 | 0.054155 | 0.054256 | 0.054357 | 0.054458 | 0.054559 | 0.05466 | 0.054761 | 0.054862 | 0.054963 | 0.055064
| OYN005-164276023 | OYN005 | 0.13197 | 0.13289 | 0.13381 | 0.13473 | 0.13565 | 0.13552 | 0.13538 | 0.13525 | 0.13511 | 0.13498 | 0.13484 | 0.13471 | 0.13457 | 0.13444 | 0.1343 | 0.13417 | 0.13403 | 0.1339 | 0.13376 | 0.13363
| OYN005-164365790 | OYN005 | 0.050274 | 0.050748 | 0.051223 | 0.051697 | 0.052172 | 0.052192 | 0.052213 | 0.052233 | 0.052254 | 0.052274 | 0.052295 | 0.052315 | 0.052336 | 0.052356 | 0.052377 | 0.052397 | 0.052418 | 0.052438 | 0.052459 | 0.052479
| OYN005-164366490 | OYN005 | 0.00068215 | 0.00068927 | 0.00069638 | 0.00070349 | 0.0007106 | 0.00071231 | 0.00071402 | 0.00071573 | 0.00071744 | 0.00071915 | 0.00072086 | 0.00072257 | 0.00072428 | 0.00072599 | 0.0007277 | 0.00072941 | 0.00073112 | 0.00073283 | 0.00073454 | 0.00073625
| OYN005-164366901 | OYN005 | 0.010547 | 0.010661 | 0.010775 | 0.010889 | 0.011004 | 0.011022 | 0.01104 | 0.011058 | 0.011076 | 0.011094 | 0.011112 | 0.01113 | 0.011148 | 0.011166 | 0.011184 | 0.011202 | 0.01122 | 0.011238 | 0.011256 | 0.011274
| OYN005-203082808 | OYN005 | 0.24552 | 0.2478 | 0.25008 | 0.25236 | 0.25464 | 0.25497 | 0.2553 | 0.25563 | 0.25596 | 0.25629 | 0.25662 | 0.25695 | 0.25728 | 0.25761 | 0.25794 | 0.25827 | 0.2586 | 0.25893 | 0.25926 | 0.25959
| OYN005-203102592 | OYN005 | 0.075446 | 0.076169 | 0.076892 | 0.077615 | 0.078338 | 0.078466 | 0.078594 | 0.078721 | 0.078849 | 0.078977 | 0.079104 | 0.079232 | 0.07936 | 0.079487 | 0.079615 | 0.079742 | 0.07987 | 0.079998 | 0.080125 | 0.080253
| OYN005-24603468 | OYN005 | 0.15855 | 0.16 | 0.16144 | 0.16289 | 0.16434 | 0.16432 | 0.16431 | 0.1643 | 0.16429 | 0.16428 | 0.16427 | 0.16426 | 0.16424 | 0.16423 | 0.16422 | 0.16421 | 0.1642 | 0.16419 | 0.16417 | 0.16416
| OYN005-24603482 | OYN005 | 4.393 | 4.4311 | 4.4692 | 4.5073 | 4.5454 | 4.5552 | 4.5651 | 4.5749 | 4.5847 | 4.5945 | 4.6044 | 4.6142 | 4.624 | 4.6338 | 4.6437 | 4.6535 | 4.6633 | 4.6731 | 4.683 | 4.6928
| OYN005-84748828 | OYN005 | 1.0334 | 1.0436 | 1.0538 | 1.064 | 1.0741 | 1.076 | 1.0778 | 1.0796 | 1.0814 | 1.0833 | 1.0851 | 1.0869 | 1.0888 | 1.0906 | 1.0924 | 1.0942 | 1.0961 | 1.0979 | 1.0997 | 1.1015
| OYN005-88333607 | OYN005 | 0.024422 | 0.024631 | 0.024841 | 0.02505 | 0.02526 | 0.025263 | 0.025267 | 0.025271 | 0.025274 | 0.025278 | 0.025282 | 0.025285 | 0.025289 | 0.025293 | 0.025297 | 0.0253 | 0.025304 | 0.025308 | 0.025311 | 0.025315
| OYN007-15412819 | OYN007 | 0.15455 | 0.15588 | 0.15722 | 0.15855 | 0.15988 | 0.15982 | 0.15975 | 0.15968 | 0.15962 | 0.15955 | 0.15948 | 0.15941 | 0.15935 | 0.15928 | 0.15921 | 0.15915 | 0.15908 | 0.15901 | 0.15895 | 0.15888
| OYN007-15412830 | OYN007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-128232196 | PLD001 | 1.54 | 1.5565 | 1.573 | 1.5895 | 1.6059 | 1.567 | 1.5282 | 1.4893 | 1.4504 | 1.4115 | 1.3726 | 1.3337 | 1.2948 | 1.2559 | 1.217 | 1.1781 | 1.1392 | 1.1003 | 1.0614 | 1.0225
| PLD001-15398772 | PLD001 | 7.9029 | 7.9808 | 8.0587 | 8.1366 | 8.2145 | 8.035 | 7.8555 | 7.676 | 7.4965 | 7.317 | 7.1375 | 6.958 | 6.7785 | 6.5989 | 6.4194 | 6.2399 | 6.0604 | 5.8809 | 5.7014 | 5.5219
| PLD001-159945085 | PLD001 | 0.0037109 | 0.0037408 | 0.0037706 | 0.0038004 | 0.0038303 | 0.0037664 | 0.0037025 | 0.0036387 | 0.0035748 | 0.0035109 | 0.0034471 | 0.0033832 | 0.0033194 | 0.0032555 | 0.0031916 | 0.0031278 | 0.0030639 | 0.003 | 0.0029362 | 0.0028723
| PLD001-160255348 | PLD001 | 0.0013898 | 0.0014 | 0.0014102 | 0.0014205 | 0.0014307 | 0.0014052 | 0.0013798 | 0.0013543 | 0.0013289 | 0.0013034 | 0.001278 | 0.0012525 | 0.001227 | 0.0012016 | 0.0011761 | 0.0011507 | 0.0011252 | 0.0010998 | 0.0010743 | 0.0010489
| PLD001-160255473 | PLD001 | 0.0086248 | 0.0086846 | 0.0087444 | 0.0088041 | 0.0088639 | 0.0087596 | 0.0086553 | 0.008551 | 0.0084467 | 0.0083424 | 0.0082381 | 0.0081338 | 0.0080295 | 0.0079252 | 0.007821 | 0.0077167 | 0.0076124 | 0.0075081 | 0.0074038 | 0.0072995
| PLD001-160255864 | PLD001 | 0.00027287 | 0.00027615 | 0.00027943 | 0.00028272 | 0.000286 | 0.00027772 | 0.00026944 | 0.00026116 | 0.00025288 | 0.0002446 | 0.00023631 | 0.00022803 | 0.00021975 | 0.00021147 | 0.00020319 | 0.00019491 | 0.00018663 | 0.00017835 | 0.00017007 | 0.00016178
| PLD001-160255960 | PLD001 | 0.00018856 | 0.00018954 | 0.00019053 | 0.00019151 | 0.0001925 | 0.00018734 | 0.00018217 | 0.00017701 | 0.00017185 | 0.00016669 | 0.00016152 | 0.00015636 | 0.0001512 | 0.00014604 | 0.00014087 | 0.00013571 | 0.00013055 | 0.00012539 | 0.00012022 | 0.00011506
| PLD001-160286437 | PLD001 | 0.00011647 | 0.00011761 | 0.00011874 | 0.00011987 | 0.000121 | 0.00011845 | 0.0001159 | 0.00011334 | 0.00011079 | 0.00010824 | 0.00010569 | 0.00010314 | 0.00010058 | 9.8032e-05 | 9.548e-05 | 9.2928e-05 | 9.0376e-05 | 8.7824e-05 | 8.5272e-05 | 8.272e-05
| PLD001-160286548 | PLD001 | 0.040734 | 0.040867 | 0.041 | 0.041133 | 0.041266 | 0.041116 | 0.040967 | 0.040817 | 0.040668 | 0.040518 | 0.040369 | 0.04022 | 0.04007 | 0.039921 | 0.039771 | 0.039622 | 0.039473 | 0.039323 | 0.039174 | 0.039024
| PLD001-160286649 | PLD001 | 0.028071 | 0.02823 | 0.028389 | 0.028548 | 0.028707 | 0.028086 | 0.027465 | 0.026844 | 0.026223 | 0.025602 | 0.02498 | 0.024359 | 0.023738 | 0.023117 | 0.022496 | 0.021875 | 0.021254 | 0.020633 | 0.020012 | 0.019391
| PLD001-162206790 | PLD001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-162207166 | PLD001 | 0.0001042 | 0.00010503 | 0.00010586 | 0.00010669 | 0.00010752 | 0.00010447 | 0.00010141 | 9.8358e-05 | 9.5304e-05 | 9.225e-05 | 8.9196e-05 | 8.6142e-05 | 8.3088e-05 | 8.0034e-05 | 7.698e-05 | 7.3926e-05 | 7.0872e-05 | 6.7818e-05 | 6.4764e-05 | 6.171e-05
| PLD001-162213349 | PLD001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-162290445 | PLD001 | 0.0089372 | 0.0090108 | 0.0090845 | 0.0091581 | 0.0092317 | 0.0090229 | 0.008814 | 0.0086051 | 0.0083962 | 0.0081874 | 0.0079785 | 0.0077696 | 0.0075608 | 0.0073519 | 0.007143 | 0.0069342 | 0.0067253 | 0.0065164 | 0.0063076 | 0.0060987
| PLD001-162290662 | PLD001 | 0.00032784 | 0.00033058 | 0.00033332 | 0.00033606 | 0.0003388 | 0.00033082 | 0.00032284 | 0.00031486 | 0.00030688 | 0.0002989 | 0.00029092 | 0.00028294 | 0.00027496 | 0.00026698 | 0.000259 | 0.00025102 | 0.00024304 | 0.00023506 | 0.00022708 | 0.0002191
| PLD001-162291051 | PLD001 | 0.00085225 | 0.00085879 | 0.00086533 | 0.00087186 | 0.0008784 | 0.00085696 | 0.00083552 | 0.00081408 | 0.00079264 | 0.0007712 | 0.00074976 | 0.00072832 | 0.00070688 | 0.00068544 | 0.000664 | 0.00064256 | 0.00062112 | 0.00059968 | 0.00057824 | 0.0005568
| PLD001-162377877 | PLD001 | 3.9207e-05 | 3.9545e-05 | 3.9883e-05 | 4.0222e-05 | 4.056e-05 | 3.9504e-05 | 3.8448e-05 | 3.7392e-05 | 3.6336e-05 | 3.528e-05 | 3.4224e-05 | 3.3168e-05 | 3.2112e-05 | 3.1056e-05 | 3e-05 | 2.8944e-05 | 2.7888e-05 | 2.6832e-05 | 2.5776e-05 | 2.472e-05
| PLD001-163864241 | PLD001 | 0.008484 | 0.0085536 | 0.0086232 | 0.0086928 | 0.0087624 | 0.0086062 | 0.00845 | 0.0082938 | 0.0081375 | 0.0079813 | 0.0078251 | 0.0076688 | 0.0075126 | 0.0073564 | 0.0072001 | 0.0070439 | 0.0068877 | 0.0067315 | 0.0065752 | 0.006419
| PLD001-24597198 | PLD001 | 2.0194 | 2.0318 | 2.0442 | 2.0566 | 2.069 | 2.0295 | 1.9901 | 1.9506 | 1.9112 | 1.8718 | 1.8323 | 1.7929 | 1.7534 | 1.714 | 1.6745 | 1.6351 | 1.5956 | 1.5562 | 1.5167 | 1.4773
| PLD001-24611964 | PLD001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-95142888 | PLD001 | 0.018994 | 0.019132 | 0.01927 | 0.019408 | 0.019546 | 0.019185 | 0.018824 | 0.018462 | 0.018101 | 0.01774 | 0.017379 | 0.017018 | 0.016657 | 0.016296 | 0.015935 | 0.015574 | 0.015213 | 0.014852 | 0.01449 | 0.014129
| PLD002-15398648 | PLD002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD002-15398661 | PLD002 | 0.026565 | 0.026861 | 0.027157 | 0.027454 | 0.02775 | 0.027014 | 0.026278 | 0.025542 | 0.024806 | 0.024071 | 0.023335 | 0.022599 | 0.021863 | 0.021127 | 0.020391 | 0.019655 | 0.018919 | 0.018183 | 0.017447 | 0.016711
| PLD003-110224899 | PLD003 | 1.5637e-05 | 1.5845e-05 | 1.6053e-05 | 1.6262e-05 | 1.647e-05 | 1.5891e-05 | 1.5312e-05 | 1.4733e-05 | 1.4153e-05 | 1.3574e-05 | 1.2995e-05 | 1.2416e-05 | 1.1837e-05 | 1.1258e-05 | 1.0678e-05 | 1.0099e-05 | 9.5202e-06 | 8.941e-06 | 8.3619e-06 | 7.7827e-06
| PLD003-147733185 | PLD003 | 0.42175 | 0.42518 | 0.42861 | 0.43204 | 0.43547 | 0.4259 | 0.41633 | 0.40676 | 0.39719 | 0.38762 | 0.37805 | 0.36848 | 0.35892 | 0.34935 | 0.33978 | 0.33021 | 0.32064 | 0.31107 | 0.3015 | 0.29193
| PLD003-15398748 | PLD003 | 0.5316 | 0.53759 | 0.54359 | 0.54958 | 0.55558 | 0.54044 | 0.52531 | 0.51018 | 0.49505 | 0.47992 | 0.46479 | 0.44966 | 0.43452 | 0.41939 | 0.40426 | 0.38913 | 0.374 | 0.35887 | 0.34374 | 0.3286
| PLD003-160436494 | PLD003 | 5.6767e-05 | 5.7347e-05 | 5.7928e-05 | 5.8509e-05 | 5.909e-05 | 5.7257e-05 | 5.5423e-05 | 5.359e-05 | 5.1756e-05 | 4.9923e-05 | 4.8089e-05 | 4.6256e-05 | 4.4422e-05 | 4.2589e-05 | 4.0755e-05 | 3.8922e-05 | 3.7088e-05 | 3.5255e-05 | 3.3421e-05 | 3.1588e-05
| PLD003-160436674 | PLD003 | 0.077075 | 0.077827 | 0.078578 | 0.07933 | 0.080082 | 0.078529 | 0.076977 | 0.075425 | 0.073872 | 0.07232 | 0.070768 | 0.069215 | 0.067663 | 0.066111 | 0.064558 | 0.063006 | 0.061454 | 0.059901 | 0.058349 | 0.056797
| PLD003-160451735 | PLD003 | 0.074015 | 0.074801 | 0.075587 | 0.076372 | 0.077158 | 0.075243 | 0.073329 | 0.071414 | 0.0695 | 0.067585 | 0.065671 | 0.063756 | 0.061842 | 0.059927 | 0.058013 | 0.056098 | 0.054184 | 0.052269 | 0.050355 | 0.04844
| PLD003-160519395 | PLD003 | 0.029157 | 0.029448 | 0.02974 | 0.030031 | 0.030322 | 0.029625 | 0.028928 | 0.02823 | 0.027533 | 0.026836 | 0.026139 | 0.025442 | 0.024744 | 0.024047 | 0.02335 | 0.022653 | 0.021955 | 0.021258 | 0.020561 | 0.019864
| PLD003-160519570 | PLD003 | 0.045224 | 0.045733 | 0.046241 | 0.04675 | 0.047259 | 0.046133 | 0.045007 | 0.043881 | 0.042755 | 0.041629 | 0.040503 | 0.039377 | 0.038251 | 0.037125 | 0.036 | 0.034874 | 0.033748 | 0.032622 | 0.031496 | 0.03037
| PLD003-160519700 | PLD003 | 0.0048157 | 0.0048523 | 0.0048888 | 0.0049253 | 0.0049619 | 0.0048596 | 0.0047573 | 0.004655 | 0.0045527 | 0.0044504 | 0.0043481 | 0.0042458 | 0.0041435 | 0.0040412 | 0.0039389 | 0.0038366 | 0.0037344 | 0.0036321 | 0.0035298 | 0.0034275
| PLD003-160519896 | PLD003 | 0.014146 | 0.014274 | 0.014402 | 0.014531 | 0.014659 | 0.014258 | 0.013858 | 0.013457 | 0.013056 | 0.012655 | 0.012255 | 0.011854 | 0.011453 | 0.011053 | 0.010652 | 0.010251 | 0.0098505 | 0.0094498 | 0.0090491 | 0.0086484
| PLD003-160520056 | PLD003 | 0.0010978 | 0.0011085 | 0.0011192 | 0.00113 | 0.0011407 | 0.0011059 | 0.001071 | 0.0010362 | 0.0010013 | 0.00096645 | 0.0009316 | 0.00089675 | 0.0008619 | 0.00082705 | 0.0007922 | 0.00075735 | 0.0007225 | 0.00068765 | 0.0006528 | 0.00061795
| PLD003-160574293 | PLD003 | 0.12767 | 0.12888 | 0.1301 | 0.13131 | 0.13252 | 0.13017 | 0.12783 | 0.12548 | 0.12313 | 0.12078 | 0.11843 | 0.11609 | 0.11374 | 0.11139 | 0.10904 | 0.10669 | 0.10434 | 0.102 | 0.099649 | 0.0973
| PLD003-160574380 | PLD003 | 0.0019113 | 0.0019252 | 0.001939 | 0.0019528 | 0.0019666 | 0.0019389 | 0.0019112 | 0.0018836 | 0.0018559 | 0.0018282 | 0.0018005 | 0.0017728 | 0.0017452 | 0.0017175 | 0.0016898 | 0.0016621 | 0.0016344 | 0.0016068 | 0.0015791 | 0.0015514
| PLD003-160574486 | PLD003 | 0.021203 | 0.021423 | 0.021643 | 0.021863 | 0.022082 | 0.021675 | 0.021268 | 0.020861 | 0.020454 | 0.020047 | 0.01964 | 0.019233 | 0.018826 | 0.018419 | 0.018012 | 0.017605 | 0.017198 | 0.016791 | 0.016384 | 0.015977
| PLD003-160574588 | PLD003 | 0.029054 | 0.029302 | 0.02955 | 0.029797 | 0.030045 | 0.029274 | 0.028503 | 0.027732 | 0.026961 | 0.026191 | 0.02542 | 0.024649 | 0.023878 | 0.023107 | 0.022336 | 0.021565 | 0.020794 | 0.020023 | 0.019252 | 0.018481
| PLD003-162199489 | PLD003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-162199732 | PLD003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD003-162199939 | PLD003 | 0.00091829 | 0.00092677 | 0.00093525 | 0.00094372 | 0.0009522 | 0.00092598 | 0.00089976 | 0.00087354 | 0.00084732 | 0.0008211 | 0.00079488 | 0.00076866 | 0.00074244 | 0.00071622 | 0.00069 | 0.00066378 | 0.00063756 | 0.00061134 | 0.00058512 | 0.0005589
| PLD003-162260412 | PLD003 | 0.00049872 | 0.00050424 | 0.00050976 | 0.00051528 | 0.0005208 | 0.0005088 | 0.0004968 | 0.0004848 | 0.0004728 | 0.0004608 | 0.0004488 | 0.0004368 | 0.0004248 | 0.0004128 | 0.0004008 | 0.0003888 | 0.0003768 | 0.0003648 | 0.0003528 | 0.0003408
| PLD003-162378154 | PLD003 | 0.00071362 | 0.0007203 | 0.00072699 | 0.00073367 | 0.00074036 | 0.00071888 | 0.0006974 | 0.00067592 | 0.00065445 | 0.00063297 | 0.00061149 | 0.00059001 | 0.00056853 | 0.00054706 | 0.00052558 | 0.0005041 | 0.00048262 | 0.00046115 | 0.00043967 | 0.00041819
| PLD003-162378402 | PLD003 | 0.0013652 | 0.0013773 | 0.0013894 | 0.0014015 | 0.0014136 | 0.0013788 | 0.001344 | 0.0013093 | 0.0012745 | 0.0012397 | 0.0012049 | 0.0011701 | 0.0011354 | 0.0011006 | 0.0010658 | 0.001031 | 0.00099624 | 0.00096146 | 0.00092668 | 0.0008919
| PLD003-163610230 | PLD003 | 3.7706e-06 | 3.8254e-06 | 3.8803e-06 | 3.9351e-06 | 3.99e-06 | 3.8455e-06 | 3.7009e-06 | 3.5564e-06 | 3.4119e-06 | 3.2674e-06 | 3.1229e-06 | 2.9783e-06 | 2.8338e-06 | 2.6893e-06 | 2.5448e-06 | 2.4002e-06 | 2.2557e-06 | 2.1112e-06 | 1.9667e-06 | 1.8221e-06
| PLD003-163610492 | PLD003 | 0.013381 | 0.013511 | 0.013641 | 0.013771 | 0.013901 | 0.013631 | 0.01336 | 0.013089 | 0.012818 | 0.012547 | 0.012276 | 0.012005 | 0.011734 | 0.011463 | 0.011192 | 0.010921 | 0.01065 | 0.01038 | 0.010109 | 0.0098377
| PLD003-24597170 | PLD003 | 0.40494 | 0.40851 | 0.41209 | 0.41566 | 0.41924 | 0.4093 | 0.39935 | 0.38941 | 0.37946 | 0.36952 | 0.35957 | 0.34963 | 0.33968 | 0.32974 | 0.3198 | 0.30985 | 0.29991 | 0.28996 | 0.28002 | 0.27007
| PLD003-24597184 | PLD003 | 7.4278 | 7.4828 | 7.5378 | 7.5928 | 7.6478 | 7.5372 | 7.4267 | 7.3161 | 7.2055 | 7.095 | 6.9844 | 6.8738 | 6.7633 | 6.6527 | 6.5422 | 6.4316 | 6.321 | 6.2105 | 6.0999 | 5.9893
| PLD003-24605460 | PLD003 | 0.50618 | 0.51084 | 0.5155 | 0.52015 | 0.52481 | 0.51465 | 0.50448 | 0.49432 | 0.48415 | 0.47399 | 0.46382 | 0.45366 | 0.44349 | 0.43333 | 0.42317 | 0.413 | 0.40284 | 0.39267 | 0.38251 | 0.37234
| PLD004-121146862 | PLD004 | 3.3178 | 3.3483 | 3.3787 | 3.4091 | 3.4395 | 3.3737 | 3.3079 | 3.2421 | 3.1763 | 3.1105 | 3.0447 | 2.9789 | 2.9131 | 2.8473 | 2.7815 | 2.7157 | 2.65 | 2.5842 | 2.5184 | 2.4526
| PLD004-15398624 | PLD004 | 3.4688 | 3.5027 | 3.5365 | 3.5703 | 3.6041 | 3.5253 | 3.4464 | 3.3676 | 3.2888 | 3.2099 | 3.1311 | 3.0522 | 2.9734 | 2.8946 | 2.8157 | 2.7369 | 2.6581 | 2.5792 | 2.5004 | 2.4215
| PLD004-72962767 | PLD004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD005-15398737 | PLD005 | 0.68351 | 0.69031 | 0.6971 | 0.7039 | 0.7107 | 0.69487 | 0.67904 | 0.66321 | 0.64739 | 0.63156 | 0.61573 | 0.5999 | 0.58407 | 0.56824 | 0.55241 | 0.53659 | 0.52076 | 0.50493 | 0.4891 | 0.47327
| PLD005-15398783 | PLD005 | 2.0026e-06 | 2.0294e-06 | 2.0563e-06 | 2.0831e-06 | 2.11e-06 | 2.0358e-06 | 1.9615e-06 | 1.8873e-06 | 1.813e-06 | 1.7388e-06 | 1.6645e-06 | 1.5903e-06 | 1.516e-06 | 1.4418e-06 | 1.3675e-06 | 1.2933e-06 | 1.219e-06 | 1.1448e-06 | 1.0705e-06 | 9.9625e-07
| PLD006-15398587 | PLD006 | 6.9038 | 6.9674 | 7.0309 | 7.0945 | 7.1581 | 7.0144 | 6.8706 | 6.7269 | 6.5832 | 6.4394 | 6.2957 | 6.152 | 6.0083 | 5.8645 | 5.7208 | 5.5771 | 5.4334 | 5.2896 | 5.1459 | 5.0022
| PLD006-161891725 | PLD006 | 0.023666 | 0.02394 | 0.024215 | 0.024489 | 0.024764 | 0.024065 | 0.023366 | 0.022667 | 0.021968 | 0.021269 | 0.020571 | 0.019872 | 0.019173 | 0.018474 | 0.017775 | 0.017076 | 0.016378 | 0.015679 | 0.01498 | 0.014281
| PLD006-161892052 | PLD006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLD006-162198254 | PLD006 | 3.253e-08 | 3.2948e-08 | 3.3365e-08 | 3.3783e-08 | 3.42e-08 | 3.2979e-08 | 3.1758e-08 | 3.0537e-08 | 2.9316e-08 | 2.8095e-08 | 2.6874e-08 | 2.5653e-08 | 2.4432e-08 | 2.3211e-08 | 2.199e-08 | 2.0769e-08 | 1.9548e-08 | 1.8327e-08 | 1.7106e-08 | 1.5885e-08
| PLD006-162198466 | PLD006 | 0.0039933 | 0.0040107 | 0.0040282 | 0.0040457 | 0.0040632 | 0.0040437 | 0.0040243 | 0.0040048 | 0.0039853 | 0.0039659 | 0.0039464 | 0.0039269 | 0.0039074 | 0.003888 | 0.0038685 | 0.003849 | 0.0038296 | 0.0038101 | 0.0037906 | 0.0037712
| PLD006-162198656 | PLD006 | 0.015927 | 0.016106 | 0.016285 | 0.016464 | 0.016643 | 0.016226 | 0.01581 | 0.015393 | 0.014976 | 0.014559 | 0.014142 | 0.013725 | 0.013309 | 0.012892 | 0.012475 | 0.012058 | 0.011641 | 0.011224 | 0.010808 | 0.010391
| PLD006-162260039 | PLD006 | 5.1863e-05 | 5.2647e-05 | 5.3431e-05 | 5.4216e-05 | 5.5e-05 | 5.3215e-05 | 5.143e-05 | 4.9645e-05 | 4.786e-05 | 4.6075e-05 | 4.429e-05 | 4.2505e-05 | 4.072e-05 | 3.8935e-05 | 3.715e-05 | 3.5365e-05 | 3.358e-05 | 3.1795e-05 | 3.001e-05 | 2.8225e-05
| PLD006-162260159 | PLD006 | 0.0026231 | 0.0026564 | 0.0026897 | 0.0027229 | 0.0027562 | 0.0026808 | 0.0026053 | 0.0025298 | 0.0024544 | 0.0023789 | 0.0023034 | 0.0022279 | 0.0021525 | 0.002077 | 0.0020015 | 0.0019261 | 0.0018506 | 0.0017751 | 0.0016997 | 0.0016242
| PLD006-162260296 | PLD006 | 0.0048984 | 0.0049253 | 0.0049521 | 0.004979 | 0.0050058 | 0.0049494 | 0.0048929 | 0.0048365 | 0.00478 | 0.0047236 | 0.0046671 | 0.0046107 | 0.0045542 | 0.0044978 | 0.0044413 | 0.0043849 | 0.0043284 | 0.004272 | 0.0042155 | 0.0041591
| PLD006-202509382 | PLD006 | 5.3365 | 5.3502 | 5.3639 | 5.3775 | 5.3912 | 5.3626 | 5.334 | 5.3054 | 5.2768 | 5.2482 | 5.2196 | 5.191 | 5.1623 | 5.1337 | 5.1051 | 5.0765 | 5.0479 | 5.0193 | 4.9907 | 4.9621
| PLD006-24597156 | PLD006 | 1.1646 | 1.1765 | 1.1883 | 1.2001 | 1.2119 | 1.1831 | 1.1544 | 1.1256 | 1.0968 | 1.068 | 1.0392 | 1.0104 | 0.98165 | 0.95286 | 0.92408 | 0.89529 | 0.86651 | 0.83773 | 0.80894 | 0.78016
| RCT011-15430907 | RCT011 | 17.9993 | 18.1069 | 18.2144 | 18.322 | 18.4296 | 18.4444 | 18.4593 | 18.4741 | 18.489 | 18.5038 | 18.5187 | 18.5335 | 18.5484 | 18.5632 | 18.5781 | 18.5929 | 18.6078 | 18.6226 | 18.6375 | 18.6523
| RCT012-109224809 | RCT012 | 6.0094e-05 | 6.0546e-05 | 6.0997e-05 | 6.1449e-05 | 6.19e-05 | 6.2225e-05 | 6.255e-05 | 6.2875e-05 | 6.32e-05 | 6.3525e-05 | 6.385e-05 | 6.4175e-05 | 6.45e-05 | 6.4825e-05 | 6.515e-05 | 6.5475e-05 | 6.58e-05 | 6.6125e-05 | 6.645e-05 | 6.6775e-05
| RCT013-15430798 | RCT013 | 8.4806 | 8.5352 | 8.5898 | 8.6444 | 8.699 | 8.7128 | 8.7266 | 8.7404 | 8.7542 | 8.7681 | 8.7819 | 8.7957 | 8.8095 | 8.8233 | 8.8372 | 8.851 | 8.8648 | 8.8786 | 8.8924 | 8.9063
| RCT013-24605168 | RCT013 | 10.0572 | 10.1097 | 10.1622 | 10.2148 | 10.2673 | 10.2572 | 10.2471 | 10.237 | 10.2269 | 10.2168 | 10.2067 | 10.1966 | 10.1865 | 10.1764 | 10.1663 | 10.1562 | 10.1461 | 10.136 | 10.1259 | 10.1158
| RCT013-24605182 | RCT013 | 1.5936 | 1.596 | 1.5985 | 1.601 | 1.6034 | 1.6 | 1.5965 | 1.5931 | 1.5896 | 1.5862 | 1.5827 | 1.5793 | 1.5758 | 1.5723 | 1.5689 | 1.5654 | 1.562 | 1.5585 | 1.5551 | 1.5516
| RCT014-15430846 | RCT014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT014-24605126 | RCT014 | 0.0055913 | 0.0056304 | 0.0056695 | 0.0057086 | 0.0057477 | 0.0057584 | 0.0057691 | 0.0057798 | 0.0057905 | 0.0058012 | 0.005812 | 0.0058227 | 0.0058334 | 0.0058441 | 0.0058548 | 0.0058655 | 0.0058762 | 0.0058869 | 0.0058976 | 0.0059084
| RCT014-24611042 | RCT014 | 3.7814 | 3.8062 | 3.831 | 3.8558 | 3.8806 | 3.8869 | 3.8933 | 3.8996 | 3.9059 | 3.9122 | 3.9186 | 3.9249 | 3.9312 | 3.9376 | 3.9439 | 3.9502 | 3.9565 | 3.9629 | 3.9692 | 3.9755
| RCT015-15430944 | RCT015 | 0.054485 | 0.05489 | 0.055295 | 0.0557 | 0.056104 | 0.056323 | 0.056542 | 0.056761 | 0.05698 | 0.057199 | 0.057418 | 0.057637 | 0.057856 | 0.058074 | 0.058293 | 0.058512 | 0.058731 | 0.05895 | 0.059169 | 0.059388
| RCT021-15430691 | RCT021 | 5.1603 | 5.1958 | 5.2313 | 5.2668 | 5.3022 | 5.3161 | 5.33 | 5.3439 | 5.3578 | 5.3717 | 5.3856 | 5.3995 | 5.4134 | 5.4273 | 5.4412 | 5.4551 | 5.469 | 5.4829 | 5.4968 | 5.5107
| RCT021-24612845 | RCT021 | 0.081773 | 0.082282 | 0.08279 | 0.083299 | 0.083807 | 0.083957 | 0.084108 | 0.084258 | 0.084408 | 0.084558 | 0.084708 | 0.084859 | 0.085009 | 0.085159 | 0.085309 | 0.085459 | 0.08561 | 0.08576 | 0.08591 | 0.08606
| RCT022-109224755 | RCT022 | 5.6175 | 5.6517 | 5.6858 | 5.7199 | 5.754 | 5.7641 | 5.7741 | 5.7842 | 5.7943 | 5.8043 | 5.8144 | 5.8244 | 5.8345 | 5.8445 | 5.8546 | 5.8646 | 5.8747 | 5.8847 | 5.8948 | 5.9048
| RCT022-160254089 | RCT022 | 0.0036283 | 0.0036523 | 0.0036762 | 0.0037001 | 0.003724 | 0.0037324 | 0.0037409 | 0.0037493 | 0.0037577 | 0.0037661 | 0.0037745 | 0.003783 | 0.0037914 | 0.0037998 | 0.0038082 | 0.0038167 | 0.0038251 | 0.0038335 | 0.0038419 | 0.0038503
| RCT022-160254223 | RCT022 | 0.021793 | 0.021952 | 0.022111 | 0.02227 | 0.022429 | 0.022431 | 0.022432 | 0.022434 | 0.022435 | 0.022437 | 0.022438 | 0.02244 | 0.022441 | 0.022443 | 0.022444 | 0.022446 | 0.022447 | 0.022449 | 0.02245 | 0.022452
| RCT022-160652528 | RCT022 | 1.2617e-05 | 1.2692e-05 | 1.2766e-05 | 1.2841e-05 | 1.2915e-05 | 1.2948e-05 | 1.298e-05 | 1.3013e-05 | 1.3045e-05 | 1.3078e-05 | 1.311e-05 | 1.3143e-05 | 1.3175e-05 | 1.3208e-05 | 1.3241e-05 | 1.3273e-05 | 1.3306e-05 | 1.3338e-05 | 1.3371e-05 | 1.3403e-05
| RCT022-162765375 | RCT022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT022-187104623 | RCT022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT022-201142435 | RCT022 | 0.36781 | 0.36964 | 0.37147 | 0.3733 | 0.37513 | 0.37505 | 0.37497 | 0.37489 | 0.37481 | 0.37473 | 0.37464 | 0.37456 | 0.37448 | 0.3744 | 0.37432 | 0.37424 | 0.37416 | 0.37407 | 0.37399 | 0.37391
| RCT022-74940140 | RCT022 | 0.017635 | 0.01775 | 0.017865 | 0.01798 | 0.018095 | 0.018157 | 0.01822 | 0.018282 | 0.018345 | 0.018407 | 0.01847 | 0.018532 | 0.018595 | 0.018657 | 0.018719 | 0.018782 | 0.018844 | 0.018907 | 0.018969 | 0.019032
| RCT023-15430737 | RCT023 | 1.0513 | 1.0579 | 1.0644 | 1.071 | 1.0776 | 1.0797 | 1.0818 | 1.084 | 1.0861 | 1.0882 | 1.0904 | 1.0925 | 1.0946 | 1.0967 | 1.0989 | 1.101 | 1.1031 | 1.1053 | 1.1074 | 1.1095
| RCT023-159364712 | RCT023 | 0.003974 | 0.0039974 | 0.0040209 | 0.0040443 | 0.0040678 | 0.0040661 | 0.0040644 | 0.0040628 | 0.0040611 | 0.0040595 | 0.0040578 | 0.0040561 | 0.0040545 | 0.0040528 | 0.0040512 | 0.0040495 | 0.0040478 | 0.0040462 | 0.0040445 | 0.0040429
| RCT023-159364841 | RCT023 | 0.02072 | 0.020827 | 0.020935 | 0.021043 | 0.02115 | 0.021142 | 0.021135 | 0.021127 | 0.021119 | 0.021112 | 0.021104 | 0.021097 | 0.021089 | 0.021081 | 0.021074 | 0.021066 | 0.021058 | 0.021051 | 0.021043 | 0.021035
| RCT023-159364971 | RCT023 | 0.016804 | 0.016916 | 0.017029 | 0.017142 | 0.017254 | 0.017258 | 0.017262 | 0.017266 | 0.017269 | 0.017273 | 0.017277 | 0.017281 | 0.017285 | 0.017288 | 0.017292 | 0.017296 | 0.0173 | 0.017304 | 0.017308 | 0.017311
| RCT023-159365116 | RCT023 | 0.0015647 | 0.001575 | 0.0015853 | 0.0015956 | 0.0016059 | 0.0016055 | 0.0016052 | 0.0016049 | 0.0016046 | 0.0016043 | 0.001604 | 0.0016037 | 0.0016033 | 0.001603 | 0.0016027 | 0.0016024 | 0.0016021 | 0.0016018 | 0.0016014 | 0.0016011
| RCT023-159365240 | RCT023 | 0.00044509 | 0.00044767 | 0.00045025 | 0.00045282 | 0.0004554 | 0.00045562 | 0.00045584 | 0.00045606 | 0.00045628 | 0.0004565 | 0.00045672 | 0.00045694 | 0.00045716 | 0.00045738 | 0.0004576 | 0.00045782 | 0.00045804 | 0.00045826 | 0.00045848 | 0.0004587
| RCT023-159365351 | RCT023 | 0.0023996 | 0.0024135 | 0.0024273 | 0.0024412 | 0.002455 | 0.0024517 | 0.0024483 | 0.0024449 | 0.0024416 | 0.0024382 | 0.0024348 | 0.0024314 | 0.0024281 | 0.0024247 | 0.0024213 | 0.0024179 | 0.0024146 | 0.0024112 | 0.0024078 | 0.0024045
| RCT023-159365509 | RCT023 | 1.6285e-06 | 1.6399e-06 | 1.6513e-06 | 1.6626e-06 | 1.674e-06 | 1.6797e-06 | 1.6854e-06 | 1.6911e-06 | 1.6968e-06 | 1.7025e-06 | 1.7082e-06 | 1.7139e-06 | 1.7196e-06 | 1.7253e-06 | 1.731e-06 | 1.7367e-06 | 1.7424e-06 | 1.7481e-06 | 1.7538e-06 | 1.7595e-06
| RCT023-160652906 | RCT023 | 0.0018487 | 0.001861 | 0.0018732 | 0.0018855 | 0.0018978 | 0.001897 | 0.0018962 | 0.0018955 | 0.0018947 | 0.001894 | 0.0018932 | 0.0018925 | 0.0018917 | 0.001891 | 0.0018902 | 0.0018895 | 0.0018887 | 0.001888 | 0.0018872 | 0.0018865
| RCT023-162905845 | RCT023 | 0.051598 | 0.051929 | 0.05226 | 0.05259 | 0.052921 | 0.052938 | 0.052956 | 0.052974 | 0.052992 | 0.053009 | 0.053027 | 0.053045 | 0.053062 | 0.05308 | 0.053098 | 0.053115 | 0.053133 | 0.053151 | 0.053169 | 0.053186
| RCT023-162905960 | RCT023 | 0.0011439 | 0.0011519 | 0.0011599 | 0.0011679 | 0.0011759 | 0.0011745 | 0.0011731 | 0.0011717 | 0.0011703 | 0.001169 | 0.0011676 | 0.0011662 | 0.0011648 | 0.0011635 | 0.0011621 | 0.0011607 | 0.0011593 | 0.001158 | 0.0011566 | 0.0011552
| RCT023-162906075 | RCT023 | 0.048675 | 0.048986 | 0.049297 | 0.049608 | 0.049919 | 0.049949 | 0.049979 | 0.050009 | 0.050039 | 0.050069 | 0.050098 | 0.050128 | 0.050158 | 0.050188 | 0.050218 | 0.050248 | 0.050278 | 0.050307 | 0.050337 | 0.050367
| RCT023-24605614 | RCT023 | 0.7496 | 0.75414 | 0.75869 | 0.76324 | 0.76779 | 0.76889 | 0.76998 | 0.77107 | 0.77217 | 0.77326 | 0.77435 | 0.77545 | 0.77654 | 0.77764 | 0.77873 | 0.77982 | 0.78092 | 0.78201 | 0.7831 | 0.7842
| RCT023-24605628 | RCT023 | 1.0162 | 1.0229 | 1.0297 | 1.0365 | 1.0432 | 1.0456 | 1.048 | 1.0504 | 1.0529 | 1.0553 | 1.0577 | 1.0601 | 1.0625 | 1.0649 | 1.0673 | 1.0697 | 1.0721 | 1.0745 | 1.0769 | 1.0793
| RCT023-24606802 | RCT023 | 0.92023 | 0.92495 | 0.92968 | 0.93441 | 0.93913 | 0.93845 | 0.93776 | 0.93708 | 0.93639 | 0.9357 | 0.93502 | 0.93433 | 0.93365 | 0.93296 | 0.93227 | 0.93159 | 0.9309 | 0.93022 | 0.92953 | 0.92884
| RCT023-24611339 | RCT023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RCT023-85530600 | RCT023 | 0.022161 | 0.022299 | 0.022437 | 0.022574 | 0.022712 | 0.022769 | 0.022826 | 0.022884 | 0.022941 | 0.022998 | 0.023055 | 0.023112 | 0.023169 | 0.023226 | 0.023284 | 0.023341 | 0.023398 | 0.023455 | 0.023512 | 0.023569
| RVL001-15418899 | RVL001 | 6.5257e-05 | 6.5843e-05 | 6.6429e-05 | 6.7014e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05
| RVL001-15418912 | RVL001 | 11.9531 | 12.0376 | 12.1221 | 12.2066 | 12.2911 | 12.27 | 12.2489 | 12.2277 | 12.2066 | 12.1855 | 12.1644 | 12.1433 | 12.1222 | 12.1011 | 12.08 | 12.0589 | 12.0378 | 12.0167 | 11.9956 | 11.9745
| RVL004-15418812 | RVL004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RVL004-15418838 | RVL004 | 2.1817 | 2.1949 | 2.2081 | 2.2213 | 2.2345 | 2.2294 | 2.2244 | 2.2193 | 2.2143 | 2.2092 | 2.2042 | 2.1991 | 2.1941 | 2.189 | 2.184 | 2.1789 | 2.1739 | 2.1688 | 2.1638 | 2.1587
| RVL004-162771521 | RVL004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RVL006-15418762 | RVL006 | 2.5177 | 2.5338 | 2.5499 | 2.566 | 2.5821 | 2.5773 | 2.5725 | 2.5677 | 2.5629 | 2.5581 | 2.5533 | 2.5484 | 2.5436 | 2.5388 | 2.534 | 2.5292 | 2.5244 | 2.5196 | 2.5147 | 2.5099
| RVL008-15418862 | RVL008 | 0.46027 | 0.4639 | 0.46753 | 0.47116 | 0.47479 | 0.47458 | 0.47437 | 0.47416 | 0.47395 | 0.47374 | 0.47353 | 0.47332 | 0.47311 | 0.4729 | 0.47269 | 0.47248 | 0.47227 | 0.47206 | 0.47184 | 0.47163
| RVL008-24613925 | RVL008 | 1.1356 | 1.1444 | 1.1531 | 1.1619 | 1.1707 | 1.1701 | 1.1695 | 1.1689 | 1.1683 | 1.1678 | 1.1672 | 1.1666 | 1.166 | 1.1654 | 1.1648 | 1.1643 | 1.1637 | 1.1631 | 1.1625 | 1.1619
| SA001-15410791 | SA001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA001-15410802 | SA001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA001-15411152 | SA001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA002-15410828 | SA002 | 0.14115 | 0.14224 | 0.14333 | 0.14442 | 0.14551 | 0.14566 | 0.14581 | 0.14596 | 0.1461 | 0.14625 | 0.1464 | 0.14654 | 0.14669 | 0.14684 | 0.14698 | 0.14713 | 0.14728 | 0.14742 | 0.14757 | 0.14772
| SA002-24612976 | SA002 | 0.095933 | 0.096663 | 0.097394 | 0.098124 | 0.098855 | 0.09896 | 0.099065 | 0.099171 | 0.099276 | 0.099381 | 0.099486 | 0.099591 | 0.099696 | 0.099802 | 0.099907 | 0.10001 | 0.10012 | 0.10022 | 0.10033 | 0.10043
| SA003-15410891 | SA003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA003-24613059 | SA003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA004-15410928 | SA004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA005-15411004 | SA005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA005-24614201 | SA005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA006-15411054 | SA006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA006-24612920 | SA006 | 1.4606 | 1.4735 | 1.4863 | 1.4992 | 1.5121 | 1.5116 | 1.5112 | 1.5108 | 1.5104 | 1.5099 | 1.5095 | 1.5091 | 1.5087 | 1.5082 | 1.5078 | 1.5074 | 1.5069 | 1.5065 | 1.5061 | 1.5057
| SA007-111739222 | SA007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA007-15411091 | SA007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA009-15436559 | SA009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA009-15436572 | SA009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA009-76846685 | SA009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA010-15436583 | SA010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA010-24613811 | SA010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SA011-15436594 | SA011 | 21.2328 | 21.3794 | 21.5259 | 21.6725 | 21.819 | 21.8615 | 21.904 | 21.9465 | 21.989 | 22.0315 | 22.074 | 22.1165 | 22.159 | 22.2015 | 22.244 | 22.2865 | 22.329 | 22.3715 | 22.414 | 22.4565
| SA012-15437079 | SA012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-15428689 | SHL001 | 5.1565 | 5.2038 | 5.2511 | 5.2983 | 5.3456 | 5.3697 | 5.3938 | 5.4178 | 5.4419 | 5.466 | 5.4901 | 5.5142 | 5.5383 | 5.5623 | 5.5864 | 5.6105 | 5.6346 | 5.6587 | 5.6828 | 5.7069
| SHL001-155492469 | SHL001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-160435720 | SHL001 | 0.038435 | 0.03877 | 0.039104 | 0.039439 | 0.039774 | 0.039949 | 0.040125 | 0.0403 | 0.040476 | 0.040651 | 0.040827 | 0.041002 | 0.041178 | 0.041354 | 0.041529 | 0.041705 | 0.04188 | 0.042056 | 0.042231 | 0.042407
| SHL001-160435873 | SHL001 | 0.1666 | 0.16803 | 0.16945 | 0.17087 | 0.17229 | 0.17319 | 0.17409 | 0.17499 | 0.17589 | 0.17679 | 0.17769 | 0.17859 | 0.17949 | 0.18039 | 0.18129 | 0.18219 | 0.1831 | 0.184 | 0.1849 | 0.1858
| SHL001-160436010 | SHL001 | 0.14706 | 0.14853 | 0.15 | 0.15148 | 0.15295 | 0.15365 | 0.15434 | 0.15504 | 0.15574 | 0.15644 | 0.15714 | 0.15784 | 0.15854 | 0.15924 | 0.15994 | 0.16063 | 0.16133 | 0.16203 | 0.16273 | 0.16343
| SHL001-160450736 | SHL001 | 0.00033358 | 0.00033674 | 0.00033989 | 0.00034305 | 0.0003462 | 0.00034683 | 0.00034746 | 0.00034809 | 0.00034872 | 0.00034935 | 0.00034998 | 0.00035061 | 0.00035124 | 0.00035187 | 0.0003525 | 0.00035313 | 0.00035376 | 0.00035439 | 0.00035502 | 0.00035565
| SHL001-160450820 | SHL001 | 0.0024001 | 0.0024234 | 0.0024467 | 0.00247 | 0.0024933 | 0.0024964 | 0.0024995 | 0.0025026 | 0.0025056 | 0.0025087 | 0.0025118 | 0.0025149 | 0.002518 | 0.0025211 | 0.0025242 | 0.0025273 | 0.0025304 | 0.0025335 | 0.0025366 | 0.0025396
| SHL001-160491672 | SHL001 | 0.053306 | 0.053326 | 0.053345 | 0.053365 | 0.053384 | 0.053369 | 0.053354 | 0.053339 | 0.053324 | 0.053308 | 0.053293 | 0.053278 | 0.053263 | 0.053248 | 0.053232 | 0.053217 | 0.053202 | 0.053187 | 0.053172 | 0.053156
| SHL001-160682032 | SHL001 | 0.045042 | 0.04542 | 0.045798 | 0.046176 | 0.046553 | 0.046786 | 0.047019 | 0.047252 | 0.047484 | 0.047717 | 0.04795 | 0.048183 | 0.048415 | 0.048648 | 0.048881 | 0.049114 | 0.049346 | 0.049579 | 0.049812 | 0.050045
| SHL001-162130935 | SHL001 | 0.00012428 | 0.00012538 | 0.00012649 | 0.00012759 | 0.0001287 | 0.00012939 | 0.00013008 | 0.00013077 | 0.00013146 | 0.00013215 | 0.00013284 | 0.00013353 | 0.00013422 | 0.00013491 | 0.0001356 | 0.00013629 | 0.00013698 | 0.00013767 | 0.00013836 | 0.00013905
| SHL001-162641927 | SHL001 | 0.00022535 | 0.00022761 | 0.00022987 | 0.00023214 | 0.0002344 | 0.00023504 | 0.00023568 | 0.00023632 | 0.00023696 | 0.0002376 | 0.00023824 | 0.00023888 | 0.00023952 | 0.00024016 | 0.0002408 | 0.00024144 | 0.00024208 | 0.00024272 | 0.00024336 | 0.000244
| SHL001-162662602 | SHL001 | 0.036518 | 0.036835 | 0.037152 | 0.037468 | 0.037785 | 0.037967 | 0.038149 | 0.038331 | 0.038513 | 0.038695 | 0.038877 | 0.039059 | 0.039241 | 0.039423 | 0.039605 | 0.039787 | 0.039969 | 0.040151 | 0.040333 | 0.040515
| SHL001-162662856 | SHL001 | 0.089098 | 0.089939 | 0.09078 | 0.091622 | 0.092463 | 0.092651 | 0.092839 | 0.093027 | 0.093215 | 0.093403 | 0.093591 | 0.093779 | 0.093967 | 0.094155 | 0.094343 | 0.094531 | 0.094719 | 0.094907 | 0.095095 | 0.095283
| SHL001-162663030 | SHL001 | 0.013226 | 0.013348 | 0.013469 | 0.013591 | 0.013712 | 0.01375 | 0.013787 | 0.013824 | 0.013861 | 0.013898 | 0.013935 | 0.013973 | 0.01401 | 0.014047 | 0.014084 | 0.014121 | 0.014158 | 0.014196 | 0.014233 | 0.01427
| SHL001-162760066 | SHL001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL002-15428854 | SHL002 | 3.9279 | 3.9594 | 3.9909 | 4.0224 | 4.054 | 4.0639 | 4.0738 | 4.0837 | 4.0936 | 4.1035 | 4.1134 | 4.1234 | 4.1333 | 4.1432 | 4.1531 | 4.163 | 4.1729 | 4.1829 | 4.1928 | 4.2027
| SHL002-160491442 | SHL002 | 0.0096716 | 0.0097587 | 0.0098458 | 0.0099328 | 0.01002 | 0.010023 | 0.010026 | 0.010029 | 0.010032 | 0.010035 | 0.010038 | 0.010041 | 0.010044 | 0.010047 | 0.010049 | 0.010052 | 0.010055 | 0.010058 | 0.010061 | 0.010064
| SHL002-160491563 | SHL002 | 0.0069521 | 0.0070154 | 0.0070788 | 0.0071421 | 0.0072055 | 0.0072168 | 0.0072281 | 0.0072394 | 0.0072507 | 0.007262 | 0.0072733 | 0.0072846 | 0.0072959 | 0.0073071 | 0.0073184 | 0.0073297 | 0.007341 | 0.0073523 | 0.0073636 | 0.0073749
| SHL002-161866668 | SHL002 | 0.011433 | 0.01154 | 0.011648 | 0.011755 | 0.011863 | 0.011884 | 0.011906 | 0.011928 | 0.011949 | 0.011971 | 0.011993 | 0.012014 | 0.012036 | 0.012057 | 0.012079 | 0.012101 | 0.012122 | 0.012144 | 0.012165 | 0.012187
| SHL002-162436238 | SHL002 | 0.00050214 | 0.00050686 | 0.00051157 | 0.00051629 | 0.000521 | 0.0005219 | 0.0005228 | 0.0005237 | 0.0005246 | 0.0005255 | 0.0005264 | 0.0005273 | 0.0005282 | 0.0005291 | 0.00053 | 0.0005309 | 0.0005318 | 0.0005327 | 0.0005336 | 0.0005345
| SHL002-162436334 | SHL002 | 0.0044089 | 0.0044466 | 0.0044844 | 0.0045222 | 0.0045599 | 0.0045674 | 0.0045749 | 0.0045824 | 0.0045899 | 0.0045974 | 0.0046049 | 0.0046124 | 0.00462 | 0.0046275 | 0.004635 | 0.0046425 | 0.00465 | 0.0046575 | 0.004665 | 0.0046725
| SHL002-162436442 | SHL002 | 0.00031445 | 0.0003174 | 0.00032034 | 0.00032328 | 0.00032623 | 0.00032601 | 0.0003258 | 0.00032558 | 0.00032537 | 0.00032515 | 0.00032494 | 0.00032472 | 0.00032451 | 0.0003243 | 0.00032408 | 0.00032387 | 0.00032365 | 0.00032344 | 0.00032322 | 0.00032301
| SHL002-162485158 | SHL002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL002-24604026 | SHL002 | 11.7285 | 11.8276 | 11.9267 | 12.0258 | 12.1249 | 12.1467 | 12.1685 | 12.1903 | 12.2121 | 12.2339 | 12.2557 | 12.2775 | 12.2993 | 12.3211 | 12.3429 | 12.3647 | 12.3865 | 12.4083 | 12.4301 | 12.4519
| SHL002-24604040 | SHL002 | 1.8144 | 1.8288 | 1.8432 | 1.8575 | 1.8719 | 1.8731 | 1.8742 | 1.8754 | 1.8765 | 1.8777 | 1.8788 | 1.88 | 1.8811 | 1.8823 | 1.8834 | 1.8846 | 1.8857 | 1.8868 | 1.888 | 1.8891
| SHL002-24614570 | SHL002 | 4.2051 | 4.2272 | 4.2493 | 4.2714 | 4.2935 | 4.2852 | 4.2769 | 4.2686 | 4.2603 | 4.252 | 4.2437 | 4.2354 | 4.2271 | 4.2188 | 4.2105 | 4.2022 | 4.1939 | 4.1855 | 4.1772 | 4.1689
| SHL002-42163201 | SHL002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL002-54520142 | SHL002 | 0.25346 | 0.25354 | 0.25361 | 0.25369 | 0.25376 | 0.25371 | 0.25365 | 0.25359 | 0.25353 | 0.25347 | 0.25341 | 0.25335 | 0.2533 | 0.25324 | 0.25318 | 0.25312 | 0.25306 | 0.253 | 0.25294 | 0.25289
| SHL004-15428865 | SHL004 | 5.8017 | 5.8514 | 5.901 | 5.9506 | 6.0003 | 6.0189 | 6.0375 | 6.0561 | 6.0747 | 6.0934 | 6.112 | 6.1306 | 6.1492 | 6.1679 | 6.1865 | 6.2051 | 6.2237 | 6.2424 | 6.261 | 6.2796
| SHL004-24604082 | SHL004 | 12.548 | 12.665 | 12.782 | 12.899 | 13.016 | 13.0206 | 13.0253 | 13.03 | 13.0347 | 13.0394 | 13.044 | 13.0487 | 13.0534 | 13.0581 | 13.0628 | 13.0674 | 13.0721 | 13.0768 | 13.0815 | 13.0861
| SHL004-24612892 | SHL004 | 5.9086 | 5.9562 | 6.0038 | 6.0514 | 6.099 | 6.1048 | 6.1106 | 6.1165 | 6.1223 | 6.1281 | 6.1339 | 6.1397 | 6.1455 | 6.1513 | 6.1571 | 6.1629 | 6.1687 | 6.1745 | 6.1803 | 6.1861
| SHL005-15428600 | SHL005 | 0.0027172 | 0.0027421 | 0.0027669 | 0.0027918 | 0.0028166 | 0.0028295 | 0.0028423 | 0.0028552 | 0.002868 | 0.0028809 | 0.0028937 | 0.0029065 | 0.0029194 | 0.0029322 | 0.0029451 | 0.0029579 | 0.0029708 | 0.0029836 | 0.0029965 | 0.0030093
| SHL005-15428613 | SHL005 | 12.1134 | 12.2082 | 12.3031 | 12.398 | 12.4929 | 12.5358 | 12.5787 | 12.6216 | 12.6645 | 12.7074 | 12.7503 | 12.7931 | 12.836 | 12.8789 | 12.9218 | 12.9647 | 13.0076 | 13.0505 | 13.0934 | 13.1363
| SHL005-15428624 | SHL005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL005-24604390 | SHL005 | 3.1709 | 3.1969 | 3.2229 | 3.2489 | 3.2749 | 3.2853 | 3.2957 | 3.3061 | 3.3165 | 3.327 | 3.3374 | 3.3478 | 3.3582 | 3.3686 | 3.379 | 3.3894 | 3.3998 | 3.4102 | 3.4207 | 3.4311
| SHL005-24613604 | SHL005 | 2.3804 | 2.4003 | 2.4202 | 2.4401 | 2.46 | 2.471 | 2.482 | 2.493 | 2.504 | 2.515 | 2.5261 | 2.5371 | 2.5481 | 2.5591 | 2.5701 | 2.5811 | 2.5921 | 2.6031 | 2.6141 | 2.6252
| SHL007-15428576 | SHL007 | 0.81156 | 0.81956 | 0.82757 | 0.83558 | 0.84359 | 0.84557 | 0.84755 | 0.84953 | 0.85151 | 0.85349 | 0.85548 | 0.85746 | 0.85944 | 0.86142 | 0.8634 | 0.86538 | 0.86736 | 0.86935 | 0.87133 | 0.87331
| SHL007-181581220 | SHL007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHL008-15428954 | SHL008 | 0.31074 | 0.31359 | 0.31644 | 0.31928 | 0.32213 | 0.32359 | 0.32506 | 0.32653 | 0.328 | 0.32946 | 0.33093 | 0.3324 | 0.33387 | 0.33533 | 0.3368 | 0.33827 | 0.33974 | 0.3412 | 0.34267 | 0.34414
| SHL008-181581109 | SHL008 | 7.3688 | 7.4349 | 7.501 | 7.5671 | 7.6332 | 7.6657 | 7.6982 | 7.7307 | 7.7632 | 7.7957 | 7.8282 | 7.8607 | 7.8932 | 7.9257 | 7.9582 | 7.9907 | 8.0232 | 8.0557 | 8.0882 | 8.1207
| SHN011-130746986 | SHN011 | 0.00035581 | 0.00035968 | 0.00036355 | 0.00036741 | 0.00037128 | 0.00037456 | 0.00037783 | 0.00038111 | 0.00038438 | 0.00038766 | 0.00039094 | 0.00039421 | 0.00039749 | 0.00040076 | 0.00040404 | 0.00040732 | 0.00041059 | 0.00041387 | 0.00041714 | 0.00042042
| SHN011-175612776 | SHN011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN011-200057131 | SHN011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN011-24605252 | SHN011 | 22.1274 | 22.2606 | 22.3938 | 22.527 | 22.6602 | 22.7855 | 22.9108 | 23.0362 | 23.1615 | 23.2869 | 23.4122 | 23.5375 | 23.6629 | 23.7882 | 23.9136 | 24.0389 | 24.1642 | 24.2896 | 24.4149 | 24.5403
| SHN011-95830821 | SHN011 | 0.00040073 | 0.00040293 | 0.00040512 | 0.00040731 | 0.0004095 | 0.00041145 | 0.0004134 | 0.00041535 | 0.0004173 | 0.00041925 | 0.0004212 | 0.00042315 | 0.0004251 | 0.00042705 | 0.000429 | 0.00043095 | 0.0004329 | 0.00043485 | 0.0004368 | 0.00043875
| SHN012-200057355 | SHN012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN012-24613290 | SHN012 | 3.7218 | 3.7453 | 3.7689 | 3.7924 | 3.816 | 3.8432 | 3.8704 | 3.8976 | 3.9248 | 3.952 | 3.9792 | 4.0064 | 4.0336 | 4.0608 | 4.088 | 4.1152 | 4.1424 | 4.1696 | 4.1968 | 4.224
| SHN014-15423299 | SHN014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN014-200219171 | SHN014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN021-15423325 | SHN021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN021-200219341 | SHN021 | 51.5238 | 51.7391 | 51.9545 | 52.1699 | 52.3853 | 52.4873 | 52.5894 | 52.6914 | 52.7935 | 52.8955 | 52.9976 | 53.0996 | 53.2017 | 53.3037 | 53.4057 | 53.5078 | 53.6098 | 53.7119 | 53.8139 | 53.916
| SHN022-200219453 | SHN022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHN023-200219561 | SHN023 | 0.50556 | 0.5084 | 0.51124 | 0.51408 | 0.51692 | 0.51795 | 0.51898 | 0.52001 | 0.52104 | 0.52207 | 0.52309 | 0.52412 | 0.52515 | 0.52618 | 0.52721 | 0.52824 | 0.52927 | 0.5303 | 0.53133 | 0.53236
| SHN024-159278517 | SHN024 | 8.9759e-05 | 9.0377e-05 | 9.0995e-05 | 9.1612e-05 | 9.223e-05 | 9.338e-05 | 9.453e-05 | 9.568e-05 | 9.683e-05 | 9.798e-05 | 9.913e-05 | 0.00010028 | 0.00010143 | 0.00010258 | 0.00010373 | 0.00010488 | 0.00010603 | 0.00010718 | 0.00010833 | 0.00010948
| SHN024-160253686 | SHN024 | 4.9817e-06 | 5.0263e-06 | 5.0709e-06 | 5.1154e-06 | 5.16e-06 | 5.2095e-06 | 5.259e-06 | 5.3085e-06 | 5.358e-06 | 5.4075e-06 | 5.457e-06 | 5.5065e-06 | 5.556e-06 | 5.6055e-06 | 5.655e-06 | 5.7045e-06 | 5.754e-06 | 5.8035e-06 | 5.853e-06 | 5.9025e-06
| SHN024-164487380 | SHN024 | 1.5687e-05 | 1.5816e-05 | 1.5944e-05 | 1.6072e-05 | 1.62e-05 | 1.6365e-05 | 1.653e-05 | 1.6695e-05 | 1.686e-05 | 1.7025e-05 | 1.719e-05 | 1.7355e-05 | 1.752e-05 | 1.7685e-05 | 1.785e-05 | 1.8015e-05 | 1.818e-05 | 1.8345e-05 | 1.851e-05 | 1.8675e-05
| SHN024-200219667 | SHN024 | 0.97048 | 0.97549 | 0.9805 | 0.9855 | 0.99051 | 0.99739 | 1.0043 | 1.0112 | 1.018 | 1.0249 | 1.0318 | 1.0387 | 1.0456 | 1.0525 | 1.0593 | 1.0662 | 1.0731 | 1.08 | 1.0869 | 1.0938
| SHN024-24605390 | SHN024 | 0.85573 | 0.86135 | 0.86698 | 0.87261 | 0.87824 | 0.88529 | 0.89234 | 0.8994 | 0.90645 | 0.91351 | 0.92056 | 0.92761 | 0.93467 | 0.94172 | 0.94877 | 0.95583 | 0.96288 | 0.96993 | 0.97699 | 0.98404
| SHP011-15432563 | SHP011 | 1.0881 | 1.092 | 1.0958 | 1.0997 | 1.1035 | 1.1058 | 1.108 | 1.1103 | 1.1125 | 1.1148 | 1.117 | 1.1192 | 1.1215 | 1.1237 | 1.126 | 1.1282 | 1.1305 | 1.1327 | 1.1349 | 1.1372
| SHP011-164003814 | SHP011 | 0.00026835 | 0.00027057 | 0.00027278 | 0.00027499 | 0.0002772 | 0.00028035 | 0.0002835 | 0.00028665 | 0.0002898 | 0.00029295 | 0.0002961 | 0.00029925 | 0.0003024 | 0.00030555 | 0.0003087 | 0.00031185 | 0.000315 | 0.00031815 | 0.0003213 | 0.00032445
| SHP011-24602590 | SHP011 | 1.4087 | 1.4175 | 1.4263 | 1.4352 | 1.444 | 1.4546 | 1.4652 | 1.4759 | 1.4865 | 1.4971 | 1.5077 | 1.5184 | 1.529 | 1.5396 | 1.5502 | 1.5609 | 1.5715 | 1.5821 | 1.5927 | 1.6034
| SHP012-153588795 | SHP012 | 0.43292 | 0.43556 | 0.4382 | 0.44083 | 0.44347 | 0.44724 | 0.451 | 0.45477 | 0.45854 | 0.4623 | 0.46607 | 0.46984 | 0.4736 | 0.47737 | 0.48114 | 0.4849 | 0.48867 | 0.49244 | 0.4962 | 0.49997
| SHP012-15432576 | SHP012 | 31.9051 | 32.1065 | 32.3078 | 32.5092 | 32.7105 | 32.9286 | 33.1467 | 33.3648 | 33.5829 | 33.8009 | 34.019 | 34.2371 | 34.4552 | 34.6733 | 34.8914 | 35.1095 | 35.3276 | 35.5457 | 35.7637 | 35.9818
| SHP012-160253286 | SHP012 | 4.9765e-05 | 5.0081e-05 | 5.0397e-05 | 5.0714e-05 | 5.103e-05 | 5.1642e-05 | 5.2254e-05 | 5.2866e-05 | 5.3478e-05 | 5.409e-05 | 5.4702e-05 | 5.5314e-05 | 5.5926e-05 | 5.6538e-05 | 5.715e-05 | 5.7762e-05 | 5.8374e-05 | 5.8986e-05 | 5.9598e-05 | 6.021e-05
| SHP012-160253407 | SHP012 | 0.00054964 | 0.00055466 | 0.00055967 | 0.00056469 | 0.0005697 | 0.00057375 | 0.0005778 | 0.00058185 | 0.0005859 | 0.00058995 | 0.000594 | 0.00059805 | 0.0006021 | 0.00060615 | 0.0006102 | 0.00061425 | 0.0006183 | 0.00062235 | 0.0006264 | 0.00063045
| SHP012-160253550 | SHP012 | 0.00041284 | 0.00041656 | 0.00042027 | 0.00042399 | 0.0004277 | 0.00042932 | 0.00043095 | 0.00043258 | 0.0004342 | 0.00043583 | 0.00043745 | 0.00043908 | 0.0004407 | 0.00044233 | 0.00044395 | 0.00044558 | 0.0004472 | 0.00044883 | 0.00045045 | 0.00045208
| SHP012-163378080 | SHP012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP012-164366336 | SHP012 | 6.8894e-05 | 6.937e-05 | 6.9847e-05 | 7.0323e-05 | 7.08e-05 | 7.161e-05 | 7.242e-05 | 7.323e-05 | 7.404e-05 | 7.485e-05 | 7.566e-05 | 7.647e-05 | 7.728e-05 | 7.809e-05 | 7.89e-05 | 7.971e-05 | 8.052e-05 | 8.133e-05 | 8.214e-05 | 8.295e-05
| SHP012-24603174 | SHP012 | 2.1694 | 2.183 | 2.1966 | 2.2101 | 2.2237 | 2.2371 | 2.2504 | 2.2638 | 2.2772 | 2.2905 | 2.3039 | 2.3172 | 2.3306 | 2.344 | 2.3573 | 2.3707 | 2.384 | 2.3974 | 2.4108 | 2.4241
| SHP012-24612048 | SHP012 | 9.2632 | 9.3147 | 9.3662 | 9.4178 | 9.4693 | 9.5441 | 9.6189 | 9.6937 | 9.7685 | 9.8433 | 9.9181 | 9.993 | 10.0678 | 10.1426 | 10.2174 | 10.2922 | 10.367 | 10.4418 | 10.5166 | 10.5914
| SHP014-15432602 | SHP014 | 3.6972 | 3.7176 | 3.7381 | 3.7585 | 3.779 | 3.808 | 3.837 | 3.866 | 3.895 | 3.924 | 3.953 | 3.982 | 4.011 | 4.04 | 4.069 | 4.098 | 4.127 | 4.1559 | 4.1849 | 4.2139
| SHP014-164366107 | SHP014 | 0.011733 | 0.011814 | 0.011894 | 0.011974 | 0.012055 | 0.012149 | 0.012243 | 0.012337 | 0.012431 | 0.012526 | 0.01262 | 0.012714 | 0.012808 | 0.012902 | 0.012996 | 0.013091 | 0.013185 | 0.013279 | 0.013373 | 0.013467
| SHP014-177037469 | SHP014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP014-24602550 | SHP014 | 32.2263 | 32.3916 | 32.557 | 32.7224 | 32.8878 | 33.1043 | 33.3209 | 33.5375 | 33.754 | 33.9706 | 34.1871 | 34.4037 | 34.6203 | 34.8368 | 35.0534 | 35.2699 | 35.4865 | 35.7031 | 35.9196 | 36.1362
| SHP014-24602854 | SHP014 | 0.14921 | 0.14994 | 0.15067 | 0.1514 | 0.15213 | 0.15371 | 0.1553 | 0.15689 | 0.15847 | 0.16006 | 0.16165 | 0.16323 | 0.16482 | 0.16641 | 0.16799 | 0.16958 | 0.17117 | 0.17275 | 0.17434 | 0.17592
| SHP014-24602868 | SHP014 | 0.5798 | 0.58341 | 0.58702 | 0.59063 | 0.59424 | 0.60119 | 0.60814 | 0.61509 | 0.62204 | 0.629 | 0.63595 | 0.6429 | 0.64985 | 0.6568 | 0.66375 | 0.6707 | 0.67765 | 0.6846 | 0.69155 | 0.6985
| SHP021-120932535 | SHP021 | 0.0024605 | 0.0024754 | 0.0024902 | 0.0025051 | 0.00252 | 0.0025329 | 0.0025458 | 0.0025586 | 0.0025715 | 0.0025844 | 0.0025973 | 0.0026102 | 0.002623 | 0.0026359 | 0.0026488 | 0.0026617 | 0.0026746 | 0.0026874 | 0.0027003 | 0.0027132
| SHP021-129439859 | SHP021 | 0.0011193 | 0.0011291 | 0.0011389 | 0.0011487 | 0.0011585 | 0.0011639 | 0.0011693 | 0.0011748 | 0.0011802 | 0.0011856 | 0.001191 | 0.0011965 | 0.0012019 | 0.0012073 | 0.0012127 | 0.0012182 | 0.0012236 | 0.001229 | 0.0012345 | 0.0012399
| SHP021-134953488 | SHP021 | 0.063507 | 0.06399 | 0.064473 | 0.064956 | 0.06544 | 0.06577 | 0.066101 | 0.066432 | 0.066763 | 0.067094 | 0.067425 | 0.067756 | 0.068086 | 0.068417 | 0.068748 | 0.069079 | 0.06941 | 0.069741 | 0.070072 | 0.070403
| SHP021-134953623 | SHP021 | 0.21019 | 0.21159 | 0.21299 | 0.2144 | 0.2158 | 0.21679 | 0.21777 | 0.21875 | 0.21973 | 0.22072 | 0.2217 | 0.22268 | 0.22366 | 0.22464 | 0.22563 | 0.22661 | 0.22759 | 0.22857 | 0.22955 | 0.23054
| SHP021-137932835 | SHP021 | 7.8894e-06 | 7.957e-06 | 8.0247e-06 | 8.0923e-06 | 8.16e-06 | 8.2592e-06 | 8.3584e-06 | 8.4576e-06 | 8.5568e-06 | 8.656e-06 | 8.7552e-06 | 8.8544e-06 | 8.9536e-06 | 9.0528e-06 | 9.152e-06 | 9.2512e-06 | 9.3504e-06 | 9.4496e-06 | 9.5488e-06 | 9.648e-06
| SHP021-138133628 | SHP021 | 0.1549 | 0.15601 | 0.15712 | 0.15824 | 0.15935 | 0.15971 | 0.16008 | 0.16044 | 0.16081 | 0.16118 | 0.16154 | 0.16191 | 0.16227 | 0.16264 | 0.16301 | 0.16337 | 0.16374 | 0.16411 | 0.16447 | 0.16484
| SHP021-15437442 | SHP021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-15437455 | SHP021 | 0.43584 | 0.43758 | 0.43932 | 0.44106 | 0.44281 | 0.44355 | 0.44429 | 0.44503 | 0.44576 | 0.4465 | 0.44724 | 0.44798 | 0.44872 | 0.44946 | 0.4502 | 0.45094 | 0.45168 | 0.45242 | 0.45316 | 0.4539
| SHP021-155422659 | SHP021 | 7.4585e-05 | 7.5199e-05 | 7.5813e-05 | 7.6426e-05 | 7.704e-05 | 7.7964e-05 | 7.8888e-05 | 7.9812e-05 | 8.0736e-05 | 8.166e-05 | 8.2584e-05 | 8.3508e-05 | 8.4432e-05 | 8.5356e-05 | 8.628e-05 | 8.7204e-05 | 8.8128e-05 | 8.9052e-05 | 8.9976e-05 | 9.09e-05
| SHP021-157015365 | SHP021 | 0.0057081 | 0.0057482 | 0.0057884 | 0.0058285 | 0.0058687 | 0.0059246 | 0.0059806 | 0.0060365 | 0.0060925 | 0.0061484 | 0.0062044 | 0.0062604 | 0.0063163 | 0.0063723 | 0.0064282 | 0.0064842 | 0.0065402 | 0.0065961 | 0.0066521 | 0.006708
| SHP021-157015736 | SHP021 | 0.067216 | 0.067754 | 0.068292 | 0.068831 | 0.069369 | 0.069751 | 0.070132 | 0.070514 | 0.070896 | 0.071277 | 0.071659 | 0.072041 | 0.072422 | 0.072804 | 0.073186 | 0.073567 | 0.073949 | 0.074331 | 0.074712 | 0.075094
| SHP021-164271438 | SHP021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-164488411 | SHP021 | 0.045084 | 0.045386 | 0.045688 | 0.04599 | 0.046292 | 0.046505 | 0.046719 | 0.046932 | 0.047146 | 0.047359 | 0.047572 | 0.047786 | 0.047999 | 0.048213 | 0.048426 | 0.048639 | 0.048853 | 0.049066 | 0.04928 | 0.049493
| SHP021-24614288 | SHP021 | 0.0015656 | 0.0015781 | 0.0015907 | 0.0016033 | 0.0016158 | 0.0016304 | 0.0016449 | 0.0016594 | 0.001674 | 0.0016885 | 0.0017031 | 0.0017176 | 0.0017321 | 0.0017467 | 0.0017612 | 0.0017758 | 0.0017903 | 0.0018048 | 0.0018194 | 0.0018339
| SHP021-24614430 | SHP021 | 3.9795 | 3.9968 | 4.0142 | 4.0315 | 4.0488 | 4.0668 | 4.0847 | 4.1027 | 4.1206 | 4.1386 | 4.1565 | 4.1745 | 4.1924 | 4.2104 | 4.2284 | 4.2463 | 4.2643 | 4.2822 | 4.3002 | 4.3181
| SHP021-66719539 | SHP021 | 0.028692 | 0.02894 | 0.029187 | 0.029435 | 0.029682 | 0.029744 | 0.029806 | 0.029867 | 0.029929 | 0.029991 | 0.030053 | 0.030115 | 0.030176 | 0.030238 | 0.0303 | 0.030362 | 0.030424 | 0.030485 | 0.030547 | 0.030609
| SHP021-85424826 | SHP021 | 0.33438 | 0.33696 | 0.33954 | 0.34213 | 0.34471 | 0.34842 | 0.35214 | 0.35586 | 0.35957 | 0.36329 | 0.367 | 0.37072 | 0.37443 | 0.37815 | 0.38186 | 0.38558 | 0.38929 | 0.39301 | 0.39672 | 0.40044
| SSE011-15435228 | SSE011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE011-201930324 | SSE011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE012-152773219 | SSE012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE012-201930283 | SSE012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE013-201930225 | SSE013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE013-74144019 | SSE013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE014-201930170 | SSE014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE014-24597938 | SSE014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE031-15437545 | SSE031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE031-201930106 | SSE031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE031-24597896 | SSE031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE031-24597910 | SSE031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE032-156444372 | SSE032 | 2.6197 | 2.6371 | 2.6545 | 2.672 | 2.6894 | 2.6934 | 2.6973 | 2.7013 | 2.7053 | 2.7093 | 2.7132 | 2.7172 | 2.7212 | 2.7252 | 2.7291 | 2.7331 | 2.7371 | 2.7411 | 2.745 | 2.749
| SSE032-201929980 | SSE032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE033-201929907 | SSE033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE034-201929860 | SSE034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SSE034-24597952 | SSE034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL004-15415692 | STL004 | 4.8872 | 4.9241 | 4.9609 | 4.9978 | 5.0347 | 5.0379 | 5.041 | 5.0442 | 5.0474 | 5.0506 | 5.0538 | 5.057 | 5.0602 | 5.0634 | 5.0666 | 5.0698 | 5.073 | 5.0761 | 5.0793 | 5.0825
| STL005-141432115 | STL005 | 0.0066498 | 0.0066958 | 0.0067417 | 0.0067876 | 0.0068335 | 0.0068504 | 0.0068673 | 0.0068842 | 0.0069011 | 0.006918 | 0.0069349 | 0.0069518 | 0.0069687 | 0.0069857 | 0.0070026 | 0.0070195 | 0.0070364 | 0.0070533 | 0.0070702 | 0.0070871
| STL005-142032974 | STL005 | 0.07131 | 0.071902 | 0.072494 | 0.073086 | 0.073677 | 0.073622 | 0.073566 | 0.073511 | 0.073455 | 0.073399 | 0.073344 | 0.073288 | 0.073232 | 0.073177 | 0.073121 | 0.073066 | 0.07301 | 0.072954 | 0.072899 | 0.072843
| STL005-143031921 | STL005 | 0.062711 | 0.063146 | 0.06358 | 0.064015 | 0.064449 | 0.06456 | 0.064671 | 0.064781 | 0.064892 | 0.065002 | 0.065113 | 0.065224 | 0.065334 | 0.065445 | 0.065556 | 0.065666 | 0.065777 | 0.065888 | 0.065998 | 0.066109
| STL005-15415831 | STL005 | 14.1009 | 14.2211 | 14.3412 | 14.4613 | 14.5814 | 14.5979 | 14.6144 | 14.6309 | 14.6474 | 14.6639 | 14.6804 | 14.6969 | 14.7134 | 14.7299 | 14.7464 | 14.7629 | 14.7794 | 14.7959 | 14.8124 | 14.829
| STL005-155503897 | STL005 | 0.00011604 | 0.00011688 | 0.00011772 | 0.00011856 | 0.0001194 | 0.00011995 | 0.0001205 | 0.00012105 | 0.0001216 | 0.00012215 | 0.0001227 | 0.00012325 | 0.0001238 | 0.00012435 | 0.0001249 | 0.00012545 | 0.000126 | 0.00012655 | 0.0001271 | 0.00012765
| STL005-164675419 | STL005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL005-24599604 | STL005 | 9.1934 | 9.2542 | 9.3151 | 9.3759 | 9.4368 | 9.4436 | 9.4504 | 9.4572 | 9.464 | 9.4708 | 9.4776 | 9.4845 | 9.4913 | 9.4981 | 9.5049 | 9.5117 | 9.5185 | 9.5253 | 9.5321 | 9.5389
| STL005-24613578 | STL005 | 2.6849 | 2.703 | 2.7211 | 2.7393 | 2.7574 | 2.7567 | 2.756 | 2.7553 | 2.7546 | 2.7539 | 2.7532 | 2.7524 | 2.7517 | 2.751 | 2.7503 | 2.7496 | 2.7489 | 2.7482 | 2.7475 | 2.7467
| STL005-78736488 | STL005 | 0.021259 | 0.021408 | 0.021557 | 0.021706 | 0.021855 | 0.021814 | 0.021772 | 0.021731 | 0.02169 | 0.021649 | 0.021608 | 0.021567 | 0.021526 | 0.021485 | 0.021443 | 0.021402 | 0.021361 | 0.02132 | 0.021279 | 0.021238
| STL005-78747550 | STL005 | 0.012788 | 0.012888 | 0.012988 | 0.013089 | 0.013189 | 0.01318 | 0.013171 | 0.013162 | 0.013152 | 0.013143 | 0.013134 | 0.013125 | 0.013115 | 0.013106 | 0.013097 | 0.013088 | 0.013079 | 0.013069 | 0.01306 | 0.013051
| STL005-78747613 | STL005 | 0.09081 | 0.091606 | 0.092402 | 0.093198 | 0.093993 | 0.093806 | 0.093619 | 0.093432 | 0.093245 | 0.093058 | 0.092871 | 0.092684 | 0.092497 | 0.09231 | 0.092123 | 0.091936 | 0.091749 | 0.091562 | 0.091375 | 0.091188
| STL005-84921818 | STL005 | 5.5743 | 5.618 | 5.6618 | 5.7055 | 5.7493 | 5.7465 | 5.7436 | 5.7408 | 5.738 | 5.7351 | 5.7323 | 5.7295 | 5.7266 | 5.7238 | 5.721 | 5.7181 | 5.7153 | 5.7125 | 5.7097 | 5.7068
| STL006-144106192 | STL006 | 0.025824 | 0.026041 | 0.026257 | 0.026473 | 0.026689 | 0.02666 | 0.026632 | 0.026603 | 0.026574 | 0.026546 | 0.026517 | 0.026488 | 0.02646 | 0.026431 | 0.026402 | 0.026374 | 0.026345 | 0.026316 | 0.026288 | 0.026259
| STL006-144106506 | STL006 | 0.001126 | 0.001136 | 0.0011459 | 0.0011559 | 0.0011658 | 0.001168 | 0.0011702 | 0.0011723 | 0.0011745 | 0.0011767 | 0.0011789 | 0.001181 | 0.0011832 | 0.0011854 | 0.0011876 | 0.0011897 | 0.0011919 | 0.0011941 | 0.0011963 | 0.0011984
| STL006-144106734 | STL006 | 0.75626 | 0.76223 | 0.7682 | 0.77417 | 0.78014 | 0.77945 | 0.77876 | 0.77807 | 0.77738 | 0.77668 | 0.77599 | 0.7753 | 0.77461 | 0.77392 | 0.77323 | 0.77253 | 0.77184 | 0.77115 | 0.77046 | 0.76977
| STL006-144631935 | STL006 | 0.1497 | 0.15112 | 0.15253 | 0.15394 | 0.15536 | 0.15528 | 0.1552 | 0.15512 | 0.15504 | 0.15496 | 0.15488 | 0.1548 | 0.15472 | 0.15464 | 0.15456 | 0.15448 | 0.1544 | 0.15431 | 0.15423 | 0.15415
| STL006-144632294 | STL006 | 0.52136 | 0.52618 | 0.53101 | 0.53583 | 0.54066 | 0.54037 | 0.54008 | 0.5398 | 0.53951 | 0.53922 | 0.53894 | 0.53865 | 0.53836 | 0.53807 | 0.53779 | 0.5375 | 0.53721 | 0.53693 | 0.53664 | 0.53635
| STL006-15415768 | STL006 | 15.1284 | 15.2229 | 15.3174 | 15.4119 | 15.5064 | 15.5014 | 15.4965 | 15.4915 | 15.4865 | 15.4815 | 15.4765 | 15.4715 | 15.4665 | 15.4616 | 15.4566 | 15.4516 | 15.4466 | 15.4416 | 15.4366 | 15.4316
| STL006-155132358 | STL006 | 0.2099 | 0.21177 | 0.21363 | 0.2155 | 0.21736 | 0.21794 | 0.21851 | 0.21908 | 0.21966 | 0.22023 | 0.2208 | 0.22138 | 0.22195 | 0.22252 | 0.2231 | 0.22367 | 0.22424 | 0.22481 | 0.22539 | 0.22596
| STL006-155132567 | STL006 | 6.3707e-05 | 6.4291e-05 | 6.4874e-05 | 6.5457e-05 | 6.604e-05 | 6.6228e-05 | 6.6417e-05 | 6.6605e-05 | 6.6794e-05 | 6.6982e-05 | 6.7171e-05 | 6.7359e-05 | 6.7548e-05 | 6.7736e-05 | 6.7925e-05 | 6.8113e-05 | 6.8302e-05 | 6.849e-05 | 6.8679e-05 | 6.8867e-05
| STL006-155132685 | STL006 | 0.31421 | 0.31646 | 0.31872 | 0.32097 | 0.32322 | 0.32357 | 0.32392 | 0.32426 | 0.32461 | 0.32496 | 0.32531 | 0.32565 | 0.326 | 0.32635 | 0.32669 | 0.32704 | 0.32739 | 0.32773 | 0.32808 | 0.32843
| STL006-155132926 | STL006 | 0.091004 | 0.091826 | 0.092649 | 0.093471 | 0.094293 | 0.094491 | 0.094689 | 0.094888 | 0.095086 | 0.095284 | 0.095482 | 0.09568 | 0.095878 | 0.096077 | 0.096275 | 0.096473 | 0.096671 | 0.096869 | 0.097067 | 0.097266
| STL006-155133021 | STL006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155133103 | STL006 | 0.038535 | 0.038841 | 0.039147 | 0.039453 | 0.039759 | 0.03973 | 0.0397 | 0.03967 | 0.039641 | 0.039611 | 0.039582 | 0.039552 | 0.039522 | 0.039493 | 0.039463 | 0.039433 | 0.039404 | 0.039374 | 0.039345 | 0.039315
| STL006-155133222 | STL006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155178765 | STL006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155178849 | STL006 | 0.055197 | 0.055747 | 0.056297 | 0.056847 | 0.057397 | 0.057359 | 0.057322 | 0.057284 | 0.057247 | 0.057209 | 0.057171 | 0.057134 | 0.057096 | 0.057059 | 0.057021 | 0.056984 | 0.056946 | 0.056908 | 0.056871 | 0.056833
| STL006-155178947 | STL006 | 0.046629 | 0.047095 | 0.047561 | 0.048027 | 0.048493 | 0.04842 | 0.048346 | 0.048273 | 0.0482 | 0.048126 | 0.048053 | 0.047979 | 0.047906 | 0.047832 | 0.047759 | 0.047686 | 0.047612 | 0.047539 | 0.047465 | 0.047392
| STL006-155179094 | STL006 | 0.015848 | 0.015994 | 0.016141 | 0.016288 | 0.016435 | 0.016412 | 0.016389 | 0.016367 | 0.016344 | 0.016321 | 0.016299 | 0.016276 | 0.016253 | 0.016231 | 0.016208 | 0.016185 | 0.016163 | 0.01614 | 0.016117 | 0.016095
| STL006-155189552 | STL006 | 0.064189 | 0.064851 | 0.065514 | 0.066176 | 0.066839 | 0.066839 | 0.066838 | 0.066838 | 0.066838 | 0.066838 | 0.066838 | 0.066838 | 0.066837 | 0.066837 | 0.066837 | 0.066837 | 0.066837 | 0.066836 | 0.066836 | 0.066836
| STL006-155189674 | STL006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155189763 | STL006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155189877 | STL006 | 0.00055296 | 0.00055872 | 0.00056448 | 0.00057024 | 0.000576 | 0.00057798 | 0.00057996 | 0.00058194 | 0.00058392 | 0.0005859 | 0.00058788 | 0.00058986 | 0.00059184 | 0.00059382 | 0.0005958 | 0.00059778 | 0.00059976 | 0.00060174 | 0.00060372 | 0.0006057
| STL006-155190011 | STL006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155190105 | STL006 | 0.016198 | 0.016309 | 0.01642 | 0.016532 | 0.016643 | 0.016649 | 0.016656 | 0.016662 | 0.016668 | 0.016674 | 0.01668 | 0.016687 | 0.016693 | 0.016699 | 0.016705 | 0.016711 | 0.016718 | 0.016724 | 0.01673 | 0.016736
| STL006-155193804 | STL006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155193946 | STL006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-155249643 | STL006 | 0.037207 | 0.037536 | 0.037865 | 0.038194 | 0.038523 | 0.038508 | 0.038493 | 0.038478 | 0.038463 | 0.038448 | 0.038433 | 0.038418 | 0.038402 | 0.038387 | 0.038372 | 0.038357 | 0.038342 | 0.038327 | 0.038312 | 0.038297
| STL006-155249816 | STL006 | 0.054235 | 0.054739 | 0.055242 | 0.055745 | 0.056249 | 0.056434 | 0.056619 | 0.056805 | 0.05699 | 0.057176 | 0.057361 | 0.057547 | 0.057732 | 0.057918 | 0.058103 | 0.058289 | 0.058474 | 0.058659 | 0.058845 | 0.05903
| STL006-155250434 | STL006 | 0.0070497 | 0.0071141 | 0.0071785 | 0.0072429 | 0.0073074 | 0.0073046 | 0.0073019 | 0.0072992 | 0.0072964 | 0.0072937 | 0.007291 | 0.0072883 | 0.0072855 | 0.0072828 | 0.0072801 | 0.0072774 | 0.0072746 | 0.0072719 | 0.0072692 | 0.0072665
| STL006-155392225 | STL006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STL006-182934752 | STL006 | 0.040716 | 0.041139 | 0.041563 | 0.041986 | 0.04241 | 0.042398 | 0.042386 | 0.042375 | 0.042363 | 0.042352 | 0.04234 | 0.042329 | 0.042317 | 0.042305 | 0.042294 | 0.042282 | 0.042271 | 0.042259 | 0.042247 | 0.042236
| STL006-24599342 | STL006 | 0.54779 | 0.55266 | 0.55753 | 0.5624 | 0.56727 | 0.56873 | 0.57018 | 0.57164 | 0.5731 | 0.57456 | 0.57602 | 0.57748 | 0.57894 | 0.58039 | 0.58185 | 0.58331 | 0.58477 | 0.58623 | 0.58769 | 0.58914
| STL006-24601812 | STL006 | 1.816 | 1.8317 | 1.8473 | 1.863 | 1.8787 | 1.8776 | 1.8766 | 1.8756 | 1.8746 | 1.8736 | 1.8726 | 1.8716 | 1.8706 | 1.8696 | 1.8686 | 1.8676 | 1.8666 | 1.8656 | 1.8646 | 1.8636
| STL006-24613426 | STL006 | 10.4113 | 10.4947 | 10.5782 | 10.6616 | 10.7451 | 10.752 | 10.7589 | 10.7659 | 10.7728 | 10.7797 | 10.7866 | 10.7936 | 10.8005 | 10.8074 | 10.8143 | 10.8212 | 10.8282 | 10.8351 | 10.842 | 10.8489
| STL006-56211052 | STL006 | 0.079468 | 0.079604 | 0.07974 | 0.079875 | 0.080011 | 0.079967 | 0.079922 | 0.079877 | 0.079833 | 0.079788 | 0.079744 | 0.079699 | 0.079654 | 0.07961 | 0.079565 | 0.079521 | 0.079476 | 0.079432 | 0.079387 | 0.079342
| STL006-82629266 | STL006 | 0.040102 | 0.04042 | 0.040738 | 0.041056 | 0.041374 | 0.041344 | 0.041313 | 0.041283 | 0.041253 | 0.041222 | 0.041192 | 0.041162 | 0.041131 | 0.041101 | 0.041071 | 0.04104 | 0.04101 | 0.040979 | 0.040949 | 0.040919
| STL006-83365075 | STL006 | 0.082261 | 0.082911 | 0.083561 | 0.084211 | 0.084861 | 0.084768 | 0.084675 | 0.084582 | 0.084489 | 0.084396 | 0.084303 | 0.08421 | 0.084117 | 0.084025 | 0.083932 | 0.083839 | 0.083746 | 0.083653 | 0.08356 | 0.083467
| STL007-143136191 | STL007 | 0.0003417 | 0.000345 | 0.0003483 | 0.0003516 | 0.0003549 | 0.0003556 | 0.0003563 | 0.000357 | 0.0003577 | 0.0003584 | 0.0003591 | 0.0003598 | 0.0003605 | 0.0003612 | 0.0003619 | 0.0003626 | 0.0003633 | 0.000364 | 0.0003647 | 0.0003654
| STL007-143136451 | STL007 | 0.11923 | 0.1205 | 0.12176 | 0.12303 | 0.1243 | 0.12427 | 0.12423 | 0.1242 | 0.12417 | 0.12414 | 0.1241 | 0.12407 | 0.12404 | 0.12401 | 0.12397 | 0.12394 | 0.12391 | 0.12388 | 0.12385 | 0.12381
| STL007-15415881 | STL007 | 4.9021 | 4.9356 | 4.9692 | 5.0027 | 5.0362 | 5.0384 | 5.0406 | 5.0429 | 5.0451 | 5.0473 | 5.0495 | 5.0517 | 5.054 | 5.0562 | 5.0584 | 5.0606 | 5.0628 | 5.065 | 5.0673 | 5.0695
| STL007-155179441 | STL007 | 0.00038423 | 0.00038817 | 0.00039211 | 0.00039606 | 0.0004 | 0.0004002 | 0.0004004 | 0.0004006 | 0.0004008 | 0.000401 | 0.0004012 | 0.0004014 | 0.0004016 | 0.0004018 | 0.000402 | 0.0004022 | 0.0004024 | 0.0004026 | 0.0004028 | 0.000403
| STL007-155179565 | STL007 | 0.065502 | 0.065969 | 0.066437 | 0.066904 | 0.067371 | 0.067493 | 0.067615 | 0.067737 | 0.067859 | 0.06798 | 0.068102 | 0.068224 | 0.068346 | 0.068467 | 0.068589 | 0.068711 | 0.068833 | 0.068954 | 0.069076 | 0.069198
| STL007-155179964 | STL007 | 0.0039759 | 0.0040112 | 0.0040465 | 0.0040818 | 0.0041171 | 0.0041211 | 0.004125 | 0.004129 | 0.0041329 | 0.0041369 | 0.0041408 | 0.0041448 | 0.0041487 | 0.0041527 | 0.0041566 | 0.0041606 | 0.0041645 | 0.0041685 | 0.0041724 | 0.0041764
| STL007-162910244 | STL007 | 0.36296 | 0.36606 | 0.36916 | 0.37227 | 0.37537 | 0.37626 | 0.37714 | 0.37803 | 0.37892 | 0.3798 | 0.38069 | 0.38157 | 0.38246 | 0.38335 | 0.38423 | 0.38512 | 0.386 | 0.38689 | 0.38777 | 0.38866
| STL007-183308767 | STL007 | 0.00076009 | 0.00076731 | 0.00077454 | 0.00078177 | 0.000789 | 0.00079035 | 0.0007917 | 0.00079305 | 0.0007944 | 0.00079575 | 0.0007971 | 0.00079845 | 0.0007998 | 0.00080115 | 0.0008025 | 0.00080385 | 0.0008052 | 0.00080655 | 0.0008079 | 0.00080925
| STL007-76065702 | STL007 | 0.076736 | 0.077307 | 0.077878 | 0.078448 | 0.079019 | 0.078923 | 0.078826 | 0.07873 | 0.078633 | 0.078536 | 0.07844 | 0.078343 | 0.078247 | 0.07815 | 0.078053 | 0.077957 | 0.07786 | 0.077764 | 0.077667 | 0.077571
| STL007-85224567 | STL007 | 1.5876 | 1.6 | 1.6124 | 1.6248 | 1.6372 | 1.6388 | 1.6405 | 1.6421 | 1.6438 | 1.6454 | 1.647 | 1.6487 | 1.6503 | 1.652 | 1.6536 | 1.6553 | 1.6569 | 1.6585 | 1.6602 | 1.6618
| STL007-87836091 | STL007 | 7.0539 | 7.093 | 7.132 | 7.171 | 7.2101 | 7.2133 | 7.2166 | 7.2199 | 7.2232 | 7.2265 | 7.2298 | 7.2331 | 7.2364 | 7.2397 | 7.243 | 7.2463 | 7.2496 | 7.2529 | 7.2561 | 7.2594
| STN011-130745907 | STN011 | 0.071531 | 0.072038 | 0.072546 | 0.073053 | 0.07356 | 0.073708 | 0.073857 | 0.074006 | 0.074154 | 0.074303 | 0.074452 | 0.0746 | 0.074749 | 0.074898 | 0.075046 | 0.075195 | 0.075344 | 0.075492 | 0.075641 | 0.07579
| STN011-160424610 | STN011 | 0.051784 | 0.052149 | 0.052514 | 0.052879 | 0.053244 | 0.053331 | 0.053418 | 0.053505 | 0.053592 | 0.053679 | 0.053766 | 0.053853 | 0.05394 | 0.054027 | 0.054113 | 0.0542 | 0.054287 | 0.054374 | 0.054461 | 0.054548
| STN011-164271487 | STN011 | 2.4167e-05 | 2.4313e-05 | 2.4459e-05 | 2.4604e-05 | 2.475e-05 | 2.496e-05 | 2.517e-05 | 2.538e-05 | 2.559e-05 | 2.58e-05 | 2.601e-05 | 2.622e-05 | 2.643e-05 | 2.664e-05 | 2.685e-05 | 2.706e-05 | 2.727e-05 | 2.748e-05 | 2.769e-05 | 2.79e-05
| STN011-184475628 | STN011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN011-200055388 | STN011 | 3.4132 | 3.4337 | 3.4541 | 3.4745 | 3.495 | 3.5143 | 3.5337 | 3.5531 | 3.5724 | 3.5918 | 3.6111 | 3.6305 | 3.6499 | 3.6692 | 3.6886 | 3.7079 | 3.7273 | 3.7466 | 3.766 | 3.7854
| STN012-200055438 | STN012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN012-72075245 | STN012 | 0.11408 | 0.11477 | 0.11546 | 0.11615 | 0.11683 | 0.11845 | 0.12006 | 0.12167 | 0.12329 | 0.1249 | 0.12651 | 0.12813 | 0.12974 | 0.13135 | 0.13297 | 0.13458 | 0.13619 | 0.13781 | 0.13942 | 0.14103
| STN013-15421517 | STN013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN013-200055508 | STN013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN014-200055610 | STN014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN021-164443076 | STN021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN021-164443183 | STN021 | 0.01948 | 0.019608 | 0.019736 | 0.019864 | 0.019991 | 0.020136 | 0.02028 | 0.020424 | 0.020568 | 0.020713 | 0.020857 | 0.021001 | 0.021145 | 0.02129 | 0.021434 | 0.021578 | 0.021722 | 0.021866 | 0.022011 | 0.022155
| STN021-193604803 | STN021 | 9.5758 | 9.6326 | 9.6894 | 9.7463 | 9.8031 | 9.8764 | 9.9496 | 10.0228 | 10.096 | 10.1693 | 10.2425 | 10.3157 | 10.3889 | 10.4622 | 10.5354 | 10.6086 | 10.6819 | 10.7551 | 10.8283 | 10.9015
| STN021-200055789 | STN021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN022-200055843 | STN022 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175
| STN023-200055989 | STN023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN024-138232567 | STN024 | 0.026344 | 0.026524 | 0.026703 | 0.026882 | 0.027061 | 0.027202 | 0.027342 | 0.027482 | 0.027623 | 0.027763 | 0.027904 | 0.028044 | 0.028185 | 0.028325 | 0.028466 | 0.028606 | 0.028746 | 0.028887 | 0.029027 | 0.029168
| STN024-160253800 | STN024 | 1.7604e-05 | 1.7748e-05 | 1.7892e-05 | 1.8036e-05 | 1.818e-05 | 1.8369e-05 | 1.8558e-05 | 1.8747e-05 | 1.8936e-05 | 1.9125e-05 | 1.9314e-05 | 1.9503e-05 | 1.9692e-05 | 1.9881e-05 | 2.007e-05 | 2.0259e-05 | 2.0448e-05 | 2.0637e-05 | 2.0826e-05 | 2.1015e-05
| STN024-160253882 | STN024 | 2.7813e-05 | 2.803e-05 | 2.8247e-05 | 2.8464e-05 | 2.8681e-05 | 2.8972e-05 | 2.9264e-05 | 2.9555e-05 | 2.9847e-05 | 3.0138e-05 | 3.043e-05 | 3.0721e-05 | 3.1013e-05 | 3.1304e-05 | 3.1596e-05 | 3.1887e-05 | 3.2178e-05 | 3.247e-05 | 3.2761e-05 | 3.3053e-05
| STN024-200056045 | STN024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN024-24605670 | STN024 | 0.82165 | 0.82766 | 0.83367 | 0.83968 | 0.84569 | 0.84883 | 0.85196 | 0.8551 | 0.85824 | 0.86138 | 0.86451 | 0.86765 | 0.87079 | 0.87393 | 0.87706 | 0.8802 | 0.88334 | 0.88648 | 0.88961 | 0.89275
| STN024-24611992 | STN024 | 0.00046818 | 0.00047196 | 0.00047574 | 0.00047952 | 0.0004833 | 0.00048829 | 0.00049329 | 0.00049828 | 0.00050328 | 0.00050827 | 0.00051327 | 0.00051826 | 0.00052326 | 0.00052825 | 0.00053325 | 0.00053824 | 0.00054324 | 0.00054823 | 0.00055323 | 0.00055822
| STN031-200777976 | STN031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STN031-200778008 | STN031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU011-94649597 | SU011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU012-24612934 | SU012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU012-24613115 | SU012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU012-94649646 | SU012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU013-94649695 | SU013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU015-24612538 | SU015 | 0.74157 | 0.74285 | 0.74413 | 0.74541 | 0.74669 | 0.74776 | 0.74883 | 0.7499 | 0.75097 | 0.75205 | 0.75312 | 0.75419 | 0.75526 | 0.75633 | 0.7574 | 0.75848 | 0.75955 | 0.76062 | 0.76169 | 0.76276
| SU015-94649793 | SU015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU015-98840126 | SU015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU021-40665700 | SU021 | 1.8677 | 1.8787 | 1.8896 | 1.9006 | 1.9116 | 1.9207 | 1.9297 | 1.9388 | 1.9478 | 1.9569 | 1.966 | 1.975 | 1.9841 | 1.9932 | 2.0022 | 2.0113 | 2.0204 | 2.0294 | 2.0385 | 2.0476
| SU021-94649866 | SU021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU022-186913526 | SU022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU022-94649915 | SU022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU023-94649964 | SU023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU024-94650013 | SU024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU034-94650323 | SU034 | 0.00016097 | 0.00016226 | 0.00016355 | 0.00016485 | 0.00016614 | 0.00016661 | 0.00016708 | 0.00016754 | 0.00016801 | 0.00016848 | 0.00016895 | 0.00016942 | 0.00016988 | 0.00017035 | 0.00017082 | 0.00017129 | 0.00017176 | 0.00017222 | 0.00017269 | 0.00017316
| SU035-183159191 | SU035 | 0.97951 | 0.98705 | 0.99458 | 1.0021 | 1.0097 | 1.016 | 1.0223 | 1.0286 | 1.0349 | 1.0412 | 1.0475 | 1.0538 | 1.0601 | 1.0664 | 1.0727 | 1.0791 | 1.0854 | 1.0917 | 1.098 | 1.1043
| SU035-24612255 | SU035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SU035-94650372 | SU035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA011-155056985 | TNA011 | 154.352 | 155.7221 | 157.0923 | 158.4624 | 159.8326 | 160.7141 | 161.5955 | 162.4769 | 163.3584 | 164.2398 | 165.1213 | 166.0027 | 166.8842 | 167.7656 | 168.6471 | 169.5285 | 170.41 | 171.2914 | 172.1728 | 173.0543
| TNA012-182581784 | TNA012 | 52.2279 | 52.68 | 53.132 | 53.584 | 54.036 | 54.2642 | 54.4924 | 54.7205 | 54.9487 | 55.1768 | 55.405 | 55.6331 | 55.8613 | 56.0895 | 56.3176 | 56.5458 | 56.7739 | 57.0021 | 57.2302 | 57.4584
| TNA014-154750885 | TNA014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA021-154751071 | TNA021 | 35.5923 | 35.9204 | 36.2486 | 36.5767 | 36.9049 | 37.1159 | 37.327 | 37.5381 | 37.7492 | 37.9602 | 38.1713 | 38.3824 | 38.5935 | 38.8046 | 39.0156 | 39.2267 | 39.4378 | 39.6489 | 39.8599 | 40.071
| TNA021-158086216 | TNA021 | 0.5294 | 0.53452 | 0.53964 | 0.54477 | 0.54989 | 0.55318 | 0.55646 | 0.55975 | 0.56304 | 0.56633 | 0.56961 | 0.5729 | 0.57619 | 0.57948 | 0.58276 | 0.58605 | 0.58934 | 0.59263 | 0.59591 | 0.5992
| TNA022-182581504 | TNA022 | 66.276 | 66.8162 | 67.3564 | 67.8966 | 68.4368 | 68.7128 | 68.9887 | 69.2646 | 69.5406 | 69.8165 | 70.0925 | 70.3684 | 70.6444 | 70.9203 | 71.1963 | 71.4722 | 71.7481 | 72.0241 | 72.3 | 72.576
| TNA022-184844358 | TNA022 | 42.3569 | 42.6954 | 43.0338 | 43.3722 | 43.7106 | 43.9177 | 44.1247 | 44.3317 | 44.5388 | 44.7458 | 44.9528 | 45.1599 | 45.3669 | 45.5739 | 45.781 | 45.988 | 46.195 | 46.402 | 46.6091 | 46.8161
| TNA022-187163239 | TNA022 | 2.1879 | 2.2115 | 2.2352 | 2.2589 | 2.2825 | 2.289 | 2.2954 | 2.3019 | 2.3084 | 2.3149 | 2.3213 | 2.3278 | 2.3343 | 2.3407 | 2.3472 | 2.3537 | 2.3602 | 2.3666 | 2.3731 | 2.3796
| TNA022-194840439 | TNA022 | 6.1872 | 6.236 | 6.2847 | 6.3335 | 6.3823 | 6.3958 | 6.4093 | 6.4228 | 6.4363 | 6.4498 | 6.4633 | 6.4769 | 6.4904 | 6.5039 | 6.5174 | 6.5309 | 6.5444 | 6.5579 | 6.5714 | 6.5849
| TNA023-154633087 | TNA023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA023-154751161 | TNA023 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679
| TNA024-154751243 | TNA024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA031-188490107 | TNA031 | 1.3108 | 1.3227 | 1.3346 | 1.3466 | 1.3585 | 1.3645 | 1.3705 | 1.3764 | 1.3824 | 1.3884 | 1.3944 | 1.4003 | 1.4063 | 1.4123 | 1.4182 | 1.4242 | 1.4302 | 1.4362 | 1.4421 | 1.4481
| TNA033-153234693 | TNA033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA033-178283696 | TNA033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TNA033-188490077 | TNA033 | 0.69714 | 0.70532 | 0.71349 | 0.72167 | 0.72984 | 0.72892 | 0.72799 | 0.72707 | 0.72615 | 0.72522 | 0.7243 | 0.72338 | 0.72245 | 0.72153 | 0.7206 | 0.71968 | 0.71876 | 0.71783 | 0.71691 | 0.71599
| TQY021-185165057 | TQY021 | 32.0833 | 32.367 | 32.6508 | 32.9346 | 33.2183 | 33.1287 | 33.0392 | 32.9496 | 32.86 | 32.7704 | 32.6809 | 32.5913 | 32.5017 | 32.4121 | 32.3225 | 32.233 | 32.1434 | 32.0538 | 31.9642 | 31.8747
| TQY021-187647017 | TQY021 | 36.7014 | 37.0335 | 37.3657 | 37.6978 | 38.03 | 37.8062 | 37.5824 | 37.3585 | 37.1347 | 36.9109 | 36.6871 | 36.4633 | 36.2395 | 36.0157 | 35.7919 | 35.568 | 35.3442 | 35.1204 | 34.8966 | 34.6728
| TQY021-192995237 | TQY021 | 34.7884 | 35.1261 | 35.4637 | 35.8013 | 36.1389 | 36.1121 | 36.0852 | 36.0583 | 36.0314 | 36.0046 | 35.9777 | 35.9508 | 35.924 | 35.8971 | 35.8702 | 35.8433 | 35.8165 | 35.7896 | 35.7627 | 35.7358
| TQY021-24613536 | TQY021 | 10.5566 | 10.572 | 10.5875 | 10.6029 | 10.6183 | 10.5716 | 10.5249 | 10.4782 | 10.4315 | 10.3848 | 10.3381 | 10.2914 | 10.2447 | 10.198 | 10.1513 | 10.1046 | 10.0579 | 10.0112 | 9.9645 | 9.9179
| TQY022-192995279 | TQY022 | 13.3301 | 13.3956 | 13.4611 | 13.5265 | 13.592 | 13.5863 | 13.5807 | 13.575 | 13.5693 | 13.5637 | 13.558 | 13.5523 | 13.5467 | 13.541 | 13.5353 | 13.5297 | 13.524 | 13.5183 | 13.5127 | 13.507
| TQY022-88336509 | TQY022 | 17.2971 | 17.4391 | 17.5811 | 17.7231 | 17.8651 | 17.8256 | 17.7861 | 17.7466 | 17.7071 | 17.6675 | 17.628 | 17.5885 | 17.549 | 17.5095 | 17.4699 | 17.4304 | 17.3909 | 17.3514 | 17.3119 | 17.2724
| TQY031-156447550 | TQY031 | 28.9671 | 29.0318 | 29.0965 | 29.1611 | 29.2258 | 29.054 | 28.8822 | 28.7104 | 28.5387 | 28.3669 | 28.1951 | 28.0233 | 27.8515 | 27.6797 | 27.5079 | 27.3362 | 27.1644 | 26.9926 | 26.8208 | 26.649
| TQY031-192995335 | TQY031 | 12.275 | 12.3131 | 12.3513 | 12.3894 | 12.4276 | 12.3277 | 12.2279 | 12.128 | 12.0282 | 11.9283 | 11.8285 | 11.7286 | 11.6288 | 11.5289 | 11.4291 | 11.3293 | 11.2294 | 11.1296 | 11.0297 | 10.9299
| TQY032-192995307 | TQY032 | 8.5957 | 8.6413 | 8.6868 | 8.7324 | 8.778 | 8.729 | 8.68 | 8.631 | 8.582 | 8.533 | 8.484 | 8.435 | 8.386 | 8.337 | 8.288 | 8.239 | 8.19 | 8.141 | 8.092 | 8.043
| TRG002-154491390 | TRG002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158166546 | TRG002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158166806 | TRG002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158205190 | TRG002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158205316 | TRG002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158205503 | TRG002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158205673 | TRG002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-158205847 | TRG002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-163035708 | TRG002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-163036120 | TRG002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-24598160 | TRG002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG002-24598202 | TRG002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-162785300 | TRG003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-162785510 | TRG003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-163036413 | TRG003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-163036890 | TRG003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-163037137 | TRG003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-163066379 | TRG003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG003-60700569 | TRG003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG004-158007081 | TRG004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG004-162802539 | TRG004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG004-24598258 | TRG004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG005-117365806 | TRG005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG005-158041024 | TRG005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG005-162822850 | TRG005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG005-162823024 | TRG005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG005-24598286 | TRG005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG005-60700588 | TRG005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG005-74127795 | TRG005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG011-185851173 | TRG011 | 1.5685 | 1.5833 | 1.5981 | 1.6129 | 1.6277 | 1.6117 | 1.5958 | 1.5798 | 1.5639 | 1.5479 | 1.532 | 1.5161 | 1.5001 | 1.4842 | 1.4682 | 1.4523 | 1.4364 | 1.4204 | 1.4045 | 1.3885
| TRG013-162785300 | TRG013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-162785510 | TRG013 | 3.227e-05 | 3.2562e-05 | 3.2855e-05 | 3.3147e-05 | 3.344e-05 | 3.3024e-05 | 3.2608e-05 | 3.2192e-05 | 3.1776e-05 | 3.136e-05 | 3.0944e-05 | 3.0528e-05 | 3.0112e-05 | 2.9696e-05 | 2.928e-05 | 2.8864e-05 | 2.8448e-05 | 2.8032e-05 | 2.7616e-05 | 2.72e-05
| TRG013-162806327 | TRG013 | 0.00086314 | 0.00087686 | 0.00089057 | 0.00090429 | 0.000918 | 0.00090425 | 0.0008905 | 0.00087675 | 0.000863 | 0.00084925 | 0.0008355 | 0.00082175 | 0.000808 | 0.00079425 | 0.0007805 | 0.00076675 | 0.000753 | 0.00073925 | 0.0007255 | 0.00071175
| TRG013-162823585 | TRG013 | 0.011334 | 0.011436 | 0.011537 | 0.011639 | 0.011741 | 0.011619 | 0.011497 | 0.011376 | 0.011254 | 0.011132 | 0.011011 | 0.010889 | 0.010768 | 0.010646 | 0.010524 | 0.010403 | 0.010281 | 0.010159 | 0.010038 | 0.0099162
| TRG013-162823910 | TRG013 | 0.00012013 | 0.00012151 | 0.00012288 | 0.00012426 | 0.00012564 | 0.00012371 | 0.00012179 | 0.00011986 | 0.00011794 | 0.00011601 | 0.00011408 | 0.00011216 | 0.00011023 | 0.00010831 | 0.00010638 | 0.00010445 | 0.00010253 | 0.0001006 | 9.8676e-05 | 9.675e-05
| TRG013-162824119 | TRG013 | 2.9007e-06 | 2.954e-06 | 3.0073e-06 | 3.0607e-06 | 3.114e-06 | 3.0456e-06 | 2.9772e-06 | 2.9088e-06 | 2.8404e-06 | 2.772e-06 | 2.7036e-06 | 2.6352e-06 | 2.5668e-06 | 2.4984e-06 | 2.43e-06 | 2.3616e-06 | 2.2932e-06 | 2.2248e-06 | 2.1564e-06 | 2.088e-06
| TRG013-163036413 | TRG013 | 6.4594e-07 | 6.5246e-07 | 6.5897e-07 | 6.6549e-07 | 6.72e-07 | 6.6435e-07 | 6.567e-07 | 6.4905e-07 | 6.414e-07 | 6.3375e-07 | 6.261e-07 | 6.1845e-07 | 6.108e-07 | 6.0315e-07 | 5.955e-07 | 5.8785e-07 | 5.802e-07 | 5.7255e-07 | 5.649e-07 | 5.5725e-07
| TRG013-163036626 | TRG013 | 3.3597e-07 | 3.4247e-07 | 3.4898e-07 | 3.5549e-07 | 3.62e-07 | 3.56e-07 | 3.5e-07 | 3.44e-07 | 3.38e-07 | 3.32e-07 | 3.26e-07 | 3.2e-07 | 3.14e-07 | 3.08e-07 | 3.02e-07 | 2.96e-07 | 2.9e-07 | 2.84e-07 | 2.78e-07 | 2.72e-07
| TRG013-163036890 | TRG013 | 5.2806e-06 | 5.3554e-06 | 5.4303e-06 | 5.5051e-06 | 5.58e-06 | 5.489e-06 | 5.398e-06 | 5.307e-06 | 5.216e-06 | 5.125e-06 | 5.034e-06 | 4.943e-06 | 4.852e-06 | 4.761e-06 | 4.67e-06 | 4.579e-06 | 4.488e-06 | 4.397e-06 | 4.306e-06 | 4.215e-06
| TRG013-163037137 | TRG013 | 0.0022992 | 0.0023176 | 0.002336 | 0.0023544 | 0.0023728 | 0.0023503 | 0.0023278 | 0.0023052 | 0.0022827 | 0.0022602 | 0.0022377 | 0.0022151 | 0.0021926 | 0.0021701 | 0.0021476 | 0.002125 | 0.0021025 | 0.00208 | 0.0020574 | 0.0020349
| TRG013-163037241 | TRG013 | 0.0020909 | 0.0021082 | 0.0021254 | 0.0021427 | 0.0021599 | 0.0021387 | 0.0021175 | 0.0020963 | 0.0020751 | 0.0020539 | 0.0020328 | 0.0020116 | 0.0019904 | 0.0019692 | 0.001948 | 0.0019268 | 0.0019056 | 0.0018844 | 0.0018632 | 0.001842
| TRG013-163065605 | TRG013 | 0.00010577 | 0.00010691 | 0.00010806 | 0.0001092 | 0.00011034 | 0.00010876 | 0.00010719 | 0.00010561 | 0.00010404 | 0.00010247 | 0.00010089 | 9.9315e-05 | 9.774e-05 | 9.6165e-05 | 9.459e-05 | 9.3015e-05 | 9.144e-05 | 8.9865e-05 | 8.829e-05 | 8.6715e-05
| TRG013-163065814 | TRG013 | 0.0002388 | 0.0002406 | 0.0002424 | 0.0002442 | 0.000246 | 0.000243 | 0.00024 | 0.000237 | 0.000234 | 0.000231 | 0.000228 | 0.000225 | 0.000222 | 0.000219 | 0.000216 | 0.000213 | 0.00021 | 0.000207 | 0.000204 | 0.000201
| TRG013-163066137 | TRG013 | 0.0074077 | 0.0075102 | 0.0076128 | 0.0077153 | 0.0078178 | 0.007687 | 0.0075562 | 0.0074254 | 0.0072946 | 0.0071638 | 0.007033 | 0.0069022 | 0.0067714 | 0.0066406 | 0.0065098 | 0.006379 | 0.0062482 | 0.0061174 | 0.0059866 | 0.0058558
| TRG013-163066379 | TRG013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG013-163066765 | TRG013 | 0.00038643 | 0.00039153 | 0.00039662 | 0.00040171 | 0.0004068 | 0.00040032 | 0.00039384 | 0.00038736 | 0.00038088 | 0.0003744 | 0.00036792 | 0.00036144 | 0.00035496 | 0.00034848 | 0.000342 | 0.00033552 | 0.00032904 | 0.00032256 | 0.00031608 | 0.0003096
| TRG013-176898414 | TRG013 | 0.81098 | 0.81968 | 0.82838 | 0.83707 | 0.84577 | 0.83276 | 0.81975 | 0.80674 | 0.79373 | 0.78071 | 0.7677 | 0.75469 | 0.74168 | 0.72867 | 0.71565 | 0.70264 | 0.68963 | 0.67662 | 0.66361 | 0.65059
| TRG013-176898441 | TRG013 | 0.47264 | 0.47667 | 0.48069 | 0.48471 | 0.48873 | 0.48373 | 0.47874 | 0.47374 | 0.46874 | 0.46374 | 0.45875 | 0.45375 | 0.44875 | 0.44375 | 0.43876 | 0.43376 | 0.42876 | 0.42376 | 0.41876 | 0.41377
| TRG013-185851126 | TRG013 | 4.0416 | 4.0755 | 4.1094 | 4.1434 | 4.1773 | 4.1387 | 4.1 | 4.0613 | 4.0227 | 3.984 | 3.9453 | 3.9067 | 3.868 | 3.8293 | 3.7906 | 3.752 | 3.7133 | 3.6746 | 3.636 | 3.5973
| TRG013-60700569 | TRG013 | 0.45797 | 0.45893 | 0.45988 | 0.46083 | 0.46178 | 0.45973 | 0.45767 | 0.45561 | 0.45355 | 0.45149 | 0.44943 | 0.44737 | 0.44531 | 0.44325 | 0.44119 | 0.43913 | 0.43707 | 0.43501 | 0.43295 | 0.43089
| TRG014-158007081 | TRG014 | 9.4025e-05 | 9.4999e-05 | 9.5973e-05 | 9.6946e-05 | 9.792e-05 | 9.6112e-05 | 9.4304e-05 | 9.2496e-05 | 9.0688e-05 | 8.888e-05 | 8.7072e-05 | 8.5264e-05 | 8.3456e-05 | 8.1648e-05 | 7.984e-05 | 7.8032e-05 | 7.6224e-05 | 7.4416e-05 | 7.2608e-05 | 7.08e-05
| TRG014-162802339 | TRG014 | 0.000975 | 0.0009822 | 0.0009894 | 0.0009966 | 0.0010038 | 0.00099029 | 0.00097678 | 0.00096327 | 0.00094976 | 0.00093625 | 0.00092274 | 0.00090923 | 0.00089572 | 0.00088221 | 0.0008687 | 0.00085519 | 0.00084168 | 0.00082817 | 0.00081466 | 0.00080115
| TRG014-162802539 | TRG014 | 0.0013975 | 0.0014117 | 0.0014259 | 0.00144 | 0.0014542 | 0.0014382 | 0.0014222 | 0.0014062 | 0.0013902 | 0.0013741 | 0.0013581 | 0.0013421 | 0.0013261 | 0.0013101 | 0.0012941 | 0.0012781 | 0.0012621 | 0.001246 | 0.00123 | 0.001214
| TRG014-182935203 | TRG014 | 5.6746e-05 | 5.723e-05 | 5.7713e-05 | 5.8197e-05 | 5.868e-05 | 5.796e-05 | 5.724e-05 | 5.652e-05 | 5.58e-05 | 5.508e-05 | 5.436e-05 | 5.364e-05 | 5.292e-05 | 5.22e-05 | 5.148e-05 | 5.076e-05 | 5.004e-05 | 4.932e-05 | 4.86e-05 | 4.788e-05
| TRG014-185851238 | TRG014 | 2.5736 | 2.5982 | 2.6228 | 2.6474 | 2.672 | 2.6487 | 2.6254 | 2.6021 | 2.5788 | 2.5556 | 2.5323 | 2.509 | 2.4857 | 2.4624 | 2.4391 | 2.4158 | 2.3925 | 2.3693 | 2.346 | 2.3227
| TRG014-24598258 | TRG014 | 1.1033 | 1.1106 | 1.1178 | 1.1251 | 1.1324 | 1.1241 | 1.1158 | 1.1075 | 1.0992 | 1.0909 | 1.0826 | 1.0743 | 1.0659 | 1.0576 | 1.0493 | 1.041 | 1.0327 | 1.0244 | 1.0161 | 1.0078
| TRG022-142033811 | TRG022 | 0.053664 | 0.054231 | 0.054798 | 0.055365 | 0.055932 | 0.055428 | 0.054924 | 0.054419 | 0.053915 | 0.053411 | 0.052907 | 0.052403 | 0.051898 | 0.051394 | 0.05089 | 0.050386 | 0.049882 | 0.049378 | 0.048873 | 0.048369
| TRG022-154491351 | TRG022 | 0.014618 | 0.01474 | 0.014863 | 0.014985 | 0.015108 | 0.015033 | 0.014958 | 0.014884 | 0.014809 | 0.014734 | 0.01466 | 0.014585 | 0.01451 | 0.014436 | 0.014361 | 0.014286 | 0.014212 | 0.014137 | 0.014062 | 0.013988
| TRG022-154491390 | TRG022 | 0.010601 | 0.010681 | 0.010761 | 0.010842 | 0.010922 | 0.010899 | 0.010877 | 0.010855 | 0.010832 | 0.01081 | 0.010787 | 0.010765 | 0.010743 | 0.01072 | 0.010698 | 0.010675 | 0.010653 | 0.010631 | 0.010608 | 0.010586
| TRG022-158166546 | TRG022 | 0.0010236 | 0.0010318 | 0.00104 | 0.0010481 | 0.0010563 | 0.0010479 | 0.0010394 | 0.0010309 | 0.0010224 | 0.0010139 | 0.0010055 | 0.00099699 | 0.00098851 | 0.00098003 | 0.00097155 | 0.00096307 | 0.00095459 | 0.00094611 | 0.00093764 | 0.00092916
| TRG022-158166693 | TRG022 | 0.010384 | 0.010493 | 0.010603 | 0.010712 | 0.010821 | 0.010669 | 0.010516 | 0.010363 | 0.01021 | 0.010057 | 0.0099043 | 0.0097515 | 0.0095986 | 0.0094458 | 0.0092929 | 0.0091401 | 0.0089872 | 0.0088344 | 0.0086815 | 0.0085287
| TRG022-158166806 | TRG022 | 0.032746 | 0.033022 | 0.033298 | 0.033574 | 0.033849 | 0.033541 | 0.033232 | 0.032924 | 0.032615 | 0.032307 | 0.031998 | 0.03169 | 0.031381 | 0.031072 | 0.030764 | 0.030455 | 0.030147 | 0.029838 | 0.02953 | 0.029221
| TRG022-158204991 | TRG022 | 0.063089 | 0.063571 | 0.064052 | 0.064534 | 0.065016 | 0.064555 | 0.064094 | 0.063633 | 0.063172 | 0.062711 | 0.06225 | 0.061789 | 0.061327 | 0.060866 | 0.060405 | 0.059944 | 0.059483 | 0.059022 | 0.058561 | 0.0581
| TRG022-158205190 | TRG022 | 0.031438 | 0.031612 | 0.031787 | 0.031961 | 0.032136 | 0.032017 | 0.031899 | 0.03178 | 0.031662 | 0.031543 | 0.031425 | 0.031306 | 0.031187 | 0.031069 | 0.03095 | 0.030832 | 0.030713 | 0.030595 | 0.030476 | 0.030358
| TRG022-158205316 | TRG022 | 0.078029 | 0.078773 | 0.079517 | 0.080261 | 0.081004 | 0.079982 | 0.07896 | 0.077938 | 0.076916 | 0.075894 | 0.074872 | 0.07385 | 0.072828 | 0.071806 | 0.070784 | 0.069762 | 0.06874 | 0.067718 | 0.066696 | 0.065674
| TRG022-158205503 | TRG022 | 0.10711 | 0.10829 | 0.10948 | 0.11066 | 0.11184 | 0.11082 | 0.1098 | 0.10878 | 0.10776 | 0.10674 | 0.10572 | 0.10469 | 0.10367 | 0.10265 | 0.10163 | 0.10061 | 0.099589 | 0.098568 | 0.097547 | 0.096526
| TRG022-158205673 | TRG022 | 0.0012302 | 0.0012442 | 0.0012583 | 0.0012723 | 0.0012864 | 0.0012656 | 0.0012449 | 0.0012241 | 0.0012034 | 0.0011826 | 0.0011618 | 0.0011411 | 0.0011203 | 0.0010996 | 0.0010788 | 0.001058 | 0.0010373 | 0.0010165 | 0.00099576 | 0.000975
| TRG022-158205847 | TRG022 | 0.00089003 | 0.00089983 | 0.00090962 | 0.00091941 | 0.0009292 | 0.00091816 | 0.00090712 | 0.00089608 | 0.00088504 | 0.000874 | 0.00086296 | 0.00085192 | 0.00084088 | 0.00082984 | 0.0008188 | 0.00080776 | 0.00079672 | 0.00078568 | 0.00077464 | 0.0007636
| TRG022-158206040 | TRG022 | 0.00019668 | 0.00019896 | 0.00020124 | 0.00020352 | 0.0002058 | 0.00020342 | 0.00020104 | 0.00019866 | 0.00019628 | 0.0001939 | 0.00019152 | 0.00018914 | 0.00018676 | 0.00018438 | 0.000182 | 0.00017962 | 0.00017724 | 0.00017486 | 0.00017248 | 0.0001701
| TRG022-160930593 | TRG022 | 0.029562 | 0.029839 | 0.030117 | 0.030395 | 0.030673 | 0.030352 | 0.030031 | 0.02971 | 0.029388 | 0.029067 | 0.028746 | 0.028425 | 0.028103 | 0.027782 | 0.027461 | 0.02714 | 0.026818 | 0.026497 | 0.026176 | 0.025855
| TRG022-163035515 | TRG022 | 3.028e-05 | 3.064e-05 | 3.1e-05 | 3.136e-05 | 3.172e-05 | 3.13e-05 | 3.088e-05 | 3.046e-05 | 3.004e-05 | 2.962e-05 | 2.92e-05 | 2.878e-05 | 2.836e-05 | 2.794e-05 | 2.752e-05 | 2.71e-05 | 2.668e-05 | 2.626e-05 | 2.584e-05 | 2.542e-05
| TRG022-163035708 | TRG022 | 0.00013267 | 0.00013445 | 0.00013623 | 0.00013802 | 0.0001398 | 0.00013782 | 0.00013584 | 0.00013386 | 0.00013188 | 0.0001299 | 0.00012792 | 0.00012594 | 0.00012396 | 0.00012198 | 0.00012 | 0.00011802 | 0.00011604 | 0.00011406 | 0.00011208 | 0.0001101
| TRG022-163035922 | TRG022 | 0.0040632 | 0.0041042 | 0.0041452 | 0.0041861 | 0.0042271 | 0.0041763 | 0.0041254 | 0.0040746 | 0.0040238 | 0.0039729 | 0.0039221 | 0.0038713 | 0.0038204 | 0.0037696 | 0.0037188 | 0.0036679 | 0.0036171 | 0.0035663 | 0.0035154 | 0.0034646
| TRG022-163036120 | TRG022 | 5.3789e-05 | 5.4341e-05 | 5.4894e-05 | 5.5447e-05 | 5.6e-05 | 5.5642e-05 | 5.5285e-05 | 5.4927e-05 | 5.457e-05 | 5.4213e-05 | 5.3855e-05 | 5.3498e-05 | 5.314e-05 | 5.2783e-05 | 5.2425e-05 | 5.2068e-05 | 5.171e-05 | 5.1353e-05 | 5.0995e-05 | 5.0638e-05
| TRG022-163036215 | TRG022 | 1.6875e-05 | 1.7082e-05 | 1.7288e-05 | 1.7494e-05 | 1.77e-05 | 1.7447e-05 | 1.7194e-05 | 1.6942e-05 | 1.6689e-05 | 1.6436e-05 | 1.6183e-05 | 1.5931e-05 | 1.5678e-05 | 1.5425e-05 | 1.5172e-05 | 1.492e-05 | 1.4667e-05 | 1.4414e-05 | 1.4161e-05 | 1.3909e-05
| TRG022-171344186 | TRG022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG022-176898220 | TRG022 | 9.2372 | 9.3155 | 9.3938 | 9.4721 | 9.5504 | 9.469 | 9.3876 | 9.3063 | 9.2249 | 9.1435 | 9.0621 | 8.9808 | 8.8994 | 8.818 | 8.7366 | 8.6553 | 8.5739 | 8.4925 | 8.4111 | 8.3298
| TRG022-176898350 | TRG022 | 0.95794 | 0.95977 | 0.96159 | 0.96341 | 0.96524 | 0.96333 | 0.96143 | 0.95953 | 0.95763 | 0.95573 | 0.95383 | 0.95193 | 0.95003 | 0.94813 | 0.94623 | 0.94433 | 0.94243 | 0.94053 | 0.93862 | 0.93672
| TRG022-176898385 | TRG022 | 0.58159 | 0.58605 | 0.59051 | 0.59496 | 0.59942 | 0.59358 | 0.58774 | 0.5819 | 0.57605 | 0.57021 | 0.56437 | 0.55853 | 0.55269 | 0.54684 | 0.541 | 0.53516 | 0.52932 | 0.52348 | 0.51763 | 0.51179
| TRG022-185851624 | TRG022 | 2.2361 | 2.2618 | 2.2876 | 2.3134 | 2.3391 | 2.3124 | 2.2856 | 2.2588 | 2.232 | 2.2052 | 2.1784 | 2.1517 | 2.1249 | 2.0981 | 2.0713 | 2.0445 | 2.0178 | 1.991 | 1.9642 | 1.9374
| TRG022-24598160 | TRG022 | 0.86191 | 0.8686 | 0.8753 | 0.88199 | 0.88868 | 0.87922 | 0.86975 | 0.86028 | 0.85082 | 0.84135 | 0.83189 | 0.82242 | 0.81295 | 0.80349 | 0.79402 | 0.78455 | 0.77509 | 0.76562 | 0.75616 | 0.74669
| TRG022-24598202 | TRG022 | 0.65409 | 0.66095 | 0.66782 | 0.67469 | 0.68156 | 0.67546 | 0.66936 | 0.66326 | 0.65716 | 0.65106 | 0.64496 | 0.63887 | 0.63277 | 0.62667 | 0.62057 | 0.61447 | 0.60837 | 0.60227 | 0.59618 | 0.59008
| TRG024-117365806 | TRG024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-158041024 | TRG024 | 0.015839 | 0.015943 | 0.016047 | 0.016152 | 0.016256 | 0.016121 | 0.015986 | 0.015852 | 0.015717 | 0.015583 | 0.015448 | 0.015313 | 0.015179 | 0.015044 | 0.014909 | 0.014775 | 0.01464 | 0.014505 | 0.014371 | 0.014236
| TRG024-158742698 | TRG024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-162822011 | TRG024 | 0.0037931 | 0.0038289 | 0.0038647 | 0.0039005 | 0.0039362 | 0.0038699 | 0.0038035 | 0.0037371 | 0.0036707 | 0.0036043 | 0.0035379 | 0.0034716 | 0.0034052 | 0.0033388 | 0.0032724 | 0.003206 | 0.0031396 | 0.0030733 | 0.0030069 | 0.0029405
| TRG024-162822186 | TRG024 | 5.6054e-06 | 5.695e-06 | 5.7847e-06 | 5.8743e-06 | 5.964e-06 | 5.8227e-06 | 5.6814e-06 | 5.5401e-06 | 5.3988e-06 | 5.2575e-06 | 5.1162e-06 | 4.9749e-06 | 4.8336e-06 | 4.6923e-06 | 4.551e-06 | 4.4097e-06 | 4.2684e-06 | 4.1271e-06 | 3.9858e-06 | 3.8445e-06
| TRG024-162822411 | TRG024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRG024-162822646 | TRG024 | 5.7036e-07 | 5.7582e-07 | 5.8128e-07 | 5.8674e-07 | 5.922e-07 | 5.7883e-07 | 5.6546e-07 | 5.5209e-07 | 5.3872e-07 | 5.2535e-07 | 5.1198e-07 | 4.9861e-07 | 4.8524e-07 | 4.7187e-07 | 4.585e-07 | 4.4513e-07 | 4.3176e-07 | 4.1839e-07 | 4.0502e-07 | 3.9165e-07
| TRG024-162822850 | TRG024 | 0.0090488 | 0.0091401 | 0.0092314 | 0.0093227 | 0.009414 | 0.0092603 | 0.0091066 | 0.0089529 | 0.0087992 | 0.0086455 | 0.0084918 | 0.0083382 | 0.0081845 | 0.0080308 | 0.0078771 | 0.0077234 | 0.0075697 | 0.007416 | 0.0072623 | 0.0071086
| TRG024-162823024 | TRG024 | 2.8546e-05 | 2.879e-05 | 2.9033e-05 | 2.9277e-05 | 2.952e-05 | 2.916e-05 | 2.88e-05 | 2.844e-05 | 2.808e-05 | 2.772e-05 | 2.736e-05 | 2.7e-05 | 2.664e-05 | 2.628e-05 | 2.592e-05 | 2.556e-05 | 2.52e-05 | 2.484e-05 | 2.448e-05 | 2.412e-05
| TRG024-162823256 | TRG024 | 2.1966e-05 | 2.2212e-05 | 2.2458e-05 | 2.2704e-05 | 2.295e-05 | 2.2519e-05 | 2.2089e-05 | 2.1658e-05 | 2.1228e-05 | 2.0797e-05 | 2.0367e-05 | 1.9936e-05 | 1.9506e-05 | 1.9075e-05 | 1.8645e-05 | 1.8214e-05 | 1.7784e-05 | 1.7353e-05 | 1.6923e-05 | 1.6492e-05
| TRG024-185851718 | TRG024 | 0.00019585 | 0.00019842 | 0.00020099 | 0.00020356 | 0.00020613 | 0.00020372 | 0.00020131 | 0.00019889 | 0.00019648 | 0.00019407 | 0.00019166 | 0.00018924 | 0.00018683 | 0.00018442 | 0.000182 | 0.00017959 | 0.00017718 | 0.00017477 | 0.00017235 | 0.00016994
| TRG024-24598286 | TRG024 | 0.090495 | 0.091294 | 0.092094 | 0.092894 | 0.093694 | 0.092199 | 0.090704 | 0.089209 | 0.087714 | 0.086219 | 0.084724 | 0.083229 | 0.081734 | 0.080239 | 0.078744 | 0.077249 | 0.075754 | 0.074259 | 0.072764 | 0.07127
| TRG024-60700588 | TRG024 | 0.57057 | 0.57681 | 0.58306 | 0.5893 | 0.59555 | 0.5851 | 0.57465 | 0.56421 | 0.55376 | 0.54331 | 0.53286 | 0.52242 | 0.51197 | 0.50152 | 0.49107 | 0.48063 | 0.47018 | 0.45973 | 0.44928 | 0.43884
| TRG024-74127795 | TRG024 | 1.7966 | 1.8153 | 1.8339 | 1.8525 | 1.8712 | 1.8534 | 1.8356 | 1.8179 | 1.8001 | 1.7823 | 1.7645 | 1.7468 | 1.729 | 1.7112 | 1.6934 | 1.6757 | 1.6579 | 1.6401 | 1.6224 | 1.6046
| WBE011-203216132 | WBE011 | 7.1367 | 7.1712 | 7.2057 | 7.2403 | 7.2748 | 7.2862 | 7.2977 | 7.3091 | 7.3206 | 7.332 | 7.3435 | 7.3549 | 7.3663 | 7.3778 | 7.3892 | 7.4007 | 7.4121 | 7.4236 | 7.435 | 7.4464
| WBE011-41045910 | WBE011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE012-203216204 | WBE012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE013-203216284 | WBE013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE014-203216348 | WBE014 | 7.8515 | 7.9026 | 7.9537 | 8.0047 | 8.0558 | 8.0802 | 8.1046 | 8.129 | 8.1534 | 8.1778 | 8.2022 | 8.2266 | 8.2509 | 8.2753 | 8.2997 | 8.3241 | 8.3485 | 8.3729 | 8.3973 | 8.4217
| WBE021-203216532 | WBE021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE022-203216606 | WBE022 | 9.0139 | 9.082 | 9.1501 | 9.2183 | 9.2864 | 9.3012 | 9.316 | 9.3308 | 9.3456 | 9.3604 | 9.3752 | 9.39 | 9.4048 | 9.4196 | 9.4344 | 9.4491 | 9.4639 | 9.4787 | 9.4935 | 9.5083
| WBE023-139765778 | WBE023 | 5.8197 | 5.8591 | 5.8985 | 5.9379 | 5.9774 | 5.9959 | 6.0145 | 6.0331 | 6.0517 | 6.0703 | 6.0889 | 6.1075 | 6.1261 | 6.1446 | 6.1632 | 6.1818 | 6.2004 | 6.219 | 6.2376 | 6.2562
| WBE023-203216893 | WBE023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE024-203216929 | WBE024 | 4.7817 | 4.82 | 4.8584 | 4.8967 | 4.935 | 4.9584 | 4.9818 | 5.0052 | 5.0286 | 5.052 | 5.0754 | 5.0988 | 5.1222 | 5.1457 | 5.1691 | 5.1925 | 5.2159 | 5.2393 | 5.2627 | 5.2861
| WBE031-15425070 | WBE031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE031-203217123 | WBE031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE031-24612962 | WBE031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE032-203217195 | WBE032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE032-24612505 | WBE032 | 22.544 | 22.6807 | 22.8174 | 22.9541 | 23.0908 | 23.1312 | 23.1717 | 23.2121 | 23.2525 | 23.2929 | 23.3333 | 23.3737 | 23.4141 | 23.4545 | 23.4949 | 23.5354 | 23.5758 | 23.6162 | 23.6566 | 23.697
| WBE033-203217267 | WBE033 | 39.5177 | 39.7879 | 40.058 | 40.3282 | 40.5984 | 40.766 | 40.9336 | 41.1012 | 41.2689 | 41.4365 | 41.6041 | 41.7717 | 41.9393 | 42.1069 | 42.2746 | 42.4422 | 42.6098 | 42.7774 | 42.945 | 43.1126
| WBE033-65838252 | WBE033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBE034-182145993 | WBE034 | 0.027051 | 0.027264 | 0.027476 | 0.027689 | 0.027902 | 0.027978 | 0.028054 | 0.02813 | 0.028206 | 0.028282 | 0.028358 | 0.028434 | 0.02851 | 0.028586 | 0.028662 | 0.028739 | 0.028815 | 0.028891 | 0.028967 | 0.029043
| WBE034-203217365 | WBE034 | 0.00638 | 0.0064416 | 0.0065032 | 0.0065648 | 0.0066264 | 0.0066455 | 0.0066646 | 0.0066837 | 0.0067029 | 0.006722 | 0.0067411 | 0.0067603 | 0.0067794 | 0.0067985 | 0.0068177 | 0.0068368 | 0.0068559 | 0.006875 | 0.0068942 | 0.0069133
| WBE034-24612477 | WBE034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL002-15395911 | WBL002 | 0.30296 | 0.30529 | 0.30762 | 0.30995 | 0.31228 | 0.30937 | 0.30646 | 0.30355 | 0.30064 | 0.29773 | 0.29483 | 0.29192 | 0.28901 | 0.2861 | 0.28319 | 0.28028 | 0.27738 | 0.27447 | 0.27156 | 0.26865
| WBL002-15395961 | WBL002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL002-163162028 | WBL002 | 6.8229e-07 | 6.8871e-07 | 6.9514e-07 | 7.0157e-07 | 7.08e-07 | 6.933e-07 | 6.786e-07 | 6.639e-07 | 6.492e-07 | 6.345e-07 | 6.198e-07 | 6.051e-07 | 5.904e-07 | 5.757e-07 | 5.61e-07 | 5.463e-07 | 5.316e-07 | 5.169e-07 | 5.022e-07 | 4.875e-07
| WBL003-15396013 | WBL003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL003-15396026 | WBL003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL003-15396039 | WBL003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL004-15395887 | WBL004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL004-24598022 | WBL004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL005-153526296 | WBL005 | 1.7972 | 1.8127 | 1.8282 | 1.8437 | 1.8592 | 1.8296 | 1.8 | 1.7704 | 1.7408 | 1.7112 | 1.6816 | 1.652 | 1.6224 | 1.5928 | 1.5631 | 1.5335 | 1.5039 | 1.4743 | 1.4447 | 1.4151
| WBL005-15396050 | WBL005 | 0.50436 | 0.50646 | 0.50857 | 0.51068 | 0.51279 | 0.51018 | 0.50756 | 0.50495 | 0.50234 | 0.49973 | 0.49711 | 0.4945 | 0.49189 | 0.48928 | 0.48666 | 0.48405 | 0.48144 | 0.47883 | 0.47621 | 0.4736
| WBL005-158638825 | WBL005 | 0.01544 | 0.015612 | 0.015784 | 0.015956 | 0.016128 | 0.015892 | 0.015655 | 0.015418 | 0.015181 | 0.014944 | 0.014707 | 0.01447 | 0.014233 | 0.013996 | 0.013759 | 0.013522 | 0.013286 | 0.013049 | 0.012812 | 0.012575
| WBL005-158639092 | WBL005 | 0.002411 | 0.0024295 | 0.0024479 | 0.0024664 | 0.0024849 | 0.0024446 | 0.0024044 | 0.0023641 | 0.0023239 | 0.0022836 | 0.0022433 | 0.0022031 | 0.0021628 | 0.0021226 | 0.0020823 | 0.002042 | 0.0020018 | 0.0019615 | 0.0019213 | 0.001881
| WBL005-158702306 | WBL005 | 0.062577 | 0.062654 | 0.062731 | 0.062808 | 0.062884 | 0.062789 | 0.062693 | 0.062597 | 0.062502 | 0.062406 | 0.06231 | 0.062215 | 0.062119 | 0.062023 | 0.061928 | 0.061832 | 0.061737 | 0.061641 | 0.061545 | 0.06145
| WBL005-163161673 | WBL005 | 0.00010996 | 0.00011134 | 0.00011273 | 0.00011411 | 0.0001155 | 0.00011392 | 0.00011235 | 0.00011077 | 0.0001092 | 0.00010763 | 0.00010605 | 0.00010448 | 0.0001029 | 0.00010133 | 9.975e-05 | 9.8175e-05 | 9.66e-05 | 9.5025e-05 | 9.345e-05 | 9.1875e-05
| WBL005-163161826 | WBL005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL006-15435914 | WBL006 | 0.00026023 | 0.00026243 | 0.00026463 | 0.00026682 | 0.00026902 | 0.00026628 | 0.00026354 | 0.0002608 | 0.00025806 | 0.00025532 | 0.00025258 | 0.00024985 | 0.00024711 | 0.00024437 | 0.00024163 | 0.00023889 | 0.00023615 | 0.00023341 | 0.00023067 | 0.00022793
| WBL008-15395863 | WBL008 | 1.133 | 1.1358 | 1.1385 | 1.1413 | 1.1441 | 1.1407 | 1.1373 | 1.1339 | 1.1305 | 1.1271 | 1.1237 | 1.1203 | 1.1169 | 1.1135 | 1.1101 | 1.1067 | 1.1033 | 1.0999 | 1.0965 | 1.0931
| WBL010-15395826 | WBL010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-153865449 | WBL012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-162960471 | WBL012 | 2.4908e-06 | 2.5138e-06 | 2.5369e-06 | 2.5599e-06 | 2.583e-06 | 2.5426e-06 | 2.5023e-06 | 2.462e-06 | 2.4216e-06 | 2.3813e-06 | 2.3409e-06 | 2.3006e-06 | 2.2602e-06 | 2.2199e-06 | 2.1795e-06 | 2.1392e-06 | 2.0988e-06 | 2.0585e-06 | 2.0181e-06 | 1.9778e-06
| WBL012-162960671 | WBL012 | 2.7216e-05 | 2.7552e-05 | 2.7888e-05 | 2.8224e-05 | 2.856e-05 | 2.7978e-05 | 2.7396e-05 | 2.6814e-05 | 2.6232e-05 | 2.565e-05 | 2.5068e-05 | 2.4486e-05 | 2.3904e-05 | 2.3322e-05 | 2.274e-05 | 2.2158e-05 | 2.1576e-05 | 2.0994e-05 | 2.0412e-05 | 1.983e-05
| WBL012-162960865 | WBL012 | 5.9277e-05 | 5.9907e-05 | 6.0538e-05 | 6.1169e-05 | 6.18e-05 | 6.0366e-05 | 5.8932e-05 | 5.7498e-05 | 5.6064e-05 | 5.463e-05 | 5.3196e-05 | 5.1762e-05 | 5.0328e-05 | 4.8894e-05 | 4.746e-05 | 4.6026e-05 | 4.4592e-05 | 4.3158e-05 | 4.1724e-05 | 4.029e-05
| WBL012-163034361 | WBL012 | 2.3079e-05 | 2.3385e-05 | 2.369e-05 | 2.3995e-05 | 2.43e-05 | 2.3883e-05 | 2.3466e-05 | 2.3049e-05 | 2.2632e-05 | 2.2215e-05 | 2.1798e-05 | 2.1381e-05 | 2.0964e-05 | 2.0547e-05 | 2.013e-05 | 1.9713e-05 | 1.9296e-05 | 1.8879e-05 | 1.8462e-05 | 1.8045e-05
| WBL012-163034588 | WBL012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163150328 | WBL012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163162276 | WBL012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163162391 | WBL012 | 0.00087727 | 0.00088537 | 0.00089348 | 0.00090159 | 0.0009097 | 0.00089694 | 0.00088418 | 0.00087142 | 0.00085866 | 0.0008459 | 0.00083314 | 0.00082038 | 0.00080762 | 0.00079486 | 0.0007821 | 0.00076934 | 0.00075658 | 0.00074382 | 0.00073106 | 0.0007183
| WBL012-163162602 | WBL012 | 0.00046781 | 0.00047399 | 0.00048016 | 0.00048633 | 0.0004925 | 0.00048435 | 0.0004762 | 0.00046805 | 0.0004599 | 0.00045175 | 0.0004436 | 0.00043545 | 0.0004273 | 0.00041915 | 0.000411 | 0.00040285 | 0.0003947 | 0.00038655 | 0.0003784 | 0.00037025
| WBL012-163162797 | WBL012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163162997 | WBL012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WBL012-163205557 | WBL012 | 4.2808e-05 | 4.3266e-05 | 4.3724e-05 | 4.4182e-05 | 4.464e-05 | 4.36e-05 | 4.256e-05 | 4.152e-05 | 4.048e-05 | 3.944e-05 | 3.84e-05 | 3.736e-05 | 3.632e-05 | 3.528e-05 | 3.4239e-05 | 3.3199e-05 | 3.2159e-05 | 3.1119e-05 | 3.0079e-05 | 2.9039e-05
| WBL012-163205740 | WBL012 | 3.9136e-10 | 3.9464e-10 | 3.9793e-10 | 4.0121e-10 | 4.045e-10 | 4.004e-10 | 3.963e-10 | 3.922e-10 | 3.881e-10 | 3.84e-10 | 3.799e-10 | 3.758e-10 | 3.717e-10 | 3.676e-10 | 3.635e-10 | 3.594e-10 | 3.553e-10 | 3.512e-10 | 3.471e-10 | 3.43e-10
| WBL012-171331101 | WBL012 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834
| WBL012-24598048 | WBL012 | 1.9193 | 1.9265 | 1.9337 | 1.9409 | 1.9481 | 1.9353 | 1.9225 | 1.9097 | 1.8969 | 1.884 | 1.8712 | 1.8584 | 1.8456 | 1.8328 | 1.82 | 1.8072 | 1.7943 | 1.7815 | 1.7687 | 1.7559
| WBL012-24611149 | WBL012 | 0.25271 | 0.2552 | 0.25769 | 0.26018 | 0.26267 | 0.25934 | 0.25601 | 0.25269 | 0.24936 | 0.24603 | 0.24271 | 0.23938 | 0.23605 | 0.23273 | 0.2294 | 0.22607 | 0.22274 | 0.21942 | 0.21609 | 0.21276
| WBL012-88823662 | WBL012 | 0.23852 | 0.23882 | 0.23912 | 0.23942 | 0.23972 | 0.23935 | 0.23899 | 0.23862 | 0.23826 | 0.23789 | 0.23753 | 0.23716 | 0.23679 | 0.23643 | 0.23606 | 0.2357 | 0.23533 | 0.23497 | 0.2346 | 0.23424
| WIN011-124931073 | WIN011 | 0.053928 | 0.054491 | 0.055053 | 0.055616 | 0.056178 | 0.056016 | 0.055853 | 0.05569 | 0.055528 | 0.055365 | 0.055202 | 0.05504 | 0.054877 | 0.054714 | 0.054552 | 0.054389 | 0.054226 | 0.054064 | 0.053901 | 0.053738
| WIN011-154067565 | WIN011 | 1.2816 | 1.2945 | 1.3074 | 1.3203 | 1.3331 | 1.3254 | 1.3176 | 1.3099 | 1.3021 | 1.2944 | 1.2866 | 1.2789 | 1.2711 | 1.2633 | 1.2556 | 1.2478 | 1.2401 | 1.2323 | 1.2246 | 1.2168
| WIN011-155049323 | WIN011 | 0.00058411 | 0.00059083 | 0.00059755 | 0.00060428 | 0.000611 | 0.00060833 | 0.00060567 | 0.000603 | 0.00060034 | 0.00059767 | 0.00059501 | 0.00059234 | 0.00058968 | 0.00058701 | 0.00058435 | 0.00058168 | 0.00057902 | 0.00057635 | 0.00057369 | 0.00057102
| WIN011-157092882 | WIN011 | 0.17408 | 0.1758 | 0.17752 | 0.17924 | 0.18096 | 0.18019 | 0.17942 | 0.17865 | 0.17788 | 0.17711 | 0.17634 | 0.17557 | 0.1748 | 0.17403 | 0.17326 | 0.17249 | 0.17172 | 0.17096 | 0.17019 | 0.16942
| WIN011-160628518 | WIN011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN011-160628528 | WIN011 | 20.8687 | 21.0708 | 21.273 | 21.4752 | 21.6774 | 21.5549 | 21.4325 | 21.3101 | 21.1877 | 21.0652 | 20.9428 | 20.8204 | 20.6979 | 20.5755 | 20.4531 | 20.3306 | 20.2082 | 20.0858 | 19.9633 | 19.8409
| WIN011-72970601 | WIN011 | 0.085638 | 0.086516 | 0.087394 | 0.088271 | 0.089149 | 0.08933 | 0.089511 | 0.089693 | 0.089874 | 0.090055 | 0.090236 | 0.090417 | 0.090598 | 0.090779 | 0.09096 | 0.091141 | 0.091323 | 0.091504 | 0.091685 | 0.091866
| WIN011-72970660 | WIN011 | 0.12089 | 0.12234 | 0.12378 | 0.12523 | 0.12667 | 0.12648 | 0.12628 | 0.12608 | 0.12589 | 0.12569 | 0.12549 | 0.1253 | 0.1251 | 0.1249 | 0.12471 | 0.12451 | 0.12431 | 0.12412 | 0.12392 | 0.12372
| WIN011-77738018 | WIN011 | 0.07007 | 0.070864 | 0.071659 | 0.072453 | 0.073247 | 0.072776 | 0.072304 | 0.071833 | 0.071362 | 0.070891 | 0.07042 | 0.069949 | 0.069478 | 0.069007 | 0.068536 | 0.068065 | 0.067594 | 0.067123 | 0.066652 | 0.066181
| WIN022-160628376 | WIN022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN022-160628386 | WIN022 | 11.9332 | 12.0331 | 12.1331 | 12.233 | 12.3329 | 12.3096 | 12.2863 | 12.263 | 12.2397 | 12.2164 | 12.1931 | 12.1698 | 12.1465 | 12.1232 | 12.0999 | 12.0766 | 12.0533 | 12.03 | 12.0068 | 11.9835
| WIN022-164674921 | WIN022 | 8.3371e-05 | 8.4229e-05 | 8.5086e-05 | 8.5943e-05 | 8.68e-05 | 8.665e-05 | 8.65e-05 | 8.635e-05 | 8.62e-05 | 8.605e-05 | 8.59e-05 | 8.575e-05 | 8.56e-05 | 8.545e-05 | 8.53e-05 | 8.515e-05 | 8.5e-05 | 8.485e-05 | 8.47e-05 | 8.455e-05
| WIN022-164675227 | WIN022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN022-183128966 | WIN022 | 0.002549 | 0.0025661 | 0.0025833 | 0.0026004 | 0.0026175 | 0.0026157 | 0.002614 | 0.0026123 | 0.0026105 | 0.0026088 | 0.002607 | 0.0026053 | 0.0026036 | 0.0026018 | 0.0026001 | 0.0025983 | 0.0025966 | 0.0025949 | 0.0025931 | 0.0025914
| WIN022-79032273 | WIN022 | 0.00073894 | 0.00074546 | 0.00075197 | 0.00075849 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765
| WIN022-79245551 | WIN022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WIN023-154876693 | WIN023 | 0.029934 | 0.03017 | 0.030406 | 0.030642 | 0.030877 | 0.030901 | 0.030924 | 0.030948 | 0.030971 | 0.030994 | 0.031018 | 0.031041 | 0.031064 | 0.031088 | 0.031111 | 0.031134 | 0.031158 | 0.031181 | 0.031205 | 0.031228
| WIN023-154908067 | WIN023 | 0.00012981 | 0.00013115 | 0.0001325 | 0.00013385 | 0.0001352 | 0.00013528 | 0.00013536 | 0.00013544 | 0.00013552 | 0.0001356 | 0.00013568 | 0.00013576 | 0.00013584 | 0.00013592 | 0.000136 | 0.00013608 | 0.00013616 | 0.00013624 | 0.00013632 | 0.0001364
| WIN023-160628335 | WIN023 | 6.582 | 6.6322 | 6.6824 | 6.7325 | 6.7827 | 6.7962 | 6.8097 | 6.8232 | 6.8367 | 6.8502 | 6.8637 | 6.8772 | 6.8906 | 6.9041 | 6.9176 | 6.9311 | 6.9446 | 6.9581 | 6.9716 | 6.9851
| WIN023-73352598 | WIN023 | 0.0051598 | 0.0052311 | 0.0053025 | 0.0053738 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452
| WIN023-84419247 | WIN023 | 0.0015749 | 0.0015927 | 0.0016105 | 0.0016282 | 0.001646 | 0.001648 | 0.00165 | 0.001652 | 0.001654 | 0.001656 | 0.001658 | 0.00166 | 0.001662 | 0.001664 | 0.001666 | 0.001668 | 0.00167 | 0.001672 | 0.001674 | 0.001676
| WMN013-117981106 | WMN013 | 0.62948 | 0.63303 | 0.63659 | 0.64014 | 0.6437 | 0.64173 | 0.63976 | 0.6378 | 0.63583 | 0.63386 | 0.6319 | 0.62993 | 0.62796 | 0.62599 | 0.62403 | 0.62206 | 0.62009 | 0.61813 | 0.61616 | 0.61419
| WMN013-24614054 | WMN013 | 1.8633 | 1.8774 | 1.8915 | 1.9056 | 1.9196 | 1.9161 | 1.9127 | 1.9092 | 1.9057 | 1.9022 | 1.8987 | 1.8952 | 1.8918 | 1.8883 | 1.8848 | 1.8813 | 1.8778 | 1.8743 | 1.8708 | 1.8674
| WMN014-122227235 | WMN014 | 1.3716 | 1.3735 | 1.3754 | 1.3774 | 1.3793 | 1.3766 | 1.3738 | 1.371 | 1.3683 | 1.3655 | 1.3627 | 1.36 | 1.3572 | 1.3545 | 1.3517 | 1.3489 | 1.3462 | 1.3434 | 1.3406 | 1.3379
| WMN014-164366245 | WMN014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WMN014-42253278 | WMN014 | 0.012478 | 0.012597 | 0.012715 | 0.012834 | 0.012952 | 0.012954 | 0.012955 | 0.012957 | 0.012958 | 0.012959 | 0.012961 | 0.012962 | 0.012964 | 0.012965 | 0.012967 | 0.012968 | 0.012969 | 0.012971 | 0.012972 | 0.012974
| WMN014-62615661 | WMN014 | 0.9741 | 0.98168 | 0.98927 | 0.99685 | 1.0044 | 1.0033 | 1.0022 | 1.0012 | 1.0001 | 0.99896 | 0.99786 | 0.99677 | 0.99567 | 0.99458 | 0.99348 | 0.99238 | 0.99129 | 0.99019 | 0.9891 | 0.988
| WMN021-160652994 | WMN021 | 0.0072323 | 0.0073048 | 0.0073772 | 0.0074497 | 0.0075221 | 0.0075163 | 0.0075104 | 0.0075045 | 0.0074987 | 0.0074928 | 0.0074869 | 0.007481 | 0.0074752 | 0.0074693 | 0.0074634 | 0.0074576 | 0.0074517 | 0.0074458 | 0.00744 | 0.0074341
| WMN021-164365974 | WMN021 | 0.009799 | 0.0098753 | 0.0099516 | 0.010028 | 0.010104 | 0.010102 | 0.010101 | 0.010099 | 0.010097 | 0.010095 | 0.010093 | 0.010091 | 0.01009 | 0.010088 | 0.010086 | 0.010084 | 0.010082 | 0.01008 | 0.010078 | 0.010077
| WMN021-24614498 | WMN021 | 0.026867 | 0.027091 | 0.027316 | 0.02754 | 0.027765 | 0.027758 | 0.027752 | 0.027746 | 0.02774 | 0.027734 | 0.027728 | 0.027722 | 0.027716 | 0.02771 | 0.027704 | 0.027698 | 0.027692 | 0.027686 | 0.02768 | 0.027674
| WMN021-24614598 | WMN021 | 0.10129 | 0.10221 | 0.10313 | 0.10405 | 0.10497 | 0.10488 | 0.10479 | 0.1047 | 0.10461 | 0.10452 | 0.10443 | 0.10434 | 0.10425 | 0.10416 | 0.10407 | 0.10398 | 0.10389 | 0.1038 | 0.10371 | 0.10362
| WMN021-65221877 | WMN021 | 0.29411 | 0.29638 | 0.29865 | 0.30091 | 0.30318 | 0.30253 | 0.30188 | 0.30123 | 0.30058 | 0.29993 | 0.29927 | 0.29862 | 0.29797 | 0.29732 | 0.29667 | 0.29602 | 0.29537 | 0.29472 | 0.29407 | 0.29342
| WND011-15425526 | WND011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND011-200942344 | WND011 | 7.506 | 7.574 | 7.6419 | 7.7099 | 7.7779 | 7.8126 | 7.8474 | 7.8821 | 7.9169 | 7.9516 | 7.9864 | 8.0211 | 8.0559 | 8.0906 | 8.1254 | 8.1601 | 8.1949 | 8.2296 | 8.2644 | 8.2991
| WND011-74053613 | WND011 | 0.09133 | 0.092199 | 0.093068 | 0.093937 | 0.094806 | 0.095546 | 0.096285 | 0.097025 | 0.097764 | 0.098504 | 0.099243 | 0.099983 | 0.10072 | 0.10146 | 0.1022 | 0.10294 | 0.10368 | 0.10442 | 0.10516 | 0.1059
| WND011-79727477 | WND011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND012-171309560 | WND012 | 0.018465 | 0.018647 | 0.018829 | 0.019011 | 0.019193 | 0.01934 | 0.019487 | 0.019634 | 0.019781 | 0.019928 | 0.020075 | 0.020222 | 0.020369 | 0.020516 | 0.020663 | 0.02081 | 0.020957 | 0.021105 | 0.021252 | 0.021399
| WND012-200942480 | WND012 | 79.173 | 79.9014 | 80.6299 | 81.3583 | 82.0868 | 82.5062 | 82.9255 | 83.3449 | 83.7643 | 84.1837 | 84.603 | 85.0224 | 85.4418 | 85.8611 | 86.2805 | 86.6999 | 87.1193 | 87.5386 | 87.958 | 88.3774
| WND012-24611463 | WND012 | 9.2844 | 9.3568 | 9.4291 | 9.5015 | 9.5739 | 9.5933 | 9.6128 | 9.6323 | 9.6518 | 9.6713 | 9.6908 | 9.7102 | 9.7297 | 9.7492 | 9.7687 | 9.7882 | 9.8076 | 9.8271 | 9.8466 | 9.8661
| WND012-72499182 | WND012 | 0.066794 | 0.067405 | 0.068016 | 0.068627 | 0.069238 | 0.069369 | 0.0695 | 0.06963 | 0.069761 | 0.069892 | 0.070023 | 0.070154 | 0.070285 | 0.070415 | 0.070546 | 0.070677 | 0.070808 | 0.070939 | 0.07107 | 0.071201
| WND012-72499328 | WND012 | 0.34716 | 0.35016 | 0.35317 | 0.35617 | 0.35917 | 0.36171 | 0.36425 | 0.36678 | 0.36932 | 0.37186 | 0.3744 | 0.37694 | 0.37947 | 0.38201 | 0.38455 | 0.38709 | 0.38963 | 0.39216 | 0.3947 | 0.39724
| WND012-73767156 | WND012 | 0.18294 | 0.18459 | 0.18625 | 0.18791 | 0.18956 | 0.18987 | 0.19017 | 0.19048 | 0.19078 | 0.19108 | 0.19139 | 0.19169 | 0.192 | 0.1923 | 0.19261 | 0.19291 | 0.19321 | 0.19352 | 0.19382 | 0.19413
| WND012-74645078 | WND012 | 0.89266 | 0.90166 | 0.91066 | 0.91965 | 0.92865 | 0.9333 | 0.93795 | 0.94261 | 0.94726 | 0.95191 | 0.95656 | 0.96122 | 0.96587 | 0.97052 | 0.97517 | 0.97983 | 0.98448 | 0.98913 | 0.99378 | 0.99844
| WND012-74645220 | WND012 | 0.0439 | 0.044305 | 0.04471 | 0.045115 | 0.045521 | 0.04587 | 0.046219 | 0.046567 | 0.046916 | 0.047265 | 0.047614 | 0.047963 | 0.048312 | 0.048661 | 0.04901 | 0.049358 | 0.049707 | 0.050056 | 0.050405 | 0.050754
| WND012-77737071 | WND012 | 0.010129 | 0.010234 | 0.010339 | 0.010443 | 0.010548 | 0.010603 | 0.010658 | 0.010712 | 0.010767 | 0.010822 | 0.010877 | 0.010932 | 0.010987 | 0.011042 | 0.011097 | 0.011152 | 0.011206 | 0.011261 | 0.011316 | 0.011371
| WND012-78928850 | WND012 | 0.0011911 | 0.0012025 | 0.001214 | 0.0012254 | 0.0012369 | 0.001241 | 0.0012452 | 0.0012493 | 0.0012534 | 0.0012576 | 0.0012617 | 0.0012658 | 0.0012699 | 0.0012741 | 0.0012782 | 0.0012823 | 0.0012865 | 0.0012906 | 0.0012947 | 0.0012989
| WND012-85319302 | WND012 | 0.095769 | 0.096802 | 0.097835 | 0.098867 | 0.0999 | 0.10038 | 0.10085 | 0.10133 | 0.1018 | 0.10228 | 0.10275 | 0.10323 | 0.1037 | 0.10418 | 0.10466 | 0.10513 | 0.10561 | 0.10608 | 0.10656 | 0.10703
| WND012-88220025 | WND012 | 0.33223 | 0.3351 | 0.33797 | 0.34084 | 0.34371 | 0.34519 | 0.34667 | 0.34815 | 0.34963 | 0.35111 | 0.35259 | 0.35407 | 0.35555 | 0.35703 | 0.35851 | 0.35999 | 0.36147 | 0.36295 | 0.36443 | 0.36591
| WND012-93532503 | WND012 | 7.0576 | 7.132 | 7.2063 | 7.2806 | 7.355 | 7.3888 | 7.4227 | 7.4566 | 7.4904 | 7.5243 | 7.5582 | 7.5921 | 7.6259 | 7.6598 | 7.6937 | 7.7275 | 7.7614 | 7.7953 | 7.8291 | 7.863
| WND012-93532641 | WND012 | 4.7741 | 4.8244 | 4.8746 | 4.9248 | 4.9751 | 4.9904 | 5.0056 | 5.0209 | 5.0361 | 5.0514 | 5.0667 | 5.0819 | 5.0972 | 5.1124 | 5.1277 | 5.143 | 5.1582 | 5.1735 | 5.1887 | 5.204
| WND013-139460835 | WND013 | 12.2943 | 12.3994 | 12.5045 | 12.6095 | 12.7146 | 12.7766 | 12.8386 | 12.9006 | 12.9626 | 13.0246 | 13.0866 | 13.1486 | 13.2106 | 13.2726 | 13.3346 | 13.3966 | 13.4586 | 13.5206 | 13.5826 | 13.6446
| WND013-163356845 | WND013 | 0.0053192 | 0.005379 | 0.0054387 | 0.0054985 | 0.0055582 | 0.0055959 | 0.0056337 | 0.0056714 | 0.0057091 | 0.0057469 | 0.0057846 | 0.0058223 | 0.0058601 | 0.0058978 | 0.0059355 | 0.0059733 | 0.006011 | 0.0060487 | 0.0060865 | 0.0061242
| WND013-172348741 | WND013 | 0.011762 | 0.011881 | 0.012 | 0.012119 | 0.012238 | 0.012332 | 0.012426 | 0.012519 | 0.012613 | 0.012706 | 0.0128 | 0.012894 | 0.012987 | 0.013081 | 0.013174 | 0.013268 | 0.013362 | 0.013455 | 0.013549 | 0.013643
| WND013-200942552 | WND013 | 32.3802 | 32.6228 | 32.8654 | 33.108 | 33.3506 | 33.493 | 33.6353 | 33.7777 | 33.9201 | 34.0624 | 34.2048 | 34.3472 | 34.4895 | 34.6319 | 34.7743 | 34.9166 | 35.059 | 35.2014 | 35.3437 | 35.4861
| WND013-76546155 | WND013 | 0.28694 | 0.28952 | 0.2921 | 0.29468 | 0.29726 | 0.29883 | 0.3004 | 0.30197 | 0.30353 | 0.3051 | 0.30667 | 0.30824 | 0.30981 | 0.31138 | 0.31295 | 0.31452 | 0.31608 | 0.31765 | 0.31922 | 0.32079
| WND013-76546231 | WND013 | 0.52772 | 0.53225 | 0.53678 | 0.54131 | 0.54584 | 0.55036 | 0.55488 | 0.5594 | 0.56392 | 0.56844 | 0.57296 | 0.57748 | 0.582 | 0.58652 | 0.59104 | 0.59557 | 0.60009 | 0.60461 | 0.60913 | 0.61365
| WND013-76546307 | WND013 | 0.082613 | 0.083349 | 0.084085 | 0.084821 | 0.085557 | 0.086164 | 0.086771 | 0.087378 | 0.087986 | 0.088593 | 0.0892 | 0.089807 | 0.090414 | 0.091021 | 0.091629 | 0.092236 | 0.092843 | 0.09345 | 0.094057 | 0.094664
| WND013-76546404 | WND013 | 0.781 | 0.78801 | 0.79502 | 0.80203 | 0.80904 | 0.81501 | 0.82097 | 0.82694 | 0.8329 | 0.83887 | 0.84483 | 0.8508 | 0.85677 | 0.86273 | 0.8687 | 0.87466 | 0.88063 | 0.88659 | 0.89256 | 0.89852
| WND013-76546454 | WND013 | 0.069963 | 0.070652 | 0.071342 | 0.072032 | 0.072721 | 0.073342 | 0.073962 | 0.074583 | 0.075203 | 0.075824 | 0.076444 | 0.077064 | 0.077685 | 0.078305 | 0.078926 | 0.079546 | 0.080166 | 0.080787 | 0.081407 | 0.082028
| WND013-76546631 | WND013 | 0.031404 | 0.031685 | 0.031966 | 0.032246 | 0.032527 | 0.032791 | 0.033054 | 0.033318 | 0.033582 | 0.033845 | 0.034109 | 0.034372 | 0.034636 | 0.034899 | 0.035163 | 0.035426 | 0.03569 | 0.035953 | 0.036217 | 0.036481
| WND013-76546854 | WND013 | 0.18477 | 0.18664 | 0.18852 | 0.19039 | 0.19226 | 0.19341 | 0.19457 | 0.19572 | 0.19688 | 0.19803 | 0.19919 | 0.20034 | 0.2015 | 0.20265 | 0.20381 | 0.20496 | 0.20612 | 0.20727 | 0.20843 | 0.20958
| WND013-78928894 | WND013 | 0.020257 | 0.020482 | 0.020707 | 0.020932 | 0.021158 | 0.021345 | 0.021533 | 0.02172 | 0.021908 | 0.022096 | 0.022283 | 0.022471 | 0.022658 | 0.022846 | 0.023034 | 0.023221 | 0.023409 | 0.023596 | 0.023784 | 0.023972
| WND013-78928958 | WND013 | 0.41166 | 0.41531 | 0.41896 | 0.42261 | 0.42627 | 0.42954 | 0.43282 | 0.4361 | 0.43938 | 0.44266 | 0.44594 | 0.44922 | 0.4525 | 0.45577 | 0.45905 | 0.46233 | 0.46561 | 0.46889 | 0.47217 | 0.47545
| WND013-78929121 | WND013 | 0.10831 | 0.1094 | 0.11049 | 0.11158 | 0.11267 | 0.11328 | 0.1139 | 0.11451 | 0.11513 | 0.11574 | 0.11635 | 0.11697 | 0.11758 | 0.11819 | 0.11881 | 0.11942 | 0.12003 | 0.12065 | 0.12126 | 0.12187
| WND013-78929255 | WND013 | 0.039875 | 0.040263 | 0.040651 | 0.04104 | 0.041428 | 0.041612 | 0.041796 | 0.04198 | 0.042164 | 0.042348 | 0.042532 | 0.042716 | 0.0429 | 0.043084 | 0.043268 | 0.043452 | 0.043636 | 0.04382 | 0.044004 | 0.044188
| WND013-78929377 | WND013 | 0.11628 | 0.11758 | 0.11887 | 0.12016 | 0.12145 | 0.12211 | 0.12276 | 0.12342 | 0.12407 | 0.12473 | 0.12538 | 0.12604 | 0.12669 | 0.12735 | 0.128 | 0.12866 | 0.12931 | 0.12997 | 0.13062 | 0.13128
| WND013-85319062 | WND013 | 0.0051103 | 0.005164 | 0.0052176 | 0.0052713 | 0.0053249 | 0.0053539 | 0.0053829 | 0.0054118 | 0.0054408 | 0.0054697 | 0.0054987 | 0.0055277 | 0.0055566 | 0.0055856 | 0.0056145 | 0.0056435 | 0.0056725 | 0.0057014 | 0.0057304 | 0.0057593
| WND013-85319560 | WND013 | 0.024369 | 0.02461 | 0.024851 | 0.025092 | 0.025333 | 0.025526 | 0.02572 | 0.025913 | 0.026107 | 0.026301 | 0.026494 | 0.026688 | 0.026881 | 0.027075 | 0.027268 | 0.027462 | 0.027656 | 0.027849 | 0.028043 | 0.028236
| WND013-85319645 | WND013 | 0.0028143 | 0.002818 | 0.0028218 | 0.0028255 | 0.0028293 | 0.0028277 | 0.002826 | 0.0028244 | 0.0028228 | 0.0028211 | 0.0028195 | 0.0028179 | 0.0028163 | 0.0028146 | 0.002813 | 0.0028114 | 0.0028097 | 0.0028081 | 0.0028065 | 0.0028049
| WND013-85319854 | WND013 | 0.013651 | 0.013802 | 0.013953 | 0.014104 | 0.014255 | 0.014319 | 0.014383 | 0.014448 | 0.014512 | 0.014576 | 0.01464 | 0.014704 | 0.014769 | 0.014833 | 0.014897 | 0.014961 | 0.015025 | 0.015089 | 0.015154 | 0.015218
| WND013-85833772 | WND013 | 0.26047 | 0.26228 | 0.26409 | 0.2659 | 0.26771 | 0.26915 | 0.27058 | 0.27202 | 0.27346 | 0.2749 | 0.27633 | 0.27777 | 0.27921 | 0.28065 | 0.28208 | 0.28352 | 0.28496 | 0.2864 | 0.28784 | 0.28927
| WND013-89020589 | WND013 | 0.0099906 | 0.010102 | 0.010214 | 0.010326 | 0.010438 | 0.010531 | 0.010624 | 0.010717 | 0.010811 | 0.010904 | 0.010997 | 0.011091 | 0.011184 | 0.011277 | 0.011371 | 0.011464 | 0.011557 | 0.011651 | 0.011744 | 0.011837
| WND014-153585710 | WND014 | 0.71934 | 0.72647 | 0.73361 | 0.74074 | 0.74787 | 0.7519 | 0.75593 | 0.75995 | 0.76398 | 0.768 | 0.77203 | 0.77606 | 0.78008 | 0.78411 | 0.78813 | 0.79216 | 0.79619 | 0.80021 | 0.80424 | 0.80826
| WND014-15425582 | WND014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND014-200942632 | WND014 | 87.708 | 88.4136 | 89.1191 | 89.8247 | 90.5302 | 90.9173 | 91.3045 | 91.6916 | 92.0787 | 92.4658 | 92.853 | 93.2401 | 93.6272 | 94.0143 | 94.4014 | 94.7886 | 95.1757 | 95.5628 | 95.9499 | 96.337
| WND014-79365293 | WND014 | 0.12572 | 0.12701 | 0.12831 | 0.1296 | 0.13089 | 0.13165 | 0.13241 | 0.13316 | 0.13392 | 0.13467 | 0.13543 | 0.13618 | 0.13694 | 0.1377 | 0.13845 | 0.13921 | 0.13996 | 0.14072 | 0.14148 | 0.14223
| WND014-79365390 | WND014 | 0.023447 | 0.023684 | 0.023921 | 0.024159 | 0.024396 | 0.024599 | 0.024802 | 0.025005 | 0.025208 | 0.025411 | 0.025614 | 0.025817 | 0.02602 | 0.026223 | 0.026426 | 0.026629 | 0.026832 | 0.027035 | 0.027238 | 0.027441
| WND014-79365841 | WND014 | 0.87982 | 0.88782 | 0.89582 | 0.90382 | 0.91183 | 0.9181 | 0.92437 | 0.93065 | 0.93692 | 0.94319 | 0.94947 | 0.95574 | 0.96201 | 0.96829 | 0.97456 | 0.98083 | 0.98711 | 0.99338 | 0.99965 | 1.0059
| WND021-15425634 | WND021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WND021-200942770 | WND021 | 14.3916 | 14.5244 | 14.6573 | 14.7902 | 14.9231 | 14.9985 | 15.0739 | 15.1494 | 15.2248 | 15.3003 | 15.3757 | 15.4512 | 15.5266 | 15.6021 | 15.6775 | 15.753 | 15.8284 | 15.9039 | 15.9793 | 16.0548
| WND022-15425649 | WND022 | 5.4839e-05 | 5.5529e-05 | 5.6219e-05 | 5.691e-05 | 5.76e-05 | 5.802e-05 | 5.844e-05 | 5.886e-05 | 5.928e-05 | 5.97e-05 | 6.012e-05 | 6.054e-05 | 6.096e-05 | 6.138e-05 | 6.18e-05 | 6.222e-05 | 6.264e-05 | 6.306e-05 | 6.348e-05 | 6.39e-05
| WND022-200942838 | WND022 | 28.1967 | 28.4871 | 28.7776 | 29.068 | 29.3584 | 29.5249 | 29.6914 | 29.8579 | 30.0244 | 30.1909 | 30.3575 | 30.524 | 30.6905 | 30.857 | 31.0235 | 31.19 | 31.3565 | 31.523 | 31.6895 | 31.856
| WND023-200942910 | WND023 | 48.6431 | 49.0717 | 49.5003 | 49.9289 | 50.3575 | 50.4639 | 50.5704 | 50.6769 | 50.7834 | 50.8899 | 50.9963 | 51.1028 | 51.2093 | 51.3158 | 51.4222 | 51.5287 | 51.6352 | 51.7417 | 51.8482 | 51.9546
| WND023-73768060 | WND023 | 0.16274 | 0.16402 | 0.1653 | 0.16657 | 0.16785 | 0.16823 | 0.16861 | 0.169 | 0.16938 | 0.16976 | 0.17014 | 0.17053 | 0.17091 | 0.17129 | 0.17168 | 0.17206 | 0.17244 | 0.17282 | 0.17321 | 0.17359
| WND023-73768112 | WND023 | 0.091781 | 0.092777 | 0.093772 | 0.094768 | 0.095764 | 0.096252 | 0.096741 | 0.09723 | 0.097718 | 0.098207 | 0.098696 | 0.099184 | 0.099673 | 0.10016 | 0.10065 | 0.10114 | 0.10163 | 0.10212 | 0.1026 | 0.10309
| WND023-73768165 | WND023 | 0.19722 | 0.19894 | 0.20067 | 0.20239 | 0.20411 | 0.20516 | 0.2062 | 0.20725 | 0.20829 | 0.20934 | 0.21038 | 0.21143 | 0.21247 | 0.21351 | 0.21456 | 0.2156 | 0.21665 | 0.21769 | 0.21874 | 0.21978
| WND023-73948116 | WND023 | 0.04247 | 0.042864 | 0.043258 | 0.043652 | 0.044046 | 0.044226 | 0.044407 | 0.044588 | 0.044769 | 0.044949 | 0.04513 | 0.045311 | 0.045492 | 0.045672 | 0.045853 | 0.046034 | 0.046215 | 0.046395 | 0.046576 | 0.046757
| WND023-73948154 | WND023 | 0.05401 | 0.054446 | 0.054881 | 0.055317 | 0.055752 | 0.05589 | 0.056027 | 0.056164 | 0.056301 | 0.056439 | 0.056576 | 0.056713 | 0.056851 | 0.056988 | 0.057125 | 0.057262 | 0.0574 | 0.057537 | 0.057674 | 0.057811
| WND024-167870308 | WND024 | 0.081093 | 0.0817 | 0.082308 | 0.082915 | 0.083523 | 0.084094 | 0.084664 | 0.085235 | 0.085806 | 0.086377 | 0.086948 | 0.087519 | 0.08809 | 0.08866 | 0.089231 | 0.089802 | 0.090373 | 0.090944 | 0.091515 | 0.092085
| WND024-183316836 | WND024 | 28.8498 | 28.9989 | 29.1481 | 29.2972 | 29.4463 | 29.5464 | 29.6464 | 29.7464 | 29.8464 | 29.9464 | 30.0465 | 30.1465 | 30.2465 | 30.3465 | 30.4465 | 30.5466 | 30.6466 | 30.7466 | 30.8466 | 30.9466
| WND024-184539432 | WND024 | 0.000346 | 0.00034941 | 0.00035283 | 0.00035624 | 0.00035966 | 0.00036473 | 0.0003698 | 0.00037487 | 0.00037995 | 0.00038502 | 0.00039009 | 0.00039516 | 0.00040023 | 0.0004053 | 0.00041037 | 0.00041545 | 0.00042052 | 0.00042559 | 0.00043066 | 0.00043573
| WND024-192414587 | WND024 | 13.5534 | 13.6274 | 13.7013 | 13.7753 | 13.8493 | 13.8943 | 13.9392 | 13.9841 | 14.0291 | 14.074 | 14.119 | 14.1639 | 14.2088 | 14.2538 | 14.2987 | 14.3437 | 14.3886 | 14.4335 | 14.4785 | 14.5234
| WND024-200942990 | WND024 | 27.2868 | 27.5251 | 27.7635 | 28.0019 | 28.2403 | 28.3633 | 28.4864 | 28.6095 | 28.7325 | 28.8556 | 28.9787 | 29.1018 | 29.2248 | 29.3479 | 29.471 | 29.594 | 29.7171 | 29.8402 | 29.9633 | 30.0863
| WND024-79365148 | WND024 | 0.016303 | 0.01643 | 0.016557 | 0.016684 | 0.016811 | 0.016941 | 0.017071 | 0.017201 | 0.017331 | 0.017462 | 0.017592 | 0.017722 | 0.017852 | 0.017982 | 0.018113 | 0.018243 | 0.018373 | 0.018503 | 0.018633 | 0.018764
| WPD011-15399272 | WPD011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD011-15399285 | WPD011 | 12.0523 | 12.1233 | 12.1943 | 12.2653 | 12.3363 | 12.3467 | 12.3571 | 12.3674 | 12.3778 | 12.3882 | 12.3986 | 12.4089 | 12.4193 | 12.4297 | 12.44 | 12.4504 | 12.4608 | 12.4711 | 12.4815 | 12.4919
| WPD012-15436728 | WPD012 | 32.281 | 32.4961 | 32.7113 | 32.9264 | 33.1415 | 33.1489 | 33.1562 | 33.1636 | 33.1709 | 33.1783 | 33.1856 | 33.193 | 33.2003 | 33.2077 | 33.215 | 33.2224 | 33.2297 | 33.237 | 33.2444 | 33.2517
| WPD012-24603816 | WPD012 | 13.8653 | 13.9572 | 14.0491 | 14.141 | 14.2329 | 14.2386 | 14.2443 | 14.25 | 14.2557 | 14.2613 | 14.267 | 14.2727 | 14.2784 | 14.2841 | 14.2898 | 14.2955 | 14.3011 | 14.3068 | 14.3125 | 14.3182
| WPD013-178115477 | WPD013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD013-40657711 | WPD013 | 0.18961 | 0.19083 | 0.19205 | 0.19327 | 0.19449 | 0.19455 | 0.1946 | 0.19465 | 0.19471 | 0.19476 | 0.19482 | 0.19487 | 0.19492 | 0.19498 | 0.19503 | 0.19508 | 0.19514 | 0.19519 | 0.19525 | 0.1953
| WPD014-15399222 | WPD014 | 13.3756 | 13.3829 | 13.3903 | 13.3976 | 13.405 | 13.3855 | 13.3661 | 13.3466 | 13.3271 | 13.3077 | 13.2882 | 13.2688 | 13.2493 | 13.2298 | 13.2104 | 13.1909 | 13.1715 | 13.152 | 13.1325 | 13.1131
| WPD014-15399233 | WPD014 | 0.25838 | 0.25995 | 0.26152 | 0.26309 | 0.26466 | 0.26453 | 0.2644 | 0.26427 | 0.26414 | 0.26401 | 0.26388 | 0.26375 | 0.26361 | 0.26348 | 0.26335 | 0.26322 | 0.26309 | 0.26296 | 0.26283 | 0.2627
| WPD021-15399198 | WPD021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD022-15399022 | WPD022 | 170.4263 | 170.5077 | 170.589 | 170.6703 | 170.7517 | 170.5366 | 170.3216 | 170.1065 | 169.8914 | 169.6764 | 169.4613 | 169.2463 | 169.0312 | 168.8162 | 168.6011 | 168.3861 | 168.171 | 167.956 | 167.7409 | 167.5259
| WPD022-72495720 | WPD022 | 7.4113 | 7.427 | 7.4426 | 7.4582 | 7.4738 | 7.4406 | 7.4073 | 7.374 | 7.3407 | 7.3074 | 7.2742 | 7.2409 | 7.2076 | 7.1743 | 7.141 | 7.1078 | 7.0745 | 7.0412 | 7.0079 | 6.9747
| WPD024-15398985 | WPD024 | 74.2573 | 74.6096 | 74.9619 | 75.3142 | 75.6665 | 75.5445 | 75.4225 | 75.3005 | 75.1785 | 75.0564 | 74.9344 | 74.8124 | 74.6904 | 74.5684 | 74.4464 | 74.3244 | 74.2024 | 74.0804 | 73.9583 | 73.8363
| WPD031-15399072 | WPD031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD031-80918872 | WPD031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WPD033-153773704 | WPD033 | 1.8639 | 1.8794 | 1.8948 | 1.9103 | 1.9257 | 1.933 | 1.9404 | 1.9477 | 1.955 | 1.9624 | 1.9697 | 1.977 | 1.9844 | 1.9917 | 1.999 | 2.0064 | 2.0137 | 2.021 | 2.0284 | 2.0357
| WPD033-15399135 | WPD033 | 55.0929 | 55.3794 | 55.6659 | 55.9524 | 56.2388 | 56.3212 | 56.4036 | 56.4859 | 56.5683 | 56.6506 | 56.733 | 56.8153 | 56.8977 | 56.98 | 57.0624 | 57.1447 | 57.2271 | 57.3095 | 57.3918 | 57.4742
| WPD033-63732110 | WPD033 | 21.0811 | 21.1563 | 21.2316 | 21.3068 | 21.382 | 21.3407 | 21.2993 | 21.258 | 21.2166 | 21.1753 | 21.134 | 21.0926 | 21.0513 | 21.0099 | 20.9686 | 20.9273 | 20.8859 | 20.8446 | 20.8032 | 20.7619

## Energy at risk
Powercor
Pole bushfire resilience program
| Equipment | No. of HV/SubT | Feeder | ZSS | North/South of | Option 1 unplanned pole replacement | Weighted average demand per customer | [19 empty] | Combined LOS0_per_year, LOS1_per_year, CUSTO and CUST1 | [19 empty] | Option 1 energy at risk (MWh) | [19 empty] | VCR for ZSS | Value of network | Value of energy at risk | Value of network | Option 1 PV of unplanned pole | Option 2 PV of unplanned concrete | Option 3 unplanned pole and | Option 3 PV of unplanned pole and
|  | wood poles |  |  | divide | capex from bushfire ($ 2023) | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | ($2023/MWh) | reliability ($2023/MWh) | mitigated ($ 2023) | reliability ($ 2023) | replacement ($ 2023) | pole replacement ($ 2023) | mesh replacement capex ($ 2023) | mesh replacement ($ 2023)
| AC024-200218081 | 35 | AC024 | AC | South | 636327.6896 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.00022523 | 0.00022778 | 0.00023033 | 0.00023289 | 0.00023544 | 0.00023449 | 0.00023354 | 0.0002326 | 0.00023165 | 0.0002307 | 0.00022976 | 0.00022881 | 0.00022786 | 0.00022691 | 0.00022597 | 0.00022502 | 0.00022407 | 0.00022313 | 0.00022218 | 0.00022123 | 0.00070543 | 0.00071342 | 0.00072141 | 0.0007294 | 0.00073739 | 0.00073443 | 0.00073146 | 0.00072849 | 0.00072553 | 0.00072256 | 0.00071959 | 0.00071663 | 0.00071366 | 0.00071069 | 0.00070773 | 0.00070476 | 0.00070179 | 0.00069883 | 0.00069586 | 0.00069289 | 31921.1819 | 1820.9407 | 331.0411 | 18.8842 | 2106.9876 | 2731.1219 | 664065.1896 | 2198.8311
| AC024-200218767 | 0 | AC024 | AC | South | 0 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31921.1819 | 1820.9407 | 0 | 0 | 0 | 0 | 0 | 0
| AC024-200218825 | 3 | AC024 | AC | South | 54542.3734 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0.1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31921.1819 | 1820.9407 | 0 | 0 | 0 | 0 | 56919.8734 | 0
| AC025-200218004 | 26 | AC025 | AC | South | 472700.5694 | 0.17368 | 0.1762 | 0.18048 | 0.18156 | 0.18076 | 0.1826 | 0.18832 | 0.1922 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0.1906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31921.1819 | 1820.9407 | 0 | 0 | 0 | 0 | 493305.5694 | 0
| AC026-200217919 | 15 | AC026 | AC | South | 272711.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31921.1819 | 1820.9407 | 0 | 0 | 139039.9269 | 180226.4954 | 284599.367 | 145100.672
| AC031-200217854 | 58 | AC031 | AC | South | 1054485.8856 | 0.10639 | 0.10806 | 0.1075 | 0.10711 | 0.10639 | 0.10622 | 0.10583 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.10639 | 0.054341 | 0.054629 | 0.054918 | 0.055207 | 0.055495 | 0.055465 | 0.055435 | 0.055405 | 0.055375 | 0.055344 | 0.055314 | 0.055284 | 0.055254 | 0.055224 | 0.055193 | 0.055163 | 0.055133 | 0.055103 | 0.055072 | 0.055042 | 0.16095 | 0.16434 | 0.16436 | 0.16462 | 0.16437 | 0.16402 | 0.16333 | 0.1641 | 0.16401 | 0.16392 | 0.16383 | 0.16374 | 0.16365 | 0.16356 | 0.16348 | 0.16339 | 0.1633 | 0.16321 | 0.16312 | 0.16303 | 31921.1819 | 1820.9407 | 75527.1339 | 4308.4381 | 93435.621 | 121113.2292 | 1100450.8856 | 97508.4762
| AC032-200217768 | 18 | AC032 | AC | South | 327254.2404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31921.1819 | 1820.9407 | 0 | 0 | 0 | 0 | 341519.2404 | 0
| AL002-15404158 | 0 | AL002 | AL | South | 0 | 0.0058768 | 0.0061817 | 0.0061927 | 0.0061817 | 0.0061501 | 0.0061232 | 0.0061596 | 0.006207 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39267.0653 | 6354.1001 | 0 | 0 | 0 | 0 | 0 | 0
| AL002-200779408 | 159 | AL002 | AL | South | 2890745.7899 | 0.0058768 | 0.0061817 | 0.0061927 | 0.0061817 | 0.0061501 | 0.0061232 | 0.0061596 | 0.006207 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.0061959 | 0.56202 | 0.56826 | 0.57451 | 0.58076 | 0.58701 | 0.585 | 0.58299 | 0.58098 | 0.57897 | 0.57696 | 0.57496 | 0.57295 | 0.57094 | 0.56893 | 0.56692 | 0.56491 | 0.5629 | 0.56089 | 0.55888 | 0.55688 | 0.091951 | 0.097797 | 0.099049 | 0.099948 | 0.10051 | 0.099725 | 0.099973 | 0.10039 | 0.099869 | 0.099523 | 0.099176 | 0.09883 | 0.098483 | 0.098137 | 0.09779 | 0.097444 | 0.097097 | 0.096751 | 0.096404 | 0.096058 | 39267.0653 | 6354.1001 | 55810.9683 | 9031.1939 | 76006.3875 | 98521.0878 | 3016753.2899 | 79319.503
| AL006-200403372 | 209 | AL006 | AL | South | 3799785.3465 | 0.0010922 | 0.0011161 | 0.001133 | 0.0011475 | 0.0011606 | 0.0011743 | 0.0011955 | 0.0012191 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 12.8578 | 12.9604 | 13.063 | 13.1656 | 13.2682 | 13.2278 | 13.1874 | 13.147 | 13.1066 | 13.0661 | 13.0257 | 12.9853 | 12.9449 | 12.9045 | 12.864 | 12.8236 | 12.7832 | 12.7428 | 12.7024 | 12.6619 | 0.39097 | 0.40269 | 0.41205 | 0.4206 | 0.4287 | 0.43246 | 0.4389 | 0.4462 | 0.45075 | 0.44936 | 0.44797 | 0.44658 | 0.44519 | 0.4438 | 0.44241 | 0.44102 | 0.43963 | 0.43824 | 0.43685 | 0.43546 | 39267.0653 | 6354.1001 | 245453.4616 | 39718.6765 | 351087.5646 | 455087.1306 | 3965417.8465 | 366391.4583
| AL007-200403464 | 0 | AL007 | AL | South | 0 | 0.001542 | 0.0015601 | 0.0015749 | 0.0015881 | 0.0016112 | 0.0016343 | 0.0016652 | 0.0016848 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39267.0653 | 6354.1001 | 0 | 0 | 0 | 0 | 0 | 0
| AL007-200403526 | 117 | AL007 | AL | South | 2127152.5624 | 0.001542 | 0.0015601 | 0.0015749 | 0.0015881 | 0.0016112 | 0.0016343 | 0.0016652 | 0.0016848 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0016863 | 0.0063708 | 0.006432 | 0.0064931 | 0.0065543 | 0.0066155 | 0.0065842 | 0.0065529 | 0.0065216 | 0.0064903 | 0.0064589 | 0.0064276 | 0.0063963 | 0.006365 | 0.0063337 | 0.0063024 | 0.0062711 | 0.0062398 | 0.0062085 | 0.0061772 | 0.0061458 | 0.00027349 | 0.00027937 | 0.00028469 | 0.00028979 | 0.00029674 | 0.00029957 | 0.00030378 | 0.0003059 | 0.0003047 | 0.00030323 | 0.00030176 | 0.00030029 | 0.00029882 | 0.00029735 | 0.00029588 | 0.00029441 | 0.00029294 | 0.00029147 | 0.00029 | 0.00028853 | 39267.0653 | 6354.1001 | 166.9856 | 27.0212 | 195.4419 | 253.3359 | 2219875.0624 | 203.9612
| AL011-200635544 | 73 | AL011 | AL | South | 1327197.7526 | 0.015947 | 0.015977 | 0.015924 | 0.015847 | 0.015733 | 0.015733 | 0.015821 | 0.015847 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0.015809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39267.0653 | 6354.1001 | 0 | 0 | 0 | 0 | 1385050.2526 | 0
| AL012-200635470 | 146 | AL012 | AL | South | 2654395.5052 | 0.0010995 | 0.0011191 | 0.001134 | 0.0011453 | 0.0011537 | 0.0011658 | 0.0011925 | 0.0012259 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0.0012543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39267.0653 | 6354.1001 | 0 | 0 | 0 | 0 | 2770100.5052 | 0
| AL014-200635260 | 264 | AL014 | AL | South | 4799728.8587 | 0.0018433 | 0.0018668 | 0.0018809 | 0.0018952 | 0.0018945 | 0.001901 | 0.0019242 | 0.0019503 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 0.0019565 | 14.1317 | 14.2259 | 14.32 | 14.4141 | 14.5082 | 14.4853 | 14.4623 | 14.4393 | 14.4163 | 14.3933 | 14.3704 | 14.3474 | 14.3244 | 14.3014 | 14.2784 | 14.2555 | 14.2325 | 14.2095 | 14.1865 | 14.1636 | 0.72522 | 0.73933 | 0.74985 | 0.76054 | 0.76522 | 0.76661 | 0.77473 | 0.78398 | 0.78523 | 0.78398 | 0.78273 | 0.78148 | 0.78022 | 0.77897 | 0.77772 | 0.77647 | 0.77522 | 0.77397 | 0.77271 | 0.77146 | 39267.0653 | 6354.1001 | 436147.4629 | 70576.3117 | 475637.2934 | 616531.1247 | 5008948.8587 | 496370.3051
| ART023-15411707 | 327 | ART023 | ART | North | 7706188.6647 | 0.0024604 | 0.0024362 | 0.0024203 | 0.0023947 | 0.0023657 | 0.0023498 | 0.0023498 | 0.0023483 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 21.4474 | 21.6185 | 21.7897 | 21.9608 | 22.132 | 22.1509 | 22.1699 | 22.1888 | 22.2078 | 22.2267 | 22.2457 | 22.2646 | 22.2835 | 22.3025 | 22.3214 | 22.3404 | 22.3593 | 22.3783 | 22.3972 | 22.4162 | 1.4691 | 1.4663 | 1.4682 | 1.4641 | 1.4576 | 1.4491 | 1.4503 | 1.4506 | 1.434 | 1.4352 | 1.4364 | 1.4376 | 1.4388 | 1.4401 | 1.4413 | 1.4425 | 1.4437 | 1.445 | 1.4462 | 1.4474 | 32690.9757 | 6311.913 | 685272.233 | 132311.0932 | 2654344.8312 | 2654344.8312 | 7706188.6647 | 2654344.8312
| ART023-15411718 | 0 | ART023 | ART | North | 0 | 0.0024604 | 0.0024362 | 0.0024203 | 0.0023947 | 0.0023657 | 0.0023498 | 0.0023498 | 0.0023483 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 7.5157e-07 | 7.6143e-07 | 7.7129e-07 | 7.8114e-07 | 7.91e-07 | 7.927e-07 | 7.944e-07 | 7.961e-07 | 7.978e-07 | 7.995e-07 | 8.012e-07 | 8.029e-07 | 8.046e-07 | 8.063e-07 | 8.08e-07 | 8.097e-07 | 8.114e-07 | 8.131e-07 | 8.148e-07 | 8.165e-07 | 5.1481e-08 | 5.1644e-08 | 5.197e-08 | 5.2077e-08 | 5.2096e-08 | 5.1856e-08 | 5.1967e-08 | 5.2047e-08 | 5.1514e-08 | 5.1624e-08 | 5.1733e-08 | 5.1843e-08 | 5.1953e-08 | 5.2063e-08 | 5.2173e-08 | 5.2282e-08 | 5.2392e-08 | 5.2502e-08 | 5.2612e-08 | 5.2721e-08 | 32690.9757 | 6311.913 | 0 | 0 | 0 | 0 | 0 | 0
| ART023-154832740 | 7 | ART023 | ART | North | 164964.2833 | 0.0024604 | 0.0024362 | 0.0024203 | 0.0023947 | 0.0023657 | 0.0023498 | 0.0023498 | 0.0023483 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.007115 | 0.007181 | 0.007247 | 0.0073131 | 0.0073791 | 0.0073805 | 0.0073818 | 0.0073832 | 0.0073846 | 0.007386 | 0.0073874 | 0.0073887 | 0.0073901 | 0.0073915 | 0.0073929 | 0.0073943 | 0.0073956 | 0.007397 | 0.0073984 | 0.0073998 | 0.00048736 | 0.00048705 | 0.00048831 | 0.00048755 | 0.00048599 | 0.00048281 | 0.0004829 | 0.00048269 | 0.00047682 | 0.00047691 | 0.000477 | 0.00047709 | 0.00047718 | 0.00047727 | 0.00047736 | 0.00047745 | 0.00047754 | 0.00047763 | 0.00047771 | 0.0004778 | 32690.9757 | 6311.913 | 227.5319 | 43.9314 | 2189.2158 | 2189.2158 | 164964.2833 | 2189.2158
| ART023-154832902 | 29 | ART023 | ART | North | 683423.4596 | 0.0024604 | 0.0024362 | 0.0024203 | 0.0023947 | 0.0023657 | 0.0023498 | 0.0023498 | 0.0023483 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32690.9757 | 6311.913 | 0 | 0 | 0 | 0 | 683423.4596 | 0
| ART023-24601770 | 275 | ART023 | ART | North | 6480739.7027 | 0.0024604 | 0.0024362 | 0.0024203 | 0.0023947 | 0.0023657 | 0.0023498 | 0.0023498 | 0.0023483 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 2.9303 | 2.9573 | 2.9842 | 3.0112 | 3.0381 | 3.0392 | 3.0403 | 3.0413 | 3.0424 | 3.0435 | 3.0445 | 3.0456 | 3.0467 | 3.0477 | 3.0488 | 3.0499 | 3.0509 | 3.052 | 3.0531 | 3.0541 | 0.20072 | 0.20058 | 0.20108 | 0.20075 | 0.20009 | 0.19882 | 0.19889 | 0.19883 | 0.19645 | 0.19652 | 0.19659 | 0.19665 | 0.19672 | 0.19679 | 0.19686 | 0.19693 | 0.197 | 0.19707 | 0.19714 | 0.19721 | 32690.9757 | 6311.913 | 93761.3558 | 18103.2689 | 1043308.5781 | 1043308.5781 | 6480739.7027 | 1043308.5781
| ART023-63832300 | 157 | ART023 | ART | North | 3699913.2121 | 0.0024604 | 0.0024362 | 0.0024203 | 0.0023947 | 0.0023657 | 0.0023498 | 0.0023498 | 0.0023483 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 4.3302 | 4.3623 | 4.3944 | 4.4265 | 4.4585 | 4.4592 | 4.4598 | 4.4605 | 4.4611 | 4.4617 | 4.4624 | 4.463 | 4.4636 | 4.4643 | 4.4649 | 4.4656 | 4.4662 | 4.4668 | 4.4675 | 4.4681 | 0.29661 | 0.29587 | 0.2961 | 0.2951 | 0.29364 | 0.29171 | 0.29175 | 0.29161 | 0.28805 | 0.28809 | 0.28814 | 0.28818 | 0.28822 | 0.28826 | 0.2883 | 0.28834 | 0.28838 | 0.28842 | 0.28846 | 0.28851 | 32690.9757 | 6311.913 | 137612.8937 | 26570.0426 | 754142.2154 | 754142.2154 | 3699913.2121 | 754142.2154
| ART023-76359967 | 101 | ART023 | ART | North | 2380198.9454 | 0.0024604 | 0.0024362 | 0.0024203 | 0.0023947 | 0.0023657 | 0.0023498 | 0.0023498 | 0.0023483 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.0023193 | 0.78702 | 0.79408 | 0.80114 | 0.8082 | 0.81526 | 0.81457 | 0.81389 | 0.8132 | 0.81251 | 0.81183 | 0.81114 | 0.81046 | 0.80977 | 0.80909 | 0.8084 | 0.80772 | 0.80703 | 0.80634 | 0.80566 | 0.80497 | 0.053908 | 0.053858 | 0.053981 | 0.053881 | 0.053694 | 0.053287 | 0.053242 | 0.053165 | 0.052464 | 0.05242 | 0.052376 | 0.052331 | 0.052287 | 0.052243 | 0.052198 | 0.052154 | 0.05211 | 0.052066 | 0.052021 | 0.051977 | 32690.9757 | 6311.913 | 25014.6157 | 4829.7757 | 342951.8467 | 342951.8467 | 2380198.9454 | 342951.8467
| ART031-140150600 | 43 | ART031 | ART | North | 1013352.0262 | 0.0012737 | 0.0012737 | 0.0012668 | 0.0012599 | 0.0012461 | 0.0012478 | 0.0012623 | 0.0012719 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.23627 | 0.23791 | 0.23955 | 0.24119 | 0.24283 | 0.24268 | 0.24253 | 0.24239 | 0.24224 | 0.24209 | 0.24194 | 0.2418 | 0.24165 | 0.2415 | 0.24135 | 0.2412 | 0.24106 | 0.24091 | 0.24076 | 0.24061 | 0.0083779 | 0.008436 | 0.0084482 | 0.0084599 | 0.0084243 | 0.0084308 | 0.0085233 | 0.0085831 | 0.0085733 | 0.008568 | 0.0085628 | 0.0085576 | 0.0085523 | 0.0085471 | 0.0085419 | 0.0085366 | 0.0085314 | 0.0085262 | 0.008521 | 0.0085157 | 32690.9757 | 6311.913 | 4019.2338 | 776.0262 | 98091.2154 | 98091.2154 | 1013352.0262 | 98091.2154
| ART031-15411744 | 203 | ART031 | ART | North | 4783964.2169 | 0.0012737 | 0.0012737 | 0.0012668 | 0.0012599 | 0.0012461 | 0.0012478 | 0.0012623 | 0.0012719 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 17.3122 | 17.4365 | 17.5607 | 17.6849 | 17.8091 | 17.8257 | 17.8423 | 17.8588 | 17.8754 | 17.892 | 17.9086 | 17.9252 | 17.9418 | 17.9583 | 17.9749 | 17.9915 | 18.0081 | 18.0247 | 18.0413 | 18.0578 | 0.61387 | 0.61828 | 0.61932 | 0.62031 | 0.61784 | 0.61927 | 0.62702 | 0.6324 | 0.63264 | 0.63323 | 0.63382 | 0.6344 | 0.63499 | 0.63558 | 0.63616 | 0.63675 | 0.63734 | 0.63793 | 0.63851 | 0.6391 | 32690.9757 | 6311.913 | 297029.8387 | 57349.971 | 955377.5772 | 955377.5772 | 4783964.2169 | 955377.5772
| ART031-155164001 | 5 | ART031 | ART | North | 117831.631 | 0.0012737 | 0.0012737 | 0.0012668 | 0.0012599 | 0.0012461 | 0.0012478 | 0.0012623 | 0.0012719 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32690.9757 | 6311.913 | 0 | 0 | 0 | 0 | 117831.631 | 0
| ART031-155164103 | 17 | ART031 | ART | North | 400627.5453 | 0.0012737 | 0.0012737 | 0.0012668 | 0.0012599 | 0.0012461 | 0.0012478 | 0.0012623 | 0.0012719 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.00025449 | 0.00025731 | 0.00026014 | 0.00026297 | 0.0002658 | 0.00026604 | 0.00026628 | 0.00026652 | 0.00026676 | 0.000267 | 0.00026724 | 0.00026748 | 0.00026772 | 0.00026796 | 0.0002682 | 0.00026844 | 0.00026868 | 0.00026892 | 0.00026916 | 0.0002694 | 9.0238e-06 | 9.1241e-06 | 9.1745e-06 | 9.2239e-06 | 9.2212e-06 | 9.2423e-06 | 9.3578e-06 | 9.4377e-06 | 9.4411e-06 | 9.4496e-06 | 9.4581e-06 | 9.4666e-06 | 9.4751e-06 | 9.4836e-06 | 9.4921e-06 | 9.5006e-06 | 9.5091e-06 | 9.5176e-06 | 9.5261e-06 | 9.5345e-06 | 32690.9757 | 6311.913 | 4.4218 | 0.85376 | 255.9841 | 255.9841 | 400627.5453 | 255.9841
| ART031-76359985 | 79 | ART031 | ART | North | 1861739.7692 | 0.0012737 | 0.0012737 | 0.0012668 | 0.0012599 | 0.0012461 | 0.0012478 | 0.0012623 | 0.0012719 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.072704 | 0.073352 | 0.074001 | 0.074649 | 0.075297 | 0.075361 | 0.075425 | 0.075488 | 0.075552 | 0.075616 | 0.07568 | 0.075744 | 0.075807 | 0.075871 | 0.075935 | 0.075999 | 0.076062 | 0.076126 | 0.07619 | 0.076254 | 0.002578 | 0.002601 | 0.0026098 | 0.0026183 | 0.0026122 | 0.002618 | 0.0026506 | 0.0026731 | 0.0026739 | 0.0026762 | 0.0026784 | 0.0026807 | 0.002683 | 0.0026852 | 0.0026875 | 0.0026897 | 0.002692 | 0.0026942 | 0.0026965 | 0.0026988 | 32690.9757 | 6311.913 | 1253.9599 | 242.1123 | 49367.4287 | 49367.4287 | 1861739.7692 | 49367.4287
| ART031-76433910 | 287 | ART031 | ART | North | 6763535.617 | 0.0012737 | 0.0012737 | 0.0012668 | 0.0012599 | 0.0012461 | 0.0012478 | 0.0012623 | 0.0012719 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 9.2195 | 9.2838 | 9.3481 | 9.4124 | 9.4767 | 9.4773 | 9.4779 | 9.4785 | 9.4791 | 9.4797 | 9.4803 | 9.4809 | 9.4815 | 9.4821 | 9.4827 | 9.4833 | 9.4839 | 9.4845 | 9.4851 | 9.4857 | 0.32691 | 0.32919 | 0.32968 | 0.33015 | 0.32877 | 0.32924 | 0.33308 | 0.33564 | 0.33548 | 0.3355 | 0.33552 | 0.33555 | 0.33557 | 0.33559 | 0.33561 | 0.33563 | 0.33565 | 0.33567 | 0.3357 | 0.33572 | 32690.9757 | 6311.913 | 157386.8009 | 30387.952 | 2198044.4062 | 2198044.4062 | 6763535.617 | 2198044.4062
| ART031-78747678 | 60 | ART031 | ART | North | 1413979.5715 | 0.0012737 | 0.0012737 | 0.0012668 | 0.0012599 | 0.0012461 | 0.0012478 | 0.0012623 | 0.0012719 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.10355 | 0.1043 | 0.10505 | 0.1058 | 0.10655 | 0.10669 | 0.10683 | 0.10697 | 0.10711 | 0.10726 | 0.1074 | 0.10754 | 0.10768 | 0.10782 | 0.10797 | 0.10811 | 0.10825 | 0.10839 | 0.10853 | 0.10868 | 0.0036719 | 0.0036984 | 0.0037048 | 0.0037109 | 0.0036963 | 0.0037064 | 0.0037543 | 0.003788 | 0.003791 | 0.003796 | 0.003801 | 0.003806 | 0.0038111 | 0.0038161 | 0.0038211 | 0.0038261 | 0.0038311 | 0.0038362 | 0.0038412 | 0.0038462 | 32690.9757 | 6311.913 | 1780.5694 | 343.789 | 72760.9338 | 72760.9338 | 1413979.5715 | 72760.9338
| ART031-78747795 | 34 | ART031 | ART | North | 801255.0905 | 0.0012737 | 0.0012737 | 0.0012668 | 0.0012599 | 0.0012461 | 0.0012478 | 0.0012623 | 0.0012719 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0.0012713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32690.9757 | 6311.913 | 0 | 0 | 55898.8055 | 55898.8055 | 801255.0905 | 55898.8055
| ART033-15411794 | 635 | ART033 | ART | North | 14964617.1318 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 35.31 | 35.5532 | 35.7963 | 36.0395 | 36.2826 | 36.1971 | 36.1116 | 36.0261 | 35.9406 | 35.8551 | 35.7696 | 35.6841 | 35.5986 | 35.5131 | 35.4276 | 35.342 | 35.2565 | 35.171 | 35.0855 | 35 | 0.90932 | 0.91897 | 0.93312 | 0.94025 | 0.94128 | 0.94251 | 0.95351 | 0.95916 | 0.94373 | 0.94148 | 0.93924 | 0.93699 | 0.93474 | 0.9325 | 0.93025 | 0.92801 | 0.92576 | 0.92352 | 0.92127 | 0.91903 | 32690.9757 | 6311.913 | 441539.9932 | 85251.7239 | 4995233.339 | 4995233.339 | 14964617.1318 | 4995233.339
| ART033-154972245 | 71 | ART033 | ART | North | 1673209.1596 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.046632 | 0.046991 | 0.047349 | 0.047707 | 0.048065 | 0.048118 | 0.04817 | 0.048222 | 0.048275 | 0.048327 | 0.04838 | 0.048432 | 0.048485 | 0.048537 | 0.048589 | 0.048642 | 0.048694 | 0.048747 | 0.048799 | 0.048852 | 0.0012009 | 0.0012146 | 0.0012343 | 0.0012447 | 0.001247 | 0.0012529 | 0.0012719 | 0.0012839 | 0.0012676 | 0.001269 | 0.0012704 | 0.0012717 | 0.0012731 | 0.0012745 | 0.0012759 | 0.0012772 | 0.0012786 | 0.00128 | 0.0012814 | 0.0012827 | 32690.9757 | 6311.913 | 594.9711 | 114.8759 | 32319.7486 | 32319.7486 | 1673209.1596 | 32319.7486
| ART033-154972416 | 51 | ART033 | ART | North | 1201882.6358 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.023887 | 0.024101 | 0.024315 | 0.024529 | 0.024743 | 0.024691 | 0.02464 | 0.024588 | 0.024537 | 0.024485 | 0.024434 | 0.024382 | 0.024331 | 0.024279 | 0.024228 | 0.024176 | 0.024125 | 0.024073 | 0.024022 | 0.02397 | 0.00061515 | 0.00062295 | 0.00063383 | 0.00063994 | 0.0006419 | 0.00064292 | 0.0006506 | 0.00065464 | 0.00064429 | 0.00064294 | 0.00064158 | 0.00064023 | 0.00063888 | 0.00063753 | 0.00063618 | 0.00063482 | 0.00063347 | 0.00063212 | 0.00063077 | 0.00062942 | 32690.9757 | 6311.913 | 301.1451 | 58.1445 | 26440.1825 | 26440.1825 | 1201882.6358 | 26440.1825
| ART033-154972520 | 31 | ART033 | ART | North | 730556.1119 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.0096584 | 0.0097545 | 0.0098506 | 0.0099467 | 0.010043 | 0.010053 | 0.010064 | 0.010075 | 0.010085 | 0.010096 | 0.010106 | 0.010117 | 0.010127 | 0.010138 | 0.010149 | 0.010159 | 0.01017 | 0.01018 | 0.010191 | 0.010202 | 0.00024873 | 0.00025213 | 0.00025678 | 0.0002595 | 0.00026054 | 0.00026177 | 0.00026573 | 0.00026823 | 0.00026481 | 0.00026509 | 0.00026537 | 0.00026565 | 0.00026593 | 0.0002662 | 0.00026648 | 0.00026676 | 0.00026704 | 0.00026732 | 0.00026759 | 0.00026787 | 32690.9757 | 6311.913 | 124.12 | 23.9649 | 8831.4433 | 8831.4433 | 730556.1119 | 8831.4433
| ART033-154972637 | 61 | ART033 | ART | North | 1437545.8977 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00016853 | 0.00017039 | 0.00017226 | 0.00017413 | 0.000176 | 0.00017508 | 0.00017416 | 0.00017324 | 0.00017232 | 0.0001714 | 0.00017048 | 0.00016956 | 0.00016864 | 0.00016772 | 0.0001668 | 0.00016588 | 0.00016496 | 0.00016404 | 0.00016312 | 0.0001622 | 4.34e-06 | 4.4043e-06 | 4.4905e-06 | 4.543e-06 | 4.566e-06 | 4.5588e-06 | 4.5986e-06 | 4.6124e-06 | 4.5248e-06 | 4.5006e-06 | 4.4765e-06 | 4.4523e-06 | 4.4281e-06 | 4.404e-06 | 4.3798e-06 | 4.3557e-06 | 4.3315e-06 | 4.3074e-06 | 4.2832e-06 | 4.259e-06 | 32690.9757 | 6311.913 | 2.1048 | 0.40639 | 176.8337 | 176.8337 | 1437545.8977 | 176.8337
| ART033-155019358 | 92 | ART033 | ART | North | 2168102.0096 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.010548 | 0.010652 | 0.010757 | 0.010862 | 0.010967 | 0.010933 | 0.010899 | 0.010866 | 0.010832 | 0.010798 | 0.010765 | 0.010731 | 0.010697 | 0.010664 | 0.01063 | 0.010596 | 0.010563 | 0.010529 | 0.010495 | 0.010462 | 0.00027163 | 0.00027534 | 0.00028041 | 0.00028338 | 0.00028451 | 0.00028468 | 0.00028779 | 0.00028929 | 0.00028443 | 0.00028354 | 0.00028266 | 0.00028177 | 0.00028089 | 0.00028001 | 0.00027912 | 0.00027824 | 0.00027735 | 0.00027647 | 0.00027559 | 0.0002747 | 32690.9757 | 6311.913 | 132.7192 | 25.6252 | 7643.8621 | 7643.8621 | 2168102.0096 | 7643.8621
| ART033-155019455 | 10 | ART033 | ART | North | 235663.2619 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32690.9757 | 6311.913 | 0 | 0 | 0.64466 | 0.64466 | 235663.2619 | 0.64466
| ART033-155019644 | 82 | ART033 | ART | North | 1932438.7477 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.096525 | 0.097303 | 0.098082 | 0.098861 | 0.099639 | 0.099956 | 0.10027 | 0.10059 | 0.10091 | 0.10122 | 0.10154 | 0.10186 | 0.10217 | 0.10249 | 0.10281 | 0.10312 | 0.10344 | 0.10376 | 0.10408 | 0.10439 | 0.0024858 | 0.0025151 | 0.0025568 | 0.0025792 | 0.0025849 | 0.0026027 | 0.0026477 | 0.0026781 | 0.0026496 | 0.0026579 | 0.0026662 | 0.0026746 | 0.0026829 | 0.0026912 | 0.0026995 | 0.0027078 | 0.0027162 | 0.0027245 | 0.0027328 | 0.0027411 | 32690.9757 | 6311.913 | 1246.0711 | 240.5891 | 46134.4191 | 46134.4191 | 1932438.7477 | 46134.4191
| ART033-155019780 | 11 | ART033 | ART | North | 259229.5881 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.0031438 | 0.0031661 | 0.0031883 | 0.0032105 | 0.0032328 | 0.0032281 | 0.0032233 | 0.0032186 | 0.0032139 | 0.0032092 | 0.0032045 | 0.0031998 | 0.0031951 | 0.0031904 | 0.0031857 | 0.003181 | 0.0031763 | 0.0031716 | 0.0031669 | 0.0031622 | 8.0961e-05 | 8.1835e-05 | 8.3111e-05 | 8.3761e-05 | 8.3867e-05 | 8.4053e-05 | 8.5111e-05 | 8.5694e-05 | 8.4391e-05 | 8.4268e-05 | 8.4144e-05 | 8.4021e-05 | 8.3897e-05 | 8.3773e-05 | 8.365e-05 | 8.3526e-05 | 8.3403e-05 | 8.3279e-05 | 8.3156e-05 | 8.3032e-05 | 32690.9757 | 6311.913 | 39.518 | 7.6301 | 5986.8227 | 5986.8227 | 259229.5881 | 5986.8227
| ART033-155019881 | 22 | ART033 | ART | North | 518459.1762 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.012499 | 0.012564 | 0.01263 | 0.012696 | 0.012762 | 0.012734 | 0.012706 | 0.012679 | 0.012651 | 0.012623 | 0.012596 | 0.012568 | 0.01254 | 0.012512 | 0.012485 | 0.012457 | 0.012429 | 0.012401 | 0.012374 | 0.012346 | 0.00032187 | 0.00032476 | 0.00032924 | 0.00033123 | 0.00033108 | 0.00033157 | 0.00033551 | 0.00033756 | 0.00033219 | 0.00033146 | 0.00033073 | 0.00033 | 0.00032928 | 0.00032855 | 0.00032782 | 0.00032709 | 0.00032637 | 0.00032564 | 0.00032491 | 0.00032418 | 32690.9757 | 6311.913 | 155.6103 | 30.045 | 10477.7834 | 10477.7834 | 518459.1762 | 10477.7834
| ART033-155025562 | 85 | ART033 | ART | North | 2003137.7263 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.033218 | 0.033541 | 0.033864 | 0.034187 | 0.03451 | 0.034345 | 0.03418 | 0.034015 | 0.03385 | 0.033685 | 0.03352 | 0.033355 | 0.033191 | 0.033026 | 0.032861 | 0.032696 | 0.032531 | 0.032366 | 0.032201 | 0.032036 | 0.00085545 | 0.00086696 | 0.00088275 | 0.00089193 | 0.0008953 | 0.00089429 | 0.00090251 | 0.00090563 | 0.00088884 | 0.00088451 | 0.00088018 | 0.00087585 | 0.00087151 | 0.00086718 | 0.00086285 | 0.00085852 | 0.00085419 | 0.00084986 | 0.00084553 | 0.00084119 | 32690.9757 | 6311.913 | 414.0175 | 79.9377 | 17951.5914 | 17951.5914 | 2003137.7263 | 17951.5914
| ART033-155025764 | 18 | ART033 | ART | North | 424193.8715 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 6.4336e-05 | 6.5152e-05 | 6.5968e-05 | 6.6784e-05 | 6.76e-05 | 6.778e-05 | 6.796e-05 | 6.814e-05 | 6.832e-05 | 6.85e-05 | 6.868e-05 | 6.886e-05 | 6.904e-05 | 6.922e-05 | 6.94e-05 | 6.958e-05 | 6.976e-05 | 6.994e-05 | 7.012e-05 | 7.03e-05 | 1.6568e-06 | 1.684e-06 | 1.7196e-06 | 1.7424e-06 | 1.7537e-06 | 1.7649e-06 | 1.7944e-06 | 1.8142e-06 | 1.7939e-06 | 1.7987e-06 | 1.8034e-06 | 1.8081e-06 | 1.8128e-06 | 1.8176e-06 | 1.8223e-06 | 1.827e-06 | 1.8318e-06 | 1.8365e-06 | 1.8412e-06 | 1.8459e-06 | 32690.9757 | 6311.913 | 0.8409 | 0.16236 | 104.2185 | 104.2185 | 424193.8715 | 104.2185
| ART033-155025850 | 55 | ART033 | ART | North | 1296147.9405 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00056881 | 0.00057575 | 0.0005827 | 0.00058965 | 0.0005966 | 0.00059812 | 0.00059964 | 0.00060116 | 0.00060268 | 0.0006042 | 0.00060572 | 0.00060724 | 0.00060876 | 0.00061028 | 0.0006118 | 0.00061332 | 0.00061484 | 0.00061636 | 0.00061788 | 0.0006194 | 1.4648e-05 | 1.4882e-05 | 1.519e-05 | 1.5384e-05 | 1.5478e-05 | 1.5574e-05 | 1.5833e-05 | 1.6005e-05 | 1.5825e-05 | 1.5865e-05 | 1.5905e-05 | 1.5945e-05 | 1.5985e-05 | 1.6025e-05 | 1.6065e-05 | 1.6105e-05 | 1.6144e-05 | 1.6184e-05 | 1.6224e-05 | 1.6264e-05 | 32690.9757 | 6311.913 | 7.4191 | 1.4325 | 295.7461 | 295.7461 | 1296147.9405 | 295.7461
| ART033-155026277 | 122 | ART033 | ART | North | 2875091.7954 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.0041639 | 0.0042062 | 0.0042486 | 0.0042909 | 0.0043332 | 0.0043339 | 0.0043346 | 0.0043353 | 0.004336 | 0.0043367 | 0.0043373 | 0.004338 | 0.0043387 | 0.0043394 | 0.0043401 | 0.0043408 | 0.0043415 | 0.0043422 | 0.0043429 | 0.0043436 | 0.00010723 | 0.00010872 | 0.00011075 | 0.00011195 | 0.00011242 | 0.00011285 | 0.00011445 | 0.00011542 | 0.00011385 | 0.00011387 | 0.00011389 | 0.00011391 | 0.00011393 | 0.00011394 | 0.00011396 | 0.00011398 | 0.000114 | 0.00011402 | 0.00011403 | 0.00011405 | 32690.9757 | 6311.913 | 53.3059 | 10.2922 | 3893.9751 | 3893.9751 | 2875091.7954 | 3893.9751
| ART033-155052342 | 81 | ART033 | ART | North | 1908872.4215 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.28445 | 0.28678 | 0.28911 | 0.29144 | 0.29378 | 0.29399 | 0.29421 | 0.29443 | 0.29464 | 0.29486 | 0.29507 | 0.29529 | 0.29551 | 0.29572 | 0.29594 | 0.29616 | 0.29637 | 0.29659 | 0.29681 | 0.29702 | 0.0073253 | 0.0074126 | 0.0075364 | 0.0076036 | 0.0076214 | 0.007655 | 0.0077684 | 0.0078388 | 0.0077367 | 0.0077424 | 0.007748 | 0.0077537 | 0.0077594 | 0.0077651 | 0.0077708 | 0.0077765 | 0.0077822 | 0.0077878 | 0.0077935 | 0.0077992 | 32690.9757 | 6311.913 | 3628.8508 | 700.6518 | 218811.3905 | 218811.3905 | 1908872.4215 | 218811.3905
| ART033-155052479 | 50 | ART033 | ART | North | 1178316.3096 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.002807 | 0.0028326 | 0.0028583 | 0.0028839 | 0.0029096 | 0.0029026 | 0.0028956 | 0.0028887 | 0.0028817 | 0.0028748 | 0.0028678 | 0.0028608 | 0.0028539 | 0.0028469 | 0.00284 | 0.002833 | 0.002826 | 0.0028191 | 0.0028121 | 0.0028052 | 7.2286e-05 | 7.3217e-05 | 7.4508e-05 | 7.524e-05 | 7.5483e-05 | 7.5578e-05 | 7.6458e-05 | 7.6909e-05 | 7.5668e-05 | 7.5485e-05 | 7.5302e-05 | 7.512e-05 | 7.4937e-05 | 7.4754e-05 | 7.4571e-05 | 7.4389e-05 | 7.4206e-05 | 7.4023e-05 | 7.384e-05 | 7.3658e-05 | 32690.9757 | 6311.913 | 35.3519 | 6.8257 | 2434.4073 | 2434.4073 | 1178316.3096 | 2434.4073
| ART033-155052606 | 18 | ART033 | ART | North | 424193.8715 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 2.5971e-05 | 2.6379e-05 | 2.6786e-05 | 2.7193e-05 | 2.76e-05 | 2.7398e-05 | 2.7195e-05 | 2.6993e-05 | 2.679e-05 | 2.6588e-05 | 2.6385e-05 | 2.6183e-05 | 2.598e-05 | 2.5778e-05 | 2.5575e-05 | 2.5373e-05 | 2.517e-05 | 2.4968e-05 | 2.4765e-05 | 2.4563e-05 | 6.6883e-07 | 6.8183e-07 | 6.9824e-07 | 7.0945e-07 | 7.1603e-07 | 7.1338e-07 | 7.1807e-07 | 7.1865e-07 | 7.0345e-07 | 6.9813e-07 | 6.9282e-07 | 6.875e-07 | 6.8218e-07 | 6.7686e-07 | 6.7155e-07 | 6.6623e-07 | 6.6091e-07 | 6.5559e-07 | 6.5028e-07 | 6.4496e-07 | 32690.9757 | 6311.913 | 0.32552 | 0.062851 | 32.2806 | 32.2806 | 424193.8715 | 32.2806
| ART033-155052720 | 13 | ART033 | ART | North | 306362.2405 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 2.3326e-05 | 2.363e-05 | 2.3933e-05 | 2.4237e-05 | 2.454e-05 | 2.4447e-05 | 2.4354e-05 | 2.4261e-05 | 2.4168e-05 | 2.4075e-05 | 2.3982e-05 | 2.3889e-05 | 2.3796e-05 | 2.3703e-05 | 2.361e-05 | 2.3517e-05 | 2.3424e-05 | 2.3331e-05 | 2.3238e-05 | 2.3145e-05 | 6.0071e-07 | 6.1078e-07 | 6.2388e-07 | 6.3232e-07 | 6.3664e-07 | 6.3656e-07 | 6.4305e-07 | 6.4593e-07 | 6.346e-07 | 6.3216e-07 | 6.2972e-07 | 6.2728e-07 | 6.2483e-07 | 6.2239e-07 | 6.1995e-07 | 6.1751e-07 | 6.1507e-07 | 6.1262e-07 | 6.1018e-07 | 6.0774e-07 | 32690.9757 | 6311.913 | 0.29533 | 0.057021 | 17.6254 | 17.6254 | 306362.2405 | 17.6254
| ART033-155062161 | 13 | ART033 | ART | North | 306362.2405 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 2.0734e-05 | 2.1026e-05 | 2.1317e-05 | 2.1609e-05 | 2.19e-05 | 2.1816e-05 | 2.1732e-05 | 2.1648e-05 | 2.1564e-05 | 2.148e-05 | 2.1396e-05 | 2.1312e-05 | 2.1228e-05 | 2.1144e-05 | 2.106e-05 | 2.0976e-05 | 2.0892e-05 | 2.0808e-05 | 2.0724e-05 | 2.064e-05 | 5.3396e-07 | 5.4347e-07 | 5.5568e-07 | 5.6376e-07 | 5.6815e-07 | 5.6805e-07 | 5.7382e-07 | 5.7636e-07 | 5.6623e-07 | 5.6402e-07 | 5.6181e-07 | 5.5961e-07 | 5.574e-07 | 5.552e-07 | 5.5299e-07 | 5.5079e-07 | 5.4858e-07 | 5.4638e-07 | 5.4417e-07 | 5.4196e-07 | 32690.9757 | 6311.913 | 0.26333 | 0.050843 | 15.7155 | 15.7155 | 306362.2405 | 15.7155
| ART033-155062324 | 15 | ART033 | ART | North | 353494.8929 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 2.2585e-06 | 2.2901e-06 | 2.3217e-06 | 2.3534e-06 | 2.385e-06 | 2.3733e-06 | 2.3616e-06 | 2.3499e-06 | 2.3382e-06 | 2.3265e-06 | 2.3148e-06 | 2.3031e-06 | 2.2914e-06 | 2.2797e-06 | 2.268e-06 | 2.2563e-06 | 2.2446e-06 | 2.2329e-06 | 2.2212e-06 | 2.2095e-06 | 5.8162e-08 | 5.9194e-08 | 6.0522e-08 | 6.1398e-08 | 6.1874e-08 | 6.1796e-08 | 6.2357e-08 | 6.2564e-08 | 6.1396e-08 | 6.1089e-08 | 6.0782e-08 | 6.0475e-08 | 6.0167e-08 | 5.986e-08 | 5.9553e-08 | 5.9246e-08 | 5.8939e-08 | 5.8631e-08 | 5.8324e-08 | 5.8017e-08 | 32690.9757 | 6311.913 | 0.028519 | 0.0055065 | 3.9279 | 3.9279 | 353494.8929 | 3.9279
| ART033-155062418 | 77 | ART033 | ART | North | 1814607.1168 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.037352 | 0.037738 | 0.038123 | 0.038508 | 0.038893 | 0.038682 | 0.038471 | 0.03826 | 0.038049 | 0.037838 | 0.037627 | 0.037416 | 0.037206 | 0.036995 | 0.036784 | 0.036573 | 0.036362 | 0.036151 | 0.03594 | 0.035729 | 0.00096192 | 0.00097543 | 0.00099376 | 0.0010046 | 0.001009 | 0.0010072 | 0.0010158 | 0.0010186 | 0.00099909 | 0.00099356 | 0.00098802 | 0.00098248 | 0.00097694 | 0.0009714 | 0.00096586 | 0.00096033 | 0.00095479 | 0.00094925 | 0.00094371 | 0.00093817 | 32690.9757 | 6311.913 | 464.8676 | 89.7558 | 25947.7226 | 25947.7226 | 1814607.1168 | 25947.7226
| ART033-155079125 | 98 | ART033 | ART | North | 2309499.9668 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.013329 | 0.013439 | 0.013548 | 0.013657 | 0.013767 | 0.013706 | 0.013644 | 0.013583 | 0.013522 | 0.013461 | 0.013399 | 0.013338 | 0.013277 | 0.013215 | 0.013154 | 0.013093 | 0.013032 | 0.01297 | 0.012909 | 0.012848 | 0.00034326 | 0.00034736 | 0.00035316 | 0.00035632 | 0.00035715 | 0.00035687 | 0.00036027 | 0.00036164 | 0.00035505 | 0.00035345 | 0.00035184 | 0.00035023 | 0.00034862 | 0.00034701 | 0.0003454 | 0.00034379 | 0.00034219 | 0.00034058 | 0.00033897 | 0.00033736 | 32690.9757 | 6311.913 | 165.6002 | 31.9738 | 19436.591 | 19436.591 | 2309499.9668 | 19436.591
| ART033-155091128 | 93 | ART033 | ART | North | 2191668.3358 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.029759 | 0.029934 | 0.030109 | 0.030283 | 0.030458 | 0.030372 | 0.030287 | 0.030201 | 0.030116 | 0.03003 | 0.029945 | 0.029859 | 0.029774 | 0.029688 | 0.029603 | 0.029517 | 0.029432 | 0.029346 | 0.029261 | 0.029175 | 0.00076637 | 0.00077372 | 0.00078485 | 0.00079007 | 0.00079017 | 0.00079084 | 0.00079971 | 0.00080409 | 0.00079078 | 0.00078854 | 0.00078629 | 0.00078405 | 0.0007818 | 0.00077956 | 0.00077731 | 0.00077507 | 0.00077282 | 0.00077058 | 0.00076833 | 0.00076608 | 32690.9757 | 6311.913 | 370.037 | 71.4461 | 28725.5502 | 28725.5502 | 2191668.3358 | 28725.5502
| ART033-155155386 | 11 | ART033 | ART | North | 259229.5881 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.0031176 | 0.0031392 | 0.0031608 | 0.0031824 | 0.003204 | 0.0031983 | 0.0031925 | 0.0031868 | 0.003181 | 0.0031752 | 0.0031695 | 0.0031637 | 0.003158 | 0.0031522 | 0.0031464 | 0.0031407 | 0.0031349 | 0.0031291 | 0.0031234 | 0.0031176 | 8.0286e-05 | 8.1142e-05 | 8.2395e-05 | 8.3028e-05 | 8.3123e-05 | 8.3278e-05 | 8.4297e-05 | 8.4845e-05 | 8.3526e-05 | 8.3375e-05 | 8.3224e-05 | 8.3073e-05 | 8.2921e-05 | 8.277e-05 | 8.2619e-05 | 8.2467e-05 | 8.2316e-05 | 8.2165e-05 | 8.2013e-05 | 8.1862e-05 | 32690.9757 | 6311.913 | 39.102 | 7.5497 | 2369.5379 | 2369.5379 | 259229.5881 | 2369.5379
| ART033-162913151 | 377 | ART033 | ART | North | 8884504.9743 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 1.4224 | 1.4333 | 1.4441 | 1.455 | 1.4659 | 1.4617 | 1.4575 | 1.4533 | 1.449 | 1.4448 | 1.4406 | 1.4364 | 1.4322 | 1.428 | 1.4238 | 1.4196 | 1.4153 | 1.4111 | 1.4069 | 1.4027 | 0.03663 | 0.037046 | 0.037645 | 0.03796 | 0.03803 | 0.03806 | 0.038484 | 0.038692 | 0.038049 | 0.037938 | 0.037828 | 0.037717 | 0.037606 | 0.037496 | 0.037385 | 0.037275 | 0.037164 | 0.037053 | 0.036943 | 0.036832 | 32690.9757 | 6311.913 | 17783.3826 | 3433.5826 | 477584.3523 | 477584.3523 | 8884504.9743 | 477584.3523
| ART033-183308941 | 17 | ART033 | ART | North | 400627.5453 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 6.3363e-06 | 6.4173e-06 | 6.4982e-06 | 6.5791e-06 | 6.66e-06 | 6.6261e-06 | 6.5922e-06 | 6.5583e-06 | 6.5244e-06 | 6.4905e-06 | 6.4566e-06 | 6.4227e-06 | 6.3888e-06 | 6.3549e-06 | 6.321e-06 | 6.2871e-06 | 6.2532e-06 | 6.2193e-06 | 6.1854e-06 | 6.1515e-06 | 1.6318e-07 | 1.6587e-07 | 1.6939e-07 | 1.7164e-07 | 1.7278e-07 | 1.7253e-07 | 1.7406e-07 | 1.7461e-07 | 1.7132e-07 | 1.7043e-07 | 1.6954e-07 | 1.6865e-07 | 1.6776e-07 | 1.6687e-07 | 1.6598e-07 | 1.6509e-07 | 1.642e-07 | 1.6331e-07 | 1.6242e-07 | 1.6153e-07 | 32690.9757 | 6311.913 | 0.079622 | 0.015373 | 6.2141 | 6.2141 | 400627.5453 | 6.2141
| ART033-24601322 | 962 | ART033 | ART | North | 22670805.7965 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 4.0046 | 4.0406 | 4.0766 | 4.1126 | 4.1486 | 4.139 | 4.1294 | 4.1197 | 4.1101 | 4.1004 | 4.0908 | 4.0812 | 4.0715 | 4.0619 | 4.0523 | 4.0426 | 4.033 | 4.0234 | 4.0137 | 4.0041 | 0.10313 | 0.10444 | 0.10627 | 0.1073 | 0.10763 | 0.10777 | 0.10903 | 0.10968 | 0.10792 | 0.10767 | 0.10742 | 0.10716 | 0.10691 | 0.10666 | 0.1064 | 0.10615 | 0.1059 | 0.10565 | 0.10539 | 0.10514 | 32690.9757 | 6311.913 | 50429.5152 | 9736.8374 | 1843183.5821 | 1843183.5821 | 22670805.7965 | 1843183.5821
| ART033-80719107 | 41 | ART033 | ART | North | 966219.3739 | 0.00092502 | 0.00092844 | 0.00093633 | 0.00093712 | 0.00093186 | 0.00093528 | 0.00094843 | 0.00095633 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.00094317 | 0.063922 | 0.06446 | 0.064998 | 0.065537 | 0.066075 | 0.06609 | 0.066105 | 0.06612 | 0.066135 | 0.066149 | 0.066164 | 0.066179 | 0.066194 | 0.066209 | 0.066224 | 0.066239 | 0.066254 | 0.066269 | 0.066283 | 0.066298 | 0.0016461 | 0.0016661 | 0.0016943 | 0.0017098 | 0.0017142 | 0.0017209 | 0.0017455 | 0.0017604 | 0.0017366 | 0.0017369 | 0.0017373 | 0.0017377 | 0.0017381 | 0.0017385 | 0.0017389 | 0.0017393 | 0.0017397 | 0.0017401 | 0.0017405 | 0.0017409 | 32690.9757 | 6311.913 | 813.9694 | 157.1597 | 26263.0352 | 26263.0352 | 966219.3739 | 26263.0352
| ART034-15411844 | 338 | ART034 | ART | North | 7965418.2528 | 0.0010736 | 0.0010742 | 0.0010687 | 0.0010631 | 0.0010514 | 0.0010481 | 0.0010574 | 0.0010623 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 63.5463 | 64.0829 | 64.6195 | 65.1561 | 65.6927 | 65.7465 | 65.8002 | 65.854 | 65.9078 | 65.9616 | 66.0154 | 66.0692 | 66.123 | 66.1768 | 66.2306 | 66.2844 | 66.3382 | 66.392 | 66.4458 | 66.4996 | 1.8994 | 1.9165 | 1.9226 | 1.9285 | 1.9229 | 1.9185 | 1.937 | 1.9476 | 1.9443 | 1.9459 | 1.9475 | 1.9491 | 1.9506 | 1.9522 | 1.9538 | 1.9554 | 1.957 | 1.9586 | 1.9602 | 1.9618 | 32690.9757 | 6311.913 | 916174.7917 | 176893.3315 | 3113491.3682 | 3113491.3682 | 7965418.2528 | 3113491.3682
| ART034-15411868 | 0 | ART034 | ART | North | 0 | 0.0010736 | 0.0010742 | 0.0010687 | 0.0010631 | 0.0010514 | 0.0010481 | 0.0010574 | 0.0010623 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 0.0010596 | 3.7579e-06 | 3.8071e-06 | 3.8564e-06 | 3.9057e-06 | 3.955e-06 | 3.9635e-06 | 3.972e-06 | 3.9805e-06 | 3.989e-06 | 3.9975e-06 | 4.006e-06 | 4.0145e-06 | 4.023e-06 | 4.0315e-06 | 4.04e-06 | 4.0485e-06 | 4.057e-06 | 4.0655e-06 | 4.074e-06 | 4.0825e-06 | 1.1232e-07 | 1.1386e-07 | 1.1474e-07 | 1.156e-07 | 1.1577e-07 | 1.1565e-07 | 1.1692e-07 | 1.1772e-07 | 1.1768e-07 | 1.1793e-07 | 1.1818e-07 | 1.1843e-07 | 1.1868e-07 | 1.1893e-07 | 1.1918e-07 | 1.1943e-07 | 1.1968e-07 | 1.1993e-07 | 1.2018e-07 | 1.2043e-07 | 32690.9757 | 6311.913 | 0 | 0 | 0 | 0 | 0 | 0
| BAN001-15414753 | 0 | BAN001 | BAN | South | 0 | 0.0062954 | 0.0062718 | 0.0062821 | 0.0062687 | 0.0062554 | 0.0062892 | 0.0063579 | 0.0064123 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32573.8452 | 5704.3195 | 0 | 0 | 0 | 0 | 0 | 0
| BAN001-15414766 | 143 | BAN001 | BAN | South | 2599853.1318 | 0.0062954 | 0.0062718 | 0.0062821 | 0.0062687 | 0.0062554 | 0.0062892 | 0.0063579 | 0.0064123 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0.0063887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32573.8452 | 5704.3195 | 0 | 0 | 0 | 0 | 2713180.6318 | 0
| BAN002-15414829 | 172 | BAN002 | BAN | South | 3127096.0746 | 0.0029349 | 0.0029381 | 0.0029339 | 0.0029265 | 0.0029181 | 0.0029197 | 0.0029385 | 0.0029517 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 0.002954 | 17.8322 | 17.9557 | 18.0793 | 18.2029 | 18.3265 | 18.365 | 18.4035 | 18.442 | 18.4805 | 18.519 | 18.5575 | 18.5961 | 18.6346 | 18.6731 | 18.7116 | 18.7501 | 18.7886 | 18.8271 | 18.8656 | 18.9042 | 1.457 | 1.4687 | 1.4767 | 1.4831 | 1.4888 | 1.4928 | 1.5055 | 1.5155 | 1.5198 | 1.523 | 1.5262 | 1.5293 | 1.5325 | 1.5357 | 1.5388 | 1.542 | 1.5452 | 1.5483 | 1.5515 | 1.5547 | 32573.8452 | 5704.3195 | 711722.176 | 124636.5195 | 539959.7208 | 699907.2162 | 3263406.0746 | 563496.5446
| BAN003-141839634 | 59 | BAN003 | BAN | South | 1072666.6768 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.039486 | 0.039823 | 0.040161 | 0.040498 | 0.040835 | 0.041 | 0.041165 | 0.04133 | 0.041495 | 0.04166 | 0.041825 | 0.04199 | 0.042155 | 0.04232 | 0.042485 | 0.04265 | 0.042815 | 0.04298 | 0.043145 | 0.04331 | 0.0013014 | 0.0013457 | 0.001396 | 0.0014393 | 0.0014785 | 0.0015242 | 0.0015811 | 0.001628 | 0.0016548 | 0.0016614 | 0.0016679 | 0.0016745 | 0.0016811 | 0.0016877 | 0.0016943 | 0.0017008 | 0.0017074 | 0.001714 | 0.0017206 | 0.0017271 | 32573.8452 | 5704.3195 | 741.6581 | 129.8789 | 26781.2493 | 34714.4221 | 1119424.1768 | 27948.643
| BAN003-141839757 | 47 | BAN003 | BAN | South | 854497.1832 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.42045 | 0.42272 | 0.42499 | 0.42726 | 0.42953 | 0.43045 | 0.43136 | 0.43228 | 0.4332 | 0.43411 | 0.43503 | 0.43594 | 0.43686 | 0.43777 | 0.43869 | 0.43961 | 0.44052 | 0.44144 | 0.44235 | 0.44327 | 0.013857 | 0.014285 | 0.014773 | 0.015185 | 0.015552 | 0.016002 | 0.016568 | 0.017028 | 0.017275 | 0.017312 | 0.017349 | 0.017385 | 0.017422 | 0.017458 | 0.017495 | 0.017531 | 0.017568 | 0.017604 | 0.017641 | 0.017677 | 32573.8452 | 5704.3195 | 7737.5184 | 1354.9913 | 100855.4097 | 130730.9163 | 891744.6832 | 105251.6932
| BAN003-141839920 | 28 | BAN003 | BAN | South | 509062.1517 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.023229 | 0.023398 | 0.023568 | 0.023738 | 0.023908 | 0.023993 | 0.024078 | 0.024163 | 0.024248 | 0.024333 | 0.024418 | 0.024503 | 0.024588 | 0.024673 | 0.024758 | 0.024843 | 0.024928 | 0.025013 | 0.025099 | 0.025184 | 0.00076558 | 0.00079069 | 0.00081925 | 0.00084368 | 0.00086565 | 0.00089196 | 0.0009248 | 0.00095178 | 0.00096699 | 0.00097038 | 0.00097377 | 0.00097716 | 0.00098056 | 0.00098395 | 0.00098734 | 0.00099073 | 0.00099412 | 0.00099752 | 0.0010009 | 0.0010043 | 32573.8452 | 5704.3195 | 433.425 | 75.9012 | 16208.8017 | 21010.1917 | 531252.1517 | 16915.3427
| BAN003-141840240 | 41 | BAN003 | BAN | South | 745412.4364 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.73646 | 0.74123 | 0.74601 | 0.75078 | 0.75556 | 0.75919 | 0.76281 | 0.76644 | 0.77006 | 0.77369 | 0.77732 | 0.78094 | 0.78457 | 0.7882 | 0.79182 | 0.79545 | 0.79907 | 0.8027 | 0.80633 | 0.80995 | 0.024272 | 0.025048 | 0.025932 | 0.026684 | 0.027357 | 0.028223 | 0.029299 | 0.03019 | 0.030709 | 0.030854 | 0.030999 | 0.031143 | 0.031288 | 0.031433 | 0.031577 | 0.031722 | 0.031866 | 0.032011 | 0.032156 | 0.0323 | 32573.8452 | 5704.3195 | 13792.0516 | 2415.2589 | 176719.3343 | 229067.3408 | 777904.9364 | 184422.5235
| BAN003-154067153 | 168 | BAN003 | BAN | South | 3054372.9101 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 139.2057 | 139.8514 | 140.4971 | 141.1427 | 141.7884 | 142.5332 | 143.2779 | 144.0226 | 144.7674 | 145.5121 | 146.2568 | 147.0015 | 147.7463 | 148.491 | 149.2357 | 149.9804 | 150.7252 | 151.4699 | 152.2146 | 152.9594 | 4.588 | 4.7259 | 4.8838 | 5.0164 | 5.1338 | 5.2988 | 5.5031 | 5.6731 | 5.7732 | 5.8029 | 5.8326 | 5.8623 | 5.892 | 5.9217 | 5.9514 | 5.9811 | 6.0108 | 6.0405 | 6.0702 | 6.0999 | 32573.8452 | 5704.3195 | 2596886.3568 | 454765.7609 | 1513719.8943 | 1962115.7591 | 3187512.9101 | 1579702.8875
| BAN003-15414742 | 373 | BAN003 | BAN | South | 6781435.092 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 320.5546 | 320.8195 | 321.0844 | 321.3493 | 321.6142 | 321.3859 | 321.1576 | 320.9293 | 320.701 | 320.4727 | 320.2444 | 320.0161 | 319.7878 | 319.5595 | 319.3312 | 319.1029 | 318.8746 | 318.6463 | 318.418 | 318.1897 | 10.565 | 10.8413 | 11.1611 | 11.4211 | 11.6449 | 11.9478 | 12.3352 | 12.6414 | 12.7893 | 12.7802 | 12.7711 | 12.762 | 12.7528 | 12.7437 | 12.7346 | 12.7255 | 12.7164 | 12.7073 | 12.6982 | 12.6891 | 32573.8452 | 5704.3195 | 5722458.5922 | 1002114.7937 | 5419737.9674 | 7025179.0414 | 7077037.592 | 5655984.141
| BAN003-159380665 | 65 | BAN003 | BAN | South | 1181751.4235 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.36564 | 0.36928 | 0.37293 | 0.37658 | 0.38023 | 0.38174 | 0.38326 | 0.38477 | 0.38628 | 0.38779 | 0.3893 | 0.39081 | 0.39233 | 0.39384 | 0.39535 | 0.39686 | 0.39837 | 0.39989 | 0.4014 | 0.40291 | 0.012051 | 0.012479 | 0.012963 | 0.013384 | 0.013767 | 0.014192 | 0.01472 | 0.015156 | 0.015404 | 0.015465 | 0.015525 | 0.015585 | 0.015646 | 0.015706 | 0.015766 | 0.015827 | 0.015887 | 0.015947 | 0.016007 | 0.016068 | 32573.8452 | 5704.3195 | 6898.2845 | 1208.025 | 177993.3905 | 230718.7993 | 1233263.9235 | 185752.1156
| BAN003-159380816 | 93 | BAN003 | BAN | South | 1690813.5752 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.78119 | 0.78654 | 0.79189 | 0.79723 | 0.80258 | 0.80477 | 0.80695 | 0.80914 | 0.81133 | 0.81352 | 0.81571 | 0.81789 | 0.82008 | 0.82227 | 0.82446 | 0.82665 | 0.82883 | 0.83102 | 0.83321 | 0.8354 | 0.025747 | 0.026579 | 0.027526 | 0.028335 | 0.02906 | 0.029918 | 0.030994 | 0.031872 | 0.032355 | 0.032442 | 0.03253 | 0.032617 | 0.032704 | 0.032791 | 0.032879 | 0.032966 | 0.033053 | 0.03314 | 0.033228 | 0.033315 | 32573.8452 | 5704.3195 | 14490.8203 | 2537.627 | 247546.5458 | 320875.071 | 1764516.0752 | 258337.0904
| BAN003-163842570 | 14 | BAN003 | BAN | South | 254531.0758 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.06279 | 0.063328 | 0.063866 | 0.064404 | 0.064942 | 0.065526 | 0.066111 | 0.066695 | 0.067279 | 0.067863 | 0.068448 | 0.069032 | 0.069616 | 0.070201 | 0.070785 | 0.071369 | 0.071953 | 0.072538 | 0.073122 | 0.073706 | 0.0020695 | 0.00214 | 0.00222 | 0.002289 | 0.0023514 | 0.002436 | 0.0025392 | 0.0026271 | 0.002683 | 0.0027063 | 0.0027296 | 0.0027529 | 0.0027762 | 0.0027995 | 0.0028228 | 0.0028461 | 0.0028694 | 0.0028927 | 0.002916 | 0.0029393 | 32573.8452 | 5704.3195 | 1209.788 | 211.8576 | 11295.5436 | 14641.5227 | 265626.0758 | 11787.916
| BAN003-164488210 | 26 | BAN003 | BAN | South | 472700.5694 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.065261 | 0.065853 | 0.066444 | 0.067035 | 0.067626 | 0.068164 | 0.068702 | 0.06924 | 0.069777 | 0.070315 | 0.070853 | 0.071391 | 0.071929 | 0.072467 | 0.073005 | 0.073543 | 0.07408 | 0.074618 | 0.075156 | 0.075694 | 0.0021509 | 0.0022253 | 0.0023096 | 0.0023825 | 0.0024486 | 0.002534 | 0.0026387 | 0.0027273 | 0.0027827 | 0.0028041 | 0.0028256 | 0.002847 | 0.0028685 | 0.0028899 | 0.0029114 | 0.0029328 | 0.0029543 | 0.0029757 | 0.0029972 | 0.0030186 | 32573.8452 | 5704.3195 | 1252.8198 | 219.3933 | 26556.427 | 34423.0026 | 493305.5694 | 27714.0206
| BAN003-171330864 | 24 | BAN003 | BAN | South | 436338.9872 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.29354 | 0.29594 | 0.29835 | 0.30076 | 0.30317 | 0.30515 | 0.30712 | 0.3091 | 0.31107 | 0.31305 | 0.31503 | 0.317 | 0.31898 | 0.32095 | 0.32293 | 0.32491 | 0.32688 | 0.32886 | 0.33083 | 0.33281 | 0.0096745 | 0.010001 | 0.010371 | 0.010689 | 0.010977 | 0.011344 | 0.011796 | 0.012175 | 0.012405 | 0.012484 | 0.012563 | 0.012642 | 0.012721 | 0.012799 | 0.012878 | 0.012957 | 0.013036 | 0.013115 | 0.013193 | 0.013272 | 32573.8452 | 5704.3195 | 5577.9986 | 976.817 | 51719.2818 | 67039.6275 | 455358.9872 | 53973.7233
| BAN003-193118819 | 436 | BAN003 | BAN | South | 7926824.9333 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 137.8172 | 138.4752 | 139.1333 | 139.7913 | 140.4494 | 141.3116 | 142.1739 | 143.0361 | 143.8984 | 144.7606 | 145.6229 | 146.4852 | 147.3474 | 148.2097 | 149.0719 | 149.9342 | 150.7964 | 151.6587 | 152.5209 | 153.3832 | 4.5422 | 4.6794 | 4.8364 | 4.9683 | 5.0854 | 5.2534 | 5.4607 | 5.6342 | 5.7385 | 5.7729 | 5.8073 | 5.8417 | 5.8761 | 5.9105 | 5.9449 | 5.9792 | 6.0136 | 6.048 | 6.0824 | 6.1168 | 32573.8452 | 5704.3195 | 2583894.6704 | 452490.6616 | 4446480.9282 | 5763622.6719 | 8272354.9333 | 4640302.8642
| BAN003-193396210 | 47 | BAN003 | BAN | South | 854497.1832 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 4.2825 | 4.3122 | 4.342 | 4.3717 | 4.4015 | 4.4372 | 4.473 | 4.5087 | 4.5444 | 4.5802 | 4.6159 | 4.6517 | 4.6874 | 4.7231 | 4.7589 | 4.7946 | 4.8304 | 4.8661 | 4.9018 | 4.9376 | 0.14114 | 0.14572 | 0.15093 | 0.15538 | 0.15937 | 0.16496 | 0.1718 | 0.1776 | 0.18123 | 0.18265 | 0.18408 | 0.1855 | 0.18693 | 0.18835 | 0.18978 | 0.19121 | 0.19263 | 0.19406 | 0.19548 | 0.19691 | 32573.8452 | 5704.3195 | 81700.9013 | 14307.4311 | 140668.5012 | 182337.488 | 891744.6832 | 146800.2359
| BAN003-193396225 | 299 | BAN003 | BAN | South | 5436056.5483 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 11.4508 | 11.5375 | 11.6242 | 11.7109 | 11.7976 | 11.8655 | 11.9334 | 12.0012 | 12.0691 | 12.137 | 12.2048 | 12.2727 | 12.3406 | 12.4085 | 12.4763 | 12.5442 | 12.6121 | 12.68 | 12.7478 | 12.8157 | 0.3774 | 0.38988 | 0.40406 | 0.41622 | 0.42716 | 0.44111 | 0.45834 | 0.47273 | 0.4813 | 0.48401 | 0.48672 | 0.48942 | 0.49213 | 0.49484 | 0.49754 | 0.50025 | 0.50296 | 0.50567 | 0.50837 | 0.51108 | 32573.8452 | 5704.3195 | 216286.811 | 37876.0649 | 2367251.0516 | 3068480.9069 | 5673014.0483 | 2470439.4356
| BAN003-193396423 | 365 | BAN003 | BAN | South | 6635988.763 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 50.716 | 50.9504 | 51.1848 | 51.4193 | 51.6537 | 51.8774 | 52.1011 | 52.3248 | 52.5485 | 52.7722 | 52.9959 | 53.2196 | 53.4433 | 53.667 | 53.8907 | 54.1144 | 54.3381 | 54.5617 | 54.7854 | 55.0091 | 1.6715 | 1.7217 | 1.7792 | 1.8275 | 1.8703 | 1.9286 | 2.0011 | 2.0611 | 2.0956 | 2.1045 | 2.1134 | 2.1223 | 2.1313 | 2.1402 | 2.1491 | 2.158 | 2.167 | 2.1759 | 2.1848 | 2.1937 | 32573.8452 | 5704.3195 | 941575.2457 | 164888.3025 | 4636025.0117 | 6009313.724 | 6925251.263 | 4838109.1672
| BAN003-24598678 | 71 | BAN003 | BAN | South | 1290836.1703 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.040082 | 0.040428 | 0.040774 | 0.04112 | 0.041465 | 0.041689 | 0.041912 | 0.042136 | 0.04236 | 0.042583 | 0.042807 | 0.043031 | 0.043254 | 0.043478 | 0.043702 | 0.043925 | 0.044149 | 0.044372 | 0.044596 | 0.04482 | 0.0013211 | 0.0013662 | 0.0014173 | 0.0014614 | 0.0015014 | 0.0015498 | 0.0016098 | 0.0016597 | 0.0016893 | 0.0016982 | 0.0017071 | 0.001716 | 0.0017249 | 0.0017339 | 0.0017428 | 0.0017517 | 0.0017606 | 0.0017695 | 0.0017785 | 0.0017874 | 32573.8452 | 5704.3195 | 758.3534 | 132.8026 | 12549.7834 | 16267.2949 | 1347103.6703 | 13096.828
| BAN003-24598720 | 161 | BAN003 | BAN | South | 2927107.3722 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 1.2278 | 1.2286 | 1.2294 | 1.2302 | 1.2309 | 1.2303 | 1.2297 | 1.229 | 1.2284 | 1.2278 | 1.2271 | 1.2265 | 1.2259 | 1.2252 | 1.2246 | 1.2239 | 1.2233 | 1.2227 | 1.222 | 1.2214 | 0.040468 | 0.041518 | 0.042735 | 0.043722 | 0.04457 | 0.045738 | 0.04723 | 0.048412 | 0.048987 | 0.048962 | 0.048937 | 0.048911 | 0.048886 | 0.048861 | 0.048835 | 0.04881 | 0.048785 | 0.048759 | 0.048734 | 0.048708 | 32573.8452 | 5704.3195 | 21926.9812 | 3839.8447 | 302196.7581 | 391713.8327 | 3054699.8722 | 315369.5034
| BAN003-24598790 | 259 | BAN003 | BAN | South | 4708824.903 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 15.5207 | 15.5928 | 15.6649 | 15.7369 | 15.809 | 15.8467 | 15.8844 | 15.9221 | 15.9598 | 15.9974 | 16.0351 | 16.0728 | 16.1105 | 16.1482 | 16.1858 | 16.2235 | 16.2612 | 16.2989 | 16.3366 | 16.3742 | 0.51154 | 0.52692 | 0.54452 | 0.55931 | 0.57241 | 0.58911 | 0.6101 | 0.62717 | 0.63646 | 0.63796 | 0.63947 | 0.64097 | 0.64247 | 0.64397 | 0.64548 | 0.64698 | 0.64848 | 0.64998 | 0.65149 | 0.65299 | 32573.8452 | 5704.3195 | 285274.9555 | 49957.2428 | 2120878.0607 | 2749127.0225 | 4914082.403 | 2213327.0554
| BAN003-24610965 | 25 | BAN003 | BAN | South | 454519.7783 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.10312 | 0.10387 | 0.10462 | 0.10537 | 0.10612 | 0.10755 | 0.10898 | 0.11042 | 0.11185 | 0.11328 | 0.11471 | 0.11614 | 0.11758 | 0.11901 | 0.12044 | 0.12187 | 0.1233 | 0.12474 | 0.12617 | 0.1276 | 0.0033987 | 0.0035101 | 0.0036367 | 0.003745 | 0.0038424 | 0.0039983 | 0.0041859 | 0.0043493 | 0.0044604 | 0.0045175 | 0.0045746 | 0.0046317 | 0.0046888 | 0.0047459 | 0.004803 | 0.0048601 | 0.0049172 | 0.0049743 | 0.0050314 | 0.0050886 | 32573.8452 | 5704.3195 | 2023.1584 | 354.2947 | 23917.2198 | 31002.0064 | 474332.2783 | 24959.7705
| BAN003-79423703 | 27 | BAN003 | BAN | South | 490881.3605 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.066188 | 0.066658 | 0.067128 | 0.067598 | 0.068067 | 0.068418 | 0.068769 | 0.06912 | 0.069471 | 0.069822 | 0.070173 | 0.070524 | 0.070875 | 0.071226 | 0.071577 | 0.071928 | 0.072279 | 0.07263 | 0.072981 | 0.073332 | 0.0021815 | 0.0022525 | 0.0023334 | 0.0024025 | 0.0024646 | 0.0025435 | 0.0026413 | 0.0027226 | 0.0027704 | 0.0027844 | 0.0027984 | 0.0028124 | 0.0028264 | 0.0028404 | 0.0028544 | 0.0028684 | 0.0028824 | 0.0028964 | 0.0029104 | 0.0029244 | 32573.8452 | 5704.3195 | 1244.3789 | 217.9152 | 21453.7753 | 27808.8375 | 512278.8605 | 22388.9445
| BAN003-79424004 | 22 | BAN003 | BAN | South | 399977.4049 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.39892 | 0.40166 | 0.4044 | 0.40713 | 0.40987 | 0.41218 | 0.41448 | 0.41679 | 0.41909 | 0.4214 | 0.42371 | 0.42601 | 0.42832 | 0.43063 | 0.43293 | 0.43524 | 0.43754 | 0.43985 | 0.44216 | 0.44446 | 0.013148 | 0.013573 | 0.014057 | 0.01447 | 0.01484 | 0.015323 | 0.01592 | 0.016417 | 0.016713 | 0.016805 | 0.016897 | 0.016989 | 0.017081 | 0.017173 | 0.017265 | 0.017357 | 0.017449 | 0.017541 | 0.017633 | 0.017725 | 32573.8452 | 5704.3195 | 7512.1942 | 1315.5326 | 31933.802 | 41393.2699 | 417412.4049 | 33325.7952
| BAN003-79424224 | 56 | BAN003 | BAN | South | 1018124.3034 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.38782 | 0.39078 | 0.39374 | 0.3967 | 0.39966 | 0.40205 | 0.40443 | 0.40681 | 0.40919 | 0.41157 | 0.41395 | 0.41633 | 0.41871 | 0.42109 | 0.42347 | 0.42585 | 0.42824 | 0.43062 | 0.433 | 0.43538 | 0.012782 | 0.013206 | 0.013687 | 0.014099 | 0.014471 | 0.014946 | 0.015533 | 0.016024 | 0.016318 | 0.016413 | 0.016508 | 0.016603 | 0.016698 | 0.016793 | 0.016888 | 0.016983 | 0.017078 | 0.017173 | 0.017268 | 0.017362 | 32573.8452 | 5704.3195 | 7334.536 | 1284.4212 | 128316.2855 | 166326.2845 | 1062504.3034 | 133909.5875
| BAN003-79424313 | 43 | BAN003 | BAN | South | 781774.0187 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.26298 | 0.26544 | 0.26791 | 0.27037 | 0.27283 | 0.27443 | 0.27603 | 0.27763 | 0.27923 | 0.28083 | 0.28243 | 0.28403 | 0.28564 | 0.28724 | 0.28884 | 0.29044 | 0.29204 | 0.29364 | 0.29524 | 0.29684 | 0.0086675 | 0.00897 | 0.0093126 | 0.0096091 | 0.0098785 | 0.010202 | 0.010602 | 0.010936 | 0.011135 | 0.011199 | 0.011263 | 0.011327 | 0.011391 | 0.011455 | 0.011519 | 0.011582 | 0.011646 | 0.01171 | 0.011774 | 0.011838 | 32573.8452 | 5704.3195 | 4999.9568 | 875.5905 | 54423.2856 | 70544.6144 | 815851.5187 | 56795.5945
| BAN003-79424384 | 77 | BAN003 | BAN | South | 1399920.9171 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.81402 | 0.8201 | 0.82619 | 0.83227 | 0.83836 | 0.84294 | 0.84753 | 0.85211 | 0.8567 | 0.86129 | 0.86587 | 0.87046 | 0.87504 | 0.87963 | 0.88421 | 0.8888 | 0.89338 | 0.89797 | 0.90256 | 0.90714 | 0.026829 | 0.027713 | 0.028719 | 0.02958 | 0.030355 | 0.031337 | 0.032552 | 0.033565 | 0.034164 | 0.034347 | 0.03453 | 0.034713 | 0.034896 | 0.035079 | 0.035262 | 0.035444 | 0.035627 | 0.03581 | 0.035993 | 0.036176 | 32573.8452 | 5704.3195 | 15348.1391 | 2687.7603 | 184625.2549 | 239315.1623 | 1460943.4171 | 192673.0628
| BAN003-79424629 | 68 | BAN003 | BAN | South | 1236293.7969 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.5117 | 0.51491 | 0.51813 | 0.52135 | 0.52456 | 0.5279 | 0.53123 | 0.53457 | 0.5379 | 0.54123 | 0.54457 | 0.5479 | 0.55123 | 0.55457 | 0.5579 | 0.56124 | 0.56457 | 0.5679 | 0.57124 | 0.57457 | 0.016865 | 0.0174 | 0.018011 | 0.018529 | 0.018993 | 0.019625 | 0.020404 | 0.021057 | 0.021451 | 0.021584 | 0.021717 | 0.02185 | 0.021983 | 0.022116 | 0.022249 | 0.022382 | 0.022515 | 0.022647 | 0.02278 | 0.022913 | 32573.8452 | 5704.3195 | 9653.3216 | 1690.486 | 120479.7942 | 156168.4587 | 1290183.7969 | 125731.5039
| BAN003-79424820 | 55 | BAN003 | BAN | South | 999943.5122 | 0.0011839 | 0.0012138 | 0.0012486 | 0.0012766 | 0.0013006 | 0.0013353 | 0.0013796 | 0.0014149 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.0014324 | 0.17995 | 0.18176 | 0.18357 | 0.18539 | 0.1872 | 0.18798 | 0.18877 | 0.18955 | 0.19034 | 0.19113 | 0.19191 | 0.1927 | 0.19348 | 0.19427 | 0.19505 | 0.19584 | 0.19662 | 0.19741 | 0.19819 | 0.19898 | 0.0059307 | 0.0061421 | 0.0063811 | 0.0065888 | 0.0067781 | 0.0069885 | 0.0072504 | 0.0074666 | 0.0075906 | 0.0076219 | 0.0076532 | 0.0076845 | 0.0077158 | 0.0077471 | 0.0077784 | 0.0078097 | 0.007841 | 0.0078723 | 0.0079037 | 0.007935 | 32573.8452 | 5704.3195 | 3399.8918 | 595.3878 | 70418.9218 | 91278.4966 | 1043531.0122 | 73488.48
| BAN004-15414853 | 0 | BAN004 | BAN | South | 0 | 0.0039187 | 0.0040154 | 0.0040049 | 0.003988 | 0.0039669 | 0.0039605 | 0.0039737 | 0.0039861 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32573.8452 | 5704.3195 | 0 | 0 | 0 | 0 | 0 | 0
| BAN004-15414866 | 0 | BAN004 | BAN | South | 0 | 0.0039187 | 0.0040154 | 0.0040049 | 0.003988 | 0.0039669 | 0.0039605 | 0.0039737 | 0.0039861 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32573.8452 | 5704.3195 | 0 | 0 | 0 | 0 | 0 | 0
| BAN004-15414892 | 187 | BAN004 | BAN | South | 3399807.9416 | 0.0039187 | 0.0040154 | 0.0040049 | 0.003988 | 0.0039669 | 0.0039605 | 0.0039737 | 0.0039861 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 0.0039733 | 2.9688 | 2.9935 | 3.0182 | 3.0429 | 3.0676 | 3.0788 | 3.0901 | 3.1014 | 3.1126 | 3.1239 | 3.1351 | 3.1464 | 3.1576 | 3.1689 | 3.1801 | 3.1914 | 3.2026 | 3.2139 | 3.2252 | 3.2364 | 0.32388 | 0.33464 | 0.33652 | 0.33784 | 0.33878 | 0.33947 | 0.34185 | 0.34416 | 0.3443 | 0.34555 | 0.34679 | 0.34804 | 0.34928 | 0.35053 | 0.35177 | 0.35302 | 0.35426 | 0.35551 | 0.35675 | 0.358 | 32573.8452 | 5704.3195 | 161979.2075 | 28365.7378 | 115390.0666 | 149571.0462 | 3548005.4416 | 120419.9153
| BAN005-15414666 | 148 | BAN005 | BAN | South | 2690757.0875 | 0.0037234 | 0.0040069 | 0.0040014 | 0.004 | 0.0039723 | 0.0039588 | 0.0039751 | 0.0040048 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0.0040024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32573.8452 | 5704.3195 | 0 | 0 | 0 | 0 | 2808047.0875 | 0
| BAN006-15414916 | 352 | BAN006 | BAN | South | 6399638.4783 | 0.0010058 | 0.0010309 | 0.0010668 | 0.0010996 | 0.0011307 | 0.0011686 | 0.0012127 | 0.0012513 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 31.9385 | 32.1947 | 32.4509 | 32.7071 | 32.9632 | 33.1131 | 33.263 | 33.4129 | 33.5628 | 33.7127 | 33.8626 | 34.0125 | 34.1624 | 34.3122 | 34.4621 | 34.612 | 34.7619 | 34.9118 | 35.0617 | 35.2116 | 0.89436 | 0.92403 | 0.96378 | 1.0013 | 1.0376 | 1.0773 | 1.123 | 1.164 | 1.1894 | 1.1947 | 1.2 | 1.2053 | 1.2107 | 1.216 | 1.2213 | 1.2266 | 1.2319 | 1.2372 | 1.2425 | 1.2478 | 32573.8452 | 5704.3195 | 527309.877 | 92342.3071 | 598235.2446 | 775445.1834 | 6678598.4783 | 624312.2964
| BAN006-157281583 | 19 | BAN006 | BAN | South | 345435.0315 | 0.0010058 | 0.0010309 | 0.0010668 | 0.0010996 | 0.0011307 | 0.0011686 | 0.0012127 | 0.0012513 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0024723 | 0.0024958 | 0.0025193 | 0.0025429 | 0.0025664 | 0.0025691 | 0.0025717 | 0.0025744 | 0.002577 | 0.0025796 | 0.0025823 | 0.0025849 | 0.0025876 | 0.0025902 | 0.0025929 | 0.0025955 | 0.0025982 | 0.0026008 | 0.0026034 | 0.0026061 | 6.9229e-05 | 7.1632e-05 | 7.4823e-05 | 7.7848e-05 | 8.0786e-05 | 8.3584e-05 | 8.6825e-05 | 8.9681e-05 | 9.1325e-05 | 9.1418e-05 | 9.1512e-05 | 9.1606e-05 | 9.1699e-05 | 9.1793e-05 | 9.1887e-05 | 9.198e-05 | 9.2074e-05 | 9.2168e-05 | 9.2262e-05 | 9.2355e-05 | 32573.8452 | 5704.3195 | 40.2681 | 7.0517 | 2134.5697 | 2766.8744 | 360492.5315 | 2227.6155
| BAN006-161068079 | 65 | BAN006 | BAN | South | 1181751.4235 | 0.0010058 | 0.0010309 | 0.0010668 | 0.0010996 | 0.0011307 | 0.0011686 | 0.0012127 | 0.0012513 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.010241 | 0.010329 | 0.010417 | 0.010504 | 0.010592 | 0.010612 | 0.010632 | 0.010652 | 0.010671 | 0.010691 | 0.010711 | 0.010731 | 0.01075 | 0.01077 | 0.01079 | 0.01081 | 0.010829 | 0.010849 | 0.010869 | 0.010889 | 0.00028676 | 0.00029644 | 0.00030937 | 0.00032158 | 0.00033343 | 0.00034526 | 0.00035895 | 0.00037106 | 0.00037818 | 0.00037888 | 0.00037958 | 0.00038028 | 0.00038098 | 0.00038168 | 0.00038238 | 0.00038307 | 0.00038377 | 0.00038447 | 0.00038517 | 0.00038587 | 32573.8452 | 5704.3195 | 167.0195 | 29.2484 | 8259.0336 | 10705.5341 | 1233263.9235 | 8619.0446
| BAN006-193339101 | 340 | BAN006 | BAN | South | 6181468.9847 | 0.0010058 | 0.0010309 | 0.0010668 | 0.0010996 | 0.0011307 | 0.0011686 | 0.0012127 | 0.0012513 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 4.6388 | 4.6678 | 4.6968 | 4.7258 | 4.7548 | 4.7673 | 4.7799 | 4.7924 | 4.805 | 4.8176 | 4.8301 | 4.8427 | 4.8552 | 4.8678 | 4.8804 | 4.8929 | 4.9055 | 4.918 | 4.9306 | 4.9432 | 0.1299 | 0.13397 | 0.13949 | 0.14468 | 0.14967 | 0.1551 | 0.16138 | 0.16695 | 0.17028 | 0.17073 | 0.17117 | 0.17162 | 0.17206 | 0.17251 | 0.17295 | 0.1734 | 0.17384 | 0.17429 | 0.17473 | 0.17518 | 32573.8452 | 5704.3195 | 75374.9396 | 13199.631 | 416988.7634 | 540509.6592 | 6450918.9847 | 435165.2879
| BAN006-193339124 | 580 | BAN006 | BAN | South | 10544858.8562 | 0.0010058 | 0.0010309 | 0.0010668 | 0.0010996 | 0.0011307 | 0.0011686 | 0.0012127 | 0.0012513 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 12.0895 | 12.1423 | 12.1952 | 12.2481 | 12.301 | 12.301 | 12.301 | 12.301 | 12.301 | 12.301 | 12.301 | 12.301 | 12.301 | 12.3011 | 12.3011 | 12.3011 | 12.3011 | 12.3011 | 12.3011 | 12.3011 | 0.33854 | 0.3485 | 0.36219 | 0.37496 | 0.38721 | 0.40021 | 0.4153 | 0.42852 | 0.43593 | 0.43593 | 0.43593 | 0.43593 | 0.43593 | 0.43593 | 0.43593 | 0.43593 | 0.43593 | 0.43593 | 0.43593 | 0.43593 | 32573.8452 | 5704.3195 | 192481.8102 | 33707.3421 | 3338991.4077 | 4328071.3197 | 11004508.8562 | 3484537.9173
| BAN006-193339156 | 216 | BAN006 | BAN | South | 3927050.8844 | 0.0010058 | 0.0010309 | 0.0010668 | 0.0010996 | 0.0011307 | 0.0011686 | 0.0012127 | 0.0012513 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 5.7285 | 5.7834 | 5.8382 | 5.8931 | 5.9479 | 5.9577 | 5.9676 | 5.9774 | 5.9872 | 5.997 | 6.0069 | 6.0167 | 6.0265 | 6.0363 | 6.0462 | 6.056 | 6.0658 | 6.0756 | 6.0855 | 6.0953 | 0.16041 | 0.16599 | 0.17339 | 0.18041 | 0.18723 | 0.19383 | 0.20147 | 0.20823 | 0.21218 | 0.21252 | 0.21287 | 0.21322 | 0.21357 | 0.21392 | 0.21427 | 0.21461 | 0.21496 | 0.21531 | 0.21566 | 0.21601 | 32573.8452 | 5704.3195 | 93631.5251 | 16396.7174 | 636249.476 | 824720.0345 | 4098230.8844 | 663983.5666
| BAN006-193339179 | 361 | BAN006 | BAN | South | 6563265.5985 | 0.0010058 | 0.0010309 | 0.0010668 | 0.0010996 | 0.0011307 | 0.0011686 | 0.0012127 | 0.0012513 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 19.6147 | 19.664 | 19.7134 | 19.7628 | 19.8121 | 19.8745 | 19.9368 | 19.9992 | 20.0616 | 20.1239 | 20.1863 | 20.2487 | 20.311 | 20.3734 | 20.4358 | 20.4981 | 20.5605 | 20.6228 | 20.6852 | 20.7476 | 0.54926 | 0.56438 | 0.58548 | 0.60502 | 0.62364 | 0.64661 | 0.6731 | 0.6967 | 0.71095 | 0.71316 | 0.71537 | 0.71758 | 0.71979 | 0.722 | 0.72421 | 0.72642 | 0.72863 | 0.73084 | 0.73305 | 0.73526 | 32573.8452 | 5704.3195 | 315546.4284 | 55258.3717 | 1753780.4079 | 2273287.2768 | 6849358.0985 | 1830227.6298
| BAN006-72501199 | 167 | BAN006 | BAN | South | 3036192.119 | 0.0010058 | 0.0010309 | 0.0010668 | 0.0010996 | 0.0011307 | 0.0011686 | 0.0012127 | 0.0012513 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.20126 | 0.20248 | 0.2037 | 0.20492 | 0.20614 | 0.20602 | 0.20591 | 0.20579 | 0.20568 | 0.20557 | 0.20545 | 0.20534 | 0.20522 | 0.20511 | 0.205 | 0.20488 | 0.20477 | 0.20465 | 0.20454 | 0.20443 | 0.0056359 | 0.0058114 | 0.0060498 | 0.0062734 | 0.0064887 | 0.0067028 | 0.0069518 | 0.0071691 | 0.0072889 | 0.0072849 | 0.0072809 | 0.0072768 | 0.0072728 | 0.0072688 | 0.0072647 | 0.0072607 | 0.0072566 | 0.0072526 | 0.0072486 | 0.0072445 | 32573.8452 | 5704.3195 | 3213.0482 | 562.6678 | 154985.0153 | 200894.8564 | 3168539.619 | 161740.8062
| BAN006-72501281 | 96 | BAN006 | BAN | South | 1745355.9486 | 0.0010058 | 0.0010309 | 0.0010668 | 0.0010996 | 0.0011307 | 0.0011686 | 0.0012127 | 0.0012513 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.38162 | 0.3846 | 0.38758 | 0.39055 | 0.39353 | 0.39497 | 0.3964 | 0.39783 | 0.39927 | 0.4007 | 0.40214 | 0.40357 | 0.405 | 0.40644 | 0.40787 | 0.4093 | 0.41074 | 0.41217 | 0.41361 | 0.41504 | 0.010686 | 0.011038 | 0.011511 | 0.011956 | 0.012388 | 0.01285 | 0.013383 | 0.013859 | 0.014149 | 0.0142 | 0.014251 | 0.014302 | 0.014353 | 0.014403 | 0.014454 | 0.014505 | 0.014556 | 0.014607 | 0.014657 | 0.014708 | 32573.8452 | 5704.3195 | 6266.2828 | 1097.3491 | 164976.182 | 213845.6182 | 1821435.9486 | 172167.4875
| BAN006-84647249 | 76 | BAN006 | BAN | South | 1381740.126 | 0.0010058 | 0.0010309 | 0.0010668 | 0.0010996 | 0.0011307 | 0.0011686 | 0.0012127 | 0.0012513 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.11931 | 0.12038 | 0.12145 | 0.12253 | 0.1236 | 0.12369 | 0.12377 | 0.12385 | 0.12394 | 0.12402 | 0.1241 | 0.12419 | 0.12427 | 0.12436 | 0.12444 | 0.12452 | 0.12461 | 0.12469 | 0.12478 | 0.12486 | 0.0033409 | 0.0034551 | 0.0036071 | 0.0037511 | 0.0038907 | 0.004024 | 0.0041786 | 0.0043146 | 0.0043921 | 0.0043951 | 0.0043981 | 0.004401 | 0.004404 | 0.004407 | 0.00441 | 0.0044129 | 0.0044159 | 0.0044189 | 0.0044219 | 0.0044248 | 32573.8452 | 5704.3195 | 1936.257 | 339.0766 | 44794.6023 | 58063.7114 | 1441970.126 | 46747.1973
| BAN006-85222599 | 32 | BAN006 | BAN | South | 581785.3162 | 0.0010058 | 0.0010309 | 0.0010668 | 0.0010996 | 0.0011307 | 0.0011686 | 0.0012127 | 0.0012513 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.0012729 | 0.10666 | 0.10764 | 0.10862 | 0.10961 | 0.11059 | 0.11093 | 0.11127 | 0.1116 | 0.11194 | 0.11228 | 0.11262 | 0.11296 | 0.1133 | 0.11364 | 0.11398 | 0.11432 | 0.11466 | 0.115 | 0.11534 | 0.11568 | 0.0029868 | 0.0030895 | 0.0032261 | 0.0033555 | 0.003481 | 0.0036089 | 0.0037565 | 0.0038879 | 0.0039671 | 0.0039791 | 0.0039911 | 0.0040032 | 0.0040152 | 0.0040272 | 0.0040392 | 0.0040513 | 0.0040633 | 0.0040753 | 0.0040873 | 0.0040994 | 32573.8452 | 5704.3195 | 1754.2843 | 307.2096 | 27622.5837 | 35804.9776 | 607145.3162 | 28826.6511
| BAN007-15414603 | 30 | BAN007 | BAN | South | 545423.7339 | 0.0010197 | 0.00010878 | 0.00011191 | 0.00011431 | 0.00011744 | 0.00012058 | 0.00012475 | 0.00012788 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32573.8452 | 5704.3195 | 0 | 0 | 0 | 0 | 569198.7339 | 0
| BAN007-156954231 | 121 | BAN007 | BAN | South | 2199875.7269 | 0.0010197 | 0.00010878 | 0.00011191 | 0.00011431 | 0.00011744 | 0.00012058 | 0.00012475 | 0.00012788 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 8.7836 | 8.8379 | 8.8923 | 8.9466 | 9.001 | 9.0294 | 9.0578 | 9.0862 | 9.1146 | 9.143 | 9.1714 | 9.1998 | 9.2282 | 9.2566 | 9.285 | 9.3134 | 9.3419 | 9.3703 | 9.3987 | 9.4271 | 0.24936 | 0.026765 | 0.027705 | 0.028472 | 0.02943 | 0.03031 | 0.031459 | 0.03235 | 0.033166 | 0.033269 | 0.033373 | 0.033476 | 0.033579 | 0.033683 | 0.033786 | 0.033889 | 0.033993 | 0.034096 | 0.034199 | 0.034303 | 32573.8452 | 5704.3195 | 21927.7619 | 3839.9814 | 1353760.5547 | 1754773.0782 | 2295768.2269 | 1412770.9262
| BAN007-24598874 | 288 | BAN007 | BAN | South | 5236067.8459 | 0.0010197 | 0.00010878 | 0.00011191 | 0.00011431 | 0.00011744 | 0.00012058 | 0.00012475 | 0.00012788 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32573.8452 | 5704.3195 | 0 | 0 | 0 | 0 | 5464307.8459 | 0
| BAN007-24598888 | 18 | BAN007 | BAN | South | 327254.2404 | 0.0010197 | 0.00010878 | 0.00011191 | 0.00011431 | 0.00011744 | 0.00012058 | 0.00012475 | 0.00012788 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 0.0001307 | 1.3454 | 1.3481 | 1.3508 | 1.3536 | 1.3563 | 1.3571 | 1.3579 | 1.3587 | 1.3595 | 1.3603 | 1.3612 | 1.362 | 1.3628 | 1.3636 | 1.3644 | 1.3653 | 1.3661 | 1.3669 | 1.3677 | 1.3685 | 0.038196 | 0.0040827 | 0.0042087 | 0.0043076 | 0.0044345 | 0.0045555 | 0.0047161 | 0.0048374 | 0.004947 | 0.00495 | 0.004953 | 0.0049559 | 0.0049589 | 0.0049619 | 0.0049649 | 0.0049678 | 0.0049708 | 0.0049738 | 0.0049768 | 0.0049797 | 32573.8452 | 5704.3195 | 3297.3277 | 577.4268 | 8617.3156 | 11169.9469 | 341519.2404 | 8992.9441
| BAN008-15414979 | 463 | BAN008 | BAN | South | 8417706.2939 | 0.0011943 | 0.0012362 | 0.0012051 | 1.3519e-05 | 1.3925e-05 | 1.4871e-05 | 1.5276e-05 | 1.5276e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 80.3681 | 80.8096 | 81.2512 | 81.6927 | 82.1342 | 82.3457 | 82.5572 | 82.7687 | 82.9802 | 83.1917 | 83.4032 | 83.6147 | 83.8262 | 84.0377 | 84.2492 | 84.4607 | 84.6722 | 84.8837 | 85.0952 | 85.3067 | 2.6721 | 2.7811 | 2.7259 | 0.030747 | 0.03184 | 0.034092 | 0.035111 | 0.035201 | 0.037477 | 0.037573 | 0.037668 | 0.037764 | 0.037859 | 0.037955 | 0.038051 | 0.038146 | 0.038242 | 0.038337 | 0.038433 | 0.038528 | 32573.8452 | 5704.3195 | 266795.8633 | 46721.1911 | 3100221.2859 | 4018572.4352 | 8784633.7939 | 3235359.8149
| BAN008-193386449 | 304 | BAN008 | BAN | South | 5526960.504 | 0.0011943 | 0.0012362 | 0.0012051 | 1.3519e-05 | 1.3925e-05 | 1.4871e-05 | 1.5276e-05 | 1.5276e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 22.3475 | 22.5221 | 22.6968 | 22.8714 | 23.046 | 23.1748 | 23.3036 | 23.4324 | 23.5613 | 23.6901 | 23.8189 | 23.9477 | 24.0765 | 24.2053 | 24.3342 | 24.463 | 24.5918 | 24.7206 | 24.8494 | 24.9782 | 0.74302 | 0.7751 | 0.76147 | 0.0086081 | 0.008934 | 0.0095945 | 0.009911 | 0.0099657 | 0.010641 | 0.010699 | 0.010758 | 0.010816 | 0.010874 | 0.010932 | 0.01099 | 0.011049 | 0.011107 | 0.011165 | 0.011223 | 0.011281 | 32573.8452 | 5704.3195 | 74453.6667 | 13038.2981 | 707935.9813 | 917641.5998 | 5767880.504 | 738794.8841
| BAN008-193386491 | 345 | BAN008 | BAN | South | 6272372.9404 | 0.0011943 | 0.0012362 | 0.0012051 | 1.3519e-05 | 1.3925e-05 | 1.4871e-05 | 1.5276e-05 | 1.5276e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 235.0751 | 236.1877 | 237.3002 | 238.4127 | 239.5253 | 240.5491 | 241.5729 | 242.5967 | 243.6205 | 244.6442 | 245.668 | 246.6918 | 247.7156 | 248.7394 | 249.7632 | 250.787 | 251.8108 | 252.8346 | 253.8584 | 254.8822 | 7.8159 | 8.1284 | 7.9613 | 0.089731 | 0.092854 | 0.099589 | 0.10274 | 0.10318 | 0.11003 | 0.11049 | 0.11095 | 0.11142 | 0.11188 | 0.11234 | 0.1128 | 0.11327 | 0.11373 | 0.11419 | 0.11465 | 0.11512 | 32573.8452 | 5704.3195 | 780138.5674 | 136617.5721 | 6091234.4423 | 7895586.9819 | 6545785.4404 | 6356751.122
| BAN008-193386514 | 223 | BAN008 | BAN | South | 4054316.4223 | 0.0011943 | 0.0012362 | 0.0012051 | 1.3519e-05 | 1.3925e-05 | 1.4871e-05 | 1.5276e-05 | 1.5276e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 46.2465 | 46.4957 | 46.7449 | 46.994 | 47.2432 | 47.445 | 47.6469 | 47.8488 | 48.0506 | 48.2525 | 48.4543 | 48.6562 | 48.8581 | 49.0599 | 49.2618 | 49.4637 | 49.6655 | 49.8674 | 50.0692 | 50.2711 | 1.5376 | 1.6002 | 1.5683 | 0.017687 | 0.018314 | 0.019643 | 0.020264 | 0.02035 | 0.021702 | 0.021793 | 0.021884 | 0.021975 | 0.022066 | 0.022158 | 0.022249 | 0.02234 | 0.022431 | 0.022522 | 0.022613 | 0.022705 | 32573.8452 | 5704.3195 | 153590.4383 | 26896.6997 | 2617722.8955 | 3393147.8113 | 4231043.9223 | 2731829.3378
| BAN008-193386533 | 184 | BAN008 | BAN | South | 3345265.5682 | 0.0011943 | 0.0012362 | 0.0012051 | 1.3519e-05 | 1.3925e-05 | 1.4871e-05 | 1.5276e-05 | 1.5276e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 1.6223e-05 | 0.78678 | 0.79247 | 0.79817 | 0.80386 | 0.80956 | 0.81357 | 0.81757 | 0.82158 | 0.82559 | 0.82959 | 0.8336 | 0.83761 | 0.84161 | 0.84562 | 0.84963 | 0.85363 | 0.85764 | 0.86165 | 0.86565 | 0.86966 | 0.026159 | 0.027273 | 0.026778 | 0.00030255 | 0.00031383 | 0.00033682 | 0.00034771 | 0.00034942 | 0.00037287 | 0.00037468 | 0.00037649 | 0.0003783 | 0.00038011 | 0.00038192 | 0.00038373 | 0.00038554 | 0.00038735 | 0.00038916 | 0.00039097 | 0.00039277 | 32573.8452 | 5704.3195 | 2619.0048 | 458.6391 | 353539.4427 | 458265.3069 | 3491085.5682 | 368950.2137
| BAN009-15414553 | 446 | BAN009 | BAN | South | 8108632.8446 | 0.0014576 | 0.0014727 | 0.0015017 | 0.0015274 | 0.0015485 | 0.0015836 | 0.0016287 | 0.0016657 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 113.0541 | 113.7627 | 114.4714 | 115.1801 | 115.8888 | 116.2705 | 116.6523 | 117.0341 | 117.4158 | 117.7976 | 118.1793 | 118.5611 | 118.9429 | 119.3246 | 119.7064 | 120.0882 | 120.4699 | 120.8517 | 121.2335 | 121.6152 | 4.5876 | 4.6643 | 4.7858 | 4.8979 | 4.9961 | 5.1261 | 5.2892 | 5.4272 | 5.4998 | 5.5176 | 5.5355 | 5.5534 | 5.5713 | 5.5892 | 5.6071 | 5.6249 | 5.6428 | 5.6607 | 5.6786 | 5.6965 | 32573.8452 | 5704.3195 | 2487233.2043 | 435563.3421 | 4856707.0706 | 6295366.4787 | 8462087.8446 | 5068410.7487
| BAN009-199768607 | 45 | BAN009 | BAN | South | 818135.6009 | 0.0014576 | 0.0014727 | 0.0015017 | 0.0015274 | 0.0015485 | 0.0015836 | 0.0016287 | 0.0016657 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 46.5187 | 46.8357 | 47.1527 | 47.4697 | 47.7867 | 48.1382 | 48.4898 | 48.8413 | 49.1928 | 49.5444 | 49.8959 | 50.2474 | 50.599 | 50.9505 | 51.302 | 51.6536 | 52.0051 | 52.3566 | 52.7082 | 53.0597 | 1.8877 | 1.9203 | 1.9713 | 2.0186 | 2.0601 | 2.1223 | 2.1986 | 2.2649 | 2.3042 | 2.3207 | 2.3371 | 2.3536 | 2.3701 | 2.3865 | 2.403 | 2.4195 | 2.4359 | 2.4524 | 2.4689 | 2.4853 | 32573.8452 | 5704.3195 | 1046765.3572 | 183309.1552 | 243143.021 | 315167.1291 | 853798.1009 | 253741.6161
| BAN009-201078585 | 884 | BAN009 | BAN | South | 16071819.3602 | 0.0014576 | 0.0014727 | 0.0015017 | 0.0015274 | 0.0015485 | 0.0015836 | 0.0016287 | 0.0016657 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 23.8434 | 24.0302 | 24.2169 | 24.4037 | 24.5905 | 24.6961 | 24.8017 | 24.9074 | 25.013 | 25.1187 | 25.2243 | 25.3299 | 25.4356 | 25.5412 | 25.6468 | 25.7525 | 25.8581 | 25.9638 | 26.0694 | 26.175 | 0.96753 | 0.98525 | 1.0125 | 1.0377 | 1.0601 | 1.0888 | 1.1246 | 1.155 | 1.1716 | 1.1766 | 1.1815 | 1.1865 | 1.1914 | 1.1964 | 1.2013 | 1.2062 | 1.2112 | 1.2161 | 1.2211 | 1.226 | 32573.8452 | 5704.3195 | 530027.8726 | 92818.2815 | 5941169.8891 | 7701070.1325 | 16772389.3602 | 6200145.2606
| BAN009-77240394 | 436 | BAN009 | BAN | South | 7926824.9333 | 0.0014576 | 0.0014727 | 0.0015017 | 0.0015274 | 0.0015485 | 0.0015836 | 0.0016287 | 0.0016657 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 1.8133 | 1.8242 | 1.8351 | 1.846 | 1.8569 | 1.8667 | 1.8765 | 1.8864 | 1.8962 | 1.906 | 1.9158 | 1.9256 | 1.9354 | 1.9452 | 1.9551 | 1.9649 | 1.9747 | 1.9845 | 1.9943 | 2.0041 | 0.073581 | 0.074793 | 0.076721 | 0.078499 | 0.080054 | 0.0823 | 0.085086 | 0.087475 | 0.088817 | 0.089277 | 0.089736 | 0.090196 | 0.090656 | 0.091116 | 0.091575 | 0.092035 | 0.092495 | 0.092954 | 0.093414 | 0.093874 | 32573.8452 | 5704.3195 | 40268.3137 | 7051.7719 | 4441967.7692 | 5757772.6198 | 8272354.9333 | 4635592.9768
| BAN009-77240588 | 124 | BAN009 | BAN | South | 2254418.1003 | 0.0014576 | 0.0014727 | 0.0015017 | 0.0015274 | 0.0015485 | 0.0015836 | 0.0016287 | 0.0016657 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.23784 | 0.23971 | 0.24159 | 0.24346 | 0.24534 | 0.24691 | 0.24849 | 0.25006 | 0.25164 | 0.25321 | 0.25479 | 0.25636 | 0.25793 | 0.25951 | 0.26108 | 0.26266 | 0.26423 | 0.26581 | 0.26738 | 0.26896 | 0.0096511 | 0.0098283 | 0.0101 | 0.010353 | 0.010577 | 0.010886 | 0.011267 | 0.011596 | 0.011787 | 0.01186 | 0.011934 | 0.012008 | 0.012082 | 0.012155 | 0.012229 | 0.012303 | 0.012377 | 0.01245 | 0.012524 | 0.012598 | 32573.8452 | 5704.3195 | 5345.4958 | 936.1012 | 200360.3981 | 259711.3879 | 2352688.1003 | 209094.1003
| BAN009-78742110 | 58 | BAN009 | BAN | South | 1054485.8856 | 0.0014576 | 0.0014727 | 0.0015017 | 0.0015274 | 0.0015485 | 0.0015836 | 0.0016287 | 0.0016657 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.063224 | 0.063798 | 0.064373 | 0.064948 | 0.065522 | 0.065702 | 0.065881 | 0.066061 | 0.06624 | 0.06642 | 0.066599 | 0.066779 | 0.066958 | 0.067138 | 0.067317 | 0.067497 | 0.067676 | 0.067856 | 0.068035 | 0.068215 | 0.0025655 | 0.0026158 | 0.0026913 | 0.0027618 | 0.0028248 | 0.0028967 | 0.0029872 | 0.0030634 | 0.0031027 | 0.0031111 | 0.0031195 | 0.0031279 | 0.0031363 | 0.0031447 | 0.0031531 | 0.0031615 | 0.00317 | 0.0031784 | 0.0031868 | 0.0031952 | 32573.8452 | 5704.3195 | 1400.0201 | 245.171 | 52999.5306 | 68699.1131 | 1100450.8856 | 55309.7781
| BAN009-78742394 | 104 | BAN009 | BAN | South | 1890802.2777 | 0.0014576 | 0.0014727 | 0.0015017 | 0.0015274 | 0.0015485 | 0.0015836 | 0.0016287 | 0.0016657 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.0016825 | 0.021284 | 0.021491 | 0.021697 | 0.021904 | 0.022111 | 0.022307 | 0.022503 | 0.0227 | 0.022896 | 0.023092 | 0.023288 | 0.023485 | 0.023681 | 0.023877 | 0.024074 | 0.02427 | 0.024466 | 0.024662 | 0.024859 | 0.025055 | 0.00086367 | 0.00088113 | 0.00090711 | 0.00093144 | 0.00095322 | 0.00098347 | 0.0010203 | 0.0010526 | 0.0010724 | 0.0010816 | 0.0010908 | 0.0011 | 0.0011092 | 0.0011184 | 0.0011276 | 0.0011368 | 0.001146 | 0.0011552 | 0.0011644 | 0.0011736 | 32573.8452 | 5704.3195 | 487.2912 | 85.3342 | 17436.8061 | 22601.9571 | 1973222.2777 | 18196.8758
| BAN011-15414529 | 89 | BAN011 | BAN | South | 1618090.4107 | 0.011912 | 0.012217 | 0.012485 | 0.012666 | 0.01263 | 0.012684 | 0.013005 | 0.013402 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 7.7984 | 7.835 | 7.8715 | 7.9081 | 7.9447 | 7.9465 | 7.9483 | 7.9501 | 7.9518 | 7.9536 | 7.9554 | 7.9572 | 7.959 | 7.9607 | 7.9625 | 7.9643 | 7.9661 | 7.9678 | 7.9696 | 7.9714 | 2.5861 | 2.6647 | 2.736 | 2.7885 | 2.7935 | 2.806 | 2.8778 | 2.9663 | 2.9497 | 2.9504 | 2.9511 | 2.9517 | 2.9524 | 2.953 | 2.9537 | 2.9544 | 2.955 | 2.9557 | 2.9563 | 2.957 | 32573.8452 | 5704.3195 | 1348906.7539 | 236220.0428 | 330696.3846 | 428655.6517 | 1688622.9107 | 345111.4276
| BAN011-171348706 | 1 | BAN011 | BAN | South | 18180.7911 | 0.011912 | 0.012217 | 0.012485 | 0.012666 | 0.01263 | 0.012684 | 0.013005 | 0.013402 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0.013324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32573.8452 | 5704.3195 | 0 | 0 | 0 | 0 | 18973.2911 | 0
| BAN013-15414453 | 394 | BAN013 | BAN | South | 7163231.7058 | 0.0021419 | 0.0022147 | 0.0023078 | 0.0024028 | 0.0024944 | 0.0026048 | 0.0027329 | 0.0028437 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0.0029364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32573.8452 | 5704.3195 | 0 | 0 | 0 | 0 | 7475476.7058 | 0
| BAN015-15414416 | 194 | BAN015 | BAN | South | 3527073.4795 | 0.0009303 | 0.0009614 | 0.00095196 | 0.00073831 | 0.00077062 | 0.0008094 | 0.00085069 | 0.00088614 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32573.8452 | 5704.3195 | 0 | 0 | 0 | 0 | 3680818.4795 | 0
| BAN015-24611936 | 392 | BAN015 | BAN | South | 7126870.1235 | 0.0009303 | 0.0009614 | 0.00095196 | 0.00073831 | 0.00077062 | 0.0008094 | 0.00085069 | 0.00088614 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 0.00091271 | 75.7295 | 76.0765 | 76.4234 | 76.7704 | 77.1173 | 77.3713 | 77.6253 | 77.8793 | 78.1333 | 78.3873 | 78.6413 | 78.8953 | 79.1492 | 79.4032 | 79.6572 | 79.9112 | 80.1652 | 80.4192 | 80.6732 | 80.9272 | 1.9614 | 2.0362 | 2.0254 | 1.578 | 1.6545 | 1.7435 | 1.8384 | 1.9213 | 1.9854 | 1.9918 | 1.9983 | 2.0047 | 2.0112 | 2.0176 | 2.0241 | 2.0305 | 2.037 | 2.0434 | 2.0499 | 2.0563 | 32573.8452 | 5704.3195 | 912107.705 | 159727.9578 | 2644347.86 | 3427659.6537 | 7437530.1235 | 2759614.8835
| BAS011-111131839 | 6 | BAS011 | BAS | South | 109084.7468 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.007553 | 0.00761 | 0.007667 | 0.0077239 | 0.0077809 | 0.00782 | 0.0078591 | 0.0078982 | 0.0079373 | 0.0079764 | 0.0080155 | 0.0080546 | 0.0080937 | 0.0081328 | 0.0081719 | 0.008211 | 0.0082501 | 0.0082892 | 0.0083283 | 0.0083674 | 0.0002207 | 0.00013405 | 0.00013753 | 0.00014175 | 0.00014549 | 0.00015033 | 0.00015651 | 0.00016251 | 0.00016628 | 0.0001671 | 0.00016792 | 0.00016874 | 0.00016956 | 0.00017038 | 0.0001712 | 0.00017201 | 0.00017283 | 0.00017365 | 0.00017447 | 0.00017529 | 32877.5686 | 7348.3186 | 77.867 | 17.4037 | 32.0285 | 41.516 | 113839.7468 | 33.4246
| BAS011-134530801 | 23 | BAS011 | BAS | South | 418158.196 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.10131 | 0.1018 | 0.10228 | 0.10277 | 0.10326 | 0.10347 | 0.10367 | 0.10388 | 0.10409 | 0.1043 | 0.10451 | 0.10472 | 0.10493 | 0.10514 | 0.10535 | 0.10555 | 0.10576 | 0.10597 | 0.10618 | 0.10639 | 0.0029602 | 0.0017931 | 0.0018348 | 0.001886 | 0.0019307 | 0.0019889 | 0.0020646 | 0.0021374 | 0.0021807 | 0.002185 | 0.0021894 | 0.0021938 | 0.0021982 | 0.0022025 | 0.0022069 | 0.0022113 | 0.0022157 | 0.00222 | 0.0022244 | 0.0022288 | 32877.5686 | 7348.3186 | 1019.7639 | 227.9229 | 24181.1667 | 31344.14 | 436385.696 | 25235.2228
| BAS011-140236715 | 92 | BAS011 | BAS | South | 1672632.7841 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.037571 | 0.037768 | 0.037965 | 0.038162 | 0.038359 | 0.038243 | 0.038128 | 0.038012 | 0.037897 | 0.037781 | 0.037666 | 0.03755 | 0.037435 | 0.037319 | 0.037204 | 0.037088 | 0.036973 | 0.036857 | 0.036742 | 0.036626 | 0.0010978 | 0.00066528 | 0.00068103 | 0.00070035 | 0.00071726 | 0.00073516 | 0.00075928 | 0.0007821 | 0.00079391 | 0.00079149 | 0.00078907 | 0.00078665 | 0.00078424 | 0.00078182 | 0.0007794 | 0.00077698 | 0.00077456 | 0.00077214 | 0.00076972 | 0.0007673 | 32877.5686 | 7348.3186 | 369.0877 | 82.4931 | 22763.3226 | 29506.3005 | 1745542.7841 | 23755.575
| BAS011-140237055 | 86 | BAS011 | BAS | South | 1563548.0373 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.022156 | 0.022333 | 0.022511 | 0.022688 | 0.022865 | 0.022794 | 0.022722 | 0.02265 | 0.022579 | 0.022507 | 0.022435 | 0.022363 | 0.022292 | 0.02222 | 0.022148 | 0.022076 | 0.022005 | 0.021933 | 0.021861 | 0.021789 | 0.00064739 | 0.0003934 | 0.00040381 | 0.00041637 | 0.00042755 | 0.00043817 | 0.00045249 | 0.00046603 | 0.00047301 | 0.0004715 | 0.00047 | 0.0004685 | 0.00046699 | 0.00046549 | 0.00046399 | 0.00046249 | 0.00046098 | 0.00045948 | 0.00045798 | 0.00045648 | 32877.5686 | 7348.3186 | 219.4445 | 49.0471 | 15337.7883 | 19881.1657 | 1631703.0373 | 16006.3619
| BAS011-15414096 | 1 | BAS011 | BAS | South | 18180.7911 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32877.5686 | 7348.3186 | 0 | 0 | 0 | 0 | 18973.2911 | 0
| BAS011-15414109 | 450 | BAS011 | BAS | South | 8181356.0092 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 61.1409 | 61.4579 | 61.7749 | 62.0918 | 62.4088 | 62.5276 | 62.6464 | 62.7651 | 62.8839 | 63.0027 | 63.1215 | 63.2403 | 63.359 | 63.4778 | 63.5966 | 63.7154 | 63.8342 | 63.9529 | 64.0717 | 64.1905 | 1.7865 | 1.0826 | 1.1081 | 1.1395 | 1.167 | 1.202 | 1.2475 | 1.2914 | 1.3174 | 1.3199 | 1.3224 | 1.3248 | 1.3273 | 1.3298 | 1.3323 | 1.3348 | 1.3373 | 1.3398 | 1.3423 | 1.3447 | 32877.5686 | 7348.3186 | 615819.6404 | 137639.0999 | 1321702.2356 | 1713218.4065 | 8537981.0092 | 1379315.1862
| BAS011-158128939 | 316 | BAS011 | BAS | South | 5745129.9975 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.08157 | 0.082247 | 0.082925 | 0.083602 | 0.08428 | 0.084501 | 0.084723 | 0.084944 | 0.085166 | 0.085387 | 0.085608 | 0.08583 | 0.086051 | 0.086273 | 0.086494 | 0.086716 | 0.086937 | 0.087158 | 0.08738 | 0.087601 | 0.0023834 | 0.0014488 | 0.0014875 | 0.0015343 | 0.0015759 | 0.0016244 | 0.0016872 | 0.0017477 | 0.0017842 | 0.0017888 | 0.0017934 | 0.0017981 | 0.0018027 | 0.0018074 | 0.001812 | 0.0018166 | 0.0018213 | 0.0018259 | 0.0018305 | 0.0018352 | 32877.5686 | 7348.3186 | 832.9195 | 186.1621 | 542800.954 | 703590.0828 | 5995559.9975 | 566461.6271
| BAS011-158493706 | 42 | BAS011 | BAS | South | 763593.2275 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.013058 | 0.013152 | 0.013247 | 0.013341 | 0.013436 | 0.013501 | 0.013566 | 0.013632 | 0.013697 | 0.013763 | 0.013828 | 0.013894 | 0.013959 | 0.014025 | 0.01409 | 0.014156 | 0.014221 | 0.014286 | 0.014352 | 0.014417 | 0.00038155 | 0.00023168 | 0.00023763 | 0.00024484 | 0.00025123 | 0.00025953 | 0.00027016 | 0.00028048 | 0.00028695 | 0.00028832 | 0.00028969 | 0.00029106 | 0.00029244 | 0.00029381 | 0.00029518 | 0.00029655 | 0.00029792 | 0.00029929 | 0.00030066 | 0.00030203 | 32877.5686 | 7348.3186 | 134.3809 | 30.0349 | 10085.5672 | 13073.1256 | 796878.2275 | 10525.1967
| BAS011-158493822 | 27 | BAS011 | BAS | South | 490881.3605 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 1.9702e-05 | 1.9952e-05 | 2.0201e-05 | 2.0451e-05 | 2.07e-05 | 2.0691e-05 | 2.0682e-05 | 2.0673e-05 | 2.0664e-05 | 2.0655e-05 | 2.0646e-05 | 2.0637e-05 | 2.0628e-05 | 2.0619e-05 | 2.061e-05 | 2.0601e-05 | 2.0592e-05 | 2.0583e-05 | 2.0574e-05 | 2.0565e-05 | 5.7569e-07 | 3.5145e-07 | 3.6238e-07 | 3.7531e-07 | 3.8706e-07 | 3.9775e-07 | 4.1186e-07 | 4.2535e-07 | 4.329e-07 | 4.3271e-07 | 4.3252e-07 | 4.3233e-07 | 4.3214e-07 | 4.3195e-07 | 4.3177e-07 | 4.3158e-07 | 4.3139e-07 | 4.312e-07 | 4.3101e-07 | 4.3082e-07 | 32877.5686 | 7348.3186 | 0.20083 | 0.044886 | 16.1597 | 20.9465 | 512278.8605 | 16.8641
| BAS011-163842929 | 8 | BAS011 | BAS | South | 145446.3291 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.035168 | 0.035393 | 0.035619 | 0.035844 | 0.03607 | 0.036209 | 0.036348 | 0.036488 | 0.036627 | 0.036766 | 0.036906 | 0.037045 | 0.037184 | 0.037324 | 0.037463 | 0.037602 | 0.037742 | 0.037881 | 0.03802 | 0.03816 | 0.0010276 | 0.00062345 | 0.00063894 | 0.00065782 | 0.00067446 | 0.00069606 | 0.00072385 | 0.00075074 | 0.00076731 | 0.00077023 | 0.00077315 | 0.00077607 | 0.00077899 | 0.00078191 | 0.00078482 | 0.00078774 | 0.00079066 | 0.00079358 | 0.0007965 | 0.00079942 | 32877.5686 | 7348.3186 | 359.1465 | 80.2712 | 6417.898 | 8319.0152 | 151786.3291 | 6697.6539
| BAS011-163930345 | 45 | BAS011 | BAS | South | 818135.6009 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.0033179 | 0.0033442 | 0.0033704 | 0.0033967 | 0.0034229 | 0.0034112 | 0.0033994 | 0.0033876 | 0.0033758 | 0.003364 | 0.0033522 | 0.0033405 | 0.0033287 | 0.0033169 | 0.0033051 | 0.0032933 | 0.0032815 | 0.0032697 | 0.003258 | 0.0032462 | 9.6947e-05 | 5.8907e-05 | 6.046e-05 | 6.2336e-05 | 6.4004e-05 | 6.5573e-05 | 6.7695e-05 | 6.97e-05 | 7.0721e-05 | 7.0474e-05 | 7.0227e-05 | 6.998e-05 | 6.9733e-05 | 6.9486e-05 | 6.924e-05 | 6.8993e-05 | 6.8746e-05 | 6.8499e-05 | 6.8252e-05 | 6.8005e-05 | 32877.5686 | 7348.3186 | 32.8005 | 7.3311 | 2639.1398 | 3420.9088 | 853798.1009 | 2754.1798
| BAS011-163930441 | 28 | BAS011 | BAS | South | 509062.1517 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 8.9358e-06 | 9.0418e-06 | 9.1479e-06 | 9.2539e-06 | 9.36e-06 | 9.324e-06 | 9.288e-06 | 9.252e-06 | 9.216e-06 | 9.18e-06 | 9.144e-06 | 9.108e-06 | 9.072e-06 | 9.036e-06 | 9e-06 | 8.964e-06 | 8.928e-06 | 8.892e-06 | 8.856e-06 | 8.82e-06 | 2.611e-07 | 1.5927e-07 | 1.641e-07 | 1.6983e-07 | 1.7502e-07 | 1.7924e-07 | 1.8496e-07 | 1.9036e-07 | 1.9307e-07 | 1.9231e-07 | 1.9156e-07 | 1.9081e-07 | 1.9005e-07 | 1.893e-07 | 1.8854e-07 | 1.8779e-07 | 1.8704e-07 | 1.8628e-07 | 1.8553e-07 | 1.8477e-07 | 32877.5686 | 7348.3186 | 0.089263 | 0.019951 | 8.3813 | 10.8641 | 531252.1517 | 8.7467
| BAS011-164206932 | 334 | BAS011 | BAS | South | 6072384.2379 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 8.095 | 8.1513 | 8.2076 | 8.264 | 8.3203 | 8.3452 | 8.37 | 8.3949 | 8.4198 | 8.4447 | 8.4695 | 8.4944 | 8.5193 | 8.5442 | 8.569 | 8.5939 | 8.6188 | 8.6437 | 8.6685 | 8.6934 | 0.23653 | 0.14358 | 0.14723 | 0.15166 | 0.15558 | 0.16042 | 0.16668 | 0.17272 | 0.17639 | 0.17691 | 0.17743 | 0.17795 | 0.17847 | 0.17899 | 0.17952 | 0.18004 | 0.18056 | 0.18108 | 0.1816 | 0.18212 | 32877.5686 | 7348.3186 | 82452.3147 | 18428.5489 | 432456.0887 | 560558.7335 | 6337079.2379 | 451306.8333
| BAS011-164206954 | 465 | BAS011 | BAS | South | 8454067.8761 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 23.2991 | 23.4765 | 23.654 | 23.8315 | 24.009 | 24.0612 | 24.1135 | 24.1657 | 24.218 | 24.2702 | 24.3225 | 24.3747 | 24.427 | 24.4792 | 24.5315 | 24.5837 | 24.636 | 24.6883 | 24.7405 | 24.7928 | 0.68079 | 0.41354 | 0.42432 | 0.43736 | 0.44893 | 0.46253 | 0.4802 | 0.49721 | 0.50735 | 0.50844 | 0.50954 | 0.51063 | 0.51173 | 0.51282 | 0.51392 | 0.51501 | 0.51611 | 0.5172 | 0.5183 | 0.51939 | 32877.5686 | 7348.3186 | 236844.6874 | 52936.0992 | 2367432.1274 | 3068715.6212 | 8822580.3761 | 2470628.4046
| BAS011-164206976 | 536 | BAS011 | BAS | South | 9744904.0465 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 15.7714 | 15.8763 | 15.9811 | 16.086 | 16.1909 | 16.2107 | 16.2305 | 16.2504 | 16.2702 | 16.29 | 16.3099 | 16.3297 | 16.3496 | 16.3694 | 16.3892 | 16.4091 | 16.4289 | 16.4487 | 16.4686 | 16.4884 | 0.46083 | 0.27966 | 0.28668 | 0.29521 | 0.30275 | 0.31162 | 0.32322 | 0.33435 | 0.34085 | 0.34127 | 0.34168 | 0.3421 | 0.34251 | 0.34293 | 0.34334 | 0.34376 | 0.34417 | 0.34459 | 0.34501 | 0.34542 | 32877.5686 | 7348.3186 | 159056.4422 | 35549.9957 | 5319849.7881 | 6895701.8697 | 10169684.0465 | 5551741.8398
| BAS011-164287379 | 4 | BAS011 | BAS | South | 72723.1645 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.40582 | 0.40946 | 0.41309 | 0.41673 | 0.42037 | 0.42164 | 0.42292 | 0.4242 | 0.42547 | 0.42675 | 0.42803 | 0.42931 | 0.43058 | 0.43186 | 0.43314 | 0.43441 | 0.43569 | 0.43697 | 0.43824 | 0.43952 | 0.011858 | 0.0072125 | 0.0074102 | 0.0076479 | 0.0078603 | 0.0081053 | 0.0084221 | 0.0087279 | 0.0089134 | 0.0089402 | 0.0089669 | 0.0089937 | 0.0090204 | 0.0090471 | 0.0090739 | 0.0091006 | 0.0091274 | 0.0091541 | 0.0091809 | 0.0092076 | 32877.5686 | 7348.3186 | 4161.1853 | 930.048 | 420.0578 | 544.4878 | 75893.1645 | 438.3681
| BAS011-172348924 | 40 | BAS011 | BAS | South | 727231.6453 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.48513 | 0.48758 | 0.49002 | 0.49247 | 0.49491 | 0.49547 | 0.49603 | 0.49659 | 0.49715 | 0.49771 | 0.49827 | 0.49883 | 0.49939 | 0.49995 | 0.50051 | 0.50107 | 0.50162 | 0.50218 | 0.50274 | 0.5033 | 0.014175 | 0.0085886 | 0.0087902 | 0.0090378 | 0.0092542 | 0.0095245 | 0.009878 | 0.010217 | 0.010415 | 0.010427 | 0.010438 | 0.01045 | 0.010462 | 0.010474 | 0.010485 | 0.010497 | 0.010509 | 0.01052 | 0.010532 | 0.010544 | 32877.5686 | 7348.3186 | 4864.9465 | 1087.3425 | 76715.5111 | 99440.2689 | 758931.6453 | 80059.5373
| BAS011-182896771 | 100 | BAS011 | BAS | South | 1818079.1131 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.0077573 | 0.0078274 | 0.0078974 | 0.0079675 | 0.0080376 | 0.0080399 | 0.0080422 | 0.0080445 | 0.0080467 | 0.008049 | 0.0080513 | 0.0080536 | 0.0080559 | 0.0080581 | 0.0080604 | 0.0080627 | 0.008065 | 0.0080673 | 0.0080695 | 0.0080718 | 0.00022666 | 0.00013788 | 0.00014167 | 0.00014622 | 0.00015029 | 0.00015455 | 0.00016015 | 0.00016551 | 0.00016857 | 0.00016862 | 0.00016867 | 0.00016872 | 0.00016876 | 0.00016881 | 0.00016886 | 0.00016891 | 0.00016896 | 0.000169 | 0.00016905 | 0.0001691 | 32877.5686 | 7348.3186 | 78.4557 | 17.5353 | 11297.622 | 14644.2167 | 1897329.1131 | 11790.0849
| BAS011-24598608 | 421 | BAS011 | BAS | South | 7654113.0663 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 4.0788 | 4.1036 | 4.1284 | 4.1533 | 4.1781 | 4.1885 | 4.1988 | 4.2091 | 4.2195 | 4.2298 | 4.2401 | 4.2505 | 4.2608 | 4.2711 | 4.2815 | 4.2918 | 4.3021 | 4.3125 | 4.3228 | 4.3331 | 0.11918 | 0.072284 | 0.074058 | 0.076221 | 0.078125 | 0.080516 | 0.083615 | 0.086603 | 0.088395 | 0.088611 | 0.088828 | 0.089044 | 0.089261 | 0.089477 | 0.089694 | 0.08991 | 0.090127 | 0.090343 | 0.09056 | 0.090776 | 32877.5686 | 7348.3186 | 41321.0354 | 9235.4802 | 918400.5736 | 1190450.258 | 7987755.5663 | 958433.62
| BAS011-24602396 | 29 | BAS011 | BAS | South | 527242.9428 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.07593 | 0.07614 | 0.076351 | 0.076562 | 0.076772 | 0.076722 | 0.076671 | 0.076621 | 0.07657 | 0.07652 | 0.076469 | 0.076418 | 0.076368 | 0.076317 | 0.076267 | 0.076216 | 0.076166 | 0.076115 | 0.076065 | 0.076014 | 0.0022186 | 0.0013412 | 0.0013696 | 0.0014051 | 0.0014355 | 0.0014748 | 0.0015268 | 0.0015765 | 0.0016041 | 0.001603 | 0.001602 | 0.0016009 | 0.0015999 | 0.0015988 | 0.0015977 | 0.0015967 | 0.0015956 | 0.0015946 | 0.0015935 | 0.0015924 | 32877.5686 | 7348.3186 | 749.0034 | 167.4064 | 9847.9117 | 12765.0715 | 550225.4428 | 10277.1818
| BAS011-24608723 | 73 | BAS011 | BAS | South | 1327197.7526 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.01372 | 0.013804 | 0.013888 | 0.013973 | 0.014057 | 0.014121 | 0.014185 | 0.014249 | 0.014313 | 0.014377 | 0.014441 | 0.014505 | 0.014569 | 0.014633 | 0.014697 | 0.014761 | 0.014825 | 0.014889 | 0.014953 | 0.015017 | 0.00040088 | 0.00024316 | 0.00024914 | 0.00025643 | 0.00026285 | 0.00027145 | 0.00028249 | 0.00029318 | 0.00029985 | 0.00030119 | 0.00030253 | 0.00030387 | 0.00030521 | 0.00030655 | 0.00030789 | 0.00030923 | 0.00031057 | 0.00031191 | 0.00031325 | 0.00031459 | 32877.5686 | 7348.3186 | 140.4754 | 31.397 | 7428.6271 | 9629.1436 | 1385050.2526 | 7752.4407
| BAS011-76148984 | 79 | BAS011 | BAS | South | 1436282.4994 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.0042882 | 0.0043198 | 0.0043513 | 0.0043829 | 0.0044144 | 0.0044175 | 0.0044206 | 0.0044236 | 0.0044267 | 0.0044297 | 0.0044328 | 0.0044359 | 0.0044389 | 0.004442 | 0.004445 | 0.0044481 | 0.0044512 | 0.0044542 | 0.0044573 | 0.0044603 | 0.0001253 | 7.6092e-05 | 7.8056e-05 | 8.0435e-05 | 8.2544e-05 | 8.4918e-05 | 8.8031e-05 | 9.1016e-05 | 9.2736e-05 | 9.28e-05 | 9.2864e-05 | 9.2928e-05 | 9.2992e-05 | 9.3056e-05 | 9.3121e-05 | 9.3185e-05 | 9.3249e-05 | 9.3313e-05 | 9.3377e-05 | 9.3441e-05 | 32877.5686 | 7348.3186 | 43.2287 | 9.6619 | 3981.0396 | 5160.3078 | 1498889.9994 | 4154.573
| BAS011-76149624 | 50 | BAS011 | BAS | South | 909039.5566 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.016055 | 0.016166 | 0.016278 | 0.016389 | 0.0165 | 0.016512 | 0.016524 | 0.016536 | 0.016548 | 0.01656 | 0.016572 | 0.016584 | 0.016596 | 0.016608 | 0.01662 | 0.016632 | 0.016644 | 0.016656 | 0.016667 | 0.016679 | 0.00046912 | 0.00028477 | 0.00029199 | 0.00030077 | 0.00030853 | 0.00031742 | 0.00032906 | 0.00034023 | 0.00034667 | 0.00034692 | 0.00034717 | 0.00034742 | 0.00034767 | 0.00034792 | 0.00034817 | 0.00034842 | 0.00034867 | 0.00034892 | 0.00034917 | 0.00034942 | 32877.5686 | 7348.3186 | 161.6513 | 36.13 | 12038.9935 | 15605.1982 | 948664.5566 | 12563.7728
| BAS011-76150176 | 138 | BAS011 | BAS | South | 2508949.1761 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.064196 | 0.064744 | 0.065291 | 0.065838 | 0.066386 | 0.066433 | 0.06648 | 0.066527 | 0.066575 | 0.066622 | 0.066669 | 0.066716 | 0.066764 | 0.066811 | 0.066858 | 0.066905 | 0.066953 | 0.067 | 0.067047 | 0.067095 | 0.0018758 | 0.0011405 | 0.0011712 | 0.0012083 | 0.0012413 | 0.0012771 | 0.0013239 | 0.0013688 | 0.0013947 | 0.0013957 | 0.0013967 | 0.0013977 | 0.0013987 | 0.0013996 | 0.0014006 | 0.0014016 | 0.0014026 | 0.0014036 | 0.0014046 | 0.0014056 | 32877.5686 | 7348.3186 | 649.6346 | 145.1969 | 60095.5123 | 77897.0747 | 2618314.1761 | 62715.0734
| BAS011-76150520 | 61 | BAS011 | BAS | South | 1109028.259 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.083564 | 0.084202 | 0.08484 | 0.085478 | 0.086116 | 0.086096 | 0.086077 | 0.086057 | 0.086037 | 0.086017 | 0.085997 | 0.085977 | 0.085958 | 0.085938 | 0.085918 | 0.085898 | 0.085878 | 0.085858 | 0.085839 | 0.085819 | 0.0024417 | 0.0014832 | 0.0015219 | 0.0015687 | 0.0016103 | 0.001655 | 0.0017141 | 0.0017706 | 0.0018024 | 0.001802 | 0.0018016 | 0.0018012 | 0.0018008 | 0.0018003 | 0.0017999 | 0.0017995 | 0.0017991 | 0.0017987 | 0.0017983 | 0.0017978 | 32877.5686 | 7348.3186 | 839.174 | 187.56 | 52791.8825 | 68429.9553 | 1157370.759 | 55093.0787
| BAS011-76150666 | 47 | BAS011 | BAS | South | 854497.1832 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.15309 | 0.15429 | 0.15549 | 0.15669 | 0.15789 | 0.15815 | 0.15841 | 0.15868 | 0.15894 | 0.1592 | 0.15946 | 0.15972 | 0.15999 | 0.16025 | 0.16051 | 0.16077 | 0.16104 | 0.1613 | 0.16156 | 0.16182 | 0.0044732 | 0.0027178 | 0.0027892 | 0.0028756 | 0.0029523 | 0.0030402 | 0.0031546 | 0.0032647 | 0.0033296 | 0.0033351 | 0.0033406 | 0.0033461 | 0.0033516 | 0.0033571 | 0.0033626 | 0.0033681 | 0.0033736 | 0.0033791 | 0.0033846 | 0.0033901 | 32877.5686 | 7348.3186 | 1553.2603 | 347.1623 | 85098.8486 | 110306.9283 | 891744.6832 | 88808.3042
| BAS011-79244341 | 58 | BAS011 | BAS | South | 1054485.8856 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.021814 | 0.021971 | 0.022127 | 0.022284 | 0.02244 | 0.022561 | 0.022682 | 0.022803 | 0.022924 | 0.023044 | 0.023165 | 0.023286 | 0.023407 | 0.023528 | 0.023648 | 0.023769 | 0.02389 | 0.024011 | 0.024132 | 0.024252 | 0.00063739 | 0.00038701 | 0.00039693 | 0.00040895 | 0.00041961 | 0.0004337 | 0.00045169 | 0.00046917 | 0.00048023 | 0.00048277 | 0.0004853 | 0.00048783 | 0.00049036 | 0.00049289 | 0.00049542 | 0.00049795 | 0.00050048 | 0.00050301 | 0.00050554 | 0.00050807 | 32877.5686 | 7348.3186 | 225.0264 | 50.2946 | 12956.488 | 16794.474 | 1100450.8856 | 13521.2609
| BAS011-79244394 | 48 | BAS011 | BAS | South | 872677.9743 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.064481 | 0.064996 | 0.065511 | 0.066025 | 0.06654 | 0.066734 | 0.066927 | 0.067121 | 0.067315 | 0.067508 | 0.067702 | 0.067895 | 0.068089 | 0.068283 | 0.068476 | 0.06867 | 0.068864 | 0.069057 | 0.069251 | 0.069445 | 0.0018841 | 0.0011449 | 0.0011752 | 0.0012117 | 0.0012442 | 0.0012828 | 0.0013328 | 0.001381 | 0.0014102 | 0.0014143 | 0.0014183 | 0.0014224 | 0.0014264 | 0.0014305 | 0.0014345 | 0.0014386 | 0.0014426 | 0.0014467 | 0.0014508 | 0.0014548 | 32877.5686 | 7348.3186 | 658.6812 | 147.2189 | 47089.2598 | 61038.095 | 910717.9743 | 49141.8788
| BAS011-79244446 | 57 | BAS011 | BAS | South | 1036305.0945 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.88669 | 0.89263 | 0.89858 | 0.90452 | 0.91047 | 0.91161 | 0.91275 | 0.91389 | 0.91503 | 0.91617 | 0.91731 | 0.91845 | 0.91958 | 0.92072 | 0.92186 | 0.923 | 0.92414 | 0.92528 | 0.92642 | 0.92756 | 0.025909 | 0.015724 | 0.016119 | 0.0166 | 0.017025 | 0.017524 | 0.018177 | 0.018803 | 0.019169 | 0.019193 | 0.019217 | 0.019241 | 0.019265 | 0.019289 | 0.019312 | 0.019336 | 0.01936 | 0.019384 | 0.019408 | 0.019432 | 32877.5686 | 7348.3186 | 8945.1518 | 1999.291 | 262876.6486 | 340746.2747 | 1081477.5945 | 274335.4318
| BAS011-79244508 | 26 | BAS011 | BAS | South | 472700.5694 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.0013723 | 0.0013835 | 0.0013948 | 0.001406 | 0.0014172 | 0.0014214 | 0.0014255 | 0.0014296 | 0.0014337 | 0.0014378 | 0.0014419 | 0.001446 | 0.0014501 | 0.0014542 | 0.0014583 | 0.0014624 | 0.0014665 | 0.0014706 | 0.0014747 | 0.0014788 | 4.0097e-05 | 2.437e-05 | 2.502e-05 | 2.5803e-05 | 2.6501e-05 | 2.7323e-05 | 2.8387e-05 | 2.9413e-05 | 3.0034e-05 | 3.012e-05 | 3.0206e-05 | 3.0292e-05 | 3.0378e-05 | 3.0464e-05 | 3.055e-05 | 3.0636e-05 | 3.0722e-05 | 3.0808e-05 | 3.0894e-05 | 3.0979e-05 | 32877.5686 | 7348.3186 | 14.0263 | 3.1349 | 814.7379 | 1056.0805 | 493305.5694 | 850.2523
| BAS011-79244589 | 20 | BAS011 | BAS | South | 363615.8226 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.033077 | 0.033396 | 0.033716 | 0.034035 | 0.034354 | 0.034375 | 0.034395 | 0.034416 | 0.034437 | 0.034458 | 0.034479 | 0.034499 | 0.03452 | 0.034541 | 0.034562 | 0.034583 | 0.034603 | 0.034624 | 0.034645 | 0.034666 | 0.0009665 | 0.00058827 | 0.0006048 | 0.00062461 | 0.00064237 | 0.00066079 | 0.00068495 | 0.00070811 | 0.00072143 | 0.00072187 | 0.0007223 | 0.00072274 | 0.00072318 | 0.00072361 | 0.00072405 | 0.00072448 | 0.00072492 | 0.00072535 | 0.00072579 | 0.00072623 | 32877.5686 | 7348.3186 | 335.7437 | 75.0406 | 13850.9405 | 17953.8821 | 379465.8226 | 14454.7024
| BAS011-79245218 | 33 | BAS011 | BAS | South | 599966.1073 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.0022017 | 0.0022069 | 0.0022121 | 0.0022173 | 0.0022225 | 0.0022213 | 0.00222 | 0.0022188 | 0.0022176 | 0.0022164 | 0.0022152 | 0.0022139 | 0.0022127 | 0.0022115 | 0.0022103 | 0.002209 | 0.0022078 | 0.0022066 | 0.0022054 | 0.0022041 | 6.4333e-05 | 3.8874e-05 | 3.9682e-05 | 4.0692e-05 | 4.1558e-05 | 4.27e-05 | 4.421e-05 | 4.5652e-05 | 4.6457e-05 | 4.6432e-05 | 4.6406e-05 | 4.638e-05 | 4.6355e-05 | 4.6329e-05 | 4.6303e-05 | 4.6278e-05 | 4.6252e-05 | 4.6226e-05 | 4.6201e-05 | 4.6175e-05 | 32877.5686 | 7348.3186 | 21.7013 | 4.8504 | 548.4841 | 710.9568 | 626118.6073 | 572.3925
| BAS011-84427318 | 128 | BAS011 | BAS | South | 2327141.2648 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.048637 | 0.04905 | 0.049463 | 0.049876 | 0.050288 | 0.050382 | 0.050476 | 0.05057 | 0.050664 | 0.050758 | 0.050852 | 0.050946 | 0.05104 | 0.051134 | 0.051228 | 0.051322 | 0.051416 | 0.051509 | 0.051603 | 0.051697 | 0.0014212 | 0.00086401 | 0.00088728 | 0.00091532 | 0.00094032 | 0.00096851 | 0.0010052 | 0.0010405 | 0.0010614 | 0.0010633 | 0.0010653 | 0.0010673 | 0.0010692 | 0.0010712 | 0.0010732 | 0.0010752 | 0.0010771 | 0.0010791 | 0.0010811 | 0.001083 | 32877.5686 | 7348.3186 | 495.0234 | 110.6405 | 32670.2196 | 42347.83 | 2428581.2648 | 34094.3132
| BAS011-84621962 | 48 | BAS011 | BAS | South | 872677.9743 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.7527 | 0.7565 | 0.76029 | 0.76409 | 0.76788 | 0.76888 | 0.76987 | 0.77087 | 0.77187 | 0.77286 | 0.77386 | 0.77486 | 0.77585 | 0.77685 | 0.77785 | 0.77884 | 0.77984 | 0.78083 | 0.78183 | 0.78283 | 0.021994 | 0.013326 | 0.013638 | 0.014023 | 0.014358 | 0.01478 | 0.015331 | 0.015861 | 0.01617 | 0.016191 | 0.016212 | 0.016233 | 0.016254 | 0.016274 | 0.016295 | 0.016316 | 0.016337 | 0.016358 | 0.016379 | 0.0164 | 32877.5686 | 7348.3186 | 7554.6144 | 1688.4982 | 164759.6764 | 213564.979 | 910717.9743 | 171941.5445
| BAS011-84622282 | 73 | BAS011 | BAS | South | 1327197.7526 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.21739 | 0.2187 | 0.22001 | 0.22132 | 0.22263 | 0.22338 | 0.22413 | 0.22488 | 0.22563 | 0.22638 | 0.22713 | 0.22788 | 0.22863 | 0.22938 | 0.23013 | 0.23088 | 0.23163 | 0.23238 | 0.23313 | 0.23388 | 0.0063521 | 0.0038524 | 0.0039467 | 0.0040617 | 0.0041629 | 0.0042941 | 0.0044634 | 0.0046269 | 0.0047268 | 0.0047425 | 0.0047583 | 0.004774 | 0.0047897 | 0.0048054 | 0.0048211 | 0.0048368 | 0.0048525 | 0.0048683 | 0.004884 | 0.0048997 | 32877.5686 | 7348.3186 | 2211.8375 | 494.3579 | 77286.6435 | 100180.5828 | 1385050.2526 | 80655.5654
| BAS011-84732066 | 67 | BAS011 | BAS | South | 1218113.0058 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.0004941 | 0.0004995 | 0.0005049 | 0.0005103 | 0.0005157 | 0.000518 | 0.00052029 | 0.00052259 | 0.00052488 | 0.00052718 | 0.00052947 | 0.00053177 | 0.00053406 | 0.00053636 | 0.00053865 | 0.00054095 | 0.00054324 | 0.00054554 | 0.00054783 | 0.00055013 | 1.4437e-05 | 8.7986e-06 | 9.0571e-06 | 9.365e-06 | 9.6429e-06 | 9.9575e-06 | 1.0361e-05 | 1.0752e-05 | 1.0996e-05 | 1.1044e-05 | 1.1092e-05 | 1.114e-05 | 1.1188e-05 | 1.1236e-05 | 1.1284e-05 | 1.1332e-05 | 1.1381e-05 | 1.1429e-05 | 1.1477e-05 | 1.1525e-05 | 32877.5686 | 7348.3186 | 5.1346 | 1.1476 | 341.6058 | 442.7967 | 1271210.5058 | 356.4964
| BAS011-85028212 | 130 | BAS011 | BAS | South | 2363502.8471 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.15036 | 0.15129 | 0.15222 | 0.15315 | 0.15409 | 0.15408 | 0.15407 | 0.15406 | 0.15405 | 0.15405 | 0.15404 | 0.15403 | 0.15402 | 0.15402 | 0.15401 | 0.154 | 0.15399 | 0.15399 | 0.15398 | 0.15397 | 0.0043934 | 0.002665 | 0.0027306 | 0.0028107 | 0.0028812 | 0.0029619 | 0.0030682 | 0.0031698 | 0.0032273 | 0.0032272 | 0.003227 | 0.0032269 | 0.0032267 | 0.0032265 | 0.0032264 | 0.0032262 | 0.003226 | 0.0032259 | 0.0032257 | 0.0032256 | 32877.5686 | 7348.3186 | 1504.3738 | 336.2359 | 124843.7521 | 161825.1133 | 2466527.8471 | 130285.6865
| BAS011-85028323 | 19 | BAS011 | BAS | South | 345435.0315 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 1.8359e-05 | 1.8489e-05 | 1.8619e-05 | 1.875e-05 | 1.888e-05 | 1.9048e-05 | 1.9216e-05 | 1.9384e-05 | 1.9552e-05 | 1.972e-05 | 1.9888e-05 | 2.0056e-05 | 2.0224e-05 | 2.0392e-05 | 2.056e-05 | 2.0728e-05 | 2.0896e-05 | 2.1064e-05 | 2.1232e-05 | 2.14e-05 | 5.3644e-07 | 3.2568e-07 | 3.34e-07 | 3.441e-07 | 3.5303e-07 | 3.6616e-07 | 3.8267e-07 | 3.9883e-07 | 4.096e-07 | 4.1312e-07 | 4.1664e-07 | 4.2016e-07 | 4.2368e-07 | 4.272e-07 | 4.3072e-07 | 4.3424e-07 | 4.3776e-07 | 4.4128e-07 | 4.448e-07 | 4.4832e-07 | 32877.5686 | 7348.3186 | 0.19264 | 0.043057 | 12.2607 | 15.8925 | 360492.5315 | 12.7951
| BAS011-85029671 | 59 | BAS011 | BAS | South | 1072666.6768 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.035171 | 0.03543 | 0.035688 | 0.035946 | 0.036205 | 0.03633 | 0.036455 | 0.03658 | 0.036705 | 0.036831 | 0.036956 | 0.037081 | 0.037206 | 0.037332 | 0.037457 | 0.037582 | 0.037707 | 0.037833 | 0.037958 | 0.038083 | 0.0010277 | 0.00062409 | 0.00064018 | 0.00065969 | 0.00067698 | 0.00069837 | 0.00072597 | 0.00075264 | 0.00076895 | 0.00077158 | 0.0007742 | 0.00077682 | 0.00077945 | 0.00078207 | 0.0007847 | 0.00078732 | 0.00078994 | 0.00079257 | 0.00079519 | 0.00079781 | 32877.5686 | 7348.3186 | 359.534 | 80.3578 | 16724.7584 | 21678.9858 | 1119424.1768 | 17453.79
| BAS011-85030316 | 61 | BAS011 | BAS | South | 1109028.259 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.017843 | 0.017976 | 0.018109 | 0.018243 | 0.018376 | 0.018431 | 0.018486 | 0.018541 | 0.018596 | 0.018652 | 0.018707 | 0.018762 | 0.018817 | 0.018872 | 0.018927 | 0.018982 | 0.019037 | 0.019093 | 0.019148 | 0.019203 | 0.00052135 | 0.00031664 | 0.00032485 | 0.00033479 | 0.0003436 | 0.0003543 | 0.00036814 | 0.00038149 | 0.00038958 | 0.00039074 | 0.00039189 | 0.00039305 | 0.0003942 | 0.00039536 | 0.00039651 | 0.00039767 | 0.00039882 | 0.00039998 | 0.00040113 | 0.00040229 | 32877.5686 | 7348.3186 | 182.0483 | 40.6888 | 9021.219 | 11693.495 | 1157370.759 | 9414.4536
| BAS011-85421065 | 38 | BAS011 | BAS | South | 690870.063 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.08516 | 0.08565 | 0.08614 | 0.08663 | 0.08712 | 0.087211 | 0.087302 | 0.087393 | 0.087484 | 0.087576 | 0.087667 | 0.087758 | 0.087849 | 0.08794 | 0.088031 | 0.088122 | 0.088213 | 0.088305 | 0.088396 | 0.088487 | 0.0024883 | 0.0015087 | 0.0015452 | 0.0015898 | 0.001629 | 0.0016765 | 0.0017385 | 0.0017981 | 0.0018327 | 0.0018346 | 0.0018366 | 0.0018385 | 0.0018404 | 0.0018423 | 0.0018442 | 0.0018461 | 0.001848 | 0.0018499 | 0.0018518 | 0.0018537 | 32877.5686 | 7348.3186 | 855.5965 | 191.2306 | 36317.4961 | 47075.5069 | 720985.063 | 37900.5743
| BAS011-85421256 | 75 | BAS011 | BAS | South | 1363559.3349 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.036771 | 0.037058 | 0.037345 | 0.037632 | 0.037919 | 0.03804 | 0.038161 | 0.038281 | 0.038402 | 0.038523 | 0.038643 | 0.038764 | 0.038885 | 0.039006 | 0.039126 | 0.039247 | 0.039368 | 0.039489 | 0.039609 | 0.03973 | 0.0010744 | 0.00065277 | 0.00066991 | 0.00069062 | 0.00070903 | 0.00073125 | 0.00075993 | 0.00078764 | 0.0008045 | 0.00080703 | 0.00080955 | 0.00081208 | 0.00081461 | 0.00081714 | 0.00081967 | 0.0008222 | 0.00082473 | 0.00082726 | 0.00082979 | 0.00083232 | 32877.5686 | 7348.3186 | 375.9236 | 84.021 | 37791.7304 | 48986.4406 | 1422996.8349 | 39439.0705
| BAS011-85724039 | 86 | BAS011 | BAS | South | 1563548.0373 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.41901 | 0.42151 | 0.424 | 0.4265 | 0.42899 | 0.42996 | 0.43092 | 0.43188 | 0.43284 | 0.43381 | 0.43477 | 0.43573 | 0.43669 | 0.43765 | 0.43862 | 0.43958 | 0.44054 | 0.4415 | 0.44246 | 0.44343 | 0.012243 | 0.0074248 | 0.0076059 | 0.0078271 | 0.0080216 | 0.0082651 | 0.0085814 | 0.0088859 | 0.0090678 | 0.0090879 | 0.0091081 | 0.0091282 | 0.0091484 | 0.0091686 | 0.0091887 | 0.0092089 | 0.009229 | 0.0092492 | 0.0092693 | 0.0092895 | 32877.5686 | 7348.3186 | 4238.1412 | 947.248 | 171413.5066 | 222189.8146 | 1631703.0373 | 178885.4149
| BAS011-89021568 | 68 | BAS011 | BAS | South | 1236293.7969 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.11226 | 0.11301 | 0.11376 | 0.11452 | 0.11527 | 0.11547 | 0.11566 | 0.11586 | 0.11606 | 0.11626 | 0.11645 | 0.11665 | 0.11685 | 0.11704 | 0.11724 | 0.11744 | 0.11764 | 0.11783 | 0.11803 | 0.11823 | 0.0032801 | 0.0019906 | 0.0020407 | 0.0021016 | 0.0021554 | 0.0022196 | 0.0023033 | 0.0023838 | 0.0024313 | 0.0024355 | 0.0024396 | 0.0024437 | 0.0024479 | 0.002452 | 0.0024561 | 0.0024603 | 0.0024644 | 0.0024685 | 0.0024727 | 0.0024768 | 32877.5686 | 7348.3186 | 1135.1321 | 253.7083 | 40575.6028 | 52594.955 | 1290183.7969 | 42344.2918
| BAS011-99529198 | 43 | BAS011 | BAS | South | 781774.0187 | 0.0010496 | 0.00063272 | 0.00064434 | 0.0006592 | 0.00067165 | 0.00069049 | 0.00071531 | 0.00073904 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.00075249 | 0.0085738 | 0.0086544 | 0.008735 | 0.0088156 | 0.0088962 | 0.0089452 | 0.0089942 | 0.0090431 | 0.0090921 | 0.0091411 | 0.00919 | 0.009239 | 0.009288 | 0.0093369 | 0.0093859 | 0.0094349 | 0.0094839 | 0.0095328 | 0.0095818 | 0.0096308 | 0.00025052 | 0.00015245 | 0.00015669 | 0.00016178 | 0.00016635 | 0.00017196 | 0.00017911 | 0.00018606 | 0.00019047 | 0.0001915 | 0.00019253 | 0.00019355 | 0.00019458 | 0.0001956 | 0.00019663 | 0.00019765 | 0.00019868 | 0.00019971 | 0.00020073 | 0.00020176 | 32877.5686 | 7348.3186 | 89.1324 | 19.9216 | 7903.1651 | 10244.2499 | 815851.5187 | 8247.6638
| BAS012-15414133 | 132 | BAS012 | BAS | South | 2399864.4294 | 0.001584 | 0.0014427 | 0.0014339 | 0.0014305 | 0.001429 | 0.0014382 | 0.0014565 | 0.0014657 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32877.5686 | 7348.3186 | 0 | 0 | 0 | 0 | 2504474.4294 | 0
| BAS012-187042122 | 95 | BAS012 | BAS | South | 1727175.1575 | 0.001584 | 0.0014427 | 0.0014339 | 0.0014305 | 0.001429 | 0.0014382 | 0.0014565 | 0.0014657 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0.0014699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32877.5686 | 7348.3186 | 0 | 0 | 0 | 0 | 1802462.6575 | 0
| BAS013-15414170 | 5 | BAS013 | BAS | South | 90903.9557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32877.5686 | 7348.3186 | 0 | 0 | 0 | 0 | 94866.4557 | 0
| BAS014-15414207 | 130 | BAS014 | BAS | South | 2363502.8471 | 0.0015642 | 0.0015658 | 0.001583 | 0.0015935 | 0.0016007 | 0.0016235 | 0.0016598 | 0.0016857 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32877.5686 | 7348.3186 | 0 | 0 | 0 | 0 | 2466527.8471 | 0
| BAS014-74639994 | 141 | BAS014 | BAS | South | 2563491.5495 | 0.0015642 | 0.0015658 | 0.001583 | 0.0015935 | 0.0016007 | 0.0016235 | 0.0016598 | 0.0016857 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0.0016844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32877.5686 | 7348.3186 | 0 | 0 | 0 | 0 | 2675234.0495 | 0
| BAS021-15414366 | 0 | BAS021 | BAS | South | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32877.5686 | 7348.3186 | 0 | 0 | 0 | 0 | 0 | 0
| BAS022-130430211 | 114 | BAS022 | BAS | South | 2072610.189 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.086221 | 0.086799 | 0.087377 | 0.087954 | 0.088532 | 0.088642 | 0.088753 | 0.088863 | 0.088974 | 0.089084 | 0.089195 | 0.089306 | 0.089416 | 0.089527 | 0.089637 | 0.089748 | 0.089858 | 0.089969 | 0.090079 | 0.09019 | 0.002252 | 0.0023444 | 0.0023249 | 0.0018372 | 0.0019243 | 0.0020189 | 0.0021223 | 0.0022153 | 0.0022862 | 0.002289 | 0.0022919 | 0.0022947 | 0.0022976 | 0.0023004 | 0.0023032 | 0.0023061 | 0.0023089 | 0.0023118 | 0.0023146 | 0.0023174 | 32877.5686 | 7348.3186 | 1055.5744 | 235.9267 | 55382.6362 | 71788.145 | 2162955.189 | 57796.7632
| BAS022-131562724 | 613 | BAS022 | BAS | South | 11144824.9636 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 37.8166 | 38.0083 | 38.2 | 38.3917 | 38.5834 | 38.763 | 38.9426 | 39.1223 | 39.3019 | 39.4815 | 39.6611 | 39.8407 | 40.0203 | 40.1999 | 40.3795 | 40.5591 | 40.7387 | 40.9183 | 41.0979 | 41.2775 | 0.98774 | 1.0266 | 1.0164 | 0.80192 | 0.83865 | 0.88287 | 0.9312 | 0.97531 | 1.0099 | 1.0145 | 1.0191 | 1.0237 | 1.0283 | 1.0329 | 1.0376 | 1.0422 | 1.0468 | 1.0514 | 1.056 | 1.0606 | 32877.5686 | 7348.3186 | 468554.34 | 104724.4897 | 8825525.3549 | 11439832.7236 | 11630627.4636 | 9210229.6724
| BAS022-139345117 | 95 | BAS022 | BAS | South | 1727175.1575 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.48903 | 0.49177 | 0.4945 | 0.49724 | 0.49997 | 0.49945 | 0.49893 | 0.4984 | 0.49788 | 0.49735 | 0.49683 | 0.49631 | 0.49578 | 0.49526 | 0.49473 | 0.49421 | 0.49369 | 0.49316 | 0.49264 | 0.49211 | 0.012773 | 0.013283 | 0.013158 | 0.010386 | 0.010867 | 0.011375 | 0.01193 | 0.012425 | 0.012793 | 0.01278 | 0.012766 | 0.012753 | 0.012739 | 0.012726 | 0.012712 | 0.012699 | 0.012685 | 0.012672 | 0.012658 | 0.012645 | 32877.5686 | 7348.3186 | 5895.3457 | 1317.6424 | 174300.408 | 225931.8772 | 1802462.6575 | 181898.1562
| BAS022-139345255 | 60 | BAS022 | BAS | South | 1090847.4679 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.39214 | 0.39267 | 0.39319 | 0.39372 | 0.39424 | 0.39344 | 0.39263 | 0.39182 | 0.39102 | 0.39021 | 0.38941 | 0.3886 | 0.38779 | 0.38699 | 0.38618 | 0.38538 | 0.38457 | 0.38376 | 0.38296 | 0.38215 | 0.010242 | 0.010606 | 0.010462 | 0.0082239 | 0.0085692 | 0.0089609 | 0.0093885 | 0.009768 | 0.010047 | 0.010027 | 0.010006 | 0.0099852 | 0.0099644 | 0.0099437 | 0.009923 | 0.0099023 | 0.0098816 | 0.0098609 | 0.0098402 | 0.0098195 | 32877.5686 | 7348.3186 | 4637.8684 | 1036.5893 | 81985.3777 | 106271.1814 | 1138397.4679 | 85559.1172
| BAS022-139345594 | 144 | BAS022 | BAS | South | 2618033.9229 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.2343 | 0.2357 | 0.2371 | 0.2385 | 0.23989 | 0.24055 | 0.24121 | 0.24187 | 0.24253 | 0.24318 | 0.24384 | 0.2445 | 0.24516 | 0.24582 | 0.24647 | 0.24713 | 0.24779 | 0.24845 | 0.24911 | 0.24976 | 0.0061198 | 0.0063662 | 0.0063087 | 0.0049817 | 0.0052143 | 0.0054788 | 0.0057678 | 0.0060297 | 0.0062318 | 0.0062487 | 0.0062656 | 0.0062825 | 0.0062994 | 0.0063163 | 0.0063332 | 0.0063501 | 0.006367 | 0.0063839 | 0.0064008 | 0.0064177 | 32877.5686 | 7348.3186 | 2883.5498 | 644.4894 | 116092.3045 | 150481.3017 | 2732153.9229 | 121152.7636
| BAS022-142437045 | 40 | BAS022 | BAS | South | 727231.6453 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 1.2552 | 1.2621 | 1.2689 | 1.2758 | 1.2826 | 1.283 | 1.2833 | 1.2836 | 1.2839 | 1.2842 | 1.2846 | 1.2849 | 1.2852 | 1.2855 | 1.2858 | 1.2862 | 1.2865 | 1.2868 | 1.2871 | 1.2875 | 0.032785 | 0.034088 | 0.033764 | 0.026648 | 0.027879 | 0.029221 | 0.030686 | 0.032 | 0.032991 | 0.032999 | 0.033007 | 0.033015 | 0.033024 | 0.033032 | 0.03304 | 0.033048 | 0.033057 | 0.033065 | 0.033073 | 0.033081 | 32877.5686 | 7348.3186 | 15227.075 | 3403.3356 | 172520.0047 | 223624.0808 | 758931.6453 | 180040.1452
| BAS022-142437276 | 11 | BAS022 | BAS | South | 199988.7024 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.032508 | 0.032693 | 0.032877 | 0.033062 | 0.033246 | 0.033257 | 0.033267 | 0.033277 | 0.033288 | 0.033298 | 0.033308 | 0.033318 | 0.033329 | 0.033339 | 0.033349 | 0.03336 | 0.03337 | 0.03338 | 0.033391 | 0.033401 | 0.00084909 | 0.00088302 | 0.0008748 | 0.00069059 | 0.00072264 | 0.00075745 | 0.00079548 | 0.00082959 | 0.00085533 | 0.00085559 | 0.00085586 | 0.00085612 | 0.00085639 | 0.00085665 | 0.00085692 | 0.00085718 | 0.00085745 | 0.00085771 | 0.00085798 | 0.00085824 | 32877.5686 | 7348.3186 | 394.7553 | 88.23 | 4360.6866 | 5652.4142 | 208706.2024 | 4550.7687
| BAS022-142437414 | 14 | BAS022 | BAS | South | 254531.0758 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.34457 | 0.34641 | 0.34825 | 0.35009 | 0.35193 | 0.35219 | 0.35246 | 0.35272 | 0.35298 | 0.35325 | 0.35351 | 0.35377 | 0.35404 | 0.3543 | 0.35456 | 0.35483 | 0.35509 | 0.35535 | 0.35562 | 0.35588 | 0.0089999 | 0.0093565 | 0.0092662 | 0.0073126 | 0.0076495 | 0.0080215 | 0.0084279 | 0.0087932 | 0.00907 | 0.0090767 | 0.0090835 | 0.0090903 | 0.009097 | 0.0091038 | 0.0091106 | 0.0091174 | 0.0091241 | 0.0091309 | 0.0091377 | 0.0091444 | 32877.5686 | 7348.3186 | 4189.0442 | 936.2746 | 28791.3532 | 37319.9613 | 265626.0758 | 30046.3672
| BAS022-144337084 | 48 | BAS022 | BAS | South | 872677.9743 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.2427 | 0.244 | 0.2453 | 0.2466 | 0.2479 | 0.24882 | 0.24975 | 0.25067 | 0.2516 | 0.25252 | 0.25344 | 0.25437 | 0.25529 | 0.25621 | 0.25714 | 0.25806 | 0.25899 | 0.25991 | 0.26083 | 0.26176 | 0.0063391 | 0.0065903 | 0.0065269 | 0.0051509 | 0.0053884 | 0.0056672 | 0.005972 | 0.0062492 | 0.0064648 | 0.0064885 | 0.0065123 | 0.006536 | 0.0065598 | 0.0065835 | 0.0066072 | 0.006631 | 0.0066547 | 0.0066784 | 0.0067022 | 0.0067259 | 32877.5686 | 7348.3186 | 2995.8584 | 669.5909 | 75613.6491 | 98012.012 | 910717.9743 | 78909.6452
| BAS022-15416117 | 132 | BAS022 | BAS | South | 2399864.4294 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 58.1743 | 58.4589 | 58.7436 | 59.0283 | 59.3129 | 59.509 | 59.7051 | 59.9012 | 60.0972 | 60.2933 | 60.4894 | 60.6855 | 60.8816 | 61.0776 | 61.2737 | 61.4698 | 61.6659 | 61.8619 | 62.058 | 62.2541 | 1.5195 | 1.579 | 1.5631 | 1.233 | 1.2892 | 1.3554 | 1.4277 | 1.4933 | 1.5442 | 1.5492 | 1.5543 | 1.5593 | 1.5644 | 1.5694 | 1.5744 | 1.5795 | 1.5845 | 1.5896 | 1.5946 | 1.5996 | 32877.5686 | 7348.3186 | 715482.9078 | 159914.3921 | 565041.2261 | 732418.3943 | 2504474.4294 | 589671.3519
| BAS022-155392787 | 13 | BAS022 | BAS | South | 236350.2847 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.16968 | 0.17026 | 0.17083 | 0.17141 | 0.17199 | 0.17238 | 0.17278 | 0.17318 | 0.17358 | 0.17398 | 0.17438 | 0.17477 | 0.17517 | 0.17557 | 0.17597 | 0.17637 | 0.17676 | 0.17716 | 0.17756 | 0.17796 | 0.0044319 | 0.0045986 | 0.0045455 | 0.0035804 | 0.0037383 | 0.0039262 | 0.0041316 | 0.0043173 | 0.0044601 | 0.0044704 | 0.0044806 | 0.0044908 | 0.0045011 | 0.0045113 | 0.0045215 | 0.0045318 | 0.004542 | 0.0045522 | 0.0045625 | 0.0045727 | 32877.5686 | 7348.3186 | 2066.25 | 461.8183 | 15212.3456 | 19718.5643 | 246652.7847 | 15875.4512
| BAS022-155392904 | 48 | BAS022 | BAS | South | 872677.9743 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.041878 | 0.042137 | 0.042397 | 0.042656 | 0.042915 | 0.043049 | 0.043183 | 0.043317 | 0.043451 | 0.043585 | 0.043719 | 0.043853 | 0.043987 | 0.044121 | 0.044255 | 0.044389 | 0.044523 | 0.044657 | 0.044791 | 0.044925 | 0.0010938 | 0.0011381 | 0.0011281 | 0.00089099 | 0.0009328 | 0.00098048 | 0.0010326 | 0.0010799 | 0.0011165 | 0.0011199 | 0.0011234 | 0.0011268 | 0.0011302 | 0.0011337 | 0.0011371 | 0.0011406 | 0.001144 | 0.0011475 | 0.0011509 | 0.0011543 | 32877.5686 | 7348.3186 | 516.7622 | 115.4992 | 24901.9794 | 32278.4727 | 910717.9743 | 25987.4558
| BAS022-155393076 | 58 | BAS022 | BAS | South | 1054485.8856 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.14938 | 0.15047 | 0.15156 | 0.15264 | 0.15373 | 0.1542 | 0.15467 | 0.15514 | 0.15561 | 0.15608 | 0.15655 | 0.15702 | 0.15749 | 0.15795 | 0.15842 | 0.15889 | 0.15936 | 0.15983 | 0.1603 | 0.16077 | 0.0039017 | 0.0040641 | 0.0040326 | 0.0031884 | 0.0033415 | 0.0035121 | 0.0036985 | 0.0038676 | 0.0039984 | 0.0040104 | 0.0040225 | 0.0040346 | 0.0040466 | 0.0040587 | 0.0040707 | 0.0040828 | 0.0040948 | 0.0041069 | 0.0041189 | 0.004131 | 32877.5686 | 7348.3186 | 1849.2187 | 413.3106 | 49353.062 | 63972.4834 | 1100450.8856 | 51504.3601
| BAS022-163916141 | 17 | BAS022 | BAS | South | 309073.4492 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.22234 | 0.22369 | 0.22504 | 0.22639 | 0.22773 | 0.22832 | 0.22891 | 0.2295 | 0.23009 | 0.23068 | 0.23127 | 0.23186 | 0.23245 | 0.23304 | 0.23363 | 0.23422 | 0.23481 | 0.2354 | 0.23599 | 0.23658 | 0.0058075 | 0.0060418 | 0.0059878 | 0.0047287 | 0.00495 | 0.0052003 | 0.0054737 | 0.0057214 | 0.0059122 | 0.0059274 | 0.0059426 | 0.0059577 | 0.0059729 | 0.005988 | 0.0060032 | 0.0060183 | 0.0060335 | 0.0060486 | 0.0060638 | 0.0060789 | 32877.5686 | 7348.3186 | 2735.0695 | 611.3032 | 41079.6061 | 53248.2547 | 322545.9492 | 42870.2645
| BAS022-164206998 | 294 | BAS022 | BAS | South | 5345152.5926 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 25.3354 | 25.4455 | 25.5556 | 25.6657 | 25.7758 | 25.8228 | 25.8698 | 25.9168 | 25.9638 | 26.0108 | 26.0578 | 26.1048 | 26.1518 | 26.1988 | 26.2458 | 26.2928 | 26.3398 | 26.3868 | 26.4338 | 26.4808 | 0.66174 | 0.68728 | 0.67998 | 0.5361 | 0.56026 | 0.58814 | 0.6186 | 0.6461 | 0.66714 | 0.66835 | 0.66956 | 0.67077 | 0.67198 | 0.67318 | 0.67439 | 0.6756 | 0.67681 | 0.67801 | 0.67922 | 0.68043 | 32877.5686 | 7348.3186 | 308704.7761 | 68997.227 | 3069990.8261 | 3979387.0735 | 5578147.5926 | 3203811.6105
| BAS022-171331284 | 22 | BAS022 | BAS | South | 399977.4049 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.39051 | 0.39243 | 0.39434 | 0.39626 | 0.39818 | 0.39914 | 0.40009 | 0.40105 | 0.402 | 0.40296 | 0.40392 | 0.40487 | 0.40583 | 0.40679 | 0.40774 | 0.4087 | 0.40966 | 0.41061 | 0.41157 | 0.41253 | 0.0102 | 0.010599 | 0.010493 | 0.008277 | 0.0086548 | 0.0090907 | 0.009567 | 0.009998 | 0.01033 | 0.010354 | 0.010379 | 0.010403 | 0.010428 | 0.010452 | 0.010477 | 0.010502 | 0.010526 | 0.010551 | 0.010575 | 0.0106 | 32877.5686 | 7348.3186 | 4781.1271 | 1068.6084 | 74944.1029 | 97144.1321 | 417412.4049 | 78210.9135
| BAS022-172349144 | 10 | BAS022 | BAS | South | 181807.9113 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00011409 | 0.00011475 | 0.0001154 | 0.00011605 | 0.0001167 | 0.00011731 | 0.00011793 | 0.00011855 | 0.00011916 | 0.00011978 | 0.00012039 | 0.00012101 | 0.00012162 | 0.00012224 | 0.00012285 | 0.00012347 | 0.00012408 | 0.0001247 | 0.00012531 | 0.00012593 | 2.9801e-06 | 3.0993e-06 | 3.0705e-06 | 2.424e-06 | 2.5366e-06 | 2.672e-06 | 2.8199e-06 | 2.9553e-06 | 3.0618e-06 | 3.0776e-06 | 3.0934e-06 | 3.1092e-06 | 3.1251e-06 | 3.1409e-06 | 3.1567e-06 | 3.1725e-06 | 3.1883e-06 | 3.2041e-06 | 3.2199e-06 | 3.2357e-06 | 32877.5686 | 7348.3186 | 1.421 | 0.3176 | 104.59 | 135.5718 | 189732.9113 | 109.1491
| BAS022-193385657 | 44 | BAS022 | BAS | South | 799954.8098 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 8.908 | 8.9362 | 8.9643 | 8.9925 | 9.0207 | 9.0294 | 9.038 | 9.0467 | 9.0554 | 9.064 | 9.0727 | 9.0814 | 9.09 | 9.0987 | 9.1074 | 9.1161 | 9.1247 | 9.1334 | 9.1421 | 9.1507 | 0.23267 | 0.24136 | 0.23852 | 0.18783 | 0.19607 | 0.20565 | 0.21612 | 0.22553 | 0.23268 | 0.2329 | 0.23312 | 0.23335 | 0.23357 | 0.23379 | 0.23402 | 0.23424 | 0.23446 | 0.23468 | 0.23491 | 0.23513 | 32877.5686 | 7348.3186 | 107645.3241 | 24059.3261 | 146332.216 | 189678.915 | 834824.8098 | 152710.8318
| BAS022-193385775 | 426 | BAS022 | BAS | South | 7745017.022 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 250.1655 | 251.3558 | 252.546 | 253.7362 | 254.9265 | 255.4082 | 255.8899 | 256.3716 | 256.8533 | 257.335 | 257.8167 | 258.2984 | 258.7801 | 259.2618 | 259.7436 | 260.2253 | 260.707 | 261.1887 | 261.6704 | 262.1521 | 6.5341 | 6.7891 | 6.7197 | 5.3 | 5.5411 | 5.8172 | 6.1188 | 6.3913 | 6.5999 | 6.6123 | 6.6247 | 6.637 | 6.6494 | 6.6618 | 6.6742 | 6.6865 | 6.6989 | 6.7113 | 6.7237 | 6.7361 | 32877.5686 | 7348.3186 | 3053344.8142 | 682439.4747 | 9665077.3289 | 12528077.7582 | 8082622.022 | 10086377.6853
| BAS022-24598930 | 380 | BAS022 | BAS | South | 6908700.63 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 10.3979 | 10.4529 | 10.5078 | 10.5628 | 10.6177 | 10.645 | 10.6723 | 10.6996 | 10.7269 | 10.7542 | 10.7815 | 10.8088 | 10.8361 | 10.8634 | 10.8908 | 10.9181 | 10.9454 | 10.9727 | 11 | 11.0273 | 0.27159 | 0.28233 | 0.27959 | 0.22063 | 0.23079 | 0.24245 | 0.2552 | 0.26674 | 0.27563 | 0.27633 | 0.27703 | 0.27774 | 0.27844 | 0.27914 | 0.27984 | 0.28054 | 0.28124 | 0.28194 | 0.28265 | 0.28335 | 32877.5686 | 7348.3186 | 127570.898 | 28512.8022 | 2067224.8695 | 2679580.6207 | 7209850.63 | 2157335.1236
| BAS022-72697775 | 19 | BAS022 | BAS | South | 345435.0315 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.028052 | 0.028221 | 0.028391 | 0.02856 | 0.02873 | 0.028774 | 0.028817 | 0.028861 | 0.028905 | 0.028948 | 0.028992 | 0.029036 | 0.029079 | 0.029123 | 0.029167 | 0.029211 | 0.029254 | 0.029298 | 0.029342 | 0.029385 | 0.0007327 | 0.00076226 | 0.00075543 | 0.00059657 | 0.00062447 | 0.00065535 | 0.00068908 | 0.0007195 | 0.00074271 | 0.00074384 | 0.00074496 | 0.00074608 | 0.0007472 | 0.00074833 | 0.00074945 | 0.00075057 | 0.00075169 | 0.00075282 | 0.00075394 | 0.00075506 | 32877.5686 | 7348.3186 | 343.1742 | 76.7013 | 11079.6461 | 14361.6717 | 360492.5315 | 11562.6074
| BAS022-72698236 | 51 | BAS022 | BAS | South | 927220.3477 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.062501 | 0.062874 | 0.063248 | 0.063621 | 0.063994 | 0.064204 | 0.064414 | 0.064624 | 0.064834 | 0.065044 | 0.065255 | 0.065465 | 0.065675 | 0.065885 | 0.066095 | 0.066305 | 0.066515 | 0.066725 | 0.066935 | 0.067145 | 0.0016325 | 0.0016982 | 0.0016829 | 0.0013289 | 0.001391 | 0.0014623 | 0.0015403 | 0.0016111 | 0.0016659 | 0.0016713 | 0.0016767 | 0.0016821 | 0.0016875 | 0.0016929 | 0.0016983 | 0.0017037 | 0.0017091 | 0.0017145 | 0.0017199 | 0.0017253 | 32877.5686 | 7348.3186 | 771.3245 | 172.3953 | 34752.1613 | 45046.4868 | 967637.8477 | 36267.0067
| BAS022-72698508 | 34 | BAS022 | BAS | South | 618146.8985 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.035106 | 0.035283 | 0.035461 | 0.035638 | 0.035816 | 0.035898 | 0.03598 | 0.036062 | 0.036144 | 0.036226 | 0.036308 | 0.03639 | 0.036472 | 0.036554 | 0.036636 | 0.036718 | 0.0368 | 0.036882 | 0.036964 | 0.037046 | 0.00091694 | 0.000953 | 0.00094354 | 0.00074441 | 0.00077849 | 0.00081761 | 0.00086035 | 0.00089901 | 0.00092872 | 0.00093083 | 0.00093294 | 0.00093504 | 0.00093715 | 0.00093926 | 0.00094136 | 0.00094347 | 0.00094557 | 0.00094768 | 0.00094979 | 0.00095189 | 32877.5686 | 7348.3186 | 429.7705 | 96.0561 | 17930.6579 | 23242.0982 | 645091.8985 | 18712.2546
| BAS022-88324187 | 3 | BAS022 | BAS | South | 54542.3734 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.26623 | 0.2677 | 0.26917 | 0.27064 | 0.27211 | 0.273 | 0.27389 | 0.27478 | 0.27567 | 0.27656 | 0.27745 | 0.27834 | 0.27923 | 0.28013 | 0.28102 | 0.28191 | 0.2828 | 0.28369 | 0.28458 | 0.28547 | 0.0069538 | 0.0072306 | 0.0071621 | 0.0056531 | 0.0059146 | 0.0062178 | 0.0065493 | 0.0068502 | 0.0070835 | 0.0071063 | 0.0071292 | 0.0071521 | 0.007175 | 0.0071979 | 0.0072208 | 0.0072437 | 0.0072665 | 0.0072894 | 0.0073123 | 0.0073352 | 32877.5686 | 7348.3186 | 3280.5486 | 733.2208 | 4939.9825 | 6403.3099 | 56919.8734 | 5155.3162
| BAS022-88324452 | 28 | BAS022 | BAS | South | 509062.1517 | 0.00093819 | 0.00097018 | 0.00095575 | 0.00075028 | 0.00078074 | 0.0008181 | 0.00085891 | 0.00089546 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.00092296 | 0.28175 | 0.2835 | 0.28525 | 0.287 | 0.28875 | 0.28935 | 0.28994 | 0.29054 | 0.29113 | 0.29172 | 0.29232 | 0.29291 | 0.2935 | 0.2941 | 0.29469 | 0.29528 | 0.29588 | 0.29647 | 0.29706 | 0.29766 | 0.007359 | 0.0076572 | 0.0075899 | 0.0059949 | 0.0062763 | 0.0065902 | 0.0069331 | 0.0072429 | 0.0074806 | 0.0074959 | 0.0075111 | 0.0075263 | 0.0075416 | 0.0075568 | 0.0075721 | 0.0075873 | 0.0076026 | 0.0076178 | 0.0076331 | 0.0076483 | 32877.5686 | 7348.3186 | 3458.1575 | 772.9174 | 46496.6449 | 60269.9351 | 531252.1517 | 48523.4319
| BAS023-141849160 | 38 | BAS023 | BAS | South | 690870.063 | 0.00091847 | 0.0002271 | 0.00023485 | 0.00024261 | 0.00025036 | 0.00026144 | 0.00027285 | 0.00028282 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.33121 | 0.33299 | 0.33477 | 0.33656 | 0.33834 | 0.33899 | 0.33964 | 0.34028 | 0.34093 | 0.34158 | 0.34223 | 0.34287 | 0.34352 | 0.34417 | 0.34482 | 0.34546 | 0.34611 | 0.34676 | 0.34741 | 0.34805 | 0.008469 | 0.0021053 | 0.0021888 | 0.0022732 | 0.0023583 | 0.0024673 | 0.0025799 | 0.0026793 | 0.002758 | 0.0027632 | 0.0027685 | 0.0027737 | 0.0027789 | 0.0027842 | 0.0027894 | 0.0027946 | 0.0027999 | 0.0028051 | 0.0028104 | 0.0028156 | 32877.5686 | 7348.3186 | 1424.6578 | 318.4189 | 113352.0742 | 146929.3573 | 720985.063 | 118293.0868
| BAS023-141849179 | 35 | BAS023 | BAS | South | 636327.6896 | 0.00091847 | 0.0002271 | 0.00023485 | 0.00024261 | 0.00025036 | 0.00026144 | 0.00027285 | 0.00028282 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.041025 | 0.041309 | 0.041592 | 0.041876 | 0.04216 | 0.042352 | 0.042545 | 0.042738 | 0.04293 | 0.043123 | 0.043316 | 0.043508 | 0.043701 | 0.043894 | 0.044087 | 0.044279 | 0.044472 | 0.044665 | 0.044857 | 0.04505 | 0.001049 | 0.00026117 | 0.00027194 | 0.00028284 | 0.00029385 | 0.00030826 | 0.00032318 | 0.0003365 | 0.00034729 | 0.00034885 | 0.0003504 | 0.00035196 | 0.00035352 | 0.00035508 | 0.00035664 | 0.0003582 | 0.00035976 | 0.00036132 | 0.00036287 | 0.00036443 | 32877.5686 | 7348.3186 | 179.4024 | 40.0974 | 20793.9323 | 26953.5351 | 664065.1896 | 21700.339
| BAS023-15416141 | 153 | BAS023 | BAS | South | 2781661.0431 | 0.00091847 | 0.0002271 | 0.00023485 | 0.00024261 | 0.00025036 | 0.00026144 | 0.00027285 | 0.00028282 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32877.5686 | 7348.3186 | 0 | 0 | 0 | 0 | 2902913.5431 | 0
| BAS023-155325011 | 39 | BAS023 | BAS | South | 709050.8541 | 0.00091847 | 0.0002271 | 0.00023485 | 0.00024261 | 0.00025036 | 0.00026144 | 0.00027285 | 0.00028282 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.41844 | 0.42089 | 0.42333 | 0.42577 | 0.42822 | 0.42914 | 0.43006 | 0.43099 | 0.43191 | 0.43283 | 0.43376 | 0.43468 | 0.43561 | 0.43653 | 0.43745 | 0.43838 | 0.4393 | 0.44022 | 0.44115 | 0.44207 | 0.0107 | 0.002661 | 0.0027678 | 0.0028757 | 0.0029847 | 0.0031235 | 0.0032668 | 0.0033934 | 0.003494 | 0.0035014 | 0.0035089 | 0.0035164 | 0.0035239 | 0.0035313 | 0.0035388 | 0.0035463 | 0.0035537 | 0.0035612 | 0.0035687 | 0.0035762 | 32877.5686 | 7348.3186 | 1804.2672 | 403.2637 | 98249.7675 | 127353.4277 | 739958.3541 | 102532.4712
| BAS023-24612761 | 261 | BAS023 | BAS | South | 4745186.4853 | 0.00091847 | 0.0002271 | 0.00023485 | 0.00024261 | 0.00025036 | 0.00026144 | 0.00027285 | 0.00028282 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 83.3881 | 83.7491 | 84.1101 | 84.4711 | 84.8321 | 84.9517 | 85.0713 | 85.1909 | 85.3105 | 85.4301 | 85.5497 | 85.6693 | 85.7889 | 85.9085 | 86.0281 | 86.1477 | 86.2673 | 86.3869 | 86.5065 | 86.6261 | 2.1322 | 0.52949 | 0.54993 | 0.57053 | 0.59128 | 0.61832 | 0.64621 | 0.67076 | 0.69012 | 0.69109 | 0.69206 | 0.69303 | 0.69399 | 0.69496 | 0.69593 | 0.6969 | 0.69786 | 0.69883 | 0.6998 | 0.70077 | 32877.5686 | 7348.3186 | 356767.5948 | 79739.5331 | 2162691.9963 | 2803327.1307 | 4952028.9853 | 2256963.6589
| BAS023-41628847 | 403 | BAS023 | BAS | South | 7326858.826 | 0.00091847 | 0.0002271 | 0.00023485 | 0.00024261 | 0.00025036 | 0.00026144 | 0.00027285 | 0.00028282 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 0.00029057 | 10.5007 | 10.5658 | 10.6308 | 10.6958 | 10.7608 | 10.7952 | 10.8297 | 10.8641 | 10.8985 | 10.9329 | 10.9673 | 11.0017 | 11.0362 | 11.0706 | 11.105 | 11.1394 | 11.1738 | 11.2083 | 11.2427 | 11.2771 | 0.26851 | 0.066801 | 0.069507 | 0.072241 | 0.075003 | 0.078572 | 0.082263 | 0.08554 | 0.088164 | 0.088442 | 0.088721 | 0.088999 | 0.089278 | 0.089556 | 0.089834 | 0.090113 | 0.090391 | 0.09067 | 0.090948 | 0.091226 | 32877.5686 | 7348.3186 | 45539.5937 | 10178.3514 | 2384718.2455 | 3091122.2533 | 7646236.326 | 2488668.0239
| BAS024-15416191 | 179 | BAS024 | BAS | South | 3254361.6125 | 0.0013416 | 0.00090106 | 0.00094742 | 0.00099199 | 0.0010356 | 0.0010877 | 0.0011457 | 0.0011987 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 0.001241 | 1.8323 | 1.8451 | 1.858 | 1.8708 | 1.8837 | 1.8942 | 1.9048 | 1.9153 | 1.9259 | 1.9365 | 1.947 | 1.9576 | 1.9681 | 1.9787 | 1.9892 | 1.9998 | 2.0104 | 2.0209 | 2.0315 | 2.042 | 0.068435 | 0.046286 | 0.049006 | 0.051667 | 0.05431 | 0.057362 | 0.060755 | 0.063921 | 0.066541 | 0.066906 | 0.067271 | 0.067636 | 0.068 | 0.068365 | 0.06873 | 0.069094 | 0.069459 | 0.069824 | 0.070189 | 0.070553 | 32877.5686 | 7348.3186 | 29741.1781 | 6647.318 | 17100.106 | 22165.5193 | 3396219.1125 | 17845.499
| BAS032-155216556 | 241 | BAS032 | BAS | South | 4381570.6627 | 0.0011604 | 0.0011881 | 0.0012256 | 0.0012741 | 0.0013261 | 0.0013818 | 0.0014421 | 0.0014955 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 118.5393 | 118.9448 | 119.3502 | 119.7557 | 120.1612 | 120.2915 | 120.4218 | 120.5521 | 120.6823 | 120.8126 | 120.9429 | 121.0732 | 121.2035 | 121.3338 | 121.4641 | 121.5944 | 121.7247 | 121.855 | 121.9853 | 122.1156 | 3.8296 | 3.9342 | 4.0723 | 4.2478 | 4.436 | 4.6276 | 4.8348 | 5.019 | 5.175 | 5.1806 | 5.1862 | 5.1918 | 5.1973 | 5.2029 | 5.2085 | 5.2141 | 5.2197 | 5.2253 | 5.2309 | 5.2365 | 32877.5686 | 7348.3186 | 2275928.2192 | 508682.5606 | 3114662.0635 | 4037290.8767 | 4572563.1627 | 3250430.0654
| BAS032-177751012 | 302 | BAS032 | BAS | South | 5490598.9217 | 0.0011604 | 0.0011881 | 0.0012256 | 0.0012741 | 0.0013261 | 0.0013818 | 0.0014421 | 0.0014955 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 0.0015403 | 55.9949 | 56.1603 | 56.3258 | 56.4912 | 56.6566 | 56.7307 | 56.8048 | 56.8789 | 56.953 | 57.027 | 57.1011 | 57.1752 | 57.2493 | 57.3234 | 57.3975 | 57.4716 | 57.5457 | 57.6198 | 57.6939 | 57.768 | 1.809 | 1.8575 | 1.9219 | 2.0038 | 2.0916 | 2.1824 | 2.2806 | 2.3681 | 2.4422 | 2.4454 | 2.4486 | 2.4517 | 2.4549 | 2.4581 | 2.4613 | 2.4644 | 2.4676 | 2.4708 | 2.474 | 2.4772 | 32877.5686 | 7348.3186 | 1074669.7369 | 240194.6375 | 996154.9064 | 1291237.0695 | 5729933.9217 | 1039577.2612
| BAS033-139662053 | 81 | BAS033 | BAS | South | 1472644.0816 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 1.0822 | 1.0899 | 1.0975 | 1.1052 | 1.1128 | 1.1105 | 1.1082 | 1.1059 | 1.1036 | 1.1013 | 1.099 | 1.0967 | 1.0944 | 1.0921 | 1.0898 | 1.0875 | 1.0851 | 1.0828 | 1.0805 | 1.0782 | 0.018716 | 0.01776 | 0.018603 | 0.019386 | 0.020091 | 0.020846 | 0.021734 | 0.022522 | 0.023005 | 0.022957 | 0.022908 | 0.02286 | 0.022812 | 0.022764 | 0.022716 | 0.022668 | 0.02262 | 0.022572 | 0.022524 | 0.022476 | 32877.5686 | 7348.3186 | 10148.7186 | 2268.2948 | 324185.9564 | 420216.6968 | 1536836.5816 | 338317.21
| BAS033-139662229 | 68 | BAS033 | BAS | South | 1236293.7969 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 1.6162 | 1.6267 | 1.6373 | 1.6479 | 1.6585 | 1.6588 | 1.6591 | 1.6594 | 1.6597 | 1.66 | 1.6603 | 1.6606 | 1.6609 | 1.6612 | 1.6615 | 1.6618 | 1.6621 | 1.6624 | 1.6626 | 1.6629 | 0.027949 | 0.026509 | 0.027752 | 0.028906 | 0.029944 | 0.031139 | 0.032539 | 0.033794 | 0.034597 | 0.034603 | 0.034609 | 0.034616 | 0.034622 | 0.034628 | 0.034634 | 0.03464 | 0.034646 | 0.034652 | 0.034659 | 0.034665 | 32877.5686 | 7348.3186 | 15314.9264 | 3422.9709 | 537254.3843 | 696400.5018 | 1290183.7969 | 560673.2826
| BAS033-140150122 | 24 | BAS033 | BAS | South | 436338.9872 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.099675 | 0.10043 | 0.10118 | 0.10193 | 0.10268 | 0.10246 | 0.10224 | 0.10202 | 0.10181 | 0.10159 | 0.10137 | 0.10115 | 0.10093 | 0.10072 | 0.1005 | 0.10028 | 0.10006 | 0.099845 | 0.099627 | 0.099409 | 0.0017237 | 0.0016365 | 0.0017149 | 0.0017879 | 0.0018538 | 0.0019234 | 0.0020052 | 0.0020778 | 0.0021222 | 0.0021177 | 0.0021131 | 0.0021086 | 0.002104 | 0.0020995 | 0.0020949 | 0.0020904 | 0.0020859 | 0.0020813 | 0.0020768 | 0.0020722 | 32877.5686 | 7348.3186 | 935.9218 | 209.1837 | 21992.4798 | 28507.1178 | 455358.9872 | 22951.1312
| BAS033-142953276 | 33 | BAS033 | BAS | South | 599966.1073 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.69213 | 0.6951 | 0.69806 | 0.70103 | 0.70399 | 0.70685 | 0.70971 | 0.71257 | 0.71543 | 0.71829 | 0.72116 | 0.72402 | 0.72688 | 0.72974 | 0.7326 | 0.73546 | 0.73832 | 0.74118 | 0.74404 | 0.74691 | 0.011969 | 0.011327 | 0.011832 | 0.012297 | 0.01271 | 0.013269 | 0.013919 | 0.014512 | 0.014914 | 0.014973 | 0.015033 | 0.015092 | 0.015152 | 0.015212 | 0.015271 | 0.015331 | 0.015391 | 0.01545 | 0.01551 | 0.01557 | 32877.5686 | 7348.3186 | 6644.5453 | 1485.0927 | 110978.3721 | 143852.5144 | 626118.6073 | 115815.9152
| BAS033-155164312 | 49 | BAS033 | BAS | South | 890858.7654 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.0021946 | 0.0022147 | 0.0022349 | 0.002255 | 0.0022752 | 0.0022738 | 0.0022723 | 0.0022709 | 0.0022694 | 0.002268 | 0.0022666 | 0.0022651 | 0.0022637 | 0.0022622 | 0.0022608 | 0.0022594 | 0.0022579 | 0.0022565 | 0.002255 | 0.0022536 | 3.7952e-05 | 3.609e-05 | 3.7881e-05 | 3.9556e-05 | 4.1078e-05 | 4.2682e-05 | 4.4566e-05 | 4.6247e-05 | 4.7307e-05 | 4.7277e-05 | 4.7247e-05 | 4.7217e-05 | 4.7187e-05 | 4.7157e-05 | 4.7127e-05 | 4.7097e-05 | 4.7067e-05 | 4.7037e-05 | 4.7007e-05 | 4.6977e-05 | 32877.5686 | 7348.3186 | 20.8881 | 4.6686 | 806.7452 | 1045.7201 | 929691.2654 | 841.9112
| BAS033-155176923 | 58 | BAS033 | BAS | South | 1054485.8856 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.7472 | 0.75266 | 0.75812 | 0.76357 | 0.76903 | 0.76766 | 0.76629 | 0.76493 | 0.76356 | 0.76219 | 0.76082 | 0.75945 | 0.75808 | 0.75671 | 0.75535 | 0.75398 | 0.75261 | 0.75124 | 0.74987 | 0.7485 | 0.012922 | 0.012265 | 0.01285 | 0.013394 | 0.013885 | 0.01441 | 0.015029 | 0.015578 | 0.015917 | 0.015888 | 0.01586 | 0.015831 | 0.015803 | 0.015774 | 0.015745 | 0.015717 | 0.015688 | 0.01566 | 0.015631 | 0.015603 | 32877.5686 | 7348.3186 | 7023.7364 | 1569.844 | 196030.1221 | 254098.3925 | 1100450.8856 | 204575.0677
| BAS033-155190238 | 125 | BAS033 | BAS | South | 2272598.8914 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.071439 | 0.071954 | 0.072469 | 0.072983 | 0.073498 | 0.073135 | 0.072771 | 0.072408 | 0.072044 | 0.071681 | 0.071317 | 0.070954 | 0.07059 | 0.070227 | 0.069863 | 0.0695 | 0.069137 | 0.068773 | 0.06841 | 0.068046 | 0.0012354 | 0.0011725 | 0.0012283 | 0.0012802 | 0.001327 | 0.0013729 | 0.0014272 | 0.0014746 | 0.0015018 | 0.0014942 | 0.0014866 | 0.0014791 | 0.0014715 | 0.0014639 | 0.0014563 | 0.0014488 | 0.0014412 | 0.0014336 | 0.001426 | 0.0014184 | 32877.5686 | 7348.3186 | 659.7677 | 147.4617 | 57170.912 | 74106.1459 | 2371661.3914 | 59662.9898
| BAS033-155190444 | 40 | BAS033 | BAS | South | 727231.6453 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.010934 | 0.011031 | 0.011127 | 0.011223 | 0.011319 | 0.01131 | 0.0113 | 0.01129 | 0.011281 | 0.011271 | 0.011262 | 0.011252 | 0.011242 | 0.011233 | 0.011223 | 0.011214 | 0.011204 | 0.011194 | 0.011185 | 0.011175 | 0.00018909 | 0.00017975 | 0.0001886 | 0.00019686 | 0.00020437 | 0.0002123 | 0.00022162 | 0.00022993 | 0.00023515 | 0.00023495 | 0.00023475 | 0.00023455 | 0.00023435 | 0.00023415 | 0.00023395 | 0.00023375 | 0.00023355 | 0.00023335 | 0.00023315 | 0.00023295 | 32877.5686 | 7348.3186 | 103.8203 | 23.2044 | 5892.5256 | 7638.0164 | 758931.6453 | 6149.3805
| BAS033-155190566 | 42 | BAS033 | BAS | South | 763593.2275 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.021402 | 0.021601 | 0.021801 | 0.022001 | 0.0222 | 0.022142 | 0.022083 | 0.022024 | 0.021965 | 0.021906 | 0.021847 | 0.021788 | 0.021729 | 0.021671 | 0.021612 | 0.021553 | 0.021494 | 0.021435 | 0.021376 | 0.021317 | 0.00037011 | 0.000352 | 0.00036952 | 0.00038591 | 0.00040082 | 0.00041564 | 0.0004331 | 0.00044852 | 0.00045787 | 0.00045664 | 0.00045541 | 0.00045419 | 0.00045296 | 0.00045173 | 0.00045051 | 0.00044928 | 0.00044805 | 0.00044682 | 0.0004456 | 0.00044437 | 32877.5686 | 7348.3186 | 201.5776 | 45.0537 | 16026.4342 | 20773.8031 | 796878.2275 | 16725.0258
| BAS033-155190689 | 22 | BAS033 | BAS | South | 399977.4049 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.0016421 | 0.0016556 | 0.001669 | 0.0016824 | 0.0016959 | 0.0016939 | 0.001692 | 0.0016901 | 0.0016881 | 0.0016862 | 0.0016843 | 0.0016823 | 0.0016804 | 0.0016785 | 0.0016765 | 0.0016746 | 0.0016727 | 0.0016707 | 0.0016688 | 0.0016669 | 2.8398e-05 | 2.6978e-05 | 2.8289e-05 | 2.9511e-05 | 3.0618e-05 | 3.1798e-05 | 3.3184e-05 | 3.4418e-05 | 3.519e-05 | 3.5149e-05 | 3.5109e-05 | 3.5069e-05 | 3.5028e-05 | 3.4988e-05 | 3.4948e-05 | 3.4908e-05 | 3.4867e-05 | 3.4827e-05 | 3.4787e-05 | 3.4747e-05 | 32877.5686 | 7348.3186 | 15.5351 | 3.4722 | 970.0388 | 1257.3848 | 417412.4049 | 1012.3228
| BAS033-155190801 | 20 | BAS033 | BAS | South | 363615.8226 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00017854 | 0.00018026 | 0.00018197 | 0.00018369 | 0.0001854 | 0.00018501 | 0.00018462 | 0.00018423 | 0.00018384 | 0.00018345 | 0.00018306 | 0.00018267 | 0.00018228 | 0.00018189 | 0.0001815 | 0.00018111 | 0.00018072 | 0.00018033 | 0.00017994 | 0.00017955 | 3.0876e-06 | 2.9374e-06 | 3.0844e-06 | 3.222e-06 | 3.3473e-06 | 3.473e-06 | 3.6209e-06 | 3.7519e-06 | 3.8322e-06 | 3.8241e-06 | 3.816e-06 | 3.8078e-06 | 3.7997e-06 | 3.7916e-06 | 3.7834e-06 | 3.7753e-06 | 3.7672e-06 | 3.7591e-06 | 3.7509e-06 | 3.7428e-06 | 32877.5686 | 7348.3186 | 1.6882 | 0.37732 | 159.7536 | 207.0761 | 379465.8226 | 166.7173
| BAS033-155250207 | 115 | BAS033 | BAS | South | 2090790.9801 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.054334 | 0.054787 | 0.05524 | 0.055693 | 0.056145 | 0.056028 | 0.05591 | 0.055793 | 0.055675 | 0.055558 | 0.05544 | 0.055323 | 0.055205 | 0.055087 | 0.05497 | 0.054852 | 0.054735 | 0.054617 | 0.0545 | 0.054382 | 0.00093962 | 0.00089278 | 0.00093629 | 0.0009769 | 0.0010137 | 0.0010517 | 0.0010965 | 0.0011362 | 0.0011606 | 0.0011581 | 0.0011557 | 0.0011532 | 0.0011508 | 0.0011483 | 0.0011459 | 0.0011434 | 0.001141 | 0.0011385 | 0.0011361 | 0.0011336 | 32877.5686 | 7348.3186 | 511.6247 | 114.351 | 47727.6428 | 61865.5806 | 2181928.4801 | 49808.089
| BAS033-155250324 | 12 | BAS033 | BAS | South | 218169.4936 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 4.2545e-05 | 4.2979e-05 | 4.3413e-05 | 4.3846e-05 | 4.428e-05 | 4.4259e-05 | 4.4238e-05 | 4.4217e-05 | 4.4196e-05 | 4.4175e-05 | 4.4154e-05 | 4.4133e-05 | 4.4112e-05 | 4.4091e-05 | 4.407e-05 | 4.4049e-05 | 4.4028e-05 | 4.4007e-05 | 4.3986e-05 | 4.3965e-05 | 7.3576e-07 | 7.0036e-07 | 7.3583e-07 | 7.6911e-07 | 7.9946e-07 | 8.3082e-07 | 8.6762e-07 | 9.0049e-07 | 9.2128e-07 | 9.2085e-07 | 9.2041e-07 | 9.1997e-07 | 9.1953e-07 | 9.1909e-07 | 9.1866e-07 | 9.1822e-07 | 9.1778e-07 | 9.1734e-07 | 9.1691e-07 | 9.1647e-07 | 32877.5686 | 7348.3186 | 0.40665 | 0.090889 | 23.075 | 29.9103 | 227679.4936 | 24.0808
| BAS033-177750890 | 210 | BAS033 | BAS | South | 3817966.1376 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 39.7469 | 39.9269 | 40.1068 | 40.2868 | 40.4668 | 40.5414 | 40.6161 | 40.6907 | 40.7654 | 40.8401 | 40.9147 | 40.9894 | 41.064 | 41.1387 | 41.2134 | 41.288 | 41.3627 | 41.4373 | 41.512 | 41.5867 | 0.68737 | 0.65063 | 0.6798 | 0.70667 | 0.73061 | 0.76103 | 0.79658 | 0.82868 | 0.84977 | 0.85133 | 0.85288 | 0.85444 | 0.856 | 0.85755 | 0.85911 | 0.86067 | 0.86222 | 0.86378 | 0.86533 | 0.86689 | 32877.5686 | 7348.3186 | 377436.3927 | 84359.1239 | 535417.1896 | 694019.0912 | 3984391.1376 | 558756.0047
| BAS033-193428051 | 539 | BAS033 | BAS | South | 9799446.4199 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 332.2525 | 333.8779 | 335.5033 | 337.1287 | 338.7541 | 339.1172 | 339.4802 | 339.8432 | 340.2062 | 340.5693 | 340.9323 | 341.2953 | 341.6583 | 342.0213 | 342.3844 | 342.7474 | 343.1104 | 343.4734 | 343.8364 | 344.1995 | 5.7458 | 5.4407 | 5.6867 | 5.9136 | 6.1161 | 6.3658 | 6.6581 | 6.921 | 7.0917 | 7.0993 | 7.1069 | 7.1144 | 7.122 | 7.1296 | 7.1371 | 7.1447 | 7.1523 | 7.1598 | 7.1674 | 7.175 | 32877.5686 | 7348.3186 | 3145958.1407 | 703139.0661 | 21742083.5463 | 28182548.7811 | 10226603.9199 | 22689820.1484
| BAS033-193428083 | 356 | BAS033 | BAS | South | 6472361.6428 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 2.7082 | 2.7279 | 2.7477 | 2.7675 | 2.7873 | 2.7784 | 2.7696 | 2.7608 | 2.7519 | 2.7431 | 2.7342 | 2.7254 | 2.7165 | 2.7077 | 2.6989 | 2.69 | 2.6812 | 2.6723 | 2.6635 | 2.6546 | 0.046834 | 0.044453 | 0.046573 | 0.048545 | 0.050323 | 0.052156 | 0.054319 | 0.056223 | 0.057365 | 0.05718 | 0.056996 | 0.056812 | 0.056627 | 0.056443 | 0.056259 | 0.056074 | 0.05589 | 0.055706 | 0.055521 | 0.055337 | 32877.5686 | 7348.3186 | 25264.2274 | 5646.6947 | 1024639.1769 | 1328158.9837 | 6754491.6428 | 1069303.16
| BAS033-193428108 | 305 | BAS033 | BAS | South | 5545141.2951 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 5.8177 | 5.8651 | 5.9125 | 5.9599 | 6.0073 | 6.0015 | 5.9957 | 5.9898 | 5.984 | 5.9782 | 5.9724 | 5.9665 | 5.9607 | 5.9549 | 5.9491 | 5.9433 | 5.9374 | 5.9316 | 5.9258 | 5.92 | 0.10061 | 0.095575 | 0.10022 | 0.10454 | 0.10846 | 0.11266 | 0.11759 | 0.12198 | 0.12474 | 0.12462 | 0.1245 | 0.12438 | 0.12425 | 0.12413 | 0.12401 | 0.12389 | 0.12377 | 0.12365 | 0.12353 | 0.1234 | 32877.5686 | 7348.3186 | 55082.2628 | 12311.1908 | 997950.9746 | 1293565.1712 | 5786853.7951 | 1041451.62
| BAS033-193428622 | 445 | BAS033 | BAS | South | 8090452.0535 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 197.1821 | 198.1483 | 199.1144 | 200.0806 | 201.0467 | 201.3966 | 201.7465 | 202.0964 | 202.4463 | 202.7962 | 203.1461 | 203.4961 | 203.846 | 204.1959 | 204.5458 | 204.8957 | 205.2456 | 205.5955 | 205.9454 | 206.2953 | 3.41 | 3.2289 | 3.3749 | 3.5096 | 3.6298 | 3.7806 | 3.9568 | 4.1157 | 4.2201 | 4.2274 | 4.2347 | 4.242 | 4.2493 | 4.2565 | 4.2638 | 4.2711 | 4.2784 | 4.2857 | 4.293 | 4.3003 | 32877.5686 | 7348.3186 | 1873752.7964 | 418794.1264 | 8225980.93 | 10662690.553 | 8443114.5535 | 8584551.1286
| BAS033-78747898 | 6 | BAS033 | BAS | South | 109084.7468 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00092916 | 0.00093452 | 0.00093988 | 0.00094524 | 0.0009506 | 0.00095564 | 0.00096068 | 0.00096572 | 0.00097076 | 0.0009758 | 0.00098084 | 0.00098588 | 0.00099092 | 0.00099596 | 0.001001 | 0.001006 | 0.0010111 | 0.0010161 | 0.0010212 | 0.0010262 | 1.6069e-05 | 1.5229e-05 | 1.5931e-05 | 1.658e-05 | 1.7163e-05 | 1.7939e-05 | 1.8841e-05 | 1.9667e-05 | 2.0236e-05 | 2.0341e-05 | 2.0446e-05 | 2.0551e-05 | 2.0656e-05 | 2.0761e-05 | 2.0866e-05 | 2.0971e-05 | 2.1076e-05 | 2.1181e-05 | 2.1286e-05 | 2.1392e-05 | 32877.5686 | 7348.3186 | 9.0233 | 2.0168 | 109.5504 | 142.0016 | 113839.7468 | 114.3257
| BAS033-78747960 | 7 | BAS033 | BAS | South | 127265.5379 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.0030851 | 0.0031008 | 0.0031165 | 0.0031323 | 0.003148 | 0.0031585 | 0.003169 | 0.0031796 | 0.0031901 | 0.0032007 | 0.0032112 | 0.0032218 | 0.0032323 | 0.0032429 | 0.0032534 | 0.0032639 | 0.0032745 | 0.003285 | 0.0032956 | 0.0033061 | 5.3353e-05 | 5.053e-05 | 5.2825e-05 | 5.4943e-05 | 5.6835e-05 | 5.9291e-05 | 6.2153e-05 | 6.4753e-05 | 6.65e-05 | 6.672e-05 | 6.6939e-05 | 6.7159e-05 | 6.7379e-05 | 6.7599e-05 | 6.7819e-05 | 6.8038e-05 | 6.8258e-05 | 6.8478e-05 | 6.8698e-05 | 6.8918e-05 | 32877.5686 | 7348.3186 | 29.5872 | 6.6129 | 978.5183 | 1268.3761 | 132813.0379 | 1021.1719
| BAS033-78748025 | 81 | BAS033 | BAS | South | 1472644.0816 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 1.4289 | 1.4349 | 1.4408 | 1.4468 | 1.4528 | 1.4552 | 1.4576 | 1.46 | 1.4624 | 1.4648 | 1.4672 | 1.4696 | 1.472 | 1.4744 | 1.4768 | 1.4792 | 1.4816 | 1.484 | 1.4864 | 1.4888 | 0.024711 | 0.023382 | 0.024422 | 0.025379 | 0.02623 | 0.027316 | 0.028587 | 0.029733 | 0.030484 | 0.030534 | 0.030584 | 0.030635 | 0.030685 | 0.030735 | 0.030785 | 0.030835 | 0.030885 | 0.030935 | 0.030985 | 0.031035 | 32877.5686 | 7348.3186 | 13539.0757 | 3026.0584 | 374789.1766 | 485809.6618 | 1536836.5816 | 391126.2227
| BAS033-78748089 | 26 | BAS033 | BAS | South | 472700.5694 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.16494 | 0.16577 | 0.16659 | 0.16742 | 0.16825 | 0.16867 | 0.16908 | 0.1695 | 0.16991 | 0.17033 | 0.17075 | 0.17116 | 0.17158 | 0.17199 | 0.17241 | 0.17282 | 0.17324 | 0.17366 | 0.17407 | 0.17449 | 0.0028524 | 0.0027013 | 0.0028237 | 0.0029368 | 0.0030377 | 0.0031662 | 0.0033161 | 0.0034519 | 0.0035419 | 0.0035506 | 0.0035593 | 0.0035679 | 0.0035766 | 0.0035853 | 0.0035939 | 0.0036026 | 0.0036113 | 0.0036199 | 0.0036286 | 0.0036373 | 32877.5686 | 7348.3186 | 1574.093 | 351.8185 | 41446.7478 | 53724.1516 | 493305.5694 | 43253.41
| BAS033-95730010 | 21 | BAS033 | BAS | South | 381796.6138 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.0071446 | 0.0071964 | 0.0072483 | 0.0073001 | 0.007352 | 0.0073274 | 0.0073027 | 0.0072781 | 0.0072534 | 0.0072288 | 0.0072041 | 0.0071795 | 0.0071549 | 0.0071302 | 0.0071056 | 0.0070809 | 0.0070563 | 0.0070317 | 0.007007 | 0.0069824 | 0.00012356 | 0.00011727 | 0.00012286 | 0.00012805 | 0.00013274 | 0.00013755 | 0.00014322 | 0.00014822 | 0.0001512 | 0.00015069 | 0.00015017 | 0.00014966 | 0.00014915 | 0.00014863 | 0.00014812 | 0.00014761 | 0.00014709 | 0.00014658 | 0.00014606 | 0.00014555 | 32877.5686 | 7348.3186 | 66.5757 | 14.88 | 7942.9105 | 10295.7686 | 398439.1138 | 8289.1416
| BAS033-96330036 | 65 | BAS033 | BAS | South | 1181751.4235 | 0.00062118 | 0.00058533 | 0.00060883 | 0.00063006 | 0.00064852 | 0.00067427 | 0.00070447 | 0.00073151 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.00074876 | 0.34419 | 0.34694 | 0.3497 | 0.35245 | 0.3552 | 0.35444 | 0.35368 | 0.35292 | 0.35217 | 0.35141 | 0.35065 | 0.34989 | 0.34913 | 0.34837 | 0.34761 | 0.34686 | 0.3461 | 0.34534 | 0.34458 | 0.34382 | 0.0059523 | 0.0056537 | 0.0059273 | 0.0061823 | 0.006413 | 0.0066535 | 0.0069366 | 0.0071874 | 0.007341 | 0.0073252 | 0.0073094 | 0.0072936 | 0.0072778 | 0.007262 | 0.0072462 | 0.0072304 | 0.0072145 | 0.0071987 | 0.0071829 | 0.0071671 | 32877.5686 | 7348.3186 | 3236.6226 | 723.4031 | 96343.1005 | 124881.9655 | 1233263.9235 | 100542.6926
| BAS034-15416250 | 195 | BAS034 | BAS | South | 3545254.2706 | 0.00076938 | 0.00077646 | 0.00079191 | 0.00081002 | 0.00082566 | 0.0008468 | 0.00087163 | 0.00089251 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32877.5686 | 7348.3186 | 0 | 0 | 0 | 0 | 3699791.7706 | 0
| BAS034-199849971 | 226 | BAS034 | BAS | South | 4108858.7957 | 0.00076938 | 0.00077646 | 0.00079191 | 0.00081002 | 0.00082566 | 0.0008468 | 0.00087163 | 0.00089251 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0.00090602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32877.5686 | 7348.3186 | 0 | 0 | 482460.9337 | 625376.0717 | 4287963.7957 | 503491.3876
| BBD013-15437974 | 200 | BBD013 | BBD | North | 4713265.2384 | 0.037003 | 0.040633 | 0.041322 | 0.041644 | 0.041401 | 0.041343 | 0.04199 | 0.042886 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 1.7781 | 1.7946 | 1.811 | 1.8275 | 1.8439 | 1.8415 | 1.839 | 1.8365 | 1.8341 | 1.8316 | 1.8292 | 1.8267 | 1.8242 | 1.8218 | 1.8193 | 1.8169 | 1.8144 | 1.8119 | 1.8095 | 1.807 | 1.8318 | 2.0301 | 2.0834 | 2.1187 | 2.1253 | 2.1195 | 2.1498 | 2.1927 | 2.1803 | 2.1773 | 2.1744 | 2.1715 | 2.1685 | 2.1656 | 2.1627 | 2.1598 | 2.1568 | 2.1539 | 2.151 | 2.1481 | 27621.832 | 1979.5401 | 847224.711 | 60717.0195 | 935777.3834 | 935777.3834 | 4713265.2384 | 935777.3834
| BBD013-24614080 | 162 | BBD013 | BBD | North | 3817744.8431 | 0.037003 | 0.040633 | 0.041322 | 0.041644 | 0.041401 | 0.041343 | 0.04199 | 0.042886 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.042699 | 0.64313 | 0.6481 | 0.65307 | 0.65804 | 0.66302 | 0.66289 | 0.66277 | 0.66265 | 0.66252 | 0.6624 | 0.66228 | 0.66215 | 0.66203 | 0.6619 | 0.66178 | 0.66166 | 0.66153 | 0.66141 | 0.66129 | 0.66116 | 0.66253 | 0.73315 | 0.75129 | 0.76291 | 0.7642 | 0.76298 | 0.77477 | 0.79116 | 0.78757 | 0.78742 | 0.78727 | 0.78713 | 0.78698 | 0.78683 | 0.78669 | 0.78654 | 0.78639 | 0.78624 | 0.7861 | 0.78595 | 27621.832 | 1979.5401 | 306720.5646 | 21981.3684 | 408812.8126 | 408812.8126 | 3817744.8431 | 408812.8126
| BBD014-15437952 | 127 | BBD014 | BBD | North | 2992923.4264 | 0.044512 | 0.04427 | 0.043601 | 0.042863 | 0.041927 | 0.041137 | 0.040734 | 0.04048 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.1366 | 0.13793 | 0.13925 | 0.14057 | 0.14189 | 0.14172 | 0.14155 | 0.14138 | 0.14121 | 0.14104 | 0.14087 | 0.14069 | 0.14052 | 0.14035 | 0.14018 | 0.14001 | 0.13984 | 0.13967 | 0.13949 | 0.13932 | 0.16928 | 0.16999 | 0.16903 | 0.16775 | 0.16563 | 0.16231 | 0.16052 | 0.15933 | 0.15624 | 0.15605 | 0.15586 | 0.15567 | 0.15548 | 0.15529 | 0.1551 | 0.15491 | 0.15472 | 0.15453 | 0.15434 | 0.15415 | 27621.832 | 1979.5401 | 64041.7698 | 4589.6034 | 52676.8764 | 52676.8764 | 2992923.4264 | 52676.8764
| BBD014-160682204 | 90 | BBD014 | BBD | North | 2120969.3573 | 0.044512 | 0.04427 | 0.043601 | 0.042863 | 0.041927 | 0.041137 | 0.040734 | 0.04048 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.0014089 | 0.0014093 | 0.0014096 | 0.00141 | 0.0014103 | 0.0014101 | 0.0014098 | 0.0014095 | 0.0014092 | 0.0014089 | 0.0014086 | 0.0014084 | 0.0014081 | 0.0014078 | 0.0014075 | 0.0014072 | 0.001407 | 0.0014067 | 0.0014064 | 0.0014061 | 0.0017459 | 0.0017369 | 0.0017111 | 0.0016825 | 0.0016462 | 0.0016149 | 0.0015987 | 0.0015884 | 0.0015592 | 0.0015589 | 0.0015585 | 0.0015582 | 0.0015579 | 0.0015576 | 0.0015573 | 0.001557 | 0.0015567 | 0.0015564 | 0.0015561 | 0.0015557 | 27621.832 | 1979.5401 | 643.8157 | 46.1396 | 4320.0304 | 4320.0304 | 2120969.3573 | 4320.0304
| BBD014-162435599 | 133 | BBD014 | BBD | North | 3134321.3835 | 0.044512 | 0.04427 | 0.043601 | 0.042863 | 0.041927 | 0.041137 | 0.040734 | 0.04048 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27621.832 | 1979.5401 | 0 | 0 | 72453.0497 | 72453.0497 | 3134321.3835 | 72453.0497
| BBD014-96325732 | 0 | BBD014 | BBD | North | 0 | 0.044512 | 0.04427 | 0.043601 | 0.042863 | 0.041927 | 0.041137 | 0.040734 | 0.04048 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.24633 | 0.24896 | 0.25159 | 0.25422 | 0.25685 | 0.25585 | 0.25484 | 0.25384 | 0.25283 | 0.25183 | 0.25082 | 0.24982 | 0.24881 | 0.24781 | 0.2468 | 0.2458 | 0.24479 | 0.24379 | 0.24278 | 0.24178 | 0.30525 | 0.30683 | 0.30539 | 0.30336 | 0.29981 | 0.29301 | 0.289 | 0.28606 | 0.27974 | 0.27862 | 0.27751 | 0.2764 | 0.27529 | 0.27418 | 0.27307 | 0.27195 | 0.27084 | 0.26973 | 0.26862 | 0.26751 | 27621.832 | 1979.5401 | 0 | 0 | 0 | 0 | 0 | 0
| BBD014-96325958 | 28 | BBD014 | BBD | North | 659857.1334 | 0.044512 | 0.04427 | 0.043601 | 0.042863 | 0.041927 | 0.041137 | 0.040734 | 0.04048 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27621.832 | 1979.5401 | 0 | 0 | 0 | 0 | 659857.1334 | 0
| BBD014-97325263 | 228 | BBD014 | BBD | North | 5373122.3717 | 0.044512 | 0.04427 | 0.043601 | 0.042863 | 0.041927 | 0.041137 | 0.040734 | 0.04048 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 0.039742 | 1.7128 | 1.7284 | 1.7441 | 1.7598 | 1.7755 | 1.7727 | 1.7698 | 1.7669 | 1.764 | 1.7612 | 1.7583 | 1.7554 | 1.7525 | 1.7497 | 1.7468 | 1.7439 | 1.741 | 1.7382 | 1.7353 | 1.7324 | 2.1225 | 2.1303 | 2.1171 | 2.1 | 2.0725 | 2.0302 | 2.007 | 1.9912 | 1.9518 | 1.9486 | 1.9454 | 1.9422 | 1.939 | 1.9359 | 1.9327 | 1.9295 | 1.9263 | 1.9231 | 1.9199 | 1.9168 | 27621.832 | 1979.5401 | 800011.9616 | 57333.481 | 1483591.0564 | 1483591.0564 | 5373122.3717 | 1483591.0564
| BBD021-15437930 | 27 | BBD021 | BBD | North | 636290.8072 | 0.020203 | 0.020449 | 0.020571 | 0.020578 | 0.020343 | 0.020154 | 0.020365 | 0.020684 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.0015363 | 0.0015511 | 0.001566 | 0.0015809 | 0.0015958 | 0.0015938 | 0.0015919 | 0.00159 | 0.0015881 | 0.0015862 | 0.0015842 | 0.0015823 | 0.0015804 | 0.0015785 | 0.0015765 | 0.0015746 | 0.0015727 | 0.0015708 | 0.0015688 | 0.0015669 | 0.00086409 | 0.00088304 | 0.00089685 | 0.0009057 | 0.00090377 | 0.0008943 | 0.00090257 | 0.00091558 | 0.00090624 | 0.00090514 | 0.00090404 | 0.00090294 | 0.00090185 | 0.00090075 | 0.00089965 | 0.00089856 | 0.00089746 | 0.00089636 | 0.00089526 | 0.00089417 | 27621.832 | 1979.5401 | 358.5672 | 25.697 | 2653.3991 | 2653.3991 | 636290.8072 | 2653.3991
| BBD021-24611491 | 107 | BBD021 | BBD | North | 2521596.9025 | 0.020203 | 0.020449 | 0.020571 | 0.020578 | 0.020343 | 0.020154 | 0.020365 | 0.020684 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 1.2433 | 1.2548 | 1.2663 | 1.2777 | 1.2892 | 1.2869 | 1.2845 | 1.2822 | 1.2798 | 1.2775 | 1.2752 | 1.2728 | 1.2705 | 1.2681 | 1.2658 | 1.2635 | 1.2611 | 1.2588 | 1.2564 | 1.2541 | 0.69932 | 0.71434 | 0.72518 | 0.73201 | 0.73014 | 0.72205 | 0.72828 | 0.73832 | 0.73034 | 0.729 | 0.72767 | 0.72633 | 0.725 | 0.72366 | 0.72233 | 0.72099 | 0.71966 | 0.71832 | 0.71698 | 0.71565 | 27621.832 | 1979.5401 | 288862.4431 | 20701.5522 | 724244.6545 | 724244.6545 | 2521596.9025 | 724244.6545
| BBD021-24613487 | 121 | BBD021 | BBD | North | 2851525.4692 | 0.020203 | 0.020449 | 0.020571 | 0.020578 | 0.020343 | 0.020154 | 0.020365 | 0.020684 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 7.0207 | 7.0782 | 7.1357 | 7.1932 | 7.2508 | 7.2353 | 7.2198 | 7.2043 | 7.1888 | 7.1733 | 7.1579 | 7.1424 | 7.1269 | 7.1114 | 7.0959 | 7.0804 | 7.065 | 7.0495 | 7.034 | 7.0185 | 3.9489 | 4.0295 | 4.0866 | 4.121 | 4.1065 | 4.0597 | 4.0934 | 4.1485 | 4.1023 | 4.0935 | 4.0846 | 4.0758 | 4.067 | 4.0581 | 4.0493 | 4.0405 | 4.0316 | 4.0228 | 4.014 | 4.0051 | 27621.832 | 1979.5401 | 1623020.4067 | 116315.0229 | 1488631.6545 | 1488631.6545 | 2851525.4692 | 1488631.6545
| BBD021-40480035 | 109 | BBD021 | BBD | North | 2568729.5549 | 0.020203 | 0.020449 | 0.020571 | 0.020578 | 0.020343 | 0.020154 | 0.020365 | 0.020684 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 0.020498 | 1.6453 | 1.6582 | 1.6712 | 1.6841 | 1.6971 | 1.6933 | 1.6895 | 1.6857 | 1.6819 | 1.6781 | 1.6743 | 1.6705 | 1.6667 | 1.6629 | 1.6591 | 1.6553 | 1.6515 | 1.6478 | 1.644 | 1.6402 | 0.92541 | 0.94401 | 0.95708 | 0.96485 | 0.96115 | 0.9501 | 0.95789 | 0.97069 | 0.95978 | 0.95762 | 0.95545 | 0.95329 | 0.95112 | 0.94896 | 0.94679 | 0.94462 | 0.94246 | 0.94029 | 0.93813 | 0.93596 | 27621.832 | 1979.5401 | 379758.3502 | 27215.6783 | 1512385.1705 | 1512385.1705 | 2568729.5549 | 1512385.1705
| BBD022-15437908 | 28 | BBD022 | BBD | North | 659857.1334 | 0.6763 | 0.6806 | 0.6816 | 0.6786 | 0.6693 | 0.663 | 0.667 | 0.6733 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.665 | 0.049911 | 0.050383 | 0.050855 | 0.051327 | 0.051799 | 0.051682 | 0.051565 | 0.051447 | 0.05133 | 0.051213 | 0.051096 | 0.050979 | 0.050861 | 0.050744 | 0.050627 | 0.05051 | 0.050393 | 0.050275 | 0.050158 | 0.050041 | 0.93974 | 0.95465 | 0.96501 | 0.96968 | 0.96519 | 0.95394 | 0.95752 | 0.96436 | 0.95031 | 0.94814 | 0.94597 | 0.9438 | 0.94163 | 0.93946 | 0.93729 | 0.93512 | 0.93295 | 0.93078 | 0.92861 | 0.92644 | 27621.832 | 1979.5401 | 378827.3595 | 27148.9581 | 97126.3411 | 97126.3411 | 659857.1334 | 97126.3411
| BET001-143534818 | 32 | BET001 | BETS | North | 754122.4381 | 0.0012824 | 0.0012964 | 0.0013015 | 0.0013063 | 0.0013059 | 0.0013092 | 0.0013193 | 0.0013312 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.19697 | 0.19826 | 0.19956 | 0.20085 | 0.20215 | 0.20245 | 0.20275 | 0.20306 | 0.20336 | 0.20366 | 0.20396 | 0.20427 | 0.20457 | 0.20487 | 0.20517 | 0.20548 | 0.20578 | 0.20608 | 0.20638 | 0.20669 | 0.0070321 | 0.0071559 | 0.0072309 | 0.0073044 | 0.0073495 | 0.0073791 | 0.0074472 | 0.0075257 | 0.0075809 | 0.0075922 | 0.0076035 | 0.0076148 | 0.0076261 | 0.0076373 | 0.0076486 | 0.0076599 | 0.0076712 | 0.0076824 | 0.0076937 | 0.007705 | 34629.4409 | 7143.0873 | 3740.5631 | 771.5738 | 71338.2388 | 71338.2388 | 754122.4381 | 71338.2388
| BET001-15424260 | 258 | BET001 | BETS | North | 6080112.1575 | 0.0012824 | 0.0012964 | 0.0013015 | 0.0013063 | 0.0013059 | 0.0013092 | 0.0013193 | 0.0013312 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 134.5314 | 135.441 | 136.3505 | 137.2601 | 138.1697 | 138.5685 | 138.9673 | 139.3662 | 139.765 | 140.1639 | 140.5627 | 140.9615 | 141.3604 | 141.7592 | 142.1581 | 142.5569 | 142.9557 | 143.3546 | 143.7534 | 144.1523 | 4.803 | 4.8884 | 4.9406 | 4.9917 | 5.0234 | 5.0507 | 5.1043 | 5.1652 | 5.2102 | 5.2251 | 5.24 | 5.2549 | 5.2697 | 5.2846 | 5.2995 | 5.3143 | 5.3292 | 5.3441 | 5.3589 | 5.3738 | 34629.4409 | 7143.0873 | 2574394.5683 | 531025.7601 | 2300439.0463 | 2300439.0463 | 6080112.1575 | 2300439.0463
| BET001-163510183 | 48 | BET001 | BETS | North | 1131183.6572 | 0.0012824 | 0.0012964 | 0.0013015 | 0.0013063 | 0.0013059 | 0.0013092 | 0.0013193 | 0.0013312 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 4.9007 | 4.9311 | 4.9615 | 4.9919 | 5.0222 | 5.0353 | 5.0483 | 5.0613 | 5.0743 | 5.0874 | 5.1004 | 5.1134 | 5.1264 | 5.1395 | 5.1525 | 5.1655 | 5.1785 | 5.1916 | 5.2046 | 5.2176 | 0.17496 | 0.17798 | 0.17978 | 0.18154 | 0.18259 | 0.18353 | 0.18543 | 0.18758 | 0.18916 | 0.18965 | 0.19014 | 0.19062 | 0.19111 | 0.19159 | 0.19208 | 0.19256 | 0.19305 | 0.19353 | 0.19402 | 0.19451 | 34629.4409 | 7143.0873 | 93468.9675 | 19280.0397 | 681382.0895 | 681382.0895 | 1131183.6572 | 681382.0895
| BET001-163510254 | 16 | BET001 | BETS | North | 377061.2191 | 0.0012824 | 0.0012964 | 0.0013015 | 0.0013063 | 0.0013059 | 0.0013092 | 0.0013193 | 0.0013312 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 6.8985 | 6.9502 | 7.0019 | 7.0536 | 7.1053 | 7.1293 | 7.1532 | 7.1771 | 7.201 | 7.2249 | 7.2488 | 7.2727 | 7.2967 | 7.3206 | 7.3445 | 7.3684 | 7.3923 | 7.4162 | 7.4401 | 7.4641 | 0.24628 | 0.25085 | 0.25371 | 0.25652 | 0.25833 | 0.25985 | 0.26274 | 0.266 | 0.26844 | 0.26934 | 0.27023 | 0.27112 | 0.27201 | 0.2729 | 0.27379 | 0.27468 | 0.27558 | 0.27647 | 0.27736 | 0.27825 | 34629.4409 | 7143.0873 | 132647.9629 | 27361.5732 | 158335.037 | 158335.037 | 377061.2191 | 158335.037
| BET001-163979859 | 10 | BET001 | BETS | North | 235663.2619 | 0.0012824 | 0.0012964 | 0.0013015 | 0.0013063 | 0.0013059 | 0.0013092 | 0.0013193 | 0.0013312 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.001339 | 0.37104 | 0.37386 | 0.37669 | 0.37951 | 0.38234 | 0.38333 | 0.38432 | 0.38531 | 0.3863 | 0.3873 | 0.38829 | 0.38928 | 0.39027 | 0.39126 | 0.39225 | 0.39325 | 0.39424 | 0.39523 | 0.39622 | 0.39721 | 0.013247 | 0.013494 | 0.013649 | 0.013802 | 0.013901 | 0.013972 | 0.014116 | 0.01428 | 0.014401 | 0.014438 | 0.014475 | 0.014512 | 0.014549 | 0.014586 | 0.014623 | 0.01466 | 0.014697 | 0.014734 | 0.014771 | 0.014808 | 34629.4409 | 7143.0873 | 7109.6188 | 1466.516 | 46908.5651 | 46908.5651 | 235663.2619 | 46908.5651
| BET002-147836095 | 151 | BET002 | BETS | North | 3558515.255 | 0.0010027 | 0.0010138 | 0.0010212 | 0.0010271 | 0.0010434 | 0.001074 | 0.0011077 | 0.0011383 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34629.4409 | 7143.0873 | 0 | 0 | 0 | 0 | 3558515.255 | 0
| BET002-15424310 | 93 | BET002 | BETS | North | 2191668.3358 | 0.0010027 | 0.0010138 | 0.0010212 | 0.0010271 | 0.0010434 | 0.001074 | 0.0011077 | 0.0011383 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0.0011585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34629.4409 | 7143.0873 | 0 | 0 | 0 | 0 | 2191668.3358 | 0
| BET003-15424094 | 59 | BET003 | BETS | North | 1390413.2453 | 0.004136 | 0.0041511 | 0.0041858 | 0.0042054 | 0.0042251 | 0.0042704 | 0.0043505 | 0.0044109 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.004435 | 0.76827 | 0.7723 | 0.77634 | 0.78037 | 0.78441 | 0.78574 | 0.78708 | 0.78841 | 0.78974 | 0.79108 | 0.79241 | 0.79374 | 0.79508 | 0.79641 | 0.79774 | 0.79908 | 0.80041 | 0.80174 | 0.80308 | 0.80441 | 0.088462 | 0.089251 | 0.090469 | 0.091366 | 0.092267 | 0.093415 | 0.095328 | 0.096816 | 0.097511 | 0.097675 | 0.09784 | 0.098005 | 0.098169 | 0.098334 | 0.098499 | 0.098663 | 0.098828 | 0.098993 | 0.099157 | 0.099322 | 34629.4409 | 7143.0873 | 47696.9342 | 9838.5465 | 47888.3084 | 47888.3084 | 1390413.2453 | 47888.3084
| BET004-112026510 | 35 | BET004 | BETS | North | 824821.4167 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.61176 | 0.6161 | 0.62043 | 0.62477 | 0.62911 | 0.63094 | 0.63276 | 0.63459 | 0.63642 | 0.63824 | 0.64007 | 0.6419 | 0.64373 | 0.64555 | 0.64738 | 0.64921 | 0.65103 | 0.65286 | 0.65469 | 0.65651 | 0.024402 | 0.024922 | 0.025287 | 0.025685 | 0.025958 | 0.02618 | 0.026642 | 0.027143 | 0.027573 | 0.027652 | 0.027732 | 0.027811 | 0.02789 | 0.027969 | 0.028048 | 0.028127 | 0.028206 | 0.028286 | 0.028365 | 0.028444 | 34629.4409 | 7143.0873 | 13459.3326 | 2776.2847 | 210506.6463 | 210506.6463 | 824821.4167 | 210506.6463
| BET004-15424334 | 205 | BET004 | BETS | North | 4831096.8693 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 65.9867 | 66.3652 | 66.7436 | 67.1221 | 67.5006 | 67.8313 | 68.162 | 68.4927 | 68.8234 | 69.1541 | 69.4848 | 69.8156 | 70.1463 | 70.477 | 70.8077 | 71.1384 | 71.4691 | 71.7998 | 72.1305 | 72.4612 | 2.6321 | 2.6845 | 2.7202 | 2.7594 | 2.7852 | 2.8145 | 2.8699 | 2.9296 | 2.9818 | 2.9961 | 3.0105 | 3.0248 | 3.0391 | 3.0535 | 3.0678 | 3.0821 | 3.0964 | 3.1108 | 3.1251 | 3.1394 | 34629.4409 | 7143.0873 | 1459931.0323 | 301143.0321 | 1579430.1966 | 1579430.1966 | 4831096.8693 | 1579430.1966
| BET004-163616866 | 9 | BET004 | BETS | North | 212096.9357 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.35139 | 0.3539 | 0.35642 | 0.35894 | 0.36145 | 0.36232 | 0.3632 | 0.36407 | 0.36494 | 0.36581 | 0.36668 | 0.36755 | 0.36843 | 0.3693 | 0.37017 | 0.37104 | 0.37191 | 0.37278 | 0.37366 | 0.37453 | 0.014016 | 0.014316 | 0.014526 | 0.014756 | 0.014914 | 0.015034 | 0.015292 | 0.015572 | 0.015811 | 0.015849 | 0.015887 | 0.015925 | 0.015962 | 0.016 | 0.016038 | 0.016076 | 0.016113 | 0.016151 | 0.016189 | 0.016227 | 34629.4409 | 7143.0873 | 7713.3205 | 1591.0428 | 34900.6809 | 34900.6809 | 212096.9357 | 34900.6809
| BET004-164487583 | 8 | BET004 | BETS | North | 188530.6095 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.035575 | 0.035782 | 0.035989 | 0.036196 | 0.036403 | 0.036471 | 0.036539 | 0.036607 | 0.036675 | 0.036743 | 0.036811 | 0.036879 | 0.036947 | 0.037015 | 0.037082 | 0.03715 | 0.037218 | 0.037286 | 0.037354 | 0.037422 | 0.001419 | 0.0014474 | 0.0014668 | 0.001488 | 0.001502 | 0.0015133 | 0.0015384 | 0.0015658 | 0.001589 | 0.0015919 | 0.0015949 | 0.0015978 | 0.0016007 | 0.0016037 | 0.0016066 | 0.0016096 | 0.0016125 | 0.0016154 | 0.0016184 | 0.0016213 | 34629.4409 | 7143.0873 | 775.2908 | 159.9209 | 19958.5148 | 19958.5148 | 188530.6095 | 19958.5148
| BET004-164487758 | 5 | BET004 | BETS | North | 117831.631 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.046905 | 0.047242 | 0.047579 | 0.047916 | 0.048253 | 0.04837 | 0.048487 | 0.048603 | 0.04872 | 0.048837 | 0.048954 | 0.049071 | 0.049188 | 0.049305 | 0.049422 | 0.049539 | 0.049656 | 0.049773 | 0.04989 | 0.050007 | 0.001871 | 0.001911 | 0.0019391 | 0.0019698 | 0.001991 | 0.002007 | 0.0020415 | 0.0020789 | 0.0021108 | 0.0021159 | 0.002121 | 0.0021261 | 0.0021311 | 0.0021362 | 0.0021413 | 0.0021463 | 0.0021514 | 0.0021565 | 0.0021615 | 0.0021666 | 34629.4409 | 7143.0873 | 1029.753 | 212.4093 | 10354.0961 | 10354.0961 | 117831.631 | 10354.0961
| BET004-24611449 | 253 | BET004 | BETS | North | 5962280.5265 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 47.3211 | 47.5879 | 47.8548 | 48.1216 | 48.3885 | 48.4588 | 48.529 | 48.5993 | 48.6695 | 48.7398 | 48.81 | 48.8803 | 48.9505 | 49.0208 | 49.091 | 49.1613 | 49.2315 | 49.3018 | 49.372 | 49.4423 | 1.8876 | 1.925 | 1.9504 | 1.9783 | 1.9966 | 2.0107 | 2.0433 | 2.0787 | 2.1086 | 2.1117 | 2.1147 | 2.1178 | 2.1208 | 2.1239 | 2.1269 | 2.1299 | 2.133 | 2.136 | 2.1391 | 2.1421 | 34629.4409 | 7143.0873 | 1028477.9684 | 212146.3049 | 5768052.3354 | 5768052.3354 | 5962280.5265 | 5768052.3354
| BET004-72499638 | 44 | BET004 | BETS | North | 1036918.3524 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.88516 | 0.89069 | 0.89622 | 0.90176 | 0.90729 | 0.90856 | 0.90983 | 0.9111 | 0.91237 | 0.91364 | 0.91491 | 0.91618 | 0.91745 | 0.91872 | 0.91999 | 0.92126 | 0.92253 | 0.9238 | 0.92507 | 0.92634 | 0.035308 | 0.036029 | 0.036527 | 0.037072 | 0.037436 | 0.037699 | 0.038308 | 0.038969 | 0.039529 | 0.039584 | 0.039639 | 0.039694 | 0.039749 | 0.039804 | 0.039859 | 0.039914 | 0.039969 | 0.040024 | 0.040079 | 0.040134 | 34629.4409 | 7143.0873 | 19271.9049 | 3975.2562 | 284247.9818 | 284247.9818 | 1036918.3524 | 284247.9818
| BET004-72499720 | 21 | BET004 | BETS | North | 494892.85 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.13681 | 0.1377 | 0.13858 | 0.13947 | 0.14036 | 0.14071 | 0.14107 | 0.14142 | 0.14177 | 0.14212 | 0.14248 | 0.14283 | 0.14318 | 0.14353 | 0.14389 | 0.14424 | 0.14459 | 0.14494 | 0.1453 | 0.14565 | 0.0054572 | 0.00557 | 0.0056482 | 0.0057338 | 0.0057914 | 0.0058386 | 0.0059394 | 0.0060487 | 0.0061423 | 0.0061576 | 0.0061729 | 0.0061881 | 0.0062034 | 0.0062187 | 0.006234 | 0.0062493 | 0.0062645 | 0.0062798 | 0.0062951 | 0.0063104 | 34629.4409 | 7143.0873 | 2997.9849 | 618.4006 | 37513.5705 | 37513.5705 | 494892.85 | 37513.5705
| BET004-72499790 | 34 | BET004 | BETS | North | 801255.0905 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.10551 | 0.10637 | 0.10723 | 0.10808 | 0.10894 | 0.10931 | 0.10968 | 0.11005 | 0.11041 | 0.11078 | 0.11115 | 0.11152 | 0.11189 | 0.11226 | 0.11263 | 0.113 | 0.11336 | 0.11373 | 0.1141 | 0.11447 | 0.0042089 | 0.0043028 | 0.0043702 | 0.0044434 | 0.004495 | 0.0045356 | 0.0046179 | 0.0047069 | 0.0047838 | 0.0047998 | 0.0048157 | 0.0048317 | 0.0048477 | 0.0048637 | 0.0048796 | 0.0048956 | 0.0049116 | 0.0049276 | 0.0049435 | 0.0049595 | 34629.4409 | 7143.0873 | 2334.9878 | 481.6428 | 34514.5699 | 34514.5699 | 801255.0905 | 34514.5699
| BET004-72500100 | 65 | BET004 | BETS | North | 1531811.2025 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.48857 | 0.49138 | 0.49418 | 0.49698 | 0.49978 | 0.50089 | 0.502 | 0.50311 | 0.50421 | 0.50532 | 0.50643 | 0.50754 | 0.50865 | 0.50975 | 0.51086 | 0.51197 | 0.51308 | 0.51419 | 0.5153 | 0.5164 | 0.019489 | 0.019877 | 0.020141 | 0.020431 | 0.020622 | 0.020784 | 0.021136 | 0.021519 | 0.021845 | 0.021893 | 0.021941 | 0.021989 | 0.022037 | 0.022085 | 0.022133 | 0.022181 | 0.02223 | 0.022278 | 0.022326 | 0.022374 | 34629.4409 | 7143.0873 | 10663.6542 | 2199.6143 | 206515.6669 | 206515.6669 | 1531811.2025 | 206515.6669
| BET004-72500230 | 25 | BET004 | BETS | North | 589158.1548 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.10541 | 0.10612 | 0.10684 | 0.10756 | 0.10828 | 0.10845 | 0.10863 | 0.10881 | 0.10899 | 0.10916 | 0.10934 | 0.10952 | 0.1097 | 0.10987 | 0.11005 | 0.11023 | 0.11041 | 0.11058 | 0.11076 | 0.11094 | 0.0042046 | 0.0042928 | 0.0043545 | 0.0044218 | 0.0044676 | 0.0045001 | 0.0045738 | 0.004654 | 0.0047219 | 0.0047296 | 0.0047373 | 0.004745 | 0.0047527 | 0.0047604 | 0.0047681 | 0.0047758 | 0.0047834 | 0.0047911 | 0.0047988 | 0.0048065 | 34629.4409 | 7143.0873 | 2301.9823 | 474.8347 | 25025.4989 | 25025.4989 | 589158.1548 | 25025.4989
| BET004-72500251 | 39 | BET004 | BETS | North | 919086.7215 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.58889 | 0.59363 | 0.59836 | 0.6031 | 0.60783 | 0.60951 | 0.61119 | 0.61287 | 0.61455 | 0.61623 | 0.6179 | 0.61958 | 0.62126 | 0.62294 | 0.62462 | 0.6263 | 0.62798 | 0.62966 | 0.63133 | 0.63301 | 0.02349 | 0.024013 | 0.024387 | 0.024794 | 0.02508 | 0.025291 | 0.025734 | 0.026214 | 0.026626 | 0.026698 | 0.026771 | 0.026844 | 0.026917 | 0.026989 | 0.027062 | 0.027135 | 0.027208 | 0.02728 | 0.027353 | 0.027426 | 34629.4409 | 7143.0873 | 12987.4983 | 2678.9585 | 173366.1094 | 173366.1094 | 919086.7215 | 173366.1094
| BET004-72500469 | 18 | BET004 | BETS | North | 424193.8715 | 0.0014328 | 0.001453 | 0.0014639 | 0.0014767 | 0.0014821 | 0.0014904 | 0.0015124 | 0.0015363 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.0015562 | 0.40919 | 0.4109 | 0.41261 | 0.41432 | 0.41602 | 0.41655 | 0.41707 | 0.41759 | 0.41812 | 0.41864 | 0.41916 | 0.41969 | 0.42021 | 0.42074 | 0.42126 | 0.42178 | 0.42231 | 0.42283 | 0.42335 | 0.42388 | 0.016322 | 0.016621 | 0.016816 | 0.017033 | 0.017166 | 0.017284 | 0.01756 | 0.017861 | 0.018115 | 0.018138 | 0.018161 | 0.018183 | 0.018206 | 0.018229 | 0.018251 | 0.018274 | 0.018297 | 0.018319 | 0.018342 | 0.018365 | 34629.4409 | 7143.0873 | 8841.4326 | 1823.7408 | 91460.0914 | 91460.0914 | 424193.8715 | 91460.0914
| BET005-110828671 | 35 | BET005 | BETS | North | 824821.4167 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.85224 | 0.85793 | 0.86362 | 0.86931 | 0.87501 | 0.8767 | 0.87839 | 0.88009 | 0.88178 | 0.88348 | 0.88517 | 0.88686 | 0.88856 | 0.89025 | 0.89195 | 0.89364 | 0.89534 | 0.89703 | 0.89872 | 0.90042 | 0.04288 | 0.043911 | 0.044796 | 0.04559 | 0.046064 | 0.046504 | 0.047403 | 0.048395 | 0.048821 | 0.048915 | 0.049009 | 0.049103 | 0.049196 | 0.04929 | 0.049384 | 0.049478 | 0.049572 | 0.049665 | 0.049759 | 0.049853 | 34629.4409 | 7143.0873 | 23778.9236 | 4904.9284 | 163941.4596 | 163941.4596 | 824821.4167 | 163941.4596
| BET005-117327746 | 9 | BET005 | BETS | North | 212096.9357 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.063892 | 0.064441 | 0.06499 | 0.065539 | 0.066087 | 0.066418 | 0.066748 | 0.067079 | 0.067409 | 0.067739 | 0.06807 | 0.0684 | 0.06873 | 0.069061 | 0.069391 | 0.069722 | 0.070052 | 0.070382 | 0.070713 | 0.071043 | 0.0032147 | 0.0032983 | 0.003371 | 0.0034371 | 0.0034791 | 0.0035231 | 0.0036021 | 0.0036886 | 0.0037322 | 0.0037505 | 0.0037688 | 0.0037871 | 0.0038054 | 0.0038237 | 0.003842 | 0.0038602 | 0.0038785 | 0.0038968 | 0.0039151 | 0.0039334 | 34629.4409 | 7143.0873 | 1822.1233 | 375.8532 | 22961.456 | 22961.456 | 212096.9357 | 22961.456
| BET005-142631975 | 7 | BET005 | BETS | North | 164964.2833 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0045161 | 0.0045538 | 0.0045916 | 0.0046293 | 0.004667 | 0.0046861 | 0.0047052 | 0.0047242 | 0.0047433 | 0.0047624 | 0.0047815 | 0.0048005 | 0.0048196 | 0.0048387 | 0.0048577 | 0.0048768 | 0.0048959 | 0.0049149 | 0.004934 | 0.0049531 | 0.00022722 | 0.00023308 | 0.00023816 | 0.00024278 | 0.00024569 | 0.00024857 | 0.00025392 | 0.00025978 | 0.00026262 | 0.00026368 | 0.00026473 | 0.00026579 | 0.00026684 | 0.0002679 | 0.00026896 | 0.00027001 | 0.00027107 | 0.00027212 | 0.00027318 | 0.00027423 | 34629.4409 | 7143.0873 | 128.1012 | 26.4237 | 2260.2323 | 2260.2323 | 164964.2833 | 2260.2323
| BET005-142632215 | 35 | BET005 | BETS | North | 824821.4167 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.11939 | 0.12032 | 0.12125 | 0.12219 | 0.12312 | 0.12353 | 0.12394 | 0.12434 | 0.12475 | 0.12516 | 0.12557 | 0.12598 | 0.12639 | 0.12679 | 0.1272 | 0.12761 | 0.12802 | 0.12843 | 0.12883 | 0.12924 | 0.006007 | 0.0061584 | 0.0062895 | 0.006408 | 0.0064815 | 0.0065525 | 0.0066883 | 0.0068376 | 0.0069071 | 0.0069297 | 0.0069523 | 0.0069749 | 0.0069975 | 0.0070201 | 0.0070427 | 0.0070653 | 0.0070879 | 0.0071105 | 0.0071331 | 0.0071557 | 34629.4409 | 7143.0873 | 3367.2627 | 694.5723 | 64585.7848 | 64585.7848 | 824821.4167 | 64585.7848
| BET005-143035133 | 48 | BET005 | BETS | North | 1131183.6572 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.21801 | 0.21966 | 0.22131 | 0.22297 | 0.22462 | 0.22509 | 0.22555 | 0.22602 | 0.22649 | 0.22695 | 0.22742 | 0.22788 | 0.22835 | 0.22882 | 0.22928 | 0.22975 | 0.23022 | 0.23068 | 0.23115 | 0.23162 | 0.010969 | 0.011243 | 0.01148 | 0.011693 | 0.011825 | 0.01194 | 0.012172 | 0.012429 | 0.01254 | 0.012566 | 0.012591 | 0.012617 | 0.012643 | 0.012669 | 0.012695 | 0.012721 | 0.012746 | 0.012772 | 0.012798 | 0.012824 | 34629.4409 | 7143.0873 | 6105.3754 | 1259.3686 | 78603.8489 | 78603.8489 | 1131183.6572 | 78603.8489
| BET005-143035406 | 23 | BET005 | BETS | North | 542025.5024 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.54983 | 0.55342 | 0.55701 | 0.5606 | 0.56418 | 0.56525 | 0.56631 | 0.56737 | 0.56844 | 0.5695 | 0.57056 | 0.57162 | 0.57269 | 0.57375 | 0.57481 | 0.57587 | 0.57694 | 0.578 | 0.57906 | 0.58013 | 0.027665 | 0.028326 | 0.028892 | 0.0294 | 0.029701 | 0.029983 | 0.030561 | 0.031199 | 0.031472 | 0.031531 | 0.03159 | 0.031649 | 0.031708 | 0.031767 | 0.031825 | 0.031884 | 0.031943 | 0.032002 | 0.032061 | 0.03212 | 34629.4409 | 7143.0873 | 15329.3821 | 3162.0238 | 105831.9314 | 105831.9314 | 542025.5024 | 105831.9314
| BET005-143035691 | 14 | BET005 | BETS | North | 329928.5667 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.082696 | 0.083266 | 0.083837 | 0.084408 | 0.084978 | 0.085245 | 0.085512 | 0.085779 | 0.086046 | 0.086313 | 0.08658 | 0.086848 | 0.087115 | 0.087382 | 0.087649 | 0.087916 | 0.088183 | 0.08845 | 0.088717 | 0.088984 | 0.0041608 | 0.0042618 | 0.0043486 | 0.0044267 | 0.0044736 | 0.0045218 | 0.0046147 | 0.0047169 | 0.0047641 | 0.0047789 | 0.0047937 | 0.0048085 | 0.0048232 | 0.004838 | 0.0048528 | 0.0048676 | 0.0048824 | 0.0048972 | 0.004912 | 0.0049267 | 34629.4409 | 7143.0873 | 2323.3001 | 479.232 | 45554.6513 | 45554.6513 | 329928.5667 | 45554.6513
| BET005-15436909 | 233 | BET005 | BETS | North | 5490954.0027 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 98.4039 | 98.7623 | 99.1208 | 99.4792 | 99.8377 | 99.948 | 100.0583 | 100.1686 | 100.279 | 100.3893 | 100.4996 | 100.6099 | 100.7202 | 100.8305 | 100.9409 | 101.0512 | 101.1615 | 101.2718 | 101.3821 | 101.4925 | 4.9511 | 5.0549 | 5.1414 | 5.2171 | 5.2559 | 5.3017 | 5.3997 | 5.5082 | 5.5521 | 5.5582 | 5.5643 | 5.5704 | 5.5765 | 5.5826 | 5.5888 | 5.5949 | 5.601 | 5.6071 | 5.6132 | 5.6193 | 34629.4409 | 7143.0873 | 2706512.0099 | 558277.9016 | 2714991.1797 | 2714991.1797 | 5490954.0027 | 2714991.1797
| BET005-162764936 | 1 | BET005 | BETS | North | 23566.3262 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.016774 | 0.016892 | 0.017011 | 0.017129 | 0.017248 | 0.017286 | 0.017324 | 0.017362 | 0.0174 | 0.017438 | 0.017476 | 0.017514 | 0.017553 | 0.017591 | 0.017629 | 0.017667 | 0.017705 | 0.017743 | 0.017781 | 0.017819 | 0.00084395 | 0.00086459 | 0.00088235 | 0.00089833 | 0.000908 | 0.00091692 | 0.0009349 | 0.00095472 | 0.00096339 | 0.0009655 | 0.00096761 | 0.00096972 | 0.00097182 | 0.00097393 | 0.00097604 | 0.00097815 | 0.00098026 | 0.00098237 | 0.00098448 | 0.00098659 | 34629.4409 | 7143.0873 | 469.2679 | 96.7969 | 591.5744 | 591.5744 | 23566.3262 | 591.5744
| BET005-24614354 | 246 | BET005 | BETS | North | 5797316.2432 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 76.2416 | 76.6578 | 77.0739 | 77.49 | 77.9062 | 78.0886 | 78.271 | 78.4534 | 78.6358 | 78.8183 | 79.0007 | 79.1831 | 79.3655 | 79.548 | 79.7304 | 79.9128 | 80.0952 | 80.2776 | 80.4601 | 80.6425 | 3.8361 | 3.9236 | 3.9978 | 4.0639 | 4.1013 | 4.1422 | 4.224 | 4.3141 | 4.3538 | 4.3639 | 4.374 | 4.3841 | 4.3942 | 4.4043 | 4.4144 | 4.4245 | 4.4346 | 4.4447 | 4.4548 | 4.4649 | 34629.4409 | 7143.0873 | 2123071.2057 | 437930.3448 | 5205092.6999 | 5205092.6999 | 5797316.2432 | 5205092.6999
| BET005-54520179 | 249 | BET005 | BETS | North | 5868015.2218 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 24.6429 | 24.8316 | 25.0204 | 25.2091 | 25.3979 | 25.4969 | 25.5959 | 25.6948 | 25.7938 | 25.8928 | 25.9918 | 26.0908 | 26.1897 | 26.2887 | 26.3877 | 26.4867 | 26.5857 | 26.6846 | 26.7836 | 26.8826 | 1.2399 | 1.271 | 1.2978 | 1.3221 | 1.3371 | 1.3525 | 1.3813 | 1.4129 | 1.4281 | 1.4336 | 1.4391 | 1.4446 | 1.45 | 1.4555 | 1.461 | 1.4665 | 1.472 | 1.4774 | 1.4829 | 1.4884 | 34629.4409 | 7143.0873 | 696736.1103 | 143717.2169 | 5689516.9917 | 5689516.9917 | 5868015.2218 | 5689516.9917
| BET005-76446461 | 46 | BET005 | BETS | North | 1084051.0048 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.38988 | 0.39302 | 0.39616 | 0.3993 | 0.40244 | 0.40372 | 0.405 | 0.40629 | 0.40757 | 0.40885 | 0.41013 | 0.41141 | 0.41269 | 0.41397 | 0.41525 | 0.41653 | 0.41781 | 0.41909 | 0.42038 | 0.42166 | 0.019617 | 0.020116 | 0.020549 | 0.020941 | 0.021186 | 0.021415 | 0.021856 | 0.022341 | 0.022566 | 0.022636 | 0.022707 | 0.022778 | 0.022849 | 0.02292 | 0.022991 | 0.023062 | 0.023133 | 0.023204 | 0.023275 | 0.023346 | 34629.4409 | 7143.0873 | 10997.6616 | 2268.5107 | 108076.0257 | 108076.0257 | 1084051.0048 | 108076.0257
| BET005-76446537 | 66 | BET005 | BETS | North | 1555377.5287 | 0.0018073 | 0.0018385 | 0.0018631 | 0.0018838 | 0.001891 | 0.0019053 | 0.0019384 | 0.0019752 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.0019887 | 0.20555 | 0.20731 | 0.20907 | 0.21083 | 0.21259 | 0.21331 | 0.21404 | 0.21477 | 0.21549 | 0.21622 | 0.21695 | 0.21767 | 0.2184 | 0.21913 | 0.21985 | 0.22058 | 0.22131 | 0.22203 | 0.22276 | 0.22349 | 0.010342 | 0.010611 | 0.010844 | 0.011057 | 0.011191 | 0.011315 | 0.011551 | 0.01181 | 0.011931 | 0.011971 | 0.012012 | 0.012052 | 0.012092 | 0.012132 | 0.012173 | 0.012213 | 0.012253 | 0.012293 | 0.012333 | 0.012374 | 34629.4409 | 7143.0873 | 5814.6818 | 1199.4066 | 156031.3736 | 156031.3736 | 1555377.5287 | 156031.3736
| BET006-122234049 | 51 | BET006 | BETS | North | 1201882.6358 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.12515 | 0.12591 | 0.12666 | 0.12742 | 0.12818 | 0.12848 | 0.12877 | 0.12907 | 0.12936 | 0.12966 | 0.12996 | 0.13025 | 0.13055 | 0.13085 | 0.13114 | 0.13144 | 0.13173 | 0.13203 | 0.13233 | 0.13262 | 0.0050924 | 0.005189 | 0.0052772 | 0.0053523 | 0.005399 | 0.0054524 | 0.0055442 | 0.0056494 | 0.005699 | 0.0057121 | 0.0057251 | 0.0057382 | 0.0057512 | 0.0057642 | 0.0057773 | 0.0057903 | 0.0058034 | 0.0058164 | 0.0058295 | 0.0058425 | 34629.4409 | 7143.0873 | 2787.6584 | 575.0161 | 72409.7125 | 72409.7125 | 1201882.6358 | 72409.7125
| BET006-123629680 | 69 | BET006 | BETS | North | 1626076.5072 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 1.3452 | 1.3542 | 1.3632 | 1.3722 | 1.3812 | 1.3832 | 1.3852 | 1.3872 | 1.3892 | 1.3912 | 1.3932 | 1.3952 | 1.3972 | 1.3992 | 1.4012 | 1.4032 | 1.4053 | 1.4073 | 1.4093 | 1.4113 | 0.054739 | 0.055812 | 0.056795 | 0.057638 | 0.058175 | 0.058701 | 0.059638 | 0.060717 | 0.061199 | 0.061288 | 0.061376 | 0.061465 | 0.061553 | 0.061642 | 0.06173 | 0.061818 | 0.061907 | 0.061995 | 0.062084 | 0.062172 | 34629.4409 | 7143.0873 | 29895.5302 | 6166.6136 | 370128.8135 | 370128.8135 | 1626076.5072 | 370128.8135
| BET006-130742783 | 101 | BET006 | BETS | North | 2380198.9454 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.29992 | 0.30183 | 0.30373 | 0.30564 | 0.30754 | 0.30823 | 0.30891 | 0.3096 | 0.31028 | 0.31097 | 0.31165 | 0.31234 | 0.31303 | 0.31371 | 0.3144 | 0.31508 | 0.31577 | 0.31645 | 0.31714 | 0.31782 | 0.012204 | 0.012439 | 0.012654 | 0.012838 | 0.012954 | 0.013081 | 0.0133 | 0.013551 | 0.013669 | 0.013699 | 0.01373 | 0.01376 | 0.01379 | 0.01382 | 0.01385 | 0.013881 | 0.013911 | 0.013941 | 0.013971 | 0.014001 | 34629.4409 | 7143.0873 | 6684.458 | 1378.8172 | 409980.4296 | 409980.4296 | 2380198.9454 | 409980.4296
| BET006-143535036 | 45 | BET006 | BETS | North | 1060484.6786 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.088357 | 0.088988 | 0.089618 | 0.090248 | 0.090878 | 0.091066 | 0.091253 | 0.091441 | 0.091629 | 0.091816 | 0.092004 | 0.092192 | 0.092379 | 0.092567 | 0.092754 | 0.092942 | 0.09313 | 0.093317 | 0.093505 | 0.093692 | 0.0035954 | 0.0036675 | 0.0037338 | 0.0037909 | 0.0038278 | 0.0038648 | 0.0039289 | 0.0040024 | 0.0040366 | 0.0040449 | 0.0040531 | 0.0040614 | 0.0040697 | 0.0040779 | 0.0040862 | 0.0040944 | 0.0041027 | 0.004111 | 0.0041192 | 0.0041275 | 34629.4409 | 7143.0873 | 1972.6899 | 406.9109 | 46719.3713 | 46719.3713 | 1060484.6786 | 46719.3713
| BET006-143535310 | 96 | BET006 | BETS | North | 2262367.3144 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.11701 | 0.1178 | 0.11859 | 0.11938 | 0.12018 | 0.1207 | 0.12121 | 0.12173 | 0.12225 | 0.12277 | 0.12329 | 0.12381 | 0.12433 | 0.12485 | 0.12537 | 0.12589 | 0.1264 | 0.12692 | 0.12744 | 0.12796 | 0.0047613 | 0.0048551 | 0.004941 | 0.0050147 | 0.0050619 | 0.0051222 | 0.0052188 | 0.0053283 | 0.0053857 | 0.0054086 | 0.0054314 | 0.0054543 | 0.0054771 | 0.0055 | 0.0055229 | 0.0055457 | 0.0055686 | 0.0055915 | 0.0056143 | 0.0056372 | 34629.4409 | 7143.0873 | 2639.2096 | 544.3953 | 105247.4756 | 105247.4756 | 2262367.3144 | 105247.4756
| BET006-143535450 | 84 | BET006 | BETS | North | 1979571.4001 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.47627 | 0.47997 | 0.48367 | 0.48737 | 0.49107 | 0.49235 | 0.49363 | 0.49491 | 0.49619 | 0.49747 | 0.49875 | 0.50003 | 0.50131 | 0.50259 | 0.50387 | 0.50515 | 0.50643 | 0.50771 | 0.50899 | 0.51027 | 0.01938 | 0.019781 | 0.020151 | 0.020472 | 0.020684 | 0.020895 | 0.021253 | 0.021662 | 0.021859 | 0.021916 | 0.021972 | 0.022028 | 0.022085 | 0.022141 | 0.022197 | 0.022254 | 0.02231 | 0.022366 | 0.022423 | 0.022479 | 34629.4409 | 7143.0873 | 10685.123 | 2204.0427 | 283402.4126 | 283402.4126 | 1979571.4001 | 283402.4126
| BET006-15436859 | 250 | BET006 | BETS | North | 5891581.5479 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 152.2601 | 152.4453 | 152.6304 | 152.8155 | 153.0006 | 153.0476 | 153.0946 | 153.1416 | 153.1886 | 153.2356 | 153.2826 | 153.3296 | 153.3766 | 153.4236 | 153.4706 | 153.5176 | 153.5646 | 153.6116 | 153.6586 | 153.7056 | 6.1957 | 6.2829 | 6.3591 | 6.419 | 6.4444 | 6.4952 | 6.5914 | 6.703 | 6.7485 | 6.7506 | 6.7527 | 6.7548 | 6.7568 | 6.7589 | 6.761 | 6.763 | 6.7651 | 6.7672 | 6.7693 | 6.7713 | 34629.4409 | 7143.0873 | 3303288.5621 | 681376.251 | 3282086.3074 | 3282086.3074 | 5891581.5479 | 3282086.3074
| BET006-160813078 | 94 | BET006 | BETS | North | 2215234.662 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.36216 | 0.3649 | 0.36764 | 0.37038 | 0.37312 | 0.3746 | 0.37607 | 0.37755 | 0.37902 | 0.3805 | 0.38197 | 0.38344 | 0.38492 | 0.38639 | 0.38787 | 0.38934 | 0.39082 | 0.39229 | 0.39376 | 0.39524 | 0.014737 | 0.015039 | 0.015317 | 0.015558 | 0.015716 | 0.015898 | 0.016192 | 0.016525 | 0.016697 | 0.016762 | 0.016827 | 0.016892 | 0.016957 | 0.017022 | 0.017087 | 0.017152 | 0.017217 | 0.017282 | 0.017347 | 0.017412 | 34629.4409 | 7143.0873 | 8175.1996 | 1686.3155 | 247563.6992 | 247563.6992 | 2215234.662 | 247563.6992
| BET006-163864001 | 15 | BET006 | BETS | North | 353494.8929 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.65787 | 0.66185 | 0.66582 | 0.66979 | 0.67377 | 0.67545 | 0.67713 | 0.67881 | 0.6805 | 0.68218 | 0.68386 | 0.68554 | 0.68723 | 0.68891 | 0.69059 | 0.69227 | 0.69395 | 0.69564 | 0.69732 | 0.699 | 0.02677 | 0.027277 | 0.02774 | 0.028135 | 0.028379 | 0.028666 | 0.029153 | 0.029712 | 0.029978 | 0.030053 | 0.030127 | 0.030201 | 0.030275 | 0.030349 | 0.030423 | 0.030497 | 0.030571 | 0.030646 | 0.03072 | 0.030794 | 34629.4409 | 7143.0873 | 14667.1358 | 3025.4208 | 157889.9443 | 157889.9443 | 353494.8929 | 157889.9443
| BET006-195895491 | 214 | BET006 | BETS | North | 5043193.805 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34629.4409 | 7143.0873 | 0 | 0 | 5729067.2049 | 5729067.2049 | 5043193.805 | 5729067.2049
| BET006-195895635 | 266 | BET006 | BETS | North | 6268642.767 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 15.1492 | 15.247 | 15.3448 | 15.4426 | 15.5404 | 15.5844 | 15.6283 | 15.6723 | 15.7162 | 15.7602 | 15.8041 | 15.848 | 15.892 | 15.9359 | 15.9799 | 16.0238 | 16.0678 | 16.1117 | 16.1557 | 16.1996 | 0.61644 | 0.62839 | 0.63932 | 0.64866 | 0.65457 | 0.66139 | 0.67287 | 0.68598 | 0.69236 | 0.6943 | 0.69623 | 0.69817 | 0.7001 | 0.70204 | 0.70398 | 0.70591 | 0.70785 | 0.70978 | 0.71172 | 0.71366 | 34629.4409 | 7143.0873 | 338783.0032 | 69881.4797 | 2211500.9146 | 2211500.9146 | 6268642.767 | 2211500.9146
| BET006-195895661 | 160 | BET006 | BETS | North | 3770612.1907 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 37.987 | 38.1367 | 38.2863 | 38.436 | 38.5857 | 38.6631 | 38.7405 | 38.8179 | 38.8952 | 38.9726 | 39.05 | 39.1274 | 39.2047 | 39.2821 | 39.3595 | 39.4369 | 39.5142 | 39.5916 | 39.669 | 39.7464 | 1.5457 | 1.5718 | 1.5951 | 1.6145 | 1.6252 | 1.6408 | 1.668 | 1.6991 | 1.7135 | 1.7169 | 1.7203 | 1.7237 | 1.7271 | 1.7305 | 1.7339 | 1.7373 | 1.7408 | 1.7442 | 1.7476 | 1.751 | 34629.4409 | 7143.0873 | 838923.0108 | 173046.4067 | 3165061.5386 | 3165061.5386 | 3770612.1907 | 3165061.5386
| BET006-195895699 | 90 | BET006 | BETS | North | 2120969.3573 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 110.878 | 111.6448 | 112.4117 | 113.1785 | 113.9454 | 114.1407 | 114.336 | 114.5313 | 114.7266 | 114.9219 | 115.1172 | 115.3126 | 115.5079 | 115.7032 | 115.8985 | 116.0938 | 116.2891 | 116.4844 | 116.6797 | 116.8751 | 4.5118 | 4.6013 | 4.6834 | 4.754 | 4.7994 | 4.844 | 4.9227 | 5.013 | 5.0541 | 5.0628 | 5.0714 | 5.08 | 5.0886 | 5.0972 | 5.1058 | 5.1144 | 5.123 | 5.1316 | 5.1402 | 5.1488 | 34629.4409 | 7143.0873 | 2469305.524 | 509348.8228 | 1389196.2062 | 1389196.2062 | 2120969.3573 | 1389196.2062
| BET006-74053669 | 9 | BET006 | BETS | North | 212096.9357 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.11125 | 0.11209 | 0.11294 | 0.11378 | 0.11462 | 0.11493 | 0.11523 | 0.11554 | 0.11585 | 0.11615 | 0.11646 | 0.11677 | 0.11708 | 0.11738 | 0.11769 | 0.118 | 0.11831 | 0.11861 | 0.11892 | 0.11923 | 0.004527 | 0.0046198 | 0.0047052 | 0.0047792 | 0.0048277 | 0.0048773 | 0.0049613 | 0.0050572 | 0.0051035 | 0.005117 | 0.0051306 | 0.0051441 | 0.0051577 | 0.0051712 | 0.0051847 | 0.0051983 | 0.0052118 | 0.0052253 | 0.0052389 | 0.0052524 | 34629.4409 | 7143.0873 | 2495.1951 | 514.6891 | 7235.4367 | 7235.4367 | 212096.9357 | 7235.4367
| BET006-74053924 | 30 | BET006 | BETS | North | 706989.7858 | 0.0014616 | 0.0014804 | 0.0014965 | 0.0015088 | 0.0015129 | 0.0015244 | 0.0015465 | 0.0015722 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.0015824 | 0.3223 | 0.32457 | 0.32685 | 0.32912 | 0.33139 | 0.33233 | 0.33327 | 0.33421 | 0.33515 | 0.33609 | 0.33704 | 0.33798 | 0.33892 | 0.33986 | 0.3408 | 0.34174 | 0.34268 | 0.34362 | 0.34456 | 0.3455 | 0.013115 | 0.013377 | 0.013617 | 0.013825 | 0.013958 | 0.014104 | 0.014349 | 0.014629 | 0.014765 | 0.014806 | 0.014848 | 0.014889 | 0.014931 | 0.014972 | 0.015013 | 0.015055 | 0.015096 | 0.015138 | 0.015179 | 0.015221 | 34629.4409 | 7143.0873 | 7222.2133 | 1489.7411 | 126689.5184 | 126689.5184 | 706989.7858 | 126689.5184
| BET007-110330821 | 24 | BET007 | BETS | North | 565591.8286 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.33479 | 0.336 | 0.33722 | 0.33843 | 0.33965 | 0.34049 | 0.34134 | 0.34219 | 0.34303 | 0.34388 | 0.34473 | 0.34557 | 0.34642 | 0.34727 | 0.34811 | 0.34896 | 0.3498 | 0.35065 | 0.3515 | 0.35234 | 0.010948 | 0.011201 | 0.011434 | 0.011871 | 0.012304 | 0.012887 | 0.013527 | 0.014108 | 0.014545 | 0.01458 | 0.014616 | 0.014652 | 0.014688 | 0.014724 | 0.01476 | 0.014796 | 0.014832 | 0.014868 | 0.014903 | 0.014939 | 34629.4409 | 7143.0873 | 6762.6899 | 1394.9542 | 59698.5293 | 59698.5293 | 565591.8286 | 59698.5293
| BET007-129159691 | 10 | BET007 | BETS | North | 235663.2619 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.070833 | 0.071264 | 0.071695 | 0.072126 | 0.072558 | 0.072791 | 0.073024 | 0.073257 | 0.073491 | 0.073724 | 0.073957 | 0.074191 | 0.074424 | 0.074657 | 0.074891 | 0.075124 | 0.075357 | 0.07559 | 0.075824 | 0.076057 | 0.0023164 | 0.0023758 | 0.0024311 | 0.0025298 | 0.0026285 | 0.0027549 | 0.0028938 | 0.0030204 | 0.003116 | 0.0031259 | 0.0031358 | 0.0031457 | 0.0031556 | 0.0031655 | 0.0031753 | 0.0031852 | 0.0031951 | 0.003205 | 0.0032149 | 0.0032248 | 34629.4409 | 7143.0873 | 1448.3798 | 298.7603 | 8073.0109 | 8073.0109 | 235663.2619 | 8073.0109
| BET007-132469306 | 129 | BET007 | BETS | North | 3040056.0787 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 2.3718 | 2.3812 | 2.3907 | 2.4001 | 2.4096 | 2.4167 | 2.4239 | 2.431 | 2.4382 | 2.4454 | 2.4525 | 2.4597 | 2.4669 | 2.474 | 2.4812 | 2.4884 | 2.4955 | 2.5027 | 2.5098 | 2.517 | 0.077564 | 0.079384 | 0.081063 | 0.084184 | 0.087291 | 0.091465 | 0.096054 | 0.10023 | 0.10338 | 0.10368 | 0.10399 | 0.10429 | 0.10459 | 0.1049 | 0.1052 | 0.10551 | 0.10581 | 0.10611 | 0.10642 | 0.10672 | 34629.4409 | 7143.0873 | 48090.5401 | 9919.7364 | 2821668.2283 | 2821668.2283 | 3040056.0787 | 2821668.2283
| BET007-132750977 | 39 | BET007 | BETS | North | 919086.7215 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.24928 | 0.25052 | 0.25176 | 0.253 | 0.25423 | 0.25528 | 0.25633 | 0.25738 | 0.25843 | 0.25948 | 0.26053 | 0.26157 | 0.26262 | 0.26367 | 0.26472 | 0.26577 | 0.26682 | 0.26787 | 0.26891 | 0.26996 | 0.0081522 | 0.0083517 | 0.0085366 | 0.0088739 | 0.0092101 | 0.0096617 | 0.010158 | 0.010612 | 0.010957 | 0.011002 | 0.011046 | 0.011091 | 0.011135 | 0.01118 | 0.011224 | 0.011269 | 0.011313 | 0.011357 | 0.011402 | 0.011446 | 34629.4409 | 7143.0873 | 5102.5172 | 1052.5069 | 76393.3747 | 76393.3747 | 919086.7215 | 76393.3747
| BET007-132751049 | 11 | BET007 | BETS | North | 259229.5881 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.019648 | 0.019752 | 0.019857 | 0.019961 | 0.020066 | 0.020162 | 0.020258 | 0.020354 | 0.02045 | 0.020546 | 0.020642 | 0.020738 | 0.020834 | 0.02093 | 0.021026 | 0.021122 | 0.021218 | 0.021314 | 0.02141 | 0.021506 | 0.00064253 | 0.00065848 | 0.0006733 | 0.00070014 | 0.00072691 | 0.00076305 | 0.00080277 | 0.00083919 | 0.00086706 | 0.00087113 | 0.00087521 | 0.00087928 | 0.00088335 | 0.00088742 | 0.00089149 | 0.00089556 | 0.00089963 | 0.00090371 | 0.00090778 | 0.00091185 | 34629.4409 | 7143.0873 | 404.0541 | 83.3451 | 4797.4934 | 4797.4934 | 259229.5881 | 4797.4934
| BET007-134953366 | 1 | BET007 | BETS | North | 23566.3262 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34629.4409 | 7143.0873 | 0 | 0 | 0 | 0 | 23566.3262 | 0
| BET007-154907496 | 17 | BET007 | BETS | North | 400627.5453 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.20526 | 0.20639 | 0.20752 | 0.20865 | 0.20978 | 0.21068 | 0.21158 | 0.21248 | 0.21338 | 0.21428 | 0.21518 | 0.21608 | 0.21698 | 0.21788 | 0.21878 | 0.21968 | 0.22058 | 0.22148 | 0.22238 | 0.22328 | 0.0067124 | 0.0068804 | 0.0070366 | 0.0073185 | 0.0075998 | 0.0079737 | 0.0083847 | 0.0087607 | 0.0090474 | 0.0090855 | 0.0091237 | 0.0091618 | 0.0091999 | 0.0092381 | 0.0092762 | 0.0093144 | 0.0093525 | 0.0093906 | 0.0094288 | 0.0094669 | 34629.4409 | 7143.0873 | 4212.8396 | 868.9912 | 37487.024 | 37487.024 | 400627.5453 | 37487.024
| BET007-154907629 | 7 | BET007 | BETS | North | 164964.2833 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.1546 | 0.15538 | 0.15616 | 0.15694 | 0.15772 | 0.15833 | 0.15893 | 0.15954 | 0.16015 | 0.16075 | 0.16136 | 0.16197 | 0.16258 | 0.16318 | 0.16379 | 0.1644 | 0.16501 | 0.16561 | 0.16622 | 0.16683 | 0.0050557 | 0.0051799 | 0.005295 | 0.0055046 | 0.0057136 | 0.0059921 | 0.0062982 | 0.0065779 | 0.0067902 | 0.006816 | 0.0068417 | 0.0068675 | 0.0068932 | 0.006919 | 0.0069447 | 0.0069705 | 0.0069962 | 0.007022 | 0.0070477 | 0.0070735 | 34629.4409 | 7143.0873 | 3160.7064 | 651.9655 | 23890.242 | 23890.242 | 164964.2833 | 23890.242
| BET007-154907735 | 14 | BET007 | BETS | North | 329928.5667 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.13021 | 0.13111 | 0.13201 | 0.13291 | 0.13381 | 0.13415 | 0.1345 | 0.13485 | 0.1352 | 0.13555 | 0.1359 | 0.13625 | 0.13659 | 0.13694 | 0.13729 | 0.13764 | 0.13799 | 0.13834 | 0.13868 | 0.13903 | 0.0042582 | 0.0043708 | 0.0044761 | 0.0046617 | 0.0048474 | 0.0050773 | 0.0053301 | 0.0055599 | 0.0057324 | 0.0057472 | 0.005762 | 0.0057768 | 0.0057915 | 0.0058063 | 0.0058211 | 0.0058359 | 0.0058506 | 0.0058654 | 0.0058802 | 0.005895 | 34629.4409 | 7143.0873 | 2661.178 | 548.9268 | 35768.9856 | 35768.9856 | 329928.5667 | 35768.9856
| BET007-154907875 | 14 | BET007 | BETS | North | 329928.5667 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.09875 | 0.099381 | 0.10001 | 0.10064 | 0.10127 | 0.10151 | 0.10175 | 0.10199 | 0.10223 | 0.10247 | 0.10271 | 0.10294 | 0.10318 | 0.10342 | 0.10366 | 0.1039 | 0.10414 | 0.10438 | 0.10462 | 0.10485 | 0.0032294 | 0.0033131 | 0.0033912 | 0.0035301 | 0.0036688 | 0.0038419 | 0.0040322 | 0.0042051 | 0.0043345 | 0.0043446 | 0.0043547 | 0.0043648 | 0.004375 | 0.0043851 | 0.0043952 | 0.0044053 | 0.0044154 | 0.0044256 | 0.0044357 | 0.0044458 | 34629.4409 | 7143.0873 | 2012.0567 | 415.0311 | 14319.4632 | 14319.4632 | 329928.5667 | 14319.4632
| BET007-155326877 | 123 | BET007 | BETS | North | 2898658.1216 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 187.0313 | 187.846 | 188.6607 | 189.4755 | 190.2902 | 190.5293 | 190.7685 | 191.0076 | 191.2467 | 191.4859 | 191.725 | 191.9642 | 192.2033 | 192.4424 | 192.6816 | 192.9207 | 193.1598 | 193.399 | 193.6381 | 193.8773 | 6.1164 | 6.2623 | 6.3971 | 6.6459 | 6.8936 | 7.2109 | 7.5598 | 7.8753 | 8.1088 | 8.119 | 8.1291 | 8.1392 | 8.1494 | 8.1595 | 8.1697 | 8.1798 | 8.1899 | 8.2001 | 8.2102 | 8.2204 | 34629.4409 | 7143.0873 | 3762403.9532 | 776078.9445 | 3189885.1607 | 3189885.1607 | 2898658.1216 | 3189885.1607
| BET007-159943710 | 109 | BET007 | BETS | North | 2568729.5549 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 7.7422 | 7.7826 | 7.8229 | 7.8633 | 7.9036 | 7.9333 | 7.963 | 7.9927 | 8.0224 | 8.052 | 8.0817 | 8.1114 | 8.1411 | 8.1707 | 8.2004 | 8.2301 | 8.2598 | 8.2894 | 8.3191 | 8.3488 | 0.25319 | 0.25945 | 0.26526 | 0.27581 | 0.28632 | 0.30025 | 0.31556 | 0.32954 | 0.34015 | 0.3414 | 0.34266 | 0.34392 | 0.34518 | 0.34644 | 0.3477 | 0.34895 | 0.35021 | 0.35147 | 0.35273 | 0.35399 | 34629.4409 | 7143.0873 | 158296.4476 | 32652.1398 | 1141367.3669 | 1141367.3669 | 2568729.5549 | 1141367.3669
| BET007-162663688 | 89 | BET007 | BETS | North | 2097403.0311 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 5.762 | 5.7971 | 5.8322 | 5.8674 | 5.9025 | 5.9156 | 5.9287 | 5.9418 | 5.9549 | 5.9681 | 5.9812 | 5.9943 | 6.0074 | 6.0205 | 6.0336 | 6.0468 | 6.0599 | 6.073 | 6.0861 | 6.0992 | 0.18843 | 0.19326 | 0.19776 | 0.2058 | 0.21383 | 0.22389 | 0.23494 | 0.24498 | 0.25249 | 0.25304 | 0.2536 | 0.25416 | 0.25471 | 0.25527 | 0.25583 | 0.25638 | 0.25694 | 0.25749 | 0.25805 | 0.25861 | 34629.4409 | 7143.0873 | 117200.758 | 24175.2458 | 650963.8933 | 650963.8933 | 2097403.0311 | 650963.8933
| BET007-24613316 | 163 | BET007 | BETS | North | 3841311.1693 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 28.64 | 28.8127 | 28.9855 | 29.1582 | 29.3309 | 29.3912 | 29.4515 | 29.5117 | 29.572 | 29.6322 | 29.6925 | 29.7527 | 29.813 | 29.8733 | 29.9335 | 29.9938 | 30.054 | 30.1143 | 30.1745 | 30.2348 | 0.9366 | 0.96054 | 0.98284 | 1.0227 | 1.0626 | 1.1124 | 1.1671 | 1.2168 | 1.2538 | 1.2564 | 1.259 | 1.2615 | 1.2641 | 1.2666 | 1.2692 | 1.2717 | 1.2743 | 1.2768 | 1.2794 | 1.282 | 34629.4409 | 7143.0873 | 581897.5419 | 120029.2249 | 447763.4198 | 447763.4198 | 3841311.1693 | 447763.4198
| BET007-63637518 | 164 | BET007 | BETS | North | 3864877.4955 | 0.0011747 | 0.0011975 | 0.001218 | 0.0012599 | 0.0013013 | 0.0013594 | 0.0014234 | 0.001481 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 0.001523 | 16.2803 | 16.3583 | 16.4363 | 16.5142 | 16.5922 | 16.6173 | 16.6424 | 16.6675 | 16.6925 | 16.7176 | 16.7427 | 16.7678 | 16.7929 | 16.818 | 16.8431 | 16.8682 | 16.8932 | 16.9183 | 16.9434 | 16.9685 | 0.53241 | 0.54534 | 0.55732 | 0.57924 | 0.60108 | 0.62891 | 0.65951 | 0.6872 | 0.70776 | 0.70882 | 0.70989 | 0.71095 | 0.71202 | 0.71308 | 0.71414 | 0.71521 | 0.71627 | 0.71733 | 0.7184 | 0.71946 | 34629.4409 | 7143.0873 | 328433.7027 | 67746.7078 | 251212.8986 | 251212.8986 | 3864877.4955 | 251212.8986
| BET008-94648877 | 218 | BET008 | BETS | North | 5137459.1098 | 0.0018096 | 0.0018494 | 0.0018362 | 0.0018233 | 0.0018031 | 0.0017898 | 0.0017927 | 0.0018 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0.0017973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34629.4409 | 7143.0873 | 0 | 0 | 0 | 0 | 5137459.1098 | 0
| BGO011-197684068 | 13 | BGO011 | BGO | North | 306362.2405 | 0.004409 | 0.0043865 | 0.0043191 | 0.0042371 | 0.0041584 | 0.0040831 | 0.0040348 | 0.0040011 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0.0039562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34030.2576 | 5837.4447 | 0 | 0 | 0 | 0 | 306362.2405 | 0
| BGO012-197683994 | 176 | BGO012 | BGO | North | 4147673.4098 | 0.001309 | 0.0013102 | 0.0013044 | 0.0012986 | 0.0012836 | 0.0012765 | 0.0012784 | 0.0012796 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 0.0012749 | 22.8589 | 22.9678 | 23.0768 | 23.1857 | 23.2947 | 23.3291 | 23.3635 | 23.3979 | 23.4323 | 23.4667 | 23.5011 | 23.5355 | 23.5699 | 23.6043 | 23.6387 | 23.6731 | 23.7075 | 23.7419 | 23.7763 | 23.8107 | 0.83306 | 0.83777 | 0.83801 | 0.83821 | 0.83247 | 0.82904 | 0.83152 | 0.8335 | 0.83169 | 0.83292 | 0.83414 | 0.83536 | 0.83658 | 0.8378 | 0.83902 | 0.84024 | 0.84146 | 0.84268 | 0.8439 | 0.84513 | 34030.2576 | 5837.4447 | 411435.2488 | 70576.3254 | 544038.1663 | 544038.1663 | 4147673.4098 | 544038.1663
| BGO013-163795489 | 56 | BGO013 | BGO | North | 1319714.2667 | 0.0020934 | 0.0021462 | 0.0021878 | 0.002227 | 0.0022577 | 0.0022927 | 0.0023417 | 0.0023956 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 4.1943 | 4.2201 | 4.2458 | 4.2715 | 4.2973 | 4.3053 | 4.3133 | 4.3213 | 4.3293 | 4.3373 | 4.3453 | 4.3533 | 4.3613 | 4.3693 | 4.3773 | 4.3853 | 4.3933 | 4.4013 | 4.4093 | 4.4173 | 0.24444 | 0.25215 | 0.25861 | 0.26484 | 0.2701 | 0.27479 | 0.28119 | 0.2882 | 0.29331 | 0.29385 | 0.29439 | 0.29493 | 0.29547 | 0.29602 | 0.29656 | 0.2971 | 0.29764 | 0.29818 | 0.29873 | 0.29927 | 34030.2576 | 5837.4447 | 138451.991 | 23749.6248 | 538844.6444 | 538844.6444 | 1319714.2667 | 538844.6444
| BGO013-197650863 | 132 | BGO013 | BGO | North | 3110755.0573 | 0.0020934 | 0.0021462 | 0.0021878 | 0.002227 | 0.0022577 | 0.0022927 | 0.0023417 | 0.0023956 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 69.4433 | 69.8061 | 70.1689 | 70.5317 | 70.8945 | 71.1757 | 71.4569 | 71.7381 | 72.0192 | 72.3004 | 72.5816 | 72.8628 | 73.144 | 73.4252 | 73.7063 | 73.9875 | 74.2687 | 74.5499 | 74.8311 | 75.1123 | 4.0471 | 4.171 | 4.2739 | 4.373 | 4.4561 | 4.543 | 4.6584 | 4.7845 | 4.8793 | 4.8983 | 4.9174 | 4.9364 | 4.9555 | 4.9745 | 4.9936 | 5.0126 | 5.0317 | 5.0507 | 5.0698 | 5.0888 | 34030.2576 | 5837.4447 | 2310242.0183 | 396291.7445 | 1270904.6095 | 1270904.6095 | 3110755.0573 | 1270904.6095
| BGO013-24606216 | 97 | BGO013 | BGO | North | 2285933.6406 | 0.0020934 | 0.0021462 | 0.0021878 | 0.002227 | 0.0022577 | 0.0022927 | 0.0023417 | 0.0023956 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 0.0024335 | 14.6847 | 14.7752 | 14.8657 | 14.9563 | 15.0468 | 15.091 | 15.1353 | 15.1795 | 15.2238 | 15.268 | 15.3122 | 15.3565 | 15.4007 | 15.4449 | 15.4892 | 15.5334 | 15.5777 | 15.6219 | 15.6661 | 15.7104 | 0.85581 | 0.88284 | 0.90546 | 0.9273 | 0.94577 | 0.96323 | 0.98669 | 1.0124 | 1.0314 | 1.0344 | 1.0374 | 1.0404 | 1.0434 | 1.0464 | 1.0494 | 1.0524 | 1.0554 | 1.0584 | 1.0614 | 1.0644 | 34030.2576 | 5837.4447 | 487490.0074 | 83622.5226 | 1291210.6147 | 1291210.6147 | 2285933.6406 | 1291210.6147
| BGO014-197650786 | 28 | BGO014 | BGO | North | 659857.1334 | 0.002961 | 0.0029487 | 0.0028983 | 0.0028384 | 0.0027785 | 0.002712 | 0.0026711 | 0.0026464 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0.0026055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34030.2576 | 5837.4447 | 0 | 0 | 0 | 0 | 659857.1334 | 0
| BGO022-164367964 | 95 | BGO022 | BGO | North | 2238800.9882 | 0.0011967 | 0.0012102 | 0.0012147 | 0.0012184 | 0.001217 | 0.0012184 | 0.0012451 | 0.0012686 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 4.3165 | 4.346 | 4.3754 | 4.4049 | 4.4344 | 4.45 | 4.4655 | 4.4811 | 4.4967 | 4.5123 | 4.5279 | 4.5434 | 4.559 | 4.5746 | 4.5902 | 4.6057 | 4.6213 | 4.6369 | 4.6525 | 4.668 | 0.14381 | 0.14643 | 0.14797 | 0.14942 | 0.15024 | 0.15094 | 0.15479 | 0.15826 | 0.16037 | 0.16092 | 0.16148 | 0.16203 | 0.16259 | 0.16314 | 0.1637 | 0.16425 | 0.16481 | 0.16536 | 0.16592 | 0.16648 | 34030.2576 | 5837.4447 | 77135.9356 | 13231.659 | 107581.3571 | 107581.3571 | 2238800.9882 | 107581.3571
| BGO022-164368050 | 109 | BGO022 | BGO | North | 2568729.5549 | 0.0011967 | 0.0012102 | 0.0012147 | 0.0012184 | 0.001217 | 0.0012184 | 0.0012451 | 0.0012686 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 2.7706 | 2.7822 | 2.7938 | 2.8054 | 2.817 | 2.8214 | 2.8258 | 2.8301 | 2.8345 | 2.8389 | 2.8432 | 2.8476 | 2.852 | 2.8564 | 2.8607 | 2.8651 | 2.8695 | 2.8738 | 2.8782 | 2.8826 | 0.092307 | 0.093741 | 0.094479 | 0.095161 | 0.095444 | 0.095703 | 0.097953 | 0.099952 | 0.10109 | 0.10124 | 0.1014 | 0.10155 | 0.10171 | 0.10187 | 0.10202 | 0.10218 | 0.10233 | 0.10249 | 0.10265 | 0.1028 | 34030.2576 | 5837.4447 | 48593.1284 | 8335.5144 | 47648.2778 | 47648.2778 | 2568729.5549 | 47648.2778
| BGO022-197683907 | 84 | BGO022 | BGO | North | 1979571.4001 | 0.0011967 | 0.0012102 | 0.0012147 | 0.0012184 | 0.001217 | 0.0012184 | 0.0012451 | 0.0012686 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0.001281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34030.2576 | 5837.4447 | 0 | 0 | 0 | 0 | 1979571.4001 | 0
| BGO023-143335276 | 131 | BGO023 | BGO | North | 3087188.7311 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 2.6784 | 2.695 | 2.7116 | 2.7282 | 2.7448 | 2.7604 | 2.776 | 2.7916 | 2.8072 | 2.8228 | 2.8384 | 2.854 | 2.8697 | 2.8853 | 2.9009 | 2.9165 | 2.9321 | 2.9477 | 2.9633 | 2.9789 | 0.1492 | 0.15226 | 0.15434 | 0.15623 | 0.15761 | 0.15907 | 0.16209 | 0.1654 | 0.16755 | 0.16848 | 0.16941 | 0.17035 | 0.17128 | 0.17221 | 0.17314 | 0.17407 | 0.175 | 0.17594 | 0.17687 | 0.1778 | 34030.2576 | 5837.4447 | 81051.6259 | 13903.3443 | 2988869.8286 | 2988869.8286 | 3087188.7311 | 2988869.8286
| BGO023-143335516 | 58 | BGO023 | BGO | North | 1366846.9191 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.13793 | 0.139 | 0.14007 | 0.14114 | 0.14222 | 0.14283 | 0.14345 | 0.14407 | 0.14469 | 0.14531 | 0.14593 | 0.14655 | 0.14717 | 0.14779 | 0.14841 | 0.14903 | 0.14965 | 0.15027 | 0.15088 | 0.1515 | 0.007683 | 0.0078533 | 0.0079729 | 0.0080828 | 0.0081661 | 0.0082311 | 0.0083762 | 0.0085364 | 0.0086361 | 0.0086731 | 0.00871 | 0.008747 | 0.0087839 | 0.0088209 | 0.0088578 | 0.0088948 | 0.0089318 | 0.0089687 | 0.0090057 | 0.0090426 | 34030.2576 | 5837.4447 | 4167.7503 | 714.923 | 58329.9826 | 58329.9826 | 1366846.9191 | 58329.9826
| BGO023-154908179 | 58 | BGO023 | BGO | North | 1366846.9191 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.078383 | 0.07897 | 0.079558 | 0.080145 | 0.080732 | 0.081004 | 0.081276 | 0.081548 | 0.081819 | 0.082091 | 0.082363 | 0.082635 | 0.082907 | 0.083178 | 0.08345 | 0.083722 | 0.083994 | 0.084266 | 0.084538 | 0.084809 | 0.0043662 | 0.0044617 | 0.0045284 | 0.0045896 | 0.0046357 | 0.004668 | 0.0047457 | 0.0048318 | 0.0048835 | 0.0048997 | 0.0049159 | 0.0049321 | 0.0049484 | 0.0049646 | 0.0049808 | 0.004997 | 0.0050133 | 0.0050295 | 0.0050457 | 0.0050619 | 34030.2576 | 5837.4447 | 2354.5748 | 403.8964 | 57674.2191 | 57674.2191 | 1366846.9191 | 57674.2191
| BGO023-154971813 | 25 | BGO023 | BGO | North | 589158.1548 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.028101 | 0.028336 | 0.028571 | 0.028806 | 0.029041 | 0.029179 | 0.029316 | 0.029454 | 0.029591 | 0.029729 | 0.029866 | 0.030004 | 0.030141 | 0.030279 | 0.030416 | 0.030554 | 0.030691 | 0.030829 | 0.030966 | 0.031104 | 0.0015653 | 0.001601 | 0.0016263 | 0.0016496 | 0.0016676 | 0.0016815 | 0.0017118 | 0.0017452 | 0.0017662 | 0.0017744 | 0.0017826 | 0.0017908 | 0.001799 | 0.0018072 | 0.0018154 | 0.0018236 | 0.0018318 | 0.0018401 | 0.0018483 | 0.0018565 | 34030.2576 | 5837.4447 | 852.4168 | 146.2209 | 27995.4309 | 27995.4309 | 589158.1548 | 27995.4309
| BGO023-154971917 | 15 | BGO023 | BGO | North | 353494.8929 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.036499 | 0.03676 | 0.037021 | 0.037282 | 0.037543 | 0.037715 | 0.037888 | 0.03806 | 0.038233 | 0.038405 | 0.038578 | 0.03875 | 0.038923 | 0.039095 | 0.039268 | 0.03944 | 0.039613 | 0.039785 | 0.039958 | 0.04013 | 0.0020331 | 0.0020769 | 0.0021072 | 0.002135 | 0.0021557 | 0.0021734 | 0.0022122 | 0.0022551 | 0.0022819 | 0.0022922 | 0.0023025 | 0.0023128 | 0.0023231 | 0.0023334 | 0.0023437 | 0.002354 | 0.0023643 | 0.0023746 | 0.0023849 | 0.0023952 | 34030.2576 | 5837.4447 | 1101.9529 | 189.0256 | 21715.3625 | 21715.3625 | 353494.8929 | 21715.3625
| BGO023-154972040 | 15 | BGO023 | BGO | North | 353494.8929 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.030847 | 0.031097 | 0.031348 | 0.031598 | 0.031848 | 0.032037 | 0.032225 | 0.032413 | 0.032602 | 0.03279 | 0.032978 | 0.033166 | 0.033355 | 0.033543 | 0.033731 | 0.03392 | 0.034108 | 0.034296 | 0.034484 | 0.034673 | 0.0017183 | 0.001757 | 0.0017843 | 0.0018095 | 0.0018288 | 0.0018462 | 0.0018816 | 0.0019205 | 0.0019459 | 0.0019571 | 0.0019683 | 0.0019796 | 0.0019908 | 0.002002 | 0.0020133 | 0.0020245 | 0.0020358 | 0.002047 | 0.0020582 | 0.0020695 | 34030.2576 | 5837.4447 | 940.4686 | 161.3251 | 15161.3591 | 15161.3591 | 353494.8929 | 15161.3591
| BGO023-155521549 | 27 | BGO023 | BGO | North | 636290.8072 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.19528 | 0.19654 | 0.1978 | 0.19906 | 0.20032 | 0.20217 | 0.20401 | 0.20585 | 0.2077 | 0.20954 | 0.21138 | 0.21323 | 0.21507 | 0.21691 | 0.21876 | 0.2206 | 0.22244 | 0.22429 | 0.22613 | 0.22797 | 0.010878 | 0.011104 | 0.011259 | 0.0114 | 0.011503 | 0.01165 | 0.011912 | 0.012197 | 0.012397 | 0.012507 | 0.012617 | 0.012727 | 0.012837 | 0.012947 | 0.013057 | 0.013167 | 0.013277 | 0.013387 | 0.013497 | 0.013607 | 34030.2576 | 5837.4447 | 6018.2615 | 1032.3539 | 101081.2316 | 101081.2316 | 636290.8072 | 101081.2316
| BGO023-159428721 | 231 | BGO023 | BGO | North | 5443821.3503 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 135.5157 | 136.1163 | 136.717 | 137.3176 | 137.9182 | 138.2889 | 138.6596 | 139.0303 | 139.4009 | 139.7716 | 140.1423 | 140.513 | 140.8836 | 141.2543 | 141.625 | 141.9957 | 142.3664 | 142.737 | 143.1077 | 143.4784 | 7.5487 | 7.6904 | 7.7819 | 7.8637 | 7.9194 | 7.9691 | 8.0963 | 8.2376 | 8.3203 | 8.3424 | 8.3645 | 8.3866 | 8.4088 | 8.4309 | 8.453 | 8.4751 | 8.4973 | 8.5194 | 8.5415 | 8.5636 | 34030.2576 | 5837.4447 | 4015954.3661 | 688884.3459 | 5325128.235 | 5325128.235 | 5443821.3503 | 5325128.235
| BGO023-159428755 | 191 | BGO023 | BGO | North | 4501168.3026 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 25.3004 | 25.4753 | 25.6502 | 25.825 | 25.9999 | 26.1212 | 26.2425 | 26.3638 | 26.4851 | 26.6064 | 26.7277 | 26.8489 | 26.9702 | 27.0915 | 27.2128 | 27.3341 | 27.4554 | 27.5767 | 27.698 | 27.8193 | 1.4093 | 1.4393 | 1.46 | 1.4789 | 1.4929 | 1.5053 | 1.5323 | 1.5621 | 1.5808 | 1.588 | 1.5953 | 1.6025 | 1.6097 | 1.617 | 1.6242 | 1.6315 | 1.6387 | 1.6459 | 1.6532 | 1.6604 | 34030.2576 | 5837.4447 | 763527.0021 | 130973.0519 | 1413764.9537 | 1413764.9537 | 4501168.3026 | 1413764.9537
| BGO023-197650699 | 134 | BGO023 | BGO | North | 3157887.7097 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 97.3517 | 97.7793 | 98.2069 | 98.6346 | 99.0622 | 99.2393 | 99.4165 | 99.5937 | 99.7708 | 99.948 | 100.1251 | 100.3023 | 100.4794 | 100.6566 | 100.8337 | 101.0109 | 101.1881 | 101.3652 | 101.5424 | 101.7195 | 5.4228 | 5.5244 | 5.59 | 5.6485 | 5.6882 | 5.7188 | 5.8049 | 5.901 | 5.9549 | 5.9655 | 5.9761 | 5.9866 | 5.9972 | 6.0078 | 6.0184 | 6.0289 | 6.0395 | 6.0501 | 6.0606 | 6.0712 | 34030.2576 | 5837.4447 | 2871472.9817 | 492563.5619 | 1709181.0929 | 1709181.0929 | 3157887.7097 | 1709181.0929
| BGO023-24604124 | 54 | BGO023 | BGO | North | 1272581.6144 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 25.4924 | 25.651 | 25.8095 | 25.9681 | 26.1267 | 26.3159 | 26.5051 | 26.6942 | 26.8834 | 27.0726 | 27.2618 | 27.451 | 27.6401 | 27.8293 | 28.0185 | 28.2077 | 28.3969 | 28.5861 | 28.7752 | 28.9644 | 1.42 | 1.4493 | 1.4691 | 1.4871 | 1.5002 | 1.5165 | 1.5476 | 1.5817 | 1.6046 | 1.6159 | 1.6271 | 1.6384 | 1.6497 | 1.661 | 1.6723 | 1.6836 | 1.6949 | 1.7062 | 1.7175 | 1.7288 | 34030.2576 | 5837.4447 | 777477.916 | 133366.1483 | 911551.9572 | 911551.9572 | 1272581.6144 | 911551.9572
| BGO023-24614382 | 83 | BGO023 | BGO | North | 1956005.0739 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 7.9729 | 8.0232 | 8.0735 | 8.1238 | 8.174 | 8.2301 | 8.2862 | 8.3423 | 8.3984 | 8.4545 | 8.5106 | 8.5666 | 8.6227 | 8.6788 | 8.7349 | 8.791 | 8.8471 | 8.9031 | 8.9592 | 9.0153 | 0.44412 | 0.4533 | 0.45954 | 0.46522 | 0.46936 | 0.47428 | 0.48383 | 0.49429 | 0.50127 | 0.50461 | 0.50796 | 0.51131 | 0.51465 | 0.518 | 0.52135 | 0.5247 | 0.52804 | 0.53139 | 0.53474 | 0.53809 | 34030.2576 | 5837.4447 | 242773.5364 | 41644.6188 | 891462.6117 | 891462.6117 | 1956005.0739 | 891462.6117
| BGO023-76446934 | 65 | BGO023 | BGO | North | 1531811.2025 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.25047 | 0.25266 | 0.25486 | 0.25705 | 0.25924 | 0.26018 | 0.26112 | 0.26207 | 0.26301 | 0.26395 | 0.26489 | 0.26583 | 0.26678 | 0.26772 | 0.26866 | 0.2696 | 0.27054 | 0.27148 | 0.27243 | 0.27337 | 0.013952 | 0.014275 | 0.014506 | 0.01472 | 0.014886 | 0.014993 | 0.015247 | 0.015528 | 0.015698 | 0.015754 | 0.01581 | 0.015866 | 0.015923 | 0.015979 | 0.016035 | 0.016091 | 0.016148 | 0.016204 | 0.01626 | 0.016316 | 34030.2576 | 5837.4447 | 7565.4073 | 1297.7465 | 157152.0864 | 157152.0864 | 1531811.2025 | 157152.0864
| BGO023-76447847 | 83 | BGO023 | BGO | North | 1956005.0739 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.18654 | 0.18825 | 0.18997 | 0.19168 | 0.1934 | 0.19471 | 0.19603 | 0.19734 | 0.19866 | 0.19997 | 0.20129 | 0.2026 | 0.20392 | 0.20523 | 0.20655 | 0.20786 | 0.20918 | 0.21049 | 0.21181 | 0.21313 | 0.010391 | 0.010636 | 0.010813 | 0.010977 | 0.011105 | 0.011221 | 0.011446 | 0.011693 | 0.011857 | 0.011936 | 0.012014 | 0.012093 | 0.012171 | 0.01225 | 0.012328 | 0.012407 | 0.012485 | 0.012564 | 0.012642 | 0.012721 | 34030.2576 | 5837.4447 | 5732.6988 | 983.3694 | 140613.8931 | 140613.8931 | 1956005.0739 | 140613.8931
| BGO023-76448158 | 38 | BGO023 | BGO | North | 895520.3953 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.20772 | 0.2095 | 0.21127 | 0.21304 | 0.21481 | 0.21649 | 0.21817 | 0.21985 | 0.22154 | 0.22322 | 0.2249 | 0.22658 | 0.22826 | 0.22994 | 0.23162 | 0.23331 | 0.23499 | 0.23667 | 0.23835 | 0.24003 | 0.011571 | 0.011836 | 0.012025 | 0.0122 | 0.012335 | 0.012476 | 0.012739 | 0.013027 | 0.013223 | 0.013323 | 0.013423 | 0.013524 | 0.013624 | 0.013724 | 0.013825 | 0.013925 | 0.014025 | 0.014126 | 0.014226 | 0.014326 | 34030.2576 | 5837.4447 | 6402.365 | 1098.2418 | 82162.8073 | 82162.8073 | 895520.3953 | 82162.8073
| BGO023-76448224 | 68 | BGO023 | BGO | North | 1602510.181 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.34007 | 0.34189 | 0.34371 | 0.34553 | 0.34735 | 0.34915 | 0.35095 | 0.35274 | 0.35454 | 0.35634 | 0.35813 | 0.35993 | 0.36173 | 0.36352 | 0.36532 | 0.36712 | 0.36891 | 0.37071 | 0.37251 | 0.3743 | 0.018943 | 0.019317 | 0.019564 | 0.019787 | 0.019945 | 0.02012 | 0.020492 | 0.0209 | 0.021161 | 0.021268 | 0.021375 | 0.021483 | 0.02159 | 0.021697 | 0.021804 | 0.021912 | 0.022019 | 0.022126 | 0.022233 | 0.022341 | 34030.2576 | 5837.4447 | 10235.8871 | 1755.8323 | 187039.4689 | 187039.4689 | 1602510.181 | 187039.4689
| BGO023-95132601 | 51 | BGO023 | BGO | North | 1201882.6358 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.12362 | 0.12466 | 0.1257 | 0.12674 | 0.12778 | 0.12823 | 0.12867 | 0.12911 | 0.12956 | 0.13 | 0.13044 | 0.13089 | 0.13133 | 0.13177 | 0.13222 | 0.13266 | 0.1331 | 0.13355 | 0.13399 | 0.13443 | 0.0068862 | 0.0070433 | 0.007155 | 0.0072581 | 0.0073374 | 0.0073893 | 0.007513 | 0.00765 | 0.0077327 | 0.0077592 | 0.0077856 | 0.0078121 | 0.0078385 | 0.007865 | 0.0078915 | 0.0079179 | 0.0079444 | 0.0079708 | 0.0079973 | 0.0080238 | 34030.2576 | 5837.4447 | 3726.7463 | 639.2745 | 64212.2548 | 64212.2548 | 1201882.6358 | 64212.2548
| BGO023-95621561 | 11 | BGO023 | BGO | North | 259229.5881 | 0.0020008 | 0.0020294 | 0.0020445 | 0.002057 | 0.0020625 | 0.0020699 | 0.0020973 | 0.0021283 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0021439 | 0.0058159 | 0.0058599 | 0.0059038 | 0.0059477 | 0.0059916 | 0.0060465 | 0.0061015 | 0.0061564 | 0.0062114 | 0.0062663 | 0.0063212 | 0.0063762 | 0.0064311 | 0.0064861 | 0.006541 | 0.0065959 | 0.0066509 | 0.0067058 | 0.0067608 | 0.0068157 | 0.00032397 | 0.00033108 | 0.00033604 | 0.0003406 | 0.00034404 | 0.00034844 | 0.00035626 | 0.00036477 | 0.00037073 | 0.00037401 | 0.00037729 | 0.00038057 | 0.00038385 | 0.00038713 | 0.0003904 | 0.00039368 | 0.00039696 | 0.00040024 | 0.00040352 | 0.0004068 | 34030.2576 | 5837.4447 | 179.8628 | 30.8531 | 3897.2855 | 3897.2855 | 259229.5881 | 3897.2855
| BLT016-15429893 | 181 | BLT016 | BLTS | South | 3290723.1948 | 0.010987 | 0.011198 | 0.011469 | 0.011739 | 0.012 | 0.012382 | 0.012826 | 0.013241 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0.013473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34977.4235 | 3675.4246 | 0 | 0 | 0 | 0 | 3434165.6948 | 0
| BLT017-15429856 | 291 | BLT017 | BLTS | South | 5290610.2193 | 0.0018009 | 0.0018147 | 0.0018186 | 0.0018263 | 0.0018275 | 0.001859 | 0.001903 | 0.0019451 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0.0019606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34977.4235 | 3675.4246 | 0 | 0 | 0 | 0 | 5521227.7193 | 0
| BLT019-15429808 | 146 | BLT019 | BLTS | South | 2654395.5052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34977.4235 | 3675.4246 | 0 | 0 | 0 | 0 | 2770100.5052 | 0
| BLT020-15429758 | 100 | BLT020 | BLTS | South | 1818079.1131 | 0.069678 | 0.071339 | 0.072322 | 0.07327 | 0.0742 | 0.07507 | 0.076113 | 0.077209 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0.07813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34977.4235 | 3675.4246 | 0 | 0 | 0 | 0 | 1897329.1131 | 0
| BLT021-15429734 | 332 | BLT021 | BLTS | South | 6036022.6556 | 0.0034494 | 0.0035594 | 0.0035782 | 0.0035905 | 0.0035773 | 0.0035813 | 0.0036496 | 0.0037052 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0.0036833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34977.4235 | 3675.4246 | 0 | 0 | 0 | 0 | 6299132.6556 | 0
| BLT022-15429547 | 139 | BLT022 | BLTS | South | 2527129.9673 | 0.0021474 | 0.0021565 | 0.0021819 | 0.0021776 | 0.0021663 | 0.0021847 | 0.0022336 | 0.0022721 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34977.4235 | 3675.4246 | 0 | 0 | 0 | 0 | 2637287.4673 | 0
| BLT022-164443534 | 114 | BLT022 | BLTS | South | 2072610.189 | 0.0021474 | 0.0021565 | 0.0021819 | 0.0021776 | 0.0021663 | 0.0021847 | 0.0022336 | 0.0022721 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0.0022467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34977.4235 | 3675.4246 | 0 | 0 | 0 | 0 | 2162955.189 | 0
| BLT030-15429658 | 245 | BLT030 | BLTS | South | 4454293.8272 | 0.0014103 | 0.0014267 | 0.0014433 | 0.0014572 | 0.0014655 | 0.001479 | 0.0015037 | 0.001528 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0.0015453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34977.4235 | 3675.4246 | 0 | 0 | 0 | 0 | 4648456.3272 | 0
| BLT031-15429682 | 36 | BLT031 | BLTS | South | 654508.4807 | 0.0032707 | 0.0033252 | 0.0033388 | 0.0033524 | 0.0033388 | 0.0033293 | 0.003366 | 0.0034204 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0.0034109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34977.4235 | 3675.4246 | 0 | 0 | 0 | 0 | 683038.4807 | 0
| BMH003-137632826 | 70 | BMH003 | BMH | South | 1272655.3792 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.25682 | 0.25834 | 0.25985 | 0.26136 | 0.26288 | 0.26375 | 0.26462 | 0.26549 | 0.26636 | 0.26723 | 0.2681 | 0.26898 | 0.26985 | 0.27072 | 0.27159 | 0.27246 | 0.27333 | 0.2742 | 0.27507 | 0.27594 | 0.0085456 | 0.0088788 | 0.0092792 | 0.0096807 | 0.010033 | 0.010455 | 0.010957 | 0.011466 | 0.011867 | 0.011906 | 0.011945 | 0.011984 | 0.012022 | 0.012061 | 0.0121 | 0.012139 | 0.012178 | 0.012216 | 0.012255 | 0.012294 | 43600.6614 | 9125.3696 | 6926.7702 | 1449.7335 | 106510.5303 | 138061.2033 | 1328130.3792 | 111153.3203
| BMH003-137632841 | 48 | BMH003 | BMH | South | 872677.9743 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.065099 | 0.065659 | 0.066218 | 0.066778 | 0.067337 | 0.067715 | 0.068094 | 0.068472 | 0.06885 | 0.069228 | 0.069606 | 0.069985 | 0.070363 | 0.070741 | 0.071119 | 0.071497 | 0.071876 | 0.072254 | 0.072632 | 0.07301 | 0.0021662 | 0.0022566 | 0.0023646 | 0.0024734 | 0.0025699 | 0.0026843 | 0.0028195 | 0.002957 | 0.0030675 | 0.0030843 | 0.0031012 | 0.003118 | 0.0031349 | 0.0031517 | 0.0031686 | 0.0031854 | 0.0032023 | 0.0032191 | 0.003236 | 0.0032528 | 43600.6614 | 9125.3696 | 1793.6641 | 375.4037 | 20209.087 | 26195.4462 | 910717.9743 | 21090.0004
| BMH003-137632864 | 62 | BMH003 | BMH | South | 1127209.0502 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.033894 | 0.034136 | 0.034378 | 0.034621 | 0.034863 | 0.035002 | 0.03514 | 0.035279 | 0.035418 | 0.035556 | 0.035695 | 0.035834 | 0.035972 | 0.036111 | 0.03625 | 0.036388 | 0.036527 | 0.036665 | 0.036804 | 0.036943 | 0.0011278 | 0.0011732 | 0.0012276 | 0.0012823 | 0.0013305 | 0.0013875 | 0.001455 | 0.0015236 | 0.001578 | 0.0015841 | 0.0015903 | 0.0015965 | 0.0016027 | 0.0016089 | 0.001615 | 0.0016212 | 0.0016274 | 0.0016336 | 0.0016397 | 0.0016459 | 43600.6614 | 9125.3696 | 921.2897 | 192.8207 | 23078.4256 | 29914.7436 | 1176344.0502 | 24084.4133
| BMH003-137632887 | 31 | BMH003 | BMH | South | 563604.5251 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.024734 | 0.024874 | 0.025013 | 0.025152 | 0.025291 | 0.025396 | 0.025501 | 0.025606 | 0.025711 | 0.025816 | 0.025921 | 0.026026 | 0.026131 | 0.026236 | 0.026341 | 0.026446 | 0.026551 | 0.026656 | 0.026761 | 0.026866 | 0.00082303 | 0.00085488 | 0.0008932 | 0.0009316 | 0.0009652 | 0.0010067 | 0.0010559 | 0.0011058 | 0.0011455 | 0.0011502 | 0.0011549 | 0.0011595 | 0.0011642 | 0.0011689 | 0.0011736 | 0.0011783 | 0.0011829 | 0.0011876 | 0.0011923 | 0.001197 | 43600.6614 | 9125.3696 | 669.4859 | 140.1196 | 13976.855 | 18117.0952 | 588172.0251 | 14586.1056
| BMH003-140036206 | 247 | BMH003 | BMH | South | 4490655.4095 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 23.4572 | 23.6124 | 23.7675 | 23.9227 | 24.0778 | 24.1446 | 24.2114 | 24.2782 | 24.3449 | 24.4117 | 24.4785 | 24.5453 | 24.6121 | 24.6788 | 24.7456 | 24.8124 | 24.8792 | 24.946 | 25.0128 | 25.0795 | 0.78053 | 0.81154 | 0.84874 | 0.88608 | 0.91891 | 0.95712 | 1.0025 | 1.0485 | 1.0846 | 1.0876 | 1.0906 | 1.0936 | 1.0965 | 1.0995 | 1.1025 | 1.1055 | 1.1084 | 1.1114 | 1.1144 | 1.1174 | 43600.6614 | 9125.3696 | 632382.8866 | 132354.1293 | 897943.2528 | 1163933.0459 | 4686402.9095 | 937084.5654
| BMH003-15408256 | 98 | BMH003 | BMH | South | 1781717.5309 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 1.2481 | 1.2494 | 1.2506 | 1.2519 | 1.2531 | 1.2512 | 1.2493 | 1.2474 | 1.2455 | 1.2436 | 1.2417 | 1.2398 | 1.2379 | 1.236 | 1.2341 | 1.2322 | 1.2303 | 1.2284 | 1.2265 | 1.2246 | 0.041532 | 0.042941 | 0.04466 | 0.046368 | 0.047824 | 0.049599 | 0.051729 | 0.053871 | 0.055491 | 0.055407 | 0.055322 | 0.055237 | 0.055153 | 0.055068 | 0.054983 | 0.054899 | 0.054814 | 0.054729 | 0.054645 | 0.05456 | 43600.6614 | 9125.3696 | 32253.9352 | 6750.5646 | 12066.9739 | 15641.467 | 1859382.5309 | 12592.9729
| BMH003-155324907 | 380 | BMH003 | BMH | South | 6908700.63 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 1.1816 | 1.1905 | 1.1995 | 1.2085 | 1.2174 | 1.2214 | 1.2254 | 1.2293 | 1.2333 | 1.2372 | 1.2412 | 1.2451 | 1.2491 | 1.2531 | 1.257 | 1.261 | 1.2649 | 1.2689 | 1.2728 | 1.2768 | 0.039317 | 0.040918 | 0.042835 | 0.044761 | 0.046463 | 0.048418 | 0.050737 | 0.053089 | 0.054946 | 0.055122 | 0.055299 | 0.055475 | 0.055651 | 0.055827 | 0.056004 | 0.05618 | 0.056356 | 0.056532 | 0.056709 | 0.056885 | 43600.6614 | 9125.3696 | 32040.6398 | 6705.9231 | 4731166.8816 | 6132638.6291 | 7209850.63 | 4937398.2676
| BMH003-24599924 | 37 | BMH003 | BMH | South | 672689.2719 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0078922 | 0.0079662 | 0.0080402 | 0.0081142 | 0.0081882 | 0.0082431 | 0.008298 | 0.0083529 | 0.0084078 | 0.0084627 | 0.0085176 | 0.0085725 | 0.0086274 | 0.0086823 | 0.0087372 | 0.0087921 | 0.008847 | 0.0089019 | 0.0089568 | 0.0090117 | 0.00026261 | 0.00027379 | 0.00028712 | 0.00030054 | 0.00031249 | 0.00032677 | 0.00034359 | 0.00036073 | 0.00037459 | 0.00037704 | 0.00037949 | 0.00038193 | 0.00038438 | 0.00038682 | 0.00038927 | 0.00039172 | 0.00039416 | 0.00039661 | 0.00039905 | 0.0004015 | 43600.6614 | 9125.3696 | 219.2771 | 45.8934 | 4307.9321 | 5584.0328 | 702011.7719 | 4495.7147
| BMH003-24599938 | 141 | BMH003 | BMH | South | 2563491.5495 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 21.0606 | 21.281 | 21.5013 | 21.7217 | 21.9421 | 21.9776 | 22.0132 | 22.0488 | 22.0844 | 22.12 | 22.1556 | 22.1912 | 22.2268 | 22.2623 | 22.2979 | 22.3335 | 22.3691 | 22.4047 | 22.4403 | 22.4759 | 0.70078 | 0.73141 | 0.76781 | 0.80455 | 0.8374 | 0.87122 | 0.91148 | 0.9522 | 0.98393 | 0.98551 | 0.9871 | 0.98869 | 0.99027 | 0.99186 | 0.99344 | 0.99503 | 0.99661 | 0.9982 | 0.99978 | 1.0014 | 43600.6614 | 9125.3696 | 571611.5094 | 119635.0269 | 508292.2822 | 658859.2122 | 2675234.0495 | 530448.7236
| BMH003-54311761 | 269 | BMH003 | BMH | South | 4890632.8144 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 1.4092 | 1.4189 | 1.4286 | 1.4384 | 1.4481 | 1.4525 | 1.457 | 1.4614 | 1.4658 | 1.4703 | 1.4747 | 1.4791 | 1.4835 | 1.488 | 1.4924 | 1.4968 | 1.5013 | 1.5057 | 1.5101 | 1.5146 | 0.046889 | 0.048766 | 0.051016 | 0.053276 | 0.055265 | 0.05758 | 0.060327 | 0.063112 | 0.065307 | 0.065504 | 0.065702 | 0.065899 | 0.066096 | 0.066294 | 0.066491 | 0.066688 | 0.066886 | 0.067083 | 0.067281 | 0.067478 | 43600.6614 | 9125.3696 | 38085.4576 | 7971.0689 | 494248.0494 | 640654.7805 | 5103815.3144 | 515792.3033
| BMH003-84023922 | 61 | BMH003 | BMH | South | 1109028.259 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0083375 | 0.0084072 | 0.0084769 | 0.0085466 | 0.0086163 | 0.0086585 | 0.0087006 | 0.0087428 | 0.0087849 | 0.008827 | 0.0088692 | 0.0089113 | 0.0089534 | 0.0089956 | 0.0090377 | 0.0090798 | 0.009122 | 0.0091641 | 0.0092062 | 0.0092484 | 0.00027743 | 0.00028895 | 0.00030271 | 0.00031656 | 0.00032883 | 0.00034323 | 0.00036026 | 0.00037756 | 0.00039139 | 0.00039327 | 0.00039515 | 0.00039703 | 0.0003989 | 0.00040078 | 0.00040266 | 0.00040453 | 0.00040641 | 0.00040829 | 0.00041017 | 0.00041204 | 43600.6614 | 9125.3696 | 228.6614 | 47.8575 | 3705.9341 | 4803.7102 | 1157370.759 | 3867.4756
| BMH003-84426167 | 68 | BMH003 | BMH | South | 1236293.7969 | 0.0011952 | 0.0012345 | 0.0012827 | 0.0013304 | 0.0013708 | 0.0014239 | 0.0014873 | 0.0015512 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.0016003 | 0.063914 | 0.064491 | 0.065068 | 0.065645 | 0.066223 | 0.066749 | 0.067275 | 0.067802 | 0.068328 | 0.068855 | 0.069381 | 0.069907 | 0.070434 | 0.07096 | 0.071486 | 0.072013 | 0.072539 | 0.073066 | 0.073592 | 0.074118 | 0.0021267 | 0.0022165 | 0.0023236 | 0.0024315 | 0.0025273 | 0.002646 | 0.0027856 | 0.0029281 | 0.0030442 | 0.0030677 | 0.0030911 | 0.0031146 | 0.003138 | 0.0031615 | 0.0031849 | 0.0032084 | 0.0032318 | 0.0032553 | 0.0032788 | 0.0033022 | 43600.6614 | 9125.3696 | 1785.2937 | 373.6518 | 55647.3423 | 72131.2627 | 1290183.7969 | 58073.0079
| BMH004-15408343 | 0 | BMH004 | BMH | South | 0 | 0.0012215 | 0.0012635 | 0.0013023 | 0.0013389 | 0.0013701 | 0.0014072 | 0.0014581 | 0.0015138 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43600.6614 | 9125.3696 | 0 | 0 | 0 | 0 | 0 | 0
| BMH004-15408369 | 234 | BMH004 | BMH | South | 4254305.1248 | 0.0012215 | 0.0012635 | 0.0013023 | 0.0013389 | 0.0013701 | 0.0014072 | 0.0014581 | 0.0015138 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 0.0015559 | 77.2219 | 77.9612 | 78.7005 | 79.4398 | 80.1791 | 80.2395 | 80.3 | 80.3604 | 80.4208 | 80.4812 | 80.5416 | 80.602 | 80.6624 | 80.7229 | 80.7833 | 80.8437 | 80.9041 | 80.9645 | 81.0249 | 81.0853 | 2.6261 | 2.7424 | 2.8534 | 2.9612 | 3.0582 | 3.1435 | 3.2596 | 3.3866 | 3.4835 | 3.4861 | 3.4887 | 3.4913 | 3.494 | 3.4966 | 3.4992 | 3.5018 | 3.5044 | 3.507 | 3.5097 | 3.5123 | 43600.6614 | 9125.3696 | 2048350.4845 | 428708.067 | 1324583.5235 | 1716953.193 | 4439750.1248 | 1382322.0694
| BMH005-15408219 | 319 | BMH005 | BMH | South | 5799672.3709 | 0.0013716 | 0.0014186 | 0.0014598 | 0.0014991 | 0.0015316 | 0.0015708 | 0.0016246 | 0.0016801 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 65.8663 | 66.4328 | 66.9992 | 67.5657 | 68.1322 | 68.0751 | 68.018 | 67.9609 | 67.9038 | 67.8468 | 67.7897 | 67.7326 | 67.6755 | 67.6184 | 67.5613 | 67.5042 | 67.4471 | 67.3901 | 67.333 | 67.2759 | 2.5152 | 2.6237 | 2.7228 | 2.8198 | 2.9051 | 2.977 | 3.0764 | 3.1788 | 3.2541 | 3.2514 | 3.2487 | 3.2459 | 3.2432 | 3.2405 | 3.2377 | 3.235 | 3.2323 | 3.2295 | 3.2268 | 3.224 | 43600.6614 | 9125.3696 | 1919354.7851 | 401710.0033 | 1511233.0372 | 1958892.2423 | 6052479.8709 | 1577107.6283
| BMH005-15408230 | 16 | BMH005 | BMH | South | 290892.6581 | 0.0013716 | 0.0014186 | 0.0014598 | 0.0014991 | 0.0015316 | 0.0015708 | 0.0016246 | 0.0016801 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.40214 | 0.40578 | 0.40942 | 0.41307 | 0.41671 | 0.41759 | 0.41846 | 0.41934 | 0.42021 | 0.42109 | 0.42196 | 0.42284 | 0.42371 | 0.42459 | 0.42546 | 0.42634 | 0.42721 | 0.42809 | 0.42896 | 0.42984 | 0.015356 | 0.016026 | 0.016639 | 0.017239 | 0.017768 | 0.018261 | 0.018926 | 0.019614 | 0.020138 | 0.02018 | 0.020222 | 0.020264 | 0.020305 | 0.020347 | 0.020389 | 0.020431 | 0.020473 | 0.020515 | 0.020557 | 0.020599 | 43600.6614 | 9125.3696 | 11921.4758 | 2495.0969 | 19567.8538 | 25364.2662 | 303572.6581 | 20420.8158
| BMH005-65434147 | 152 | BMH005 | BMH | South | 2763480.252 | 0.0013716 | 0.0014186 | 0.0014598 | 0.0014991 | 0.0015316 | 0.0015708 | 0.0016246 | 0.0016801 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 0.0017214 | 8.4955 | 8.5973 | 8.6992 | 8.801 | 8.9029 | 8.9212 | 8.9395 | 8.9578 | 8.9761 | 8.9944 | 9.0127 | 9.031 | 9.0492 | 9.0675 | 9.0858 | 9.1041 | 9.1224 | 9.1407 | 9.159 | 9.1773 | 0.32441 | 0.33955 | 0.35353 | 0.36731 | 0.37961 | 0.39013 | 0.40432 | 0.41899 | 0.43016 | 0.43103 | 0.43191 | 0.43279 | 0.43366 | 0.43454 | 0.43542 | 0.4363 | 0.43717 | 0.43805 | 0.43893 | 0.4398 | 43600.6614 | 9125.3696 | 254245.6537 | 53212.1644 | 155370.4314 | 201394.441 | 2883940.252 | 162143.0227
| BMH006-15408306 | 163 | BMH006 | BMH | South | 2963468.9544 | 0.002817 | 0.0028832 | 0.002937 | 0.0029769 | 0.0029968 | 0.0030727 | 0.0031835 | 0.0032885 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 10.6533 | 10.7347 | 10.8161 | 10.8976 | 10.979 | 11.0123 | 11.0456 | 11.0789 | 11.1123 | 11.1456 | 11.1789 | 11.2122 | 11.2455 | 11.2789 | 11.3122 | 11.3455 | 11.3788 | 11.4122 | 11.4455 | 11.4788 | 0.83549 | 0.86166 | 0.8844 | 0.90314 | 0.91598 | 0.94202 | 0.97897 | 1.0143 | 1.0303 | 1.0334 | 1.0365 | 1.0396 | 1.0427 | 1.0458 | 1.0489 | 1.052 | 1.055 | 1.0581 | 1.0612 | 1.0643 | 43600.6614 | 9125.3696 | 618784.5523 | 129508.0756 | 565107.0847 | 732503.7615 | 3092646.4544 | 589740.0812
| BMH006-201878277 | 281 | BMH006 | BMH | South | 5108802.3079 | 0.002817 | 0.0028832 | 0.002937 | 0.0029769 | 0.0029968 | 0.0030727 | 0.0031835 | 0.0032885 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 2.5645 | 2.5844 | 2.6043 | 2.6243 | 2.6442 | 2.6527 | 2.6613 | 2.6699 | 2.6784 | 2.687 | 2.6956 | 2.7042 | 2.7127 | 2.7213 | 2.7299 | 2.7385 | 2.747 | 2.7556 | 2.7642 | 2.7727 | 0.20113 | 0.20745 | 0.21295 | 0.21749 | 0.2206 | 0.22692 | 0.23587 | 0.24443 | 0.24835 | 0.24914 | 0.24994 | 0.25073 | 0.25153 | 0.25232 | 0.25311 | 0.25391 | 0.2547 | 0.2555 | 0.25629 | 0.25709 | 43600.6614 | 9125.3696 | 149177.5689 | 31222.0138 | 937029.171 | 1214597.0401 | 5331494.8079 | 977874.2373
| BMH006-24602242 | 1 | BMH006 | BMH | South | 18180.7911 | 0.002817 | 0.0028832 | 0.002937 | 0.0029769 | 0.0029968 | 0.0030727 | 0.0031835 | 0.0032885 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0034569 | 0.0034883 | 0.0035196 | 0.003551 | 0.0035823 | 0.0035906 | 0.0035989 | 0.0036072 | 0.0036155 | 0.0036237 | 0.003632 | 0.0036403 | 0.0036486 | 0.0036569 | 0.0036652 | 0.0036735 | 0.0036818 | 0.0036901 | 0.0036984 | 0.0037066 | 0.00027111 | 0.00028 | 0.00028779 | 0.00029429 | 0.00029887 | 0.00030715 | 0.00031897 | 0.00033024 | 0.00033523 | 0.00033599 | 0.00033676 | 0.00033753 | 0.0003383 | 0.00033907 | 0.00033984 | 0.00034061 | 0.00034137 | 0.00034214 | 0.00034291 | 0.00034368 | 43600.6614 | 9125.3696 | 200.9867 | 42.0654 | 315.7432 | 409.273 | 18973.2911 | 329.5064
| BMH006-74239819 | 31 | BMH006 | BMH | South | 563604.5251 | 0.002817 | 0.0028832 | 0.002937 | 0.0029769 | 0.0029968 | 0.0030727 | 0.0031835 | 0.0032885 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.020735 | 0.02091 | 0.021084 | 0.021259 | 0.021434 | 0.021504 | 0.021575 | 0.021646 | 0.021716 | 0.021787 | 0.021858 | 0.021929 | 0.021999 | 0.02207 | 0.022141 | 0.022211 | 0.022282 | 0.022353 | 0.022423 | 0.022494 | 0.0016261 | 0.0016784 | 0.001724 | 0.0017619 | 0.0017882 | 0.0018395 | 0.0019122 | 0.0019817 | 0.0020136 | 0.0020201 | 0.0020267 | 0.0020332 | 0.0020398 | 0.0020463 | 0.0020529 | 0.0020594 | 0.002066 | 0.0020726 | 0.0020791 | 0.0020857 | 43600.6614 | 9125.3696 | 1209.1526 | 253.0687 | 11774.9416 | 15262.9285 | 588172.0251 | 12288.2109
| BMH006-84024816 | 40 | BMH006 | BMH | South | 727231.6453 | 0.002817 | 0.0028832 | 0.002937 | 0.0029769 | 0.0029968 | 0.0030727 | 0.0031835 | 0.0032885 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.023689 | 0.023895 | 0.024102 | 0.024308 | 0.024515 | 0.024602 | 0.024689 | 0.024776 | 0.024863 | 0.02495 | 0.025037 | 0.025124 | 0.025211 | 0.025298 | 0.025385 | 0.025472 | 0.025559 | 0.025646 | 0.025733 | 0.025821 | 0.0018578 | 0.001918 | 0.0019707 | 0.0020146 | 0.0020453 | 0.0021045 | 0.0021882 | 0.0022683 | 0.0023053 | 0.0023134 | 0.0023214 | 0.0023295 | 0.0023376 | 0.0023457 | 0.0023537 | 0.0023618 | 0.0023699 | 0.0023779 | 0.002386 | 0.0023941 | 43600.6614 | 9125.3696 | 1384.5596 | 289.7804 | 21745.3097 | 28186.7306 | 758931.6453 | 22693.187
| BMH006-85029171 | 35 | BMH006 | BMH | South | 636327.6896 | 0.002817 | 0.0028832 | 0.002937 | 0.0029769 | 0.0029968 | 0.0030727 | 0.0031835 | 0.0032885 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.04975 | 0.050172 | 0.050595 | 0.051017 | 0.051439 | 0.051553 | 0.051667 | 0.051781 | 0.051895 | 0.052009 | 0.052123 | 0.052237 | 0.052351 | 0.052465 | 0.052579 | 0.052693 | 0.052807 | 0.052921 | 0.053035 | 0.053149 | 0.0039017 | 0.0040273 | 0.004137 | 0.0042281 | 0.0042916 | 0.00441 | 0.0045792 | 0.0047406 | 0.0048117 | 0.0048223 | 0.0048329 | 0.0048434 | 0.004854 | 0.0048646 | 0.0048751 | 0.0048857 | 0.0048963 | 0.0049068 | 0.0049174 | 0.004928 | 43600.6614 | 9125.3696 | 2885.4606 | 603.9104 | 19039.494 | 24679.395 | 664065.1896 | 19869.4248
| BMH006-85031037 | 52 | BMH006 | BMH | South | 945401.1388 | 0.002817 | 0.0028832 | 0.002937 | 0.0029769 | 0.0029968 | 0.0030727 | 0.0031835 | 0.0032885 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.0033305 | 0.020241 | 0.020413 | 0.020584 | 0.020756 | 0.020928 | 0.020969 | 0.02101 | 0.021051 | 0.021092 | 0.021133 | 0.021174 | 0.021215 | 0.021256 | 0.021297 | 0.021338 | 0.021379 | 0.02142 | 0.021461 | 0.021502 | 0.021543 | 0.0015874 | 0.0016385 | 0.0016831 | 0.0017202 | 0.001746 | 0.0017937 | 0.0018621 | 0.0019272 | 0.0019556 | 0.0019594 | 0.0019632 | 0.001967 | 0.0019708 | 0.0019746 | 0.0019784 | 0.0019822 | 0.001986 | 0.0019898 | 0.0019936 | 0.0019975 | 43600.6614 | 9125.3696 | 1172.3614 | 245.3686 | 15963.5755 | 20692.3244 | 986611.1388 | 16659.4272
| CDN001-144336613 | 20 | CDN001 | CDN | South | 363615.8226 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0045509 | 0.0045572 | 0.0045636 | 0.00457 | 0.0045763 | 0.0045697 | 0.004563 | 0.0045564 | 0.0045498 | 0.0045431 | 0.0045365 | 0.0045298 | 0.0045232 | 0.0045165 | 0.0045099 | 0.0045033 | 0.0044966 | 0.00449 | 0.0044833 | 0.0044767 | 0.0003068 | 0.00030787 | 0.00031045 | 0.00031066 | 0.00030946 | 0.0003109 | 0.00031483 | 0.00031641 | 0.0003112 | 0.00031075 | 0.00031029 | 0.00030984 | 0.00030939 | 0.00030893 | 0.00030848 | 0.00030802 | 0.00030757 | 0.00030711 | 0.00030666 | 0.00030621 | 32556.0223 | 6405.4024 | 145.8157 | 28.6893 | 2386.2693 | 3093.1328 | 379465.8226 | 2490.2867
| CDN001-147732702 | 28 | CDN001 | CDN | South | 509062.1517 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0030979 | 0.0031356 | 0.0031733 | 0.0032109 | 0.0032486 | 0.0031819 | 0.0031153 | 0.0030487 | 0.0029821 | 0.0029154 | 0.0028488 | 0.0027822 | 0.0027156 | 0.0026489 | 0.0025823 | 0.0025157 | 0.0024491 | 0.0023824 | 0.0023158 | 0.0022492 | 0.00020885 | 0.00021183 | 0.00021587 | 0.00021827 | 0.00021968 | 0.00021649 | 0.00021494 | 0.00021171 | 0.00020397 | 0.00019942 | 0.00019486 | 0.0001903 | 0.00018574 | 0.00018119 | 0.00017663 | 0.00017207 | 0.00016752 | 0.00016296 | 0.0001584 | 0.00015384 | 32556.0223 | 6405.4024 | 92.7986 | 18.2581 | 2658.2587 | 3445.6912 | 531252.1517 | 2774.1321
| CDN001-147732747 | 31 | CDN001 | CDN | South | 563604.5251 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0062139 | 0.0062767 | 0.0063396 | 0.0064025 | 0.0064654 | 0.0063869 | 0.0063085 | 0.00623 | 0.0061516 | 0.0060731 | 0.0059947 | 0.0059162 | 0.0058378 | 0.0057593 | 0.0056809 | 0.0056024 | 0.005524 | 0.0054455 | 0.0053671 | 0.0052886 | 0.00041891 | 0.00042403 | 0.00043127 | 0.00043523 | 0.0004372 | 0.00043454 | 0.00043526 | 0.00043263 | 0.00042077 | 0.0004154 | 0.00041003 | 0.00040467 | 0.0003993 | 0.00039394 | 0.00038857 | 0.0003832 | 0.00037784 | 0.00037247 | 0.00036711 | 0.00036174 | 32556.0223 | 6405.4024 | 193.7035 | 38.1112 | 6142.4555 | 7961.9808 | 588172.0251 | 6410.2049
| CDN001-15400083 | 618 | CDN001 | CDN | South | 11235728.9192 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 7.0535 | 7.1147 | 7.1759 | 7.2371 | 7.2983 | 7.2268 | 7.1553 | 7.0839 | 7.0124 | 6.9409 | 6.8694 | 6.798 | 6.7265 | 6.655 | 6.5835 | 6.5121 | 6.4406 | 6.3691 | 6.2976 | 6.2262 | 0.47551 | 0.48064 | 0.48816 | 0.49196 | 0.49353 | 0.49168 | 0.49369 | 0.49192 | 0.47965 | 0.47476 | 0.46987 | 0.46498 | 0.46009 | 0.4552 | 0.45031 | 0.44542 | 0.44054 | 0.43565 | 0.43076 | 0.42587 | 32556.0223 | 6405.4024 | 221626.7651 | 43605.1003 | 743432.4646 | 963652.8926 | 11725493.9192 | 775838.6578
| CDN001-15400094 | 0 | CDN001 | CDN | South | 0 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.4951 | 0.50037 | 0.50564 | 0.5109 | 0.51617 | 0.50989 | 0.50361 | 0.49733 | 0.49105 | 0.48478 | 0.4785 | 0.47222 | 0.46594 | 0.45966 | 0.45338 | 0.4471 | 0.44083 | 0.43455 | 0.42827 | 0.42199 | 0.033378 | 0.033803 | 0.034397 | 0.03473 | 0.034904 | 0.034691 | 0.034747 | 0.034536 | 0.033588 | 0.033159 | 0.032729 | 0.0323 | 0.03187 | 0.031441 | 0.031011 | 0.030582 | 0.030152 | 0.029723 | 0.029294 | 0.028864 | 32556.0223 | 6405.4024 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001-154719434 | 22 | CDN001 | CDN | South | 399977.4049 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0028577 | 0.002887 | 0.0029164 | 0.0029457 | 0.0029751 | 0.0029363 | 0.0028974 | 0.0028586 | 0.0028198 | 0.002781 | 0.0027421 | 0.0027033 | 0.0026645 | 0.0026257 | 0.0025868 | 0.002548 | 0.0025092 | 0.0024704 | 0.0024316 | 0.0023927 | 0.00019265 | 0.00019504 | 0.0001984 | 0.00020025 | 0.00020118 | 0.00019977 | 0.00019991 | 0.00019851 | 0.00019287 | 0.00019022 | 0.00018756 | 0.00018491 | 0.00018225 | 0.0001796 | 0.00017694 | 0.00017428 | 0.00017163 | 0.00016897 | 0.00016632 | 0.00016366 | 32556.0223 | 6405.4024 | 88.6847 | 17.4487 | 939.2068 | 1217.4198 | 417412.4049 | 980.1468
| CDN001-156321963 | 316 | CDN001 | CDN | South | 5745129.9975 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 1.4408 | 1.4563 | 1.4718 | 1.4873 | 1.5028 | 1.4829 | 1.4631 | 1.4432 | 1.4234 | 1.4036 | 1.3837 | 1.3639 | 1.344 | 1.3242 | 1.3044 | 1.2845 | 1.2647 | 1.2448 | 1.225 | 1.2052 | 0.097129 | 0.098379 | 0.10012 | 0.1011 | 0.10162 | 0.10089 | 0.10095 | 0.10022 | 0.09736 | 0.096003 | 0.094646 | 0.093289 | 0.091932 | 0.090575 | 0.089218 | 0.087861 | 0.086504 | 0.085147 | 0.08379 | 0.082432 | 32556.0223 | 6405.4024 | 44744.446 | 8803.4767 | 276070.4564 | 357848.3676 | 5995559.9975 | 288104.3572
| CDN001-158379454 | 32 | CDN001 | CDN | South | 581785.3162 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.019597 | 0.019627 | 0.019657 | 0.019687 | 0.019718 | 0.019686 | 0.019655 | 0.019623 | 0.019591 | 0.01956 | 0.019528 | 0.019497 | 0.019465 | 0.019434 | 0.019402 | 0.019371 | 0.019339 | 0.019308 | 0.019276 | 0.019244 | 0.0013211 | 0.0013259 | 0.0013372 | 0.0013383 | 0.0013333 | 0.0013394 | 0.0013561 | 0.0013627 | 0.0013401 | 0.0013379 | 0.0013357 | 0.0013336 | 0.0013314 | 0.0013293 | 0.0013271 | 0.0013249 | 0.0013228 | 0.0013206 | 0.0013185 | 0.0013163 | 32556.0223 | 6405.4024 | 627.7318 | 123.5063 | 7146.3123 | 9263.2013 | 607145.3162 | 7457.8198
| CDN001-160252941 | 45 | CDN001 | CDN | South | 818135.6009 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.000962 | 0.00097372 | 0.00098545 | 0.00099717 | 0.0010089 | 0.00099493 | 0.00098097 | 0.000967 | 0.00095304 | 0.00093907 | 0.00092511 | 0.00091114 | 0.00089718 | 0.00088322 | 0.00086925 | 0.00085529 | 0.00084132 | 0.00082736 | 0.00081339 | 0.00079943 | 6.4853e-05 | 6.5781e-05 | 6.7038e-05 | 6.7786e-05 | 6.8224e-05 | 6.7691e-05 | 6.7683e-05 | 6.7151e-05 | 6.5188e-05 | 6.4233e-05 | 6.3278e-05 | 6.2322e-05 | 6.1367e-05 | 6.0412e-05 | 5.9457e-05 | 5.8501e-05 | 5.7546e-05 | 5.6591e-05 | 5.5636e-05 | 5.4681e-05 | 32556.0223 | 6405.4024 | 29.908 | 5.8844 | 579.6765 | 751.389 | 853798.1009 | 604.9446
| CDN001-162435420 | 23 | CDN001 | CDN | South | 418158.196 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.00053254 | 0.0005405 | 0.00054847 | 0.00055643 | 0.0005644 | 0.00055318 | 0.00054196 | 0.00053074 | 0.00051952 | 0.0005083 | 0.00049708 | 0.00048586 | 0.00047464 | 0.00046342 | 0.0004522 | 0.00044098 | 0.00042976 | 0.00041854 | 0.00040732 | 0.0003961 | 3.5901e-05 | 3.6514e-05 | 3.7311e-05 | 3.7825e-05 | 3.8166e-05 | 3.7636e-05 | 3.7393e-05 | 3.6856e-05 | 3.5535e-05 | 3.4768e-05 | 3.4e-05 | 3.3233e-05 | 3.2465e-05 | 3.1698e-05 | 3.093e-05 | 3.0163e-05 | 2.9396e-05 | 2.8628e-05 | 2.7861e-05 | 2.7093e-05 | 32556.0223 | 6405.4024 | 16.1504 | 3.1776 | 178.8287 | 231.8015 | 436385.696 | 186.6238
| CDN001-162435922 | 13 | CDN001 | CDN | South | 236350.2847 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.004864 | 0.0049105 | 0.0049569 | 0.0050034 | 0.0050498 | 0.0049908 | 0.0049318 | 0.0048728 | 0.0048138 | 0.0047547 | 0.0046957 | 0.0046367 | 0.0045777 | 0.0045186 | 0.0044596 | 0.0044006 | 0.0043416 | 0.0042826 | 0.0042235 | 0.0041645 | 0.00032791 | 0.00033173 | 0.00033721 | 0.00034012 | 0.00034148 | 0.00033955 | 0.00034027 | 0.00033838 | 0.00032926 | 0.00032522 | 0.00032119 | 0.00031715 | 0.00031311 | 0.00030908 | 0.00030504 | 0.000301 | 0.00029696 | 0.00029293 | 0.00028889 | 0.00028485 | 32556.0223 | 6405.4024 | 151.7144 | 29.8498 | 1793.3242 | 2324.5448 | 246652.7847 | 1871.4951
| CDN001-164044162 | 1 | CDN001 | CDN | South | 18180.7911 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32556.0223 | 6405.4024 | 0 | 0 | 92.1529 | 119.4505 | 18973.2911 | 96.1698
| CDN001-164044516 | 102 | CDN001 | CDN | South | 1854440.6954 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.056501 | 0.056955 | 0.057409 | 0.057863 | 0.058317 | 0.057492 | 0.056667 | 0.055843 | 0.055018 | 0.054193 | 0.053369 | 0.052544 | 0.05172 | 0.050895 | 0.05007 | 0.049246 | 0.048421 | 0.047596 | 0.046772 | 0.045947 | 0.003809 | 0.0038476 | 0.0039054 | 0.0039334 | 0.0039435 | 0.0039115 | 0.0039098 | 0.0038779 | 0.0037632 | 0.0037068 | 0.0036504 | 0.003594 | 0.0035376 | 0.0034812 | 0.0034248 | 0.0033684 | 0.003312 | 0.0032556 | 0.0031992 | 0.0031428 | 32556.0223 | 6405.4024 | 1730.6105 | 340.4979 | 28832.8497 | 37373.75 | 1935275.6954 | 30089.6726
| CDN001-171348505 | 13 | CDN001 | CDN | South | 236350.2847 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0026855 | 0.0027006 | 0.0027157 | 0.0027309 | 0.002746 | 0.0027189 | 0.0026919 | 0.0026648 | 0.0026378 | 0.0026107 | 0.0025836 | 0.0025566 | 0.0025295 | 0.0025024 | 0.0024754 | 0.0024483 | 0.0024213 | 0.0023942 | 0.0023671 | 0.0023401 | 0.00018104 | 0.00018244 | 0.00018474 | 0.00018564 | 0.00018569 | 0.00018499 | 0.00018573 | 0.00018505 | 0.00018042 | 0.00017857 | 0.00017672 | 0.00017487 | 0.00017302 | 0.00017117 | 0.00016932 | 0.00016747 | 0.00016561 | 0.00016376 | 0.00016191 | 0.00016006 | 32556.0223 | 6405.4024 | 83.5256 | 16.4337 | 2221.4238 | 2879.4565 | 246652.7847 | 2318.2556
| CDN001-177002783 | 16 | CDN001 | CDN | South | 290892.6581 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.011224 | 0.011346 | 0.011468 | 0.01159 | 0.011713 | 0.011556 | 0.011398 | 0.011241 | 0.011084 | 0.010927 | 0.01077 | 0.010613 | 0.010455 | 0.010298 | 0.010141 | 0.009984 | 0.0098268 | 0.0096696 | 0.0095125 | 0.0093553 | 0.00075664 | 0.00076648 | 0.00078015 | 0.0007879 | 0.00079204 | 0.0007862 | 0.00078645 | 0.00078063 | 0.00075816 | 0.0007474 | 0.00073665 | 0.0007259 | 0.00071515 | 0.0007044 | 0.00069365 | 0.0006829 | 0.00067215 | 0.0006614 | 0.00065065 | 0.0006399 | 32556.0223 | 6405.4024 | 348.308 | 68.5297 | 4560.6116 | 5911.5612 | 303572.6581 | 4759.4084
| CDN001-178141597 | 1 | CDN001 | CDN | South | 18180.7911 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 4.1902e-06 | 2.8248e-07 | 2.8307e-07 | 2.8505e-07 | 2.8484e-07 | 2.8335e-07 | 2.8508e-07 | 2.8911e-07 | 2.9098e-07 | 2.8661e-07 | 2.8661e-07 | 2.8661e-07 | 2.8661e-07 | 2.8661e-07 | 2.8661e-07 | 2.8661e-07 | 2.8661e-07 | 2.8661e-07 | 2.8661e-07 | 2.8661e-07 | 2.8661e-07 | 32556.0223 | 6405.4024 | 0.13462 | 0.026486 | 0.013433 | 0.017412 | 18973.2911 | 0.014018
| CDN001-202076817 | 312 | CDN001 | CDN | South | 5672406.833 | 0.0024215 | 0.0024266 | 0.0024435 | 0.0024417 | 0.002429 | 0.0024438 | 0.0024783 | 0.0024944 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.0024569 | 0.43317 | 0.43721 | 0.44125 | 0.44529 | 0.44933 | 0.44333 | 0.43734 | 0.43135 | 0.42536 | 0.41936 | 0.41337 | 0.40738 | 0.40138 | 0.39539 | 0.3894 | 0.3834 | 0.37741 | 0.37142 | 0.36543 | 0.35943 | 0.029202 | 0.029536 | 0.030017 | 0.03027 | 0.030384 | 0.030163 | 0.030175 | 0.029954 | 0.029094 | 0.028684 | 0.028274 | 0.027865 | 0.027455 | 0.027045 | 0.026635 | 0.026225 | 0.025815 | 0.025405 | 0.024995 | 0.024585 | 32556.0223 | 6405.4024 | 13381.3408 | 2632.7809 | 119410.1832 | 154782.0064 | 5919666.833 | 124615.2686
| CDN002-15400020 | 920 | CDN002 | CDN | South | 16726327.8409 | 0.0018667 | 0.0018931 | 0.0019029 | 0.0019059 | 0.0018931 | 0.0018765 | 0.0018961 | 0.0019255 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 2.8324 | 2.8603 | 2.8882 | 2.9161 | 2.944 | 2.9156 | 2.8871 | 2.8586 | 2.8301 | 2.8017 | 2.7732 | 2.7447 | 2.7163 | 2.6878 | 2.6593 | 2.6309 | 2.6024 | 2.5739 | 2.5455 | 2.517 | 0.1472 | 0.15075 | 0.15301 | 0.15473 | 0.15516 | 0.15231 | 0.1524 | 0.15324 | 0.15071 | 0.14919 | 0.14768 | 0.14616 | 0.14464 | 0.14313 | 0.14161 | 0.1401 | 0.13858 | 0.13706 | 0.13555 | 0.13403 | 32556.0223 | 6405.4024 | 69415.3305 | 13657.477 | 1537824.5069 | 1993360.668 | 17455427.8409 | 1604858.2192
| CDN002-15400044 | 0 | CDN002 | CDN | South | 0 | 0.0018667 | 0.0018931 | 0.0019029 | 0.0019059 | 0.0018931 | 0.0018765 | 0.0018961 | 0.0019255 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32556.0223 | 6405.4024 | 0 | 0 | 0 | 0 | 0 | 0
| CDN002-162961049 | 26 | CDN002 | CDN | South | 472700.5694 | 0.0018667 | 0.0018931 | 0.0019029 | 0.0019059 | 0.0018931 | 0.0018765 | 0.0018961 | 0.0019255 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.003308 | 0.0033491 | 0.0033901 | 0.0034312 | 0.0034722 | 0.0034231 | 0.0033739 | 0.0033248 | 0.0032756 | 0.0032264 | 0.0031773 | 0.0031281 | 0.003079 | 0.0030298 | 0.0029806 | 0.0029315 | 0.0028823 | 0.0028332 | 0.002784 | 0.0027348 | 0.00017191 | 0.00017651 | 0.0001796 | 0.00018206 | 0.000183 | 0.00017882 | 0.0001781 | 0.00017823 | 0.00017443 | 0.00017181 | 0.00016919 | 0.00016657 | 0.00016396 | 0.00016134 | 0.00015872 | 0.0001561 | 0.00015349 | 0.00015087 | 0.00014825 | 0.00014563 | 32556.0223 | 6405.4024 | 79.776 | 15.6959 | 1561.4307 | 2023.9596 | 493305.5694 | 1629.4934
| CDN002-162961261 | 7 | CDN002 | CDN | South | 127265.5379 | 0.0018667 | 0.0018931 | 0.0019029 | 0.0019059 | 0.0018931 | 0.0018765 | 0.0018961 | 0.0019255 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.00014585 | 0.00014779 | 0.00014973 | 0.00015166 | 0.0001536 | 0.00015207 | 0.00015054 | 0.00014901 | 0.00014748 | 0.00014595 | 0.00014442 | 0.00014289 | 0.00014136 | 0.00013983 | 0.0001383 | 0.00013677 | 0.00013524 | 0.00013371 | 0.00013218 | 0.00013065 | 7.5796e-06 | 7.7892e-06 | 7.9322e-06 | 8.0472e-06 | 8.0955e-06 | 7.9443e-06 | 7.9465e-06 | 7.9878e-06 | 7.8534e-06 | 7.772e-06 | 7.6905e-06 | 7.609e-06 | 7.5275e-06 | 7.4461e-06 | 7.3646e-06 | 7.2831e-06 | 7.2016e-06 | 7.1202e-06 | 7.0387e-06 | 6.9572e-06 | 32556.0223 | 6405.4024 | 3.6082 | 0.70991 | 44.3602 | 57.5007 | 132813.0379 | 46.2939
| CDN002-162961458 | 5 | CDN002 | CDN | South | 90903.9557 | 0.0018667 | 0.0018931 | 0.0019029 | 0.0019059 | 0.0018931 | 0.0018765 | 0.0018961 | 0.0019255 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.000914 | 0.00092526 | 0.00093652 | 0.00094778 | 0.00095904 | 0.00094989 | 0.00094073 | 0.00093158 | 0.00092243 | 0.00091327 | 0.00090412 | 0.00089497 | 0.00088581 | 0.00087666 | 0.00086751 | 0.00085835 | 0.0008492 | 0.00084005 | 0.00083089 | 0.00082174 | 4.7499e-05 | 4.8766e-05 | 4.9615e-05 | 5.0289e-05 | 5.0546e-05 | 4.9623e-05 | 4.9658e-05 | 4.9938e-05 | 4.912e-05 | 4.8633e-05 | 4.8145e-05 | 4.7658e-05 | 4.717e-05 | 4.6683e-05 | 4.6195e-05 | 4.5708e-05 | 4.5221e-05 | 4.4733e-05 | 4.4246e-05 | 4.3758e-05 | 32556.0223 | 6405.4024 | 22.5926 | 4.4451 | 595.1962 | 771.5059 | 94866.4557 | 621.1408
| CDN002-163179235 | 29 | CDN002 | CDN | South | 527242.9428 | 0.0018667 | 0.0018931 | 0.0019029 | 0.0019059 | 0.0018931 | 0.0018765 | 0.0018961 | 0.0019255 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.017873 | 0.01803 | 0.018188 | 0.018345 | 0.018503 | 0.0183 | 0.018098 | 0.017895 | 0.017693 | 0.01749 | 0.017288 | 0.017085 | 0.016882 | 0.01668 | 0.016477 | 0.016275 | 0.016072 | 0.01587 | 0.015667 | 0.015465 | 0.00092881 | 0.00095028 | 0.00096355 | 0.0009734 | 0.0009752 | 0.00095603 | 0.00095533 | 0.00095929 | 0.00094215 | 0.00093137 | 0.00092058 | 0.00090979 | 0.00089901 | 0.00088822 | 0.00087743 | 0.00086665 | 0.00085586 | 0.00084507 | 0.00083429 | 0.0008235 | 32556.0223 | 6405.4024 | 433.5839 | 85.3077 | 11042.5476 | 14313.5838 | 550225.4428 | 11523.8918
| CDN002-163194789 | 8 | CDN002 | CDN | South | 145446.3291 | 0.0018667 | 0.0018931 | 0.0019029 | 0.0019059 | 0.0018931 | 0.0018765 | 0.0018961 | 0.0019255 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 1.7509e-05 | 1.7731e-05 | 1.7954e-05 | 1.8177e-05 | 1.84e-05 | 1.8135e-05 | 1.787e-05 | 1.7605e-05 | 1.734e-05 | 1.7075e-05 | 1.681e-05 | 1.6545e-05 | 1.628e-05 | 1.6015e-05 | 1.575e-05 | 1.5485e-05 | 1.522e-05 | 1.4955e-05 | 1.469e-05 | 1.4425e-05 | 9.0989e-07 | 9.3453e-07 | 9.5118e-07 | 9.6447e-07 | 9.6977e-07 | 9.4739e-07 | 9.433e-07 | 9.4373e-07 | 9.2337e-07 | 9.0926e-07 | 8.9515e-07 | 8.8103e-07 | 8.6692e-07 | 8.5281e-07 | 8.387e-07 | 8.2459e-07 | 8.1048e-07 | 7.9637e-07 | 7.8225e-07 | 7.6814e-07 | 32556.0223 | 6405.4024 | 0.4221 | 0.083047 | 35.5884 | 46.1304 | 151786.3291 | 37.1397
| CDN002-163309826 | 22 | CDN002 | CDN | South | 399977.4049 | 0.0018667 | 0.0018931 | 0.0019029 | 0.0019059 | 0.0018931 | 0.0018765 | 0.0018961 | 0.0019255 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.017983 | 0.018204 | 0.018424 | 0.018644 | 0.018865 | 0.018665 | 0.018465 | 0.018265 | 0.018066 | 0.017866 | 0.017666 | 0.017466 | 0.017266 | 0.017067 | 0.016867 | 0.016667 | 0.016467 | 0.016268 | 0.016068 | 0.015868 | 0.00093456 | 0.00095942 | 0.00097606 | 0.00098926 | 0.00099426 | 0.00097507 | 0.00097471 | 0.00097912 | 0.00096201 | 0.00095137 | 0.00094073 | 0.00093009 | 0.00091945 | 0.00090881 | 0.00089818 | 0.00088754 | 0.0008769 | 0.00086626 | 0.00085562 | 0.00084498 | 32556.0223 | 6405.4024 | 441.9391 | 86.9516 | 20491.8637 | 26561.9874 | 417412.4049 | 21385.1033
| CDN002-85030215 | 228 | CDN002 | CDN | South | 4145220.378 | 0.0018667 | 0.0018931 | 0.0019029 | 0.0019059 | 0.0018931 | 0.0018765 | 0.0018961 | 0.0019255 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.0019127 | 0.40168 | 0.40652 | 0.41135 | 0.41619 | 0.42103 | 0.41544 | 0.40986 | 0.40428 | 0.39869 | 0.39311 | 0.38753 | 0.38195 | 0.37636 | 0.37078 | 0.3652 | 0.35961 | 0.35403 | 0.34845 | 0.34286 | 0.33728 | 0.020875 | 0.021425 | 0.021793 | 0.022083 | 0.02219 | 0.021703 | 0.021635 | 0.021672 | 0.021231 | 0.020934 | 0.020636 | 0.020339 | 0.020042 | 0.019744 | 0.019447 | 0.01915 | 0.018852 | 0.018555 | 0.018258 | 0.017961 | 32556.0223 | 6405.4024 | 9723.1093 | 1913.0233 | 188561.3105 | 244417.1609 | 4325910.378 | 196780.691
| CDN003-15400133 | 202 | CDN003 | CDN | South | 3672519.8086 | 0.0010038 | 0.0010017 | 0.0010017 | 0.00099884 | 0.00099303 | 0.000991 | 0.00099681 | 0.00099971 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 0.0009939 | 1.1794 | 1.1883 | 1.1971 | 1.206 | 1.2149 | 1.2037 | 1.1926 | 1.1815 | 1.1703 | 1.1592 | 1.1481 | 1.137 | 1.1258 | 1.1147 | 1.1036 | 1.0924 | 1.0813 | 1.0702 | 1.0591 | 1.0479 | 0.032958 | 0.033139 | 0.033386 | 0.033536 | 0.033586 | 0.03321 | 0.033096 | 0.032882 | 0.032383 | 0.032076 | 0.031768 | 0.03146 | 0.031152 | 0.030844 | 0.030536 | 0.030228 | 0.02992 | 0.029612 | 0.029304 | 0.028996 | 32556.0223 | 6405.4024 | 15054.5526 | 2961.9856 | 35558.911 | 46092.2129 | 3832604.8086 | 37108.9226
| CDN004-139244393 | 68 | CDN004 | CDN | South | 1236293.7969 | 0.00096252 | 0.00096696 | 0.00097522 | 0.00097522 | 0.00096252 | 0.00095616 | 0.00097332 | 0.00098158 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.0019911 | 0.0020167 | 0.0020422 | 0.0020677 | 0.0020932 | 0.0020913 | 0.0020893 | 0.0020874 | 0.0020854 | 0.0020835 | 0.0020815 | 0.0020795 | 0.0020776 | 0.0020756 | 0.0020737 | 0.0020717 | 0.0020698 | 0.0020678 | 0.0020659 | 0.0020639 | 5.3356e-05 | 5.4289e-05 | 5.5446e-05 | 5.6139e-05 | 5.6091e-05 | 5.5669e-05 | 5.6615e-05 | 5.7042e-05 | 5.625e-05 | 5.6198e-05 | 5.6145e-05 | 5.6092e-05 | 5.604e-05 | 5.5987e-05 | 5.5934e-05 | 5.5881e-05 | 5.5829e-05 | 5.5776e-05 | 5.5723e-05 | 5.567e-05 | 32556.0223 | 6405.4024 | 26.2421 | 5.1631 | 2308.8949 | 2992.8384 | 1290183.7969 | 2409.5395
| CDN004-139244670 | 185 | CDN004 | CDN | South | 3363446.3593 | 0.00096252 | 0.00096696 | 0.00097522 | 0.00097522 | 0.00096252 | 0.00095616 | 0.00097332 | 0.00098158 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.099924 | 0.10096 | 0.102 | 0.10304 | 0.10408 | 0.10346 | 0.10284 | 0.10222 | 0.1016 | 0.10098 | 0.10036 | 0.099744 | 0.099124 | 0.098505 | 0.097885 | 0.097266 | 0.096646 | 0.096027 | 0.095407 | 0.094788 | 0.0026776 | 0.002718 | 0.0027694 | 0.0027976 | 0.002789 | 0.0027541 | 0.0027867 | 0.0027934 | 0.0027406 | 0.0027238 | 0.0027071 | 0.0026904 | 0.0026737 | 0.002657 | 0.0026403 | 0.0026236 | 0.0026069 | 0.0025902 | 0.0025734 | 0.0025567 | 32556.0223 | 6405.4024 | 1273.4156 | 250.5447 | 79952.7646 | 103636.4654 | 3510058.8593 | 83437.9026
| CDN004-139351301 | 30 | CDN004 | CDN | South | 545423.7339 | 0.00096252 | 0.00096696 | 0.00097522 | 0.00097522 | 0.00096252 | 0.00095616 | 0.00097332 | 0.00098158 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.0031208 | 0.0031556 | 0.0031904 | 0.0032252 | 0.0032601 | 0.0032444 | 0.0032287 | 0.003213 | 0.0031973 | 0.0031816 | 0.0031659 | 0.0031502 | 0.0031345 | 0.0031188 | 0.0031031 | 0.0030874 | 0.0030717 | 0.003056 | 0.0030403 | 0.0030246 | 8.3625e-05 | 8.4949e-05 | 8.662e-05 | 8.7566e-05 | 8.7358e-05 | 8.6364e-05 | 8.7488e-05 | 8.7801e-05 | 8.6241e-05 | 8.5817e-05 | 8.5394e-05 | 8.4971e-05 | 8.4547e-05 | 8.4124e-05 | 8.37e-05 | 8.3277e-05 | 8.2853e-05 | 8.243e-05 | 8.2006e-05 | 8.1583e-05 | 32556.0223 | 6405.4024 | 40.104 | 7.8905 | 2767.4932 | 3587.2833 | 569198.7339 | 2888.1281
| CDN004-142953493 | 29 | CDN004 | CDN | South | 527242.9428 | 0.00096252 | 0.00096696 | 0.00097522 | 0.00097522 | 0.00096252 | 0.00095616 | 0.00097332 | 0.00098158 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.0094316 | 0.009516 | 0.0096004 | 0.0096848 | 0.0097692 | 0.0096967 | 0.0096242 | 0.0095517 | 0.0094792 | 0.0094066 | 0.0093341 | 0.0092616 | 0.0091891 | 0.0091166 | 0.009044 | 0.0089715 | 0.008899 | 0.0088265 | 0.008754 | 0.0086815 | 0.00025273 | 0.00025617 | 0.00026065 | 0.00026295 | 0.00026178 | 0.00025812 | 0.00026079 | 0.00026102 | 0.00025568 | 0.00025373 | 0.00025177 | 0.00024982 | 0.00024786 | 0.0002459 | 0.00024395 | 0.00024199 | 0.00024004 | 0.00023808 | 0.00023612 | 0.00023417 | 32556.0223 | 6405.4024 | 118.7185 | 23.3579 | 4454.7097 | 5774.289 | 550225.4428 | 4648.8903
| CDN004-15399970 | 220 | CDN004 | CDN | South | 3999774.0489 | 0.00096252 | 0.00096696 | 0.00097522 | 0.00097522 | 0.00096252 | 0.00095616 | 0.00097332 | 0.00098158 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 2.0391 | 2.0555 | 2.0718 | 2.0882 | 2.1045 | 2.0828 | 2.061 | 2.0393 | 2.0175 | 1.9957 | 1.974 | 1.9522 | 1.9305 | 1.9087 | 1.887 | 1.8652 | 1.8435 | 1.8217 | 1.8 | 1.7782 | 0.054641 | 0.055333 | 0.05625 | 0.056694 | 0.056393 | 0.055442 | 0.055847 | 0.055727 | 0.054419 | 0.053832 | 0.053245 | 0.052658 | 0.052072 | 0.051485 | 0.050898 | 0.050311 | 0.049725 | 0.049138 | 0.048551 | 0.047964 | 32556.0223 | 6405.4024 | 25198.7401 | 4957.856 | 157876.5794 | 204642.9631 | 4174124.0489 | 164758.4135
| CDN004-159428859 | 50 | CDN004 | CDN | South | 909039.5566 | 0.00096252 | 0.00096696 | 0.00097522 | 0.00097522 | 0.00096252 | 0.00095616 | 0.00097332 | 0.00098158 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.0017646 | 0.0017801 | 0.0017956 | 0.001811 | 0.0018265 | 0.0018194 | 0.0018123 | 0.0018053 | 0.0017982 | 0.0017911 | 0.001784 | 0.0017769 | 0.0017699 | 0.0017628 | 0.0017557 | 0.0017486 | 0.0017415 | 0.0017345 | 0.0017274 | 0.0017203 | 4.7286e-05 | 4.7921e-05 | 4.875e-05 | 4.917e-05 | 4.8943e-05 | 4.8432e-05 | 4.9109e-05 | 4.9332e-05 | 4.8503e-05 | 4.8312e-05 | 4.8121e-05 | 4.793e-05 | 4.7739e-05 | 4.7548e-05 | 4.7357e-05 | 4.7166e-05 | 4.6975e-05 | 4.6784e-05 | 4.6593e-05 | 4.6402e-05 | 32556.0223 | 6405.4024 | 22.612 | 4.4489 | 4681.2182 | 6067.8941 | 948664.5566 | 4885.2723
| CDN004-159428956 | 65 | CDN004 | CDN | South | 1181751.4235 | 0.00096252 | 0.00096696 | 0.00097522 | 0.00097522 | 0.00096252 | 0.00095616 | 0.00097332 | 0.00098158 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.0067627 | 0.0068217 | 0.0068806 | 0.0069396 | 0.0069986 | 0.0069652 | 0.0069319 | 0.0068985 | 0.0068651 | 0.0068318 | 0.0067984 | 0.0067651 | 0.0067317 | 0.0066984 | 0.006665 | 0.0066317 | 0.0065983 | 0.0065649 | 0.0065316 | 0.0064982 | 0.00018122 | 0.00018364 | 0.00018681 | 0.00018841 | 0.00018754 | 0.00018541 | 0.00018783 | 0.00018852 | 0.00018518 | 0.00018428 | 0.00018338 | 0.00018248 | 0.00018158 | 0.00018068 | 0.00017978 | 0.00017888 | 0.00017798 | 0.00017708 | 0.00017618 | 0.00017528 | 32556.0223 | 6405.4024 | 86.2473 | 16.9692 | 4463.8227 | 5786.1014 | 1233263.9235 | 4658.4005
| CDN004-159429052 | 27 | CDN004 | CDN | South | 490881.3605 | 0.00096252 | 0.00096696 | 0.00097522 | 0.00097522 | 0.00096252 | 0.00095616 | 0.00097332 | 0.00098158 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00055189 | 0.00055211 | 0.00055234 | 0.00055257 | 0.0005528 | 0.00055256 | 0.00055232 | 0.00055208 | 0.00055184 | 0.0005516 | 0.00055136 | 0.00055112 | 0.00055088 | 0.00055064 | 0.0005504 | 0.00055016 | 0.00054992 | 0.00054968 | 0.00054944 | 0.0005492 | 1.4789e-05 | 1.4863e-05 | 1.4996e-05 | 1.5002e-05 | 1.4813e-05 | 1.4709e-05 | 1.4966e-05 | 1.5087e-05 | 1.4885e-05 | 1.4878e-05 | 1.4872e-05 | 1.4866e-05 | 1.4859e-05 | 1.4853e-05 | 1.4846e-05 | 1.484e-05 | 1.4833e-05 | 1.4827e-05 | 1.482e-05 | 1.4814e-05 | 32556.0223 | 6405.4024 | 7.0021 | 1.3777 | 489.2446 | 634.1691 | 512278.8605 | 510.5707
| CDN004-162436765 | 93 | CDN004 | CDN | South | 1690813.5752 | 0.00096252 | 0.00096696 | 0.00097522 | 0.00097522 | 0.00096252 | 0.00095616 | 0.00097332 | 0.00098158 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.0039939 | 0.0040351 | 0.0040763 | 0.0041175 | 0.0041587 | 0.0041355 | 0.0041122 | 0.0040889 | 0.0040657 | 0.0040424 | 0.0040191 | 0.0039958 | 0.0039726 | 0.0039493 | 0.003926 | 0.0039028 | 0.0038795 | 0.0038562 | 0.003833 | 0.0038097 | 0.00010702 | 0.00010863 | 0.00011067 | 0.00011179 | 0.00011144 | 0.00011008 | 0.00011143 | 0.00011174 | 0.00010966 | 0.00010904 | 0.00010841 | 0.00010778 | 0.00010715 | 0.00010653 | 0.0001059 | 0.00010527 | 0.00010464 | 0.00010402 | 0.00010339 | 0.00010276 | 32556.0223 | 6405.4024 | 50.9789 | 10.0301 | 2804.3144 | 3635.0116 | 1764516.0752 | 2926.5543
| CDN004-202037935 | 218 | CDN004 | CDN | South | 3963412.4667 | 0.00096252 | 0.00096696 | 0.00097522 | 0.00097522 | 0.00096252 | 0.00095616 | 0.00097332 | 0.00098158 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.51743 | 0.52082 | 0.52421 | 0.52761 | 0.531 | 0.53173 | 0.53247 | 0.5332 | 0.53393 | 0.53467 | 0.5354 | 0.53613 | 0.53687 | 0.5376 | 0.53833 | 0.53907 | 0.5398 | 0.54053 | 0.54127 | 0.542 | 0.013865 | 0.014021 | 0.014233 | 0.014325 | 0.014229 | 0.014155 | 0.014428 | 0.014571 | 0.014402 | 0.014422 | 0.014441 | 0.014461 | 0.014481 | 0.014501 | 0.014521 | 0.01454 | 0.01456 | 0.01458 | 0.0146 | 0.01462 | 32556.0223 | 6405.4024 | 6761.0393 | 1330.2355 | 83084.4172 | 107695.7798 | 4136177.4667 | 86706.0638
| CDN004-202768387 | 608 | CDN004 | CDN | South | 11053921.0079 | 0.00096252 | 0.00096696 | 0.00097522 | 0.00097522 | 0.00096252 | 0.00095616 | 0.00097332 | 0.00098158 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 0.00096887 | 1.6599 | 1.6752 | 1.6905 | 1.7059 | 1.7212 | 1.7154 | 1.7096 | 1.7039 | 1.6981 | 1.6923 | 1.6866 | 1.6808 | 1.675 | 1.6693 | 1.6635 | 1.6577 | 1.652 | 1.6462 | 1.6404 | 1.6347 | 0.044479 | 0.045097 | 0.045898 | 0.046314 | 0.046122 | 0.045664 | 0.046326 | 0.046562 | 0.045804 | 0.045648 | 0.045493 | 0.045337 | 0.045181 | 0.045026 | 0.04487 | 0.044715 | 0.044559 | 0.044404 | 0.044248 | 0.044093 | 32556.0223 | 6405.4024 | 21359.5979 | 4202.5042 | 551330.0427 | 714645.6682 | 11535761.0079 | 575362.4985
| CDN006-143338433 | 65 | CDN006 | CDN | South | 1181751.4235 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.018719 | 0.018885 | 0.019051 | 0.019217 | 0.019382 | 0.019318 | 0.019254 | 0.01919 | 0.019126 | 0.019062 | 0.018998 | 0.018934 | 0.01887 | 0.018805 | 0.018741 | 0.018677 | 0.018613 | 0.018549 | 0.018485 | 0.018421 | 0.0006769 | 0.00068103 | 0.0006897 | 0.00068757 | 0.0006853 | 0.00068031 | 0.0006862 | 0.00068662 | 0.00066815 | 0.00066591 | 0.00066367 | 0.00066143 | 0.00065919 | 0.00065695 | 0.00065471 | 0.00065247 | 0.00065023 | 0.00064799 | 0.00064575 | 0.00064351 | 32556.0223 | 6405.4024 | 315.3677 | 62.0487 | 11166.2828 | 14473.9721 | 1233263.9235 | 11653.0207
| CDN006-143338709 | 118 | CDN006 | CDN | South | 2145333.3535 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0039237 | 0.0039617 | 0.0039996 | 0.0040376 | 0.0040756 | 0.0040634 | 0.0040512 | 0.004039 | 0.0040268 | 0.0040146 | 0.0040025 | 0.0039903 | 0.0039781 | 0.0039659 | 0.0039537 | 0.0039415 | 0.0039293 | 0.0039171 | 0.0039049 | 0.0038928 | 0.00014188 | 0.00014287 | 0.0001448 | 0.00014447 | 0.0001441 | 0.0001431 | 0.00014438 | 0.00014452 | 0.00014067 | 0.00014025 | 0.00013982 | 0.0001394 | 0.00013897 | 0.00013854 | 0.00013812 | 0.00013769 | 0.00013727 | 0.00013684 | 0.00013642 | 0.00013599 | 32556.0223 | 6405.4024 | 66.3852 | 13.0613 | 2690.1957 | 3487.0886 | 2238848.3535 | 2807.4613
| CDN006-143338924 | 47 | CDN006 | CDN | South | 854497.1832 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.00027981 | 0.00028275 | 0.0002857 | 0.00028865 | 0.0002916 | 0.00029016 | 0.00028872 | 0.00028728 | 0.00028584 | 0.0002844 | 0.00028296 | 0.00028152 | 0.00028008 | 0.00027864 | 0.0002772 | 0.00027576 | 0.00027432 | 0.00027288 | 0.00027144 | 0.00027 | 1.0118e-05 | 1.0197e-05 | 1.0343e-05 | 1.0328e-05 | 1.031e-05 | 1.0218e-05 | 1.029e-05 | 1.0279e-05 | 9.9855e-06 | 9.9352e-06 | 9.8849e-06 | 9.8346e-06 | 9.7843e-06 | 9.734e-06 | 9.6837e-06 | 9.6334e-06 | 9.5831e-06 | 9.5328e-06 | 9.4825e-06 | 9.4322e-06 | 32556.0223 | 6405.4024 | 4.7002 | 0.92476 | 290.789 | 376.9268 | 891744.6832 | 303.4645
| CDN006-143339149 | 16 | CDN006 | CDN | South | 290892.6581 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0045544 | 0.0045868 | 0.0046191 | 0.0046514 | 0.0046838 | 0.004654 | 0.0046242 | 0.0045945 | 0.0045647 | 0.004535 | 0.0045052 | 0.0044754 | 0.0044457 | 0.0044159 | 0.0043862 | 0.0043564 | 0.0043266 | 0.0042969 | 0.0042671 | 0.0042374 | 0.00016469 | 0.00016541 | 0.00016723 | 0.00016643 | 0.0001656 | 0.0001639 | 0.0001648 | 0.00016439 | 0.00015946 | 0.00015842 | 0.00015738 | 0.00015634 | 0.00015531 | 0.00015427 | 0.00015323 | 0.00015219 | 0.00015115 | 0.00015011 | 0.00014907 | 0.00014803 | 32556.0223 | 6405.4024 | 75.1151 | 14.7789 | 2711.7055 | 3514.9701 | 303572.6581 | 2829.9087
| CDN006-15399920 | 304 | CDN006 | CDN | South | 5526960.504 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 1.7556 | 1.7714 | 1.7872 | 1.8029 | 1.8187 | 1.7974 | 1.7761 | 1.7548 | 1.7335 | 1.7122 | 1.6909 | 1.6696 | 1.6482 | 1.6269 | 1.6056 | 1.5843 | 1.563 | 1.5417 | 1.5204 | 1.4991 | 0.063483 | 0.063879 | 0.064701 | 0.06451 | 0.064305 | 0.063298 | 0.063299 | 0.062787 | 0.060558 | 0.059813 | 0.059069 | 0.058324 | 0.05758 | 0.056835 | 0.056091 | 0.055346 | 0.054602 | 0.053857 | 0.053113 | 0.052368 | 32556.0223 | 6405.4024 | 28324.8534 | 5572.9193 | 188116.3865 | 243840.441 | 5767880.504 | 196316.3727
| CDN006-158379713 | 120 | CDN006 | CDN | South | 2181694.9358 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.015389 | 0.015538 | 0.015686 | 0.015835 | 0.015983 | 0.015933 | 0.015882 | 0.015831 | 0.01578 | 0.015729 | 0.015678 | 0.015627 | 0.015576 | 0.015526 | 0.015475 | 0.015424 | 0.015373 | 0.015322 | 0.015271 | 0.01522 | 0.00055649 | 0.00056033 | 0.0005679 | 0.00056657 | 0.00056513 | 0.00056108 | 0.00056601 | 0.00056643 | 0.00055125 | 0.00054948 | 0.0005477 | 0.00054592 | 0.00054415 | 0.00054237 | 0.00054059 | 0.00053881 | 0.00053704 | 0.00053526 | 0.00053348 | 0.0005317 | 32556.0223 | 6405.4024 | 260.0958 | 51.1739 | 14087.3723 | 18260.3501 | 2276794.9358 | 14701.4404
| CDN006-158379840 | 43 | CDN006 | CDN | South | 781774.0187 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0042044 | 0.0042493 | 0.0042943 | 0.0043392 | 0.0043842 | 0.0043689 | 0.0043535 | 0.0043382 | 0.0043228 | 0.0043075 | 0.0042921 | 0.0042768 | 0.0042614 | 0.0042461 | 0.0042308 | 0.0042154 | 0.0042001 | 0.0041847 | 0.0041694 | 0.004154 | 0.00015204 | 0.00015324 | 0.00015547 | 0.00015526 | 0.00015501 | 0.00015385 | 0.00015516 | 0.00015522 | 0.00015101 | 0.00015048 | 0.00014994 | 0.00014941 | 0.00014887 | 0.00014833 | 0.0001478 | 0.00014726 | 0.00014672 | 0.00014619 | 0.00014565 | 0.00014512 | 32556.0223 | 6405.4024 | 71.1816 | 14.005 | 3453.7433 | 4476.8152 | 815851.5187 | 3604.2919
| CDN006-160451043 | 78 | CDN006 | CDN | South | 1418101.7083 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.013821 | 0.013967 | 0.014114 | 0.01426 | 0.014406 | 0.014361 | 0.014315 | 0.014269 | 0.014223 | 0.014177 | 0.014132 | 0.014086 | 0.01404 | 0.013994 | 0.013948 | 0.013902 | 0.013857 | 0.013811 | 0.013765 | 0.013719 | 0.00049979 | 0.0005037 | 0.00051097 | 0.00051023 | 0.00050937 | 0.00050572 | 0.00051017 | 0.00051055 | 0.00049687 | 0.00049527 | 0.00049367 | 0.00049207 | 0.00049047 | 0.00048887 | 0.00048727 | 0.00048567 | 0.00048407 | 0.00048247 | 0.00048087 | 0.00047927 | 32556.0223 | 6405.4024 | 234.2988 | 46.0983 | 10692.7627 | 13860.1853 | 1479916.7083 | 11158.8598
| CDN006-162450281 | 21 | CDN006 | CDN | South | 381796.6138 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 1.9716e-05 | 1.9992e-05 | 2.0268e-05 | 2.0544e-05 | 2.082e-05 | 2.0757e-05 | 2.0694e-05 | 2.0631e-05 | 2.0568e-05 | 2.0505e-05 | 2.0442e-05 | 2.0379e-05 | 2.0316e-05 | 2.0253e-05 | 2.019e-05 | 2.0127e-05 | 2.0064e-05 | 2.0001e-05 | 1.9938e-05 | 1.9875e-05 | 7.1295e-07 | 7.2096e-07 | 7.3377e-07 | 7.3507e-07 | 7.3613e-07 | 7.3098e-07 | 7.3752e-07 | 7.3818e-07 | 7.1852e-07 | 7.1632e-07 | 7.1412e-07 | 7.1192e-07 | 7.0972e-07 | 7.0752e-07 | 7.0532e-07 | 7.0312e-07 | 7.0092e-07 | 6.9871e-07 | 6.9651e-07 | 6.9431e-07 | 32556.0223 | 6405.4024 | 0.33815 | 0.066531 | 18.6977 | 24.2364 | 398439.1138 | 19.5128
| CDN006-162451240 | 22 | CDN006 | CDN | South | 399977.4049 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.00062951 | 0.00063537 | 0.00064122 | 0.00064708 | 0.00065294 | 0.00064859 | 0.00064425 | 0.0006399 | 0.00063556 | 0.00063121 | 0.00062687 | 0.00062252 | 0.00061818 | 0.00061383 | 0.00060949 | 0.00060514 | 0.0006008 | 0.00059645 | 0.00059211 | 0.00058776 | 2.2764e-05 | 2.2913e-05 | 2.3214e-05 | 2.3153e-05 | 2.3086e-05 | 2.2841e-05 | 2.296e-05 | 2.2896e-05 | 2.2203e-05 | 2.2051e-05 | 2.1899e-05 | 2.1747e-05 | 2.1595e-05 | 2.1444e-05 | 2.1292e-05 | 2.114e-05 | 2.0988e-05 | 2.0836e-05 | 2.0685e-05 | 2.0533e-05 | 32556.0223 | 6405.4024 | 10.4401 | 2.0541 | 1209.2142 | 1567.4091 | 417412.4049 | 1261.9239
| CDN006-162572514 | 25 | CDN006 | CDN | South | 454519.7783 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 6.88e-05 | 2.4879e-06 | 2.4811e-06 | 2.4908e-06 | 2.4617e-06 | 2.4326e-06 | 2.4229e-06 | 2.452e-06 | 2.4617e-06 | 2.4035e-06 | 2.4035e-06 | 2.4035e-06 | 2.4035e-06 | 2.4035e-06 | 2.4035e-06 | 2.4035e-06 | 2.4035e-06 | 2.4035e-06 | 2.4035e-06 | 2.4035e-06 | 2.4035e-06 | 32556.0223 | 6405.4024 | 1.1448 | 0.22524 | 226.0731 | 293.0408 | 474332.2783 | 235.9276
| CDN006-162572817 | 7 | CDN006 | CDN | South | 127265.5379 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 5.8661e-05 | 5.9395e-05 | 6.013e-05 | 6.0865e-05 | 6.16e-05 | 6.078e-05 | 5.996e-05 | 5.914e-05 | 5.832e-05 | 5.75e-05 | 5.668e-05 | 5.586e-05 | 5.504e-05 | 5.422e-05 | 5.34e-05 | 5.258e-05 | 5.176e-05 | 5.094e-05 | 5.012e-05 | 4.93e-05 | 2.1212e-06 | 2.1419e-06 | 2.1769e-06 | 2.1778e-06 | 2.178e-06 | 2.1404e-06 | 2.1369e-06 | 2.116e-06 | 2.0373e-06 | 2.0087e-06 | 1.9801e-06 | 1.9514e-06 | 1.9228e-06 | 1.8941e-06 | 1.8655e-06 | 1.8368e-06 | 1.8082e-06 | 1.7795e-06 | 1.7509e-06 | 1.7222e-06 | 32556.0223 | 6405.4024 | 0.949 | 0.18672 | 26.2213 | 33.9886 | 132813.0379 | 27.3643
| CDN006-162588679 | 20 | CDN006 | CDN | South | 363615.8226 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0035757 | 0.0036155 | 0.0036554 | 0.0036952 | 0.003735 | 0.0036795 | 0.003624 | 0.0035685 | 0.003513 | 0.0034575 | 0.003402 | 0.0033465 | 0.003291 | 0.0032355 | 0.00318 | 0.0031245 | 0.003069 | 0.0030135 | 0.002958 | 0.0029025 | 0.0001293 | 0.00013038 | 0.00013234 | 0.00013221 | 0.00013206 | 0.00012958 | 0.00012916 | 0.00012768 | 0.00012272 | 0.00012078 | 0.00011885 | 0.00011691 | 0.00011497 | 0.00011303 | 0.00011109 | 0.00010915 | 0.00010721 | 0.00010527 | 0.00010333 | 0.0001014 | 32556.0223 | 6405.4024 | 57.1156 | 11.2375 | 2576.2534 | 3339.3942 | 379465.8226 | 2688.5522
| CDN006-162675220 | 27 | CDN006 | CDN | South | 490881.3605 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 1.5637e-05 | 1.5803e-05 | 1.5969e-05 | 1.6134e-05 | 1.63e-05 | 1.6145e-05 | 1.599e-05 | 1.5835e-05 | 1.568e-05 | 1.5525e-05 | 1.537e-05 | 1.5215e-05 | 1.506e-05 | 1.4905e-05 | 1.475e-05 | 1.4595e-05 | 1.444e-05 | 1.4285e-05 | 1.413e-05 | 1.3975e-05 | 5.6545e-07 | 5.6989e-07 | 5.7811e-07 | 5.7729e-07 | 5.7632e-07 | 5.6856e-07 | 5.6987e-07 | 5.6658e-07 | 5.4776e-07 | 5.4235e-07 | 5.3694e-07 | 5.3152e-07 | 5.2611e-07 | 5.2069e-07 | 5.1528e-07 | 5.0986e-07 | 5.0445e-07 | 4.9903e-07 | 4.9362e-07 | 4.882e-07 | 32556.0223 | 6405.4024 | 0.25656 | 0.050478 | 10.9393 | 14.1798 | 512278.8605 | 11.4162
| CDN006-162675596 | 11 | CDN006 | CDN | South | 199988.7024 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 4.48e-06 | 4.54e-06 | 4.6e-06 | 4.66e-06 | 4.72e-06 | 4.701e-06 | 4.682e-06 | 4.663e-06 | 4.644e-06 | 4.625e-06 | 4.606e-06 | 4.587e-06 | 4.568e-06 | 4.549e-06 | 4.53e-06 | 4.511e-06 | 4.492e-06 | 4.473e-06 | 4.454e-06 | 4.435e-06 | 1.62e-07 | 1.6372e-07 | 1.6654e-07 | 1.6674e-07 | 1.6689e-07 | 1.6555e-07 | 1.6686e-07 | 1.6684e-07 | 1.6223e-07 | 1.6157e-07 | 1.6091e-07 | 1.6024e-07 | 1.5958e-07 | 1.5891e-07 | 1.5825e-07 | 1.5759e-07 | 1.5692e-07 | 1.5626e-07 | 1.556e-07 | 1.5493e-07 | 32556.0223 | 6405.4024 | 0.076299 | 0.015012 | 6.6293 | 8.593 | 208706.2024 | 6.9182
| CDN006-183157401 | 11 | CDN006 | CDN | South | 199988.7024 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.00016962 | 0.00017182 | 0.00017401 | 0.00017621 | 0.0001784 | 0.00017544 | 0.00017248 | 0.00016952 | 0.00016656 | 0.0001636 | 0.00016064 | 0.00015768 | 0.00015472 | 0.00015176 | 0.0001488 | 0.00014584 | 0.00014288 | 0.00013992 | 0.00013696 | 0.000134 | 6.1337e-06 | 6.1961e-06 | 6.2998e-06 | 6.3047e-06 | 6.3077e-06 | 6.1783e-06 | 6.147e-06 | 6.0655e-06 | 5.8186e-06 | 5.7152e-06 | 5.6118e-06 | 5.5084e-06 | 5.405e-06 | 5.3016e-06 | 5.1982e-06 | 5.0948e-06 | 4.9914e-06 | 4.888e-06 | 4.7846e-06 | 4.6812e-06 | 32556.0223 | 6405.4024 | 2.6993 | 0.53108 | 58.5888 | 75.944 | 208706.2024 | 61.1426
| CDN006-202038054 | 709 | CDN006 | CDN | South | 12890180.9122 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 1.1756 | 1.1842 | 1.1928 | 1.2014 | 1.2101 | 1.2067 | 1.2033 | 1.2 | 1.1966 | 1.1932 | 1.1898 | 1.1865 | 1.1831 | 1.1797 | 1.1764 | 1.173 | 1.1696 | 1.1662 | 1.1629 | 1.1595 | 0.042509 | 0.042704 | 0.043184 | 0.042988 | 0.042785 | 0.042495 | 0.042886 | 0.042935 | 0.041802 | 0.041684 | 0.041566 | 0.041448 | 0.041331 | 0.041213 | 0.041095 | 0.040977 | 0.040859 | 0.040742 | 0.040624 | 0.040506 | 32556.0223 | 6405.4024 | 19760.3508 | 3887.8521 | 425563.5722 | 551624.5078 | 13452063.4122 | 444113.8723
| CDN006-202248649 | 316 | CDN006 | CDN | South | 5745129.9975 | 0.0012989 | 0.0012953 | 0.0013004 | 0.0012852 | 0.00127 | 0.0012649 | 0.0012801 | 0.0012852 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 0.0012548 | 1.3847 | 1.3968 | 1.4089 | 1.4209 | 1.433 | 1.4256 | 1.4182 | 1.4108 | 1.4034 | 1.396 | 1.3887 | 1.3813 | 1.3739 | 1.3665 | 1.3591 | 1.3517 | 1.3443 | 1.3369 | 1.3295 | 1.3221 | 0.050074 | 0.050372 | 0.051006 | 0.050842 | 0.050667 | 0.050205 | 0.050544 | 0.05048 | 0.049028 | 0.048769 | 0.048511 | 0.048253 | 0.047995 | 0.047736 | 0.047478 | 0.04722 | 0.046962 | 0.046703 | 0.046445 | 0.046187 | 32556.0223 | 6405.4024 | 23099.0021 | 4544.7322 | 204212.2948 | 264704.2979 | 5995559.9975 | 213113.901
| CHA003-15429144 | 142 | CHA003 | CHA | North | 3346418.3192 | 0.0015012 | 0.0015012 | 0.0014917 | 0.0014793 | 0.0014545 | 0.0014367 | 0.0014284 | 0.0014243 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 3.6025 | 3.6298 | 3.657 | 3.6843 | 3.7116 | 3.7498 | 3.788 | 3.8262 | 3.8644 | 3.9027 | 3.9409 | 3.9791 | 4.0173 | 4.0555 | 4.0938 | 4.132 | 4.1702 | 4.2084 | 4.2466 | 4.2849 | 0.15057 | 0.1517 | 0.15188 | 0.15173 | 0.15029 | 0.14998 | 0.15064 | 0.15171 | 0.151 | 0.1525 | 0.15399 | 0.15548 | 0.15698 | 0.15847 | 0.15996 | 0.16146 | 0.16295 | 0.16444 | 0.16594 | 0.16743 | 26719.9676 | 3421.3779 | 59868.7252 | 7665.9349 | 163887.7686 | 163887.7686 | 3346418.3192 | 163887.7686
| CHA003-155052833 | 9 | CHA003 | CHA | North | 212096.9357 | 0.0015012 | 0.0015012 | 0.0014917 | 0.0014793 | 0.0014545 | 0.0014367 | 0.0014284 | 0.0014243 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.00028677 | 0.00028907 | 0.00029138 | 0.00029369 | 0.000296 | 0.00029956 | 0.00030312 | 0.00030668 | 0.00031024 | 0.0003138 | 0.00031736 | 0.00032092 | 0.00032448 | 0.00032804 | 0.0003316 | 0.00033516 | 0.00033872 | 0.00034228 | 0.00034584 | 0.0003494 | 1.1985e-05 | 1.2082e-05 | 1.2101e-05 | 1.2095e-05 | 1.1986e-05 | 1.1981e-05 | 1.2054e-05 | 1.216e-05 | 1.2123e-05 | 1.2262e-05 | 1.2401e-05 | 1.254e-05 | 1.2679e-05 | 1.2818e-05 | 1.2957e-05 | 1.3096e-05 | 1.3236e-05 | 1.3375e-05 | 1.3514e-05 | 1.3653e-05 | 26719.9676 | 3421.3779 | 4.812 | 0.61616 | 119.7404 | 119.7404 | 212096.9357 | 119.7404
| CHA003-155052965 | 5 | CHA003 | CHA | North | 117831.631 | 0.0015012 | 0.0015012 | 0.0014917 | 0.0014793 | 0.0014545 | 0.0014367 | 0.0014284 | 0.0014243 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.00087787 | 0.00088455 | 0.00089124 | 0.00089793 | 0.00090461 | 0.00091569 | 0.00092676 | 0.00093784 | 0.00094891 | 0.00095999 | 0.00097106 | 0.00098214 | 0.00099321 | 0.0010043 | 0.0010154 | 0.0010264 | 0.0010375 | 0.0010486 | 0.0010597 | 0.0010707 | 3.669e-05 | 3.697e-05 | 3.7013e-05 | 3.698e-05 | 3.663e-05 | 3.6625e-05 | 3.6854e-05 | 3.7186e-05 | 3.7079e-05 | 3.7512e-05 | 3.7944e-05 | 3.8377e-05 | 3.881e-05 | 3.9243e-05 | 3.9675e-05 | 4.0108e-05 | 4.0541e-05 | 4.0974e-05 | 4.1406e-05 | 4.1839e-05 | 26719.9676 | 3421.3779 | 14.7248 | 1.8855 | 1628.4877 | 1628.4877 | 117831.631 | 1628.4877
| CHA003-24606706 | 115 | CHA003 | CHA | North | 2710127.5121 | 0.0015012 | 0.0015012 | 0.0014917 | 0.0014793 | 0.0014545 | 0.0014367 | 0.0014284 | 0.0014243 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 0.0014036 | 2.541 | 2.5565 | 2.572 | 2.5875 | 2.6029 | 2.6236 | 2.6443 | 2.6649 | 2.6856 | 2.7063 | 2.7269 | 2.7476 | 2.7682 | 2.7889 | 2.8096 | 2.8302 | 2.8509 | 2.8715 | 2.8922 | 2.9129 | 0.1062 | 0.10685 | 0.10681 | 0.10656 | 0.1054 | 0.10494 | 0.10515 | 0.10567 | 0.10494 | 0.10575 | 0.10655 | 0.10736 | 0.10817 | 0.10898 | 0.10978 | 0.11059 | 0.1114 | 0.11221 | 0.11301 | 0.11382 | 26719.9676 | 3421.3779 | 41558.7501 | 5321.4207 | 471806.096 | 471806.096 | 2710127.5121 | 471806.096
| CHA005-15429107 | 164 | CHA005 | CHA | North | 3864877.4955 | 0.0018658 | 0.0018855 | 0.0018971 | 0.0019008 | 0.0018784 | 0.0018673 | 0.0018896 | 0.0019206 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 6.0766 | 6.121 | 6.1654 | 6.2098 | 6.2542 | 6.3147 | 6.3753 | 6.4359 | 6.4964 | 6.557 | 6.6175 | 6.6781 | 6.7387 | 6.7992 | 6.8598 | 6.9203 | 6.9809 | 7.0415 | 7.102 | 7.1626 | 0.31563 | 0.32131 | 0.32562 | 0.32861 | 0.32707 | 0.32827 | 0.33539 | 0.34412 | 0.34446 | 0.34767 | 0.35088 | 0.35409 | 0.3573 | 0.36051 | 0.36372 | 0.36694 | 0.37015 | 0.37336 | 0.37657 | 0.37978 | 26719.9676 | 3421.3779 | 133201.8796 | 17055.9325 | 495056.8808 | 495056.8808 | 3864877.4955 | 495056.8808
| CHA005-155053189 | 7 | CHA005 | CHA | North | 164964.2833 | 0.0018658 | 0.0018855 | 0.0018971 | 0.0019008 | 0.0018784 | 0.0018673 | 0.0018896 | 0.0019206 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.00035367 | 0.00035661 | 0.00035954 | 0.00036247 | 0.0003654 | 0.00036999 | 0.00037458 | 0.00037917 | 0.00038376 | 0.00038835 | 0.00039294 | 0.00039753 | 0.00040212 | 0.00040671 | 0.0004113 | 0.00041589 | 0.00042048 | 0.00042507 | 0.00042966 | 0.00043425 | 1.8371e-05 | 1.8719e-05 | 1.8989e-05 | 1.9181e-05 | 1.9109e-05 | 1.9234e-05 | 1.9706e-05 | 2.0274e-05 | 2.0348e-05 | 2.0591e-05 | 2.0835e-05 | 2.1078e-05 | 2.1321e-05 | 2.1565e-05 | 2.1808e-05 | 2.2052e-05 | 2.2295e-05 | 2.2538e-05 | 2.2782e-05 | 2.3025e-05 | 26719.9676 | 3421.3779 | 7.886 | 1.0098 | 102.4386 | 102.4386 | 164964.2833 | 102.4386
| CHA005-24606076 | 200 | CHA005 | CHA | North | 4713265.2384 | 0.0018658 | 0.0018855 | 0.0018971 | 0.0019008 | 0.0018784 | 0.0018673 | 0.0018896 | 0.0019206 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 28.8313 | 29.0034 | 29.1755 | 29.3476 | 29.5197 | 29.701 | 29.8824 | 30.0637 | 30.245 | 30.4263 | 30.6077 | 30.789 | 30.9703 | 31.1516 | 31.333 | 31.5143 | 31.6956 | 31.8769 | 32.0583 | 32.2396 | 1.4976 | 1.5225 | 1.5409 | 1.553 | 1.5438 | 1.544 | 1.572 | 1.6075 | 1.6037 | 1.6133 | 1.6229 | 1.6325 | 1.6421 | 1.6517 | 1.6614 | 1.671 | 1.6806 | 1.6902 | 1.6998 | 1.7094 | 26719.9676 | 3421.3779 | 618459.1925 | 79191.0617 | 2472604.8079 | 2472604.8079 | 4713265.2384 | 2472604.8079
| CHA005-24606160 | 56 | CHA005 | CHA | North | 1319714.2667 | 0.0018658 | 0.0018855 | 0.0018971 | 0.0019008 | 0.0018784 | 0.0018673 | 0.0018896 | 0.0019206 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.84994 | 0.85577 | 0.8616 | 0.86743 | 0.87326 | 0.87992 | 0.88659 | 0.89326 | 0.89992 | 0.90659 | 0.91326 | 0.91992 | 0.92659 | 0.93326 | 0.93992 | 0.94659 | 0.95326 | 0.95993 | 0.96659 | 0.97326 | 0.044149 | 0.044922 | 0.045505 | 0.045903 | 0.045668 | 0.045742 | 0.046641 | 0.047762 | 0.047716 | 0.04807 | 0.048423 | 0.048777 | 0.04913 | 0.049484 | 0.049837 | 0.050191 | 0.050544 | 0.050898 | 0.051251 | 0.051605 | 26719.9676 | 3421.3779 | 18419.5725 | 2358.5477 | 170584.7026 | 170584.7026 | 1319714.2667 | 170584.7026
| CHA005-53118475 | 35 | CHA005 | CHA | North | 824821.4167 | 0.0018658 | 0.0018855 | 0.0018971 | 0.0019008 | 0.0018784 | 0.0018673 | 0.0018896 | 0.0019206 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.68623 | 0.69058 | 0.69494 | 0.69929 | 0.70365 | 0.70797 | 0.7123 | 0.71663 | 0.72096 | 0.72529 | 0.72961 | 0.73394 | 0.73827 | 0.7426 | 0.74693 | 0.75125 | 0.75558 | 0.75991 | 0.76424 | 0.76856 | 0.035645 | 0.036251 | 0.036703 | 0.037006 | 0.036798 | 0.036804 | 0.037472 | 0.038317 | 0.038227 | 0.038457 | 0.038686 | 0.038915 | 0.039145 | 0.039374 | 0.039604 | 0.039833 | 0.040063 | 0.040292 | 0.040522 | 0.040751 | 26719.9676 | 3421.3779 | 14739.1342 | 1887.2833 | 130558.0826 | 130558.0826 | 824821.4167 | 130558.0826
| CHA005-56709738 | 111 | CHA005 | CHA | North | 2615862.2073 | 0.0018658 | 0.0018855 | 0.0018971 | 0.0019008 | 0.0018784 | 0.0018673 | 0.0018896 | 0.0019206 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.16167 | 0.16299 | 0.16432 | 0.16564 | 0.16697 | 0.16861 | 0.17024 | 0.17188 | 0.17352 | 0.17515 | 0.17679 | 0.17843 | 0.18007 | 0.1817 | 0.18334 | 0.18498 | 0.18661 | 0.18825 | 0.18989 | 0.19152 | 0.0083976 | 0.0085561 | 0.0086785 | 0.0087657 | 0.0087319 | 0.008765 | 0.0089561 | 0.0091903 | 0.0092004 | 0.0092872 | 0.0093739 | 0.0094607 | 0.0095475 | 0.0096343 | 0.0097211 | 0.0098079 | 0.0098947 | 0.0099815 | 0.010068 | 0.010155 | 26719.9676 | 3421.3779 | 3556.344 | 455.3747 | 67971.6478 | 67971.6478 | 2615862.2073 | 67971.6478
| CHA005-56710238 | 202 | CHA005 | CHA | North | 4760397.8907 | 0.0018658 | 0.0018855 | 0.0018971 | 0.0019008 | 0.0018784 | 0.0018673 | 0.0018896 | 0.0019206 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 0.0019045 | 18.3502 | 18.4628 | 18.5755 | 18.6881 | 18.8007 | 18.8928 | 18.9849 | 19.077 | 19.1691 | 19.2612 | 19.3533 | 19.4454 | 19.5375 | 19.6296 | 19.7217 | 19.8138 | 19.9058 | 19.9979 | 20.09 | 20.1821 | 0.95317 | 0.96917 | 0.98106 | 0.98895 | 0.9832 | 0.98214 | 0.99875 | 1.02 | 1.0164 | 1.0213 | 1.0262 | 1.031 | 1.0359 | 1.0408 | 1.0457 | 1.0506 | 1.0555 | 1.0603 | 1.0652 | 1.0701 | 26719.9676 | 3421.3779 | 391442.6803 | 50122.5656 | 4288326.2617 | 4288326.2617 | 4760397.8907 | 4288326.2617
| CHA006-120251163 | 114 | CHA006 | CHA | North | 2686561.1859 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.11141 | 0.11212 | 0.11282 | 0.11353 | 0.11423 | 0.11502 | 0.1158 | 0.11659 | 0.11737 | 0.11816 | 0.11895 | 0.11973 | 0.12052 | 0.1213 | 0.12209 | 0.12287 | 0.12366 | 0.12444 | 0.12523 | 0.12601 | 0.0064017 | 0.0064978 | 0.0065675 | 0.0066 | 0.0065586 | 0.0065519 | 0.0066488 | 0.0067753 | 0.0067416 | 0.0067867 | 0.0068318 | 0.0068769 | 0.006922 | 0.0069671 | 0.0070122 | 0.0070574 | 0.0071025 | 0.0071476 | 0.0071927 | 0.0072378 | 26719.9676 | 3421.3779 | 2617.9813 | 335.2213 | 95262.2966 | 95262.2966 | 2686561.1859 | 95262.2966
| CHA006-130745345 | 29 | CHA006 | CHA | North | 683423.4596 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.00054069 | 0.00054421 | 0.00054774 | 0.00055127 | 0.0005548 | 0.00056031 | 0.00056582 | 0.00057133 | 0.00057684 | 0.00058235 | 0.00058786 | 0.00059337 | 0.00059888 | 0.00060439 | 0.0006099 | 0.00061541 | 0.00062092 | 0.00062643 | 0.00063194 | 0.00063745 | 3.1067e-05 | 3.154e-05 | 3.1884e-05 | 3.2048e-05 | 3.1853e-05 | 3.1917e-05 | 3.2486e-05 | 3.3201e-05 | 3.3132e-05 | 3.3448e-05 | 3.3765e-05 | 3.4081e-05 | 3.4398e-05 | 3.4714e-05 | 3.5031e-05 | 3.5347e-05 | 3.5664e-05 | 3.598e-05 | 3.6297e-05 | 3.6613e-05 | 26719.9676 | 3421.3779 | 12.9024 | 1.6521 | 301.7291 | 301.7291 | 683423.4596 | 301.7291
| CHA006-138134893 | 15 | CHA006 | CHA | North | 353494.8929 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.00021287 | 0.00021475 | 0.00021663 | 0.00021852 | 0.0002204 | 0.00022163 | 0.00022287 | 0.0002241 | 0.00022534 | 0.00022657 | 0.00022781 | 0.00022905 | 0.00023028 | 0.00023152 | 0.00023275 | 0.00023399 | 0.00023522 | 0.00023646 | 0.00023769 | 0.00023893 | 1.2231e-05 | 1.2446e-05 | 1.261e-05 | 1.2703e-05 | 1.2654e-05 | 1.2625e-05 | 1.2796e-05 | 1.3023e-05 | 1.2943e-05 | 1.3014e-05 | 1.3085e-05 | 1.3156e-05 | 1.3227e-05 | 1.3298e-05 | 1.3368e-05 | 1.3439e-05 | 1.351e-05 | 1.3581e-05 | 1.3652e-05 | 1.3723e-05 | 26719.9676 | 3421.3779 | 5.0122 | 0.64179 | 60.6252 | 60.6252 | 353494.8929 | 60.6252
| CHA006-15429283 | 274 | CHA006 | CHA | North | 6457173.3765 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 8.7738 | 8.8328 | 8.8919 | 8.951 | 9.0101 | 9.0862 | 9.1624 | 9.2385 | 9.3146 | 9.3907 | 9.4669 | 9.543 | 9.6191 | 9.6953 | 9.7714 | 9.8475 | 9.9236 | 9.9998 | 10.0759 | 10.152 | 0.50414 | 0.51191 | 0.5176 | 0.52037 | 0.51731 | 0.51759 | 0.52605 | 0.53687 | 0.535 | 0.53938 | 0.54375 | 0.54812 | 0.55249 | 0.55687 | 0.56124 | 0.56561 | 0.56998 | 0.57436 | 0.57873 | 0.5831 | 26719.9676 | 3421.3779 | 208022.8949 | 26636.4444 | 709718.1854 | 709718.1854 | 6457173.3765 | 709718.1854
| CHA006-155505830 | 129 | CHA006 | CHA | North | 3040056.0787 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0082267 | 0.0082901 | 0.0083535 | 0.0084169 | 0.0084804 | 0.008524 | 0.0085677 | 0.0086114 | 0.008655 | 0.0086987 | 0.0087424 | 0.008786 | 0.0088297 | 0.0088733 | 0.008917 | 0.0089607 | 0.0090043 | 0.009048 | 0.0090917 | 0.0091353 | 0.0004727 | 0.00048045 | 0.00048626 | 0.00048932 | 0.00048689 | 0.00048556 | 0.00049191 | 0.00050043 | 0.00049712 | 0.00049963 | 0.00050213 | 0.00050464 | 0.00050715 | 0.00050966 | 0.00051217 | 0.00051467 | 0.00051718 | 0.00051969 | 0.0005222 | 0.00052471 | 26719.9676 | 3421.3779 | 192.5578 | 24.6562 | 12276.4952 | 12276.4952 | 3040056.0787 | 12276.4952
| CHA006-155506079 | 82 | CHA006 | CHA | North | 1932438.7477 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.099325 | 0.099816 | 0.10031 | 0.1008 | 0.10129 | 0.10164 | 0.10198 | 0.10233 | 0.10267 | 0.10302 | 0.10337 | 0.10371 | 0.10406 | 0.1044 | 0.10475 | 0.1051 | 0.10544 | 0.10579 | 0.10614 | 0.10648 | 0.0057071 | 0.0057848 | 0.0058389 | 0.0058599 | 0.0058154 | 0.0057895 | 0.0058552 | 0.0059465 | 0.0058972 | 0.0059171 | 0.005937 | 0.0059569 | 0.0059768 | 0.0059967 | 0.0060165 | 0.0060364 | 0.0060563 | 0.0060762 | 0.0060961 | 0.0061159 | 26719.9676 | 3421.3779 | 2284.2582 | 292.4895 | 71742.0358 | 71742.0358 | 1932438.7477 | 71742.0358
| CHA006-155506186 | 102 | CHA006 | CHA | North | 2403765.2716 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0098412 | 0.0099007 | 0.0099601 | 0.01002 | 0.010079 | 0.010116 | 0.010152 | 0.010189 | 0.010225 | 0.010262 | 0.010298 | 0.010335 | 0.010372 | 0.010408 | 0.010445 | 0.010481 | 0.010518 | 0.010554 | 0.010591 | 0.010628 | 0.00056547 | 0.00057379 | 0.00057978 | 0.00058249 | 0.00057868 | 0.00057623 | 0.00058288 | 0.0005921 | 0.00058731 | 0.00058941 | 0.00059151 | 0.00059361 | 0.00059571 | 0.00059781 | 0.00059992 | 0.00060202 | 0.00060412 | 0.00060622 | 0.00060832 | 0.00061042 | 26719.9676 | 3421.3779 | 227.3835 | 29.1155 | 11104.1686 | 11104.1686 | 2403765.2716 | 11104.1686
| CHA006-155506347 | 42 | CHA006 | CHA | North | 989785.7001 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.011962 | 0.012031 | 0.012099 | 0.012167 | 0.012235 | 0.012281 | 0.012326 | 0.012372 | 0.012417 | 0.012462 | 0.012508 | 0.012553 | 0.012599 | 0.012644 | 0.01269 | 0.012735 | 0.012781 | 0.012826 | 0.012871 | 0.012917 | 0.00068736 | 0.00069724 | 0.00070428 | 0.00070733 | 0.00070248 | 0.00069956 | 0.0007077 | 0.00071895 | 0.0007132 | 0.0007158 | 0.00071841 | 0.00072102 | 0.00072363 | 0.00072624 | 0.00072885 | 0.00073146 | 0.00073407 | 0.00073668 | 0.00073929 | 0.0007419 | 26719.9676 | 3421.3779 | 276.2023 | 35.3665 | 6128.5161 | 6128.5161 | 989785.7001 | 6128.5161
| CHA006-155506472 | 23 | CHA006 | CHA | North | 542025.5024 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.019381 | 0.019478 | 0.019575 | 0.019671 | 0.019768 | 0.019832 | 0.019897 | 0.019961 | 0.020025 | 0.020089 | 0.020154 | 0.020218 | 0.020282 | 0.020346 | 0.02041 | 0.020475 | 0.020539 | 0.020603 | 0.020667 | 0.020732 | 0.0011136 | 0.0011288 | 0.0011394 | 0.0011436 | 0.001135 | 0.0011297 | 0.0011424 | 0.00116 | 0.0011502 | 0.0011539 | 0.0011576 | 0.0011612 | 0.0011649 | 0.0011686 | 0.0011723 | 0.001176 | 0.0011797 | 0.0011834 | 0.0011871 | 0.0011908 | 26719.9676 | 3421.3779 | 445.4248 | 57.0347 | 15695.5375 | 15695.5375 | 542025.5024 | 15695.5375
| CHA006-155506614 | 48 | CHA006 | CHA | North | 1131183.6572 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.00016294 | 0.00016446 | 0.00016597 | 0.00016749 | 0.000169 | 0.0001702 | 0.0001714 | 0.0001726 | 0.0001738 | 0.000175 | 0.0001762 | 0.0001774 | 0.0001786 | 0.0001798 | 0.000181 | 0.0001822 | 0.0001834 | 0.0001846 | 0.0001858 | 0.000187 | 9.3626e-06 | 9.5311e-06 | 9.6612e-06 | 9.7368e-06 | 9.703e-06 | 9.6953e-06 | 9.8408e-06 | 1.003e-05 | 9.9825e-06 | 1.0051e-05 | 1.012e-05 | 1.0189e-05 | 1.0258e-05 | 1.0327e-05 | 1.0396e-05 | 1.0465e-05 | 1.0534e-05 | 1.0603e-05 | 1.0672e-05 | 1.0741e-05 | 26719.9676 | 3421.3779 | 3.8705 | 0.4956 | 569.2838 | 569.2838 | 1131183.6572 | 569.2838
| CHA006-155618024 | 25 | CHA006 | CHA | North | 589158.1548 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.00045352 | 0.00045704 | 0.00046056 | 0.00046408 | 0.0004676 | 0.00047215 | 0.0004767 | 0.00048125 | 0.0004858 | 0.00049035 | 0.0004949 | 0.00049945 | 0.000504 | 0.00050855 | 0.0005131 | 0.00051765 | 0.0005222 | 0.00052675 | 0.0005313 | 0.00053585 | 2.6059e-05 | 2.6488e-05 | 2.6809e-05 | 2.6979e-05 | 2.6847e-05 | 2.6895e-05 | 2.7369e-05 | 2.7967e-05 | 2.7903e-05 | 2.8164e-05 | 2.8426e-05 | 2.8687e-05 | 2.8948e-05 | 2.921e-05 | 2.9471e-05 | 2.9732e-05 | 2.9994e-05 | 3.0255e-05 | 3.0516e-05 | 3.0778e-05 | 26719.9676 | 3421.3779 | 10.856 | 1.3901 | 297.019 | 297.019 | 589158.1548 | 297.019
| CHA006-155618140 | 28 | CHA006 | CHA | North | 659857.1334 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.11383 | 0.1139 | 0.11398 | 0.11405 | 0.11412 | 0.11407 | 0.11401 | 0.11395 | 0.1139 | 0.11384 | 0.11379 | 0.11373 | 0.11367 | 0.11362 | 0.11356 | 0.1135 | 0.11345 | 0.11339 | 0.11334 | 0.11328 | 0.0065408 | 0.0066014 | 0.0066346 | 0.0066303 | 0.0065522 | 0.0064976 | 0.0065458 | 0.0066221 | 0.0065419 | 0.0065387 | 0.0065355 | 0.0065322 | 0.006529 | 0.0065258 | 0.0065226 | 0.0065194 | 0.0065162 | 0.0065129 | 0.0065097 | 0.0065065 | 26719.9676 | 3421.3779 | 2530.9932 | 324.0829 | 60315.4829 | 60315.4829 | 659857.1334 | 60315.4829
| CHA006-155618314 | 209 | CHA006 | CHA | North | 4925362.1741 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.020321 | 0.020416 | 0.020511 | 0.020606 | 0.020701 | 0.020774 | 0.020847 | 0.020919 | 0.020992 | 0.021065 | 0.021137 | 0.02121 | 0.021282 | 0.021355 | 0.021428 | 0.0215 | 0.021573 | 0.021646 | 0.021718 | 0.021791 | 0.0011676 | 0.0011832 | 0.001194 | 0.0011979 | 0.0011886 | 0.0011834 | 0.0011969 | 0.0012157 | 0.0012057 | 0.0012099 | 0.0012141 | 0.0012182 | 0.0012224 | 0.0012266 | 0.0012307 | 0.0012349 | 0.0012391 | 0.0012433 | 0.0012474 | 0.0012516 | 26719.9676 | 3421.3779 | 467.143 | 59.8157 | 67990.4871 | 67990.4871 | 4925362.1741 | 67990.4871
| CHA006-155621164 | 17 | CHA006 | CHA | North | 400627.5453 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.045638 | 0.045852 | 0.046066 | 0.046279 | 0.046493 | 0.046583 | 0.046674 | 0.046764 | 0.046854 | 0.046944 | 0.047034 | 0.047124 | 0.047215 | 0.047305 | 0.047395 | 0.047485 | 0.047575 | 0.047666 | 0.047756 | 0.047846 | 0.0026223 | 0.0026573 | 0.0026815 | 0.0026905 | 0.0026694 | 0.0026536 | 0.0026797 | 0.0027176 | 0.0026911 | 0.0026963 | 0.0027015 | 0.0027067 | 0.0027119 | 0.002717 | 0.0027222 | 0.0027274 | 0.0027326 | 0.0027378 | 0.0027429 | 0.0027481 | 26719.9676 | 3421.3779 | 1041.0201 | 133.2982 | 24648.0901 | 24648.0901 | 400627.5453 | 24648.0901
| CHA006-155668372 | 34 | CHA006 | CHA | North | 801255.0905 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0026839 | 0.0027067 | 0.0027294 | 0.0027522 | 0.0027749 | 0.0028038 | 0.0028327 | 0.0028616 | 0.0028904 | 0.0029193 | 0.0029482 | 0.0029771 | 0.003006 | 0.0030349 | 0.0030637 | 0.0030926 | 0.0031215 | 0.0031504 | 0.0031793 | 0.0032081 | 0.00015422 | 0.00015686 | 0.00015888 | 0.00016 | 0.00015932 | 0.00015972 | 0.00016264 | 0.00016629 | 0.00016602 | 0.00016768 | 0.00016934 | 0.00017099 | 0.00017265 | 0.00017431 | 0.00017597 | 0.00017763 | 0.00017929 | 0.00018095 | 0.00018261 | 0.00018427 | 26719.9676 | 3421.3779 | 64.6057 | 8.2725 | 4206.9505 | 4206.9505 | 801255.0905 | 4206.9505
| CHA006-155668704 | 32 | CHA006 | CHA | North | 754122.4381 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0030997 | 0.0031238 | 0.0031478 | 0.0031719 | 0.003196 | 0.0032294 | 0.0032627 | 0.0032961 | 0.0033295 | 0.0033629 | 0.0033963 | 0.0034297 | 0.0034631 | 0.0034965 | 0.0035298 | 0.0035632 | 0.0035966 | 0.00363 | 0.0036634 | 0.0036968 | 0.00017811 | 0.00018104 | 0.00018324 | 0.0001844 | 0.00018349 | 0.00018396 | 0.00018733 | 0.00019155 | 0.00019124 | 0.00019316 | 0.00019507 | 0.00019699 | 0.00019891 | 0.00020083 | 0.00020274 | 0.00020466 | 0.00020658 | 0.0002085 | 0.00021041 | 0.00021233 | 26719.9676 | 3421.3779 | 74.4537 | 9.5335 | 4056.0302 | 4056.0302 | 754122.4381 | 4056.0302
| CHA006-155668831 | 85 | CHA006 | CHA | North | 2003137.7263 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.017441 | 0.017579 | 0.017717 | 0.017854 | 0.017992 | 0.018123 | 0.018253 | 0.018384 | 0.018514 | 0.018644 | 0.018775 | 0.018905 | 0.019036 | 0.019166 | 0.019296 | 0.019427 | 0.019557 | 0.019688 | 0.019818 | 0.019948 | 0.0010022 | 0.0010188 | 0.0010313 | 0.001038 | 0.001033 | 0.0010323 | 0.001048 | 0.0010683 | 0.0010634 | 0.0010709 | 0.0010784 | 0.0010859 | 0.0010933 | 0.0011008 | 0.0011083 | 0.0011158 | 0.0011233 | 0.0011308 | 0.0011383 | 0.0011458 | 26719.9676 | 3421.3779 | 412.7011 | 52.8446 | 19906.0467 | 19906.0467 | 2003137.7263 | 19906.0467
| CHA006-155727138 | 26 | CHA006 | CHA | North | 612724.481 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0019791 | 0.0019943 | 0.0020095 | 0.0020248 | 0.00204 | 0.0020634 | 0.0020869 | 0.0021103 | 0.0021337 | 0.0021572 | 0.0021806 | 0.002204 | 0.0022274 | 0.0022509 | 0.0022743 | 0.0022977 | 0.0023212 | 0.0023446 | 0.002368 | 0.0023915 | 0.00011372 | 0.00011558 | 0.00011698 | 0.00011771 | 0.00011712 | 0.00011754 | 0.00011982 | 0.00012263 | 0.00012255 | 0.0001239 | 0.00012525 | 0.00012659 | 0.00012794 | 0.00012928 | 0.00013063 | 0.00013198 | 0.00013332 | 0.00013467 | 0.00013601 | 0.00013736 | 26719.9676 | 3421.3779 | 47.7623 | 6.1158 | 1902.6985 | 1902.6985 | 612724.481 | 1902.6985
| CHA006-155747849 | 151 | CHA006 | CHA | North | 3558515.255 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.11696 | 0.11765 | 0.11834 | 0.11903 | 0.11973 | 0.12009 | 0.12044 | 0.1208 | 0.12116 | 0.12152 | 0.12188 | 0.12224 | 0.1226 | 0.12296 | 0.12332 | 0.12368 | 0.12404 | 0.12439 | 0.12475 | 0.12511 | 0.0067204 | 0.0068184 | 0.0068887 | 0.0069201 | 0.006874 | 0.0068406 | 0.0069153 | 0.0070202 | 0.0069592 | 0.0069799 | 0.0070005 | 0.0070211 | 0.0070417 | 0.0070623 | 0.007083 | 0.0071036 | 0.0071242 | 0.0071448 | 0.0071655 | 0.0071861 | 26719.9676 | 3421.3779 | 2692.8429 | 344.8071 | 327875.023 | 327875.023 | 3558515.255 | 327875.023
| CHA006-156354256 | 25 | CHA006 | CHA | North | 589158.1548 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0038565 | 0.0038821 | 0.0039078 | 0.0039334 | 0.003959 | 0.004013 | 0.004067 | 0.004121 | 0.0041751 | 0.0042291 | 0.0042831 | 0.0043371 | 0.0043911 | 0.0044451 | 0.0044991 | 0.0045531 | 0.0046072 | 0.0046612 | 0.0047152 | 0.0047692 | 0.00022159 | 0.00022499 | 0.00022747 | 0.00022867 | 0.0002273 | 0.0002286 | 0.00023351 | 0.00023948 | 0.0002398 | 0.0002429 | 0.00024601 | 0.00024911 | 0.00025221 | 0.00025531 | 0.00025842 | 0.00026152 | 0.00026462 | 0.00026772 | 0.00027083 | 0.00027393 | 26719.9676 | 3421.3779 | 93.7017 | 11.9981 | 1560.5523 | 1560.5523 | 589158.1548 | 1560.5523
| CHA006-164004018 | 12 | CHA006 | CHA | North | 282795.9143 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.018701 | 0.018851 | 0.019001 | 0.019151 | 0.019301 | 0.019507 | 0.019713 | 0.01992 | 0.020126 | 0.020332 | 0.020539 | 0.020745 | 0.020952 | 0.021158 | 0.021364 | 0.021571 | 0.021777 | 0.021983 | 0.02219 | 0.022396 | 0.0010746 | 0.0010925 | 0.0011061 | 0.0011133 | 0.0011081 | 0.0011112 | 0.0011318 | 0.0011576 | 0.001156 | 0.0011678 | 0.0011797 | 0.0011915 | 0.0012034 | 0.0012152 | 0.0012271 | 0.0012389 | 0.0012508 | 0.0012627 | 0.0012745 | 0.0012864 | 26719.9676 | 3421.3779 | 450.0922 | 57.6324 | 6896.2012 | 6896.2012 | 282795.9143 | 6896.2012
| CHA006-164004212 | 12 | CHA006 | CHA | North | 282795.9143 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0016069 | 0.0016193 | 0.0016316 | 0.001644 | 0.0016564 | 0.0016754 | 0.0016944 | 0.0017134 | 0.0017325 | 0.0017515 | 0.0017705 | 0.0017896 | 0.0018086 | 0.0018276 | 0.0018466 | 0.0018657 | 0.0018847 | 0.0019037 | 0.0019227 | 0.0019418 | 9.2332e-05 | 9.3845e-05 | 9.4978e-05 | 9.5575e-05 | 9.5099e-05 | 9.5437e-05 | 9.7284e-05 | 9.9573e-05 | 9.9508e-05 | 0.0001006 | 0.00010169 | 0.00010279 | 0.00010388 | 0.00010497 | 0.00010606 | 0.00010716 | 0.00010825 | 0.00010934 | 0.00011044 | 0.00011153 | 26719.9676 | 3421.3779 | 38.7806 | 4.9657 | 713.029 | 713.029 | 282795.9143 | 713.029
| CHA006-164004465 | 10 | CHA006 | CHA | North | 235663.2619 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.00057641 | 0.00058071 | 0.00058501 | 0.0005893 | 0.0005936 | 0.000602 | 0.0006104 | 0.0006188 | 0.0006272 | 0.0006356 | 0.000644 | 0.0006524 | 0.0006608 | 0.0006692 | 0.0006776 | 0.000686 | 0.0006944 | 0.0007028 | 0.0007112 | 0.0007196 | 3.312e-05 | 3.3655e-05 | 3.4053e-05 | 3.4259e-05 | 3.4081e-05 | 3.4292e-05 | 3.5046e-05 | 3.596e-05 | 3.6024e-05 | 3.6507e-05 | 3.6989e-05 | 3.7472e-05 | 3.7954e-05 | 3.8437e-05 | 3.8919e-05 | 3.9402e-05 | 3.9884e-05 | 4.0367e-05 | 4.0849e-05 | 4.1332e-05 | 26719.9676 | 3421.3779 | 14.0762 | 1.8024 | 269.5989 | 269.5989 | 235663.2619 | 269.5989
| CHA006-164281123 | 9 | CHA006 | CHA | North | 212096.9357 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26719.9676 | 3421.3779 | 0 | 0 | 0 | 0 | 212096.9357 | 0
| CHA006-181783097 | 8 | CHA006 | CHA | North | 188530.6095 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26719.9676 | 3421.3779 | 0 | 0 | 0 | 0 | 188530.6095 | 0
| CHA006-185820630 | 198 | CHA006 | CHA | North | 4666132.586 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 3.0018 | 3.0176 | 3.0333 | 3.049 | 3.0647 | 3.0744 | 3.0842 | 3.0939 | 3.1036 | 3.1133 | 3.123 | 3.1327 | 3.1424 | 3.1522 | 3.1619 | 3.1716 | 3.1813 | 3.191 | 3.2007 | 3.2104 | 0.17248 | 0.17488 | 0.17657 | 0.17725 | 0.17596 | 0.17513 | 0.17708 | 0.17979 | 0.17826 | 0.17882 | 0.17938 | 0.17993 | 0.18049 | 0.18105 | 0.18161 | 0.18217 | 0.18272 | 0.18328 | 0.18384 | 0.1844 | 26719.9676 | 3421.3779 | 69018.2067 | 8837.487 | 262708.8951 | 262708.8951 | 4666132.586 | 262708.8951
| CHA006-202038162 | 339 | CHA006 | CHA | North | 7988984.579 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 1.8645 | 1.8744 | 1.8843 | 1.8941 | 1.904 | 1.9103 | 1.9167 | 1.923 | 1.9293 | 1.9356 | 1.9419 | 1.9482 | 1.9545 | 1.9608 | 1.9671 | 1.9735 | 1.9798 | 1.9861 | 1.9924 | 1.9987 | 0.10713 | 0.10863 | 0.10968 | 0.11012 | 0.10932 | 0.10882 | 0.11004 | 0.11175 | 0.11081 | 0.11117 | 0.11154 | 0.1119 | 0.11226 | 0.11262 | 0.11299 | 0.11335 | 0.11371 | 0.11407 | 0.11444 | 0.1148 | 26719.9676 | 3421.3779 | 42908.1501 | 5494.2056 | 1267036.4345 | 1267036.4345 | 7988984.579 | 1267036.4345
| CHA006-24606426 | 180 | CHA006 | CHA | North | 4241938.7145 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 4.3522 | 4.3635 | 4.3748 | 4.3862 | 4.3975 | 4.4052 | 4.4129 | 4.4207 | 4.4284 | 4.4361 | 4.4438 | 4.4516 | 4.4593 | 4.467 | 4.4747 | 4.4824 | 4.4902 | 4.4979 | 4.5056 | 4.5133 | 0.25007 | 0.25289 | 0.25466 | 0.25499 | 0.25248 | 0.25094 | 0.25337 | 0.2569 | 0.25435 | 0.2548 | 0.25524 | 0.25568 | 0.25613 | 0.25657 | 0.25701 | 0.25746 | 0.2579 | 0.25834 | 0.25879 | 0.25923 | 26719.9676 | 3421.3779 | 98504.1871 | 12613.041 | 870498.0764 | 870498.0764 | 4241938.7145 | 870498.0764
| CHA006-56709766 | 112 | CHA006 | CHA | North | 2639428.5335 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.022845 | 0.023016 | 0.023186 | 0.023357 | 0.023527 | 0.023859 | 0.024191 | 0.024523 | 0.024854 | 0.025186 | 0.025518 | 0.02585 | 0.026182 | 0.026513 | 0.026845 | 0.027177 | 0.027509 | 0.027841 | 0.028172 | 0.028504 | 0.0013127 | 0.0013339 | 0.0013497 | 0.0013578 | 0.0013508 | 0.0013591 | 0.0013889 | 0.0014251 | 0.0014276 | 0.0014466 | 0.0014657 | 0.0014847 | 0.0015038 | 0.0015228 | 0.0015419 | 0.001561 | 0.00158 | 0.0015991 | 0.0016181 | 0.0016372 | 26719.9676 | 3421.3779 | 557.7782 | 71.4211 | 8617.3799 | 8617.3799 | 2639428.5335 | 8617.3799
| CHA006-95436119 | 161 | CHA006 | CHA | North | 3794178.5169 | 0.0020639 | 0.0020817 | 0.0020909 | 0.0020882 | 0.0020623 | 0.0020461 | 0.0020623 | 0.0020874 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 0.0020631 | 3.739 | 3.7628 | 3.7865 | 3.8103 | 3.8341 | 3.8715 | 3.9088 | 3.9462 | 3.9835 | 4.0209 | 4.0583 | 4.0956 | 4.133 | 4.1704 | 4.2077 | 4.2451 | 4.2824 | 4.3198 | 4.3572 | 4.3945 | 0.21484 | 0.21807 | 0.22041 | 0.22151 | 0.22013 | 0.22053 | 0.22442 | 0.22932 | 0.2288 | 0.23095 | 0.23309 | 0.23524 | 0.23739 | 0.23953 | 0.24168 | 0.24382 | 0.24597 | 0.24812 | 0.25026 | 0.25241 | 26719.9676 | 3421.3779 | 89094.2939 | 11408.1443 | 1322180.8887 | 1322180.8887 | 3794178.5169 | 1322180.8887
| CHA007-162618256 | 0 | CHA007 | CHA | North | 0 | 0.086 | 0.086 | 0.0845 | 0.081 | 0.0795 | 0.0795 | 0.076 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 0.0745 | 1.4454e-05 | 1.4566e-05 | 1.4677e-05 | 1.4789e-05 | 1.49e-05 | 1.509e-05 | 1.528e-05 | 1.547e-05 | 1.566e-05 | 1.585e-05 | 1.604e-05 | 1.623e-05 | 1.642e-05 | 1.661e-05 | 1.68e-05 | 1.699e-05 | 1.718e-05 | 1.737e-05 | 1.756e-05 | 1.775e-05 | 3.4607e-05 | 3.4874e-05 | 3.4528e-05 | 3.3349e-05 | 3.2978e-05 | 3.3398e-05 | 3.233e-05 | 3.2086e-05 | 3.248e-05 | 3.2874e-05 | 3.3268e-05 | 3.3662e-05 | 3.4056e-05 | 3.445e-05 | 3.4845e-05 | 3.5239e-05 | 3.5633e-05 | 3.6027e-05 | 3.6421e-05 | 3.6815e-05 | 26719.9676 | 3421.3779 | 0 | 0 | 0 | 0 | 0 | 0
| CHA008-162618131 | 0 | CHA008 | CHA | North | 0 | 0.07 | 0.07 | 0.0665 | 0.065 | 0.065 | 0.065 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 1.1642e-05 | 1.1732e-05 | 1.1821e-05 | 1.1911e-05 | 1.2e-05 | 1.215e-05 | 1.23e-05 | 1.245e-05 | 1.26e-05 | 1.275e-05 | 1.29e-05 | 1.305e-05 | 1.32e-05 | 1.335e-05 | 1.35e-05 | 1.365e-05 | 1.38e-05 | 1.395e-05 | 1.41e-05 | 1.425e-05 | 2.2688e-05 | 2.2863e-05 | 2.1885e-05 | 2.1553e-05 | 2.1715e-05 | 2.1987e-05 | 2.0546e-05 | 2.0796e-05 | 2.1047e-05 | 2.1298e-05 | 2.1548e-05 | 2.1799e-05 | 2.2049e-05 | 2.23e-05 | 2.255e-05 | 2.2801e-05 | 2.3052e-05 | 2.3302e-05 | 2.3553e-05 | 2.3803e-05 | 26719.9676 | 3421.3779 | 0 | 0 | 0 | 0 | 0 | 0
| CHM011-15436218 | 6 | CHM011 | CHM | North | 141397.9572 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 7.7143e-06 | 7.7657e-06 | 7.8171e-06 | 7.8686e-06 | 7.92e-06 | 7.914e-06 | 7.908e-06 | 7.902e-06 | 7.896e-06 | 7.89e-06 | 7.884e-06 | 7.878e-06 | 7.872e-06 | 7.866e-06 | 7.86e-06 | 7.854e-06 | 7.848e-06 | 7.842e-06 | 7.836e-06 | 7.83e-06 | 1.6831e-07 | 1.662e-07 | 1.666e-07 | 1.6556e-07 | 1.6378e-07 | 1.6151e-07 | 1.6138e-07 | 1.6198e-07 | 1.595e-07 | 1.5937e-07 | 1.5925e-07 | 1.5913e-07 | 1.5901e-07 | 1.5889e-07 | 1.5877e-07 | 1.5865e-07 | 1.5853e-07 | 1.5841e-07 | 1.5828e-07 | 1.5816e-07 | 33888.7274 | 7378.012 | 0.079205 | 0.017244 | 5.3538 | 5.3538 | 141397.9572 | 5.3538
| CHM011-159371854 | 31 | CHM011 | CHM | North | 730556.1119 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.035807 | 0.036022 | 0.036238 | 0.036453 | 0.036669 | 0.036444 | 0.03622 | 0.035995 | 0.035771 | 0.035546 | 0.035322 | 0.035097 | 0.034873 | 0.034648 | 0.034424 | 0.034199 | 0.033975 | 0.03375 | 0.033526 | 0.033301 | 0.00078124 | 0.00077096 | 0.00077229 | 0.000767 | 0.00075827 | 0.00074374 | 0.00073916 | 0.00073783 | 0.00072256 | 0.00071802 | 0.00071349 | 0.00070895 | 0.00070442 | 0.00069988 | 0.00069535 | 0.00069081 | 0.00068628 | 0.00068174 | 0.00067721 | 0.00067267 | 33888.7274 | 7378.012 | 357.0834 | 77.7416 | 26709.3005 | 26709.3005 | 730556.1119 | 26709.3005
| CHM011-159371937 | 84 | CHM011 | CHM | North | 1979571.4001 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.0049465 | 0.0049794 | 0.0050124 | 0.0050453 | 0.0050783 | 0.0050456 | 0.0050128 | 0.0049801 | 0.0049474 | 0.0049147 | 0.0048819 | 0.0048492 | 0.0048165 | 0.0047838 | 0.0047511 | 0.0047183 | 0.0046856 | 0.0046529 | 0.0046202 | 0.0045874 | 0.00010792 | 0.00010657 | 0.00010682 | 0.00010616 | 0.00010501 | 0.00010297 | 0.0001023 | 0.00010208 | 9.9935e-05 | 9.9274e-05 | 9.8613e-05 | 9.7952e-05 | 9.7291e-05 | 9.663e-05 | 9.5969e-05 | 9.5308e-05 | 9.4647e-05 | 9.3986e-05 | 9.3325e-05 | 9.2664e-05 | 33888.7274 | 7378.012 | 49.3499 | 10.7441 | 10771.5201 | 10771.5201 | 1979571.4001 | 10771.5201
| CHM011-159372020 | 97 | CHM011 | CHM | North | 2285933.6406 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.1102 | 0.11083 | 0.11146 | 0.11209 | 0.11272 | 0.11205 | 0.11139 | 0.11073 | 0.11006 | 0.1094 | 0.10874 | 0.10808 | 0.10741 | 0.10675 | 0.10609 | 0.10542 | 0.10476 | 0.1041 | 0.10344 | 0.10277 | 0.0024044 | 0.002372 | 0.0023754 | 0.0023584 | 0.0023308 | 0.0022867 | 0.0022732 | 0.0022697 | 0.0022233 | 0.0022099 | 0.0021965 | 0.0021831 | 0.0021697 | 0.0021563 | 0.0021429 | 0.0021295 | 0.0021161 | 0.0021028 | 0.0020894 | 0.002076 | 33888.7274 | 7378.012 | 1099.2257 | 239.3156 | 133401.2384 | 133401.2384 | 2285933.6406 | 133401.2384
| CHM011-159372116 | 38 | CHM011 | CHM | North | 895520.3953 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.0117 | 0.011772 | 0.011844 | 0.011916 | 0.011988 | 0.011914 | 0.011839 | 0.011764 | 0.01169 | 0.011615 | 0.01154 | 0.011466 | 0.011391 | 0.011316 | 0.011242 | 0.011167 | 0.011092 | 0.011017 | 0.010943 | 0.010868 | 0.00025526 | 0.00025194 | 0.00025242 | 0.00025072 | 0.00024791 | 0.00024313 | 0.00024161 | 0.00024115 | 0.00023613 | 0.00023462 | 0.00023311 | 0.0002316 | 0.00023009 | 0.00022858 | 0.00022707 | 0.00022557 | 0.00022406 | 0.00022255 | 0.00022104 | 0.00021953 | 33888.7274 | 7378.012 | 116.6675 | 25.4 | 10697.0089 | 10697.0089 | 895520.3953 | 10697.0089
| CHM011-159372219 | 117 | CHM011 | CHM | North | 2757260.1644 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.088855 | 0.089313 | 0.089771 | 0.09023 | 0.090688 | 0.090193 | 0.089697 | 0.089202 | 0.088706 | 0.088211 | 0.087715 | 0.08722 | 0.086724 | 0.086229 | 0.085734 | 0.085238 | 0.084743 | 0.084247 | 0.083752 | 0.083256 | 0.0019386 | 0.0019115 | 0.0019132 | 0.0018985 | 0.0018753 | 0.0018406 | 0.0018305 | 0.0018285 | 0.0017918 | 0.0017818 | 0.0017718 | 0.0017618 | 0.0017518 | 0.0017418 | 0.0017318 | 0.0017218 | 0.0017118 | 0.0017018 | 0.0016917 | 0.0016817 | 33888.7274 | 7378.012 | 886.618 | 193.0281 | 83434.9484 | 83434.9484 | 2757260.1644 | 83434.9484
| CHM011-159372384 | 67 | CHM011 | CHM | North | 1578943.8548 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.01258 | 0.012651 | 0.012723 | 0.012794 | 0.012865 | 0.012803 | 0.012741 | 0.01268 | 0.012618 | 0.012556 | 0.012494 | 0.012432 | 0.01237 | 0.012308 | 0.012247 | 0.012185 | 0.012123 | 0.012061 | 0.011999 | 0.011937 | 0.00027447 | 0.00027077 | 0.00027114 | 0.00026919 | 0.00026603 | 0.00026128 | 0.00026002 | 0.0002599 | 0.00025487 | 0.00025362 | 0.00025237 | 0.00025112 | 0.00024988 | 0.00024863 | 0.00024738 | 0.00024613 | 0.00024488 | 0.00024363 | 0.00024238 | 0.00024113 | 33888.7274 | 7378.012 | 126.1529 | 27.4651 | 8158.5299 | 8158.5299 | 1578943.8548 | 8158.5299
| CHM011-159372472 | 25 | CHM011 | CHM | North | 589158.1548 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.0038911 | 0.0039106 | 0.0039302 | 0.0039498 | 0.0039693 | 0.0039494 | 0.0039294 | 0.0039095 | 0.0038895 | 0.0038695 | 0.0038496 | 0.0038296 | 0.0038097 | 0.0037897 | 0.0037697 | 0.0037498 | 0.0037298 | 0.0037099 | 0.0036899 | 0.0036699 | 8.4896e-05 | 8.3696e-05 | 8.376e-05 | 8.3105e-05 | 8.2081e-05 | 8.0597e-05 | 8.019e-05 | 8.0136e-05 | 7.8566e-05 | 7.8163e-05 | 7.776e-05 | 7.7357e-05 | 7.6953e-05 | 7.655e-05 | 7.6147e-05 | 7.5744e-05 | 7.5341e-05 | 7.4938e-05 | 7.4534e-05 | 7.4131e-05 | 33888.7274 | 7378.012 | 38.8957 | 8.4681 | 2737.4833 | 2737.4833 | 589158.1548 | 2737.4833
| CHM011-159372576 | 30 | CHM011 | CHM | North | 706989.7858 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.030201 | 0.030376 | 0.030551 | 0.030726 | 0.030902 | 0.030718 | 0.030534 | 0.03035 | 0.030166 | 0.029982 | 0.029798 | 0.029614 | 0.02943 | 0.029246 | 0.029063 | 0.028879 | 0.028695 | 0.028511 | 0.028327 | 0.028143 | 0.00065893 | 0.00065012 | 0.0006511 | 0.0006465 | 0.00063901 | 0.00062687 | 0.00062312 | 0.00062211 | 0.00060934 | 0.00060563 | 0.00060191 | 0.0005982 | 0.00059448 | 0.00059077 | 0.00058705 | 0.00058334 | 0.00057962 | 0.00057591 | 0.00057219 | 0.00056848 | 33888.7274 | 7378.012 | 301.2298 | 65.5816 | 50878.1447 | 50878.1447 | 706989.7858 | 50878.1447
| CHM011-159372815 | 30 | CHM011 | CHM | North | 706989.7858 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00033572 | 0.00033814 | 0.00034056 | 0.00034298 | 0.0003454 | 0.00034276 | 0.00034012 | 0.00033748 | 0.00033484 | 0.0003322 | 0.00032956 | 0.00032692 | 0.00032428 | 0.00032164 | 0.000319 | 0.00031636 | 0.00031372 | 0.00031108 | 0.00030844 | 0.0003058 | 7.3248e-06 | 7.2369e-06 | 7.2579e-06 | 7.2165e-06 | 7.1425e-06 | 6.9949e-06 | 6.941e-06 | 6.9177e-06 | 6.7636e-06 | 6.7103e-06 | 6.657e-06 | 6.6037e-06 | 6.5503e-06 | 6.497e-06 | 6.4437e-06 | 6.3903e-06 | 6.337e-06 | 6.2837e-06 | 6.2304e-06 | 6.177e-06 | 33888.7274 | 7378.012 | 3.3347 | 0.726 | 307.1823 | 307.1823 | 706989.7858 | 307.1823
| CHM011-159372981 | 22 | CHM011 | CHM | North | 518459.1762 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.017015 | 0.0171 | 0.017185 | 0.01727 | 0.017355 | 0.017251 | 0.017147 | 0.017043 | 0.016938 | 0.016834 | 0.01673 | 0.016625 | 0.016521 | 0.016417 | 0.016313 | 0.016208 | 0.016104 | 0.016 | 0.015896 | 0.015791 | 0.00037123 | 0.00036597 | 0.00036624 | 0.00036337 | 0.00035889 | 0.00035205 | 0.00034993 | 0.00034934 | 0.00034215 | 0.00034004 | 0.00033793 | 0.00033583 | 0.00033372 | 0.00033162 | 0.00032951 | 0.0003274 | 0.0003253 | 0.00032319 | 0.00032108 | 0.00031898 | 33888.7274 | 7378.012 | 169.2231 | 36.842 | 8982.6651 | 8982.6651 | 518459.1762 | 8982.6651
| CHM011-159373200 | 78 | CHM011 | CHM | North | 1838173.443 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.076187 | 0.076622 | 0.077058 | 0.077494 | 0.077929 | 0.07742 | 0.076911 | 0.076402 | 0.075892 | 0.075383 | 0.074874 | 0.074364 | 0.073855 | 0.073346 | 0.072837 | 0.072327 | 0.071818 | 0.071309 | 0.070799 | 0.07029 | 0.0016623 | 0.0016399 | 0.0016422 | 0.0016305 | 0.0016115 | 0.00158 | 0.0015696 | 0.0015661 | 0.001533 | 0.0015227 | 0.0015124 | 0.0015021 | 0.0014918 | 0.0014816 | 0.0014713 | 0.001461 | 0.0014507 | 0.0014404 | 0.0014301 | 0.0014198 | 33888.7274 | 7378.012 | 757.4358 | 164.9035 | 52516.4535 | 52516.4535 | 1838173.443 | 52516.4535
| CHM011-159373315 | 27 | CHM011 | CHM | North | 636290.8072 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.0041733 | 0.0041953 | 0.0042172 | 0.0042392 | 0.0042612 | 0.0042341 | 0.004207 | 0.00418 | 0.0041529 | 0.0041258 | 0.0040988 | 0.0040717 | 0.0040446 | 0.0040176 | 0.0039905 | 0.0039634 | 0.0039364 | 0.0039093 | 0.0038822 | 0.0038552 | 9.1053e-05 | 8.9788e-05 | 8.9877e-05 | 8.9195e-05 | 8.8116e-05 | 8.6408e-05 | 8.5855e-05 | 8.5681e-05 | 8.3887e-05 | 8.334e-05 | 8.2793e-05 | 8.2247e-05 | 8.17e-05 | 8.1153e-05 | 8.0606e-05 | 8.006e-05 | 7.9513e-05 | 7.8966e-05 | 7.8419e-05 | 7.7872e-05 | 33888.7274 | 7378.012 | 41.4682 | 9.0282 | 2909.2122 | 2909.2122 | 636290.8072 | 2909.2122
| CHM011-159373411 | 33 | CHM011 | CHM | North | 777688.7643 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.0067318 | 0.006772 | 0.0068122 | 0.0068524 | 0.0068926 | 0.0068564 | 0.0068202 | 0.0067841 | 0.0067479 | 0.0067118 | 0.0066756 | 0.0066395 | 0.0066033 | 0.0065671 | 0.006531 | 0.0064948 | 0.0064587 | 0.0064225 | 0.0063863 | 0.0063502 | 0.00014687 | 0.00014493 | 0.00014518 | 0.00014418 | 0.00014253 | 0.00013992 | 0.00013918 | 0.00013906 | 0.00013631 | 0.00013558 | 0.00013484 | 0.00013411 | 0.00013338 | 0.00013265 | 0.00013192 | 0.00013119 | 0.00013046 | 0.00012973 | 0.000129 | 0.00012827 | 33888.7274 | 7378.012 | 67.4229 | 14.6788 | 6833.1791 | 6833.1791 | 777688.7643 | 6833.1791
| CHM011-160317885 | 74 | CHM011 | CHM | North | 1743908.1382 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.03315 | 0.033322 | 0.033494 | 0.033666 | 0.033839 | 0.033667 | 0.033496 | 0.033324 | 0.033153 | 0.032982 | 0.03281 | 0.032639 | 0.032467 | 0.032296 | 0.032125 | 0.031953 | 0.031782 | 0.031611 | 0.031439 | 0.031268 | 0.00072328 | 0.00071317 | 0.00071383 | 0.00070836 | 0.00069974 | 0.00068706 | 0.00068357 | 0.00068308 | 0.00066968 | 0.00066622 | 0.00066275 | 0.00065929 | 0.00065583 | 0.00065237 | 0.00064891 | 0.00064544 | 0.00064198 | 0.00063852 | 0.00063506 | 0.0006316 | 33888.7274 | 7378.012 | 331.4885 | 72.1693 | 34528.7104 | 34528.7104 | 1743908.1382 | 34528.7104
| CHM011-160318163 | 12 | CHM011 | CHM | North | 282795.9143 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00012646 | 0.00012735 | 0.00012825 | 0.00012915 | 0.00013005 | 0.00012917 | 0.0001283 | 0.00012742 | 0.00012655 | 0.00012567 | 0.0001248 | 0.00012392 | 0.00012305 | 0.00012217 | 0.00012129 | 0.00012042 | 0.00011954 | 0.00011867 | 0.00011779 | 0.00011692 | 2.759e-06 | 2.7257e-06 | 2.7333e-06 | 2.7174e-06 | 2.6893e-06 | 2.6361e-06 | 2.6183e-06 | 2.6119e-06 | 2.5562e-06 | 2.5385e-06 | 2.5208e-06 | 2.5032e-06 | 2.4855e-06 | 2.4678e-06 | 2.4501e-06 | 2.4324e-06 | 2.4147e-06 | 2.3971e-06 | 2.3794e-06 | 2.3617e-06 | 33888.7274 | 7378.012 | 1.2616 | 0.27466 | 30.0808 | 30.0808 | 282795.9143 | 30.0808
| CHM011-160318338 | 60 | CHM011 | CHM | North | 1413979.5715 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.0027712 | 0.0027887 | 0.0028063 | 0.0028239 | 0.0028415 | 0.0028221 | 0.0028027 | 0.0027832 | 0.0027638 | 0.0027444 | 0.002725 | 0.0027056 | 0.0026862 | 0.0026667 | 0.0026473 | 0.0026279 | 0.0026085 | 0.0025891 | 0.0025697 | 0.0025503 | 6.0461e-05 | 5.9685e-05 | 5.9808e-05 | 5.9416e-05 | 5.8758e-05 | 5.7591e-05 | 5.7195e-05 | 5.7051e-05 | 5.5828e-05 | 5.5436e-05 | 5.5044e-05 | 5.4652e-05 | 5.4259e-05 | 5.3867e-05 | 5.3475e-05 | 5.3083e-05 | 5.2691e-05 | 5.2299e-05 | 5.1906e-05 | 5.1514e-05 | 33888.7274 | 7378.012 | 27.564 | 6.001 | 3103.5282 | 3103.5282 | 1413979.5715 | 3103.5282
| CHM011-160677964 | 65 | CHM011 | CHM | North | 1531811.2025 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.046749 | 0.047033 | 0.047317 | 0.047601 | 0.047885 | 0.04763 | 0.047375 | 0.04712 | 0.046865 | 0.046611 | 0.046356 | 0.046101 | 0.045846 | 0.045591 | 0.045336 | 0.045081 | 0.044826 | 0.044571 | 0.044316 | 0.044062 | 0.00102 | 0.0010066 | 0.0010084 | 0.0010015 | 0.00099021 | 0.00097202 | 0.00096681 | 0.00096587 | 0.00094666 | 0.00094151 | 0.00093637 | 0.00093122 | 0.00092607 | 0.00092092 | 0.00091577 | 0.00091062 | 0.00090547 | 0.00090032 | 0.00089517 | 0.00089002 | 33888.7274 | 7378.012 | 468.193 | 101.9316 | 33164.1519 | 33164.1519 | 1531811.2025 | 33164.1519
| CHM011-160678238 | 83 | CHM011 | CHM | North | 1956005.0739 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.041363 | 0.041578 | 0.041793 | 0.042008 | 0.042223 | 0.041985 | 0.041747 | 0.041508 | 0.04127 | 0.041031 | 0.040793 | 0.040554 | 0.040316 | 0.040078 | 0.039839 | 0.039601 | 0.039362 | 0.039124 | 0.038885 | 0.038647 | 0.00090247 | 0.00088987 | 0.00089069 | 0.00088388 | 0.00087313 | 0.00085681 | 0.00085195 | 0.00085083 | 0.00083363 | 0.00082882 | 0.000824 | 0.00081918 | 0.00081437 | 0.00080955 | 0.00080473 | 0.00079992 | 0.0007951 | 0.00079029 | 0.00078547 | 0.00078065 | 33888.7274 | 7378.012 | 412.4029 | 89.7854 | 77086.1912 | 77086.1912 | 1956005.0739 | 77086.1912
| CHM011-160721783 | 32 | CHM011 | CHM | North | 754122.4381 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00023411 | 0.00023571 | 0.00023731 | 0.0002389 | 0.0002405 | 0.00023887 | 0.00023725 | 0.00023562 | 0.000234 | 0.00023237 | 0.00023075 | 0.00022912 | 0.0002275 | 0.00022587 | 0.00022425 | 0.00022263 | 0.000221 | 0.00021938 | 0.00021775 | 0.00021613 | 5.1079e-06 | 5.0447e-06 | 5.0574e-06 | 5.0266e-06 | 4.9733e-06 | 4.8749e-06 | 4.8417e-06 | 4.8298e-06 | 4.7267e-06 | 4.6939e-06 | 4.6611e-06 | 4.6282e-06 | 4.5954e-06 | 4.5626e-06 | 4.5298e-06 | 4.4969e-06 | 4.4641e-06 | 4.4313e-06 | 4.3985e-06 | 4.3656e-06 | 33888.7274 | 7378.012 | 2.3331 | 0.50795 | 193.9954 | 193.9954 | 754122.4381 | 193.9954
| CHM011-163177271 | 34 | CHM011 | CHM | North | 801255.0905 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.0064558 | 0.0065036 | 0.0065514 | 0.0065992 | 0.006647 | 0.0065942 | 0.0065415 | 0.0064887 | 0.0064359 | 0.0063831 | 0.0063303 | 0.0062776 | 0.0062248 | 0.006172 | 0.0061192 | 0.0060664 | 0.0060137 | 0.0059609 | 0.0059081 | 0.0058553 | 0.00014085 | 0.00013919 | 0.00013962 | 0.00013885 | 0.00013745 | 0.00013457 | 0.0001335 | 0.000133 | 0.00013 | 0.00012894 | 0.00012787 | 0.0001268 | 0.00012574 | 0.00012467 | 0.00012361 | 0.00012254 | 0.00012147 | 0.00012041 | 0.00011934 | 0.00011828 | 33888.7274 | 7378.012 | 64.0673 | 13.9483 | 7357.2877 | 7357.2877 | 801255.0905 | 7357.2877
| CHM011-163198394 | 40 | CHM011 | CHM | North | 942653.0477 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.018797 | 0.018897 | 0.018997 | 0.019097 | 0.019197 | 0.019061 | 0.018924 | 0.018788 | 0.018652 | 0.018516 | 0.018379 | 0.018243 | 0.018107 | 0.017971 | 0.017834 | 0.017698 | 0.017562 | 0.017426 | 0.017289 | 0.017153 | 0.00041011 | 0.00040443 | 0.00040486 | 0.00040181 | 0.00039697 | 0.00038898 | 0.0003862 | 0.00038512 | 0.00037676 | 0.00037401 | 0.00037126 | 0.0003685 | 0.00036575 | 0.000363 | 0.00036025 | 0.0003575 | 0.00035474 | 0.00035199 | 0.00034924 | 0.00034649 | 33888.7274 | 7378.012 | 186.0981 | 40.5159 | 14789.8367 | 14789.8367 | 942653.0477 | 14789.8367
| CHM011-163198509 | 189 | CHM011 | CHM | North | 4454035.6502 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.2988 | 0.30054 | 0.30228 | 0.30402 | 0.30576 | 0.30413 | 0.30249 | 0.30085 | 0.29922 | 0.29758 | 0.29594 | 0.2943 | 0.29267 | 0.29103 | 0.28939 | 0.28776 | 0.28612 | 0.28448 | 0.28285 | 0.28121 | 0.0065192 | 0.0064322 | 0.0064422 | 0.0063968 | 0.0063228 | 0.0062065 | 0.0061731 | 0.0061669 | 0.006044 | 0.006011 | 0.0059779 | 0.0059448 | 0.0059118 | 0.0058787 | 0.0058456 | 0.0058126 | 0.0057795 | 0.0057464 | 0.0057134 | 0.0056803 | 33888.7274 | 7378.012 | 2989.6282 | 650.8805 | 414962.6877 | 414962.6877 | 4454035.6502 | 414962.6877
| CHM011-163310655 | 42 | CHM011 | CHM | North | 989785.7001 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.14162 | 0.14252 | 0.14342 | 0.14432 | 0.14522 | 0.14426 | 0.1433 | 0.14235 | 0.14139 | 0.14044 | 0.13948 | 0.13853 | 0.13757 | 0.13661 | 0.13566 | 0.1347 | 0.13375 | 0.13279 | 0.13184 | 0.13088 | 0.0030899 | 0.0030502 | 0.0030565 | 0.0030365 | 0.0030029 | 0.002944 | 0.0029245 | 0.0029179 | 0.0028561 | 0.0028368 | 0.0028175 | 0.0027982 | 0.0027789 | 0.0027596 | 0.0027403 | 0.002721 | 0.0027017 | 0.0026823 | 0.002663 | 0.0026437 | 33888.7274 | 7378.012 | 1410.4934 | 307.0826 | 222342.5944 | 222342.5944 | 989785.7001 | 222342.5944
| CHM011-164238923 | 19 | CHM011 | CHM | North | 447760.1976 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00022194 | 0.00022346 | 0.00022497 | 0.00022649 | 0.000228 | 0.00022615 | 0.0002243 | 0.00022245 | 0.0002206 | 0.00021875 | 0.0002169 | 0.00021505 | 0.0002132 | 0.00021135 | 0.0002095 | 0.00020765 | 0.0002058 | 0.00020395 | 0.0002021 | 0.00020025 | 4.8424e-06 | 4.7825e-06 | 4.7945e-06 | 4.7654e-06 | 4.7148e-06 | 4.6152e-06 | 4.5774e-06 | 4.5598e-06 | 4.456e-06 | 4.4187e-06 | 4.3813e-06 | 4.3439e-06 | 4.3066e-06 | 4.2692e-06 | 4.2318e-06 | 4.1944e-06 | 4.1571e-06 | 4.1197e-06 | 4.0823e-06 | 4.045e-06 | 33888.7274 | 7378.012 | 2.1965 | 0.4782 | 140.9511 | 140.9511 | 447760.1976 | 140.9511
| CHM011-164366730 | 19 | CHM011 | CHM | North | 447760.1976 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.0084031 | 0.008452 | 0.0085008 | 0.0085497 | 0.0085986 | 0.0085467 | 0.0084949 | 0.008443 | 0.0083912 | 0.0083393 | 0.0082875 | 0.0082356 | 0.0081837 | 0.0081319 | 0.00808 | 0.0080282 | 0.0079763 | 0.0079245 | 0.0078726 | 0.0078208 | 0.00018334 | 0.00018089 | 0.00018117 | 0.00017989 | 0.00017781 | 0.00017442 | 0.00017336 | 0.00017306 | 0.0001695 | 0.00016845 | 0.0001674 | 0.00016636 | 0.00016531 | 0.00016426 | 0.00016321 | 0.00016217 | 0.00016112 | 0.00016007 | 0.00015902 | 0.00015798 | 33888.7274 | 7378.012 | 83.7843 | 18.2409 | 10754.9095 | 10754.9095 | 447760.1976 | 10754.9095
| CHM011-187119686 | 372 | CHM011 | CHM | North | 8766673.3433 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 21.0675 | 21.1724 | 21.2772 | 21.3821 | 21.487 | 21.3851 | 21.2832 | 21.1814 | 21.0795 | 20.9776 | 20.8758 | 20.7739 | 20.672 | 20.5701 | 20.4683 | 20.3664 | 20.2645 | 20.1627 | 20.0608 | 19.9589 | 0.45965 | 0.45313 | 0.45346 | 0.44989 | 0.44433 | 0.43642 | 0.43434 | 0.43418 | 0.4258 | 0.42374 | 0.42168 | 0.41962 | 0.41757 | 0.41551 | 0.41345 | 0.41139 | 0.40934 | 0.40728 | 0.40522 | 0.40316 | 33888.7274 | 7378.012 | 210866.6647 | 45908.3862 | 1985838.0298 | 1985838.0298 | 8766673.3433 | 1985838.0298
| CHM011-24600428 | 357 | CHM011 | CHM | North | 8413178.4505 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 1.5518 | 1.5595 | 1.5673 | 1.575 | 1.5827 | 1.5744 | 1.5661 | 1.5578 | 1.5495 | 1.5411 | 1.5328 | 1.5245 | 1.5162 | 1.5079 | 1.4996 | 1.4913 | 1.483 | 1.4746 | 1.4663 | 1.458 | 0.033857 | 0.033377 | 0.033401 | 0.033138 | 0.032729 | 0.03213 | 0.03196 | 0.031931 | 0.031298 | 0.031131 | 0.030963 | 0.030795 | 0.030627 | 0.030459 | 0.030291 | 0.030123 | 0.029955 | 0.029787 | 0.029619 | 0.029451 | 33888.7274 | 7378.012 | 15491.958 | 3372.7986 | 1043098.6963 | 1043098.6963 | 8413178.4505 | 1043098.6963
| CHM011-24600540 | 754 | CHM011 | CHM | North | 17769009.9486 | 0.0007837 | 0.00076876 | 0.00076551 | 0.00075576 | 0.00074277 | 0.00073303 | 0.00073303 | 0.00073628 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 0.00072556 | 4.2593 | 4.2838 | 4.3083 | 4.3327 | 4.3572 | 4.3332 | 4.3091 | 4.2851 | 4.261 | 4.2369 | 4.2129 | 4.1888 | 4.1648 | 4.1407 | 4.1166 | 4.0926 | 4.0685 | 4.0444 | 4.0204 | 3.9963 | 0.092929 | 0.091682 | 0.091817 | 0.091163 | 0.090103 | 0.08843 | 0.087939 | 0.087835 | 0.08607 | 0.085584 | 0.085098 | 0.084612 | 0.084126 | 0.08364 | 0.083154 | 0.082668 | 0.082182 | 0.081696 | 0.08121 | 0.080724 | 33888.7274 | 7378.012 | 42568.9593 | 9267.8102 | 2200878.0634 | 2200878.0634 | 17769009.9486 | 2200878.0634
| CLC001-15400682 | 169 | CLC001 | CLC | South | 3072553.7012 | 0.0026139 | 0.0025917 | 0.0025618 | 0.0025305 | 0.0025041 | 0.0025033 | 0.0025059 | 0.0025083 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.97255 | 0.97398 | 0.97542 | 0.97686 | 0.97829 | 0.97645 | 0.97461 | 0.97277 | 0.97093 | 0.96909 | 0.96725 | 0.96541 | 0.96357 | 0.96174 | 0.9599 | 0.95806 | 0.95622 | 0.95438 | 0.95254 | 0.9507 | 0.070773 | 0.070276 | 0.069568 | 0.068818 | 0.068202 | 0.06805 | 0.067994 | 0.067929 | 0.067617 | 0.067489 | 0.067361 | 0.067233 | 0.067104 | 0.066976 | 0.066848 | 0.06672 | 0.066592 | 0.066464 | 0.066336 | 0.066208 | 33280.5878 | 5114.8533 | 32704.4116 | 5026.3015 | 25449.223 | 32987.8214 | 3206486.2012 | 26558.5537
| CLC001-15400693 | 0 | CLC001 | CLC | South | 0 | 0.0026139 | 0.0025917 | 0.0025618 | 0.0025305 | 0.0025041 | 0.0025033 | 0.0025059 | 0.0025083 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0.0025015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33280.5878 | 5114.8533 | 0 | 0 | 0 | 0 | 0 | 0
| CLC002-15400645 | 392 | CLC002 | CLC | South | 7126870.1235 | 0.00094001 | 0.00094335 | 0.00095204 | 0.00095922 | 0.00097092 | 0.00099265 | 0.0010165 | 0.0010378 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 7.0767 | 7.0845 | 7.0923 | 7.1001 | 7.1079 | 7.0955 | 7.0831 | 7.0706 | 7.0582 | 7.0458 | 7.0333 | 7.0209 | 7.0085 | 6.996 | 6.9836 | 6.9711 | 6.9587 | 6.9463 | 6.9338 | 6.9214 | 0.18519 | 0.18606 | 0.18798 | 0.18961 | 0.19213 | 0.19609 | 0.20046 | 0.20428 | 0.20524 | 0.20487 | 0.20451 | 0.20415 | 0.20379 | 0.20343 | 0.20307 | 0.2027 | 0.20234 | 0.20198 | 0.20162 | 0.20126 | 33280.5878 | 5114.8533 | 95275.3641 | 14642.7554 | 242476.105 | 314302.6584 | 7437530.1235 | 253045.6293
| CLC003-119149948 | 26 | CLC003 | CLC | South | 472700.5694 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0046904 | 0.0047501 | 0.0048097 | 0.0048693 | 0.0049289 | 0.0048507 | 0.0047724 | 0.0046941 | 0.0046159 | 0.0045376 | 0.0044593 | 0.004381 | 0.0043028 | 0.0042245 | 0.0041462 | 0.004068 | 0.0039897 | 0.0039114 | 0.0038331 | 0.0037549 | 0.00015635 | 0.00015964 | 0.00016287 | 0.0001652 | 0.00016666 | 0.00016445 | 0.00016382 | 0.00016291 | 0.00015938 | 0.00015668 | 0.00015398 | 0.00015128 | 0.00014857 | 0.00014587 | 0.00014317 | 0.00014047 | 0.00013776 | 0.00013506 | 0.00013236 | 0.00012965 | 33280.5878 | 5114.8533 | 74.0197 | 11.376 | 878.1017 | 1138.214 | 493305.5694 | 916.3781
| CLC003-123633044 | 23 | CLC003 | CLC | South | 418158.196 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.013955 | 0.014072 | 0.014189 | 0.014307 | 0.014424 | 0.014256 | 0.014089 | 0.013921 | 0.013754 | 0.013587 | 0.013419 | 0.013252 | 0.013084 | 0.012917 | 0.012749 | 0.012582 | 0.012414 | 0.012247 | 0.01208 | 0.011912 | 0.00046518 | 0.00047294 | 0.00048048 | 0.00048538 | 0.0004877 | 0.00048332 | 0.00048361 | 0.00048313 | 0.00047492 | 0.00046914 | 0.00046336 | 0.00045758 | 0.00045179 | 0.00044601 | 0.00044023 | 0.00043445 | 0.00042867 | 0.00042289 | 0.00041711 | 0.00041132 | 33280.5878 | 5114.8533 | 222.3548 | 34.1734 | 5832.6971 | 7560.4654 | 436385.696 | 6086.9441
| CLC003-130014430 | 11 | CLC003 | CLC | South | 199988.7024 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0001463 | 0.00014842 | 0.00015055 | 0.00015267 | 0.0001548 | 0.00015294 | 0.00015108 | 0.00014922 | 0.00014736 | 0.0001455 | 0.00014364 | 0.00014178 | 0.00013992 | 0.00013806 | 0.0001362 | 0.00013434 | 0.00013248 | 0.00013062 | 0.00012876 | 0.0001269 | 4.8767e-06 | 4.9882e-06 | 5.0979e-06 | 5.1798e-06 | 5.2342e-06 | 5.185e-06 | 5.1859e-06 | 5.1785e-06 | 5.0883e-06 | 5.0241e-06 | 4.9599e-06 | 4.8956e-06 | 4.8314e-06 | 4.7672e-06 | 4.703e-06 | 4.6387e-06 | 4.5745e-06 | 4.5103e-06 | 4.4461e-06 | 4.3818e-06 | 33280.5878 | 5114.8533 | 2.3719 | 0.36454 | 104.1432 | 134.9926 | 208706.2024 | 108.6828
| CLC003-130014725 | 19 | CLC003 | CLC | South | 345435.0315 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012008 | 0.0012236 | 0.0012464 | 0.0012692 | 0.001292 | 0.0012627 | 0.0012335 | 0.0012042 | 0.001175 | 0.0011457 | 0.0011164 | 0.0010872 | 0.0010579 | 0.0010287 | 0.0009994 | 0.00097014 | 0.00094088 | 0.00091162 | 0.00088236 | 0.0008531 | 4.0028e-05 | 4.1123e-05 | 4.2206e-05 | 4.306e-05 | 4.3686e-05 | 4.281e-05 | 4.234e-05 | 4.1791e-05 | 4.0571e-05 | 3.9561e-05 | 3.855e-05 | 3.754e-05 | 3.653e-05 | 3.5519e-05 | 3.4509e-05 | 3.3499e-05 | 3.2488e-05 | 3.1478e-05 | 3.0468e-05 | 2.9457e-05 | 33280.5878 | 5114.8533 | 18.5968 | 2.8581 | 297.066 | 385.0633 | 360492.5315 | 310.0151
| CLC003-130014949 | 14 | CLC003 | CLC | South | 254531.0758 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0037333 | 0.0037837 | 0.0038341 | 0.0038845 | 0.0039349 | 0.00389 | 0.0038452 | 0.0038003 | 0.0037555 | 0.0037106 | 0.0036658 | 0.0036209 | 0.0035761 | 0.0035312 | 0.0034864 | 0.0034415 | 0.0033967 | 0.0033518 | 0.0033069 | 0.0032621 | 0.00012445 | 0.00012716 | 0.00012983 | 0.00013179 | 0.00013305 | 0.00013188 | 0.00013199 | 0.00013189 | 0.00012968 | 0.00012813 | 0.00012658 | 0.00012503 | 0.00012348 | 0.00012193 | 0.00012038 | 0.00011883 | 0.00011729 | 0.00011574 | 0.00011419 | 0.00011264 | 33280.5878 | 5114.8533 | 60.5331 | 9.3033 | 4510.1527 | 5846.1554 | 265626.0758 | 4706.7501
| CLC003-130747301 | 18 | CLC003 | CLC | South | 327254.2404 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0058191 | 0.0059032 | 0.0059872 | 0.0060712 | 0.0061553 | 0.0060805 | 0.0060058 | 0.005931 | 0.0058562 | 0.0057815 | 0.0057067 | 0.005632 | 0.0055572 | 0.0054824 | 0.0054077 | 0.0053329 | 0.0052582 | 0.0051834 | 0.0051086 | 0.0050339 | 0.00019398 | 0.00019839 | 0.00020274 | 0.00020598 | 0.00020813 | 0.00020614 | 0.00020615 | 0.00020583 | 0.00020221 | 0.00019963 | 0.00019705 | 0.00019447 | 0.00019189 | 0.00018931 | 0.00018673 | 0.00018414 | 0.00018156 | 0.00017898 | 0.0001764 | 0.00017382 | 33280.5878 | 5114.8533 | 94.2521 | 14.4855 | 1128.6396 | 1462.9665 | 341519.2404 | 1177.8369
| CLC003-130748256 | 30 | CLC003 | CLC | South | 545423.7339 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0062733 | 0.0063381 | 0.0064028 | 0.0064676 | 0.0065323 | 0.0064514 | 0.0063704 | 0.0062895 | 0.0062086 | 0.0061276 | 0.0060467 | 0.0059657 | 0.0058848 | 0.0058039 | 0.0057229 | 0.005642 | 0.0055611 | 0.0054801 | 0.0053992 | 0.0053183 | 0.00020912 | 0.00021301 | 0.00021681 | 0.00021942 | 0.00022087 | 0.00021871 | 0.00021867 | 0.00021827 | 0.00021438 | 0.00021159 | 0.00020879 | 0.000206 | 0.0002032 | 0.00020041 | 0.00019761 | 0.00019482 | 0.00019202 | 0.00018923 | 0.00018643 | 0.00018364 | 33280.5878 | 5114.8533 | 100.1516 | 15.3922 | 3198.2854 | 4145.6852 | 569198.7339 | 3337.6985
| CLC003-152030196 | 29 | CLC003 | CLC | South | 527242.9428 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.024238 | 0.024304 | 0.024371 | 0.024437 | 0.024504 | 0.024361 | 0.024219 | 0.024076 | 0.023934 | 0.023791 | 0.023648 | 0.023506 | 0.023363 | 0.02322 | 0.023078 | 0.022935 | 0.022792 | 0.02265 | 0.022507 | 0.022365 | 0.00080794 | 0.00081682 | 0.00082525 | 0.00082909 | 0.00082854 | 0.00082591 | 0.00083132 | 0.00083554 | 0.00082642 | 0.0008215 | 0.00081657 | 0.00081164 | 0.00080672 | 0.00080179 | 0.00079687 | 0.00079194 | 0.00078702 | 0.00078209 | 0.00077717 | 0.00077224 | 33280.5878 | 5114.8533 | 390.9929 | 60.0912 | 11313.1013 | 14664.2813 | 550225.4428 | 11806.2389
| CLC003-15400758 | 425 | CLC003 | CLC | South | 7726836.2309 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 31.1319 | 31.3438 | 31.5558 | 31.7677 | 31.9797 | 31.7309 | 31.4822 | 31.2335 | 30.9848 | 30.7361 | 30.4873 | 30.2386 | 29.9899 | 29.7412 | 29.4925 | 29.2437 | 28.995 | 28.7463 | 28.4976 | 28.2489 | 1.0378 | 1.0534 | 1.0686 | 1.0778 | 1.0813 | 1.0757 | 1.0806 | 1.0839 | 1.0699 | 1.0613 | 1.0527 | 1.0441 | 1.0355 | 1.027 | 1.0184 | 1.0098 | 1.0012 | 0.9926 | 0.98401 | 0.97543 | 33280.5878 | 5114.8533 | 503726.6519 | 77417.1397 | 1313497.1126 | 1702582.7525 | 8063648.7309 | 1370752.4022
| CLC003-154876479 | 13 | CLC003 | CLC | South | 236350.2847 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0019078 | 0.0019209 | 0.001934 | 0.001947 | 0.0019601 | 0.0019544 | 0.0019487 | 0.001943 | 0.0019372 | 0.0019315 | 0.0019258 | 0.0019201 | 0.0019143 | 0.0019086 | 0.0019029 | 0.0018972 | 0.0018914 | 0.0018857 | 0.00188 | 0.0018743 | 6.3594e-05 | 6.4557e-05 | 6.5488e-05 | 6.6057e-05 | 6.6277e-05 | 6.6259e-05 | 6.689e-05 | 6.7429e-05 | 6.6892e-05 | 6.6695e-05 | 6.6497e-05 | 6.6299e-05 | 6.6102e-05 | 6.5904e-05 | 6.5706e-05 | 6.5509e-05 | 6.5311e-05 | 6.5113e-05 | 6.4916e-05 | 6.4718e-05 | 33280.5878 | 5114.8533 | 31.6683 | 4.8671 | 1095.1473 | 1419.5531 | 246652.7847 | 1142.8847
| CLC003-154908324 | 95 | CLC003 | CLC | South | 1727175.1575 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.070032 | 0.070206 | 0.070381 | 0.070555 | 0.070729 | 0.070354 | 0.069978 | 0.069603 | 0.069227 | 0.068851 | 0.068476 | 0.0681 | 0.067725 | 0.067349 | 0.066973 | 0.066598 | 0.066222 | 0.065847 | 0.065471 | 0.065095 | 0.0023345 | 0.0023595 | 0.0023833 | 0.0023937 | 0.0023915 | 0.0023851 | 0.002402 | 0.0024155 | 0.0023904 | 0.0023774 | 0.0023645 | 0.0023515 | 0.0023385 | 0.0023255 | 0.0023126 | 0.0022996 | 0.0022866 | 0.0022737 | 0.0022607 | 0.0022477 | 33280.5878 | 5114.8533 | 1131.7761 | 173.9413 | 31206.6744 | 40450.7517 | 1802462.6575 | 32566.9721
| CLC003-154908634 | 13 | CLC003 | CLC | South | 236350.2847 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.00052533 | 0.00053019 | 0.00053506 | 0.00053993 | 0.0005448 | 0.00054344 | 0.00054208 | 0.00054072 | 0.00053936 | 0.000538 | 0.00053664 | 0.00053528 | 0.00053392 | 0.00053256 | 0.0005312 | 0.00052984 | 0.00052848 | 0.00052712 | 0.00052576 | 0.0005244 | 1.7511e-05 | 1.7819e-05 | 1.8118e-05 | 1.8318e-05 | 1.8421e-05 | 1.8424e-05 | 1.8607e-05 | 1.8765e-05 | 1.8624e-05 | 1.8577e-05 | 1.853e-05 | 1.8483e-05 | 1.8436e-05 | 1.8389e-05 | 1.8342e-05 | 1.8295e-05 | 1.8248e-05 | 1.8201e-05 | 1.8154e-05 | 1.8107e-05 | 33280.5878 | 5114.8533 | 8.8081 | 1.3537 | 228.4393 | 296.1079 | 246652.7847 | 238.397
| CLC003-154908755 | 10 | CLC003 | CLC | South | 181807.9113 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.00023512 | 0.00023794 | 0.00024076 | 0.00024358 | 0.0002464 | 0.00024318 | 0.00023996 | 0.00023674 | 0.00023352 | 0.0002303 | 0.00022708 | 0.00022386 | 0.00022064 | 0.00021742 | 0.0002142 | 0.00021098 | 0.00020776 | 0.00020454 | 0.00020132 | 0.0001981 | 7.8376e-06 | 7.9967e-06 | 8.1527e-06 | 8.2639e-06 | 8.3314e-06 | 8.2443e-06 | 8.2368e-06 | 8.2159e-06 | 8.0634e-06 | 7.9522e-06 | 7.841e-06 | 7.7298e-06 | 7.6186e-06 | 7.5075e-06 | 7.3963e-06 | 7.2851e-06 | 7.1739e-06 | 7.0627e-06 | 6.9515e-06 | 6.8403e-06 | 33280.5878 | 5114.8533 | 3.7598 | 0.57784 | 85.7631 | 111.168 | 189732.9113 | 89.5015
| CLC003-154908853 | 16 | CLC003 | CLC | South | 290892.6581 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0016691 | 0.0016838 | 0.0016985 | 0.0017131 | 0.0017278 | 0.0017183 | 0.0017088 | 0.0016993 | 0.0016898 | 0.0016802 | 0.0016707 | 0.0016612 | 0.0016517 | 0.0016422 | 0.0016327 | 0.0016232 | 0.0016137 | 0.0016042 | 0.0015947 | 0.0015851 | 5.5639e-05 | 5.6589e-05 | 5.7514e-05 | 5.8121e-05 | 5.8421e-05 | 5.8253e-05 | 5.8655e-05 | 5.8971e-05 | 5.8347e-05 | 5.8018e-05 | 5.769e-05 | 5.7362e-05 | 5.7033e-05 | 5.6705e-05 | 5.6377e-05 | 5.6048e-05 | 5.572e-05 | 5.5392e-05 | 5.5063e-05 | 5.4735e-05 | 33280.5878 | 5114.8533 | 27.5089 | 4.2278 | 439.1054 | 569.1777 | 303572.6581 | 458.246
| CLC003-154908977 | 32 | CLC003 | CLC | South | 581785.3162 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.042845 | 0.043207 | 0.043569 | 0.04393 | 0.044292 | 0.043994 | 0.043696 | 0.043399 | 0.043101 | 0.042803 | 0.042505 | 0.042208 | 0.04191 | 0.041612 | 0.041314 | 0.041017 | 0.040719 | 0.040421 | 0.040123 | 0.039826 | 0.0014282 | 0.0014521 | 0.0014753 | 0.0014904 | 0.0014976 | 0.0014915 | 0.0014999 | 0.0015061 | 0.0014883 | 0.001478 | 0.0014677 | 0.0014574 | 0.0014471 | 0.0014369 | 0.0014266 | 0.0014163 | 0.001406 | 0.0013957 | 0.0013854 | 0.0013752 | 33280.5878 | 5114.8533 | 700.8378 | 107.7109 | 17047.8879 | 22097.8331 | 607145.3162 | 17791.0047
| CLC003-193886326 | 141 | CLC003 | CLC | South | 2563491.5495 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.41101 | 0.41531 | 0.41961 | 0.42391 | 0.4282 | 0.42262 | 0.41703 | 0.41144 | 0.40585 | 0.40026 | 0.39467 | 0.38908 | 0.38349 | 0.3779 | 0.37231 | 0.36672 | 0.36113 | 0.35555 | 0.34996 | 0.34437 | 0.013701 | 0.013958 | 0.014209 | 0.014382 | 0.014479 | 0.014328 | 0.014315 | 0.014279 | 0.014014 | 0.013821 | 0.013628 | 0.013435 | 0.013242 | 0.013049 | 0.012856 | 0.012663 | 0.01247 | 0.012277 | 0.012084 | 0.011891 | 33280.5878 | 5114.8533 | 6540.8763 | 1005.2594 | 139583.9982 | 180931.7322 | 2675234.0495 | 145668.4594
| CLC003-198593463 | 79 | CLC003 | CLC | South | 1436282.4994 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.23982 | 0.24171 | 0.24359 | 0.24548 | 0.24736 | 0.24392 | 0.24048 | 0.23705 | 0.23361 | 0.23017 | 0.22673 | 0.2233 | 0.21986 | 0.21642 | 0.21298 | 0.20955 | 0.20611 | 0.20267 | 0.19923 | 0.19579 | 0.0079943 | 0.0081233 | 0.0082485 | 0.0083283 | 0.0083639 | 0.0082695 | 0.0082548 | 0.0082265 | 0.0080665 | 0.0079478 | 0.0078291 | 0.0077104 | 0.0075917 | 0.007473 | 0.0073543 | 0.0072356 | 0.0071168 | 0.0069981 | 0.0068794 | 0.0067607 | 33280.5878 | 5114.8533 | 3767.3725 | 579.0029 | 36090.7621 | 46781.6096 | 1498889.9994 | 37663.9571
| CLC003-24597492 | 148 | CLC003 | CLC | South | 2690757.0875 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 3.746 | 3.7814 | 3.8168 | 3.8522 | 3.8875 | 3.8348 | 3.7821 | 3.7293 | 3.6766 | 3.6238 | 3.5711 | 3.5183 | 3.4656 | 3.4129 | 3.3601 | 3.3074 | 3.2546 | 3.2019 | 3.1491 | 3.0964 | 0.12487 | 0.12709 | 0.12924 | 0.13069 | 0.13145 | 0.13001 | 0.12982 | 0.12942 | 0.12695 | 0.12513 | 0.12331 | 0.12149 | 0.11967 | 0.11785 | 0.11602 | 0.1142 | 0.11238 | 0.11056 | 0.10874 | 0.10692 | 33280.5878 | 5114.8533 | 59254.4641 | 9106.7469 | 152016.2599 | 197046.6929 | 2808047.0875 | 158642.6429
| CLC003-24597520 | 118 | CLC003 | CLC | South | 2145333.3535 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.86668 | 0.87281 | 0.87895 | 0.88509 | 0.89123 | 0.87961 | 0.868 | 0.85638 | 0.84477 | 0.83315 | 0.82154 | 0.80992 | 0.79831 | 0.78669 | 0.77508 | 0.76347 | 0.75185 | 0.74024 | 0.72862 | 0.71701 | 0.02889 | 0.029334 | 0.029763 | 0.030028 | 0.030135 | 0.029821 | 0.029794 | 0.02972 | 0.02917 | 0.028769 | 0.028368 | 0.027966 | 0.027565 | 0.027164 | 0.026763 | 0.026362 | 0.025961 | 0.02556 | 0.025159 | 0.024758 | 33280.5878 | 5114.8533 | 13644.9264 | 2097.0722 | 68564.2288 | 88874.4043 | 2238848.3535 | 71552.941
| CLC003-24597576 | 141 | CLC003 | CLC | South | 2563491.5495 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 1.2633 | 1.277 | 1.2906 | 1.3043 | 1.318 | 1.2974 | 1.2769 | 1.2564 | 1.2359 | 1.2154 | 1.1948 | 1.1743 | 1.1538 | 1.1333 | 1.1128 | 1.0922 | 1.0717 | 1.0512 | 1.0307 | 1.0101 | 0.042111 | 0.042916 | 0.043704 | 0.044251 | 0.044564 | 0.043986 | 0.043831 | 0.043602 | 0.042675 | 0.041966 | 0.041257 | 0.040549 | 0.03984 | 0.039132 | 0.038423 | 0.037714 | 0.037006 | 0.036297 | 0.035589 | 0.03488 | 33280.5878 | 5114.8533 | 19850.5589 | 3050.8084 | 110288.9446 | 142958.8639 | 2675234.0495 | 115096.4356
| CLC003-24607110 | 150 | CLC003 | CLC | South | 2727118.6697 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 3.6858 | 3.6954 | 3.705 | 3.7146 | 3.7243 | 3.7036 | 3.6828 | 3.6621 | 3.6414 | 3.6206 | 3.5999 | 3.5792 | 3.5584 | 3.5377 | 3.517 | 3.4963 | 3.4755 | 3.4548 | 3.4341 | 3.4133 | 0.12286 | 0.1242 | 0.12546 | 0.12603 | 0.12593 | 0.12556 | 0.12641 | 0.12709 | 0.12574 | 0.12502 | 0.1243 | 0.12359 | 0.12287 | 0.12216 | 0.12144 | 0.12073 | 0.12001 | 0.11929 | 0.11858 | 0.11786 | 33280.5878 | 5114.8533 | 59509.9403 | 9146.0107 | 248689.0291 | 322355.982 | 2845993.6697 | 259529.3745
| CLC003-24607264 | 556 | CLC003 | CLC | South | 10108519.8691 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 1.5684 | 1.5847 | 1.601 | 1.6173 | 1.6336 | 1.6142 | 1.5947 | 1.5753 | 1.5559 | 1.5365 | 1.517 | 1.4976 | 1.4782 | 1.4587 | 1.4393 | 1.4199 | 1.4004 | 1.381 | 1.3616 | 1.3421 | 0.052283 | 0.05326 | 0.054214 | 0.054871 | 0.055236 | 0.054724 | 0.054741 | 0.05467 | 0.053724 | 0.053053 | 0.052383 | 0.051712 | 0.051041 | 0.05037 | 0.049699 | 0.049028 | 0.048357 | 0.047686 | 0.047015 | 0.046344 | 33280.5878 | 5114.8533 | 25112.5725 | 3859.5209 | 634205.6562 | 822070.7921 | 10549149.8691 | 661850.6568
| CLC003-24613704 | 138 | CLC003 | CLC | South | 2508949.1761 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.2442 | 0.24633 | 0.24846 | 0.2506 | 0.25273 | 0.24979 | 0.24685 | 0.24391 | 0.24098 | 0.23804 | 0.2351 | 0.23216 | 0.22922 | 0.22629 | 0.22335 | 0.22041 | 0.21747 | 0.21453 | 0.21159 | 0.20866 | 0.0081401 | 0.0082787 | 0.0084135 | 0.008502 | 0.0085454 | 0.0084685 | 0.0084734 | 0.0084648 | 0.0083209 | 0.0082194 | 0.008118 | 0.0080165 | 0.007915 | 0.0078136 | 0.0077121 | 0.0076107 | 0.0075092 | 0.0074078 | 0.0073063 | 0.0072049 | 33280.5878 | 5114.8533 | 3894.8425 | 598.5936 | 85820.4229 | 111242.2482 | 2618314.1761 | 89561.3319
| CLC003-78545961 | 3 | CLC003 | CLC | South | 54542.3734 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33280.5878 | 5114.8533 | 0 | 0 | 0 | 0 | 56919.8734 | 0
| CLC003-80120806 | 10 | CLC003 | CLC | South | 181807.9113 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0088237 | 0.0089036 | 0.0089835 | 0.0090633 | 0.0091432 | 0.0090697 | 0.0089962 | 0.0089227 | 0.0088492 | 0.0087757 | 0.0087022 | 0.0086287 | 0.0085552 | 0.0084817 | 0.0084082 | 0.0083347 | 0.0082612 | 0.0081877 | 0.0081142 | 0.0080407 | 0.00029413 | 0.00029923 | 0.0003042 | 0.00030749 | 0.00030915 | 0.00030748 | 0.0003088 | 0.00030965 | 0.00030556 | 0.00030302 | 0.00030049 | 0.00029795 | 0.00029541 | 0.00029287 | 0.00029033 | 0.0002878 | 0.00028526 | 0.00028272 | 0.00028018 | 0.00027764 | 33280.5878 | 5114.8533 | 143.615 | 22.072 | 3821.1513 | 4953.0572 | 189732.9113 | 3987.7151
| CLC003-80121007 | 12 | CLC003 | CLC | South | 218169.4936 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.00031174 | 0.00031518 | 0.00031862 | 0.00032206 | 0.0003255 | 0.00032287 | 0.00032025 | 0.00031762 | 0.000315 | 0.00031237 | 0.00030975 | 0.00030712 | 0.0003045 | 0.00030187 | 0.00029925 | 0.00029662 | 0.000294 | 0.00029137 | 0.00028875 | 0.00028612 | 1.0392e-05 | 1.0593e-05 | 1.0789e-05 | 1.0927e-05 | 1.1006e-05 | 1.0946e-05 | 1.0993e-05 | 1.1023e-05 | 1.0877e-05 | 1.0786e-05 | 1.0696e-05 | 1.0605e-05 | 1.0514e-05 | 1.0424e-05 | 1.0333e-05 | 1.0242e-05 | 1.0152e-05 | 1.0061e-05 | 9.9705e-06 | 9.8798e-06 | 33280.5878 | 5114.8533 | 5.1057 | 0.78469 | 139.7247 | 181.1142 | 227679.4936 | 145.8153
| CLC003-80919181 | 70 | CLC003 | CLC | South | 1272655.3792 | 0.0011974 | 0.0012072 | 0.0012163 | 0.0012186 | 0.0012145 | 0.0012177 | 0.001233 | 0.0012466 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.0012403 | 0.27795 | 0.28076 | 0.28357 | 0.28638 | 0.28919 | 0.28642 | 0.28365 | 0.28087 | 0.2781 | 0.27533 | 0.27255 | 0.26978 | 0.26701 | 0.26423 | 0.26146 | 0.25869 | 0.25591 | 0.25314 | 0.25037 | 0.2476 | 0.0092651 | 0.0094358 | 0.0096023 | 0.009716 | 0.0097783 | 0.0097102 | 0.0097363 | 0.0097474 | 0.0096027 | 0.0095069 | 0.0094112 | 0.0093154 | 0.0092197 | 0.0091239 | 0.0090282 | 0.0089324 | 0.0088367 | 0.0087409 | 0.0086452 | 0.0085494 | 33280.5878 | 5114.8533 | 4501.9796 | 691.9038 | 75092.8558 | 97336.9487 | 1328130.3792 | 78366.1505
| CLC004-15400582 | 528 | CLC004 | CLC | South | 9599457.7174 | 0.0021126 | 0.0021618 | 0.0021593 | 0.002154 | 0.0021425 | 0.0021454 | 0.0021583 | 0.0021679 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 16.3219 | 16.4455 | 16.5691 | 16.6927 | 16.8164 | 16.7428 | 16.6693 | 16.5958 | 16.5223 | 16.4488 | 16.3753 | 16.3018 | 16.2283 | 16.1548 | 16.0813 | 16.0078 | 15.9343 | 15.8608 | 15.7873 | 15.7138 | 0.95996 | 0.98976 | 0.99606 | 1.001 | 1.0031 | 1 | 1.0016 | 1.0016 | 0.99249 | 0.98808 | 0.98366 | 0.97925 | 0.97483 | 0.97042 | 0.966 | 0.96159 | 0.95717 | 0.95276 | 0.94834 | 0.94392 | 33280.5878 | 5114.8533 | 472201.0609 | 72572.0097 | 1049412.0174 | 1360270.0638 | 10017897.7174 | 1095155.8477
| CLC004-176886107 | 21 | CLC004 | CLC | South | 381796.6138 | 0.0021126 | 0.0021618 | 0.0021593 | 0.002154 | 0.0021425 | 0.0021454 | 0.0021583 | 0.0021679 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0010129 | 0.0010229 | 0.0010329 | 0.001043 | 0.001053 | 0.0010504 | 0.0010479 | 0.0010453 | 0.0010427 | 0.0010402 | 0.0010376 | 0.001035 | 0.0010325 | 0.0010299 | 0.0010274 | 0.0010248 | 0.0010222 | 0.0010197 | 0.0010171 | 0.0010145 | 5.9572e-05 | 6.1563e-05 | 6.2096e-05 | 6.2544e-05 | 6.2809e-05 | 6.274e-05 | 6.2963e-05 | 6.309e-05 | 6.2637e-05 | 6.2483e-05 | 6.2329e-05 | 6.2175e-05 | 6.2021e-05 | 6.1867e-05 | 6.1713e-05 | 6.1559e-05 | 6.1405e-05 | 6.125e-05 | 6.1096e-05 | 6.0942e-05 | 33280.5878 | 5114.8533 | 29.8208 | 4.5831 | 211.3138 | 273.9094 | 398439.1138 | 220.5249
| CLC004-201015049 | 368 | CLC004 | CLC | South | 6690531.1364 | 0.0021126 | 0.0021618 | 0.0021593 | 0.002154 | 0.0021425 | 0.0021454 | 0.0021583 | 0.0021679 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 1.2637 | 1.2744 | 1.2851 | 1.2959 | 1.3066 | 1.2993 | 1.292 | 1.2847 | 1.2774 | 1.2702 | 1.2629 | 1.2556 | 1.2483 | 1.241 | 1.2337 | 1.2264 | 1.2191 | 1.2118 | 1.2045 | 1.1972 | 0.074321 | 0.076699 | 0.077257 | 0.07771 | 0.077936 | 0.077605 | 0.077634 | 0.077541 | 0.076736 | 0.076298 | 0.07586 | 0.075422 | 0.074984 | 0.074546 | 0.074108 | 0.07367 | 0.073231 | 0.072793 | 0.072355 | 0.071917 | 33280.5878 | 5114.8533 | 36438.6993 | 5600.2196 | 538560.378 | 698093.3585 | 6982171.1364 | 562036.2045
| CLC004-24597506 | 654 | CLC004 | CLC | South | 11890237.4 | 0.0021126 | 0.0021618 | 0.0021593 | 0.002154 | 0.0021425 | 0.0021454 | 0.0021583 | 0.0021679 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 0.0021577 | 3.7056 | 3.7296 | 3.7537 | 3.7778 | 3.8019 | 3.784 | 3.766 | 3.7481 | 3.7302 | 3.7123 | 3.6944 | 3.6765 | 3.6586 | 3.6406 | 3.6227 | 3.6048 | 3.5869 | 3.569 | 3.5511 | 3.5331 | 0.21794 | 0.22446 | 0.22566 | 0.22654 | 0.22677 | 0.22601 | 0.22629 | 0.22622 | 0.22407 | 0.223 | 0.22192 | 0.22084 | 0.21977 | 0.21869 | 0.21762 | 0.21654 | 0.21546 | 0.21439 | 0.21331 | 0.21224 | 33280.5878 | 5114.8533 | 106640.7535 | 16389.4884 | 1176726.4104 | 1525297.6742 | 12408532.4 | 1228019.8703
| CLC006-142438034 | 76 | CLC006 | CLC | South | 1381740.126 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0028372 | 0.002873 | 0.0029087 | 0.0029445 | 0.0029803 | 0.0029803 | 0.0029803 | 0.0029803 | 0.0029803 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029802 | 0.0029801 | 0.0029801 | 0.00028709 | 0.00028982 | 0.00029043 | 0.00029159 | 0.00029139 | 0.0002884 | 0.00028755 | 0.00028657 | 0.00028479 | 0.00028479 | 0.00028479 | 0.00028478 | 0.00028478 | 0.00028478 | 0.00028478 | 0.00028478 | 0.00028478 | 0.00028478 | 0.00028478 | 0.00028478 | 33280.5878 | 5114.8533 | 138.0539 | 21.2173 | 3281.7292 | 4253.8469 | 1441970.126 | 3424.7797
| CLC006-142438492 | 21 | CLC006 | CLC | South | 381796.6138 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.030719 | 0.030892 | 0.031065 | 0.031238 | 0.031411 | 0.031367 | 0.031323 | 0.031279 | 0.031235 | 0.031191 | 0.031147 | 0.031103 | 0.031059 | 0.031015 | 0.030971 | 0.030927 | 0.030884 | 0.03084 | 0.030796 | 0.030752 | 0.0031085 | 0.0031164 | 0.0031017 | 0.0030934 | 0.0030711 | 0.0030353 | 0.0030221 | 0.0030076 | 0.0029848 | 0.0029806 | 0.0029764 | 0.0029722 | 0.002968 | 0.0029638 | 0.0029596 | 0.0029554 | 0.0029512 | 0.002947 | 0.0029428 | 0.0029386 | 33280.5878 | 5114.8533 | 1451.3892 | 223.0622 | 10091.4296 | 13080.7245 | 398439.1138 | 10531.3146
| CLC006-144337956 | 80 | CLC006 | CLC | South | 1454463.2905 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.068388 | 0.068967 | 0.069545 | 0.070123 | 0.070702 | 0.070356 | 0.07001 | 0.069664 | 0.069319 | 0.068973 | 0.068627 | 0.068281 | 0.067935 | 0.067589 | 0.067243 | 0.066898 | 0.066552 | 0.066206 | 0.06586 | 0.065514 | 0.0069202 | 0.0069573 | 0.0069438 | 0.0069442 | 0.0069128 | 0.0068082 | 0.0067548 | 0.0066985 | 0.006624 | 0.0065909 | 0.0065579 | 0.0065248 | 0.0064918 | 0.0064587 | 0.0064257 | 0.0063926 | 0.0063596 | 0.0063265 | 0.0062935 | 0.0062604 | 33280.5878 | 5114.8533 | 3203.8162 | 492.3906 | 51512.2065 | 66771.2122 | 1517863.2905 | 53757.6217
| CLC006-144337978 | 42 | CLC006 | CLC | South | 763593.2275 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.017387 | 0.017526 | 0.017665 | 0.017804 | 0.017944 | 0.017914 | 0.017885 | 0.017855 | 0.017826 | 0.017797 | 0.017767 | 0.017738 | 0.017709 | 0.017679 | 0.01765 | 0.01762 | 0.017591 | 0.017562 | 0.017532 | 0.017503 | 0.0017594 | 0.001768 | 0.0017638 | 0.0017631 | 0.0017544 | 0.0017335 | 0.0017256 | 0.0017169 | 0.0017034 | 0.0017006 | 0.0016978 | 0.001695 | 0.0016922 | 0.0016894 | 0.0016866 | 0.0016838 | 0.001681 | 0.0016782 | 0.0016753 | 0.0016725 | 33280.5878 | 5114.8533 | 826.8409 | 127.0762 | 16289.3806 | 21114.6398 | 796878.2275 | 16999.4341
| CLC006-15400532 | 507 | CLC006 | CLC | South | 9217661.1037 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 11.4739 | 11.5145 | 11.5551 | 11.5958 | 11.6364 | 11.6037 | 11.5711 | 11.5384 | 11.5057 | 11.4731 | 11.4404 | 11.4078 | 11.3751 | 11.3425 | 11.3098 | 11.2771 | 11.2445 | 11.2118 | 11.1792 | 11.1465 | 1.161 | 1.1616 | 1.1537 | 1.1483 | 1.1377 | 1.1229 | 1.1164 | 1.1095 | 1.0995 | 1.0963 | 1.0932 | 1.0901 | 1.087 | 1.0839 | 1.0807 | 1.0776 | 1.0745 | 1.0714 | 1.0683 | 1.0651 | 33280.5878 | 5114.8533 | 534639.3165 | 82168.0697 | 1121928.5451 | 1454267.5215 | 9619458.6037 | 1170833.3681
| CLC006-154827505 | 25 | CLC006 | CLC | South | 454519.7783 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.00034365 | 0.00034803 | 0.00035242 | 0.00035681 | 0.0003612 | 0.00036102 | 0.00036084 | 0.00036066 | 0.00036048 | 0.0003603 | 0.00036012 | 0.00035994 | 0.00035976 | 0.00035958 | 0.0003594 | 0.00035922 | 0.00035904 | 0.00035886 | 0.00035868 | 0.0003585 | 3.4774e-05 | 3.5109e-05 | 3.5188e-05 | 3.5334e-05 | 3.5316e-05 | 3.4935e-05 | 3.4815e-05 | 3.4679e-05 | 3.4447e-05 | 3.443e-05 | 3.4412e-05 | 3.4395e-05 | 3.4378e-05 | 3.4361e-05 | 3.4344e-05 | 3.4326e-05 | 3.4309e-05 | 3.4292e-05 | 3.4275e-05 | 3.4258e-05 | 33280.5878 | 5114.8533 | 16.6886 | 2.5649 | 195.7393 | 253.7214 | 474332.2783 | 204.2716
| CLC006-154827674 | 21 | CLC006 | CLC | South | 381796.6138 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.022834 | 0.023058 | 0.023281 | 0.023505 | 0.023728 | 0.023591 | 0.023454 | 0.023317 | 0.02318 | 0.023043 | 0.022906 | 0.022769 | 0.022632 | 0.022495 | 0.022359 | 0.022222 | 0.022085 | 0.021948 | 0.021811 | 0.021674 | 0.0023106 | 0.002326 | 0.0023245 | 0.0023276 | 0.00232 | 0.0022829 | 0.002263 | 0.0022421 | 0.0022151 | 0.002202 | 0.0021889 | 0.0021758 | 0.0021627 | 0.0021496 | 0.0021365 | 0.0021235 | 0.0021104 | 0.0020973 | 0.0020842 | 0.0020711 | 33280.5878 | 5114.8533 | 1069.4653 | 164.3648 | 6018.1181 | 7800.812 | 398439.1138 | 6280.4476
| CLC006-154827847 | 14 | CLC006 | CLC | South | 254531.0758 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0050121 | 0.0050126 | 0.0050132 | 0.0050137 | 0.0050142 | 0.005013 | 0.0050119 | 0.0050107 | 0.0050095 | 0.0050083 | 0.0050071 | 0.0050059 | 0.0050047 | 0.0050035 | 0.0050023 | 0.0050011 | 0.005 | 0.0049988 | 0.0049976 | 0.0049964 | 0.00050718 | 0.00050567 | 0.00050055 | 0.0004965 | 0.00049026 | 0.0004851 | 0.00048356 | 0.0004818 | 0.0004787 | 0.00047858 | 0.00047847 | 0.00047835 | 0.00047824 | 0.00047813 | 0.00047801 | 0.0004779 | 0.00047779 | 0.00047767 | 0.00047756 | 0.00047745 | 33280.5878 | 5114.8533 | 233.8985 | 35.9476 | 3686.0807 | 4777.9758 | 265626.0758 | 3846.7568
| CLC006-154828072 | 127 | CLC006 | CLC | South | 2308960.4737 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.037031 | 0.037367 | 0.037703 | 0.038039 | 0.038375 | 0.038218 | 0.038062 | 0.037906 | 0.037749 | 0.037593 | 0.037437 | 0.03728 | 0.037124 | 0.036968 | 0.036811 | 0.036655 | 0.036499 | 0.036343 | 0.036186 | 0.03603 | 0.0037472 | 0.0037696 | 0.0037645 | 0.0037669 | 0.003752 | 0.0036983 | 0.0036723 | 0.0036448 | 0.0036073 | 0.0035923 | 0.0035774 | 0.0035624 | 0.0035475 | 0.0035326 | 0.0035176 | 0.0035027 | 0.0034878 | 0.0034728 | 0.0034579 | 0.003443 | 33280.5878 | 5114.8533 | 1745.4832 | 268.2612 | 35644.763 | 46203.4961 | 2409607.9737 | 37198.5169
| CLC006-154828287 | 65 | CLC006 | CLC | South | 1181751.4235 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.028491 | 0.028849 | 0.029207 | 0.029564 | 0.029922 | 0.029802 | 0.029683 | 0.029563 | 0.029443 | 0.029324 | 0.029204 | 0.029084 | 0.028965 | 0.028845 | 0.028725 | 0.028606 | 0.028486 | 0.028366 | 0.028246 | 0.028127 | 0.002883 | 0.0029102 | 0.0029162 | 0.0029277 | 0.0029256 | 0.0028839 | 0.0028639 | 0.0028426 | 0.0028136 | 0.0028021 | 0.0027907 | 0.0027792 | 0.0027678 | 0.0027564 | 0.0027449 | 0.0027335 | 0.0027221 | 0.0027106 | 0.0026992 | 0.0026877 | 33280.5878 | 5114.8533 | 1358.4737 | 208.7822 | 23666.1028 | 30676.5033 | 1233263.9235 | 24697.7074
| CLC006-154828396 | 119 | CLC006 | CLC | South | 2163514.1446 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.098675 | 0.099885 | 0.1011 | 0.10231 | 0.10352 | 0.10311 | 0.10271 | 0.10231 | 0.10191 | 0.10151 | 0.10111 | 0.10071 | 0.10031 | 0.099908 | 0.099508 | 0.099107 | 0.098706 | 0.098305 | 0.097905 | 0.097504 | 0.009985 | 0.010076 | 0.010094 | 0.010131 | 0.010121 | 0.0099782 | 0.0099102 | 0.0098378 | 0.0097385 | 0.0097002 | 0.0096619 | 0.0096237 | 0.0095854 | 0.0095471 | 0.0095088 | 0.0094705 | 0.0094322 | 0.0093939 | 0.0093556 | 0.0093173 | 33280.5878 | 5114.8533 | 4703.577 | 722.8871 | 98448.2693 | 127610.7299 | 2257821.6446 | 102739.6256
| CLC006-154907356 | 24 | CLC006 | CLC | South | 436338.9872 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0081171 | 0.0082026 | 0.0082881 | 0.0083736 | 0.008459 | 0.0084374 | 0.0084158 | 0.0083942 | 0.0083725 | 0.0083509 | 0.0083293 | 0.0083077 | 0.008286 | 0.0082644 | 0.0082428 | 0.0082212 | 0.0081996 | 0.0081779 | 0.0081563 | 0.0081347 | 0.00082138 | 0.00082747 | 0.00082754 | 0.00082922 | 0.00082707 | 0.00081647 | 0.00081198 | 0.00080713 | 0.00080006 | 0.000798 | 0.00079593 | 0.00079387 | 0.0007918 | 0.00078973 | 0.00078767 | 0.0007856 | 0.00078354 | 0.00078147 | 0.0007794 | 0.00077734 | 33280.5878 | 5114.8533 | 387.3634 | 59.5334 | 5232.862 | 6782.9465 | 455358.9872 | 5460.9623
| CLC006-156831394 | 640 | CLC006 | CLC | South | 11635706.3241 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 4.1972 | 4.2411 | 4.2849 | 4.3288 | 4.3726 | 4.3622 | 4.3519 | 4.3415 | 4.3311 | 4.3208 | 4.3104 | 4.3 | 4.2897 | 4.2793 | 4.2689 | 4.2586 | 4.2482 | 4.2378 | 4.2275 | 4.2171 | 0.42472 | 0.42783 | 0.42783 | 0.42867 | 0.42752 | 0.42213 | 0.41988 | 0.41745 | 0.41387 | 0.41288 | 0.41189 | 0.4109 | 0.40991 | 0.40892 | 0.40793 | 0.40694 | 0.40595 | 0.40496 | 0.40397 | 0.40298 | 33280.5878 | 5114.8533 | 200431.7181 | 30804.1083 | 1412661.481 | 1831121.7053 | 12142906.3241 | 1474239.3417
| CLC006-44811375 | 504 | CLC006 | CLC | South | 9163118.7303 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 1.4763 | 1.4909 | 1.5055 | 1.52 | 1.5346 | 1.5306 | 1.5266 | 1.5226 | 1.5186 | 1.5146 | 1.5106 | 1.5065 | 1.5025 | 1.4985 | 1.4945 | 1.4905 | 1.4865 | 1.4825 | 1.4785 | 1.4745 | 0.14939 | 0.1504 | 0.15032 | 0.15053 | 0.15004 | 0.14811 | 0.14729 | 0.1464 | 0.14511 | 0.14473 | 0.14435 | 0.14396 | 0.14358 | 0.1432 | 0.14281 | 0.14243 | 0.14205 | 0.14167 | 0.14128 | 0.1409 | 33280.5878 | 5114.8533 | 70284.1035 | 10801.8788 | 675875.5076 | 876084.1353 | 9562538.7303 | 705336.8955
| CLC006-80819775 | 110 | CLC006 | CLC | South | 1999887.0245 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.17815 | 0.18015 | 0.18216 | 0.18416 | 0.18617 | 0.18551 | 0.18485 | 0.18419 | 0.18352 | 0.18286 | 0.1822 | 0.18154 | 0.18088 | 0.18022 | 0.17955 | 0.17889 | 0.17823 | 0.17757 | 0.17691 | 0.17624 | 0.018027 | 0.018174 | 0.018188 | 0.018237 | 0.018203 | 0.017951 | 0.017835 | 0.01771 | 0.017537 | 0.017474 | 0.017411 | 0.017347 | 0.017284 | 0.017221 | 0.017158 | 0.017095 | 0.017031 | 0.016968 | 0.016905 | 0.016842 | 33280.5878 | 5114.8533 | 8478.371 | 1303.0306 | 90502.5237 | 117311.2864 | 2087062.0245 | 94447.5253
| CLC006-80819849 | 105 | CLC006 | CLC | South | 1908983.0688 | 0.0036347 | 0.0036235 | 0.0035864 | 0.003557 | 0.003512 | 0.0034759 | 0.0034656 | 0.0034538 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.0034324 | 0.04054 | 0.041086 | 0.041633 | 0.042179 | 0.042725 | 0.042555 | 0.042385 | 0.042215 | 0.042045 | 0.041874 | 0.041704 | 0.041534 | 0.041364 | 0.041194 | 0.041024 | 0.040854 | 0.040684 | 0.040513 | 0.040343 | 0.040173 | 0.0041023 | 0.0041447 | 0.0041569 | 0.0041769 | 0.0041774 | 0.004118 | 0.0040894 | 0.0040591 | 0.0040177 | 0.0040014 | 0.0039852 | 0.0039689 | 0.0039527 | 0.0039364 | 0.0039202 | 0.0039039 | 0.0038877 | 0.0038714 | 0.0038551 | 0.0038389 | 33280.5878 | 5114.8533 | 1938.7841 | 297.9694 | 23870.886 | 30941.9475 | 1992195.5688 | 24911.417
| CLC013-120141536 | 54 | CLC013 | CLC | South | 981762.7211 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.066737 | 0.067457 | 0.068176 | 0.068896 | 0.069616 | 0.068892 | 0.068168 | 0.067445 | 0.066721 | 0.065997 | 0.065273 | 0.064549 | 0.063826 | 0.063102 | 0.062378 | 0.061654 | 0.060931 | 0.060207 | 0.059483 | 0.058759 | 0.002257 | 0.0022996 | 0.0023506 | 0.0023856 | 0.0024074 | 0.0023985 | 0.002405 | 0.0024056 | 0.0023677 | 0.002342 | 0.0023164 | 0.0022907 | 0.002265 | 0.0022393 | 0.0022136 | 0.0021879 | 0.0021623 | 0.0021366 | 0.0021109 | 0.0020852 | 33280.5878 | 5114.8533 | 1105.0439 | 169.8329 | 29996.8525 | 38882.555 | 1024557.7211 | 31304.4142
| CLC013-155048935 | 17 | CLC013 | CLC | South | 309073.4492 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.00095362 | 0.0009613 | 0.00096899 | 0.00097667 | 0.00098435 | 0.00098184 | 0.00097933 | 0.00097683 | 0.00097432 | 0.00097181 | 0.00096931 | 0.0009668 | 0.00096429 | 0.00096179 | 0.00095928 | 0.00095677 | 0.00095426 | 0.00095176 | 0.00094925 | 0.00094674 | 3.2251e-05 | 3.2771e-05 | 3.3408e-05 | 3.3819e-05 | 3.404e-05 | 3.4184e-05 | 3.4551e-05 | 3.4841e-05 | 3.4576e-05 | 3.4487e-05 | 3.4398e-05 | 3.4309e-05 | 3.422e-05 | 3.4131e-05 | 3.4042e-05 | 3.3953e-05 | 3.3864e-05 | 3.3775e-05 | 3.3686e-05 | 3.3597e-05 | 33280.5878 | 5114.8533 | 16.3145 | 2.5074 | 480.0126 | 622.2025 | 322545.9492 | 500.9363
| CLC013-155049125 | 36 | CLC013 | CLC | South | 654508.4807 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.1077 | 0.10837 | 0.10904 | 0.10972 | 0.11039 | 0.10993 | 0.10947 | 0.10901 | 0.10855 | 0.10809 | 0.10762 | 0.10716 | 0.1067 | 0.10624 | 0.10578 | 0.10532 | 0.10486 | 0.1044 | 0.10394 | 0.10348 | 0.0036423 | 0.0036944 | 0.0037596 | 0.0037991 | 0.0038174 | 0.0038273 | 0.003862 | 0.003888 | 0.003852 | 0.0038356 | 0.0038193 | 0.0038029 | 0.0037866 | 0.0037702 | 0.0037539 | 0.0037375 | 0.0037211 | 0.0037048 | 0.0036884 | 0.0036721 | 33280.5878 | 5114.8533 | 1816.2064 | 279.1306 | 42440.9938 | 55012.9143 | 683038.4807 | 44290.9951
| CLC013-155049446 | 31 | CLC013 | CLC | South | 563604.5251 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.033904 | 0.034267 | 0.03463 | 0.034992 | 0.035355 | 0.0351 | 0.034845 | 0.034589 | 0.034334 | 0.034079 | 0.033824 | 0.033569 | 0.033313 | 0.033058 | 0.032803 | 0.032548 | 0.032292 | 0.032037 | 0.031782 | 0.031527 | 0.0011466 | 0.0011682 | 0.001194 | 0.0012117 | 0.0012226 | 0.001222 | 0.0012293 | 0.0012337 | 0.0012184 | 0.0012094 | 0.0012003 | 0.0011913 | 0.0011822 | 0.0011731 | 0.0011641 | 0.001155 | 0.001146 | 0.0011369 | 0.0011279 | 0.0011188 | 33280.5878 | 5114.8533 | 570.8718 | 87.7366 | 18381.7106 | 23826.7623 | 588172.0251 | 19182.9687
| CLC013-155049582 | 25 | CLC013 | CLC | South | 454519.7783 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.012793 | 0.013011 | 0.013229 | 0.013447 | 0.013665 | 0.013364 | 0.013063 | 0.012761 | 0.01246 | 0.012159 | 0.011858 | 0.011556 | 0.011255 | 0.010954 | 0.010653 | 0.010352 | 0.01005 | 0.0097491 | 0.0094479 | 0.0091467 | 0.00043266 | 0.00044355 | 0.00045611 | 0.00046562 | 0.00047256 | 0.00046527 | 0.00046085 | 0.00045517 | 0.00044218 | 0.00043149 | 0.0004208 | 0.00041011 | 0.00039942 | 0.00038873 | 0.00037804 | 0.00036735 | 0.00035666 | 0.00034597 | 0.00033528 | 0.00032459 | 33280.5878 | 5114.8533 | 202.437 | 31.1123 | 3156.8584 | 4091.9867 | 474332.2783 | 3294.4658
| CLC013-155079387 | 16 | CLC013 | CLC | South | 290892.6581 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0031291 | 0.0031653 | 0.0032015 | 0.0032376 | 0.0032738 | 0.0032281 | 0.0031823 | 0.0031366 | 0.0030909 | 0.0030452 | 0.0029995 | 0.0029538 | 0.0029081 | 0.0028624 | 0.0028167 | 0.0027709 | 0.0027252 | 0.0026795 | 0.0026338 | 0.0025881 | 0.00010583 | 0.00010791 | 0.00011038 | 0.00011211 | 0.00011321 | 0.00011239 | 0.00011227 | 0.00011188 | 0.00010969 | 0.00010807 | 0.00010644 | 0.00010482 | 0.0001032 | 0.00010158 | 9.9955e-05 | 9.8333e-05 | 9.6711e-05 | 9.5089e-05 | 9.3467e-05 | 9.1845e-05 | 33280.5878 | 5114.8533 | 50.94 | 7.8289 | 1814.8523 | 2352.45 | 303572.6581 | 1893.9616
| CLC013-155079659 | 23 | CLC013 | CLC | South | 418158.196 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.029883 | 0.030177 | 0.030471 | 0.030765 | 0.031058 | 0.030875 | 0.030691 | 0.030508 | 0.030324 | 0.030141 | 0.029957 | 0.029774 | 0.02959 | 0.029406 | 0.029223 | 0.029039 | 0.028856 | 0.028672 | 0.028489 | 0.028305 | 0.0010107 | 0.0010287 | 0.0010506 | 0.0010653 | 0.001074 | 0.0010749 | 0.0010828 | 0.0010881 | 0.0010761 | 0.0010696 | 0.0010631 | 0.0010566 | 0.0010501 | 0.0010436 | 0.001037 | 0.0010305 | 0.001024 | 0.0010175 | 0.001011 | 0.0010045 | 33280.5878 | 5114.8533 | 505.248 | 77.651 | 18104.2493 | 23467.111 | 436385.696 | 18893.4128
| CLC013-161744857 | 350 | CLC013 | CLC | South | 6363276.896 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 35.7129 | 35.9291 | 36.1453 | 36.3615 | 36.5777 | 36.3942 | 36.2107 | 36.0273 | 35.8438 | 35.6603 | 35.4768 | 35.2933 | 35.1098 | 34.9263 | 34.7429 | 34.5594 | 34.3759 | 34.1924 | 34.0089 | 33.8254 | 1.2078 | 1.2248 | 1.2462 | 1.2591 | 1.2649 | 1.2671 | 1.2775 | 1.285 | 1.272 | 1.2655 | 1.259 | 1.2525 | 1.246 | 1.2394 | 1.2329 | 1.2264 | 1.2199 | 1.2134 | 1.2069 | 1.2004 | 33280.5878 | 5114.8533 | 599236.6231 | 92095.9516 | 1199351.1419 | 1554624.3298 | 6640651.896 | 1251630.8129
| CLC013-24598538 | 68 | CLC013 | CLC | South | 1236293.7969 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.08382 | 0.08453 | 0.085239 | 0.085949 | 0.086658 | 0.086158 | 0.085658 | 0.085158 | 0.084657 | 0.084157 | 0.083657 | 0.083157 | 0.082657 | 0.082157 | 0.081657 | 0.081156 | 0.080656 | 0.080156 | 0.079656 | 0.079156 | 0.0028348 | 0.0028816 | 0.0029389 | 0.0029761 | 0.0029968 | 0.0029997 | 0.003022 | 0.0030374 | 0.0030043 | 0.0029865 | 0.0029688 | 0.002951 | 0.0029333 | 0.0029155 | 0.0028978 | 0.00288 | 0.0028623 | 0.0028445 | 0.0028268 | 0.002809 | 33280.5878 | 5114.8533 | 1411.9422 | 216.9997 | 28223.0956 | 36583.3738 | 1290183.7969 | 29453.3393
| CLC013-24598566 | 64 | CLC013 | CLC | South | 1163570.6324 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.17758 | 0.17869 | 0.17979 | 0.1809 | 0.182 | 0.18122 | 0.18043 | 0.17964 | 0.17885 | 0.17807 | 0.17728 | 0.17649 | 0.1757 | 0.17491 | 0.17413 | 0.17334 | 0.17255 | 0.17176 | 0.17097 | 0.17019 | 0.0060058 | 0.0060915 | 0.0061989 | 0.0062639 | 0.006294 | 0.0063092 | 0.0063655 | 0.0064073 | 0.006347 | 0.006319 | 0.0062911 | 0.0062631 | 0.0062352 | 0.0062072 | 0.0061792 | 0.0061513 | 0.0061233 | 0.0060954 | 0.0060674 | 0.0060394 | 33280.5878 | 5114.8533 | 2992.1062 | 459.8532 | 62151.1328 | 80561.6136 | 1214290.6324 | 64860.2984
| CLC013-24602770 | 220 | CLC013 | CLC | South | 3999774.0489 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 5.8443 | 5.9141 | 5.9839 | 6.0536 | 6.1234 | 6.0294 | 5.9355 | 5.8415 | 5.7475 | 5.6536 | 5.5596 | 5.4656 | 5.3716 | 5.2777 | 5.1837 | 5.0897 | 4.9958 | 4.9018 | 4.8078 | 4.7139 | 0.19765 | 0.20161 | 0.20631 | 0.20962 | 0.21176 | 0.20992 | 0.2094 | 0.20835 | 0.20396 | 0.20063 | 0.19729 | 0.19396 | 0.19062 | 0.18729 | 0.18396 | 0.18062 | 0.17729 | 0.17395 | 0.17062 | 0.16728 | 33280.5878 | 5114.8533 | 94531.0657 | 14528.3651 | 107934.6091 | 139907.1243 | 4174124.0489 | 112639.4746
| CLC013-24602784 | 227 | CLC013 | CLC | South | 4127039.5868 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 6.5474 | 6.6089 | 6.6704 | 6.7319 | 6.7933 | 6.7053 | 6.6172 | 6.5292 | 6.4411 | 6.353 | 6.265 | 6.1769 | 6.0889 | 6.0008 | 5.9127 | 5.8247 | 5.7366 | 5.6486 | 5.5605 | 5.4725 | 0.22143 | 0.2253 | 0.22998 | 0.2331 | 0.23492 | 0.23345 | 0.23345 | 0.23288 | 0.22858 | 0.22545 | 0.22233 | 0.2192 | 0.21608 | 0.21295 | 0.20983 | 0.2067 | 0.20358 | 0.20045 | 0.19733 | 0.1942 | 33280.5878 | 5114.8533 | 106433.4363 | 16357.6261 | 596791.33 | 773573.5507 | 4306937.0868 | 622805.4416
| CLC013-40996443 | 233 | CLC013 | CLC | South | 4236124.3336 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 14.4298 | 14.4617 | 14.4936 | 14.5255 | 14.5574 | 14.489 | 14.4206 | 14.3523 | 14.2839 | 14.2156 | 14.1472 | 14.0788 | 14.0105 | 13.9421 | 13.8738 | 13.8054 | 13.737 | 13.6687 | 13.6003 | 13.5319 | 0.48801 | 0.493 | 0.49971 | 0.50297 | 0.50341 | 0.50445 | 0.50876 | 0.51191 | 0.5069 | 0.50447 | 0.50204 | 0.49962 | 0.49719 | 0.49477 | 0.49234 | 0.48991 | 0.48749 | 0.48506 | 0.48264 | 0.48021 | 33280.5878 | 5114.8533 | 239470.8212 | 36803.9808 | 238308.4806 | 308900.4954 | 4420776.8336 | 248696.3383
| CLC013-77737876 | 21 | CLC013 | CLC | South | 381796.6138 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0017487 | 0.0017571 | 0.0017655 | 0.0017738 | 0.0017822 | 0.0017764 | 0.0017706 | 0.0017647 | 0.0017589 | 0.0017531 | 0.0017472 | 0.0017414 | 0.0017356 | 0.0017298 | 0.0017239 | 0.0017181 | 0.0017123 | 0.0017065 | 0.0017006 | 0.0016948 | 5.9141e-05 | 5.9899e-05 | 6.0869e-05 | 6.1422e-05 | 6.1632e-05 | 6.1846e-05 | 6.2465e-05 | 6.2944e-05 | 6.2419e-05 | 6.2212e-05 | 6.2005e-05 | 6.1798e-05 | 6.1591e-05 | 6.1385e-05 | 6.1178e-05 | 6.0971e-05 | 6.0764e-05 | 6.0557e-05 | 6.0351e-05 | 6.0144e-05 | 33280.5878 | 5114.8533 | 29.4874 | 4.5319 | 689.0387 | 893.1466 | 398439.1138 | 719.0739
| CLC013-77738225 | 12 | CLC013 | CLC | South | 218169.4936 | 0.0012148 | 0.0012245 | 0.0012384 | 0.0012438 | 0.0012421 | 0.0012506 | 0.0012672 | 0.0012812 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0012747 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 0.0001395 | 4.7179e-06 | 4.7556e-06 | 4.8097e-06 | 4.8304e-06 | 4.8241e-06 | 4.8568e-06 | 4.9215e-06 | 4.9756e-06 | 4.9505e-06 | 4.9505e-06 | 4.9505e-06 | 4.9505e-06 | 4.9505e-06 | 4.9505e-06 | 4.9505e-06 | 4.9505e-06 | 4.9505e-06 | 4.9505e-06 | 4.9505e-06 | 4.9505e-06 | 33280.5878 | 5114.8533 | 2.3543 | 0.36182 | 146.6847 | 190.1357 | 227679.4936 | 153.0786
| CLC014-119350337 | 56 | CLC014 | CLC | South | 1018124.3034 | 0.001878 | 0.001878 | 0.0018881 | 0.0018847 | 0.0018737 | 0.0018737 | 0.0018837 | 0.0018871 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33280.5878 | 5114.8533 | 0 | 0 | 0 | 0 | 1062504.3034 | 0
| CLC014-161744928 | 84 | CLC014 | CLC | South | 1527186.455 | 0.001878 | 0.001878 | 0.0018881 | 0.0018847 | 0.0018737 | 0.0018737 | 0.0018837 | 0.0018871 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 0.0018694 | 21.6312 | 21.8019 | 21.9726 | 22.1433 | 22.3139 | 22.1925 | 22.0711 | 21.9496 | 21.8282 | 21.7067 | 21.5853 | 21.4638 | 21.3424 | 21.221 | 21.0995 | 20.9781 | 20.8566 | 20.7352 | 20.6137 | 20.4923 | 1.131 | 1.1399 | 1.155 | 1.1619 | 1.164 | 1.1576 | 1.1575 | 1.1531 | 1.136 | 1.1297 | 1.1234 | 1.117 | 1.1107 | 1.1044 | 1.0981 | 1.0918 | 1.0854 | 1.0791 | 1.0728 | 1.0665 | 33280.5878 | 5114.8533 | 542361.4118 | 83354.8692 | 318491.3057 | 412835.1702 | 1593756.455 | 332374.3298
| CME014-15423823 | 0 | CME014 | CME | North | 0 | 0.0014149 | 0.0014222 | 0.0014401 | 0.0014495 | 0.0014563 | 0.0014725 | 0.0014966 | 0.0015177 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29027.5783 | 3468.8748 | 0 | 0 | 0 | 0 | 0 | 0
| CME014-15423849 | 204 | CME014 | CME | North | 4807530.5431 | 0.0014149 | 0.0014222 | 0.0014401 | 0.0014495 | 0.0014563 | 0.0014725 | 0.0014966 | 0.0015177 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 169.8191 | 170.6824 | 171.5457 | 172.4091 | 173.2724 | 174.0323 | 174.7921 | 175.552 | 176.3119 | 177.0717 | 177.8316 | 178.5914 | 179.3513 | 180.1112 | 180.871 | 181.6309 | 182.3908 | 183.1506 | 183.9105 | 184.6704 | 6.6894 | 6.758 | 6.8778 | 6.9576 | 7.025 | 7.1341 | 7.2826 | 7.4176 | 7.4696 | 7.5018 | 7.534 | 7.5662 | 7.5983 | 7.6305 | 7.6627 | 7.6949 | 7.7271 | 7.7593 | 7.7915 | 7.8237 | 29027.5783 | 3468.8748 | 3075136.8402 | 367487.2443 | 3307370.8837 | 3307370.8837 | 4807530.5431 | 3307370.8837
| CME014-24612269 | 41 | CME014 | CME | North | 966219.3739 | 0.0014149 | 0.0014222 | 0.0014401 | 0.0014495 | 0.0014563 | 0.0014725 | 0.0014966 | 0.0015177 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0.0015218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29027.5783 | 3468.8748 | 0 | 0 | 0 | 0 | 966219.3739 | 0
| CME015-15423773 | 229 | CME015 | CME | North | 5396688.6979 | 0.0031269 | 0.0031341 | 0.0031168 | 0.0030941 | 0.0030541 | 0.0030222 | 0.003017 | 0.003021 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 5.1516 | 5.1895 | 5.2275 | 5.2655 | 5.3034 | 5.3348 | 5.3661 | 5.3975 | 5.4289 | 5.4602 | 5.4916 | 5.523 | 5.5543 | 5.5857 | 5.6171 | 5.6484 | 5.6798 | 5.7112 | 5.7425 | 5.7739 | 0.44846 | 0.45281 | 0.45359 | 0.45357 | 0.45093 | 0.44886 | 0.45071 | 0.45396 | 0.45195 | 0.45456 | 0.45718 | 0.45979 | 0.4624 | 0.46501 | 0.46762 | 0.47023 | 0.47284 | 0.47545 | 0.47806 | 0.48068 | 29027.5783 | 3468.8748 | 192495.6258 | 23003.7526 | 416956.2259 | 416956.2259 | 5396688.6979 | 416956.2259
| CME015-182988165 | 113 | CME015 | CME | North | 2662994.8597 | 0.0031269 | 0.0031341 | 0.0031168 | 0.0030941 | 0.0030541 | 0.0030222 | 0.003017 | 0.003021 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 0.0029903 | 9.7716 | 9.8314 | 9.8913 | 9.9512 | 10.0111 | 10.0632 | 10.1153 | 10.1674 | 10.2195 | 10.2716 | 10.3237 | 10.3758 | 10.4279 | 10.48 | 10.5321 | 10.5843 | 10.6364 | 10.6885 | 10.7406 | 10.7927 | 0.85063 | 0.85784 | 0.85828 | 0.8572 | 0.85121 | 0.8467 | 0.84961 | 0.85513 | 0.85077 | 0.85511 | 0.85945 | 0.86379 | 0.86813 | 0.87246 | 0.8768 | 0.88114 | 0.88548 | 0.88982 | 0.89415 | 0.89849 | 29027.5783 | 3468.8748 | 362403.4246 | 43308.1982 | 419180.1085 | 419180.1085 | 2662994.8597 | 419180.1085
| CME016-142932211 | 1 | CME016 | CME | North | 23566.3262 | 0.0016877 | 0.0017174 | 0.001744 | 0.0017627 | 0.001767 | 0.0017774 | 0.0018065 | 0.0018412 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29027.5783 | 3468.8748 | 0 | 0 | 0 | 0 | 23566.3262 | 0
| CME016-142932557 | 49 | CME016 | CME | North | 1154749.9834 | 0.0016877 | 0.0017174 | 0.001744 | 0.0017627 | 0.001767 | 0.0017774 | 0.0018065 | 0.0018412 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.050781 | 0.051092 | 0.051403 | 0.051715 | 0.052026 | 0.052422 | 0.052819 | 0.053216 | 0.053612 | 0.054009 | 0.054406 | 0.054802 | 0.055199 | 0.055595 | 0.055992 | 0.056389 | 0.056785 | 0.057182 | 0.057578 | 0.057975 | 0.002386 | 0.0024428 | 0.0024958 | 0.0025378 | 0.0025593 | 0.002594 | 0.0026565 | 0.0027278 | 0.0027565 | 0.0027769 | 0.0027973 | 0.0028177 | 0.0028381 | 0.0028585 | 0.0028789 | 0.0028993 | 0.0029197 | 0.00294 | 0.0029604 | 0.0029808 | 29027.5783 | 3468.8748 | 1135.8677 | 135.7393 | 34557.4361 | 34557.4361 | 1154749.9834 | 34557.4361
| CME016-142932825 | 88 | CME016 | CME | North | 2073836.7049 | 0.0016877 | 0.0017174 | 0.001744 | 0.0017627 | 0.001767 | 0.0017774 | 0.0018065 | 0.0018412 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.03518 | 0.035414 | 0.035647 | 0.03588 | 0.036113 | 0.036299 | 0.036486 | 0.036672 | 0.036858 | 0.037044 | 0.03723 | 0.037416 | 0.037602 | 0.037788 | 0.037974 | 0.03816 | 0.038346 | 0.038532 | 0.038718 | 0.038904 | 0.001653 | 0.0016932 | 0.0017308 | 0.0017608 | 0.0017765 | 0.0017962 | 0.001835 | 0.0018798 | 0.0018951 | 0.0019046 | 0.0019142 | 0.0019238 | 0.0019333 | 0.0019429 | 0.0019525 | 0.001962 | 0.0019716 | 0.0019812 | 0.0019907 | 0.0020003 | 29027.5783 | 3468.8748 | 778.5653 | 93.0407 | 39510.8606 | 39510.8606 | 2073836.7049 | 39510.8606
| CME016-142933135 | 48 | CME016 | CME | North | 1131183.6572 | 0.0016877 | 0.0017174 | 0.001744 | 0.0017627 | 0.001767 | 0.0017774 | 0.0018065 | 0.0018412 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.085005 | 0.085505 | 0.086004 | 0.086504 | 0.087003 | 0.087807 | 0.08861 | 0.089414 | 0.090217 | 0.091021 | 0.091824 | 0.092628 | 0.093431 | 0.094235 | 0.095038 | 0.095842 | 0.096645 | 0.097449 | 0.098252 | 0.099056 | 0.003994 | 0.0040881 | 0.0041758 | 0.004245 | 0.0042799 | 0.004345 | 0.0044565 | 0.0045833 | 0.0046386 | 0.0046799 | 0.0047212 | 0.0047625 | 0.0048038 | 0.0048451 | 0.0048865 | 0.0049278 | 0.0049691 | 0.0050104 | 0.0050517 | 0.005093 | 29027.5783 | 3468.8748 | 1914.9773 | 228.845 | 42389.5954 | 42389.5954 | 1131183.6572 | 42389.5954
| CME016-154143626 | 121 | CME016 | CME | North | 2851525.4692 | 0.0016877 | 0.0017174 | 0.001744 | 0.0017627 | 0.001767 | 0.0017774 | 0.0018065 | 0.0018412 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 3.1758 | 3.1899 | 3.204 | 3.2181 | 3.2322 | 3.2675 | 3.3029 | 3.3383 | 3.3737 | 3.409 | 3.4444 | 3.4798 | 3.5151 | 3.5505 | 3.5859 | 3.6213 | 3.6566 | 3.692 | 3.7274 | 3.7627 | 0.14922 | 0.15251 | 0.15557 | 0.15792 | 0.159 | 0.16169 | 0.16612 | 0.17112 | 0.17346 | 0.17528 | 0.1771 | 0.17891 | 0.18073 | 0.18255 | 0.18437 | 0.18619 | 0.18801 | 0.18983 | 0.19165 | 0.19346 | 29027.5783 | 3468.8748 | 71798.1696 | 8580.0772 | 234614.2394 | 234614.2394 | 2851525.4692 | 234614.2394
| CME016-15423749 | 294 | CME016 | CME | North | 6928499.9004 | 0.0016877 | 0.0017174 | 0.001744 | 0.0017627 | 0.001767 | 0.0017774 | 0.0018065 | 0.0018412 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 122.858 | 123.4715 | 124.085 | 124.6985 | 125.312 | 125.8108 | 126.3095 | 126.8083 | 127.3071 | 127.8059 | 128.3046 | 128.8034 | 129.3022 | 129.801 | 130.2997 | 130.7985 | 131.2973 | 131.7961 | 132.2948 | 132.7936 | 5.7725 | 5.9033 | 6.0248 | 6.1194 | 6.1644 | 6.2256 | 6.3526 | 6.5002 | 6.5456 | 6.5712 | 6.5969 | 6.6225 | 6.6482 | 6.6738 | 6.6995 | 6.7251 | 6.7507 | 6.7764 | 6.802 | 6.8277 | 29027.5783 | 3468.8748 | 2688268.8156 | 321255.4596 | 4881418.116 | 4881418.116 | 6928499.9004 | 4881418.116
| CME016-163066872 | 79 | CME016 | CME | North | 1861739.7692 | 0.0016877 | 0.0017174 | 0.001744 | 0.0017627 | 0.001767 | 0.0017774 | 0.0018065 | 0.0018412 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0012425 | 0.0012535 | 0.0012645 | 0.0012754 | 0.0012864 | 0.001303 | 0.0013195 | 0.0013361 | 0.0013526 | 0.0013692 | 0.0013858 | 0.0014023 | 0.0014189 | 0.0014354 | 0.001452 | 0.0014686 | 0.0014851 | 0.0015017 | 0.0015182 | 0.0015348 | 5.838e-05 | 5.993e-05 | 6.1394e-05 | 6.2589e-05 | 6.3281e-05 | 6.4475e-05 | 6.6364e-05 | 6.8487e-05 | 6.9547e-05 | 7.0398e-05 | 7.125e-05 | 7.2101e-05 | 7.2953e-05 | 7.3804e-05 | 7.4656e-05 | 7.5507e-05 | 7.6358e-05 | 7.721e-05 | 7.8061e-05 | 7.8913e-05 | 29027.5783 | 3468.8748 | 28.7737 | 3.4385 | 764.024 | 764.024 | 1861739.7692 | 764.024
| CME016-171344649 | 0 | CME016 | CME | North | 0 | 0.0016877 | 0.0017174 | 0.001744 | 0.0017627 | 0.001767 | 0.0017774 | 0.0018065 | 0.0018412 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29027.5783 | 3468.8748 | 0 | 0 | 0 | 0 | 0 | 0
| CME016-24605950 | 49 | CME016 | CME | North | 1154749.9834 | 0.0016877 | 0.0017174 | 0.001744 | 0.0017627 | 0.001767 | 0.0017774 | 0.0018065 | 0.0018412 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.055418 | 0.055792 | 0.056167 | 0.056541 | 0.056915 | 0.057432 | 0.057949 | 0.058466 | 0.058982 | 0.059499 | 0.060016 | 0.060533 | 0.06105 | 0.061567 | 0.062084 | 0.062601 | 0.063118 | 0.063635 | 0.064151 | 0.064668 | 0.0026038 | 0.0026675 | 0.0027271 | 0.0027746 | 0.0027998 | 0.0028419 | 0.0029145 | 0.0029969 | 0.0030326 | 0.0030592 | 0.0030858 | 0.0031124 | 0.0031389 | 0.0031655 | 0.0031921 | 0.0032187 | 0.0032452 | 0.0032718 | 0.0032984 | 0.003325 | 29027.5783 | 3468.8748 | 1251.1536 | 149.5163 | 718.033 | 718.033 | 1154749.9834 | 718.033
| CME016-68675557 | 28 | CME016 | CME | North | 659857.1334 | 0.0016877 | 0.0017174 | 0.001744 | 0.0017627 | 0.001767 | 0.0017774 | 0.0018065 | 0.0018412 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.0018468 | 0.76698 | 0.77192 | 0.77686 | 0.78179 | 0.78673 | 0.79413 | 0.80153 | 0.80892 | 0.81632 | 0.82372 | 0.83112 | 0.83852 | 0.84592 | 0.85331 | 0.86071 | 0.86811 | 0.87551 | 0.88291 | 0.89031 | 0.8977 | 0.036037 | 0.036906 | 0.037719 | 0.038365 | 0.038701 | 0.039296 | 0.040312 | 0.041465 | 0.041972 | 0.042352 | 0.042733 | 0.043113 | 0.043493 | 0.043874 | 0.044254 | 0.044635 | 0.045015 | 0.045395 | 0.045776 | 0.046156 | 29027.5783 | 3468.8748 | 17325.0925 | 2070.3958 | 4696.596 | 4696.596 | 659857.1334 | 4696.596
| CME021-15423551 | 0 | CME021 | CME | North | 0 | 0.0018757 | 0.0018798 | 0.0018726 | 0.0018599 | 0.001836 | 0.0018169 | 0.0018105 | 0.0018105 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29027.5783 | 3468.8748 | 0 | 0 | 0 | 0 | 0 | 0
| CME021-15423564 | 76 | CME021 | CME | North | 1791040.7906 | 0.0018757 | 0.0018798 | 0.0018726 | 0.0018599 | 0.001836 | 0.0018169 | 0.0018105 | 0.0018105 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 9.8524 | 9.902 | 9.9517 | 10.0013 | 10.051 | 10.0771 | 10.1033 | 10.1294 | 10.1556 | 10.1817 | 10.2078 | 10.234 | 10.2601 | 10.2863 | 10.3124 | 10.3386 | 10.3647 | 10.3909 | 10.417 | 10.4432 | 0.51449 | 0.5182 | 0.51881 | 0.51788 | 0.51376 | 0.50973 | 0.50924 | 0.51056 | 0.50762 | 0.50892 | 0.51023 | 0.51154 | 0.51285 | 0.51415 | 0.51546 | 0.51677 | 0.51807 | 0.51938 | 0.52069 | 0.52199 | 29027.5783 | 3468.8748 | 215850.9932 | 25794.7827 | 143557.2855 | 143557.2855 | 1791040.7906 | 143557.2855
| CME021-184455628 | 55 | CME021 | CME | North | 1296147.9405 | 0.0018757 | 0.0018798 | 0.0018726 | 0.0018599 | 0.001836 | 0.0018169 | 0.0018105 | 0.0018105 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 0.0017954 | 7.6129 | 7.6623 | 7.7117 | 7.7611 | 7.8105 | 7.8573 | 7.9041 | 7.9509 | 7.9977 | 8.0446 | 8.0914 | 8.1382 | 8.185 | 8.2318 | 8.2786 | 8.3254 | 8.3722 | 8.4191 | 8.4659 | 8.5127 | 0.39754 | 0.40099 | 0.40204 | 0.40188 | 0.39924 | 0.39745 | 0.39839 | 0.40075 | 0.39976 | 0.4021 | 0.40444 | 0.40678 | 0.40912 | 0.41146 | 0.4138 | 0.41614 | 0.41848 | 0.42082 | 0.42316 | 0.4255 | 29027.5783 | 3468.8748 | 170372.6588 | 20359.9977 | 129015.3725 | 129015.3725 | 1296147.9405 | 129015.3725
| CME022-15423527 | 41 | CME022 | CME | North | 966219.3739 | 0.012464 | 0.012438 | 0.012236 | 0.012014 | 0.01179 | 0.011583 | 0.01142 | 0.01128 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.01114 | 0.058211 | 0.058679 | 0.059147 | 0.059616 | 0.060084 | 0.060667 | 0.061249 | 0.061832 | 0.062415 | 0.062997 | 0.06358 | 0.064162 | 0.064745 | 0.065328 | 0.06591 | 0.066493 | 0.067076 | 0.067658 | 0.068241 | 0.068824 | 0.020199 | 0.02032 | 0.020148 | 0.01994 | 0.019721 | 0.019563 | 0.019474 | 0.019418 | 0.019357 | 0.019538 | 0.019719 | 0.019899 | 0.02008 | 0.020261 | 0.020442 | 0.020622 | 0.020803 | 0.020984 | 0.021164 | 0.021345 | 29027.5783 | 3468.8748 | 8428.4945 | 1007.2281 | 1946.6388 | 1946.6388 | 966219.3739 | 1946.6388
| CMN001-124828418 | 431 | CMN001 | CMN | North | 10157086.5887 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 62.606 | 63.0895 | 63.573 | 64.0565 | 64.54 | 64.7141 | 64.8882 | 65.0624 | 65.2365 | 65.4107 | 65.5848 | 65.759 | 65.9331 | 66.1073 | 66.2814 | 66.4556 | 66.6297 | 66.8039 | 66.978 | 67.1522 | 0.71849 | 0.73987 | 0.76736 | 0.79231 | 0.81504 | 0.84016 | 0.86831 | 0.89242 | 0.90755 | 0.90997 | 0.91239 | 0.91481 | 0.91724 | 0.91966 | 0.92208 | 0.92451 | 0.92693 | 0.92935 | 0.93177 | 0.9342 | 32853.392 | 6411.4371 | 409364.5508 | 79888.7086 | 9184778.1172 | 9184778.1172 | 10157086.5887 | 9184778.1172
| CMN001-132430534 | 123 | CMN001 | CMN | North | 2898658.1216 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 24.8324 | 24.9976 | 25.1629 | 25.3281 | 25.4934 | 25.5564 | 25.6194 | 25.6825 | 25.7455 | 25.8085 | 25.8715 | 25.9345 | 25.9976 | 26.0606 | 26.1236 | 26.1866 | 26.2496 | 26.3127 | 26.3757 | 26.4387 | 0.28498 | 0.29316 | 0.30373 | 0.31328 | 0.32194 | 0.33179 | 0.34283 | 0.35227 | 0.35816 | 0.35904 | 0.35992 | 0.36079 | 0.36167 | 0.36255 | 0.36342 | 0.3643 | 0.36518 | 0.36605 | 0.36693 | 0.36781 | 32853.392 | 6411.4371 | 161603.0598 | 31537.3174 | 836433.249 | 836433.249 | 2898658.1216 | 836433.249
| CMN001-15420462 | 238 | CMN001 | CMN | North | 5608785.6336 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 157.9234 | 158.6808 | 159.4382 | 160.1956 | 160.9529 | 161.121 | 161.289 | 161.457 | 161.625 | 161.793 | 161.9611 | 162.1291 | 162.2971 | 162.4651 | 162.6331 | 162.8012 | 162.9692 | 163.1372 | 163.3052 | 163.4733 | 1.8124 | 1.8609 | 1.9245 | 1.9815 | 2.0326 | 2.0918 | 2.1583 | 2.2146 | 2.2485 | 2.2508 | 2.2531 | 2.2555 | 2.2578 | 2.2602 | 2.2625 | 2.2648 | 2.2672 | 2.2695 | 2.2718 | 2.2742 | 32853.392 | 6411.4371 | 1013718.9311 | 197830.262 | 3934932.6986 | 3934932.6986 | 5608785.6336 | 3934932.6986
| CMN001-156820944 | 375 | CMN001 | CMN | North | 8837372.3219 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 142.2185 | 142.9385 | 143.6586 | 144.3786 | 145.0986 | 145.4969 | 145.8952 | 146.2935 | 146.6918 | 147.0901 | 147.4885 | 147.8868 | 148.2851 | 148.6834 | 149.0817 | 149.48 | 149.8783 | 150.2767 | 150.675 | 151.0733 | 1.6321 | 1.6763 | 1.734 | 1.7858 | 1.8324 | 1.8889 | 1.9523 | 2.0066 | 2.0407 | 2.0463 | 2.0518 | 2.0573 | 2.0629 | 2.0684 | 2.074 | 2.0795 | 2.0851 | 2.0906 | 2.0961 | 2.1017 | 32853.392 | 6411.4371 | 921903.7345 | 179912.2535 | 11040534.9336 | 11040534.9336 | 8837372.3219 | 11040534.9336
| CMN001-163864096 | 7 | CMN001 | CMN | North | 164964.2833 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.24895 | 0.25053 | 0.25211 | 0.25369 | 0.25527 | 0.25583 | 0.25639 | 0.25696 | 0.25752 | 0.25808 | 0.25865 | 0.25921 | 0.25977 | 0.26034 | 0.2609 | 0.26146 | 0.26203 | 0.26259 | 0.26315 | 0.26372 | 0.002857 | 0.002938 | 0.0030431 | 0.0031379 | 0.0032236 | 0.0033214 | 0.003431 | 0.0035245 | 0.0035825 | 0.0035904 | 0.0035982 | 0.003606 | 0.0036139 | 0.0036217 | 0.0036295 | 0.0036374 | 0.0036452 | 0.0036531 | 0.0036609 | 0.0036687 | 32853.392 | 6411.4371 | 1616.1728 | 315.4009 | 25547.4206 | 25547.4206 | 164964.2833 | 25547.4206
| CMN001-182014538 | 100 | CMN001 | CMN | North | 2356632.6192 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 7.1016 | 7.1631 | 7.2246 | 7.2861 | 7.3476 | 7.3473 | 7.3471 | 7.3468 | 7.3466 | 7.3463 | 7.3461 | 7.3458 | 7.3456 | 7.3453 | 7.3451 | 7.3448 | 7.3446 | 7.3443 | 7.344 | 7.3438 | 0.0815 | 0.084005 | 0.087205 | 0.090122 | 0.092789 | 0.095388 | 0.098316 | 0.10077 | 0.1022 | 0.1022 | 0.1022 | 0.10219 | 0.10219 | 0.10219 | 0.10218 | 0.10218 | 0.10217 | 0.10217 | 0.10217 | 0.10216 | 32853.392 | 6411.4371 | 45915.6503 | 8960.5756 | 629648.6684 | 629648.6684 | 2356632.6192 | 629648.6684
| CMN001-73767965 | 62 | CMN001 | CMN | North | 1461112.2239 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.1574 | 0.1587 | 0.16001 | 0.16132 | 0.16263 | 0.16276 | 0.16289 | 0.16301 | 0.16314 | 0.16327 | 0.1634 | 0.16353 | 0.16366 | 0.16379 | 0.16391 | 0.16404 | 0.16417 | 0.1643 | 0.16443 | 0.16456 | 0.0018063 | 0.0018612 | 0.0019314 | 0.0019954 | 0.0020537 | 0.002113 | 0.0021797 | 0.002236 | 0.0022696 | 0.0022714 | 0.0022732 | 0.0022749 | 0.0022767 | 0.0022785 | 0.0022803 | 0.0022821 | 0.0022839 | 0.0022857 | 0.0022875 | 0.0022892 | 32853.392 | 6411.4371 | 1020.9155 | 199.2347 | 79795.3226 | 79795.3226 | 1461112.2239 | 79795.3226
| CMN001-73948224 | 40 | CMN001 | CMN | North | 942653.0477 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.24432 | 0.24608 | 0.24784 | 0.24959 | 0.25135 | 0.25221 | 0.25307 | 0.25393 | 0.25479 | 0.25565 | 0.25651 | 0.25737 | 0.25823 | 0.25909 | 0.25995 | 0.26081 | 0.26167 | 0.26253 | 0.26339 | 0.26425 | 0.0028039 | 0.0028859 | 0.0029915 | 0.0030872 | 0.0031741 | 0.0032743 | 0.0033864 | 0.003483 | 0.0035445 | 0.0035565 | 0.0035685 | 0.0035804 | 0.0035924 | 0.0036044 | 0.0036163 | 0.0036283 | 0.0036403 | 0.0036523 | 0.0036642 | 0.0036762 | 32853.392 | 6411.4371 | 1600.7437 | 312.3899 | 128480.4649 | 128480.4649 | 942653.0477 | 128480.4649
| CMN001-73948442 | 11 | CMN001 | CMN | North | 259229.5881 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.01881 | 0.01901 | 0.01921 | 0.019411 | 0.019611 | 0.019768 | 0.019924 | 0.020081 | 0.020238 | 0.020395 | 0.020551 | 0.020708 | 0.020865 | 0.021022 | 0.021179 | 0.021335 | 0.021492 | 0.021649 | 0.021806 | 0.021962 | 0.00021587 | 0.00022294 | 0.00023188 | 0.00024009 | 0.00024765 | 0.00025664 | 0.00026662 | 0.00027544 | 0.00028154 | 0.00028372 | 0.0002859 | 0.00028809 | 0.00029027 | 0.00029245 | 0.00029463 | 0.00029681 | 0.00029899 | 0.00030117 | 0.00030335 | 0.00030553 | 32853.392 | 6411.4371 | 127.632 | 24.9078 | 5425.9367 | 5425.9367 | 259229.5881 | 5425.9367
| CMN001-74644085 | 67 | CMN001 | CMN | North | 1578943.8548 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.70799 | 0.71354 | 0.71908 | 0.72462 | 0.73017 | 0.73325 | 0.73633 | 0.73941 | 0.74249 | 0.74557 | 0.74865 | 0.75173 | 0.75481 | 0.7579 | 0.76098 | 0.76406 | 0.76714 | 0.77022 | 0.7733 | 0.77638 | 0.0081252 | 0.0083679 | 0.0086797 | 0.0089629 | 0.0092209 | 0.0095196 | 0.0098533 | 0.010142 | 0.010329 | 0.010372 | 0.010415 | 0.010458 | 0.010501 | 0.010544 | 0.010586 | 0.010629 | 0.010672 | 0.010715 | 0.010758 | 0.010801 | 32853.392 | 6411.4371 | 4667.8306 | 910.941 | 260611.409 | 260611.409 | 1578943.8548 | 260611.409
| CMN001-74644167 | 32 | CMN001 | CMN | North | 754122.4381 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.508 | 0.51177 | 0.51555 | 0.51933 | 0.5231 | 0.52367 | 0.52424 | 0.52481 | 0.52539 | 0.52596 | 0.52653 | 0.5271 | 0.52767 | 0.52824 | 0.52881 | 0.52938 | 0.52995 | 0.53052 | 0.5311 | 0.53167 | 0.0058299 | 0.0060018 | 0.0062229 | 0.0064235 | 0.006606 | 0.0067987 | 0.0070152 | 0.0071985 | 0.007309 | 0.0073169 | 0.0073249 | 0.0073328 | 0.0073407 | 0.0073487 | 0.0073566 | 0.0073646 | 0.0073725 | 0.0073805 | 0.0073884 | 0.0073963 | 32853.392 | 6411.4371 | 3290.6172 | 642.1737 | 163086.3914 | 163086.3914 | 754122.4381 | 163086.3914
| CMN001-74644242 | 33 | CMN001 | CMN | North | 777688.7643 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.91052 | 0.91796 | 0.9254 | 0.93284 | 0.94028 | 0.9416 | 0.94291 | 0.94423 | 0.94554 | 0.94686 | 0.94817 | 0.94949 | 0.9508 | 0.95212 | 0.95343 | 0.95474 | 0.95606 | 0.95737 | 0.95869 | 0.96 | 0.010449 | 0.010765 | 0.01117 | 0.011538 | 0.011874 | 0.012224 | 0.012618 | 0.012951 | 0.013154 | 0.013172 | 0.013191 | 0.013209 | 0.013227 | 0.013245 | 0.013264 | 0.013282 | 0.0133 | 0.013319 | 0.013337 | 0.013355 | 32853.392 | 6411.4371 | 5922.0874 | 1155.713 | 158094.7269 | 158094.7269 | 777688.7643 | 158094.7269
| CMN001-74644428 | 31 | CMN001 | CMN | North | 730556.1119 | 0.00041222 | 0.00042124 | 0.00043357 | 0.00044429 | 0.00045361 | 0.00046633 | 0.00048066 | 0.00049269 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.0004997 | 0.058883 | 0.059349 | 0.059814 | 0.06028 | 0.060746 | 0.060903 | 0.061061 | 0.061218 | 0.061375 | 0.061533 | 0.06169 | 0.061848 | 0.062005 | 0.062162 | 0.06232 | 0.062477 | 0.062635 | 0.062792 | 0.062949 | 0.063107 | 0.00067576 | 0.00069601 | 0.00072199 | 0.0007456 | 0.00076712 | 0.00079069 | 0.00081709 | 0.00083969 | 0.00085383 | 0.00085602 | 0.00085821 | 0.0008604 | 0.00086259 | 0.00086478 | 0.00086697 | 0.00086916 | 0.00087135 | 0.00087354 | 0.00087573 | 0.00087792 | 32853.392 | 6411.4371 | 385.0445 | 75.1426 | 26949.2161 | 26949.2161 | 730556.1119 | 26949.2161
| CMN002-138133472 | 31 | CMN002 | CMN | North | 730556.1119 | 0.0012053 | 0.0012053 | 0.0012117 | 0.0012117 | 0.0012085 | 0.0012139 | 0.0012213 | 0.0012299 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.06312 | 0.063538 | 0.063957 | 0.064376 | 0.064794 | 0.064932 | 0.065069 | 0.065207 | 0.065344 | 0.065482 | 0.065619 | 0.065757 | 0.065894 | 0.066032 | 0.066169 | 0.066307 | 0.066444 | 0.066581 | 0.066719 | 0.066856 | 0.002118 | 0.0021321 | 0.0021575 | 0.0021716 | 0.00218 | 0.0021944 | 0.0022124 | 0.0022328 | 0.0022317 | 0.0022363 | 0.002241 | 0.0022457 | 0.0022504 | 0.0022551 | 0.0022598 | 0.0022645 | 0.0022692 | 0.0022739 | 0.0022786 | 0.0022833 | 32853.392 | 6411.4371 | 1052.2551 | 205.3507 | 36253.3962 | 36253.3962 | 730556.1119 | 36253.3962
| CMN002-15420512 | 525 | CMN002 | CMN | North | 12372321.2507 | 0.0012053 | 0.0012053 | 0.0012117 | 0.0012117 | 0.0012085 | 0.0012139 | 0.0012213 | 0.0012299 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 121.8083 | 122.4279 | 123.0475 | 123.6671 | 124.2867 | 124.6614 | 125.036 | 125.4106 | 125.7852 | 126.1599 | 126.5345 | 126.9091 | 127.2837 | 127.6584 | 128.033 | 128.4076 | 128.7822 | 129.1569 | 129.5315 | 129.9061 | 4.0874 | 4.1082 | 4.1509 | 4.1718 | 4.1816 | 4.2131 | 4.2513 | 4.2942 | 4.2959 | 4.3086 | 4.3214 | 4.3342 | 4.347 | 4.3598 | 4.3726 | 4.3854 | 4.3982 | 4.411 | 4.4238 | 4.4366 | 32853.392 | 6411.4371 | 2029371.975 | 396037.9718 | 14546156.2596 | 14546156.2596 | 12372321.2507 | 14546156.2596
| CMN002-15420523 | 1 | CMN002 | CMN | North | 23566.3262 | 0.0012053 | 0.0012053 | 0.0012117 | 0.0012117 | 0.0012085 | 0.0012139 | 0.0012213 | 0.0012299 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32853.392 | 6411.4371 | 0 | 0 | 0 | 0 | 23566.3262 | 0
| CMN002-78928402 | 1 | CMN002 | CMN | North | 23566.3262 | 0.0012053 | 0.0012053 | 0.0012117 | 0.0012117 | 0.0012085 | 0.0012139 | 0.0012213 | 0.0012299 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.084371 | 0.084945 | 0.085519 | 0.086093 | 0.086667 | 0.086828 | 0.08699 | 0.087152 | 0.087314 | 0.087476 | 0.087638 | 0.0878 | 0.087961 | 0.088123 | 0.088285 | 0.088447 | 0.088609 | 0.088771 | 0.088933 | 0.089094 | 0.0028311 | 0.0028504 | 0.0028849 | 0.0029042 | 0.0029159 | 0.0029345 | 0.0029578 | 0.0029842 | 0.002982 | 0.0029875 | 0.002993 | 0.0029986 | 0.0030041 | 0.0030096 | 0.0030151 | 0.0030207 | 0.0030262 | 0.0030317 | 0.0030372 | 0.0030428 | 32853.392 | 6411.4371 | 1405.5197 | 274.2913 | 1236.6524 | 1236.6524 | 23566.3262 | 1236.6524
| CMN002-78928472 | 44 | CMN002 | CMN | North | 1036918.3524 | 0.0012053 | 0.0012053 | 0.0012117 | 0.0012117 | 0.0012085 | 0.0012139 | 0.0012213 | 0.0012299 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.22412 | 0.22546 | 0.22679 | 0.22813 | 0.22946 | 0.22982 | 0.23018 | 0.23054 | 0.2309 | 0.23126 | 0.23163 | 0.23199 | 0.23235 | 0.23271 | 0.23307 | 0.23343 | 0.23379 | 0.23415 | 0.23451 | 0.23487 | 0.0075206 | 0.0075654 | 0.0076506 | 0.0076957 | 0.0077203 | 0.0077672 | 0.0078265 | 0.0078942 | 0.0078859 | 0.0078982 | 0.0079105 | 0.0079228 | 0.0079351 | 0.0079474 | 0.0079597 | 0.007972 | 0.0079843 | 0.0079966 | 0.0080089 | 0.0080212 | 32853.392 | 6411.4371 | 3717.7117 | 725.5225 | 157012.2337 | 157012.2337 | 1036918.3524 | 157012.2337
| CMN002-87920200 | 21 | CMN002 | CMN | North | 494892.85 | 0.0012053 | 0.0012053 | 0.0012117 | 0.0012117 | 0.0012085 | 0.0012139 | 0.0012213 | 0.0012299 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.0012267 | 0.066253 | 0.066737 | 0.06722 | 0.067704 | 0.068188 | 0.068508 | 0.068829 | 0.069149 | 0.069469 | 0.06979 | 0.07011 | 0.070431 | 0.070751 | 0.071072 | 0.071392 | 0.071712 | 0.072033 | 0.072353 | 0.072674 | 0.072994 | 0.0022232 | 0.0022394 | 0.0022676 | 0.0022839 | 0.0022942 | 0.0023153 | 0.0023402 | 0.0023678 | 0.0023725 | 0.0023835 | 0.0023944 | 0.0024054 | 0.0024163 | 0.0024273 | 0.0024382 | 0.0024491 | 0.0024601 | 0.002471 | 0.002482 | 0.0024929 | 32853.392 | 6411.4371 | 1121.2325 | 218.8119 | 19121.8703 | 19121.8703 | 494892.85 | 19121.8703
| CMN003-123737154 | 330 | CMN003 | CMN | North | 7776887.6433 | 0.0011756 | 0.0012005 | 0.0012358 | 0.0012646 | 0.0012895 | 0.0013248 | 0.0013679 | 0.0014037 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 73.9419 | 74.3863 | 74.8306 | 75.275 | 75.7194 | 75.8163 | 75.9133 | 76.0102 | 76.1071 | 76.204 | 76.301 | 76.3979 | 76.4948 | 76.5918 | 76.6887 | 76.7856 | 76.8825 | 76.9795 | 77.0764 | 77.1733 | 2.42 | 2.4861 | 2.5745 | 2.6502 | 2.7183 | 2.7963 | 2.891 | 2.9705 | 3.0108 | 3.0147 | 3.0185 | 3.0223 | 3.0262 | 3.03 | 3.0338 | 3.0377 | 3.0415 | 3.0453 | 3.0492 | 3.053 | 32853.392 | 6411.4371 | 1357667.3523 | 264952.8185 | 7635947.3402 | 7635947.3402 | 7776887.6433 | 7635947.3402
| CMN003-15420636 | 0 | CMN003 | CMN | North | 0 | 0.0011756 | 0.0012005 | 0.0012358 | 0.0012646 | 0.0012895 | 0.0013248 | 0.0013679 | 0.0014037 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.0077718 | 0.007827 | 0.0078821 | 0.0079373 | 0.0079924 | 0.008015 | 0.0080376 | 0.0080603 | 0.0080829 | 0.0081055 | 0.0081281 | 0.0081507 | 0.0081734 | 0.008196 | 0.0082186 | 0.0082412 | 0.0082638 | 0.0082865 | 0.0083091 | 0.0083317 | 0.00025436 | 0.00026158 | 0.00027118 | 0.00027945 | 0.00028693 | 0.00029562 | 0.0003061 | 0.000315 | 0.00031976 | 0.00032066 | 0.00032155 | 0.00032245 | 0.00032334 | 0.00032424 | 0.00032513 | 0.00032603 | 0.00032692 | 0.00032782 | 0.00032871 | 0.00032961 | 32853.392 | 6411.4371 | 0 | 0 | 0 | 0 | 0 | 0
| CMN003-15420649 | 166 | CMN003 | CMN | North | 3912010.1478 | 0.0011756 | 0.0012005 | 0.0012358 | 0.0012646 | 0.0012895 | 0.0013248 | 0.0013679 | 0.0014037 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 95.8677 | 96.4251 | 96.9825 | 97.5399 | 98.0973 | 98.2743 | 98.4512 | 98.6281 | 98.805 | 98.9819 | 99.1588 | 99.3358 | 99.5127 | 99.6896 | 99.8665 | 100.0434 | 100.2203 | 100.3972 | 100.5742 | 100.7511 | 3.1376 | 3.2226 | 3.3366 | 3.4341 | 3.5217 | 3.6247 | 3.7493 | 3.8544 | 3.9088 | 3.9158 | 3.9228 | 3.9298 | 3.9368 | 3.9438 | 3.9508 | 3.9578 | 3.9648 | 3.9718 | 3.9788 | 3.9858 | 32853.392 | 6411.4371 | 1763936.622 | 344237.4738 | 2354852.0435 | 2354852.0435 | 3912010.1478 | 2354852.0435
| CMN003-164373106 | 234 | CMN003 | CMN | North | 5514520.3289 | 0.0011756 | 0.0012005 | 0.0012358 | 0.0012646 | 0.0012895 | 0.0013248 | 0.0013679 | 0.0014037 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 11.976 | 12.0462 | 12.1164 | 12.1866 | 12.2568 | 12.2693 | 12.2818 | 12.2943 | 12.3068 | 12.3193 | 12.3318 | 12.3443 | 12.3568 | 12.3693 | 12.3818 | 12.3943 | 12.4068 | 12.4193 | 12.4318 | 12.4443 | 0.39196 | 0.4026 | 0.41685 | 0.42906 | 0.44002 | 0.45253 | 0.46773 | 0.48046 | 0.48686 | 0.48736 | 0.48785 | 0.48834 | 0.48884 | 0.48933 | 0.48983 | 0.49032 | 0.49082 | 0.49131 | 0.49181 | 0.4923 | 32853.392 | 6411.4371 | 219484.5591 | 42833.064 | 2698969.3698 | 2698969.3698 | 5514520.3289 | 2698969.3698
| CMN003-164373173 | 80 | CMN003 | CMN | North | 1885306.0953 | 0.0011756 | 0.0012005 | 0.0012358 | 0.0012646 | 0.0012895 | 0.0013248 | 0.0013679 | 0.0014037 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 1.1097 | 1.1165 | 1.1234 | 1.1302 | 1.137 | 1.1418 | 1.1467 | 1.1515 | 1.1563 | 1.1611 | 1.1659 | 1.1708 | 1.1756 | 1.1804 | 1.1852 | 1.1901 | 1.1949 | 1.1997 | 1.2045 | 1.2093 | 0.03632 | 0.037316 | 0.038649 | 0.039791 | 0.040819 | 0.042115 | 0.043669 | 0.045 | 0.045744 | 0.045935 | 0.046125 | 0.046316 | 0.046507 | 0.046697 | 0.046888 | 0.047079 | 0.04727 | 0.04746 | 0.047651 | 0.047842 | 32853.392 | 6411.4371 | 20702.4805 | 4040.1506 | 187693.418 | 187693.418 | 1885306.0953 | 187693.418
| CMN003-75645317 | 9 | CMN003 | CMN | North | 212096.9357 | 0.0011756 | 0.0012005 | 0.0012358 | 0.0012646 | 0.0012895 | 0.0013248 | 0.0013679 | 0.0014037 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.014047 | 0.014118 | 0.014189 | 0.014261 | 0.014332 | 0.014404 | 0.014477 | 0.01455 | 0.014622 | 0.014695 | 0.014768 | 0.01484 | 0.014913 | 0.014985 | 0.015058 | 0.015131 | 0.015203 | 0.015276 | 0.015349 | 0.015421 | 0.00045974 | 0.00047184 | 0.00048818 | 0.00050208 | 0.00051451 | 0.00053128 | 0.00055133 | 0.00056861 | 0.00057846 | 0.00058134 | 0.00058421 | 0.00058708 | 0.00058996 | 0.00059283 | 0.0005957 | 0.00059858 | 0.00060145 | 0.00060432 | 0.00060719 | 0.00061007 | 32853.392 | 6411.4371 | 262.2203 | 51.1731 | 4492.6471 | 4492.6471 | 212096.9357 | 4492.6471
| CMN003-75645537 | 19 | CMN003 | CMN | North | 447760.1976 | 0.0011756 | 0.0012005 | 0.0012358 | 0.0012646 | 0.0012895 | 0.0013248 | 0.0013679 | 0.0014037 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.01839 | 0.018521 | 0.018652 | 0.018783 | 0.018914 | 0.018992 | 0.01907 | 0.019148 | 0.019227 | 0.019305 | 0.019383 | 0.019461 | 0.019539 | 0.019617 | 0.019695 | 0.019773 | 0.019851 | 0.019929 | 0.020007 | 0.020086 | 0.00060188 | 0.00061899 | 0.00064171 | 0.00066131 | 0.00067902 | 0.00070049 | 0.00072626 | 0.00074833 | 0.00076061 | 0.0007637 | 0.00076679 | 0.00076988 | 0.00077297 | 0.00077606 | 0.00077915 | 0.00078224 | 0.00078533 | 0.00078841 | 0.0007915 | 0.00079459 | 32853.392 | 6411.4371 | 344.0022 | 67.133 | 8295.6815 | 8295.6815 | 447760.1976 | 8295.6815
| CMN003-76447191 | 12 | CMN003 | CMN | North | 282795.9143 | 0.0011756 | 0.0012005 | 0.0012358 | 0.0012646 | 0.0012895 | 0.0013248 | 0.0013679 | 0.0014037 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.11901 | 0.12 | 0.12099 | 0.12197 | 0.12296 | 0.12302 | 0.12309 | 0.12315 | 0.12322 | 0.12328 | 0.12334 | 0.12341 | 0.12347 | 0.12353 | 0.1236 | 0.12366 | 0.12372 | 0.12379 | 0.12385 | 0.12392 | 0.0038951 | 0.0040105 | 0.0041624 | 0.0042944 | 0.0044143 | 0.0045375 | 0.0046876 | 0.0048128 | 0.0048745 | 0.004877 | 0.0048795 | 0.004882 | 0.0048845 | 0.004887 | 0.0048896 | 0.0048921 | 0.0048946 | 0.0048971 | 0.0048996 | 0.0049021 | 32853.392 | 6411.4371 | 2193.1105 | 427.992 | 33428.9237 | 33428.9237 | 282795.9143 | 33428.9237
| CMN003-76447226 | 35 | CMN003 | CMN | North | 824821.4167 | 0.0011756 | 0.0012005 | 0.0012358 | 0.0012646 | 0.0012895 | 0.0013248 | 0.0013679 | 0.0014037 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.001421 | 0.026998 | 0.027181 | 0.027363 | 0.027546 | 0.027729 | 0.027819 | 0.027909 | 0.028 | 0.02809 | 0.02818 | 0.02827 | 0.028361 | 0.028451 | 0.028541 | 0.028631 | 0.028721 | 0.028812 | 0.028902 | 0.028992 | 0.029082 | 0.0008836 | 0.0009084 | 0.00094142 | 0.00096983 | 0.00099547 | 0.0010261 | 0.0010629 | 0.0010942 | 0.0011112 | 0.0011148 | 0.0011184 | 0.001122 | 0.0011255 | 0.0011291 | 0.0011327 | 0.0011362 | 0.0011398 | 0.0011434 | 0.0011469 | 0.0011505 | 32853.392 | 6411.4371 | 502.1336 | 97.9929 | 20916.8714 | 20916.8714 | 824821.4167 | 20916.8714
| CMN004-15420549 | 464 | CMN004 | CMN | North | 10934775.353 | 0.0009415 | 0.00094435 | 0.00095006 | 0.00095377 | 0.00095205 | 0.00095976 | 0.00097603 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 83.7897 | 84.4001 | 85.0106 | 85.621 | 86.2314 | 86.2938 | 86.3562 | 86.4186 | 86.481 | 86.5434 | 86.6058 | 86.6682 | 86.7306 | 86.7931 | 86.8555 | 86.9179 | 86.9803 | 87.0427 | 87.1051 | 87.1675 | 2.1962 | 2.2189 | 2.2485 | 2.2735 | 2.2856 | 2.3057 | 2.3465 | 2.3825 | 2.3843 | 2.386 | 2.3877 | 2.3894 | 2.3912 | 2.3929 | 2.3946 | 2.3963 | 2.398 | 2.3998 | 2.4015 | 2.4032 | 32853.392 | 6411.4371 | 1110241.674 | 216666.9621 | 8336382.0167 | 8336382.0167 | 10934775.353 | 8336382.0167
| CMN004-24614626 | 293 | CMN004 | CMN | North | 6904933.5742 | 0.0009415 | 0.00094435 | 0.00095006 | 0.00095377 | 0.00095205 | 0.00095976 | 0.00097603 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 11.589 | 11.6816 | 11.7742 | 11.8668 | 11.9593 | 11.9693 | 11.9792 | 11.9891 | 11.999 | 12.009 | 12.0189 | 12.0288 | 12.0387 | 12.0486 | 12.0586 | 12.0685 | 12.0784 | 12.0883 | 12.0982 | 12.1082 | 0.30376 | 0.30712 | 0.31142 | 0.3151 | 0.31698 | 0.31982 | 0.32551 | 0.33054 | 0.33081 | 0.33109 | 0.33136 | 0.33163 | 0.33191 | 0.33218 | 0.33245 | 0.33273 | 0.333 | 0.33327 | 0.33355 | 0.33382 | 32853.392 | 6411.4371 | 153996.4651 | 30052.8678 | 3106512.8044 | 3106512.8044 | 6904933.5742 | 3106512.8044
| CMN004-74052344 | 0 | CMN004 | CMN | North | 0 | 0.0009415 | 0.00094435 | 0.00095006 | 0.00095377 | 0.00095205 | 0.00095976 | 0.00097603 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.16083 | 0.16176 | 0.1627 | 0.16363 | 0.16456 | 0.16485 | 0.16513 | 0.16542 | 0.1657 | 0.16598 | 0.16627 | 0.16655 | 0.16684 | 0.16712 | 0.16741 | 0.16769 | 0.16798 | 0.16826 | 0.16854 | 0.16883 | 0.0042155 | 0.0042529 | 0.0043032 | 0.0043448 | 0.0043618 | 0.0044047 | 0.0044871 | 0.0045605 | 0.0045683 | 0.0045762 | 0.004584 | 0.0045919 | 0.0045997 | 0.0046075 | 0.0046154 | 0.0046232 | 0.004631 | 0.0046389 | 0.0046467 | 0.0046546 | 32853.392 | 6411.4371 | 0 | 0 | 0 | 0 | 0 | 0
| CMN004-76446391 | 48 | CMN004 | CMN | North | 1131183.6572 | 0.0009415 | 0.00094435 | 0.00095006 | 0.00095377 | 0.00095205 | 0.00095976 | 0.00097603 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.084324 | 0.08507 | 0.085816 | 0.086562 | 0.087308 | 0.087392 | 0.087477 | 0.087562 | 0.087646 | 0.087731 | 0.087815 | 0.0879 | 0.087984 | 0.088069 | 0.088153 | 0.088238 | 0.088323 | 0.088407 | 0.088492 | 0.088576 | 0.0022102 | 0.0022366 | 0.0022698 | 0.0022985 | 0.0023141 | 0.0023351 | 0.002377 | 0.0024141 | 0.0024164 | 0.0024187 | 0.0024211 | 0.0024234 | 0.0024257 | 0.002428 | 0.0024304 | 0.0024327 | 0.002435 | 0.0024374 | 0.0024397 | 0.002442 | 32853.392 | 6411.4371 | 1124.4558 | 219.4409 | 67948.3217 | 67948.3217 | 1131183.6572 | 67948.3217
| CMN004-76547682 | 90 | CMN004 | CMN | North | 2120969.3573 | 0.0009415 | 0.00094435 | 0.00095006 | 0.00095377 | 0.00095205 | 0.00095976 | 0.00097603 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0.0009903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32853.392 | 6411.4371 | 0 | 0 | 416287.6613 | 416287.6613 | 2120969.3573 | 416287.6613
| CMN005-15420597 | 160 | CMN005 | CMN | North | 3770612.1907 | 0.0042291 | 0.0042103 | 0.0041929 | 0.0041773 | 0.0041557 | 0.0041496 | 0.0041482 | 0.0041421 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 0.0041232 | 40.6654 | 40.9175 | 41.1695 | 41.4216 | 41.6737 | 41.7627 | 41.8517 | 41.9408 | 42.0298 | 42.1188 | 42.2079 | 42.2969 | 42.3859 | 42.475 | 42.564 | 42.653 | 42.742 | 42.8311 | 42.9201 | 43.0091 | 4.7878 | 4.7961 | 4.8057 | 4.8172 | 4.8214 | 4.8246 | 4.8332 | 4.8364 | 4.8246 | 4.8349 | 4.8451 | 4.8553 | 4.8655 | 4.8757 | 4.886 | 4.8962 | 4.9064 | 4.9166 | 4.9268 | 4.9371 | 32853.392 | 6411.4371 | 2302158.3003 | 449273.0338 | 2151798.5841 | 2151798.5841 | 3770612.1907 | 2151798.5841
| COB011-15431802 | 0 | COB011 | COB | South | 0 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 7.5611e-05 | 7.6467e-05 | 7.7323e-05 | 7.818e-05 | 7.9036e-05 | 7.8016e-05 | 7.6995e-05 | 7.5974e-05 | 7.4954e-05 | 7.3933e-05 | 7.2913e-05 | 7.1892e-05 | 7.0872e-05 | 6.9851e-05 | 6.8831e-05 | 6.781e-05 | 6.679e-05 | 6.5769e-05 | 6.4749e-05 | 6.3728e-05 | 7.523e-06 | 7.7621e-06 | 7.9723e-06 | 8.1302e-06 | 8.1794e-06 | 8.0699e-06 | 8.1129e-06 | 8.1992e-06 | 8.0387e-06 | 7.9293e-06 | 7.8198e-06 | 7.7104e-06 | 7.6009e-06 | 7.4915e-06 | 7.382e-06 | 7.2726e-06 | 7.1631e-06 | 7.0537e-06 | 6.9442e-06 | 6.8348e-06 | 32029.1653 | 2375.0502 | 0 | 0 | 0 | 0 | 0 | 0
| COB011-15431815 | 541 | COB011 | COB | South | 9835808.0021 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 3.4888 | 3.5134 | 3.538 | 3.5626 | 3.5872 | 3.558 | 3.5288 | 3.4996 | 3.4705 | 3.4413 | 3.4121 | 3.383 | 3.3538 | 3.3246 | 3.2955 | 3.2663 | 3.2371 | 3.208 | 3.1788 | 3.1496 | 0.34712 | 0.35664 | 0.36478 | 0.37048 | 0.37123 | 0.36804 | 0.37183 | 0.37768 | 0.3722 | 0.36908 | 0.36595 | 0.36282 | 0.35969 | 0.35656 | 0.35343 | 0.35031 | 0.34718 | 0.34405 | 0.34092 | 0.33779 | 32029.1653 | 2375.0502 | 167021.1314 | 12385.0736 | 673250.0394 | 872680.9479 | 10264550.5021 | 702596.9833
| COB011-162571445 | 5 | COB011 | COB | South | 90903.9557 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 3.7841e-05 | 3.8371e-05 | 3.8901e-05 | 3.943e-05 | 3.996e-05 | 3.9342e-05 | 3.8724e-05 | 3.8106e-05 | 3.7488e-05 | 3.687e-05 | 3.6252e-05 | 3.5634e-05 | 3.5016e-05 | 3.4398e-05 | 3.378e-05 | 3.3162e-05 | 3.2544e-05 | 3.1926e-05 | 3.1308e-05 | 3.069e-05 | 3.765e-06 | 3.895e-06 | 4.0108e-06 | 4.1005e-06 | 4.1354e-06 | 4.0695e-06 | 4.0803e-06 | 4.1124e-06 | 4.0205e-06 | 3.9543e-06 | 3.888e-06 | 3.8217e-06 | 3.7554e-06 | 3.6891e-06 | 3.6229e-06 | 3.5566e-06 | 3.4903e-06 | 3.424e-06 | 3.3577e-06 | 3.2915e-06 | 32029.1653 | 2375.0502 | 1.7796 | 0.13196 | 7.9976 | 10.3666 | 94866.4557 | 8.3462
| COB011-162571831 | 3 | COB011 | COB | South | 54542.3734 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 9.0569e-07 | 9.1751e-07 | 9.2934e-07 | 9.4117e-07 | 9.53e-07 | 9.3745e-07 | 9.219e-07 | 9.0635e-07 | 8.908e-07 | 8.7525e-07 | 8.597e-07 | 8.4415e-07 | 8.286e-07 | 8.1305e-07 | 7.975e-07 | 7.8195e-07 | 7.664e-07 | 7.5085e-07 | 7.353e-07 | 7.1975e-07 | 9.0112e-08 | 9.3136e-08 | 9.5819e-08 | 9.7875e-08 | 9.8626e-08 | 9.6969e-08 | 9.714e-08 | 9.7813e-08 | 9.5537e-08 | 9.3869e-08 | 9.2202e-08 | 9.0534e-08 | 8.8866e-08 | 8.7198e-08 | 8.5531e-08 | 8.3863e-08 | 8.2195e-08 | 8.0528e-08 | 7.886e-08 | 7.7192e-08 | 32029.1653 | 2375.0502 | 0.042265 | 0.003134 | 0.68384 | 0.88641 | 56919.8734 | 0.71365
| COB011-162572039 | 7 | COB011 | COB | South | 127265.5379 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0010207 | 0.0010298 | 0.0010388 | 0.0010479 | 0.001057 | 0.0010466 | 0.0010362 | 0.0010257 | 0.0010153 | 0.0010049 | 0.00099445 | 0.00098402 | 0.00097359 | 0.00096316 | 0.00095273 | 0.0009423 | 0.00093187 | 0.00092144 | 0.00091101 | 0.00090059 | 0.00010155 | 0.00010453 | 0.00010711 | 0.00010898 | 0.00010939 | 0.00010826 | 0.00010918 | 0.0001107 | 0.00010889 | 0.00010777 | 0.00010665 | 0.00010553 | 0.00010442 | 0.0001033 | 0.00010218 | 0.00010106 | 9.9942e-05 | 9.8823e-05 | 9.7705e-05 | 9.6586e-05 | 32029.1653 | 2375.0502 | 48.7019 | 3.6114 | 459.421 | 595.5112 | 132813.0379 | 479.4471
| COB011-162572240 | 20 | COB011 | COB | South | 363615.8226 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.00088051 | 0.00089089 | 0.00090126 | 0.00091163 | 0.000922 | 0.00090765 | 0.0008933 | 0.00087895 | 0.0008646 | 0.00085025 | 0.0008359 | 0.00082155 | 0.0008072 | 0.00079285 | 0.0007785 | 0.00076415 | 0.0007498 | 0.00073545 | 0.0007211 | 0.00070675 | 8.7607e-05 | 9.0433e-05 | 9.2923e-05 | 9.4803e-05 | 9.5417e-05 | 9.3887e-05 | 9.4126e-05 | 9.4856e-05 | 9.2727e-05 | 9.1188e-05 | 8.9649e-05 | 8.811e-05 | 8.6571e-05 | 8.5032e-05 | 8.3493e-05 | 8.1954e-05 | 8.0415e-05 | 7.8876e-05 | 7.7337e-05 | 7.5798e-05 | 32029.1653 | 2375.0502 | 41.096 | 3.0474 | 443.2682 | 574.5736 | 379465.8226 | 462.5902
| COB011-162572975 | 11 | COB011 | COB | South | 199988.7024 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 1.3598e-05 | 1.3843e-05 | 1.4089e-05 | 1.4334e-05 | 1.458e-05 | 1.4281e-05 | 1.3982e-05 | 1.3684e-05 | 1.3385e-05 | 1.3086e-05 | 1.2787e-05 | 1.2488e-05 | 1.219e-05 | 1.1891e-05 | 1.1592e-05 | 1.1293e-05 | 1.0994e-05 | 1.0696e-05 | 1.0397e-05 | 1.0098e-05 | 1.3529e-06 | 1.4052e-06 | 1.4526e-06 | 1.4907e-06 | 1.5089e-06 | 1.4772e-06 | 1.4733e-06 | 1.4767e-06 | 1.4355e-06 | 1.4035e-06 | 1.3714e-06 | 1.3394e-06 | 1.3073e-06 | 1.2753e-06 | 1.2432e-06 | 1.2112e-06 | 1.1791e-06 | 1.1471e-06 | 1.115e-06 | 1.083e-06 | 32029.1653 | 2375.0502 | 0.62944 | 0.046674 | 4.1504 | 5.3799 | 208706.2024 | 4.3314
| COB011-162661437 | 11 | COB011 | COB | South | 199988.7024 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.00066191 | 0.00066969 | 0.00067746 | 0.00068523 | 0.000693 | 0.00068255 | 0.0006721 | 0.00066165 | 0.0006512 | 0.00064075 | 0.0006303 | 0.00061985 | 0.0006094 | 0.00059895 | 0.0005885 | 0.00057805 | 0.0005676 | 0.00055715 | 0.0005467 | 0.00053625 | 6.5858e-05 | 6.7979e-05 | 6.9848e-05 | 7.1259e-05 | 7.1718e-05 | 7.0602e-05 | 7.0819e-05 | 7.1405e-05 | 6.984e-05 | 6.872e-05 | 6.7599e-05 | 6.6478e-05 | 6.5357e-05 | 6.4237e-05 | 6.3116e-05 | 6.1995e-05 | 6.0874e-05 | 5.9754e-05 | 5.8633e-05 | 5.7512e-05 | 32029.1653 | 2375.0502 | 30.9733 | 2.2968 | 183.7371 | 238.1639 | 208706.2024 | 191.7461
| COB011-162661589 | 49 | COB011 | COB | South | 890858.7654 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.021741 | 0.021965 | 0.022189 | 0.022414 | 0.022638 | 0.0223 | 0.021962 | 0.021624 | 0.021286 | 0.020948 | 0.02061 | 0.020272 | 0.019934 | 0.019596 | 0.019258 | 0.01892 | 0.018582 | 0.018244 | 0.017906 | 0.017568 | 0.0021632 | 0.0022297 | 0.0022878 | 0.0023309 | 0.0023428 | 0.0023067 | 0.0023141 | 0.0023336 | 0.0022829 | 0.0022466 | 0.0022104 | 0.0021741 | 0.0021379 | 0.0021016 | 0.0020654 | 0.0020291 | 0.0019929 | 0.0019566 | 0.0019204 | 0.0018841 | 32029.1653 | 2375.0502 | 1013.5366 | 75.1565 | 11644.8424 | 15094.2912 | 929691.2654 | 12152.4407
| COB011-162661811 | 25 | COB011 | COB | South | 454519.7783 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 8.7588e-05 | 8.9316e-05 | 9.1044e-05 | 9.2772e-05 | 9.45e-05 | 9.261e-05 | 9.072e-05 | 8.883e-05 | 8.694e-05 | 8.505e-05 | 8.316e-05 | 8.127e-05 | 7.938e-05 | 7.749e-05 | 7.56e-05 | 7.371e-05 | 7.182e-05 | 6.993e-05 | 6.804e-05 | 6.615e-05 | 8.7146e-06 | 9.0664e-06 | 9.387e-06 | 9.6476e-06 | 9.7798e-06 | 9.5795e-06 | 9.5591e-06 | 9.5865e-06 | 9.3242e-06 | 9.1215e-06 | 8.9188e-06 | 8.7161e-06 | 8.5134e-06 | 8.3107e-06 | 8.108e-06 | 7.9053e-06 | 7.7026e-06 | 7.4999e-06 | 7.2972e-06 | 7.0945e-06 | 32029.1653 | 2375.0502 | 4.0871 | 0.30307 | 26.2476 | 34.0226 | 474332.2783 | 27.3917
| COB011-162798633 | 17 | COB011 | COB | South | 309073.4492 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.003334 | 0.0033592 | 0.0033844 | 0.0034096 | 0.0034348 | 0.0033954 | 0.0033561 | 0.0033167 | 0.0032774 | 0.003238 | 0.0031987 | 0.0031593 | 0.00312 | 0.0030806 | 0.0030413 | 0.0030019 | 0.0029626 | 0.0029232 | 0.0028839 | 0.0028445 | 0.00033172 | 0.00034099 | 0.00034894 | 0.00035457 | 0.00035546 | 0.00035122 | 0.00035362 | 0.00035794 | 0.00035149 | 0.00034727 | 0.00034305 | 0.00033883 | 0.00033461 | 0.00033039 | 0.00032617 | 0.00032195 | 0.00031773 | 0.00031351 | 0.00030929 | 0.00030507 | 32029.1653 | 2375.0502 | 157.0279 | 11.644 | 2878.4817 | 3731.1489 | 322545.9492 | 3003.9546
| COB011-163103340 | 15 | COB011 | COB | South | 272711.867 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0060328 | 0.0061095 | 0.0061862 | 0.0062629 | 0.0063396 | 0.0062477 | 0.0061558 | 0.0060639 | 0.005972 | 0.0058801 | 0.0057882 | 0.0056964 | 0.0056045 | 0.0055126 | 0.0054207 | 0.0053288 | 0.0052369 | 0.005145 | 0.0050531 | 0.0049613 | 0.00060024 | 0.00062017 | 0.00063782 | 0.0006513 | 0.00065608 | 0.00064626 | 0.00064863 | 0.00065442 | 0.00064049 | 0.00063064 | 0.00062078 | 0.00061093 | 0.00060107 | 0.00059122 | 0.00058136 | 0.00057151 | 0.00056165 | 0.0005518 | 0.00054194 | 0.00053209 | 32029.1653 | 2375.0502 | 284.0959 | 21.0665 | 1531.9541 | 1985.7514 | 284599.367 | 1598.7319
| COB011-164044294 | 1 | COB011 | COB | South | 18180.7911 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32029.1653 | 2375.0502 | 0 | 0 | 0.2655 | 0.34415 | 18973.2911 | 0.27708
| COB011-201141604 | 77 | COB011 | COB | South | 1399920.9171 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.25379 | 0.25556 | 0.25733 | 0.25909 | 0.26086 | 0.25821 | 0.25555 | 0.2529 | 0.25025 | 0.24759 | 0.24494 | 0.24229 | 0.23964 | 0.23698 | 0.23433 | 0.23168 | 0.22902 | 0.22637 | 0.22372 | 0.22107 | 0.025251 | 0.025942 | 0.026531 | 0.026944 | 0.026996 | 0.026709 | 0.026927 | 0.027293 | 0.026839 | 0.026554 | 0.02627 | 0.025985 | 0.025701 | 0.025416 | 0.025132 | 0.024847 | 0.024563 | 0.024278 | 0.023994 | 0.023709 | 32029.1653 | 2375.0502 | 12013.9442 | 890.8668 | 18492.764 | 23970.712 | 1460943.4171 | 19298.8629
| COB011-202349052 | 341 | COB011 | COB | South | 6199649.7758 | 0.0035738 | 0.0036462 | 0.0037034 | 0.0037354 | 0.0037173 | 0.0037155 | 0.0037848 | 0.0038764 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.85506 | 0.86083 | 0.86659 | 0.87236 | 0.87813 | 0.86919 | 0.86025 | 0.85131 | 0.84237 | 0.83342 | 0.82448 | 0.81554 | 0.8066 | 0.79766 | 0.78872 | 0.77978 | 0.77084 | 0.76189 | 0.75295 | 0.74401 | 0.085075 | 0.087382 | 0.089349 | 0.09072 | 0.090878 | 0.089908 | 0.090644 | 0.091873 | 0.090343 | 0.089384 | 0.088425 | 0.087466 | 0.086507 | 0.085548 | 0.084589 | 0.08363 | 0.082671 | 0.081712 | 0.080753 | 0.079794 | 32029.1653 | 2375.0502 | 40445.3797 | 2999.1355 | 255279.3515 | 330898.4975 | 6469892.2758 | 266406.9689
| COB012-15431852 | 87 | COB012 | COB | South | 1581728.8284 | 0.018455 | 0.018303 | 0.017955 | 0.017545 | 0.017197 | 0.016894 | 0.016591 | 0.016394 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.016136 | 0.023437 | 0.023639 | 0.02384 | 0.024042 | 0.024243 | 0.024008 | 0.023774 | 0.02354 | 0.023305 | 0.023071 | 0.022836 | 0.022602 | 0.022367 | 0.022133 | 0.021898 | 0.021664 | 0.021429 | 0.021195 | 0.02096 | 0.020726 | 0.012042 | 0.012045 | 0.011917 | 0.011743 | 0.011607 | 0.011292 | 0.010981 | 0.010744 | 0.010469 | 0.010364 | 0.010259 | 0.010153 | 0.010048 | 0.0099428 | 0.0098375 | 0.0097321 | 0.0096268 | 0.0095215 | 0.0094161 | 0.0093108 | 32029.1653 | 2375.0502 | 4969.2883 | 368.4863 | 15893.3842 | 20601.3409 | 1650676.3284 | 16586.1762
| COB021-15436290 | 169 | COB021 | COB | South | 3072553.7012 | 0.16975 | 0.16832 | 0.16486 | 0.16154 | 0.15796 | 0.15464 | 0.15179 | 0.14954 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.028752 | 0.028993 | 0.029234 | 0.029475 | 0.029716 | 0.029429 | 0.029143 | 0.028856 | 0.02857 | 0.028283 | 0.027996 | 0.02771 | 0.027423 | 0.027137 | 0.02685 | 0.026563 | 0.026277 | 0.02599 | 0.025704 | 0.025417 | 0.13588 | 0.13586 | 0.13417 | 0.13255 | 0.13068 | 0.1267 | 0.12315 | 0.12013 | 0.11695 | 0.11578 | 0.1146 | 0.11343 | 0.11226 | 0.11108 | 0.10991 | 0.10874 | 0.10756 | 0.10639 | 0.10522 | 0.10404 | 32029.1653 | 2375.0502 | 55725.1531 | 4132.1725 | 89226.9672 | 115657.883 | 3206486.2012 | 93116.3673
| COB021-24613718 | 6 | COB021 | COB | South | 109084.7468 | 0.16975 | 0.16832 | 0.16486 | 0.16154 | 0.15796 | 0.15464 | 0.15179 | 0.14954 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0.14704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32029.1653 | 2375.0502 | 0 | 0 | 0.72582 | 0.94082 | 113839.7468 | 0.75746
| COB022-160576265 | 16 | COB022 | COB | South | 290892.6581 | 1.1922 | 1.1683 | 1.1435 | 1.1192 | 1.0943 | 1.0722 | 1.0545 | 1.0385 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32029.1653 | 2375.0502 | 0 | 0 | 0 | 0 | 303572.6581 | 0
| CRO013-15404871 | 0 | CRO013 | CRO | South | 0 | 0.00057774 | 0.00058241 | 0.00058425 | 0.00058624 | 0.00058482 | 0.00058581 | 0.00060379 | 0.00061965 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35001.1248 | 3719.1254 | 0 | 0 | 0 | 0 | 0 | 0
| CRO013-15404884 | 226 | CRO013 | CRO | South | 4108858.7957 | 0.00057774 | 0.00058241 | 0.00058425 | 0.00058624 | 0.00058482 | 0.00058581 | 0.00060379 | 0.00061965 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0.00063098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35001.1248 | 3719.1254 | 0 | 0 | 0 | 0 | 4287963.7957 | 0
| CRO014-15404821 | 30 | CRO014 | CRO | South | 545423.7339 | 0.035149 | 0.035014 | 0.034878 | 0.034743 | 0.034608 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0.034473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35001.1248 | 3719.1254 | 0 | 0 | 0 | 0 | 569198.7339 | 0
| CRO021-153844129 | 63 | CRO021 | CRO | South | 1145389.8413 | 0.0027936 | 0.0027855 | 0.0027954 | 0.0027786 | 0.002748 | 0.002752 | 0.0027884 | 0.0028075 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35001.1248 | 3719.1254 | 0 | 0 | 0 | 0 | 1195317.3413 | 0
| CRO021-15404447 | 134 | CRO021 | CRO | South | 2436226.0116 | 0.0027936 | 0.0027855 | 0.0027954 | 0.0027786 | 0.002748 | 0.002752 | 0.0027884 | 0.0028075 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.0027728 | 0.44132 | 0.44336 | 0.4454 | 0.44743 | 0.44947 | 0.44925 | 0.44902 | 0.4488 | 0.44857 | 0.44835 | 0.44812 | 0.4479 | 0.44767 | 0.44745 | 0.44722 | 0.447 | 0.44677 | 0.44654 | 0.44632 | 0.44609 | 0.034324 | 0.034382 | 0.034662 | 0.034612 | 0.034386 | 0.03442 | 0.034858 | 0.035079 | 0.034628 | 0.03461 | 0.034593 | 0.034576 | 0.034558 | 0.034541 | 0.034523 | 0.034506 | 0.034489 | 0.034471 | 0.034454 | 0.034437 | 35001.1248 | 3719.1254 | 17488.6703 | 1858.2991 | 18203.2409 | 23595.426 | 2542421.0116 | 18996.7195
| CRO022-15404471 | 127 | CRO022 | CRO | South | 2308960.4737 | 0.00052158 | 0.00052322 | 0.00052273 | 0.00052273 | 0.00052011 | 0.00052011 | 0.00052616 | 0.00053156 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35001.1248 | 3719.1254 | 0 | 0 | 0 | 0 | 2409607.9737 | 0
| CRO022-24612421 | 91 | CRO022 | CRO | South | 1654451.993 | 0.00052158 | 0.00052322 | 0.00052273 | 0.00052273 | 0.00052011 | 0.00052011 | 0.00052616 | 0.00053156 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0.00053385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35001.1248 | 3719.1254 | 0 | 0 | 0 | 0 | 1726569.493 | 0
| CRO023-15404521 | 98 | CRO023 | CRO | South | 1781717.5309 | 0.0016087 | 0.0016087 | 0.001592 | 0.001587 | 0.0015702 | 0.0015652 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0015769 | 0.0046798 | 0.0047208 | 0.0047618 | 0.0048028 | 0.0048438 | 0.0048632 | 0.0048827 | 0.0049021 | 0.0049215 | 0.004941 | 0.0049604 | 0.0049798 | 0.0049993 | 0.0050187 | 0.0050382 | 0.0050576 | 0.005077 | 0.0050965 | 0.0051159 | 0.0051353 | 0.00020959 | 0.00021143 | 0.00021105 | 0.00021219 | 0.00021175 | 0.00021192 | 0.00021436 | 0.00021521 | 0.00021606 | 0.00021692 | 0.00021777 | 0.00021862 | 0.00021948 | 0.00022033 | 0.00022118 | 0.00022204 | 0.00022289 | 0.00022374 | 0.0002246 | 0.00022545 | 35001.1248 | 3719.1254 | 109.502 | 11.6354 | 423.4295 | 548.8582 | 1859382.5309 | 441.8868
| CRO031-15404634 | 0 | CRO031 | CRO | South | 0 | 2.8065 | 2.7865 | 2.7465 | 2.7065 | 2.665 | 2.625 | 2.595 | 2.5685 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35001.1248 | 3719.1254 | 0 | 0 | 0 | 0 | 0 | 0
| CRO031-15404660 | 23 | CRO031 | CRO | South | 418158.196 | 2.8065 | 2.7865 | 2.7465 | 2.7065 | 2.665 | 2.625 | 2.595 | 2.5685 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35001.1248 | 3719.1254 | 0 | 0 | 0 | 0 | 436385.696 | 0
| CRO032-15404697 | 40 | CRO032 | CRO | South | 727231.6453 | 1.0189 | 1.0356 | 1.0622 | 1.0668 | 1.0625 | 1.0751 | 1.1112 | 1.1358 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 1.1238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35001.1248 | 3719.1254 | 0 | 0 | 0 | 0 | 758931.6453 | 0
| CRO033-15404721 | 62 | CRO033 | CRO | South | 1127209.0502 | 0.13716 | 0.13644 | 0.13456 | 0.13259 | 0.13072 | 0.12875 | 0.12719 | 0.12616 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.12491 | 0.034285 | 0.034573 | 0.03486 | 0.035148 | 0.035436 | 0.035561 | 0.035687 | 0.035812 | 0.035938 | 0.036064 | 0.036189 | 0.036315 | 0.036441 | 0.036566 | 0.036692 | 0.036818 | 0.036943 | 0.037069 | 0.037194 | 0.03732 | 0.13092 | 0.13132 | 0.13059 | 0.12975 | 0.12896 | 0.12747 | 0.12636 | 0.12578 | 0.12497 | 0.12541 | 0.12584 | 0.12628 | 0.12672 | 0.12716 | 0.12759 | 0.12803 | 0.12847 | 0.1289 | 0.12934 | 0.12978 | 35001.1248 | 3719.1254 | 64823.6616 | 6887.988 | 36546.4399 | 47372.2687 | 1176344.0502 | 38139.4978
| CRO034-15404810 | 195 | CRO034 | CRO | South | 3545254.2706 | 0.0017724 | 0.0017776 | 0.0017665 | 0.0017529 | 0.0017298 | 0.0017125 | 0.0017162 | 0.001721 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0.0017088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35001.1248 | 3719.1254 | 0 | 0 | 0 | 0 | 3699791.7706 | 0
| CTN001-129145544 | 454 | CTN001 | CTN | North | 10699112.0911 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 4.5716 | 4.5953 | 4.6189 | 4.6426 | 4.6662 | 4.6703 | 4.6744 | 4.6785 | 4.6827 | 4.6868 | 4.6909 | 4.695 | 4.6991 | 4.7032 | 4.7073 | 4.7115 | 4.7156 | 4.7197 | 4.7238 | 4.7279 | 0.27233 | 0.37519 | 0.37965 | 0.38068 | 0.37931 | 0.37804 | 0.3801 | 0.38243 | 0.3796 | 0.37994 | 0.38027 | 0.38061 | 0.38094 | 0.38127 | 0.38161 | 0.38194 | 0.38227 | 0.38261 | 0.38294 | 0.38327 | 27432.6704 | 4182.9743 | 147965.5631 | 22562.0089 | 1363510.6852 | 1363510.6852 | 10699112.0911 | 1363510.6852
| CTN001-15418475 | 57 | CTN001 | CTN | North | 1343280.5929 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 3.7046 | 3.7178 | 3.731 | 3.7443 | 3.7575 | 3.7559 | 3.7544 | 3.7529 | 3.7513 | 3.7498 | 3.7482 | 3.7467 | 3.7451 | 3.7436 | 3.742 | 3.7405 | 3.739 | 3.7374 | 3.7359 | 3.7343 | 0.22069 | 0.30355 | 0.30667 | 0.30702 | 0.30544 | 0.30403 | 0.30528 | 0.30676 | 0.3041 | 0.30398 | 0.30385 | 0.30373 | 0.3036 | 0.30348 | 0.30335 | 0.30323 | 0.3031 | 0.30298 | 0.30285 | 0.30273 | 27432.6704 | 4182.9743 | 118475.6859 | 18065.3486 | 76236.5072 | 76236.5072 | 1343280.5929 | 76236.5072
| CTN001-155143379 | 72 | CTN001 | CTN | North | 1696775.4858 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.08267 | 0.083459 | 0.084247 | 0.085036 | 0.085824 | 0.085744 | 0.085665 | 0.085585 | 0.085505 | 0.085425 | 0.085345 | 0.085265 | 0.085185 | 0.085106 | 0.085026 | 0.084946 | 0.084866 | 0.084786 | 0.084706 | 0.084626 | 0.0049247 | 0.0068142 | 0.0069247 | 0.0069728 | 0.0069765 | 0.0069407 | 0.0069657 | 0.0069958 | 0.0069315 | 0.0069251 | 0.0069186 | 0.0069121 | 0.0069056 | 0.0068992 | 0.0068927 | 0.0068862 | 0.0068797 | 0.0068733 | 0.0068668 | 0.0068603 | 27432.6704 | 4182.9743 | 2689.6703 | 410.1249 | 99191.8544 | 99191.8544 | 1696775.4858 | 99191.8544
| CTN001-155143591 | 119 | CTN001 | CTN | North | 2804392.8168 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.15881 | 0.16048 | 0.16215 | 0.16382 | 0.16549 | 0.16502 | 0.16456 | 0.16409 | 0.16363 | 0.16316 | 0.16269 | 0.16223 | 0.16176 | 0.1613 | 0.16083 | 0.16036 | 0.1599 | 0.15943 | 0.15897 | 0.1585 | 0.0094602 | 0.013103 | 0.013328 | 0.013433 | 0.013452 | 0.013358 | 0.013381 | 0.013413 | 0.013265 | 0.013227 | 0.013189 | 0.013151 | 0.013113 | 0.013076 | 0.013038 | 0.013 | 0.012962 | 0.012925 | 0.012887 | 0.012849 | 27432.6704 | 4182.9743 | 5133.0904 | 782.7012 | 243369.6612 | 243369.6612 | 2804392.8168 | 243369.6612
| CTN001-155143776 | 74 | CTN001 | CTN | North | 1743908.1382 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.14406 | 0.14515 | 0.14624 | 0.14733 | 0.14843 | 0.14874 | 0.14905 | 0.14936 | 0.14966 | 0.14997 | 0.15028 | 0.15059 | 0.1509 | 0.15121 | 0.15152 | 0.15183 | 0.15214 | 0.15245 | 0.15276 | 0.15307 | 0.0085818 | 0.011851 | 0.01202 | 0.012081 | 0.012065 | 0.01204 | 0.012119 | 0.012209 | 0.012133 | 0.012158 | 0.012183 | 0.012208 | 0.012233 | 0.012258 | 0.012283 | 0.012309 | 0.012334 | 0.012359 | 0.012384 | 0.012409 | 27432.6704 | 4182.9743 | 4729.079 | 721.097 | 117616.6187 | 117616.6187 | 1743908.1382 | 117616.6187
| CTN001-155143905 | 4 | CTN001 | CTN | North | 94265.3048 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.00056092 | 0.00056684 | 0.00057276 | 0.00057868 | 0.0005846 | 0.00058589 | 0.00058719 | 0.00058848 | 0.00058978 | 0.00059107 | 0.00059237 | 0.00059366 | 0.00059496 | 0.00059625 | 0.00059755 | 0.00059884 | 0.00060014 | 0.00060143 | 0.00060273 | 0.00060402 | 3.3414e-05 | 4.6281e-05 | 4.7078e-05 | 4.7451e-05 | 4.7521e-05 | 4.7426e-05 | 4.7747e-05 | 4.8104e-05 | 4.7811e-05 | 4.7916e-05 | 4.8021e-05 | 4.8126e-05 | 4.8231e-05 | 4.8336e-05 | 4.8441e-05 | 4.8546e-05 | 4.8651e-05 | 4.8756e-05 | 4.8861e-05 | 4.8966e-05 | 27432.6704 | 4182.9743 | 18.6076 | 2.8373 | 21.6314 | 21.6314 | 94265.3048 | 21.6314
| CTN001-155145203 | 11 | CTN001 | CTN | North | 259229.5881 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0069808 | 0.007057 | 0.0071332 | 0.0072094 | 0.0072856 | 0.0072754 | 0.0072651 | 0.0072549 | 0.0072446 | 0.0072344 | 0.0072241 | 0.0072139 | 0.0072036 | 0.0071933 | 0.0071831 | 0.0071728 | 0.0071626 | 0.0071523 | 0.0071421 | 0.0071318 | 0.00041585 | 0.00057619 | 0.00058631 | 0.00059116 | 0.00059224 | 0.00058892 | 0.00059076 | 0.00059302 | 0.00058729 | 0.00058646 | 0.00058563 | 0.0005848 | 0.00058397 | 0.00058314 | 0.0005823 | 0.00058147 | 0.00058064 | 0.00057981 | 0.00057898 | 0.00057815 | 27432.6704 | 4182.9743 | 227.5895 | 34.7032 | 6731.8046 | 6731.8046 | 259229.5881 | 6731.8046
| CTN001-155179699 | 26 | CTN001 | CTN | North | 612724.481 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0069178 | 0.0070025 | 0.0070872 | 0.007172 | 0.0072567 | 0.0072449 | 0.0072332 | 0.0072214 | 0.0072097 | 0.0071979 | 0.0071862 | 0.0071744 | 0.0071627 | 0.0071509 | 0.0071392 | 0.0071274 | 0.0071157 | 0.0071039 | 0.0070922 | 0.0070804 | 0.00041209 | 0.00057174 | 0.00058253 | 0.00058809 | 0.00058988 | 0.00058645 | 0.00058816 | 0.00059029 | 0.00058446 | 0.00058351 | 0.00058256 | 0.0005816 | 0.00058065 | 0.0005797 | 0.00057874 | 0.00057779 | 0.00057684 | 0.00057589 | 0.00057493 | 0.00057398 | 27432.6704 | 4182.9743 | 226.2697 | 34.5019 | 9039.0673 | 9039.0673 | 612724.481 | 9039.0673
| CTN001-155179789 | 31 | CTN001 | CTN | North | 730556.1119 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.014282 | 0.01446 | 0.014637 | 0.014815 | 0.014992 | 0.014963 | 0.014934 | 0.014905 | 0.014875 | 0.014846 | 0.014817 | 0.014788 | 0.014758 | 0.014729 | 0.0147 | 0.014671 | 0.014641 | 0.014612 | 0.014583 | 0.014554 | 0.00085081 | 0.0011806 | 0.0012031 | 0.0012148 | 0.0012187 | 0.0012112 | 0.0012143 | 0.0012183 | 0.0012059 | 0.0012035 | 0.0012011 | 0.0011988 | 0.0011964 | 0.001194 | 0.0011917 | 0.0011893 | 0.0011869 | 0.0011846 | 0.0011822 | 0.0011798 | 27432.6704 | 4182.9743 | 466.6251 | 71.1517 | 14143.8004 | 14143.8004 | 730556.1119 | 14143.8004
| CTN001-155190934 | 18 | CTN001 | CTN | North | 424193.8715 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0013431 | 0.0013572 | 0.0013714 | 0.0013855 | 0.0013996 | 0.0013969 | 0.0013942 | 0.0013915 | 0.0013887 | 0.001386 | 0.0013833 | 0.0013806 | 0.0013779 | 0.0013752 | 0.0013725 | 0.0013698 | 0.0013671 | 0.0013644 | 0.0013617 | 0.001359 | 8.0011e-05 | 0.00011082 | 0.00011272 | 0.00011361 | 0.00011377 | 0.00011307 | 0.00011336 | 0.00011374 | 0.00011258 | 0.00011236 | 0.00011214 | 0.00011192 | 0.0001117 | 0.00011148 | 0.00011126 | 0.00011104 | 0.00011082 | 0.0001106 | 0.00011038 | 0.00011016 | 27432.6704 | 4182.9743 | 43.6108 | 6.6498 | 2814.621 | 2814.621 | 424193.8715 | 2814.621
| CTN001-155191080 | 4 | CTN001 | CTN | North | 94265.3048 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 7.8811e-06 | 7.9709e-06 | 8.0606e-06 | 8.1503e-06 | 8.24e-06 | 8.257e-06 | 8.274e-06 | 8.291e-06 | 8.308e-06 | 8.325e-06 | 8.342e-06 | 8.359e-06 | 8.376e-06 | 8.393e-06 | 8.41e-06 | 8.427e-06 | 8.444e-06 | 8.461e-06 | 8.478e-06 | 8.495e-06 | 4.6948e-07 | 6.508e-07 | 6.6254e-07 | 6.6831e-07 | 6.6982e-07 | 6.6837e-07 | 6.7279e-07 | 6.7772e-07 | 6.735e-07 | 6.7487e-07 | 6.7625e-07 | 6.7763e-07 | 6.7901e-07 | 6.8039e-07 | 6.8177e-07 | 6.8314e-07 | 6.8452e-07 | 6.859e-07 | 6.8728e-07 | 6.8866e-07 | 27432.6704 | 4182.9743 | 0.26196 | 0.039943 | 5.6335 | 5.6335 | 94265.3048 | 5.6335
| CTN001-155191213 | 17 | CTN001 | CTN | North | 400627.5453 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0093863 | 0.009498 | 0.0096096 | 0.0097213 | 0.009833 | 0.0098069 | 0.0097809 | 0.0097548 | 0.0097288 | 0.0097027 | 0.0096767 | 0.0096506 | 0.0096246 | 0.0095985 | 0.0095725 | 0.0095464 | 0.0095204 | 0.0094943 | 0.0094683 | 0.0094422 | 0.00055915 | 0.00077548 | 0.00078986 | 0.00079713 | 0.00079931 | 0.00079384 | 0.00079532 | 0.00079738 | 0.00078867 | 0.00078656 | 0.00078445 | 0.00078234 | 0.00078023 | 0.00077811 | 0.000776 | 0.00077389 | 0.00077178 | 0.00076967 | 0.00076756 | 0.00076544 | 27432.6704 | 4182.9743 | 305.0243 | 46.5106 | 11155.2353 | 11155.2353 | 400627.5453 | 11155.2353
| CTN001-155191322 | 102 | CTN001 | CTN | North | 2403765.2716 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.23946 | 0.24208 | 0.2447 | 0.24731 | 0.24993 | 0.24965 | 0.24937 | 0.24909 | 0.2488 | 0.24852 | 0.24824 | 0.24796 | 0.24768 | 0.2474 | 0.24712 | 0.24683 | 0.24655 | 0.24627 | 0.24599 | 0.24571 | 0.014265 | 0.019765 | 0.020113 | 0.020279 | 0.020316 | 0.020208 | 0.020277 | 0.020361 | 0.02017 | 0.020147 | 0.020124 | 0.020101 | 0.020078 | 0.020055 | 0.020033 | 0.02001 | 0.019987 | 0.019964 | 0.019941 | 0.019919 | 27432.6704 | 4182.9743 | 7818.6529 | 1192.1998 | 295781.5267 | 295781.5267 | 2403765.2716 | 295781.5267
| CTN001-155250725 | 29 | CTN001 | CTN | North | 683423.4596 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 2.97e-05 | 1.7692e-06 | 2.4249e-06 | 2.4412e-06 | 2.4353e-06 | 2.4143e-06 | 2.4041e-06 | 2.415e-06 | 2.4277e-06 | 2.4077e-06 | 2.4077e-06 | 2.4077e-06 | 2.4077e-06 | 2.4077e-06 | 2.4077e-06 | 2.4077e-06 | 2.4077e-06 | 2.4077e-06 | 2.4077e-06 | 2.4077e-06 | 2.4077e-06 | 27432.6704 | 4182.9743 | 0.94041 | 0.14339 | 32.6093 | 32.6093 | 683423.4596 | 32.6093
| CTN001-155250997 | 374 | CTN001 | CTN | North | 8813805.9957 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.34403 | 0.34665 | 0.34926 | 0.35188 | 0.35449 | 0.35498 | 0.35548 | 0.35597 | 0.35646 | 0.35696 | 0.35745 | 0.35794 | 0.35844 | 0.35893 | 0.35943 | 0.35992 | 0.36041 | 0.36091 | 0.3614 | 0.36189 | 0.020494 | 0.028303 | 0.028707 | 0.028853 | 0.028816 | 0.028735 | 0.028905 | 0.029098 | 0.028897 | 0.028937 | 0.028977 | 0.029017 | 0.029057 | 0.029097 | 0.029137 | 0.029177 | 0.029217 | 0.029257 | 0.029297 | 0.029337 | 27432.6704 | 4182.9743 | 11254.6277 | 1716.1223 | 1741254.232 | 1741254.232 | 8813805.9957 | 1741254.232
| CTN001-155668176 | 32 | CTN001 | CTN | North | 754122.4381 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.05758 | 0.058236 | 0.058891 | 0.059547 | 0.060202 | 0.06013 | 0.060059 | 0.059987 | 0.059915 | 0.059843 | 0.059772 | 0.0597 | 0.059628 | 0.059556 | 0.059485 | 0.059413 | 0.059341 | 0.059269 | 0.059197 | 0.059126 | 0.0034301 | 0.0047548 | 0.0048405 | 0.0048827 | 0.0048937 | 0.0048673 | 0.0048836 | 0.0049034 | 0.0048571 | 0.0048513 | 0.0048454 | 0.0048396 | 0.0048338 | 0.004828 | 0.0048222 | 0.0048164 | 0.0048105 | 0.0048047 | 0.0047989 | 0.0047931 | 27432.6704 | 4182.9743 | 1882.21 | 287.0022 | 43187.1942 | 43187.1942 | 754122.4381 | 43187.1942
| CTN001-155668272 | 40 | CTN001 | CTN | North | 942653.0477 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.014831 | 0.015004 | 0.015177 | 0.015349 | 0.015522 | 0.015514 | 0.015505 | 0.015497 | 0.015488 | 0.01548 | 0.015471 | 0.015463 | 0.015454 | 0.015446 | 0.015437 | 0.015429 | 0.015421 | 0.015412 | 0.015404 | 0.015395 | 0.00088348 | 0.001225 | 0.0012474 | 0.0012586 | 0.0012618 | 0.0012558 | 0.0012608 | 0.0012667 | 0.0012556 | 0.0012549 | 0.0012542 | 0.0012535 | 0.0012528 | 0.0012521 | 0.0012515 | 0.0012508 | 0.0012501 | 0.0012494 | 0.0012487 | 0.001248 | 27432.6704 | 4182.9743 | 486.8464 | 74.2351 | 29919.4775 | 29919.4775 | 942653.0477 | 29919.4775
| CTN001-155821745 | 66 | CTN001 | CTN | North | 1555377.5287 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.084583 | 0.085536 | 0.086489 | 0.087442 | 0.088395 | 0.088242 | 0.088089 | 0.087936 | 0.087783 | 0.08763 | 0.087477 | 0.087324 | 0.08717 | 0.087017 | 0.086864 | 0.086711 | 0.086558 | 0.086405 | 0.086252 | 0.086099 | 0.0050387 | 0.0069838 | 0.007109 | 0.0071701 | 0.0071855 | 0.0071429 | 0.0071629 | 0.007188 | 0.0071162 | 0.0071038 | 0.0070914 | 0.007079 | 0.0070666 | 0.0070542 | 0.0070417 | 0.0070293 | 0.0070169 | 0.0070045 | 0.0069921 | 0.0069797 | 27432.6704 | 4182.9743 | 2756.1302 | 420.2588 | 108697.7209 | 108697.7209 | 1555377.5287 | 108697.7209
| CTN001-155821947 | 45 | CTN001 | CTN | North | 1060484.6786 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.019895 | 0.019902 | 0.019909 | 0.019915 | 0.019922 | 0.019916 | 0.019909 | 0.019903 | 0.019897 | 0.019891 | 0.019884 | 0.019878 | 0.019872 | 0.019866 | 0.01986 | 0.019853 | 0.019847 | 0.019841 | 0.019835 | 0.019828 | 0.0011852 | 0.001625 | 0.0016364 | 0.001633 | 0.0016194 | 0.0016121 | 0.0016189 | 0.0016269 | 0.001613 | 0.0016125 | 0.001612 | 0.0016114 | 0.0016109 | 0.0016104 | 0.0016099 | 0.0016094 | 0.0016089 | 0.0016084 | 0.0016079 | 0.0016074 | 27432.6704 | 4182.9743 | 629.6658 | 96.0124 | 14470.5137 | 14470.5137 | 1060484.6786 | 14470.5137
| CTN001-155822474 | 31 | CTN001 | CTN | North | 730556.1119 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.019703 | 0.019921 | 0.020139 | 0.020356 | 0.020574 | 0.020564 | 0.020555 | 0.020545 | 0.020535 | 0.020526 | 0.020516 | 0.020507 | 0.020497 | 0.020487 | 0.020478 | 0.020468 | 0.020459 | 0.020449 | 0.020439 | 0.02043 | 0.0011737 | 0.0016265 | 0.0016553 | 0.0016692 | 0.0016724 | 0.0016646 | 0.0016714 | 0.0016794 | 0.0016647 | 0.001664 | 0.0016632 | 0.0016624 | 0.0016616 | 0.0016608 | 0.0016601 | 0.0016593 | 0.0016585 | 0.0016577 | 0.0016569 | 0.0016562 | 27432.6704 | 4182.9743 | 645.7697 | 98.4679 | 30757.6545 | 30757.6545 | 730556.1119 | 30757.6545
| CTN001-155822565 | 64 | CTN001 | CTN | North | 1508244.8763 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.078603 | 0.079448 | 0.080293 | 0.081138 | 0.081983 | 0.081983 | 0.081982 | 0.081982 | 0.081981 | 0.081981 | 0.081981 | 0.08198 | 0.08198 | 0.08198 | 0.081979 | 0.081979 | 0.081979 | 0.081978 | 0.081978 | 0.081978 | 0.0046824 | 0.0064867 | 0.0065997 | 0.0066532 | 0.0066643 | 0.0066362 | 0.0066663 | 0.0067013 | 0.0066459 | 0.0066459 | 0.0066459 | 0.0066458 | 0.0066458 | 0.0066458 | 0.0066457 | 0.0066457 | 0.0066457 | 0.0066457 | 0.0066456 | 0.0066456 | 27432.6704 | 4182.9743 | 2579.8134 | 393.3738 | 110981.8048 | 110981.8048 | 1508244.8763 | 110981.8048
| CTN001-156780450 | 79 | CTN001 | CTN | North | 1861739.7692 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.076742 | 0.077276 | 0.07781 | 0.078343 | 0.078877 | 0.079063 | 0.079249 | 0.079435 | 0.079621 | 0.079807 | 0.079993 | 0.080179 | 0.080366 | 0.080552 | 0.080738 | 0.080924 | 0.08111 | 0.081296 | 0.081482 | 0.081668 | 0.0045716 | 0.0063094 | 0.0063955 | 0.006424 | 0.0064118 | 0.0063999 | 0.0064441 | 0.0064931 | 0.0064546 | 0.0064697 | 0.0064847 | 0.0064998 | 0.0065149 | 0.00653 | 0.0065451 | 0.0065602 | 0.0065753 | 0.0065904 | 0.0066054 | 0.0066205 | 27432.6704 | 4182.9743 | 2517.4788 | 383.8689 | 76392.5985 | 76392.5985 | 1861739.7692 | 76392.5985
| CTN001-158006395 | 1 | CTN001 | CTN | North | 23566.3262 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 6.624e-07 | 3.9459e-08 | 5.4083e-08 | 5.4446e-08 | 5.4315e-08 | 5.3845e-08 | 5.3619e-08 | 5.3862e-08 | 5.4146e-08 | 5.3698e-08 | 5.3698e-08 | 5.3698e-08 | 5.3698e-08 | 5.3698e-08 | 5.3698e-08 | 5.3698e-08 | 5.3698e-08 | 5.3698e-08 | 5.3698e-08 | 5.3698e-08 | 5.3698e-08 | 27432.6704 | 4182.9743 | 0.020974 | 0.0031981 | 0.0070534 | 0.0070534 | 23566.3262 | 0.0070534
| CTN001-161785823 | 97 | CTN001 | CTN | North | 2285933.6406 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.12639 | 0.12733 | 0.12828 | 0.12923 | 0.13018 | 0.13035 | 0.13052 | 0.13069 | 0.13087 | 0.13104 | 0.13121 | 0.13138 | 0.13155 | 0.13172 | 0.13189 | 0.13206 | 0.13223 | 0.1324 | 0.13257 | 0.13275 | 0.0075288 | 0.010397 | 0.010544 | 0.010597 | 0.010582 | 0.010552 | 0.010613 | 0.010683 | 0.010609 | 0.010623 | 0.010636 | 0.01065 | 0.010664 | 0.010678 | 0.010692 | 0.010706 | 0.01072 | 0.010733 | 0.010747 | 0.010761 | 27432.6704 | 4182.9743 | 4131.6579 | 630.0013 | 205264.7581 | 205264.7581 | 2285933.6406 | 205264.7581
| CTN001-163126863 | 53 | CTN001 | CTN | North | 1249015.2882 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0083989 | 0.0084534 | 0.0085078 | 0.0085623 | 0.0086168 | 0.0086245 | 0.0086323 | 0.0086401 | 0.0086478 | 0.0086556 | 0.0086634 | 0.0086711 | 0.0086789 | 0.0086867 | 0.0086944 | 0.0087022 | 0.00871 | 0.0087177 | 0.0087255 | 0.0087333 | 0.00050033 | 0.0006902 | 0.0006993 | 0.00070209 | 0.00070044 | 0.00069813 | 0.00070193 | 0.00070625 | 0.00070105 | 0.00070168 | 0.00070231 | 0.00070294 | 0.00070357 | 0.00070419 | 0.00070482 | 0.00070545 | 0.00070608 | 0.00070671 | 0.00070734 | 0.00070797 | 27432.6704 | 4182.9743 | 273.0612 | 41.6368 | 5559.735 | 5559.735 | 1249015.2882 | 5559.735
| CTN001-163266702 | 13 | CTN001 | CTN | North | 306362.2405 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0077005 | 0.0077876 | 0.0078747 | 0.0079618 | 0.0080489 | 0.0080529 | 0.0080568 | 0.0080607 | 0.0080647 | 0.0080686 | 0.0080726 | 0.0080765 | 0.0080804 | 0.0080844 | 0.0080883 | 0.0080923 | 0.0080962 | 0.0081002 | 0.0081041 | 0.008108 | 0.00045872 | 0.00063584 | 0.00064726 | 0.00065285 | 0.00065428 | 0.00065185 | 0.00065513 | 0.0006589 | 0.00065377 | 0.00065409 | 0.00065441 | 0.00065473 | 0.00065505 | 0.00065537 | 0.00065569 | 0.00065601 | 0.00065633 | 0.00065665 | 0.00065697 | 0.00065729 | 27432.6704 | 4182.9743 | 253.8447 | 38.7066 | 11829.434 | 11829.434 | 306362.2405 | 11829.434
| CTN001-24604306 | 353 | CTN001 | CTN | North | 8318913.1457 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 13.1559 | 13.2784 | 13.4009 | 13.5235 | 13.646 | 13.6249 | 13.6038 | 13.5827 | 13.5616 | 13.5405 | 13.5194 | 13.4983 | 13.4772 | 13.4561 | 13.435 | 13.4139 | 13.3928 | 13.3717 | 13.3505 | 13.3294 | 0.7837 | 1.0841 | 1.1015 | 1.1089 | 1.1093 | 1.1029 | 1.1062 | 1.1103 | 1.0994 | 1.0977 | 1.096 | 1.0943 | 1.0925 | 1.0908 | 1.0891 | 1.0874 | 1.0857 | 1.084 | 1.0823 | 1.0806 | 27432.6704 | 4182.9743 | 426351.678 | 65010.7373 | 2222381.4517 | 2222381.4517 | 8318913.1457 | 2222381.4517
| CTN001-24604862 | 87 | CTN001 | CTN | North | 2050270.3787 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.44669 | 0.44705 | 0.4474 | 0.44776 | 0.44812 | 0.44769 | 0.44725 | 0.44682 | 0.44639 | 0.44595 | 0.44552 | 0.44509 | 0.44466 | 0.44422 | 0.44379 | 0.44336 | 0.44292 | 0.44249 | 0.44206 | 0.44162 | 0.026609 | 0.0365 | 0.036774 | 0.036716 | 0.036427 | 0.036239 | 0.036368 | 0.036524 | 0.036187 | 0.036152 | 0.036117 | 0.036082 | 0.036046 | 0.036011 | 0.035976 | 0.035941 | 0.035906 | 0.035871 | 0.035836 | 0.035801 | 27432.6704 | 4182.9743 | 14112.3475 | 2151.8717 | 248351.1825 | 248351.1825 | 2050270.3787 | 248351.1825
| CTN001-24611782 | 45 | CTN001 | CTN | North | 1060484.6786 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 1.2303 | 1.2398 | 1.2493 | 1.2588 | 1.2682 | 1.2689 | 1.2695 | 1.2701 | 1.2708 | 1.2714 | 1.272 | 1.2727 | 1.2733 | 1.2739 | 1.2746 | 1.2752 | 1.2758 | 1.2765 | 1.2771 | 1.2777 | 0.073289 | 0.10123 | 0.10268 | 0.10322 | 0.10309 | 0.10271 | 0.10323 | 0.10382 | 0.10302 | 0.10307 | 0.10312 | 0.10317 | 0.10322 | 0.10327 | 0.10332 | 0.10338 | 0.10343 | 0.10348 | 0.10353 | 0.10358 | 27432.6704 | 4182.9743 | 40079.5906 | 6111.3955 | 47245.3953 | 47245.3953 | 1060484.6786 | 47245.3953
| CTN001-24611950 | 155 | CTN001 | CTN | North | 3652780.5597 | 0.0021397 | 0.0029327 | 0.0029524 | 0.0029453 | 0.0029198 | 0.0029076 | 0.0029208 | 0.0029361 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.0029119 | 0.58397 | 0.58899 | 0.59401 | 0.59903 | 0.60405 | 0.60302 | 0.60199 | 0.60096 | 0.59993 | 0.5989 | 0.59787 | 0.59684 | 0.59581 | 0.59479 | 0.59376 | 0.59273 | 0.5917 | 0.59067 | 0.58964 | 0.58861 | 0.034787 | 0.048089 | 0.048824 | 0.049119 | 0.049102 | 0.048812 | 0.04895 | 0.049123 | 0.048634 | 0.048551 | 0.048467 | 0.048384 | 0.0483 | 0.048217 | 0.048134 | 0.04805 | 0.047967 | 0.047883 | 0.0478 | 0.047717 | 27432.6704 | 4182.9743 | 18864.9706 | 2876.5587 | 221006.251 | 221006.251 | 3652780.5597 | 221006.251
| CTN002-15418512 | 243 | CTN002 | CTN | North | 5726617.2646 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 64.892 | 65.2263 | 65.5607 | 65.8951 | 66.2294 | 66.2768 | 66.3242 | 66.3716 | 66.419 | 66.4664 | 66.5139 | 66.5613 | 66.6087 | 66.6561 | 66.7035 | 66.7509 | 66.7983 | 66.8457 | 66.8931 | 66.9405 | 2.1494 | 2.1629 | 2.1661 | 2.1636 | 2.1506 | 2.1282 | 2.1321 | 2.1416 | 2.1191 | 2.1206 | 2.1221 | 2.1236 | 2.1252 | 2.1267 | 2.1282 | 2.1297 | 2.1312 | 2.1327 | 2.1342 | 2.1357 | 27432.6704 | 4182.9743 | 848044.9032 | 129311.1468 | 4966671.2784 | 4966671.2784 | 5726617.2646 | 4966671.2784
| CTN002-154876793 | 70 | CTN002 | CTN | North | 1649642.8334 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.18591 | 0.18712 | 0.18832 | 0.18953 | 0.19074 | 0.19101 | 0.19128 | 0.19154 | 0.19181 | 0.19208 | 0.19234 | 0.19261 | 0.19288 | 0.19314 | 0.19341 | 0.19368 | 0.19394 | 0.19421 | 0.19448 | 0.19474 | 0.0061578 | 0.0062047 | 0.006222 | 0.0062231 | 0.0061938 | 0.0061333 | 0.0061488 | 0.0061805 | 0.0061197 | 0.0061282 | 0.0061367 | 0.0061452 | 0.0061537 | 0.0061623 | 0.0061708 | 0.0061793 | 0.0061878 | 0.0061963 | 0.0062048 | 0.0062133 | 27432.6704 | 4182.9743 | 2448.5546 | 373.3592 | 157332.0233 | 157332.0233 | 1649642.8334 | 157332.0233
| CTN002-154876923 | 109 | CTN002 | CTN | North | 2568729.5549 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.28079 | 0.28271 | 0.28463 | 0.28655 | 0.28847 | 0.29042 | 0.29237 | 0.29432 | 0.29627 | 0.29822 | 0.30017 | 0.30212 | 0.30407 | 0.30602 | 0.30798 | 0.30993 | 0.31188 | 0.31383 | 0.31578 | 0.31773 | 0.0093007 | 0.0093745 | 0.0094039 | 0.0094085 | 0.0093671 | 0.0093254 | 0.0093986 | 0.0094968 | 0.0094525 | 0.0095148 | 0.009577 | 0.0096393 | 0.0097015 | 0.0097637 | 0.009826 | 0.0098882 | 0.0099504 | 0.010013 | 0.010075 | 0.010137 | 27432.6704 | 4182.9743 | 3800.6706 | 579.5319 | 275777.2755 | 275777.2755 | 2568729.5549 | 275777.2755
| CTN002-154877191 | 82 | CTN002 | CTN | North | 1932438.7477 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.14997 | 0.15087 | 0.15177 | 0.15267 | 0.15357 | 0.15381 | 0.15404 | 0.15427 | 0.15451 | 0.15474 | 0.15497 | 0.1552 | 0.15544 | 0.15567 | 0.1559 | 0.15614 | 0.15637 | 0.1566 | 0.15684 | 0.15707 | 0.0049675 | 0.0050028 | 0.0050144 | 0.0050128 | 0.0049868 | 0.0049387 | 0.0049518 | 0.0049779 | 0.0049295 | 0.0049369 | 0.0049444 | 0.0049518 | 0.0049592 | 0.0049667 | 0.0049741 | 0.0049815 | 0.004989 | 0.0049964 | 0.0050038 | 0.0050113 | 27432.6704 | 4182.9743 | 1973.1993 | 300.8764 | 105052.7907 | 105052.7907 | 1932438.7477 | 105052.7907
| CTN002-154877287 | 93 | CTN002 | CTN | North | 2191668.3358 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.011246 | 0.011265 | 0.011283 | 0.011301 | 0.011319 | 0.011313 | 0.011307 | 0.011301 | 0.011295 | 0.011289 | 0.011283 | 0.011277 | 0.011271 | 0.011265 | 0.011259 | 0.011253 | 0.011247 | 0.011242 | 0.011236 | 0.01123 | 0.00037251 | 0.00037353 | 0.00037277 | 0.00037106 | 0.00036756 | 0.00036327 | 0.00036349 | 0.00036466 | 0.00036038 | 0.00036019 | 0.00036 | 0.00035981 | 0.00035962 | 0.00035942 | 0.00035923 | 0.00035904 | 0.00035885 | 0.00035866 | 0.00035847 | 0.00035828 | 27432.6704 | 4182.9743 | 144.3796 | 22.0152 | 16244.0199 | 16244.0199 | 2191668.3358 | 16244.0199
| CTN002-154877444 | 67 | CTN002 | CTN | North | 1578943.8548 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.00072291 | 0.00073069 | 0.00073846 | 0.00074623 | 0.000754 | 0.0007572 | 0.0007604 | 0.0007636 | 0.0007668 | 0.00077 | 0.0007732 | 0.0007764 | 0.0007796 | 0.0007828 | 0.000786 | 0.0007892 | 0.0007924 | 0.0007956 | 0.0007988 | 0.000802 | 2.3945e-05 | 2.4229e-05 | 2.4398e-05 | 2.4502e-05 | 2.4484e-05 | 2.4314e-05 | 2.4444e-05 | 2.4639e-05 | 2.4465e-05 | 2.4567e-05 | 2.4669e-05 | 2.4771e-05 | 2.4873e-05 | 2.4975e-05 | 2.5077e-05 | 2.5179e-05 | 2.5282e-05 | 2.5384e-05 | 2.5486e-05 | 2.5588e-05 | 27432.6704 | 4182.9743 | 9.7897 | 1.4927 | 873.2032 | 873.2032 | 1578943.8548 | 873.2032
| CTN002-155259126 | 72 | CTN002 | CTN | North | 1696775.4858 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.059317 | 0.059685 | 0.060052 | 0.06042 | 0.060787 | 0.060923 | 0.061059 | 0.061195 | 0.061331 | 0.061467 | 0.061603 | 0.061739 | 0.061875 | 0.062011 | 0.062146 | 0.062282 | 0.062418 | 0.062554 | 0.06269 | 0.062826 | 0.0019648 | 0.0019791 | 0.0019841 | 0.0019838 | 0.0019739 | 0.0019563 | 0.0019628 | 0.0019746 | 0.0019568 | 0.0019611 | 0.0019654 | 0.0019698 | 0.0019741 | 0.0019784 | 0.0019828 | 0.0019871 | 0.0019915 | 0.0019958 | 0.0020001 | 0.0020045 | 27432.6704 | 4182.9743 | 783.7146 | 119.502 | 79060.8616 | 79060.8616 | 1696775.4858 | 79060.8616
| CTN002-155504946 | 9 | CTN002 | CTN | North | 212096.9357 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27432.6704 | 4182.9743 | 0 | 0 | 0 | 0 | 212096.9357 | 0
| CTN002-155616870 | 13 | CTN002 | CTN | North | 306362.2405 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.011773 | 0.011862 | 0.011951 | 0.01204 | 0.012129 | 0.012157 | 0.012186 | 0.012215 | 0.012244 | 0.012273 | 0.012302 | 0.012331 | 0.01236 | 0.012389 | 0.012417 | 0.012446 | 0.012475 | 0.012504 | 0.012533 | 0.012562 | 0.00038997 | 0.00039334 | 0.00039484 | 0.00039531 | 0.00039384 | 0.00039038 | 0.00039175 | 0.00039415 | 0.00039065 | 0.00039157 | 0.00039249 | 0.00039341 | 0.00039433 | 0.00039526 | 0.00039618 | 0.0003971 | 0.00039802 | 0.00039894 | 0.00039986 | 0.00040078 | 27432.6704 | 4182.9743 | 156.3487 | 23.8403 | 9018.278 | 9018.278 | 306362.2405 | 9018.278
| CTN002-155622465 | 47 | CTN002 | CTN | North | 1107617.331 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.006673 | 0.0067262 | 0.0067795 | 0.0068327 | 0.006886 | 0.006902 | 0.006918 | 0.006934 | 0.00695 | 0.0069661 | 0.0069821 | 0.0069981 | 0.0070141 | 0.0070301 | 0.0070461 | 0.0070621 | 0.0070781 | 0.0070941 | 0.0071101 | 0.0071261 | 0.00022103 | 0.00022304 | 0.00022399 | 0.00022435 | 0.0002236 | 0.00022162 | 0.00022239 | 0.00022374 | 0.00022174 | 0.00022225 | 0.00022276 | 0.00022327 | 0.00022378 | 0.0002243 | 0.00022481 | 0.00022532 | 0.00022583 | 0.00022634 | 0.00022685 | 0.00022736 | 27432.6704 | 4182.9743 | 88.718 | 13.5279 | 7400.439 | 7400.439 | 1107617.331 | 7400.439
| CTN002-155683683 | 50 | CTN002 | CTN | North | 1178316.3096 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.10318 | 0.10387 | 0.10456 | 0.10525 | 0.10594 | 0.10641 | 0.10689 | 0.10737 | 0.10785 | 0.10832 | 0.1088 | 0.10928 | 0.10975 | 0.11023 | 0.11071 | 0.11119 | 0.11166 | 0.11214 | 0.11262 | 0.1131 | 0.0034177 | 0.0034442 | 0.0034545 | 0.0034557 | 0.0034399 | 0.0034169 | 0.0034361 | 0.0034644 | 0.0034408 | 0.003456 | 0.0034713 | 0.0034865 | 0.0035017 | 0.003517 | 0.0035322 | 0.0035474 | 0.0035627 | 0.0035779 | 0.0035931 | 0.0036084 | 27432.6704 | 4182.9743 | 1380.678 | 210.5278 | 52484.9002 | 52484.9002 | 1178316.3096 | 52484.9002
| CTN002-155683893 | 24 | CTN002 | CTN | North | 565591.8286 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.051801 | 0.052229 | 0.052657 | 0.053085 | 0.053514 | 0.053704 | 0.053895 | 0.054086 | 0.054277 | 0.054468 | 0.054658 | 0.054849 | 0.05504 | 0.055231 | 0.055422 | 0.055612 | 0.055803 | 0.055994 | 0.056185 | 0.056376 | 0.0017158 | 0.0017319 | 0.0017397 | 0.001743 | 0.0017377 | 0.0017245 | 0.0017325 | 0.0017452 | 0.0017317 | 0.0017378 | 0.0017439 | 0.00175 | 0.0017561 | 0.0017621 | 0.0017682 | 0.0017743 | 0.0017804 | 0.0017865 | 0.0017926 | 0.0017987 | 27432.6704 | 4182.9743 | 693.5588 | 105.7549 | 26068.4387 | 26068.4387 | 565591.8286 | 26068.4387
| CTN002-158379241 | 50 | CTN002 | CTN | North | 1178316.3096 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.34853 | 0.35033 | 0.35214 | 0.35394 | 0.35574 | 0.35605 | 0.35636 | 0.35667 | 0.35697 | 0.35728 | 0.35759 | 0.35789 | 0.3582 | 0.35851 | 0.35881 | 0.35912 | 0.35943 | 0.35974 | 0.36004 | 0.36035 | 0.011544 | 0.011617 | 0.011634 | 0.011621 | 0.011552 | 0.011433 | 0.011456 | 0.011508 | 0.011389 | 0.011399 | 0.011409 | 0.011419 | 0.011428 | 0.011438 | 0.011448 | 0.011458 | 0.011468 | 0.011477 | 0.011487 | 0.011497 | 27432.6704 | 4182.9743 | 4558.4432 | 695.0782 | 62777.3139 | 62777.3139 | 1178316.3096 | 62777.3139
| CTN002-182897070 | 10 | CTN002 | CTN | North | 235663.2619 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 6.1326e-06 | 6.1994e-06 | 6.2663e-06 | 6.3331e-06 | 6.4e-06 | 6.42e-06 | 6.44e-06 | 6.46e-06 | 6.48e-06 | 6.5e-06 | 6.52e-06 | 6.54e-06 | 6.56e-06 | 6.58e-06 | 6.6e-06 | 6.62e-06 | 6.64e-06 | 6.66e-06 | 6.68e-06 | 6.7e-06 | 2.0313e-07 | 2.0557e-07 | 2.0703e-07 | 2.0794e-07 | 2.0782e-07 | 2.0615e-07 | 2.0702e-07 | 2.0844e-07 | 2.0674e-07 | 2.0738e-07 | 2.0802e-07 | 2.0866e-07 | 2.093e-07 | 2.0994e-07 | 2.1057e-07 | 2.1121e-07 | 2.1185e-07 | 2.1249e-07 | 2.1313e-07 | 2.1376e-07 | 27432.6704 | 4182.9743 | 0.082632 | 0.0126 | 11.0001 | 11.0001 | 235663.2619 | 11.0001
| CTN002-24605474 | 354 | CTN002 | CTN | North | 8342479.4719 | 0.0011898 | 0.0011911 | 0.0011867 | 0.0011794 | 0.0011664 | 0.0011534 | 0.0011547 | 0.001159 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 0.001146 | 9.2548 | 9.2994 | 9.3441 | 9.3888 | 9.4334 | 9.4374 | 9.4414 | 9.4455 | 9.4495 | 9.4535 | 9.4575 | 9.4615 | 9.4655 | 9.4695 | 9.4735 | 9.4775 | 9.4815 | 9.4855 | 9.4895 | 9.4935 | 0.30655 | 0.30837 | 0.30872 | 0.30827 | 0.30632 | 0.30304 | 0.30351 | 0.30478 | 0.30149 | 0.30161 | 0.30174 | 0.30187 | 0.302 | 0.30212 | 0.30225 | 0.30238 | 0.30251 | 0.30263 | 0.30276 | 0.30289 | 27432.6704 | 4182.9743 | 120642.7023 | 18395.7785 | 2589880.2128 | 2589880.2128 | 8342479.4719 | 2589880.2128
| CTN003-15418451 | 169 | CTN003 | CTN | North | 3982709.1264 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 17.8975 | 18.0088 | 18.1201 | 18.2314 | 18.3427 | 18.3541 | 18.3655 | 18.3769 | 18.3883 | 18.3997 | 18.4111 | 18.4225 | 18.4339 | 18.4453 | 18.4568 | 18.4682 | 18.4796 | 18.491 | 18.5024 | 18.5138 | 0.45129 | 0.45619 | 0.45901 | 0.45823 | 0.45463 | 0.45001 | 0.45093 | 0.45121 | 0.44572 | 0.446 | 0.44628 | 0.44655 | 0.44683 | 0.44711 | 0.44738 | 0.44766 | 0.44794 | 0.44821 | 0.44849 | 0.44876 | 27432.6704 | 4182.9743 | 178682.106 | 27245.713 | 964399.3565 | 964399.3565 | 3982709.1264 | 964399.3565
| CTN003-155024326 | 26 | CTN003 | CTN | North | 612724.481 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.021345 | 0.02157 | 0.021794 | 0.022019 | 0.022244 | 0.022288 | 0.022332 | 0.022376 | 0.02242 | 0.022464 | 0.022508 | 0.022552 | 0.022596 | 0.02264 | 0.022684 | 0.022728 | 0.022772 | 0.022816 | 0.02286 | 0.022904 | 0.00053821 | 0.00054638 | 0.00055208 | 0.00055342 | 0.00055132 | 0.00054646 | 0.00054832 | 0.0005494 | 0.00054345 | 0.00054452 | 0.00054558 | 0.00054665 | 0.00054772 | 0.00054879 | 0.00054985 | 0.00055092 | 0.00055199 | 0.00055305 | 0.00055412 | 0.00055519 | 27432.6704 | 4182.9743 | 217.5525 | 33.1727 | 19771.7107 | 19771.7107 | 612724.481 | 19771.7107
| CTN003-155024531 | 50 | CTN003 | CTN | North | 1178316.3096 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.033178 | 0.033517 | 0.033856 | 0.034196 | 0.034535 | 0.034585 | 0.034636 | 0.034686 | 0.034736 | 0.034787 | 0.034837 | 0.034887 | 0.034937 | 0.034988 | 0.035038 | 0.035088 | 0.035139 | 0.035189 | 0.035239 | 0.035289 | 0.00083658 | 0.00084903 | 0.00085763 | 0.00085947 | 0.00085597 | 0.00084797 | 0.00085041 | 0.00085165 | 0.00084199 | 0.00084321 | 0.00084443 | 0.00084565 | 0.00084687 | 0.00084808 | 0.0008493 | 0.00085052 | 0.00085174 | 0.00085296 | 0.00085418 | 0.0008554 | 27432.6704 | 4182.9743 | 336.9551 | 51.3794 | 45298.9905 | 45298.9905 | 1178316.3096 | 45298.9905
| CTN003-155024643 | 14 | CTN003 | CTN | North | 329928.5667 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27432.6704 | 4182.9743 | 0 | 0 | 0 | 0 | 329928.5667 | 0
| CTN003-155024758 | 70 | CTN003 | CTN | North | 1649642.8334 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.090938 | 0.091841 | 0.092743 | 0.093646 | 0.094549 | 0.094799 | 0.095049 | 0.095298 | 0.095548 | 0.095798 | 0.096048 | 0.096298 | 0.096548 | 0.096798 | 0.097048 | 0.097298 | 0.097548 | 0.097798 | 0.098048 | 0.098298 | 0.002293 | 0.0023264 | 0.0023493 | 0.0023537 | 0.0023434 | 0.0023243 | 0.0023337 | 0.0023399 | 0.002316 | 0.0023221 | 0.0023282 | 0.0023342 | 0.0023403 | 0.0023463 | 0.0023524 | 0.0023585 | 0.0023645 | 0.0023706 | 0.0023766 | 0.0023827 | 27432.6704 | 4182.9743 | 928.0988 | 141.5179 | 151398.6307 | 151398.6307 | 1649642.8334 | 151398.6307
| CTN003-155024899 | 60 | CTN003 | CTN | North | 1413979.5715 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.095547 | 0.096331 | 0.097114 | 0.097897 | 0.09868 | 0.099095 | 0.09951 | 0.099926 | 0.10034 | 0.10076 | 0.10117 | 0.10159 | 0.102 | 0.10242 | 0.10283 | 0.10325 | 0.10366 | 0.10408 | 0.10449 | 0.10491 | 0.0024092 | 0.0024402 | 0.00246 | 0.0024605 | 0.0024458 | 0.0024296 | 0.0024433 | 0.0024535 | 0.0024322 | 0.0024423 | 0.0024523 | 0.0024624 | 0.0024725 | 0.0024825 | 0.0024926 | 0.0025027 | 0.0025127 | 0.0025228 | 0.0025329 | 0.0025429 | 27432.6704 | 4182.9743 | 977.1584 | 148.9986 | 107873.3186 | 107873.3186 | 1413979.5715 | 107873.3186
| CTN003-155024988 | 49 | CTN003 | CTN | North | 1154749.9834 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.028229 | 0.028456 | 0.028683 | 0.02891 | 0.029137 | 0.029323 | 0.029509 | 0.029694 | 0.02988 | 0.030066 | 0.030252 | 0.030438 | 0.030623 | 0.030809 | 0.030995 | 0.031181 | 0.031367 | 0.031553 | 0.031738 | 0.031924 | 0.00071181 | 0.00072083 | 0.00072658 | 0.00072662 | 0.00072217 | 0.00071894 | 0.00072453 | 0.00072909 | 0.00072428 | 0.00072879 | 0.00073329 | 0.00073779 | 0.0007423 | 0.0007468 | 0.00075131 | 0.00075581 | 0.00076031 | 0.00076482 | 0.00076932 | 0.00077382 | 27432.6704 | 4182.9743 | 291.6068 | 44.4646 | 41631.458 | 41631.458 | 1154749.9834 | 41631.458
| CTN003-155025108 | 27 | CTN003 | CTN | North | 636290.8072 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.009166 | 0.0092468 | 0.0093275 | 0.0094083 | 0.0094891 | 0.0095239 | 0.0095587 | 0.0095935 | 0.0096283 | 0.0096632 | 0.009698 | 0.0097328 | 0.0097676 | 0.0098024 | 0.0098373 | 0.0098721 | 0.0099069 | 0.0099417 | 0.0099765 | 0.010011 | 0.00023112 | 0.00023423 | 0.00023628 | 0.00023647 | 0.00023519 | 0.00023351 | 0.0002347 | 0.00023555 | 0.00023339 | 0.00023423 | 0.00023507 | 0.00023592 | 0.00023676 | 0.00023761 | 0.00023845 | 0.00023929 | 0.00024014 | 0.00024098 | 0.00024183 | 0.00024267 | 27432.6704 | 4182.9743 | 93.6809 | 14.2846 | 17684.221 | 17684.221 | 636290.8072 | 17684.221
| CTN003-155025214 | 18 | CTN003 | CTN | North | 424193.8715 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.01894 | 0.019127 | 0.019315 | 0.019502 | 0.019689 | 0.019726 | 0.019763 | 0.0198 | 0.019836 | 0.019873 | 0.01991 | 0.019946 | 0.019983 | 0.02002 | 0.020056 | 0.020093 | 0.02013 | 0.020166 | 0.020203 | 0.02024 | 0.00047758 | 0.00048452 | 0.00048927 | 0.00049016 | 0.00048801 | 0.00048365 | 0.00048524 | 0.00048614 | 0.00048082 | 0.00048171 | 0.0004826 | 0.00048349 | 0.00048438 | 0.00048527 | 0.00048616 | 0.00048705 | 0.00048794 | 0.00048883 | 0.00048972 | 0.0004906 | 27432.6704 | 4182.9743 | 192.5358 | 29.3581 | 20189.7835 | 20189.7835 | 424193.8715 | 20189.7835
| CTN003-155025401 | 77 | CTN003 | CTN | North | 1814607.1168 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.13884 | 0.14 | 0.14116 | 0.14232 | 0.14348 | 0.14339 | 0.1433 | 0.1432 | 0.14311 | 0.14302 | 0.14293 | 0.14283 | 0.14274 | 0.14265 | 0.14255 | 0.14246 | 0.14237 | 0.14228 | 0.14218 | 0.14209 | 0.0035008 | 0.0035463 | 0.0035757 | 0.003577 | 0.0035562 | 0.0035156 | 0.0035184 | 0.0035161 | 0.0034689 | 0.0034667 | 0.0034644 | 0.0034622 | 0.0034599 | 0.0034577 | 0.0034554 | 0.0034532 | 0.003451 | 0.0034487 | 0.0034465 | 0.0034442 | 27432.6704 | 4182.9743 | 1386.9898 | 211.4903 | 124411.0396 | 124411.0396 | 1814607.1168 | 124411.0396
| CTN003-155052230 | 40 | CTN003 | CTN | North | 942653.0477 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.031302 | 0.031622 | 0.031943 | 0.032263 | 0.032583 | 0.032649 | 0.032715 | 0.032781 | 0.032846 | 0.032912 | 0.032978 | 0.033044 | 0.03311 | 0.033176 | 0.033242 | 0.033308 | 0.033374 | 0.03344 | 0.033506 | 0.033572 | 0.00078929 | 0.00080104 | 0.00080915 | 0.00081088 | 0.00080758 | 0.00080049 | 0.00080324 | 0.00080486 | 0.00079618 | 0.00079778 | 0.00079938 | 0.00080098 | 0.00080257 | 0.00080417 | 0.00080577 | 0.00080737 | 0.00080897 | 0.00081056 | 0.00081216 | 0.00081376 | 27432.6704 | 4182.9743 | 318.7996 | 48.611 | 55717.7526 | 55717.7526 | 942653.0477 | 55717.7526
| CTN003-155063034 | 55 | CTN003 | CTN | North | 1296147.9405 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.073846 | 0.074596 | 0.075347 | 0.076098 | 0.076848 | 0.077025 | 0.077202 | 0.077379 | 0.077556 | 0.077733 | 0.077909 | 0.078086 | 0.078263 | 0.07844 | 0.078617 | 0.078794 | 0.07897 | 0.079147 | 0.079324 | 0.079501 | 0.001862 | 0.0018896 | 0.0019086 | 0.0019126 | 0.0019047 | 0.0018885 | 0.0018956 | 0.0018999 | 0.0018799 | 0.0018842 | 0.0018885 | 0.0018928 | 0.0018971 | 0.0019013 | 0.0019056 | 0.0019099 | 0.0019142 | 0.0019185 | 0.0019228 | 0.0019271 | 27432.6704 | 4182.9743 | 752.9678 | 114.8137 | 90475.7658 | 90475.7658 | 1296147.9405 | 90475.7658
| CTN003-155063181 | 39 | CTN003 | CTN | North | 919086.7215 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.0042747 | 0.0043198 | 0.0043649 | 0.00441 | 0.0044551 | 0.0044671 | 0.004479 | 0.004491 | 0.0045029 | 0.0045149 | 0.0045269 | 0.0045388 | 0.0045508 | 0.0045627 | 0.0045747 | 0.0045866 | 0.0045986 | 0.0046105 | 0.0046225 | 0.0046345 | 0.00010779 | 0.00010943 | 0.00011057 | 0.00011084 | 0.00011042 | 0.00010953 | 0.00010997 | 0.00011027 | 0.00010915 | 0.00010944 | 0.00010973 | 0.00011002 | 0.00011031 | 0.0001106 | 0.00011089 | 0.00011118 | 0.00011147 | 0.00011176 | 0.00011205 | 0.00011234 | 27432.6704 | 4182.9743 | 43.7236 | 6.667 | 7451.041 | 7451.041 | 919086.7215 | 7451.041
| CTN003-155063369 | 67 | CTN003 | CTN | North | 1578943.8548 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.023883 | 0.024101 | 0.024319 | 0.024537 | 0.024755 | 0.024872 | 0.024989 | 0.025106 | 0.025223 | 0.02534 | 0.025457 | 0.025574 | 0.025691 | 0.025808 | 0.025925 | 0.026042 | 0.026159 | 0.026276 | 0.026393 | 0.02651 | 0.00060221 | 0.00061051 | 0.00061603 | 0.00061671 | 0.00061357 | 0.00060982 | 0.00061356 | 0.00061643 | 0.0006114 | 0.00061423 | 0.00061707 | 0.00061991 | 0.00062274 | 0.00062558 | 0.00062842 | 0.00063125 | 0.00063409 | 0.00063692 | 0.00063976 | 0.0006426 | 27432.6704 | 4182.9743 | 245.6119 | 37.4513 | 63922.5577 | 63922.5577 | 1578943.8548 | 63922.5577
| CTN003-155063514 | 14 | CTN003 | CTN | North | 329928.5667 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.002458 | 0.0024788 | 0.0024995 | 0.0025203 | 0.002541 | 0.0025518 | 0.0025626 | 0.0025734 | 0.0025842 | 0.0025949 | 0.0026057 | 0.0026165 | 0.0026273 | 0.0026381 | 0.0026489 | 0.0026597 | 0.0026705 | 0.0026813 | 0.0026921 | 0.0027028 | 6.1979e-05 | 6.279e-05 | 6.3316e-05 | 6.3344e-05 | 6.298e-05 | 6.2565e-05 | 6.2919e-05 | 6.3184e-05 | 6.2639e-05 | 6.29e-05 | 6.3162e-05 | 6.3423e-05 | 6.3685e-05 | 6.3946e-05 | 6.4208e-05 | 6.4469e-05 | 6.4731e-05 | 6.4992e-05 | 6.5254e-05 | 6.5515e-05 | 27432.6704 | 4182.9743 | 25.1626 | 3.8368 | 3078.7777 | 3078.7777 | 329928.5667 | 3078.7777
| CTN003-155063645 | 11 | CTN003 | CTN | North | 259229.5881 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.0043109 | 0.0043513 | 0.0043917 | 0.0044322 | 0.0044726 | 0.004488 | 0.0045035 | 0.0045189 | 0.0045344 | 0.0045498 | 0.0045653 | 0.0045807 | 0.0045962 | 0.0046116 | 0.0046271 | 0.0046425 | 0.004658 | 0.0046734 | 0.0046889 | 0.0047043 | 0.0001087 | 0.00011022 | 0.00011125 | 0.0001114 | 0.00011085 | 0.00011004 | 0.00011057 | 0.00011095 | 0.00010991 | 0.00011029 | 0.00011066 | 0.00011103 | 0.00011141 | 0.00011178 | 0.00011216 | 0.00011253 | 0.00011291 | 0.00011328 | 0.00011366 | 0.00011403 | 27432.6704 | 4182.9743 | 44.0936 | 6.7235 | 8477.6952 | 8477.6952 | 259229.5881 | 8477.6952
| CTN003-155063885 | 79 | CTN003 | CTN | North | 1861739.7692 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.23106 | 0.23339 | 0.23572 | 0.23804 | 0.24037 | 0.24128 | 0.2422 | 0.24311 | 0.24402 | 0.24493 | 0.24584 | 0.24676 | 0.24767 | 0.24858 | 0.24949 | 0.2504 | 0.25131 | 0.25223 | 0.25314 | 0.25405 | 0.0058261 | 0.005912 | 0.005971 | 0.005983 | 0.0059577 | 0.0059159 | 0.0059467 | 0.0059691 | 0.0059149 | 0.005937 | 0.0059591 | 0.0059812 | 0.0060033 | 0.0060254 | 0.0060475 | 0.0060696 | 0.0060917 | 0.0061138 | 0.0061359 | 0.006158 | 27432.6704 | 4182.9743 | 2372.6585 | 361.7865 | 297847.204 | 297847.204 | 1861739.7692 | 297847.204
| CTN003-155155512 | 94 | CTN003 | CTN | North | 2215234.662 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.061841 | 0.0623 | 0.06276 | 0.063219 | 0.063679 | 0.063965 | 0.064251 | 0.064536 | 0.064822 | 0.065108 | 0.065394 | 0.06568 | 0.065966 | 0.066251 | 0.066537 | 0.066823 | 0.067109 | 0.067395 | 0.067681 | 0.067966 | 0.0015593 | 0.0015781 | 0.0015898 | 0.0015889 | 0.0015783 | 0.0015683 | 0.0015776 | 0.0015846 | 0.0015713 | 0.0015782 | 0.0015851 | 0.001592 | 0.001599 | 0.0016059 | 0.0016128 | 0.0016198 | 0.0016267 | 0.0016336 | 0.0016405 | 0.0016475 | 27432.6704 | 4182.9743 | 631.7346 | 96.3278 | 76886.8684 | 76886.8684 | 2215234.662 | 76886.8684
| CTN003-155155602 | 31 | CTN003 | CTN | North | 730556.1119 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 2.0439e-05 | 2.0625e-05 | 2.081e-05 | 2.0995e-05 | 2.118e-05 | 2.1301e-05 | 2.1423e-05 | 2.1545e-05 | 2.1666e-05 | 2.1787e-05 | 2.1909e-05 | 2.203e-05 | 2.2152e-05 | 2.2273e-05 | 2.2395e-05 | 2.2516e-05 | 2.2638e-05 | 2.2759e-05 | 2.2881e-05 | 2.3002e-05 | 5.1538e-07 | 5.2245e-07 | 5.2714e-07 | 5.2768e-07 | 5.2495e-07 | 5.2228e-07 | 5.26e-07 | 5.2898e-07 | 5.2517e-07 | 5.2812e-07 | 5.3106e-07 | 5.3401e-07 | 5.3695e-07 | 5.399e-07 | 5.4284e-07 | 5.4579e-07 | 5.4873e-07 | 5.5168e-07 | 5.5462e-07 | 5.5757e-07 | 27432.6704 | 4182.9743 | 0.21118 | 0.032202 | 76.2956 | 76.2956 | 730556.1119 | 76.2956
| CTN003-155176630 | 58 | CTN003 | CTN | North | 1366846.9191 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.040313 | 0.040698 | 0.041082 | 0.041467 | 0.041851 | 0.041896 | 0.041941 | 0.041986 | 0.04203 | 0.042075 | 0.04212 | 0.042164 | 0.042209 | 0.042254 | 0.042299 | 0.042343 | 0.042388 | 0.042433 | 0.042477 | 0.042522 | 0.0010165 | 0.0010309 | 0.0010407 | 0.0010422 | 0.0010373 | 0.0010272 | 0.0010298 | 0.0010309 | 0.0010188 | 0.0010199 | 0.001021 | 0.001022 | 0.0010231 | 0.0010242 | 0.0010253 | 0.0010264 | 0.0010275 | 0.0010285 | 0.0010296 | 0.0010307 | 27432.6704 | 4182.9743 | 407.7306 | 62.1714 | 51660.0975 | 51660.0975 | 1366846.9191 | 51660.0975
| CTN003-155177865 | 24 | CTN003 | CTN | North | 565591.8286 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.0027739 | 0.0028017 | 0.0028295 | 0.0028573 | 0.0028851 | 0.0028893 | 0.0028934 | 0.0028976 | 0.0029017 | 0.0029058 | 0.00291 | 0.0029141 | 0.0029183 | 0.0029224 | 0.0029266 | 0.0029307 | 0.0029349 | 0.002939 | 0.0029431 | 0.0029473 | 6.9945e-05 | 7.0971e-05 | 7.1675e-05 | 7.1815e-05 | 7.1509e-05 | 7.084e-05 | 7.1042e-05 | 7.1144e-05 | 7.0336e-05 | 7.0436e-05 | 7.0537e-05 | 7.0637e-05 | 7.0738e-05 | 7.0838e-05 | 7.0939e-05 | 7.1039e-05 | 7.114e-05 | 7.124e-05 | 7.134e-05 | 7.1441e-05 | 27432.6704 | 4182.9743 | 28.1507 | 4.2925 | 4723.0041 | 4723.0041 | 565591.8286 | 4723.0041
| CTN003-155392598 | 36 | CTN003 | CTN | North | 848387.7429 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.014055 | 0.014207 | 0.01436 | 0.014512 | 0.014665 | 0.014661 | 0.014657 | 0.014653 | 0.014649 | 0.014645 | 0.014641 | 0.014637 | 0.014633 | 0.014629 | 0.014625 | 0.014621 | 0.014617 | 0.014613 | 0.014609 | 0.014605 | 0.00035439 | 0.00035989 | 0.00036375 | 0.00036475 | 0.00036348 | 0.00035946 | 0.00035988 | 0.00035978 | 0.00035508 | 0.00035499 | 0.00035489 | 0.00035479 | 0.00035469 | 0.0003546 | 0.0003545 | 0.0003544 | 0.0003543 | 0.00035421 | 0.00035411 | 0.00035401 | 27432.6704 | 4182.9743 | 141.8031 | 21.6224 | 25487.9938 | 25487.9938 | 848387.7429 | 25487.9938
| CTN003-155422079 | 107 | CTN003 | CTN | North | 2521596.9025 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.10946 | 0.11051 | 0.11157 | 0.11262 | 0.11368 | 0.11401 | 0.11434 | 0.11467 | 0.115 | 0.11532 | 0.11565 | 0.11598 | 0.11631 | 0.11664 | 0.11697 | 0.1173 | 0.11763 | 0.11796 | 0.11829 | 0.11861 | 0.00276 | 0.0027994 | 0.0028262 | 0.0028307 | 0.0028176 | 0.0027953 | 0.0028073 | 0.0028154 | 0.0027874 | 0.0027954 | 0.0028034 | 0.0028114 | 0.0028193 | 0.0028273 | 0.0028353 | 0.0028433 | 0.0028512 | 0.0028592 | 0.0028672 | 0.0028751 | 27432.6704 | 4182.9743 | 1117.4609 | 170.3921 | 170251.3816 | 170251.3816 | 2521596.9025 | 170251.3816
| CTN003-158006357 | 93 | CTN003 | CTN | North | 2191668.3358 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.95132 | 0.96147 | 0.97161 | 0.98176 | 0.99191 | 0.99395 | 0.99599 | 0.99804 | 1.0001 | 1.0021 | 1.0042 | 1.0062 | 1.0083 | 1.0103 | 1.0123 | 1.0144 | 1.0164 | 1.0185 | 1.0205 | 1.0226 | 0.023988 | 0.024355 | 0.024612 | 0.024675 | 0.024585 | 0.02437 | 0.024455 | 0.024505 | 0.024241 | 0.024291 | 0.024341 | 0.02439 | 0.02444 | 0.024489 | 0.024539 | 0.024588 | 0.024638 | 0.024687 | 0.024737 | 0.024786 | 27432.6704 | 4182.9743 | 9704.2518 | 1479.7187 | 76030.4486 | 76030.4486 | 2191668.3358 | 76030.4486
| CTN003-182897268 | 9 | CTN003 | CTN | North | 212096.9357 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27432.6704 | 4182.9743 | 0 | 0 | 0 | 0 | 212096.9357 | 0
| CTN003-24603160 | 273 | CTN003 | CTN | North | 6433607.0504 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 5.5397 | 5.574 | 5.6083 | 5.6426 | 5.6769 | 5.6777 | 5.6786 | 5.6795 | 5.6804 | 5.6813 | 5.6821 | 5.683 | 5.6839 | 5.6848 | 5.6857 | 5.6865 | 5.6874 | 5.6883 | 5.6892 | 5.6901 | 0.13968 | 0.1412 | 0.14207 | 0.14182 | 0.1407 | 0.13921 | 0.13943 | 0.13945 | 0.13769 | 0.13771 | 0.13773 | 0.13775 | 0.13777 | 0.1378 | 0.13782 | 0.13784 | 0.13786 | 0.13788 | 0.1379 | 0.13792 | 27432.6704 | 4182.9743 | 55173.0951 | 8412.8755 | 1585669.6522 | 1585669.6522 | 6433607.0504 | 1585669.6522
| CTN003-47810169 | 408 | CTN003 | CTN | North | 9615061.0862 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 6.9307 | 6.9867 | 7.0428 | 7.0988 | 7.1549 | 7.1677 | 7.1805 | 7.1933 | 7.2061 | 7.2189 | 7.2317 | 7.2445 | 7.2572 | 7.27 | 7.2828 | 7.2956 | 7.3084 | 7.3212 | 7.334 | 7.3468 | 0.17476 | 0.17698 | 0.1784 | 0.17842 | 0.17734 | 0.17574 | 0.1763 | 0.17662 | 0.17467 | 0.17498 | 0.17529 | 0.1756 | 0.17591 | 0.17622 | 0.17653 | 0.17684 | 0.17715 | 0.17746 | 0.17777 | 0.17808 | 27432.6704 | 4182.9743 | 70018.1298 | 10676.4685 | 2655847.5638 | 2655847.5638 | 9615061.0862 | 2655847.5638
| CTN003-88138723 | 98 | CTN003 | CTN | North | 2309499.9668 | 0.00090572 | 0.00090989 | 0.00090989 | 0.0009028 | 0.00089028 | 0.00088068 | 0.00088194 | 0.00088194 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.00087067 | 0.055552 | 0.056103 | 0.056654 | 0.057205 | 0.057757 | 0.057926 | 0.058096 | 0.058266 | 0.058436 | 0.058605 | 0.058775 | 0.058945 | 0.059115 | 0.059284 | 0.059454 | 0.059624 | 0.059794 | 0.059963 | 0.060133 | 0.060303 | 0.0014007 | 0.0014212 | 0.0014351 | 0.0014378 | 0.0014315 | 0.0014203 | 0.0014264 | 0.0014306 | 0.0014164 | 0.0014206 | 0.0014247 | 0.0014288 | 0.0014329 | 0.001437 | 0.0014411 | 0.0014453 | 0.0014494 | 0.0014535 | 0.0014576 | 0.0014617 | 27432.6704 | 4182.9743 | 567.7705 | 86.5745 | 108057.6582 | 108057.6582 | 2309499.9668 | 108057.6582
| CTN004-134372186 | 89 | CTN004 | CTN | North | 2097403.0311 | 0.0012528 | 0.0012437 | 0.001229 | 0.001212 | 0.0011922 | 0.0011775 | 0.0011696 | 0.0011616 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.16436 | 0.16567 | 0.16699 | 0.1683 | 0.16961 | 0.16985 | 0.1701 | 0.17034 | 0.17059 | 0.17084 | 0.17108 | 0.17133 | 0.17157 | 0.17182 | 0.17207 | 0.17231 | 0.17256 | 0.1728 | 0.17305 | 0.1733 | 0.0057326 | 0.0057362 | 0.0057135 | 0.0056785 | 0.0056292 | 0.005568 | 0.0055386 | 0.005509 | 0.0054285 | 0.0054363 | 0.0054441 | 0.005452 | 0.0054598 | 0.0054676 | 0.0054754 | 0.0054833 | 0.0054911 | 0.0054989 | 0.0055067 | 0.0055146 | 27432.6704 | 4182.9743 | 2202.8374 | 335.8919 | 128871.7918 | 128871.7918 | 2097403.0311 | 128871.7918
| CTN004-134372435 | 46 | CTN004 | CTN | North | 1084051.0048 | 0.0012528 | 0.0012437 | 0.001229 | 0.001212 | 0.0011922 | 0.0011775 | 0.0011696 | 0.0011616 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.10518 | 0.10606 | 0.10693 | 0.1078 | 0.10867 | 0.10877 | 0.10887 | 0.10897 | 0.10907 | 0.10917 | 0.10927 | 0.10937 | 0.10947 | 0.10957 | 0.10967 | 0.10977 | 0.10987 | 0.10997 | 0.11007 | 0.11017 | 0.0036685 | 0.003672 | 0.0036586 | 0.0036373 | 0.0036068 | 0.0035657 | 0.003545 | 0.0035242 | 0.0034708 | 0.003474 | 0.0034772 | 0.0034803 | 0.0034835 | 0.0034867 | 0.0034898 | 0.003493 | 0.0034962 | 0.0034993 | 0.0035025 | 0.0035057 | 27432.6704 | 4182.9743 | 1407.4581 | 214.6113 | 70925.6971 | 70925.6971 | 1084051.0048 | 70925.6971
| CTN004-15418536 | 266 | CTN004 | CTN | North | 6268642.767 | 0.0012528 | 0.0012437 | 0.001229 | 0.001212 | 0.0011922 | 0.0011775 | 0.0011696 | 0.0011616 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 71.1466 | 71.5681 | 71.9897 | 72.4112 | 72.8328 | 72.8872 | 72.9416 | 72.996 | 73.0504 | 73.1048 | 73.1592 | 73.2136 | 73.2681 | 73.3225 | 73.3769 | 73.4313 | 73.4857 | 73.5401 | 73.5945 | 73.649 | 2.4814 | 2.4779 | 2.4632 | 2.4432 | 2.4173 | 2.3893 | 2.375 | 2.3607 | 2.3246 | 2.3263 | 2.3281 | 2.3298 | 2.3315 | 2.3333 | 2.335 | 2.3367 | 2.3385 | 2.3402 | 2.3419 | 2.3436 | 27432.6704 | 4182.9743 | 943970.4406 | 143938.0153 | 5317182.6616 | 5317182.6616 | 6268642.767 | 5317182.6616
| CTN004-15418547 | 0 | CTN004 | CTN | North | 0 | 0.0012528 | 0.0012437 | 0.001229 | 0.001212 | 0.0011922 | 0.0011775 | 0.0011696 | 0.0011616 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27432.6704 | 4182.9743 | 0 | 0 | 0 | 0 | 0 | 0
| CTN004-155091767 | 20 | CTN004 | CTN | North | 471326.5238 | 0.0012528 | 0.0012437 | 0.001229 | 0.001212 | 0.0011922 | 0.0011775 | 0.0011696 | 0.0011616 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.036433 | 0.036706 | 0.036979 | 0.037252 | 0.037525 | 0.037599 | 0.037673 | 0.037748 | 0.037822 | 0.037896 | 0.037971 | 0.038045 | 0.038119 | 0.038193 | 0.038268 | 0.038342 | 0.038416 | 0.038491 | 0.038565 | 0.038639 | 0.0012707 | 0.0012709 | 0.0012653 | 0.0012569 | 0.0012454 | 0.0012326 | 0.0012267 | 0.0012208 | 0.0012036 | 0.0012059 | 0.0012083 | 0.0012107 | 0.001213 | 0.0012154 | 0.0012177 | 0.0012201 | 0.0012225 | 0.0012248 | 0.0012272 | 0.0012296 | 27432.6704 | 4182.9743 | 488.7855 | 74.5307 | 21420.6873 | 21420.6873 | 471326.5238 | 21420.6873
| CTN004-155091935 | 50 | CTN004 | CTN | North | 1178316.3096 | 0.0012528 | 0.0012437 | 0.001229 | 0.001212 | 0.0011922 | 0.0011775 | 0.0011696 | 0.0011616 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.059629 | 0.060133 | 0.060637 | 0.061142 | 0.061646 | 0.061716 | 0.061786 | 0.061856 | 0.061926 | 0.061996 | 0.062066 | 0.062136 | 0.062206 | 0.062277 | 0.062347 | 0.062417 | 0.062487 | 0.062557 | 0.062627 | 0.062697 | 0.0020797 | 0.002082 | 0.0020747 | 0.002063 | 0.002046 | 0.0020231 | 0.0020118 | 0.0020004 | 0.0019706 | 0.0019728 | 0.0019751 | 0.0019773 | 0.0019795 | 0.0019818 | 0.001984 | 0.0019862 | 0.0019884 | 0.0019907 | 0.0019929 | 0.0019951 | 27432.6704 | 4182.9743 | 799.1753 | 121.8594 | 45679.384 | 45679.384 | 1178316.3096 | 45679.384
| CTN004-155092023 | 17 | CTN004 | CTN | North | 400627.5453 | 0.0012528 | 0.0012437 | 0.001229 | 0.001212 | 0.0011922 | 0.0011775 | 0.0011696 | 0.0011616 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.036735 | 0.037026 | 0.037317 | 0.037608 | 0.037899 | 0.03795 | 0.038002 | 0.038054 | 0.038105 | 0.038157 | 0.038209 | 0.03826 | 0.038312 | 0.038364 | 0.038416 | 0.038467 | 0.038519 | 0.038571 | 0.038622 | 0.038674 | 0.0012812 | 0.001282 | 0.0012768 | 0.0012689 | 0.0012578 | 0.0012441 | 0.0012374 | 0.0012307 | 0.0012126 | 0.0012142 | 0.0012159 | 0.0012175 | 0.0012192 | 0.0012208 | 0.0012225 | 0.0012241 | 0.0012257 | 0.0012274 | 0.001229 | 0.0012307 | 27432.6704 | 4182.9743 | 492.0365 | 75.0265 | 24436.7623 | 24436.7623 | 400627.5453 | 24436.7623
| CTN004-155092123 | 34 | CTN004 | CTN | North | 801255.0905 | 0.0012528 | 0.0012437 | 0.001229 | 0.001212 | 0.0011922 | 0.0011775 | 0.0011696 | 0.0011616 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.18212 | 0.18343 | 0.18474 | 0.18605 | 0.18736 | 0.18737 | 0.18737 | 0.18738 | 0.18738 | 0.18739 | 0.1874 | 0.1874 | 0.18741 | 0.18741 | 0.18742 | 0.18742 | 0.18743 | 0.18744 | 0.18744 | 0.18745 | 0.0063519 | 0.006351 | 0.006321 | 0.0062775 | 0.0062184 | 0.0061421 | 0.006101 | 0.0060599 | 0.0059629 | 0.0059631 | 0.0059633 | 0.0059635 | 0.0059636 | 0.0059638 | 0.005964 | 0.0059642 | 0.0059644 | 0.0059646 | 0.0059648 | 0.005965 | 27432.6704 | 4182.9743 | 2417.7917 | 368.6685 | 86439.8979 | 86439.8979 | 801255.0905 | 86439.8979
| CTN004-160370806 | 0 | CTN004 | CTN | North | 0 | 0.0012528 | 0.0012437 | 0.001229 | 0.001212 | 0.0011922 | 0.0011775 | 0.0011696 | 0.0011616 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0.001143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27432.6704 | 4182.9743 | 0 | 0 | 0 | 0 | 0 | 0
| CTN005-15418323 | 94 | CTN005 | CTN | North | 2215234.662 | 0.001132 | 0.001132 | 0.0011243 | 0.0011089 | 0.0010934 | 0.001078 | 0.0010703 | 0.0010625 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 4.5515 | 4.5748 | 4.598 | 4.6212 | 4.6445 | 4.6466 | 4.6487 | 4.6508 | 4.653 | 4.6551 | 4.6572 | 4.6593 | 4.6615 | 4.6636 | 4.6657 | 4.6678 | 4.67 | 4.6721 | 4.6742 | 4.6764 | 0.14345 | 0.14418 | 0.14392 | 0.14266 | 0.14138 | 0.13945 | 0.13851 | 0.13758 | 0.13564 | 0.1357 | 0.13576 | 0.13583 | 0.13589 | 0.13595 | 0.13601 | 0.13607 | 0.13614 | 0.1362 | 0.13626 | 0.13632 | 27432.6704 | 4182.9743 | 55003.8831 | 8387.0738 | 229344.1089 | 229344.1089 | 2215234.662 | 229344.1089
| CTN006-100525030 | 45 | CTN006 | CTN | North | 1060484.6786 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.11302 | 0.11378 | 0.11453 | 0.11529 | 0.11604 | 0.11606 | 0.11608 | 0.1161 | 0.11612 | 0.11614 | 0.11615 | 0.11617 | 0.11619 | 0.11621 | 0.11623 | 0.11625 | 0.11627 | 0.11629 | 0.1163 | 0.11632 | 0.0050464 | 0.0050616 | 0.0050628 | 0.0050416 | 0.0049902 | 0.0049229 | 0.0048991 | 0.0048835 | 0.0048162 | 0.004817 | 0.0048178 | 0.0048186 | 0.0048193 | 0.0048201 | 0.0048209 | 0.0048217 | 0.0048224 | 0.0048232 | 0.004824 | 0.0048248 | 27432.6704 | 4182.9743 | 1945.2005 | 296.6071 | 44329.331 | 44329.331 | 1060484.6786 | 44329.331
| CTN006-123737136 | 38 | CTN006 | CTN | North | 895520.3953 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.17358 | 0.1747 | 0.17583 | 0.17695 | 0.17807 | 0.17814 | 0.17821 | 0.17827 | 0.17834 | 0.17841 | 0.17848 | 0.17854 | 0.17861 | 0.17868 | 0.17875 | 0.17881 | 0.17888 | 0.17895 | 0.17901 | 0.17908 | 0.0077501 | 0.0077719 | 0.0077722 | 0.0077381 | 0.0076576 | 0.0075561 | 0.0075212 | 0.0074989 | 0.0073972 | 0.0074 | 0.0074027 | 0.0074055 | 0.0074083 | 0.0074111 | 0.0074139 | 0.0074167 | 0.0074195 | 0.0074223 | 0.0074251 | 0.0074279 | 27432.6704 | 4182.9743 | 2988.6015 | 455.7064 | 16337.4421 | 16337.4421 | 895520.3953 | 16337.4421
| CTN006-138230928 | 78 | CTN006 | CTN | North | 1838173.443 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.084043 | 0.084675 | 0.085308 | 0.085941 | 0.086574 | 0.086668 | 0.086763 | 0.086858 | 0.086953 | 0.087048 | 0.087143 | 0.087238 | 0.087333 | 0.087428 | 0.087523 | 0.087618 | 0.087713 | 0.087808 | 0.087903 | 0.087998 | 0.0037524 | 0.0037669 | 0.0037709 | 0.0037582 | 0.0037229 | 0.0036762 | 0.0036618 | 0.0036536 | 0.0036066 | 0.0036105 | 0.0036145 | 0.0036184 | 0.0036224 | 0.0036263 | 0.0036302 | 0.0036342 | 0.0036381 | 0.003642 | 0.003646 | 0.0036499 | 27432.6704 | 4182.9743 | 1457.1121 | 222.1826 | 109646.837 | 109646.837 | 1838173.443 | 109646.837
| CTN006-15418599 | 17 | CTN006 | CTN | North | 400627.5453 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0012676 | 0.001281 | 0.0012944 | 0.0013078 | 0.0013213 | 0.0013253 | 0.0013294 | 0.0013334 | 0.0013375 | 0.0013415 | 0.0013456 | 0.0013496 | 0.0013537 | 0.0013577 | 0.0013618 | 0.0013658 | 0.0013699 | 0.0013739 | 0.001378 | 0.001382 | 5.6594e-05 | 5.6986e-05 | 5.7218e-05 | 5.7193e-05 | 5.6819e-05 | 5.6216e-05 | 5.6106e-05 | 5.6089e-05 | 5.5475e-05 | 5.5643e-05 | 5.5811e-05 | 5.5979e-05 | 5.6147e-05 | 5.6315e-05 | 5.6483e-05 | 5.665e-05 | 5.6818e-05 | 5.6986e-05 | 5.7154e-05 | 5.7322e-05 | 27432.6704 | 4182.9743 | 22.4096 | 3.417 | 110.8079 | 110.8079 | 400627.5453 | 110.8079
| CTN006-154972740 | 59 | CTN006 | CTN | North | 1390413.2453 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.051395 | 0.051809 | 0.052222 | 0.052636 | 0.05305 | 0.053028 | 0.053005 | 0.052983 | 0.052961 | 0.052939 | 0.052917 | 0.052895 | 0.052872 | 0.05285 | 0.052828 | 0.052806 | 0.052784 | 0.052762 | 0.052739 | 0.052717 | 0.0022947 | 0.0023048 | 0.0023084 | 0.0023018 | 0.0022813 | 0.0022493 | 0.0022371 | 0.0022287 | 0.0021967 | 0.0021958 | 0.0021949 | 0.0021939 | 0.002193 | 0.0021921 | 0.0021912 | 0.0021903 | 0.0021893 | 0.0021884 | 0.0021875 | 0.0021866 | 27432.6704 | 4182.9743 | 885.9289 | 135.0878 | 44116.9154 | 44116.9154 | 1390413.2453 | 44116.9154
| CTN006-154972844 | 9 | CTN006 | CTN | North | 212096.9357 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 1.1106e-05 | 1.123e-05 | 1.1353e-05 | 1.1477e-05 | 1.16e-05 | 1.1612e-05 | 1.1624e-05 | 1.1636e-05 | 1.1648e-05 | 1.166e-05 | 1.1672e-05 | 1.1684e-05 | 1.1696e-05 | 1.1708e-05 | 1.172e-05 | 1.1732e-05 | 1.1744e-05 | 1.1756e-05 | 1.1768e-05 | 1.178e-05 | 4.9588e-07 | 4.9957e-07 | 5.0185e-07 | 5.0188e-07 | 4.9883e-07 | 4.9254e-07 | 4.9059e-07 | 4.8945e-07 | 4.8313e-07 | 4.8363e-07 | 4.8413e-07 | 4.8462e-07 | 4.8512e-07 | 4.8562e-07 | 4.8612e-07 | 4.8661e-07 | 4.8711e-07 | 4.8761e-07 | 4.8811e-07 | 4.886e-07 | 27432.6704 | 4182.9743 | 0.19473 | 0.029693 | 8.8775 | 8.8775 | 212096.9357 | 8.8775
| CTN006-154972931 | 107 | CTN006 | CTN | North | 2521596.9025 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.1336 | 0.13485 | 0.1361 | 0.13736 | 0.13861 | 0.13874 | 0.13887 | 0.139 | 0.13913 | 0.13925 | 0.13938 | 0.13951 | 0.13964 | 0.13977 | 0.1399 | 0.14003 | 0.14016 | 0.14029 | 0.14042 | 0.14055 | 0.005965 | 0.005999 | 0.0060163 | 0.0060066 | 0.0059605 | 0.0058848 | 0.0058609 | 0.0058467 | 0.0057706 | 0.0057759 | 0.0057813 | 0.0057867 | 0.0057921 | 0.0057974 | 0.0058028 | 0.0058082 | 0.0058135 | 0.0058189 | 0.0058243 | 0.0058296 | 27432.6704 | 4182.9743 | 2328.2592 | 355.0164 | 210304.1555 | 210304.1555 | 2521596.9025 | 210304.1555
| CTN006-154973045 | 49 | CTN006 | CTN | North | 1154749.9834 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.042373 | 0.042829 | 0.043286 | 0.043742 | 0.044199 | 0.044192 | 0.044185 | 0.044178 | 0.044171 | 0.044164 | 0.044157 | 0.04415 | 0.044143 | 0.044136 | 0.044129 | 0.044122 | 0.044115 | 0.044108 | 0.044101 | 0.044094 | 0.0018919 | 0.0019053 | 0.0019134 | 0.0019129 | 0.0019007 | 0.0018745 | 0.0018648 | 0.0018583 | 0.0018321 | 0.0018318 | 0.0018315 | 0.0018312 | 0.0018309 | 0.0018307 | 0.0018304 | 0.0018301 | 0.0018298 | 0.0018295 | 0.0018292 | 0.0018289 | 27432.6704 | 4182.9743 | 737.7724 | 112.4966 | 81374.4544 | 81374.4544 | 1154749.9834 | 81374.4544
| CTN006-155015964 | 48 | CTN006 | CTN | North | 1131183.6572 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.024775 | 0.024948 | 0.025121 | 0.025294 | 0.025467 | 0.025479 | 0.02549 | 0.025502 | 0.025514 | 0.025525 | 0.025537 | 0.025549 | 0.02556 | 0.025572 | 0.025584 | 0.025595 | 0.025607 | 0.025619 | 0.02563 | 0.025642 | 0.0011061 | 0.0011098 | 0.0011104 | 0.0011061 | 0.0010952 | 0.0010807 | 0.0010758 | 0.0010727 | 0.0010582 | 0.0010587 | 0.0010592 | 0.0010597 | 0.0010602 | 0.0010607 | 0.0010611 | 0.0010616 | 0.0010621 | 0.0010626 | 0.0010631 | 0.0010636 | 27432.6704 | 4182.9743 | 427.4394 | 65.1766 | 18892.3079 | 18892.3079 | 1131183.6572 | 18892.3079
| CTN006-155016184 | 23 | CTN006 | CTN | North | 542025.5024 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.00074391 | 0.00074551 | 0.00074711 | 0.0007487 | 0.0007503 | 0.00074977 | 0.00074924 | 0.00074872 | 0.00074819 | 0.00074766 | 0.00074713 | 0.0007466 | 0.00074607 | 0.00074554 | 0.00074501 | 0.00074448 | 0.00074396 | 0.00074343 | 0.0007429 | 0.00074237 | 3.3215e-05 | 3.3165e-05 | 3.3025e-05 | 3.2741e-05 | 3.2265e-05 | 3.1803e-05 | 3.1622e-05 | 3.1494e-05 | 3.1033e-05 | 3.1011e-05 | 3.0989e-05 | 3.0967e-05 | 3.0945e-05 | 3.0923e-05 | 3.0901e-05 | 3.0879e-05 | 3.0857e-05 | 3.0835e-05 | 3.0814e-05 | 3.0792e-05 | 27432.6704 | 4182.9743 | 12.5615 | 1.9154 | 835.8824 | 835.8824 | 542025.5024 | 835.8824
| CTN006-155016351 | 37 | CTN006 | CTN | North | 871954.0691 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.00011128 | 0.00011246 | 0.00011364 | 0.00011482 | 0.000116 | 0.00011636 | 0.00011672 | 0.00011708 | 0.00011744 | 0.0001178 | 0.00011816 | 0.00011852 | 0.00011888 | 0.00011924 | 0.0001196 | 0.00011996 | 0.00012032 | 0.00012068 | 0.00012104 | 0.0001214 | 4.9686e-06 | 5.003e-06 | 5.0233e-06 | 5.0212e-06 | 4.9883e-06 | 4.9356e-06 | 4.9262e-06 | 4.9248e-06 | 4.8711e-06 | 4.886e-06 | 4.901e-06 | 4.9159e-06 | 4.9308e-06 | 4.9458e-06 | 4.9607e-06 | 4.9756e-06 | 4.9906e-06 | 5.0055e-06 | 5.0204e-06 | 5.0354e-06 | 27432.6704 | 4182.9743 | 1.9678 | 0.30005 | 184.4375 | 184.4375 | 871954.0691 | 184.4375
| CTN006-155016482 | 73 | CTN006 | CTN | North | 1720341.812 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.23799 | 0.24 | 0.242 | 0.24401 | 0.24601 | 0.24615 | 0.2463 | 0.24644 | 0.24659 | 0.24673 | 0.24687 | 0.24702 | 0.24716 | 0.2473 | 0.24745 | 0.24759 | 0.24773 | 0.24788 | 0.24802 | 0.24816 | 0.010626 | 0.010677 | 0.010697 | 0.010671 | 0.010579 | 0.010441 | 0.010395 | 0.010366 | 0.010228 | 0.010234 | 0.01024 | 0.010246 | 0.010252 | 0.010257 | 0.010263 | 0.010269 | 0.010275 | 0.010281 | 0.010287 | 0.010293 | 27432.6704 | 4182.9743 | 4127.7513 | 629.4057 | 169570.3377 | 169570.3377 | 1720341.812 | 169570.3377
| CTN006-155018538 | 39 | CTN006 | CTN | North | 919086.7215 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.052714 | 0.053174 | 0.053634 | 0.054094 | 0.054555 | 0.054655 | 0.054756 | 0.054856 | 0.054957 | 0.055057 | 0.055158 | 0.055259 | 0.055359 | 0.05546 | 0.05556 | 0.055661 | 0.055762 | 0.055862 | 0.055963 | 0.056063 | 0.0023536 | 0.0023655 | 0.0023708 | 0.0023656 | 0.002346 | 0.0023183 | 0.002311 | 0.0023075 | 0.0022795 | 0.0022836 | 0.0022878 | 0.002292 | 0.0022962 | 0.0023003 | 0.0023045 | 0.0023087 | 0.0023128 | 0.002317 | 0.0023212 | 0.0023254 | 27432.6704 | 4182.9743 | 920.8609 | 140.4142 | 60639.307 | 60639.307 | 919086.7215 | 60639.307
| CTN006-155018674 | 21 | CTN006 | CTN | North | 494892.85 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.059745 | 0.060129 | 0.060514 | 0.060898 | 0.061283 | 0.061308 | 0.061333 | 0.061359 | 0.061384 | 0.061409 | 0.061434 | 0.061459 | 0.061485 | 0.06151 | 0.061535 | 0.06156 | 0.061585 | 0.06161 | 0.061636 | 0.061661 | 0.0026675 | 0.0026749 | 0.0026749 | 0.0026631 | 0.0026354 | 0.0026005 | 0.0025886 | 0.002581 | 0.002546 | 0.0025471 | 0.0025481 | 0.0025492 | 0.0025502 | 0.0025513 | 0.0025523 | 0.0025534 | 0.0025544 | 0.0025554 | 0.0025565 | 0.0025575 | 27432.6704 | 4182.9743 | 1028.7067 | 156.8587 | 33662.7927 | 33662.7927 | 494892.85 | 33662.7927
| CTN006-155018773 | 93 | CTN006 | CTN | North | 2191668.3358 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.069789 | 0.070424 | 0.071059 | 0.071694 | 0.072329 | 0.072355 | 0.072381 | 0.072407 | 0.072432 | 0.072458 | 0.072484 | 0.07251 | 0.072535 | 0.072561 | 0.072587 | 0.072613 | 0.072639 | 0.072664 | 0.07269 | 0.072716 | 0.003116 | 0.0031329 | 0.0031411 | 0.0031352 | 0.0031104 | 0.0030691 | 0.0030548 | 0.0030457 | 0.0030043 | 0.0030054 | 0.0030065 | 0.0030075 | 0.0030086 | 0.0030097 | 0.0030107 | 0.0030118 | 0.0030129 | 0.0030139 | 0.003015 | 0.0030161 | 27432.6704 | 4182.9743 | 1211.7049 | 184.7626 | 99258.1845 | 99258.1845 | 2191668.3358 | 99258.1845
| CTN006-155018968 | 40 | CTN006 | CTN | North | 942653.0477 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0001329 | 0.0001345 | 0.0001361 | 0.0001377 | 0.0001393 | 0.00013944 | 0.00013958 | 0.00013972 | 0.00013986 | 0.00014 | 0.00014014 | 0.00014028 | 0.00014042 | 0.00014056 | 0.0001407 | 0.00014084 | 0.00014098 | 0.00014112 | 0.00014126 | 0.0001414 | 5.9338e-06 | 5.9834e-06 | 6.0161e-06 | 6.0217e-06 | 5.9903e-06 | 5.9146e-06 | 5.891e-06 | 5.8771e-06 | 5.801e-06 | 5.8069e-06 | 5.8127e-06 | 5.8185e-06 | 5.8243e-06 | 5.8301e-06 | 5.8359e-06 | 5.8417e-06 | 5.8475e-06 | 5.8533e-06 | 5.8591e-06 | 5.8649e-06 | 27432.6704 | 4182.9743 | 2.3368 | 0.35631 | 270.5547 | 270.5547 | 942653.0477 | 270.5547
| CTN006-155019123 | 65 | CTN006 | CTN | North | 1531811.2025 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.067699 | 0.068222 | 0.068745 | 0.069269 | 0.069792 | 0.06986 | 0.069928 | 0.069996 | 0.070063 | 0.070131 | 0.070199 | 0.070267 | 0.070335 | 0.070402 | 0.07047 | 0.070538 | 0.070606 | 0.070673 | 0.070741 | 0.070809 | 0.0030226 | 0.0030349 | 0.0030388 | 0.0030292 | 0.0030013 | 0.0029632 | 0.0029513 | 0.0029443 | 0.0029061 | 0.0029089 | 0.0029117 | 0.0029145 | 0.0029173 | 0.0029201 | 0.0029229 | 0.0029257 | 0.0029285 | 0.0029314 | 0.0029342 | 0.002937 | 27432.6704 | 4182.9743 | 1173.7893 | 178.9811 | 81353.2024 | 81353.2024 | 1531811.2025 | 81353.2024
| CTN006-155062010 | 62 | CTN006 | CTN | North | 1461112.2239 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.048869 | 0.04931 | 0.049751 | 0.050191 | 0.050632 | 0.05066 | 0.050688 | 0.050715 | 0.050743 | 0.050771 | 0.050799 | 0.050826 | 0.050854 | 0.050882 | 0.05091 | 0.050937 | 0.050965 | 0.050993 | 0.051021 | 0.051048 | 0.0021819 | 0.0021936 | 0.0021992 | 0.0021949 | 0.0021773 | 0.0021488 | 0.0021393 | 0.0021333 | 0.0021047 | 0.0021058 | 0.002107 | 0.0021082 | 0.0021093 | 0.0021105 | 0.0021116 | 0.0021128 | 0.0021139 | 0.0021151 | 0.0021162 | 0.0021174 | 27432.6704 | 4182.9743 | 849.0686 | 129.4672 | 41018.8169 | 41018.8169 | 1461112.2239 | 41018.8169
| CTN006-155062651 | 135 | CTN006 | CTN | North | 3181454.0359 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.16123 | 0.16266 | 0.16408 | 0.16551 | 0.16693 | 0.16694 | 0.16695 | 0.16696 | 0.16697 | 0.16698 | 0.16699 | 0.167 | 0.16701 | 0.16702 | 0.16703 | 0.16704 | 0.16705 | 0.16706 | 0.16706 | 0.16707 | 0.0071988 | 0.007236 | 0.0072531 | 0.0072378 | 0.0071787 | 0.0070812 | 0.0070462 | 0.007023 | 0.0069256 | 0.0069259 | 0.0069263 | 0.0069267 | 0.0069271 | 0.0069275 | 0.0069279 | 0.0069283 | 0.0069286 | 0.006929 | 0.0069294 | 0.0069298 | 27432.6704 | 4182.9743 | 2792.8995 | 425.8655 | 201003.1292 | 201003.1292 | 3181454.0359 | 201003.1292
| CTN006-155077957 | 84 | CTN006 | CTN | North | 1979571.4001 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.092645 | 0.093409 | 0.094172 | 0.094936 | 0.095699 | 0.095852 | 0.096004 | 0.096156 | 0.096309 | 0.096461 | 0.096614 | 0.096766 | 0.096919 | 0.097071 | 0.097223 | 0.097376 | 0.097528 | 0.097681 | 0.097833 | 0.097986 | 0.0041365 | 0.0041554 | 0.0041628 | 0.0041516 | 0.0041153 | 0.0040657 | 0.0040518 | 0.0040447 | 0.0039946 | 0.004001 | 0.0040073 | 0.0040136 | 0.0040199 | 0.0040263 | 0.0040326 | 0.0040389 | 0.0040452 | 0.0040516 | 0.0040579 | 0.0040642 | 27432.6704 | 4182.9743 | 1613.8893 | 246.0882 | 105642.5845 | 105642.5845 | 1979571.4001 | 105642.5845
| CTN006-155078265 | 36 | CTN006 | CTN | North | 848387.7429 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.00034018 | 0.00034424 | 0.00034829 | 0.00035235 | 0.0003564 | 0.00035651 | 0.00035662 | 0.00035673 | 0.00035684 | 0.00035695 | 0.00035706 | 0.00035717 | 0.00035728 | 0.00035739 | 0.0003575 | 0.00035761 | 0.00035772 | 0.00035783 | 0.00035794 | 0.00035805 | 1.5189e-05 | 1.5314e-05 | 1.5396e-05 | 1.5408e-05 | 1.5326e-05 | 1.5122e-05 | 1.5051e-05 | 1.5005e-05 | 1.4801e-05 | 1.4805e-05 | 1.481e-05 | 1.4815e-05 | 1.4819e-05 | 1.4824e-05 | 1.4828e-05 | 1.4833e-05 | 1.4837e-05 | 1.4842e-05 | 1.4846e-05 | 1.4851e-05 | 27432.6704 | 4182.9743 | 5.9585 | 0.90856 | 395.0897 | 395.0897 | 848387.7429 | 395.0897
| CTN006-155078364 | 68 | CTN006 | CTN | North | 1602510.181 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.061014 | 0.061667 | 0.06232 | 0.062973 | 0.063626 | 0.063665 | 0.063704 | 0.063743 | 0.063782 | 0.063821 | 0.06386 | 0.063899 | 0.063938 | 0.063978 | 0.064017 | 0.064056 | 0.064095 | 0.064134 | 0.064173 | 0.064212 | 0.0027242 | 0.0027433 | 0.0027548 | 0.0027538 | 0.0027361 | 0.0027005 | 0.0026886 | 0.0026813 | 0.0026455 | 0.0026472 | 0.0026488 | 0.0026504 | 0.002652 | 0.0026536 | 0.0026552 | 0.0026569 | 0.0026585 | 0.0026601 | 0.0026617 | 0.0026633 | 27432.6704 | 4182.9743 | 1066.1656 | 162.5705 | 112989.1054 | 112989.1054 | 1602510.181 | 112989.1054
| CTN006-155078558 | 74 | CTN006 | CTN | North | 1743908.1382 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.082003 | 0.082737 | 0.083471 | 0.084205 | 0.08494 | 0.084941 | 0.084942 | 0.084943 | 0.084945 | 0.084946 | 0.084947 | 0.084948 | 0.084949 | 0.084951 | 0.084952 | 0.084953 | 0.084954 | 0.084955 | 0.084957 | 0.084958 | 0.0036613 | 0.0036806 | 0.0036897 | 0.0036823 | 0.0036527 | 0.0036029 | 0.003585 | 0.003573 | 0.0035233 | 0.0035233 | 0.0035234 | 0.0035234 | 0.0035235 | 0.0035235 | 0.0035236 | 0.0035236 | 0.0035237 | 0.0035237 | 0.0035238 | 0.0035238 | 27432.6704 | 4182.9743 | 1420.6937 | 216.6295 | 106487.6021 | 106487.6021 | 1743908.1382 | 106487.6021
| CTN006-155078784 | 36 | CTN006 | CTN | North | 848387.7429 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.00045454 | 0.00045866 | 0.00046277 | 0.00046689 | 0.000471 | 0.00047165 | 0.0004723 | 0.00047295 | 0.0004736 | 0.00047425 | 0.0004749 | 0.00047555 | 0.0004762 | 0.00047685 | 0.0004775 | 0.00047815 | 0.0004788 | 0.00047945 | 0.0004801 | 0.00048075 | 2.0295e-05 | 2.0404e-05 | 2.0456e-05 | 2.0417e-05 | 2.0254e-05 | 2.0006e-05 | 1.9933e-05 | 1.9894e-05 | 1.9644e-05 | 1.9671e-05 | 1.9698e-05 | 1.9725e-05 | 1.9752e-05 | 1.9779e-05 | 1.9806e-05 | 1.9832e-05 | 1.9859e-05 | 1.9886e-05 | 1.9913e-05 | 1.994e-05 | 27432.6704 | 4182.9743 | 7.9306 | 1.2093 | 1156.9099 | 1156.9099 | 848387.7429 | 1156.9099
| CTN006-155078876 | 23 | CTN006 | CTN | North | 542025.5024 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 4.5906e-05 | 4.643e-05 | 4.6953e-05 | 4.7477e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 4.8e-05 | 2.0496e-06 | 2.0655e-06 | 2.0755e-06 | 2.0762e-06 | 2.0641e-06 | 2.036e-06 | 2.0258e-06 | 2.0191e-06 | 1.9909e-06 | 1.9909e-06 | 1.9909e-06 | 1.9909e-06 | 1.9909e-06 | 1.9909e-06 | 1.9909e-06 | 1.9909e-06 | 1.9909e-06 | 1.9909e-06 | 1.9909e-06 | 1.9909e-06 | 27432.6704 | 4182.9743 | 0.80153 | 0.12222 | 46.6858 | 46.6858 | 542025.5024 | 46.6858
| CTN006-155392437 | 89 | CTN006 | CTN | North | 2097403.0311 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.050011 | 0.050466 | 0.050921 | 0.051376 | 0.051831 | 0.051856 | 0.051882 | 0.051907 | 0.051933 | 0.051958 | 0.051984 | 0.05201 | 0.052035 | 0.052061 | 0.052086 | 0.052112 | 0.052137 | 0.052163 | 0.052188 | 0.052214 | 0.0022329 | 0.002245 | 0.0022509 | 0.0022467 | 0.0022289 | 0.0021996 | 0.0021897 | 0.0021834 | 0.002154 | 0.0021551 | 0.0021562 | 0.0021572 | 0.0021583 | 0.0021593 | 0.0021604 | 0.0021615 | 0.0021625 | 0.0021636 | 0.0021646 | 0.0021657 | 27432.6704 | 4182.9743 | 868.8896 | 132.4896 | 92156.5411 | 92156.5411 | 2097403.0311 | 92156.5411
| CTN006-157466480 | 90 | CTN006 | CTN | North | 2120969.3573 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.1882 | 0.18949 | 0.19078 | 0.19207 | 0.19336 | 0.19367 | 0.19397 | 0.19428 | 0.19458 | 0.19489 | 0.19519 | 0.1955 | 0.1958 | 0.1961 | 0.19641 | 0.19671 | 0.19702 | 0.19732 | 0.19763 | 0.19793 | 0.008403 | 0.0084298 | 0.0084333 | 0.0083994 | 0.0083152 | 0.0082148 | 0.0081866 | 0.008172 | 0.0080708 | 0.0080834 | 0.008096 | 0.0081087 | 0.0081213 | 0.0081339 | 0.0081466 | 0.0081592 | 0.0081719 | 0.0081845 | 0.0081971 | 0.0082098 | 27432.6704 | 4182.9743 | 3263.5612 | 497.6327 | 50337.6417 | 50337.6417 | 2120969.3573 | 50337.6417
| CTN006-157466735 | 172 | CTN006 | CTN | North | 4053408.105 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.26692 | 0.26881 | 0.2707 | 0.27259 | 0.27448 | 0.27465 | 0.27481 | 0.27498 | 0.27515 | 0.27532 | 0.27548 | 0.27565 | 0.27582 | 0.27599 | 0.27615 | 0.27632 | 0.27649 | 0.27666 | 0.27682 | 0.27699 | 0.011918 | 0.011958 | 0.011966 | 0.01192 | 0.011803 | 0.01165 | 0.011598 | 0.011567 | 0.011412 | 0.011419 | 0.011426 | 0.011433 | 0.01144 | 0.011447 | 0.011454 | 0.011461 | 0.011468 | 0.011475 | 0.011482 | 0.011489 | 27432.6704 | 4182.9743 | 4610.0394 | 702.9457 | 172600.1296 | 172600.1296 | 4053408.105 | 172600.1296
| CTN006-157466858 | 238 | CTN006 | CTN | North | 5608785.6336 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 8.9099 | 8.9762 | 9.0425 | 9.1088 | 9.1751 | 9.1873 | 9.1994 | 9.2115 | 9.2236 | 9.2357 | 9.2478 | 9.2599 | 9.2721 | 9.2842 | 9.2963 | 9.3084 | 9.3205 | 9.3326 | 9.3448 | 9.3569 | 0.39781 | 0.39932 | 0.39971 | 0.39833 | 0.39456 | 0.38969 | 0.38826 | 0.38747 | 0.38257 | 0.38307 | 0.38358 | 0.38408 | 0.38458 | 0.38508 | 0.38559 | 0.38609 | 0.38659 | 0.38709 | 0.3876 | 0.3881 | 27432.6704 | 4182.9743 | 154604.5258 | 23574.3278 | 764025.8823 | 764025.8823 | 5608785.6336 | 764025.8823
| CTN006-158006328 | 153 | CTN006 | CTN | North | 3605647.9073 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 6.4093 | 6.4551 | 6.5008 | 6.5466 | 6.5923 | 6.5918 | 6.5913 | 6.5909 | 6.5904 | 6.5899 | 6.5894 | 6.5889 | 6.5884 | 6.5879 | 6.5875 | 6.587 | 6.5865 | 6.586 | 6.5855 | 6.585 | 0.28617 | 0.28716 | 0.28736 | 0.28628 | 0.28349 | 0.2796 | 0.27819 | 0.27724 | 0.27335 | 0.27333 | 0.27331 | 0.27329 | 0.27327 | 0.27325 | 0.27323 | 0.27321 | 0.27319 | 0.27317 | 0.27315 | 0.27313 | 27432.6704 | 4182.9743 | 110344.5897 | 16825.507 | 469335.9699 | 469335.9699 | 3605647.9073 | 469335.9699
| CTN006-163924253 | 44 | CTN006 | CTN | North | 1036918.3524 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.05831 | 0.058655 | 0.059 | 0.059345 | 0.059691 | 0.059716 | 0.059742 | 0.059767 | 0.059793 | 0.059818 | 0.059844 | 0.059869 | 0.059895 | 0.05992 | 0.059946 | 0.059971 | 0.059997 | 0.060022 | 0.060048 | 0.060073 | 0.0026035 | 0.0026093 | 0.002608 | 0.0025952 | 0.0025669 | 0.002533 | 0.0025214 | 0.002514 | 0.00248 | 0.0024811 | 0.0024822 | 0.0024832 | 0.0024843 | 0.0024853 | 0.0024864 | 0.0024875 | 0.0024885 | 0.0024896 | 0.0024906 | 0.0024917 | 27432.6704 | 4182.9743 | 1002.3975 | 152.8471 | 49636.0003 | 49636.0003 | 1036918.3524 | 49636.0003
| CTN006-24603272 | 174 | CTN006 | CTN | North | 4100540.7574 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 3.7314 | 3.7558 | 3.7801 | 3.8045 | 3.8288 | 3.8312 | 3.8336 | 3.836 | 3.8384 | 3.8408 | 3.8432 | 3.8457 | 3.8481 | 3.8505 | 3.8529 | 3.8553 | 3.8577 | 3.8601 | 3.8625 | 3.8649 | 0.1666 | 0.16708 | 0.1671 | 0.16637 | 0.16465 | 0.16251 | 0.1618 | 0.16136 | 0.15921 | 0.15931 | 0.15941 | 0.15951 | 0.15961 | 0.15971 | 0.15981 | 0.15991 | 0.16001 | 0.16011 | 0.16021 | 0.16031 | 27432.6704 | 4182.9743 | 64336.2306 | 9810.084 | 499400.5442 | 499400.5442 | 4100540.7574 | 499400.5442
| CTN006-24605098 | 85 | CTN006 | CTN | North | 2003137.7263 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.45888 | 0.46295 | 0.46702 | 0.47109 | 0.47516 | 0.47574 | 0.47633 | 0.47691 | 0.4775 | 0.47808 | 0.47867 | 0.47926 | 0.47984 | 0.48043 | 0.48101 | 0.4816 | 0.48218 | 0.48277 | 0.48335 | 0.48394 | 0.020488 | 0.020595 | 0.020644 | 0.020601 | 0.020433 | 0.020179 | 0.020103 | 0.020061 | 0.019805 | 0.01983 | 0.019854 | 0.019878 | 0.019903 | 0.019927 | 0.019951 | 0.019975 | 0.02 | 0.020024 | 0.020048 | 0.020073 | 27432.6704 | 4182.9743 | 7995.7505 | 1219.2039 | 176224.5314 | 176224.5314 | 2003137.7263 | 176224.5314
| CTN006-24605334 | 148 | CTN006 | CTN | North | 3487816.2764 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 8.0592 | 8.1065 | 8.1538 | 8.2011 | 8.2484 | 8.2531 | 8.2577 | 8.2624 | 8.2671 | 8.2718 | 8.2764 | 8.2811 | 8.2858 | 8.2905 | 8.2951 | 8.2998 | 8.3045 | 8.3092 | 8.3138 | 8.3185 | 0.35983 | 0.36063 | 0.36043 | 0.35864 | 0.35471 | 0.35007 | 0.34852 | 0.34755 | 0.3429 | 0.34309 | 0.34329 | 0.34348 | 0.34367 | 0.34387 | 0.34406 | 0.34426 | 0.34445 | 0.34464 | 0.34484 | 0.34503 | 27432.6704 | 4182.9743 | 138616.7146 | 21136.4826 | 1013621.5005 | 1013621.5005 | 3487816.2764 | 1013621.5005
| CTN006-88333121 | 15 | CTN006 | CTN | North | 353494.8929 | 0.0016038 | 0.0015979 | 0.0015878 | 0.0015708 | 0.0015446 | 0.0015236 | 0.001516 | 0.0015109 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.0014899 | 0.011353 | 0.011452 | 0.01155 | 0.011649 | 0.011748 | 0.011763 | 0.011778 | 0.011793 | 0.011808 | 0.011823 | 0.011838 | 0.011854 | 0.011869 | 0.011884 | 0.011899 | 0.011914 | 0.011929 | 0.011944 | 0.01196 | 0.011975 | 0.00050691 | 0.00050945 | 0.00051057 | 0.00050941 | 0.00050518 | 0.00049893 | 0.00049708 | 0.00049606 | 0.00048977 | 0.0004904 | 0.00049103 | 0.00049166 | 0.00049228 | 0.00049291 | 0.00049354 | 0.00049417 | 0.0004948 | 0.00049543 | 0.00049605 | 0.00049668 | 27432.6704 | 4182.9743 | 197.7618 | 30.155 | 15025.3635 | 15025.3635 | 353494.8929 | 15025.3635
| DDL011-193014102 | 329 | DDL011 | DDL | South | 5981480.2823 | 0.0010839 | 0.0011125 | 0.0011377 | 0.0011623 | 0.0011805 | 0.0011976 | 0.0012374 | 0.0012852 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 35.4528 | 35.5094 | 35.5661 | 35.6228 | 35.6795 | 35.5566 | 35.4337 | 35.3109 | 35.188 | 35.0651 | 34.9422 | 34.8194 | 34.6965 | 34.5736 | 34.4508 | 34.3279 | 34.205 | 34.0822 | 33.9593 | 33.8364 | 1.0698 | 1.0998 | 1.1265 | 1.1527 | 1.1726 | 1.1855 | 1.2206 | 1.2634 | 1.2935 | 1.289 | 1.2845 | 1.2799 | 1.2754 | 1.2709 | 1.2664 | 1.2619 | 1.2574 | 1.2528 | 1.2483 | 1.2438 | 35130.2353 | 8191.5474 | 617398.4867 | 143962.8545 | 598694.749 | 776040.8028 | 6242212.7823 | 624791.8306
| DDL011-24612671 | 111 | DDL011 | DDL | South | 2018067.8156 | 0.0010839 | 0.0011125 | 0.0011377 | 0.0011623 | 0.0011805 | 0.0011976 | 0.0012374 | 0.0012852 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 0.0013204 | 1.0641 | 1.0658 | 1.0674 | 1.0691 | 1.0708 | 1.0672 | 1.0635 | 1.0599 | 1.0563 | 1.0527 | 1.0491 | 1.0455 | 1.0419 | 1.0383 | 1.0347 | 1.031 | 1.0274 | 1.0238 | 1.0202 | 1.0166 | 0.032111 | 0.033008 | 0.033808 | 0.034594 | 0.035189 | 0.035582 | 0.036638 | 0.037925 | 0.03883 | 0.038697 | 0.038565 | 0.038432 | 0.038299 | 0.038166 | 0.038034 | 0.037901 | 0.037768 | 0.037635 | 0.037503 | 0.03737 | 35130.2353 | 8191.5474 | 18536.1225 | 4322.1892 | 16621.3772 | 21544.9808 | 2106035.3156 | 17345.9024
| DDL012-193014212 | 314 | DDL012 | DDL | South | 5708768.4153 | 0.0011129 | 0.0011306 | 0.0011397 | 0.0011478 | 0.0011537 | 0.0011595 | 0.001173 | 0.0011911 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 15.3062 | 15.3964 | 15.4866 | 15.5768 | 15.667 | 15.7719 | 15.8768 | 15.9817 | 16.0866 | 16.1915 | 16.2964 | 16.4013 | 16.5062 | 16.6111 | 16.716 | 16.8209 | 16.9258 | 17.0307 | 17.1356 | 17.2405 | 0.47425 | 0.48459 | 0.49138 | 0.49776 | 0.50323 | 0.50914 | 0.51847 | 0.52994 | 0.54422 | 0.54777 | 0.55132 | 0.55487 | 0.55842 | 0.56197 | 0.56552 | 0.56907 | 0.57262 | 0.57616 | 0.57971 | 0.58326 | 35130.2353 | 8191.5474 | 270255.0625 | 63017.1454 | 324210.7337 | 420248.8137 | 5957613.4153 | 338343.0674
| DDL012-24612381 | 217 | DDL012 | DDL | South | 3945231.6755 | 0.0011129 | 0.0011306 | 0.0011397 | 0.0011478 | 0.0011537 | 0.0011595 | 0.001173 | 0.0011911 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.91166 | 0.91338 | 0.91511 | 0.91683 | 0.91856 | 0.91486 | 0.91116 | 0.90746 | 0.90376 | 0.90007 | 0.89637 | 0.89267 | 0.88897 | 0.88527 | 0.88157 | 0.87787 | 0.87417 | 0.87048 | 0.86678 | 0.86308 | 0.028247 | 0.028748 | 0.029036 | 0.029298 | 0.029504 | 0.029533 | 0.029755 | 0.030091 | 0.030575 | 0.03045 | 0.030325 | 0.0302 | 0.030075 | 0.029949 | 0.029824 | 0.029699 | 0.029574 | 0.029449 | 0.029324 | 0.029199 | 35130.2353 | 8191.5474 | 15034.0157 | 3505.5801 | 19110.6938 | 24771.6858 | 4117204.1755 | 19943.7283
| DDL012-24612395 | 140 | DDL012 | DDL | South | 2545310.7584 | 0.0011129 | 0.0011306 | 0.0011397 | 0.0011478 | 0.0011537 | 0.0011595 | 0.001173 | 0.0011911 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 0.0012152 | 1.3631 | 1.3662 | 1.3692 | 1.3723 | 1.3754 | 1.3689 | 1.3624 | 1.3559 | 1.3494 | 1.3429 | 1.3364 | 1.3299 | 1.3234 | 1.3169 | 1.3104 | 1.3039 | 1.2974 | 1.2909 | 1.2844 | 1.2779 | 0.042235 | 0.043 | 0.043445 | 0.043852 | 0.044177 | 0.044189 | 0.044489 | 0.04496 | 0.04565 | 0.045431 | 0.045211 | 0.044991 | 0.044771 | 0.044552 | 0.044332 | 0.044112 | 0.043892 | 0.043673 | 0.043453 | 0.043233 | 35130.2353 | 8191.5474 | 22422.9132 | 5228.4977 | 45560.5378 | 59056.5332 | 2656260.7584 | 47546.5199
| DDL013-197602097 | 364 | DDL013 | DDL | South | 6617807.9719 | 0.00098601 | 0.0010134 | 0.0010372 | 0.0010617 | 0.0010803 | 0.0010977 | 0.0011232 | 0.0011524 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 15.3931 | 15.4032 | 15.4134 | 15.4236 | 15.4337 | 15.4198 | 15.4058 | 15.3918 | 15.3778 | 15.3638 | 15.3498 | 15.3359 | 15.3219 | 15.3079 | 15.2939 | 15.2799 | 15.266 | 15.252 | 15.238 | 15.224 | 0.42255 | 0.43457 | 0.44507 | 0.45587 | 0.4642 | 0.47121 | 0.48172 | 0.49382 | 0.50345 | 0.50299 | 0.50253 | 0.50207 | 0.50161 | 0.50116 | 0.5007 | 0.50024 | 0.49978 | 0.49933 | 0.49887 | 0.49841 | 35130.2353 | 8191.5474 | 243667.3111 | 56817.5051 | 272380.2411 | 353065.0324 | 6906277.9719 | 284253.2855
| DDL013-24612353 | 267 | DDL013 | DDL | South | 4854271.2321 | 0.00098601 | 0.0010134 | 0.0010372 | 0.0010617 | 0.0010803 | 0.0010977 | 0.0011232 | 0.0011524 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 7.9163 | 7.9233 | 7.9302 | 7.9371 | 7.944 | 7.9349 | 7.9258 | 7.9167 | 7.9077 | 7.8986 | 7.8895 | 7.8804 | 7.8713 | 7.8622 | 7.8531 | 7.844 | 7.8349 | 7.8258 | 7.8167 | 7.8076 | 0.21731 | 0.22354 | 0.22899 | 0.23459 | 0.23893 | 0.24248 | 0.24783 | 0.25399 | 0.25888 | 0.25859 | 0.25829 | 0.25799 | 0.25769 | 0.2574 | 0.2571 | 0.2568 | 0.2565 | 0.2562 | 0.25591 | 0.25561 | 35130.2353 | 8191.5474 | 125246.0838 | 29204.4508 | 269741.4277 | 349644.5467 | 5065868.7321 | 281499.4464
| DDL013-24612367 | 117 | DDL013 | DDL | South | 2127152.5624 | 0.00098601 | 0.0010134 | 0.0010372 | 0.0010617 | 0.0010803 | 0.0010977 | 0.0011232 | 0.0011524 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.0011759 | 0.4084 | 0.40922 | 0.41004 | 0.41086 | 0.41168 | 0.41069 | 0.4097 | 0.40871 | 0.40771 | 0.40672 | 0.40573 | 0.40474 | 0.40375 | 0.40275 | 0.40176 | 0.40077 | 0.39978 | 0.39879 | 0.39779 | 0.3968 | 0.011211 | 0.011545 | 0.01184 | 0.012144 | 0.012382 | 0.01255 | 0.012811 | 0.013113 | 0.013348 | 0.013315 | 0.013283 | 0.01325 | 0.013218 | 0.013186 | 0.013153 | 0.013121 | 0.013088 | 0.013056 | 0.013023 | 0.012991 | 35130.2353 | 8191.5474 | 6442.8899 | 1502.3309 | 6516.4726 | 8446.7896 | 2219875.0624 | 6800.5254
| DDL014-197602155 | 612 | DDL014 | DDL | South | 11126644.1725 | 0.0010067 | 0.0010246 | 0.0010398 | 0.0010518 | 0.0010578 | 0.00109 | 0.0011414 | 0.001188 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 0.0012251 | 48.6184 | 48.6696 | 48.7209 | 48.7722 | 48.8234 | 48.7139 | 48.6044 | 48.4949 | 48.3854 | 48.2759 | 48.1664 | 48.0569 | 47.9474 | 47.8379 | 47.7284 | 47.6189 | 47.5093 | 47.3998 | 47.2903 | 47.1808 | 1.3626 | 1.3882 | 1.4103 | 1.4282 | 1.4378 | 1.4782 | 1.5445 | 1.604 | 1.6503 | 1.6466 | 1.6428 | 1.6391 | 1.6354 | 1.6316 | 1.6279 | 1.6241 | 1.6204 | 1.6167 | 1.6129 | 1.6092 | 35130.2353 | 8191.5474 | 784314.5514 | 182883.768 | 1543211.4115 | 2000343.2877 | 11611654.1725 | 1610479.9387
| DDL021-193014245 | 425 | DDL021 | DDL | South | 7726836.2309 | 0.0011964 | 0.0012321 | 0.0012609 | 0.0012894 | 0.0013104 | 0.0013332 | 0.0013672 | 0.0014044 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 16.3757 | 16.4101 | 16.4445 | 16.4789 | 16.5133 | 16.44 | 16.3667 | 16.2934 | 16.2201 | 16.1469 | 16.0736 | 16.0003 | 15.927 | 15.8537 | 15.7804 | 15.7072 | 15.6339 | 15.5606 | 15.4873 | 15.414 | 0.54542 | 0.56291 | 0.57728 | 0.59152 | 0.60243 | 0.61017 | 0.62297 | 0.63707 | 0.64703 | 0.64411 | 0.64119 | 0.63826 | 0.63534 | 0.63242 | 0.62949 | 0.62657 | 0.62365 | 0.62072 | 0.6178 | 0.61488 | 35130.2353 | 8191.5474 | 311102.539 | 72541.8194 | 537875.1271 | 697205.1219 | 8063648.7309 | 561321.0836
| DDL021-24613592 | 255 | DDL021 | DDL | South | 4636101.7385 | 0.0011964 | 0.0012321 | 0.0012609 | 0.0012894 | 0.0013104 | 0.0013332 | 0.0013672 | 0.0014044 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 0.0014329 | 10.3361 | 10.3446 | 10.3531 | 10.3616 | 10.3701 | 10.3589 | 10.3476 | 10.3363 | 10.325 | 10.3137 | 10.3025 | 10.2912 | 10.2799 | 10.2686 | 10.2574 | 10.2461 | 10.2348 | 10.2235 | 10.2123 | 10.201 | 0.34426 | 0.35485 | 0.36344 | 0.37194 | 0.37832 | 0.38447 | 0.39386 | 0.40415 | 0.41187 | 0.41142 | 0.41097 | 0.41052 | 0.41007 | 0.40962 | 0.40917 | 0.40872 | 0.40827 | 0.40782 | 0.40737 | 0.40692 | 35130.2353 | 8191.5474 | 199045.0651 | 46412.6433 | 253661.139 | 328800.9361 | 4838189.2385 | 264718.2185
| DDL022-197602273 | 248 | DDL022 | DDL | South | 4508836.2006 | 0.001025 | 0.0010653 | 0.0011042 | 0.0011402 | 0.0011893 | 0.0012524 | 0.001325 | 0.0014008 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 20.3786 | 20.3983 | 20.4181 | 20.4378 | 20.4576 | 20.4127 | 20.3679 | 20.3231 | 20.2783 | 20.2334 | 20.1886 | 20.1438 | 20.099 | 20.0542 | 20.0093 | 19.9645 | 19.9197 | 19.8749 | 19.83 | 19.7852 | 0.58151 | 0.60496 | 0.62766 | 0.64876 | 0.67733 | 0.71175 | 0.75132 | 0.79256 | 0.8257 | 0.82387 | 0.82205 | 0.82022 | 0.8184 | 0.81657 | 0.81475 | 0.81292 | 0.8111 | 0.80927 | 0.80745 | 0.80562 | 35130.2353 | 8191.5474 | 378516.494 | 88261.1735 | 262693.4475 | 340508.8055 | 4705376.2006 | 274144.2449
| DDL022-24596878 | 172 | DDL022 | DDL | South | 3127096.0746 | 0.001025 | 0.0010653 | 0.0011042 | 0.0011402 | 0.0011893 | 0.0012524 | 0.001325 | 0.0014008 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 0.0014626 | 1.2108 | 1.2106 | 1.2105 | 1.2103 | 1.2102 | 1.2102 | 1.2101 | 1.2101 | 1.2101 | 1.21 | 1.21 | 1.21 | 1.2099 | 1.2099 | 1.2099 | 1.2098 | 1.2098 | 1.2098 | 1.2097 | 1.2097 | 0.03455 | 0.035904 | 0.037211 | 0.03842 | 0.040068 | 0.042196 | 0.044639 | 0.047192 | 0.049272 | 0.049271 | 0.049269 | 0.049268 | 0.049266 | 0.049265 | 0.049264 | 0.049262 | 0.049261 | 0.049259 | 0.049258 | 0.049257 | 35130.2353 | 8191.5474 | 22675.3091 | 5287.3505 | 25833.5525 | 33485.9974 | 3263406.0746 | 26959.6361
| DDL023-197602323 | 437 | DDL023 | DDL | South | 7945005.7244 | 0.0018166 | 0.0018883 | 0.0019482 | 0.0020056 | 0.0020515 | 0.0021019 | 0.00217 | 0.0022387 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 16.1692 | 16.1973 | 16.2254 | 16.2535 | 16.2816 | 16.221 | 16.1604 | 16.0998 | 16.0393 | 15.9787 | 15.9181 | 15.8575 | 15.7969 | 15.7363 | 15.6758 | 15.6152 | 15.5546 | 15.494 | 15.4334 | 15.3729 | 0.81774 | 0.85148 | 0.88004 | 0.90754 | 0.92989 | 0.94919 | 0.97631 | 1.0034 | 1.0227 | 1.0189 | 1.015 | 1.0112 | 1.0073 | 1.0034 | 0.99957 | 0.99571 | 0.99184 | 0.98798 | 0.98412 | 0.98025 | 35130.2353 | 8191.5474 | 486599.9148 | 113463.6936 | 556557.3012 | 721421.3513 | 8291328.2244 | 580817.613
| DDL023-24612657 | 31 | DDL023 | DDL | South | 563604.5251 | 0.0018166 | 0.0018883 | 0.0019482 | 0.0020056 | 0.0020515 | 0.0021019 | 0.00217 | 0.0022387 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.86161 | 0.8637 | 0.86578 | 0.86786 | 0.86995 | 0.86554 | 0.86113 | 0.85673 | 0.85232 | 0.84792 | 0.84351 | 0.8391 | 0.8347 | 0.83029 | 0.82588 | 0.82148 | 0.81707 | 0.81266 | 0.80826 | 0.80385 | 0.043575 | 0.045404 | 0.046959 | 0.048458 | 0.049685 | 0.050648 | 0.052024 | 0.053395 | 0.054349 | 0.054068 | 0.053787 | 0.053506 | 0.053225 | 0.052944 | 0.052663 | 0.052382 | 0.052101 | 0.05182 | 0.051539 | 0.051258 | 35130.2353 | 8191.5474 | 25799.8322 | 6015.9161 | 4418.8502 | 5727.8071 | 588172.0251 | 4611.4677
| DDL023-72495872 | 110 | DDL023 | DDL | South | 1999887.0245 | 0.0018166 | 0.0018883 | 0.0019482 | 0.0020056 | 0.0020515 | 0.0021019 | 0.00217 | 0.0022387 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 0.0022904 | 1.2211 | 1.2253 | 1.2294 | 1.2336 | 1.2378 | 1.2269 | 1.216 | 1.2052 | 1.1943 | 1.1834 | 1.1725 | 1.1617 | 1.1508 | 1.1399 | 1.1291 | 1.1182 | 1.1073 | 1.0965 | 1.0856 | 1.0747 | 0.061756 | 0.064411 | 0.066683 | 0.06888 | 0.070692 | 0.071793 | 0.073464 | 0.07511 | 0.076154 | 0.075461 | 0.074768 | 0.074074 | 0.073381 | 0.072688 | 0.071995 | 0.071302 | 0.070609 | 0.069916 | 0.069222 | 0.068529 | 35130.2353 | 8191.5474 | 35940.7933 | 8380.5505 | 24346.4857 | 31558.4299 | 2087062.0245 | 25407.7481
| DDL024-203514186 | 494 | DDL024 | DDL | South | 8981310.8189 | 0.0012958 | 0.0013344 | 0.0013675 | 0.0013975 | 0.0014211 | 0.001468 | 0.0015322 | 0.0015936 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 37.5461 | 37.5875 | 37.6289 | 37.6702 | 37.7116 | 37.623 | 37.5343 | 37.4456 | 37.357 | 37.2683 | 37.1797 | 37.091 | 37.0023 | 36.9137 | 36.825 | 36.7363 | 36.6477 | 36.559 | 36.4704 | 36.3817 | 1.3545 | 1.3964 | 1.4326 | 1.4656 | 1.492 | 1.5376 | 1.6011 | 1.6613 | 1.7063 | 1.7023 | 1.6982 | 1.6942 | 1.6901 | 1.6861 | 1.682 | 1.678 | 1.6739 | 1.6699 | 1.6658 | 1.6618 | 35130.2353 | 8191.5474 | 806968.8335 | 188166.2156 | 1368592.586 | 1773998.671 | 9372805.8189 | 1428249.4852
| DDL024-73759432 | 102 | DDL024 | DDL | South | 1854440.6954 | 0.0012958 | 0.0013344 | 0.0013675 | 0.0013975 | 0.0014211 | 0.001468 | 0.0015322 | 0.0015936 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 0.0016407 | 1.9883 | 1.9918 | 1.9953 | 1.9988 | 2.0023 | 1.9947 | 1.9872 | 1.9797 | 1.9721 | 1.9646 | 1.957 | 1.9495 | 1.942 | 1.9344 | 1.9269 | 1.9193 | 1.9118 | 1.9043 | 1.8967 | 1.8892 | 0.071726 | 0.073997 | 0.075962 | 0.077763 | 0.079219 | 0.081521 | 0.084766 | 0.087828 | 0.090079 | 0.089735 | 0.08939 | 0.089046 | 0.088701 | 0.088357 | 0.088012 | 0.087668 | 0.087324 | 0.086979 | 0.086635 | 0.08629 | 35130.2353 | 8191.5474 | 42500.6087 | 9910.1457 | 25391.2733 | 32912.7058 | 1935275.6954 | 26498.0779
| ECA001-15422792 | 0 | ECA001 | ECA | North | 0 | 0.0014241 | 0.0014305 | 0.0014298 | 0.0014283 | 0.0014195 | 0.0014151 | 0.0014204 | 0.001427 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28328.8661 | 3778.7406 | 0 | 0 | 0 | 0 | 0 | 0
| ECA001-15422805 | 0 | ECA001 | ECA | North | 0 | 0.0014241 | 0.0014305 | 0.0014298 | 0.0014283 | 0.0014195 | 0.0014151 | 0.0014204 | 0.001427 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28328.8661 | 3778.7406 | 0 | 0 | 0 | 0 | 0 | 0
| ECA001-15422818 | 10 | ECA001 | ECA | North | 235663.2619 | 0.0014241 | 0.0014305 | 0.0014298 | 0.0014283 | 0.0014195 | 0.0014151 | 0.0014204 | 0.001427 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28328.8661 | 3778.7406 | 0 | 0 | 0 | 0 | 235663.2619 | 0
| ECA001-24613400 | 54 | ECA001 | ECA | North | 1272581.6144 | 0.0014241 | 0.0014305 | 0.0014298 | 0.0014283 | 0.0014195 | 0.0014151 | 0.0014204 | 0.001427 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 62.1998 | 62.5587 | 62.9175 | 63.2764 | 63.6353 | 63.9183 | 64.2012 | 64.4841 | 64.7671 | 65.05 | 65.3329 | 65.6159 | 65.8988 | 66.1817 | 66.4647 | 66.7476 | 67.0305 | 67.3135 | 67.5964 | 67.8794 | 2.466 | 2.4914 | 2.5045 | 2.5161 | 2.5148 | 2.5181 | 2.5387 | 2.5617 | 2.5718 | 2.583 | 2.5943 | 2.6055 | 2.6167 | 2.628 | 2.6392 | 2.6504 | 2.6617 | 2.6729 | 2.6841 | 2.6954 | 28328.8661 | 3778.7406 | 1053655.7783 | 140545.4002 | 890083.0818 | 890083.0818 | 1272581.6144 | 890083.0818
| ECA001-24613414 | 55 | ECA001 | ECA | North | 1296147.9405 | 0.0014241 | 0.0014305 | 0.0014298 | 0.0014283 | 0.0014195 | 0.0014151 | 0.0014204 | 0.001427 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 0.0014263 | 2.2579 | 2.2671 | 2.2764 | 2.2856 | 2.2948 | 2.2993 | 2.3037 | 2.3082 | 2.3126 | 2.317 | 2.3215 | 2.3259 | 2.3304 | 2.3348 | 2.3392 | 2.3437 | 2.3481 | 2.3526 | 2.357 | 2.3614 | 0.08952 | 0.090288 | 0.090614 | 0.090883 | 0.090688 | 0.090582 | 0.091096 | 0.091696 | 0.091829 | 0.092006 | 0.092182 | 0.092358 | 0.092535 | 0.092711 | 0.092887 | 0.093064 | 0.09324 | 0.093416 | 0.093593 | 0.093769 | 28328.8661 | 3778.7406 | 37566.1992 | 5010.8931 | 52948.1994 | 52948.1994 | 1296147.9405 | 52948.1994
| ECA003-15422755 | 208 | ECA003 | ECA | North | 4901795.8479 | 0.0015527 | 0.0015587 | 0.0015521 | 0.0015433 | 0.0015327 | 0.0015266 | 0.0015313 | 0.0015379 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 0.0015345 | 119.6296 | 120.2278 | 120.826 | 121.4242 | 122.0223 | 122.6099 | 123.1974 | 123.7849 | 124.3724 | 124.9599 | 125.5475 | 126.135 | 126.7225 | 127.31 | 127.8975 | 128.4851 | 129.0726 | 129.6601 | 130.2476 | 130.8352 | 5.1712 | 5.2172 | 5.2209 | 5.2169 | 5.2066 | 5.2111 | 5.2519 | 5.2997 | 5.3131 | 5.3382 | 5.3633 | 5.3884 | 5.4135 | 5.4386 | 5.4637 | 5.4888 | 5.5139 | 5.539 | 5.5641 | 5.5892 | 28328.8661 | 3778.7406 | 2185306.0436 | 291494.3559 | 3537499.5712 | 3537499.5712 | 4901795.8479 | 3537499.5712
| ECA005-15422679 | 42 | ECA005 | ECA | North | 989785.7001 | 0.006354 | 0.0063958 | 0.0063947 | 0.0063755 | 0.0063326 | 0.0063055 | 0.0063151 | 0.0063427 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 4.4524 | 4.4649 | 4.4774 | 4.4899 | 4.5023 | 4.5027 | 4.5031 | 4.5035 | 4.5039 | 4.5042 | 4.5046 | 4.505 | 4.5054 | 4.5058 | 4.5062 | 4.5065 | 4.5069 | 4.5073 | 4.5077 | 4.5081 | 0.78762 | 0.79502 | 0.7971 | 0.79692 | 0.79376 | 0.79043 | 0.7917 | 0.79523 | 0.79091 | 0.79098 | 0.79105 | 0.79111 | 0.79118 | 0.79125 | 0.79132 | 0.79138 | 0.79145 | 0.79152 | 0.79158 | 0.79165 | 28328.8661 | 3778.7406 | 324535.6114 | 43289.268 | 79304.7631 | 79304.7631 | 989785.7001 | 79304.7631
| ECA005-24596794 | 109 | ECA005 | ECA | North | 2568729.5549 | 0.006354 | 0.0063958 | 0.0063947 | 0.0063755 | 0.0063326 | 0.0063055 | 0.0063151 | 0.0063427 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0049422 | 0.0049786 | 0.0050149 | 0.0050513 | 0.0050876 | 0.0051496 | 0.0052116 | 0.0052736 | 0.0053355 | 0.0053975 | 0.0054595 | 0.0055215 | 0.0055835 | 0.0056455 | 0.0057074 | 0.0057694 | 0.0058314 | 0.0058934 | 0.0059554 | 0.0060174 | 0.00087426 | 0.00088648 | 0.0008928 | 0.00089657 | 0.00089694 | 0.00090398 | 0.00091626 | 0.00093121 | 0.00093696 | 0.00094785 | 0.00095873 | 0.00096962 | 0.0009805 | 0.00099139 | 0.0010023 | 0.0010132 | 0.001024 | 0.0010349 | 0.0010458 | 0.0010567 | 28328.8661 | 3778.7406 | 387.9003 | 51.7414 | 1239.9686 | 1239.9686 | 2568729.5549 | 1239.9686
| ECA005-88419875 | 224 | ECA005 | ECA | North | 5278857.067 | 0.006354 | 0.0063958 | 0.0063947 | 0.0063755 | 0.0063326 | 0.0063055 | 0.0063151 | 0.0063427 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 0.0063077 | 4.6405 | 4.6684 | 4.6962 | 4.724 | 4.7519 | 4.7824 | 4.813 | 4.8435 | 4.874 | 4.9046 | 4.9351 | 4.9657 | 4.9962 | 5.0268 | 5.0573 | 5.0879 | 5.1184 | 5.149 | 5.1795 | 5.21 | 0.82089 | 0.83125 | 0.83606 | 0.83849 | 0.83775 | 0.83953 | 0.84617 | 0.85528 | 0.85592 | 0.86128 | 0.86665 | 0.87201 | 0.87737 | 0.88274 | 0.8881 | 0.89347 | 0.89883 | 0.90419 | 0.90956 | 0.91492 | 28328.8661 | 3778.7406 | 352712.2593 | 47047.7044 | 624357.2785 | 624357.2785 | 5278857.067 | 624357.2785
| ECA007-111138070 | 245 | ECA007 | ECA | North | 5773749.917 | 0.0015804 | 0.0016068 | 0.0016226 | 0.0016324 | 0.0016281 | 0.0016209 | 0.0016435 | 0.0016588 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 12.0424 | 12.1126 | 12.1828 | 12.253 | 12.3232 | 12.3534 | 12.3836 | 12.4138 | 12.444 | 12.4742 | 12.5044 | 12.5346 | 12.5648 | 12.595 | 12.6252 | 12.6554 | 12.6856 | 12.7158 | 12.746 | 12.7762 | 0.52984 | 0.54184 | 0.55034 | 0.55685 | 0.55858 | 0.55746 | 0.56661 | 0.5733 | 0.57425 | 0.57564 | 0.57704 | 0.57843 | 0.57982 | 0.58122 | 0.58261 | 0.584 | 0.5854 | 0.58679 | 0.58819 | 0.58958 | 28328.8661 | 3778.7406 | 232582.1066 | 31023.7422 | 1472340.8425 | 1472340.8425 | 5773749.917 | 1472340.8425
| ECA007-139030671 | 37 | ECA007 | ECA | North | 871954.0691 | 0.0015804 | 0.0016068 | 0.0016226 | 0.0016324 | 0.0016281 | 0.0016209 | 0.0016435 | 0.0016588 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0080024 | 0.0080609 | 0.0081193 | 0.0081777 | 0.0082361 | 0.0082773 | 0.0083186 | 0.0083598 | 0.0084011 | 0.0084423 | 0.0084835 | 0.0085248 | 0.008566 | 0.0086073 | 0.0086485 | 0.0086897 | 0.008731 | 0.0087722 | 0.0088134 | 0.0088547 | 0.00035209 | 0.00036059 | 0.00036677 | 0.00037165 | 0.00037332 | 0.00037352 | 0.00038062 | 0.00038608 | 0.00038768 | 0.00038958 | 0.00039149 | 0.00039339 | 0.00039529 | 0.0003972 | 0.0003991 | 0.000401 | 0.00040291 | 0.00040481 | 0.00040671 | 0.00040861 | 28328.8661 | 3778.7406 | 157.3043 | 20.9826 | 8151.1077 | 8151.1077 | 871954.0691 | 8151.1077
| ECA007-139030700 | 84 | ECA007 | ECA | North | 1979571.4001 | 0.0015804 | 0.0016068 | 0.0016226 | 0.0016324 | 0.0016281 | 0.0016209 | 0.0016435 | 0.0016588 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.12276 | 0.12365 | 0.12455 | 0.12544 | 0.12634 | 0.12683 | 0.12732 | 0.12781 | 0.1283 | 0.12879 | 0.12928 | 0.12977 | 0.13026 | 0.13075 | 0.13124 | 0.13173 | 0.13222 | 0.13271 | 0.1332 | 0.13369 | 0.0054011 | 0.0055315 | 0.0056263 | 0.005701 | 0.0057267 | 0.0057233 | 0.0058255 | 0.0059025 | 0.0059206 | 0.0059432 | 0.0059658 | 0.0059884 | 0.006011 | 0.0060337 | 0.0060563 | 0.0060789 | 0.0061015 | 0.0061241 | 0.0061467 | 0.0061693 | 28328.8661 | 3778.7406 | 2399.483 | 320.0631 | 74893.0786 | 74893.0786 | 1979571.4001 | 74893.0786
| ECA007-15422655 | 59 | ECA007 | ECA | North | 1390413.2453 | 0.0015804 | 0.0016068 | 0.0016226 | 0.0016324 | 0.0016281 | 0.0016209 | 0.0016435 | 0.0016588 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 11.7645 | 11.8231 | 11.8817 | 11.9404 | 11.999 | 12.0965 | 12.1939 | 12.2914 | 12.3889 | 12.4863 | 12.5838 | 12.6813 | 12.7787 | 12.8762 | 12.9737 | 13.0712 | 13.1686 | 13.2661 | 13.3636 | 13.461 | 0.51761 | 0.5289 | 0.53674 | 0.54265 | 0.54388 | 0.54586 | 0.55793 | 0.56765 | 0.57171 | 0.5762 | 0.5807 | 0.5852 | 0.5897 | 0.5942 | 0.59869 | 0.60319 | 0.60769 | 0.61219 | 0.61669 | 0.62118 | 28328.8661 | 3778.7406 | 233038.9051 | 31084.6738 | 218393.365 | 218393.365 | 1390413.2453 | 218393.365
| ECA007-155422337 | 58 | ECA007 | ECA | North | 1366846.9191 | 0.0015804 | 0.0016068 | 0.0016226 | 0.0016324 | 0.0016281 | 0.0016209 | 0.0016435 | 0.0016588 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.073194 | 0.073651 | 0.074108 | 0.074564 | 0.075021 | 0.075572 | 0.076123 | 0.076674 | 0.077225 | 0.077776 | 0.078327 | 0.078878 | 0.079429 | 0.07998 | 0.080531 | 0.081082 | 0.081633 | 0.082184 | 0.082735 | 0.083286 | 0.0032204 | 0.0032947 | 0.0033477 | 0.0033887 | 0.0034005 | 0.0034102 | 0.003483 | 0.003541 | 0.0035637 | 0.0035891 | 0.0036145 | 0.00364 | 0.0036654 | 0.0036908 | 0.0037162 | 0.0037417 | 0.0037671 | 0.0037925 | 0.0038179 | 0.0038434 | 28328.8661 | 3778.7406 | 1450.3978 | 193.4662 | 42539.2692 | 42539.2692 | 1366846.9191 | 42539.2692
| ECA007-155422427 | 15 | ECA007 | ECA | North | 353494.8929 | 0.0015804 | 0.0016068 | 0.0016226 | 0.0016324 | 0.0016281 | 0.0016209 | 0.0016435 | 0.0016588 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.011223 | 0.011293 | 0.011364 | 0.011434 | 0.011505 | 0.011592 | 0.011679 | 0.011766 | 0.011853 | 0.011939 | 0.012026 | 0.012113 | 0.0122 | 0.012287 | 0.012374 | 0.012461 | 0.012548 | 0.012634 | 0.012721 | 0.012808 | 0.00049378 | 0.00050519 | 0.00051334 | 0.00051965 | 0.00052149 | 0.00052309 | 0.00053436 | 0.00054336 | 0.00054695 | 0.00055096 | 0.00055497 | 0.00055898 | 0.00056299 | 0.000567 | 0.00057101 | 0.00057502 | 0.00057903 | 0.00058304 | 0.00058705 | 0.00059106 | 28328.8661 | 3778.7406 | 222.6483 | 29.6987 | 8685.314 | 8685.314 | 353494.8929 | 8685.314
| ECA007-155422573 | 72 | ECA007 | ECA | North | 1696775.4858 | 0.0015804 | 0.0016068 | 0.0016226 | 0.0016324 | 0.0016281 | 0.0016209 | 0.0016435 | 0.0016588 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.070463 | 0.071016 | 0.071569 | 0.072121 | 0.072674 | 0.073157 | 0.073639 | 0.074122 | 0.074604 | 0.075087 | 0.07557 | 0.076052 | 0.076535 | 0.077017 | 0.0775 | 0.077983 | 0.078465 | 0.078948 | 0.07943 | 0.079913 | 0.0031002 | 0.0031768 | 0.003233 | 0.0032776 | 0.0032941 | 0.0033013 | 0.0033694 | 0.0034231 | 0.0034428 | 0.003465 | 0.0034873 | 0.0035096 | 0.0035318 | 0.0035541 | 0.0035764 | 0.0035986 | 0.0036209 | 0.0036432 | 0.0036655 | 0.0036877 | 28328.8661 | 3778.7406 | 1398.8457 | 186.5897 | 76396.2893 | 76396.2893 | 1696775.4858 | 76396.2893
| ECA007-175612541 | 0 | ECA007 | ECA | North | 0 | 0.0015804 | 0.0016068 | 0.0016226 | 0.0016324 | 0.0016281 | 0.0016209 | 0.0016435 | 0.0016588 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28328.8661 | 3778.7406 | 0 | 0 | 0 | 0 | 0 | 0
| ECA007-24611056 | 35 | ECA007 | ECA | North | 824821.4167 | 0.0015804 | 0.0016068 | 0.0016226 | 0.0016324 | 0.0016281 | 0.0016209 | 0.0016435 | 0.0016588 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 0.0016576 | 4.2362 | 4.2573 | 4.2784 | 4.2995 | 4.3205 | 4.3511 | 4.3817 | 4.4123 | 4.4429 | 4.4734 | 4.504 | 4.5346 | 4.5652 | 4.5958 | 4.6263 | 4.6569 | 4.6875 | 4.7181 | 4.7487 | 4.7792 | 0.18638 | 0.19045 | 0.19327 | 0.19539 | 0.19584 | 0.19635 | 0.20048 | 0.20377 | 0.20502 | 0.20643 | 0.20785 | 0.20926 | 0.21067 | 0.21208 | 0.21349 | 0.2149 | 0.21631 | 0.21772 | 0.21914 | 0.22055 | 28328.8661 | 3778.7406 | 83483.3799 | 11135.7099 | 88352.7772 | 88352.7772 | 824821.4167 | 88352.7772
| ECA010-15423016 | 186 | ECA010 | ECA | North | 4383336.6717 | 0.0017393 | 0.0017557 | 0.0017652 | 0.0017674 | 0.0017586 | 0.0017548 | 0.0017703 | 0.0017909 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 0.001788 | 101.9039 | 102.5708 | 103.2378 | 103.9048 | 104.5718 | 105.1378 | 105.7039 | 106.27 | 106.8361 | 107.4021 | 107.9682 | 108.5343 | 109.1003 | 109.6664 | 110.2325 | 110.7985 | 111.3646 | 111.9307 | 112.4968 | 113.0628 | 4.9345 | 5.0135 | 5.0735 | 5.1127 | 5.1197 | 5.1364 | 5.2096 | 5.2984 | 5.3181 | 5.3463 | 5.3745 | 5.4026 | 5.4308 | 5.459 | 5.4872 | 5.5153 | 5.5435 | 5.5717 | 5.5999 | 5.6281 | 28328.8661 | 3778.7406 | 2166311.3707 | 288960.6879 | 3000005.9019 | 3000005.9019 | 4383336.6717 | 3000005.9019
| ECA012-15423053 | 138 | ECA012 | ECA | North | 3252153.0145 | 0.0015702 | 0.0015928 | 0.001616 | 0.0016267 | 0.0016187 | 0.0016212 | 0.001647 | 0.0016777 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 26.4164 | 26.5888 | 26.7612 | 26.9336 | 27.106 | 27.277 | 27.448 | 27.619 | 27.79 | 27.9609 | 28.1319 | 28.3029 | 28.4739 | 28.6449 | 28.8158 | 28.9868 | 29.1578 | 29.3288 | 29.4998 | 29.6707 | 1.1548 | 1.179 | 1.204 | 1.2198 | 1.2216 | 1.2312 | 1.2586 | 1.29 | 1.2936 | 1.3015 | 1.3095 | 1.3175 | 1.3254 | 1.3334 | 1.3413 | 1.3493 | 1.3573 | 1.3652 | 1.3732 | 1.3811 | 28328.8661 | 3778.7406 | 523217.9259 | 69791.1731 | 733800.3712 | 733800.3712 | 3252153.0145 | 733800.3712
| ECA012-160768254 | 28 | ECA012 | ECA | North | 659857.1334 | 0.0015702 | 0.0015928 | 0.001616 | 0.0016267 | 0.0016187 | 0.0016212 | 0.001647 | 0.0016777 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.038762 | 0.03902 | 0.039279 | 0.039537 | 0.039796 | 0.040059 | 0.040323 | 0.040587 | 0.040851 | 0.041114 | 0.041378 | 0.041642 | 0.041906 | 0.04217 | 0.042433 | 0.042697 | 0.042961 | 0.043225 | 0.043489 | 0.043752 | 0.0016945 | 0.0017302 | 0.0017671 | 0.0017906 | 0.0017934 | 0.0018081 | 0.0018489 | 0.0018958 | 0.0019015 | 0.0019138 | 0.0019261 | 0.0019384 | 0.0019507 | 0.0019629 | 0.0019752 | 0.0019875 | 0.0019998 | 0.002012 | 0.0020243 | 0.0020366 | 28328.8661 | 3778.7406 | 769.3173 | 102.618 | 19535.1685 | 19535.1685 | 659857.1334 | 19535.1685
| ECA012-164487948 | 12 | ECA012 | ECA | North | 282795.9143 | 0.0015702 | 0.0015928 | 0.001616 | 0.0016267 | 0.0016187 | 0.0016212 | 0.001647 | 0.0016777 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.0022192 | 0.0022327 | 0.0022461 | 0.0022596 | 0.0022731 | 0.0022922 | 0.0023114 | 0.0023305 | 0.0023496 | 0.0023687 | 0.0023878 | 0.002407 | 0.0024261 | 0.0024452 | 0.0024643 | 0.0024835 | 0.0025026 | 0.0025217 | 0.0025408 | 0.0025599 | 9.7013e-05 | 9.9001e-05 | 0.00010105 | 0.00010234 | 0.00010244 | 0.00010346 | 0.00010598 | 0.00010885 | 0.00010937 | 0.00011026 | 0.00011115 | 0.00011204 | 0.00011293 | 0.00011382 | 0.00011471 | 0.0001156 | 0.00011649 | 0.00011738 | 0.00011827 | 0.00011916 | 28328.8661 | 3778.7406 | 44.3465 | 5.9153 | 1608.5131 | 1608.5131 | 282795.9143 | 1608.5131
| ECA012-202230762 | 509 | ECA012 | ECA | North | 11995260.0316 | 0.0015702 | 0.0015928 | 0.001616 | 0.0016267 | 0.0016187 | 0.0016212 | 0.001647 | 0.0016777 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 0.001672 | 5.3036 | 5.3201 | 5.3366 | 5.3531 | 5.3695 | 5.3708 | 5.3721 | 5.3733 | 5.3746 | 5.3759 | 5.3771 | 5.3784 | 5.3797 | 5.3809 | 5.3822 | 5.3835 | 5.3847 | 5.386 | 5.3873 | 5.3885 | 0.23185 | 0.2359 | 0.24009 | 0.24243 | 0.24198 | 0.24241 | 0.24632 | 0.25098 | 0.25018 | 0.25024 | 0.2503 | 0.25036 | 0.25042 | 0.25047 | 0.25053 | 0.25059 | 0.25065 | 0.25071 | 0.25077 | 0.25083 | 28328.8661 | 3778.7406 | 100736.6224 | 13437.0913 | 1164318.1461 | 1164318.1461 | 11995260.0316 | 1164318.1461
| EHK021-15417698 | 64 | EHK021 | EHK | North | 1508244.8763 | 0.018215 | 0.017689 | 0.017689 | 0.017662 | 0.017481 | 0.01741 | 0.017523 | 0.017564 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 0.017343 | 2.3457 | 2.3578 | 2.37 | 2.3822 | 2.3943 | 2.3984 | 2.4024 | 2.4065 | 2.4105 | 2.4146 | 2.4186 | 2.4226 | 2.4267 | 2.4307 | 2.4348 | 2.4388 | 2.4429 | 2.4469 | 2.4509 | 2.455 | 1.1895 | 1.1612 | 1.1672 | 1.1713 | 1.1652 | 1.1625 | 1.172 | 1.1767 | 1.1639 | 1.1658 | 1.1678 | 1.1697 | 1.1717 | 1.1736 | 1.1756 | 1.1775 | 1.1795 | 1.1815 | 1.1834 | 1.1854 | 33701.7776 | 5314.4363 | 571293.804 | 90087.3711 | 143006.3619 | 143006.3619 | 1508244.8763 | 143006.3619
| EHK022-15417761 | 95 | EHK022 | EHK | North | 2238800.9882 | 0.0023655 | 0.0023571 | 0.0023366 | 0.0023231 | 0.0023154 | 0.0023217 | 0.0023322 | 0.0023472 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0.002349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33701.7776 | 5314.4363 | 0 | 0 | 0 | 0 | 2238800.9882 | 0
| EHK023-15417824 | 270 | EHK023 | EHK | North | 6362908.0718 | 0.0010301 | 0.0010418 | 0.0010523 | 0.0010602 | 0.0010618 | 0.0010676 | 0.001085 | 0.0011151 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 0.001138 | 439.3042 | 441.9157 | 444.5271 | 447.1386 | 449.7501 | 450.6294 | 451.5086 | 452.3879 | 453.2672 | 454.1465 | 455.0258 | 455.905 | 456.7843 | 457.6636 | 458.5429 | 459.4222 | 460.3014 | 461.1807 | 462.06 | 462.9393 | 12.5985 | 12.8166 | 13.0234 | 13.198 | 13.2942 | 13.394 | 13.6389 | 14.0447 | 14.36 | 14.3878 | 14.4157 | 14.4435 | 14.4714 | 14.4992 | 14.5271 | 14.555 | 14.5828 | 14.6107 | 14.6385 | 14.6664 | 33701.7776 | 5314.4363 | 6764051.0404 | 1066623.8144 | 9792027.9479 | 9792027.9479 | 6362908.0718 | 9792027.9479
| EHK024-109924737 | 48 | EHK024 | EHK | North | 1131183.6572 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0042357 | 0.0042699 | 0.0043041 | 0.0043383 | 0.0043725 | 0.0043955 | 0.0044185 | 0.0044415 | 0.0044645 | 0.0044876 | 0.0045106 | 0.0045336 | 0.0045566 | 0.0045796 | 0.0046026 | 0.0046256 | 0.0046486 | 0.0046716 | 0.0046946 | 0.0047176 | 0.00025544 | 0.00027925 | 0.00028215 | 0.00028447 | 0.00028504 | 0.00028609 | 0.00028872 | 0.00029258 | 0.00029352 | 0.00029503 | 0.00029655 | 0.00029806 | 0.00029957 | 0.00030109 | 0.0003026 | 0.00030411 | 0.00030562 | 0.00030714 | 0.00030865 | 0.00031016 | 33701.7776 | 5314.4363 | 142.023 | 22.3956 | 4564.8872 | 4564.8872 | 1131183.6572 | 4564.8872
| EHK024-119636484 | 455 | EHK024 | EHK | North | 10722678.4173 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 3.7642 | 3.7728 | 3.7814 | 3.7901 | 3.7987 | 3.7958 | 3.7929 | 3.79 | 3.7871 | 3.7843 | 3.7814 | 3.7785 | 3.7756 | 3.7727 | 3.7698 | 3.767 | 3.7641 | 3.7612 | 3.7583 | 3.7554 | 0.22701 | 0.24674 | 0.24789 | 0.24852 | 0.24764 | 0.24706 | 0.24784 | 0.24966 | 0.24899 | 0.2488 | 0.24861 | 0.24842 | 0.24823 | 0.24804 | 0.24785 | 0.24766 | 0.24747 | 0.24728 | 0.24709 | 0.2469 | 33701.7776 | 5314.4363 | 120132.5693 | 18943.7156 | 1979119.0367 | 1979119.0367 | 10722678.4173 | 1979119.0367
| EHK024-130742429 | 16 | EHK024 | EHK | North | 377061.2191 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.42343 | 0.42641 | 0.42939 | 0.43237 | 0.43534 | 0.43745 | 0.43955 | 0.44165 | 0.44375 | 0.44585 | 0.44795 | 0.45005 | 0.45215 | 0.45425 | 0.45635 | 0.45845 | 0.46055 | 0.46265 | 0.46475 | 0.46685 | 0.025536 | 0.027887 | 0.028148 | 0.028351 | 0.02838 | 0.028472 | 0.028721 | 0.029092 | 0.029174 | 0.029312 | 0.02945 | 0.029589 | 0.029727 | 0.029865 | 0.030003 | 0.030141 | 0.030279 | 0.030417 | 0.030555 | 0.030693 | 33701.7776 | 5314.4363 | 14118.4162 | 2226.3343 | 80676.9588 | 80676.9588 | 377061.2191 | 80676.9588
| EHK024-15417874 | 193 | EHK024 | EHK | North | 4548300.955 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 73.2482 | 73.7302 | 74.2121 | 74.6941 | 75.1761 | 75.2989 | 75.4216 | 75.5444 | 75.6672 | 75.79 | 75.9127 | 76.0355 | 76.1583 | 76.2811 | 76.4038 | 76.5266 | 76.6494 | 76.7722 | 76.8949 | 77.0177 | 4.4174 | 4.822 | 4.8649 | 4.8979 | 4.9007 | 4.901 | 4.9283 | 4.9763 | 4.9747 | 4.9828 | 4.9909 | 4.999 | 5.007 | 5.0151 | 5.0232 | 5.0312 | 5.0393 | 5.0474 | 5.0555 | 5.0635 | 33701.7776 | 5314.4363 | 2400047.7076 | 378463.738 | 3010638.4581 | 3010638.4581 | 4548300.955 | 3010638.4581
| EHK024-155053117 | 54 | EHK024 | EHK | North | 1272581.6144 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.037591 | 0.037851 | 0.03811 | 0.038369 | 0.038629 | 0.038832 | 0.039036 | 0.03924 | 0.039444 | 0.039647 | 0.039851 | 0.040055 | 0.040259 | 0.040462 | 0.040666 | 0.04087 | 0.041074 | 0.041277 | 0.041481 | 0.041685 | 0.002267 | 0.0024754 | 0.0024982 | 0.002516 | 0.0025182 | 0.0025275 | 0.0025507 | 0.0025848 | 0.0025932 | 0.0026066 | 0.00262 | 0.0026334 | 0.0026468 | 0.0026602 | 0.0026736 | 0.002687 | 0.0027004 | 0.0027138 | 0.0027272 | 0.0027406 | 33701.7776 | 5314.4363 | 1255.6359 | 198.0013 | 29058.719 | 29058.719 | 1272581.6144 | 29058.719
| EHK024-155155262 | 20 | EHK024 | EHK | North | 471326.5238 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0042697 | 0.0043054 | 0.0043411 | 0.0043768 | 0.0044124 | 0.0044241 | 0.0044359 | 0.0044476 | 0.0044593 | 0.004471 | 0.0044827 | 0.0044944 | 0.0045062 | 0.0045179 | 0.0045296 | 0.0045413 | 0.004553 | 0.0045647 | 0.0045764 | 0.0045882 | 0.0002575 | 0.00028158 | 0.00028457 | 0.000287 | 0.00028764 | 0.00028796 | 0.00028985 | 0.00029297 | 0.00029318 | 0.00029395 | 0.00029472 | 0.00029549 | 0.00029626 | 0.00029703 | 0.0002978 | 0.00029857 | 0.00029934 | 0.00030011 | 0.00030088 | 0.00030165 | 33701.7776 | 5314.4363 | 141.4454 | 22.3045 | 3367.9405 | 3367.9405 | 471326.5238 | 3367.9405
| EHK024-155423299 | 55 | EHK024 | EHK | North | 1296147.9405 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.047156 | 0.047484 | 0.047812 | 0.04814 | 0.048468 | 0.048738 | 0.049009 | 0.049279 | 0.049549 | 0.04982 | 0.05009 | 0.050361 | 0.050631 | 0.050901 | 0.051172 | 0.051442 | 0.051712 | 0.051983 | 0.052253 | 0.052523 | 0.0028438 | 0.0031055 | 0.0031342 | 0.0031567 | 0.0031596 | 0.0031723 | 0.0032024 | 0.0032461 | 0.0032576 | 0.0032754 | 0.0032932 | 0.003311 | 0.0033287 | 0.0033465 | 0.0033643 | 0.0033821 | 0.0033998 | 0.0034176 | 0.0034354 | 0.0034532 | 33701.7776 | 5314.4363 | 1577.782 | 248.8006 | 40423.6714 | 40423.6714 | 1296147.9405 | 40423.6714
| EHK024-155616704 | 29 | EHK024 | EHK | North | 683423.4596 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0055486 | 0.0055628 | 0.0055771 | 0.0055913 | 0.0056056 | 0.0056093 | 0.005613 | 0.0056167 | 0.0056204 | 0.0056241 | 0.0056278 | 0.0056315 | 0.0056352 | 0.0056389 | 0.0056426 | 0.0056463 | 0.00565 | 0.0056537 | 0.0056574 | 0.0056611 | 0.00033462 | 0.00036381 | 0.0003656 | 0.00036664 | 0.00036543 | 0.0003651 | 0.00036677 | 0.00036999 | 0.00036951 | 0.00036976 | 0.00037 | 0.00037024 | 0.00037049 | 0.00037073 | 0.00037097 | 0.00037122 | 0.00037146 | 0.0003717 | 0.00037195 | 0.00037219 | 33701.7776 | 5314.4363 | 178.5251 | 28.1516 | 4267.9566 | 4267.9566 | 683423.4596 | 4267.9566
| EHK024-155621039 | 52 | EHK024 | EHK | North | 1225448.962 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.11862 | 0.11942 | 0.12022 | 0.12102 | 0.12182 | 0.12217 | 0.12252 | 0.12286 | 0.12321 | 0.12356 | 0.1239 | 0.12425 | 0.12459 | 0.12494 | 0.12529 | 0.12563 | 0.12598 | 0.12633 | 0.12667 | 0.12702 | 0.0071538 | 0.0078103 | 0.007881 | 0.0079358 | 0.0079416 | 0.0079517 | 0.0080056 | 0.0080933 | 0.0081004 | 0.0081232 | 0.0081459 | 0.0081687 | 0.0081915 | 0.0082143 | 0.008237 | 0.0082598 | 0.0082826 | 0.0083054 | 0.0083281 | 0.0083509 | 33701.7776 | 5314.4363 | 3912.6282 | 616.9827 | 48445.9255 | 48445.9255 | 1225448.962 | 48445.9255
| EHK024-161138740 | 246 | EHK024 | EHK | North | 5797316.2432 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 12.8621 | 12.922 | 12.982 | 13.0419 | 13.1019 | 13.1424 | 13.183 | 13.2236 | 13.2641 | 13.3047 | 13.3453 | 13.3858 | 13.4264 | 13.467 | 13.5075 | 13.5481 | 13.5887 | 13.6292 | 13.6698 | 13.7104 | 0.77568 | 0.8451 | 0.85101 | 0.85519 | 0.85411 | 0.85541 | 0.86142 | 0.87107 | 0.87205 | 0.87472 | 0.87738 | 0.88005 | 0.88272 | 0.88539 | 0.88805 | 0.89072 | 0.89339 | 0.89605 | 0.89872 | 0.90139 | 33701.7776 | 5314.4363 | 421857.3605 | 66522.725 | 1746566.0185 | 1746566.0185 | 5797316.2432 | 1746566.0185
| EHK024-162768321 | 5 | EHK024 | EHK | North | 117831.631 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33701.7776 | 5314.4363 | 0 | 0 | 0 | 0 | 117831.631 | 0
| EHK024-162802004 | 8 | EHK024 | EHK | North | 188530.6095 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.00015391 | 0.00015533 | 0.00015675 | 0.00015818 | 0.0001596 | 0.00016053 | 0.00016146 | 0.00016239 | 0.00016332 | 0.00016425 | 0.00016518 | 0.00016611 | 0.00016704 | 0.00016797 | 0.0001689 | 0.00016983 | 0.00017076 | 0.00017169 | 0.00017262 | 0.00017355 | 9.2818e-06 | 1.0159e-05 | 1.0276e-05 | 1.0372e-05 | 1.0404e-05 | 1.0449e-05 | 1.055e-05 | 1.0697e-05 | 1.0737e-05 | 1.0799e-05 | 1.086e-05 | 1.0921e-05 | 1.0982e-05 | 1.1043e-05 | 1.1104e-05 | 1.1165e-05 | 1.1227e-05 | 1.1288e-05 | 1.1349e-05 | 1.141e-05 | 33701.7776 | 5314.4363 | 5.1949 | 0.81919 | 74.2077 | 74.2077 | 188530.6095 | 74.2077
| EHK024-162802163 | 0 | EHK024 | EHK | North | 0 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.00021429 | 0.00021611 | 0.00021794 | 0.00021977 | 0.0002216 | 0.00022272 | 0.00022384 | 0.00022496 | 0.00022608 | 0.0002272 | 0.00022832 | 0.00022944 | 0.00023056 | 0.00023168 | 0.0002328 | 0.00023392 | 0.00023504 | 0.00023616 | 0.00023728 | 0.0002384 | 1.2923e-05 | 1.4134e-05 | 1.4287e-05 | 1.4411e-05 | 1.4446e-05 | 1.4496e-05 | 1.4626e-05 | 1.4819e-05 | 1.4864e-05 | 1.4937e-05 | 1.5011e-05 | 1.5085e-05 | 1.5158e-05 | 1.5232e-05 | 1.5305e-05 | 1.5379e-05 | 1.5453e-05 | 1.5526e-05 | 1.56e-05 | 1.5674e-05 | 33701.7776 | 5314.4363 | 0 | 0 | 0 | 0 | 0 | 0
| EHK024-171210602 | 2 | EHK024 | EHK | North | 47132.6524 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 5.9349e-05 | 5.9811e-05 | 6.0274e-05 | 6.0737e-05 | 6.12e-05 | 6.165e-05 | 6.21e-05 | 6.255e-05 | 6.3e-05 | 6.345e-05 | 6.39e-05 | 6.435e-05 | 6.48e-05 | 6.525e-05 | 6.57e-05 | 6.615e-05 | 6.66e-05 | 6.705e-05 | 6.75e-05 | 6.795e-05 | 3.5791e-06 | 3.9117e-06 | 3.9512e-06 | 3.9827e-06 | 3.9896e-06 | 4.0127e-06 | 4.0578e-06 | 4.1203e-06 | 4.1419e-06 | 4.1715e-06 | 4.2011e-06 | 4.2307e-06 | 4.2603e-06 | 4.2899e-06 | 4.3194e-06 | 4.349e-06 | 4.3786e-06 | 4.4082e-06 | 4.4378e-06 | 4.4674e-06 | 33701.7776 | 5314.4363 | 2.0087 | 0.31676 | 7.1733 | 7.1733 | 47132.6524 | 7.1733
| EHK024-63048145 | 238 | EHK024 | EHK | North | 5608785.6336 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 1.7752 | 1.7871 | 1.799 | 1.8109 | 1.8227 | 1.8315 | 1.8402 | 1.8489 | 1.8577 | 1.8664 | 1.8752 | 1.8839 | 1.8926 | 1.9014 | 1.9101 | 1.9189 | 1.9276 | 1.9363 | 1.9451 | 1.9538 | 0.10706 | 0.11688 | 0.11793 | 0.11874 | 0.11882 | 0.11921 | 0.12024 | 0.1218 | 0.12213 | 0.12271 | 0.12328 | 0.12386 | 0.12443 | 0.12501 | 0.12558 | 0.12615 | 0.12673 | 0.1273 | 0.12788 | 0.12845 | 33701.7776 | 5314.4363 | 59114.818 | 9321.821 | 597562.22 | 597562.22 | 5608785.6336 | 597562.22
| EHK024-63048164 | 301 | EHK024 | EHK | North | 7093464.1837 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 9.2358 | 9.2913 | 9.3468 | 9.4023 | 9.4579 | 9.4838 | 9.5098 | 9.5358 | 9.5618 | 9.5877 | 9.6137 | 9.6397 | 9.6657 | 9.6917 | 9.7176 | 9.7436 | 9.7696 | 9.7956 | 9.8215 | 9.8475 | 0.55698 | 0.60765 | 0.61272 | 0.61654 | 0.61656 | 0.61728 | 0.6214 | 0.62815 | 0.62864 | 0.63035 | 0.63205 | 0.63376 | 0.63547 | 0.63718 | 0.63889 | 0.64059 | 0.6423 | 0.64401 | 0.64572 | 0.64743 | 33701.7776 | 5314.4363 | 303746.3613 | 47897.7909 | 1641466.7215 | 1641466.7215 | 7093464.1837 | 1641466.7215
| EHK024-73766693 | 31 | EHK024 | EHK | North | 730556.1119 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.33003 | 0.33234 | 0.33465 | 0.33697 | 0.33928 | 0.34004 | 0.34079 | 0.34155 | 0.3423 | 0.34306 | 0.34381 | 0.34457 | 0.34532 | 0.34608 | 0.34683 | 0.34759 | 0.34834 | 0.3491 | 0.34985 | 0.35061 | 0.019903 | 0.021735 | 0.021938 | 0.022096 | 0.022118 | 0.022132 | 0.022268 | 0.022499 | 0.022505 | 0.022554 | 0.022604 | 0.022654 | 0.022703 | 0.022753 | 0.022802 | 0.022852 | 0.022902 | 0.022951 | 0.023001 | 0.023051 | 33701.7776 | 5314.4363 | 10861.3339 | 1712.7247 | 87996.7142 | 87996.7142 | 730556.1119 | 87996.7142
| EHK024-73766943 | 34 | EHK024 | EHK | North | 801255.0905 | 0.0021662 | 0.0023492 | 0.0023547 | 0.0023553 | 0.0023416 | 0.0023379 | 0.0023471 | 0.0023661 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.0023615 | 0.066905 | 0.067275 | 0.067644 | 0.068014 | 0.068384 | 0.068677 | 0.068971 | 0.069265 | 0.069558 | 0.069852 | 0.070145 | 0.070439 | 0.070733 | 0.071026 | 0.07132 | 0.071614 | 0.071907 | 0.072201 | 0.072495 | 0.072788 | 0.0040349 | 0.0043998 | 0.0044343 | 0.0044599 | 0.0044579 | 0.00447 | 0.0045068 | 0.0045626 | 0.0045731 | 0.0045924 | 0.0046117 | 0.004631 | 0.0046503 | 0.0046696 | 0.0046889 | 0.0047083 | 0.0047276 | 0.0047469 | 0.0047662 | 0.0047855 | 33701.7776 | 5314.4363 | 2213.8621 | 349.1041 | 33604.9408 | 33604.9408 | 801255.0905 | 33604.9408
| EHK031-134953753 | 41 | EHK031 | EHK | North | 966219.3739 | 0.0021813 | 0.0022585 | 0.0023124 | 0.0023584 | 0.0023959 | 0.0024432 | 0.0025368 | 0.0026369 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.5385 | 0.54188 | 0.54526 | 0.54864 | 0.55202 | 0.55314 | 0.55426 | 0.55538 | 0.5565 | 0.55762 | 0.55874 | 0.55986 | 0.56098 | 0.5621 | 0.56322 | 0.56433 | 0.56545 | 0.56657 | 0.56769 | 0.56881 | 0.032702 | 0.034071 | 0.035102 | 0.036023 | 0.036821 | 0.037624 | 0.039144 | 0.040771 | 0.042002 | 0.042087 | 0.042171 | 0.042256 | 0.04234 | 0.042425 | 0.042509 | 0.042594 | 0.042678 | 0.042763 | 0.042847 | 0.042932 | 33701.7776 | 5314.4363 | 19240.8794 | 3034.096 | 204198.4506 | 204198.4506 | 966219.3739 | 204198.4506
| EHK031-134953882 | 30 | EHK031 | EHK | North | 706989.7858 | 0.0021813 | 0.0022585 | 0.0023124 | 0.0023584 | 0.0023959 | 0.0024432 | 0.0025368 | 0.0026369 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.21184 | 0.21336 | 0.21487 | 0.21639 | 0.2179 | 0.2182 | 0.2185 | 0.2188 | 0.2191 | 0.2194 | 0.2197 | 0.22 | 0.2203 | 0.22059 | 0.22089 | 0.22119 | 0.22149 | 0.22179 | 0.22209 | 0.22239 | 0.012865 | 0.013415 | 0.013833 | 0.014207 | 0.014534 | 0.014842 | 0.015431 | 0.016062 | 0.016537 | 0.016559 | 0.016582 | 0.016604 | 0.016627 | 0.01665 | 0.016672 | 0.016695 | 0.016717 | 0.01674 | 0.016762 | 0.016785 | 33701.7776 | 5314.4363 | 7565.147 | 1192.9487 | 55816.1919 | 55816.1919 | 706989.7858 | 55816.1919
| EHK031-134954057 | 28 | EHK031 | EHK | North | 659857.1334 | 0.0021813 | 0.0022585 | 0.0023124 | 0.0023584 | 0.0023959 | 0.0024432 | 0.0025368 | 0.0026369 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.083922 | 0.084504 | 0.085087 | 0.085669 | 0.086252 | 0.086462 | 0.086672 | 0.086882 | 0.087092 | 0.087302 | 0.087513 | 0.087723 | 0.087933 | 0.088143 | 0.088353 | 0.088563 | 0.088773 | 0.088984 | 0.089194 | 0.089404 | 0.0050964 | 0.0053133 | 0.0054776 | 0.0056249 | 0.0057532 | 0.0058811 | 0.0061211 | 0.0063781 | 0.0065734 | 0.0065892 | 0.0066051 | 0.0066209 | 0.0066368 | 0.0066527 | 0.0066685 | 0.0066844 | 0.0067003 | 0.0067161 | 0.006732 | 0.0067478 | 33701.7776 | 5314.4363 | 3011.7316 | 474.9202 | 30716.0235 | 30716.0235 | 659857.1334 | 30716.0235
| EHK031-15417885 | 0 | EHK031 | EHK | North | 0 | 0.0021813 | 0.0022585 | 0.0023124 | 0.0023584 | 0.0023959 | 0.0024432 | 0.0025368 | 0.0026369 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33701.7776 | 5314.4363 | 0 | 0 | 0 | 0 | 0 | 0
| EHK031-15417924 | 674 | EHK031 | EHK | North | 15883703.8533 | 0.0021813 | 0.0022585 | 0.0023124 | 0.0023584 | 0.0023959 | 0.0024432 | 0.0025368 | 0.0026369 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 183.8058 | 184.9938 | 186.1818 | 187.3699 | 188.5579 | 188.9632 | 189.3685 | 189.7737 | 190.179 | 190.5843 | 190.9896 | 191.3949 | 191.8002 | 192.2054 | 192.6107 | 193.016 | 193.4213 | 193.8266 | 194.2318 | 194.6371 | 11.1622 | 11.6316 | 11.9858 | 12.3023 | 12.5772 | 12.8531 | 13.3738 | 13.9316 | 14.3539 | 14.3845 | 14.4151 | 14.4457 | 14.4763 | 14.5069 | 14.5375 | 14.5681 | 14.5986 | 14.6292 | 14.6598 | 14.6904 | 33701.7776 | 5314.4363 | 6575800.1141 | 1036938.509 | 19503091.3522 | 19503091.3522 | 15883703.8533 | 19503091.3522
| EHK031-156804503 | 105 | EHK031 | EHK | North | 2474464.2501 | 0.0021813 | 0.0022585 | 0.0023124 | 0.0023584 | 0.0023959 | 0.0024432 | 0.0025368 | 0.0026369 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 2.6683 | 2.6824 | 2.6966 | 2.7107 | 2.7248 | 2.7253 | 2.7258 | 2.7263 | 2.7267 | 2.7272 | 2.7277 | 2.7282 | 2.7286 | 2.7291 | 2.7296 | 2.73 | 2.7305 | 2.731 | 2.7315 | 2.7319 | 0.16204 | 0.16866 | 0.1736 | 0.17798 | 0.18175 | 0.18537 | 0.1925 | 0.20014 | 0.2058 | 0.20584 | 0.20587 | 0.20591 | 0.20595 | 0.20598 | 0.20602 | 0.20605 | 0.20609 | 0.20612 | 0.20616 | 0.2062 | 33701.7776 | 5314.4363 | 94096.1451 | 14838.0296 | 444029.5805 | 444029.5805 | 2474464.2501 | 444029.5805
| EHK031-156804528 | 231 | EHK031 | EHK | North | 5443821.3503 | 0.0021813 | 0.0022585 | 0.0023124 | 0.0023584 | 0.0023959 | 0.0024432 | 0.0025368 | 0.0026369 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 0.0027111 | 2.7263 | 2.7437 | 2.7611 | 2.7785 | 2.7958 | 2.8012 | 2.8066 | 2.812 | 2.8174 | 2.8228 | 2.8282 | 2.8336 | 2.839 | 2.8444 | 2.8498 | 2.8552 | 2.8606 | 2.866 | 2.8714 | 2.8768 | 0.16557 | 0.17251 | 0.17775 | 0.18243 | 0.18649 | 0.19054 | 0.19821 | 0.20643 | 0.21265 | 0.21305 | 0.21346 | 0.21387 | 0.21427 | 0.21468 | 0.21509 | 0.2155 | 0.2159 | 0.21631 | 0.21672 | 0.21713 | 33701.7776 | 5314.4363 | 97393.8859 | 15358.0506 | 961048.1976 | 961048.1976 | 5443821.3503 | 961048.1976
| EHK032-15417935 | 0 | EHK032 | EHK | North | 0 | 0.0028304 | 0.0028198 | 0.0028198 | 0.0028198 | 0.0028445 | 0.0028799 | 0.0029152 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33701.7776 | 5314.4363 | 0 | 0 | 0 | 0 | 0 | 0
| EHK032-15417948 | 33 | EHK032 | EHK | North | 777688.7643 | 0.0028304 | 0.0028198 | 0.0028198 | 0.0028198 | 0.0028445 | 0.0028799 | 0.0029152 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0.0029505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33701.7776 | 5314.4363 | 0 | 0 | 0 | 0 | 777688.7643 | 0
| EHK033-15418024 | 420 | EHK033 | EHK | North | 9897857.0005 | 0.0013299 | 0.0013691 | 0.0014005 | 0.0014265 | 0.0014484 | 0.0014773 | 0.001515 | 0.0015559 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 0.0015875 | 763.7168 | 767.9218 | 772.1267 | 776.3317 | 780.5366 | 781.3918 | 782.2469 | 783.102 | 783.9571 | 784.8122 | 785.6673 | 786.5225 | 787.3776 | 788.2327 | 789.0878 | 789.9429 | 790.798 | 791.6532 | 792.5083 | 793.3634 | 28.2761 | 29.269 | 30.1062 | 30.8304 | 31.4735 | 32.1375 | 32.9936 | 33.9213 | 34.6476 | 34.6854 | 34.7232 | 34.761 | 34.7988 | 34.8366 | 34.8744 | 34.9122 | 34.95 | 34.9878 | 35.0256 | 35.0634 | 33701.7776 | 5314.4363 | 16069125.793 | 2533941.8857 | 20431545.733 | 20431545.733 | 9897857.0005 | 20431545.733
| EHK034-15431419 | 67 | EHK034 | EHK | North | 1578943.8548 | 0.0035422 | 0.003518 | 0.0034707 | 0.0034274 | 0.0033789 | 0.0033395 | 0.0033209 | 0.0033041 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0.0032911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33701.7776 | 5314.4363 | 0 | 0 | 0 | 0 | 1578943.8548 | 0
| FNS011-15405543 | 341 | FNS011 | FNS | South | 6199649.7758 | 0.0020848 | 0.0021092 | 0.0021269 | 0.0021382 | 0.0021323 | 0.0021396 | 0.0021696 | 0.0022027 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 56.7662 | 57.1043 | 57.4423 | 57.7803 | 58.1183 | 58.3839 | 58.6494 | 58.9149 | 59.1804 | 59.4459 | 59.7114 | 59.9769 | 60.2425 | 60.508 | 60.7735 | 61.039 | 61.3045 | 61.57 | 61.8355 | 62.1011 | 3.2948 | 3.3531 | 3.4014 | 3.4394 | 3.4501 | 3.4778 | 3.5425 | 3.6129 | 3.6344 | 3.6507 | 3.667 | 3.6833 | 3.6996 | 3.7159 | 3.7322 | 3.7485 | 3.7648 | 3.7811 | 3.7975 | 3.8138 | 38932.1147 | 6166.9477 | 2016848.7534 | 319474.0608 | 2641671.4775 | 3424190.4701 | 6469892.2758 | 2756821.8376
| FNS011-24604152 | 74 | FNS011 | FNS | South | 1345378.5437 | 0.0020848 | 0.0021092 | 0.0021269 | 0.0021382 | 0.0021323 | 0.0021396 | 0.0021696 | 0.0022027 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 0.0022059 | 1.4319 | 1.4417 | 1.4515 | 1.4613 | 1.4711 | 1.4788 | 1.4865 | 1.4942 | 1.5019 | 1.5097 | 1.5174 | 1.5251 | 1.5328 | 1.5405 | 1.5482 | 1.556 | 1.5637 | 1.5714 | 1.5791 | 1.5868 | 0.083106 | 0.084653 | 0.085948 | 0.086984 | 0.087329 | 0.088088 | 0.089788 | 0.091632 | 0.092238 | 0.092712 | 0.093186 | 0.093659 | 0.094133 | 0.094607 | 0.095081 | 0.095555 | 0.096029 | 0.096503 | 0.096976 | 0.09745 | 38932.1147 | 6166.9477 | 51195.7419 | 8109.538 | 121854.7813 | 157950.7462 | 1404023.5437 | 127166.4267
| FNS012-15405393 | 260 | FNS012 | FNS | South | 4727005.6942 | 0.0011069 | 0.0011273 | 0.0011536 | 0.0011806 | 0.0012044 | 0.0012412 | 0.0012858 | 0.0013233 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 60.3646 | 60.8608 | 61.357 | 61.8532 | 62.3494 | 62.5812 | 62.813 | 63.0448 | 63.2766 | 63.5084 | 63.7402 | 63.972 | 64.2038 | 64.4356 | 64.6674 | 64.8992 | 65.131 | 65.3628 | 65.5946 | 65.8264 | 1.8601 | 1.9101 | 1.9705 | 2.033 | 2.0905 | 2.1626 | 2.2485 | 2.3227 | 2.3725 | 2.3812 | 2.3899 | 2.3986 | 2.4073 | 2.416 | 2.4246 | 2.4333 | 2.442 | 2.4507 | 2.4594 | 2.4681 | 38932.1147 | 6166.9477 | 1264075.1784 | 200232.7788 | 1538763.3626 | 1994577.6327 | 4933055.6942 | 1605837.9996
| FNS012-76065032 | 135 | FNS012 | FNS | South | 2454406.8027 | 0.0011069 | 0.0011273 | 0.0011536 | 0.0011806 | 0.0012044 | 0.0012412 | 0.0012858 | 0.0013233 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 0.0013468 | 5.6676 | 5.7098 | 5.752 | 5.7942 | 5.8364 | 5.8724 | 5.9084 | 5.9445 | 5.9805 | 6.0165 | 6.0526 | 6.0886 | 6.1246 | 6.1607 | 6.1967 | 6.2327 | 6.2688 | 6.3048 | 6.3408 | 6.3769 | 0.17464 | 0.1792 | 0.18472 | 0.19044 | 0.19569 | 0.20293 | 0.2115 | 0.219 | 0.22423 | 0.22558 | 0.22694 | 0.22829 | 0.22964 | 0.23099 | 0.23234 | 0.23369 | 0.23504 | 0.23639 | 0.23774 | 0.23909 | 38932.1147 | 6166.9477 | 119892.0892 | 18991.2171 | 133769.9626 | 173395.4563 | 2561394.3027 | 139600.9903
| FNS013-15405406 | 441 | FNS013 | FNS | South | 8017728.889 | 0.0014161 | 0.0014494 | 0.0014742 | 0.0014997 | 0.0015196 | 0.0015422 | 0.0015749 | 0.0016104 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 72.5472 | 73.1578 | 73.7683 | 74.3789 | 74.9894 | 74.8302 | 74.671 | 74.5118 | 74.3526 | 74.1934 | 74.0342 | 73.875 | 73.7158 | 73.5566 | 73.3974 | 73.2382 | 73.079 | 72.9198 | 72.7606 | 72.6014 | 2.8601 | 2.952 | 3.0277 | 3.1054 | 3.1725 | 3.2128 | 3.274 | 3.3406 | 3.3949 | 3.3877 | 3.3804 | 3.3731 | 3.3659 | 3.3586 | 3.3513 | 3.3441 | 3.3368 | 3.3295 | 3.3223 | 3.315 | 38932.1147 | 6166.9477 | 1821675.2373 | 288558.0709 | 2162162.8299 | 2802641.214 | 8367221.389 | 2256411.4261
| FNS013-73561266 | 231 | FNS013 | FNS | South | 4199762.7514 | 0.0014161 | 0.0014494 | 0.0014742 | 0.0014997 | 0.0015196 | 0.0015422 | 0.0015749 | 0.0016104 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 0.0016401 | 1.6144 | 1.6261 | 1.6378 | 1.6495 | 1.6612 | 1.6673 | 1.6734 | 1.6795 | 1.6855 | 1.6916 | 1.6977 | 1.7038 | 1.7099 | 1.7159 | 1.722 | 1.7281 | 1.7342 | 1.7402 | 1.7463 | 1.7524 | 0.063647 | 0.065617 | 0.067221 | 0.06887 | 0.070281 | 0.071585 | 0.07337 | 0.075296 | 0.076962 | 0.07724 | 0.077517 | 0.077795 | 0.078072 | 0.07835 | 0.078627 | 0.078905 | 0.079182 | 0.07946 | 0.079737 | 0.080014 | 38932.1147 | 6166.9477 | 41619.77 | 6592.6793 | 1054267.114 | 1366563.3427 | 4382830.2514 | 1100222.5777
| FNS021-15405600 | 241 | FNS021 | FNS | South | 4381570.6627 | 0.0034296 | 0.0034966 | 0.0035428 | 0.0035814 | 0.0035997 | 0.0036531 | 0.003758 | 0.003851 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 55.9815 | 56.2057 | 56.4298 | 56.6539 | 56.878 | 56.9604 | 57.0427 | 57.125 | 57.2073 | 57.2897 | 57.372 | 57.4543 | 57.5366 | 57.619 | 57.7013 | 57.7836 | 57.866 | 57.9483 | 58.0306 | 58.1129 | 5.3452 | 5.4714 | 5.5657 | 5.6487 | 5.7001 | 5.793 | 5.9679 | 6.1245 | 6.2024 | 6.2114 | 6.2203 | 6.2292 | 6.2381 | 6.2471 | 6.256 | 6.2649 | 6.2738 | 6.2828 | 6.2917 | 6.3006 | 38932.1147 | 6166.9477 | 3363392.4183 | 532770.0613 | 1861452.7377 | 2412854.4291 | 4572563.1627 | 1942593.3923
| FNS021-24604138 | 64 | FNS021 | FNS | South | 1163570.6324 | 0.0034296 | 0.0034966 | 0.0035428 | 0.0035814 | 0.0035997 | 0.0036531 | 0.003758 | 0.003851 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 0.0038944 | 2.8211 | 2.8427 | 2.8642 | 2.8858 | 2.9073 | 2.9259 | 2.9445 | 2.963 | 2.9816 | 3.0002 | 3.0187 | 3.0373 | 3.0559 | 3.0744 | 3.093 | 3.1115 | 3.1301 | 3.1487 | 3.1672 | 3.1858 | 0.26936 | 0.27672 | 0.2825 | 0.28773 | 0.29136 | 0.29757 | 0.30805 | 0.31767 | 0.32327 | 0.32528 | 0.32729 | 0.3293 | 0.33132 | 0.33333 | 0.33534 | 0.33735 | 0.33937 | 0.34138 | 0.34339 | 0.34541 | 38932.1147 | 6166.9477 | 175950.5161 | 27871.017 | 76824.7872 | 99581.9149 | 1214290.6324 | 80173.5768
| FNS022-15405419 | 388 | FNS022 | FNS | South | 7054146.959 | 0.0036473 | 0.0037275 | 0.0037841 | 0.0038319 | 0.0038735 | 0.0039419 | 0.0040458 | 0.0041404 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 56.3293 | 56.6996 | 57.07 | 57.4404 | 57.8107 | 57.7765 | 57.7423 | 57.7081 | 57.6738 | 57.6396 | 57.6054 | 57.5711 | 57.5369 | 57.5027 | 57.4684 | 57.4342 | 57.4 | 57.3658 | 57.3315 | 57.2973 | 5.7197 | 5.8839 | 6.0122 | 6.1277 | 6.2342 | 6.3405 | 6.5037 | 6.6519 | 6.7032 | 6.6993 | 6.6953 | 6.6913 | 6.6873 | 6.6833 | 6.6794 | 6.6754 | 6.6714 | 6.6674 | 6.6634 | 6.6595 | 38932.1147 | 6166.9477 | 3619926.8595 | 573405.7805 | 6802755.3266 | 8817875.4088 | 7361636.959 | 7099287.1749
| FNS022-24604096 | 450 | FNS022 | FNS | South | 8181356.0092 | 0.0036473 | 0.0037275 | 0.0037841 | 0.0038319 | 0.0038735 | 0.0039419 | 0.0040458 | 0.0041404 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 0.0041748 | 13.5807 | 13.6935 | 13.8063 | 13.9191 | 14.0319 | 14.0615 | 14.0911 | 14.1206 | 14.1502 | 14.1798 | 14.2094 | 14.239 | 14.2686 | 14.2982 | 14.3278 | 14.3574 | 14.387 | 14.4166 | 14.4462 | 14.4757 | 1.379 | 1.421 | 1.4545 | 1.4849 | 1.5132 | 1.5431 | 1.5871 | 1.6277 | 1.6446 | 1.6481 | 1.6515 | 1.655 | 1.6584 | 1.6618 | 1.6653 | 1.6687 | 1.6721 | 1.6756 | 1.679 | 1.6825 | 38932.1147 | 6166.9477 | 890189.2187 | 141008.2755 | 2902084.2855 | 3761743.0624 | 8537981.0092 | 3028586.0301
| FNS032-15405445 | 142 | FNS032 | FNS | South | 2581672.3407 | 0.013763 | 0.013853 | 0.013853 | 0.013815 | 0.013748 | 0.013732 | 0.013815 | 0.013853 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 4.0131 | 4.0397 | 4.0664 | 4.0931 | 4.1197 | 4.1238 | 4.1278 | 4.1319 | 4.136 | 4.14 | 4.1441 | 4.1481 | 4.1522 | 4.1563 | 4.1603 | 4.1644 | 4.1684 | 4.1725 | 4.1766 | 4.1806 | 1.5377 | 1.558 | 1.5682 | 1.5742 | 1.5768 | 1.5765 | 1.5876 | 1.5935 | 1.5881 | 1.5897 | 1.5912 | 1.5928 | 1.5944 | 1.5959 | 1.5975 | 1.599 | 1.6006 | 1.6022 | 1.6037 | 1.6053 | 38932.1147 | 6166.9477 | 891449.2552 | 141207.8685 | 687551.8075 | 891219.2023 | 2694207.3407 | 717522.1649
| FNS032-156356596 | 12 | FNS032 | FNS | South | 218169.4936 | 0.013763 | 0.013853 | 0.013853 | 0.013815 | 0.013748 | 0.013732 | 0.013815 | 0.013853 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.00030031 | 0.00030349 | 0.00030666 | 0.00030983 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.000313 | 0.00011507 | 0.00011704 | 0.00011826 | 0.00011916 | 0.0001198 | 0.00011966 | 0.00012038 | 0.00012071 | 0.00012019 | 0.00012019 | 0.00012019 | 0.00012019 | 0.00012019 | 0.00012019 | 0.00012019 | 0.00012019 | 0.00012019 | 0.00012019 | 0.00012019 | 0.00012019 | 38932.1147 | 6166.9477 | 67.2309 | 10.6496 | 98.0786 | 127.1316 | 227679.4936 | 102.3539
| FNS032-24606816 | 232 | FNS032 | FNS | South | 4217943.5425 | 0.013763 | 0.013853 | 0.013853 | 0.013815 | 0.013748 | 0.013732 | 0.013815 | 0.013853 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 0.013792 | 2.0816 | 2.0945 | 2.1073 | 2.1201 | 2.133 | 2.129 | 2.125 | 2.1211 | 2.1171 | 2.1131 | 2.1092 | 2.1052 | 2.1012 | 2.0973 | 2.0933 | 2.0893 | 2.0853 | 2.0814 | 2.0774 | 2.0734 | 0.79762 | 0.80775 | 0.8127 | 0.81541 | 0.81637 | 0.81393 | 0.81729 | 0.81801 | 0.81293 | 0.8114 | 0.80988 | 0.80835 | 0.80683 | 0.80531 | 0.80378 | 0.80226 | 0.80073 | 0.79921 | 0.79769 | 0.79616 | 38932.1147 | 6166.9477 | 455092.4038 | 72087.8142 | 950905.3695 | 1232583.6622 | 4401803.5425 | 992355.2987
| GB011-15403523 | 4 | GB011 | GB | South | 72723.1645 | 0.36075 | 0.36075 | 0.36 | 0.36075 | 0.3665 | 0.37225 | 0.37475 | 0.37225 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33266.8997 | 2572.7789 | 0 | 0 | 0 | 0 | 75893.1645 | 0
| GB011-15403536 | 4 | GB011 | GB | South | 72723.1645 | 0.36075 | 0.36075 | 0.36 | 0.36075 | 0.3665 | 0.37225 | 0.37475 | 0.37225 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33266.8997 | 2572.7789 | 0 | 0 | 0 | 0 | 75893.1645 | 0
| GB012-15403573 | 92 | GB012 | GB | South | 1672632.7841 | 0.13131 | 0.13224 | 0.13193 | 0.1315 | 0.13076 | 0.13033 | 0.13039 | 0.13057 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.13052 | 0.4944 | 0.4955 | 0.4966 | 0.49771 | 0.49881 | 0.49648 | 0.49416 | 0.49184 | 0.48952 | 0.48719 | 0.48487 | 0.48255 | 0.48023 | 0.4779 | 0.47558 | 0.47326 | 0.47093 | 0.46861 | 0.46629 | 0.46397 | 1.8074 | 1.8242 | 1.8239 | 1.8221 | 1.8158 | 1.8015 | 1.7938 | 1.7879 | 1.7787 | 1.7703 | 1.7618 | 1.7534 | 1.745 | 1.7365 | 1.7281 | 1.7196 | 1.7112 | 1.7028 | 1.6943 | 1.6859 | 33266.8997 | 2572.7789 | 852261.8877 | 65911.8053 | 435696.7141 | 564759.3007 | 1745542.7841 | 454688.7174
| GB014-15403449 | 1 | GB014 | GB | South | 18180.7911 | 0.0010623 | 0.001099 | 0.0011421 | 0.0011815 | 0.0012246 | 0.0012731 | 0.0013217 | 0.0013676 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33266.8997 | 2572.7789 | 0 | 0 | 0 | 0 | 18973.2911 | 0
| GB014-15403475 | 73 | GB014 | GB | South | 1327197.7526 | 0.0010623 | 0.001099 | 0.0011421 | 0.0011815 | 0.0012246 | 0.0012731 | 0.0013217 | 0.0013676 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0014042 | 0.0073396 | 0.0073643 | 0.0073889 | 0.0074136 | 0.0074382 | 0.007422 | 0.0074059 | 0.0073897 | 0.0073735 | 0.0073574 | 0.0073412 | 0.007325 | 0.0073088 | 0.0072927 | 0.0072765 | 0.0072603 | 0.0072442 | 0.007228 | 0.0072118 | 0.0071957 | 0.00021707 | 0.00022532 | 0.00023493 | 0.00024385 | 0.00025358 | 0.00026307 | 0.00027251 | 0.00028135 | 0.00028826 | 0.00028762 | 0.00028699 | 0.00028636 | 0.00028573 | 0.0002851 | 0.00028446 | 0.00028383 | 0.0002832 | 0.00028257 | 0.00028193 | 0.0002813 | 33266.8997 | 2572.7789 | 128.3219 | 9.9241 | 261.3531 | 338.7714 | 1385050.2526 | 272.7455
| GB031-15403499 | 257 | GB031 | GB | South | 4672463.3208 | 0.0041338 | 0.0041599 | 0.0042019 | 0.0042336 | 0.0042629 | 0.0043254 | 0.0044204 | 0.0045075 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0.0045313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33266.8997 | 2572.7789 | 0 | 0 | 0 | 0 | 4876135.8208 | 0
| GB032-15403425 | 1 | GB032 | GB | South | 18180.7911 | 1.0587 | 1.0687 | 1.0637 | 1.0603 | 1.0565 | 1.0543 | 1.0527 | 1.0527 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33266.8997 | 2572.7789 | 0 | 0 | 0 | 0 | 18973.2911 | 0
| GB032-15403438 | 20 | GB032 | GB | South | 363615.8226 | 1.0587 | 1.0687 | 1.0637 | 1.0603 | 1.0565 | 1.0543 | 1.0527 | 1.0527 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 1.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33266.8997 | 2572.7789 | 0 | 0 | 0 | 0 | 379465.8226 | 0
| GCY011-153967160 | 118 | GCY011 | GCY | South | 2145333.3535 | 0.0015696 | 0.0015866 | 0.0015937 | 0.0016 | 0.0015966 | 0.0016016 | 0.0016157 | 0.0016358 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38111.0689 | 5619.5185 | 0 | 0 | 0 | 0 | 2238848.3535 | 0
| GCY011-15403919 | 319 | GCY011 | GCY | South | 5799672.3709 | 0.0015696 | 0.0015866 | 0.0015937 | 0.0016 | 0.0015966 | 0.0016016 | 0.0016157 | 0.0016358 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0.0016463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38111.0689 | 5619.5185 | 0 | 0 | 0 | 0 | 6052479.8709 | 0
| GCY012-15403889 | 22 | GCY012 | GCY | South | 399977.4049 | 0.003224 | 0.0032144 | 0.0031736 | 0.0031232 | 0.0030711 | 0.003023 | 0.002995 | 0.002967 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0.0029272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38111.0689 | 5619.5185 | 0 | 0 | 0 | 0 | 417412.4049 | 0
| GCY013-15403874 | 7 | GCY013 | GCY | South | 127265.5379 | 0.0070173 | 0.0070173 | 0.0069552 | 0.0068931 | 0.0068165 | 0.0067543 | 0.006711 | 0.0066864 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0.0066532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38111.0689 | 5619.5185 | 0 | 0 | 0 | 0 | 132813.0379 | 0
| GCY014-116530590 | 512 | GCY014 | GCY | South | 9308565.0593 | 0.0014556 | 0.0014588 | 0.0014579 | 0.0014592 | 0.001483 | 0.0015185 | 0.0015667 | 0.0016121 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38111.0689 | 5619.5185 | 0 | 0 | 0 | 0 | 9714325.0593 | 0
| GCY014-15403904 | 76 | GCY014 | GCY | South | 1381740.126 | 0.0014556 | 0.0014588 | 0.0014579 | 0.0014592 | 0.001483 | 0.0015185 | 0.0015667 | 0.0016121 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0.0016434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38111.0689 | 5619.5185 | 0 | 0 | 0 | 0 | 1441970.126 | 0
| GCY022-15403949 | 47 | GCY022 | GCY | South | 854497.1832 | 0.005599 | 0.0055952 | 0.0055569 | 0.0054995 | 0.0054201 | 0.0053694 | 0.0053569 | 0.0053569 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0.0053033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38111.0689 | 5619.5185 | 0 | 0 | 0 | 0 | 891744.6832 | 0
| GCY024-15403979 | 97 | GCY024 | GCY | South | 1763536.7398 | 0.0015837 | 0.0015863 | 0.00158 | 0.0015759 | 0.001567 | 0.0015623 | 0.0015641 | 0.0015872 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38111.0689 | 5619.5185 | 0 | 0 | 0 | 0 | 1840409.2398 | 0
| GCY024-77737752 | 128 | GCY024 | GCY | South | 2327141.2648 | 0.0015837 | 0.0015863 | 0.00158 | 0.0015759 | 0.001567 | 0.0015623 | 0.0015641 | 0.0015872 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.0016096 | 0.17782 | 0.17861 | 0.17939 | 0.18018 | 0.18096 | 0.18061 | 0.18025 | 0.17989 | 0.17954 | 0.17918 | 0.17882 | 0.17847 | 0.17811 | 0.17775 | 0.1774 | 0.17704 | 0.17668 | 0.17633 | 0.17597 | 0.17561 | 0.0078401 | 0.007888 | 0.0078911 | 0.0079052 | 0.0078945 | 0.0078553 | 0.007849 | 0.0079489 | 0.0080452 | 0.0080292 | 0.0080132 | 0.0079972 | 0.0079812 | 0.0079652 | 0.0079493 | 0.0079333 | 0.0079173 | 0.0079013 | 0.0078853 | 0.0078693 | 38111.0689 | 5619.5185 | 4366.9049 | 643.9049 | 3819.2058 | 4950.5354 | 2428581.2648 | 3985.6848
| GHP011-123128913 | 14 | GHP011 | GHP | South | 254531.0758 | 0.0037036 | 0.0037978 | 0.0038736 | 0.0039399 | 0.0039761 | 0.0040341 | 0.0041496 | 0.0042764 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.00015493 | 0.00015659 | 0.00015826 | 0.00015993 | 0.0001616 | 0.00016188 | 0.00016216 | 0.00016244 | 0.00016272 | 0.000163 | 0.00016328 | 0.00016356 | 0.00016384 | 0.00016412 | 0.0001644 | 0.00016468 | 0.00016496 | 0.00016524 | 0.00016552 | 0.0001658 | 1.5974e-05 | 1.6557e-05 | 1.7067e-05 | 1.7542e-05 | 1.7888e-05 | 1.818e-05 | 1.8734e-05 | 1.934e-05 | 1.9819e-05 | 1.9853e-05 | 1.9888e-05 | 1.9922e-05 | 1.9956e-05 | 1.999e-05 | 2.0024e-05 | 2.0058e-05 | 2.0092e-05 | 2.0126e-05 | 2.016e-05 | 2.0194e-05 | 34766.6344 | 8178.6057 | 9.4632 | 2.2261 | 74.4837 | 96.5473 | 265626.0758 | 77.7304
| GHP011-124927621 | 35 | GHP011 | GHP | South | 636327.6896 | 0.0037036 | 0.0037978 | 0.0038736 | 0.0039399 | 0.0039761 | 0.0040341 | 0.0041496 | 0.0042764 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.053218 | 0.053669 | 0.05412 | 0.054571 | 0.055022 | 0.054978 | 0.054934 | 0.054889 | 0.054845 | 0.054801 | 0.054756 | 0.054712 | 0.054668 | 0.054624 | 0.054579 | 0.054535 | 0.054491 | 0.054446 | 0.054402 | 0.054358 | 0.0054873 | 0.0056745 | 0.0058363 | 0.0059857 | 0.0060906 | 0.0061745 | 0.0063463 | 0.0065349 | 0.0066801 | 0.0066747 | 0.0066693 | 0.0066639 | 0.0066585 | 0.0066531 | 0.0066478 | 0.0066424 | 0.006637 | 0.0066316 | 0.0066262 | 0.0066208 | 34766.6344 | 8178.6057 | 3183.3263 | 748.8551 | 27859.2414 | 36111.7383 | 664065.1896 | 29073.6247
| GHP011-144337307 | 27 | GHP011 | GHP | South | 490881.3605 | 0.0037036 | 0.0037978 | 0.0038736 | 0.0039399 | 0.0039761 | 0.0040341 | 0.0041496 | 0.0042764 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.050245 | 0.050647 | 0.05105 | 0.051452 | 0.051854 | 0.052086 | 0.052317 | 0.052548 | 0.05278 | 0.053011 | 0.053242 | 0.053473 | 0.053705 | 0.053936 | 0.054167 | 0.054399 | 0.05463 | 0.054861 | 0.055093 | 0.055324 | 0.0051807 | 0.005355 | 0.0055052 | 0.0056435 | 0.00574 | 0.0058496 | 0.006044 | 0.0062562 | 0.0064285 | 0.0064567 | 0.0064849 | 0.0065131 | 0.0065412 | 0.0065694 | 0.0065976 | 0.0066258 | 0.0066539 | 0.0066821 | 0.0067103 | 0.0067384 | 34766.6344 | 8178.6057 | 3084.5705 | 725.6235 | 26743.7141 | 34665.7681 | 512278.8605 | 27909.4715
| GHP011-144337672 | 80 | GHP011 | GHP | South | 1454463.2905 | 0.0037036 | 0.0037978 | 0.0038736 | 0.0039399 | 0.0039761 | 0.0040341 | 0.0041496 | 0.0042764 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.063153 | 0.063554 | 0.063956 | 0.064357 | 0.064759 | 0.064934 | 0.065109 | 0.065285 | 0.06546 | 0.065635 | 0.065811 | 0.065986 | 0.066161 | 0.066337 | 0.066512 | 0.066687 | 0.066863 | 0.067038 | 0.067213 | 0.067389 | 0.0065116 | 0.0067197 | 0.006897 | 0.0070591 | 0.0071684 | 0.0072926 | 0.0075218 | 0.0077726 | 0.007973 | 0.0079944 | 0.0080157 | 0.0080371 | 0.0080584 | 0.0080798 | 0.0081012 | 0.0081225 | 0.0081439 | 0.0081652 | 0.0081866 | 0.0082079 | 34766.6344 | 8178.6057 | 3820.8923 | 898.838 | 65468.994 | 84862.2954 | 1517863.2905 | 68322.7849
| GHP011-187048453 | 521 | GHP011 | GHP | South | 9472192.1795 | 0.0037036 | 0.0037978 | 0.0038736 | 0.0039399 | 0.0039761 | 0.0040341 | 0.0041496 | 0.0042764 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 25.5075 | 25.6981 | 25.8886 | 26.0792 | 26.2697 | 26.3121 | 26.3545 | 26.3969 | 26.4393 | 26.4817 | 26.5241 | 26.5665 | 26.6089 | 26.6513 | 26.6937 | 26.7361 | 26.7785 | 26.8209 | 26.8633 | 26.9057 | 2.6301 | 2.7171 | 2.7918 | 2.8605 | 2.9079 | 2.9551 | 3.0446 | 3.1427 | 3.2203 | 3.2255 | 3.2306 | 3.2358 | 3.241 | 3.2461 | 3.2513 | 3.2565 | 3.2616 | 3.2668 | 3.272 | 3.2771 | 34766.6344 | 8178.6057 | 1540192.3415 | 362319.3933 | 3484862.0813 | 4517151.9737 | 9885084.6795 | 3636767.0881
| GHP011-190579532 | 554 | GHP011 | GHP | South | 10072158.2868 | 0.0037036 | 0.0037978 | 0.0038736 | 0.0039399 | 0.0039761 | 0.0040341 | 0.0041496 | 0.0042764 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 4.7079 | 4.7465 | 4.785 | 4.8235 | 4.8621 | 4.8607 | 4.8593 | 4.8579 | 4.8565 | 4.8552 | 4.8538 | 4.8524 | 4.851 | 4.8496 | 4.8482 | 4.8468 | 4.8455 | 4.8441 | 4.8427 | 4.8413 | 0.48543 | 0.50185 | 0.51601 | 0.52907 | 0.5382 | 0.5459 | 0.56138 | 0.57837 | 0.59153 | 0.59136 | 0.59119 | 0.59102 | 0.59085 | 0.59068 | 0.59051 | 0.59035 | 0.59018 | 0.59001 | 0.58984 | 0.58967 | 34766.6344 | 8178.6057 | 282118.6124 | 66366.4152 | 1148140.4274 | 1488243.918 | 10511203.2868 | 1198187.8253
| GHP011-62939475 | 328 | GHP011 | GHP | South | 5963299.4911 | 0.0037036 | 0.0037978 | 0.0038736 | 0.0039399 | 0.0039761 | 0.0040341 | 0.0041496 | 0.0042764 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 4.8219 | 4.8516 | 4.8814 | 4.9111 | 4.9408 | 4.9582 | 4.9755 | 4.9928 | 5.0102 | 5.0275 | 5.0448 | 5.0621 | 5.0795 | 5.0968 | 5.1141 | 5.1315 | 5.1488 | 5.1661 | 5.1835 | 5.2008 | 0.49718 | 0.51297 | 0.5264 | 0.53868 | 0.54692 | 0.55684 | 0.5748 | 0.59443 | 0.61024 | 0.61235 | 0.61446 | 0.61657 | 0.61868 | 0.62079 | 0.6229 | 0.62501 | 0.62712 | 0.62923 | 0.63135 | 0.63346 | 34766.6344 | 8178.6057 | 292762.4609 | 68870.3056 | 950614.3289 | 1232206.4092 | 6223239.4911 | 992051.5716
| GHP011-72503866 | 153 | GHP011 | GHP | South | 2781661.0431 | 0.0037036 | 0.0037978 | 0.0038736 | 0.0039399 | 0.0039761 | 0.0040341 | 0.0041496 | 0.0042764 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.004375 | 0.1152 | 0.11621 | 0.11722 | 0.11823 | 0.11924 | 0.11915 | 0.11905 | 0.11896 | 0.11887 | 0.11878 | 0.11868 | 0.11859 | 0.1185 | 0.11841 | 0.11831 | 0.11822 | 0.11813 | 0.11804 | 0.11794 | 0.11785 | 0.011878 | 0.012287 | 0.012641 | 0.012968 | 0.013199 | 0.013381 | 0.013754 | 0.014163 | 0.014478 | 0.014467 | 0.014456 | 0.014444 | 0.014433 | 0.014422 | 0.014411 | 0.014399 | 0.014388 | 0.014377 | 0.014366 | 0.014354 | 34766.6344 | 8178.6057 | 6898.5619 | 1622.8381 | 67863.2096 | 87965.7283 | 2902913.5431 | 70821.3643
| GHP012-190579518 | 405 | GHP012 | GHP | South | 7363220.4082 | 0.0025731 | 0.0026181 | 0.0026561 | 0.0026847 | 0.0027025 | 0.0027225 | 0.0027678 | 0.0028172 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 30.9983 | 31.2185 | 31.4386 | 31.6587 | 31.8789 | 31.9829 | 32.0869 | 32.1909 | 32.295 | 32.399 | 32.503 | 32.607 | 32.7111 | 32.8151 | 32.9191 | 33.0231 | 33.1271 | 33.2312 | 33.3352 | 33.4392 | 2.2205 | 2.2754 | 2.3248 | 2.3663 | 2.3985 | 2.4241 | 2.4725 | 2.5248 | 2.5684 | 2.5767 | 2.585 | 2.5932 | 2.6015 | 2.6098 | 2.618 | 2.6263 | 2.6346 | 2.6429 | 2.6511 | 2.6594 | 34766.6344 | 8178.6057 | 1253428.1644 | 294860.1417 | 1783995.7606 | 2312453.0564 | 7684182.9082 | 1861760.0685
| GHP012-77546539 | 142 | GHP012 | GHP | South | 2581672.3407 | 0.0025731 | 0.0026181 | 0.0026561 | 0.0026847 | 0.0027025 | 0.0027225 | 0.0027678 | 0.0028172 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 0.0028567 | 6.9486 | 6.9848 | 7.021 | 7.0572 | 7.0935 | 7.0937 | 7.0939 | 7.0941 | 7.0943 | 7.0946 | 7.0948 | 7.095 | 7.0952 | 7.0954 | 7.0957 | 7.0959 | 7.0961 | 7.0963 | 7.0965 | 7.0968 | 0.49776 | 0.5091 | 0.51918 | 0.52748 | 0.53369 | 0.53766 | 0.54662 | 0.5564 | 0.56421 | 0.56423 | 0.56424 | 0.56426 | 0.56428 | 0.5643 | 0.56431 | 0.56433 | 0.56435 | 0.56437 | 0.56439 | 0.5644 | 34766.6344 | 8178.6057 | 274615.1982 | 64601.2899 | 137111.7222 | 177727.1158 | 2694207.3407 | 143088.417
| GHP021-130746528 | 89 | GHP021 | GHP | South | 1618090.4107 | 0.0029461 | 0.0030217 | 0.0030882 | 0.0031923 | 0.003306 | 0.003463 | 0.003653 | 0.003829 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 10.2125 | 10.2919 | 10.3713 | 10.4506 | 10.53 | 10.5912 | 10.6524 | 10.7136 | 10.7747 | 10.8359 | 10.8971 | 10.9583 | 11.0195 | 11.0807 | 11.1419 | 11.2031 | 11.2642 | 11.3254 | 11.3866 | 11.4478 | 0.83761 | 0.8658 | 0.89167 | 0.92879 | 0.96916 | 1.0211 | 1.0833 | 1.1421 | 1.1859 | 1.1927 | 1.1994 | 1.2061 | 1.2129 | 1.2196 | 1.2263 | 1.2331 | 1.2398 | 1.2465 | 1.2533 | 1.26 | 34766.6344 | 8178.6057 | 550041.61 | 129393.4121 | 189772.4919 | 245987.1198 | 1688622.9107 | 198044.6676
| GHP021-140732642 | 161 | GHP021 | GHP | South | 2927107.3722 | 0.0029461 | 0.0030217 | 0.0030882 | 0.0031923 | 0.003306 | 0.003463 | 0.003653 | 0.003829 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.04709 | 0.047392 | 0.047694 | 0.047996 | 0.048298 | 0.048354 | 0.048411 | 0.048468 | 0.048524 | 0.048581 | 0.048637 | 0.048694 | 0.048751 | 0.048807 | 0.048864 | 0.04892 | 0.048977 | 0.049034 | 0.04909 | 0.049147 | 0.0038622 | 0.0039868 | 0.0041005 | 0.0042656 | 0.0044452 | 0.0046619 | 0.0049234 | 0.0051667 | 0.0053409 | 0.0053471 | 0.0053533 | 0.0053596 | 0.0053658 | 0.005372 | 0.0053783 | 0.0053845 | 0.0053907 | 0.0053969 | 0.0054032 | 0.0054094 | 34766.6344 | 8178.6057 | 2462.589 | 579.3067 | 62052.6544 | 80433.9638 | 3054699.8722 | 64757.5273
| GHP021-141034135 | 173 | GHP021 | GHP | South | 3145276.8657 | 0.0029461 | 0.0030217 | 0.0030882 | 0.0031923 | 0.003306 | 0.003463 | 0.003653 | 0.003829 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.023146 | 0.0233 | 0.023454 | 0.023608 | 0.023762 | 0.023751 | 0.023741 | 0.02373 | 0.023719 | 0.023709 | 0.023698 | 0.023687 | 0.023677 | 0.023666 | 0.023655 | 0.023645 | 0.023634 | 0.023623 | 0.023612 | 0.023602 | 0.0018984 | 0.0019601 | 0.0020164 | 0.0020981 | 0.002187 | 0.0022899 | 0.0024144 | 0.0025296 | 0.0026107 | 0.0026095 | 0.0026083 | 0.0026072 | 0.002606 | 0.0026048 | 0.0026036 | 0.0026025 | 0.0026013 | 0.0026001 | 0.0025989 | 0.0025978 | 34766.6344 | 8178.6057 | 1200.7531 | 282.4687 | 21471.8358 | 27832.2479 | 3282379.3657 | 22407.7923
| GHP021-187048221 | 328 | GHP021 | GHP | South | 5963299.4911 | 0.0029461 | 0.0030217 | 0.0030882 | 0.0031923 | 0.003306 | 0.003463 | 0.003653 | 0.003829 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 20.3151 | 20.4474 | 20.5798 | 20.7121 | 20.8444 | 20.839 | 20.8335 | 20.8281 | 20.8226 | 20.8172 | 20.8117 | 20.8063 | 20.8008 | 20.7954 | 20.7899 | 20.7845 | 20.779 | 20.7736 | 20.7681 | 20.7627 | 1.6662 | 1.7201 | 1.7694 | 1.8408 | 1.9185 | 2.0091 | 2.1188 | 2.2203 | 2.2919 | 2.2913 | 2.2907 | 2.2901 | 2.2895 | 2.2889 | 2.2883 | 2.2877 | 2.2871 | 2.2865 | 2.2859 | 2.2853 | 34766.6344 | 8178.6057 | 1054484.0232 | 248059.9346 | 1673641.1247 | 2169409.042 | 6223239.4911 | 1746595.0782
| GHP021-190579468 | 260 | GHP021 | GHP | South | 4727005.6942 | 0.0029461 | 0.0030217 | 0.0030882 | 0.0031923 | 0.003306 | 0.003463 | 0.003653 | 0.003829 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 7.2513 | 7.3107 | 7.3701 | 7.4294 | 7.4888 | 7.4998 | 7.5109 | 7.5219 | 7.533 | 7.544 | 7.5551 | 7.5661 | 7.5772 | 7.5882 | 7.5993 | 7.6103 | 7.6214 | 7.6324 | 7.6435 | 7.6545 | 0.59474 | 0.61501 | 0.63364 | 0.66029 | 0.68926 | 0.72306 | 0.76385 | 0.80184 | 0.82913 | 0.83034 | 0.83156 | 0.83278 | 0.83399 | 0.83521 | 0.83642 | 0.83764 | 0.83886 | 0.84007 | 0.84129 | 0.84251 | 34766.6344 | 8178.6057 | 382116.5884 | 89890.2343 | 753941.5262 | 977274.9605 | 4933055.6942 | 786805.8089
| GHP021-24614163 | 143 | GHP021 | GHP | South | 2599853.1318 | 0.0029461 | 0.0030217 | 0.0030882 | 0.0031923 | 0.003306 | 0.003463 | 0.003653 | 0.003829 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 0.0039535 | 5.269 | 5.2746 | 5.2802 | 5.2857 | 5.2913 | 5.2793 | 5.2673 | 5.2553 | 5.2434 | 5.2314 | 5.2194 | 5.2074 | 5.1954 | 5.1834 | 5.1714 | 5.1594 | 5.1474 | 5.1354 | 5.1234 | 5.1114 | 0.43215 | 0.44372 | 0.45396 | 0.46977 | 0.48701 | 0.50898 | 0.53568 | 0.56022 | 0.57712 | 0.5758 | 0.57447 | 0.57315 | 0.57183 | 0.57051 | 0.56919 | 0.56787 | 0.56655 | 0.56523 | 0.56391 | 0.56259 | 34766.6344 | 8178.6057 | 265520.0366 | 62461.7173 | 261309.5446 | 338714.9614 | 2713180.6318 | 272700.0178
| GHP022-141431252 | 74 | GHP022 | GHP | South | 1345378.5437 | 0.0029735 | 0.0030256 | 0.0030634 | 0.0030965 | 0.0031107 | 0.0031973 | 0.0033559 | 0.0034993 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.085461 | 0.086196 | 0.086931 | 0.087666 | 0.088401 | 0.088696 | 0.088992 | 0.089287 | 0.089582 | 0.089878 | 0.090173 | 0.090468 | 0.090764 | 0.091059 | 0.091354 | 0.09165 | 0.091945 | 0.09224 | 0.092536 | 0.092831 | 0.0070747 | 0.0072604 | 0.007414 | 0.0075575 | 0.0076558 | 0.0078952 | 0.0083143 | 0.0086984 | 0.0089549 | 0.0089845 | 0.009014 | 0.0090435 | 0.009073 | 0.0091025 | 0.0091321 | 0.0091616 | 0.0091911 | 0.0092206 | 0.0092502 | 0.0092797 | 34766.6344 | 8178.6057 | 4234.2523 | 996.078 | 66888.6676 | 86702.5063 | 1404023.5437 | 69804.3421
| GHP022-141431280 | 28 | GHP022 | GHP | South | 509062.1517 | 0.0029735 | 0.0030256 | 0.0030634 | 0.0030965 | 0.0031107 | 0.0031973 | 0.0033559 | 0.0034993 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.013485 | 0.013583 | 0.013681 | 0.013778 | 0.013876 | 0.013889 | 0.013902 | 0.013914 | 0.013927 | 0.01394 | 0.013952 | 0.013965 | 0.013978 | 0.01399 | 0.014003 | 0.014016 | 0.014029 | 0.014041 | 0.014054 | 0.014067 | 0.0011163 | 0.0011441 | 0.0011668 | 0.0011878 | 0.0012017 | 0.0012363 | 0.0012988 | 0.0013555 | 0.0013922 | 0.0013935 | 0.0013947 | 0.001396 | 0.0013973 | 0.0013985 | 0.0013998 | 0.0014011 | 0.0014023 | 0.0014036 | 0.0014049 | 0.0014061 | 34766.6344 | 8178.6057 | 656.6687 | 154.4767 | 9284.7723 | 12035.1183 | 531252.1517 | 9689.4951
| GHP022-188587433 | 623 | GHP022 | GHP | South | 11326632.8749 | 0.0029735 | 0.0030256 | 0.0030634 | 0.0030965 | 0.0031107 | 0.0031973 | 0.0033559 | 0.0034993 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 10.4682 | 10.5319 | 10.5957 | 10.6594 | 10.7232 | 10.7538 | 10.7844 | 10.8151 | 10.8457 | 10.8763 | 10.9069 | 10.9376 | 10.9682 | 10.9988 | 11.0295 | 11.0601 | 11.0907 | 11.1214 | 11.152 | 11.1826 | 0.86658 | 0.88712 | 0.90366 | 0.91893 | 0.92866 | 0.95724 | 1.0076 | 1.0536 | 1.0842 | 1.0872 | 1.0903 | 1.0934 | 1.0964 | 1.0995 | 1.1025 | 1.1056 | 1.1087 | 1.1117 | 1.1148 | 1.1179 | 34766.6344 | 8178.6057 | 513019.7386 | 120684.2778 | 3838507.2571 | 4975554.334 | 11820360.3749 | 4005827.6437
| GHP022-190579440 | 300 | GHP022 | GHP | South | 5454237.3394 | 0.0029735 | 0.0030256 | 0.0030634 | 0.0030965 | 0.0031107 | 0.0031973 | 0.0033559 | 0.0034993 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 5.0881 | 5.1261 | 5.164 | 5.202 | 5.2399 | 5.26 | 5.2802 | 5.3003 | 5.3204 | 5.3405 | 5.3607 | 5.3808 | 5.4009 | 5.421 | 5.4412 | 5.4613 | 5.4814 | 5.5016 | 5.5217 | 5.5418 | 0.42121 | 0.43178 | 0.44042 | 0.44845 | 0.45379 | 0.46822 | 0.49331 | 0.51635 | 0.53184 | 0.53386 | 0.53587 | 0.53788 | 0.53989 | 0.5419 | 0.54392 | 0.54593 | 0.54794 | 0.54995 | 0.55196 | 0.55398 | 34766.6344 | 8178.6057 | 251797.2858 | 59233.5369 | 947496.9688 | 1228165.6211 | 5691987.3394 | 988798.3259
| GHP022-72503462 | 72 | GHP022 | GHP | South | 1309016.9615 | 0.0029735 | 0.0030256 | 0.0030634 | 0.0030965 | 0.0031107 | 0.0031973 | 0.0033559 | 0.0034993 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.0035906 | 0.17888 | 0.18049 | 0.1821 | 0.1837 | 0.18531 | 0.18592 | 0.18652 | 0.18713 | 0.18773 | 0.18834 | 0.18895 | 0.18955 | 0.19016 | 0.19076 | 0.19137 | 0.19197 | 0.19258 | 0.19319 | 0.19379 | 0.1944 | 0.014808 | 0.015203 | 0.01553 | 0.015837 | 0.016048 | 0.016549 | 0.017426 | 0.01823 | 0.018766 | 0.018827 | 0.018888 | 0.018948 | 0.019009 | 0.019069 | 0.01913 | 0.01919 | 0.019251 | 0.019311 | 0.019372 | 0.019433 | 34766.6344 | 8178.6057 | 8870.8544 | 2086.806 | 82441.3023 | 106862.1607 | 1366076.9615 | 86034.9156
| GL011-15402625 | 147 | GL011 | GL | South | 2672576.2963 | 0.0034914 | 0.0035721 | 0.003569 | 0.003569 | 0.0035726 | 0.0035951 | 0.003628 | 0.0036519 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0.0036623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43985.3039 | 9317.9043 | 0 | 0 | 0 | 0 | 2789073.7963 | 0
| GL012-15402649 | 165 | GL012 | GL | South | 2999830.5367 | 0.00041005 | 0.00041286 | 0.00041583 | 0.00041706 | 0.00042021 | 0.00042634 | 0.0004365 | 0.00044544 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0.00045122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43985.3039 | 9317.9043 | 0 | 0 | 0 | 0 | 3130593.0367 | 0
| GL013-15402686 | 197 | GL013 | GL | South | 3581615.8529 | 0.00096164 | 0.00097685 | 0.00099047 | 0.0010082 | 0.0010377 | 0.0010815 | 0.0011291 | 0.0011684 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0.0011979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43985.3039 | 9317.9043 | 0 | 0 | 0 | 0 | 3737738.3529 | 0
| GL014-15402723 | 206 | GL014 | GL | South | 3745242.9731 | 0.00078033 | 0.00079554 | 0.00082038 | 0.00084995 | 0.00088256 | 0.00091906 | 0.00095843 | 0.00099155 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0.0010186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43985.3039 | 9317.9043 | 0 | 0 | 0 | 0 | 3908497.9731 | 0
| GL015-15402771 | 201 | GL015 | GL | South | 3654339.0174 | 0.00062824 | 0.00064216 | 0.0006597 | 0.00067363 | 0.00068616 | 0.00071498 | 0.00074603 | 0.0007743 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0.00079101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43985.3039 | 9317.9043 | 0 | 0 | 0 | 0 | 3813631.5174 | 0
| GL021-15402795 | 141 | GL021 | GL | South | 2563491.5495 | 0.00081306 | 0.00082282 | 0.00083213 | 0.000837 | 0.00083804 | 0.00084158 | 0.00086538 | 0.00088651 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43985.3039 | 9317.9043 | 0 | 0 | 0 | 0 | 2675234.0495 | 0
| GL021-24612685 | 110 | GL021 | GL | South | 1999887.0245 | 0.00081306 | 0.00082282 | 0.00083213 | 0.000837 | 0.00083804 | 0.00084158 | 0.00086538 | 0.00088651 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0.00089685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43985.3039 | 9317.9043 | 0 | 0 | 0 | 0 | 2087062.0245 | 0
| GL022-15402832 | 71 | GL022 | GL | South | 1290836.1703 | 0.001011 | 0.0010221 | 0.0010287 | 0.0010355 | 0.0010351 | 0.0010539 | 0.0010861 | 0.0011152 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43985.3039 | 9317.9043 | 0 | 0 | 0 | 0 | 1347103.6703 | 0
| GL022-24612699 | 261 | GL022 | GL | South | 4745186.4853 | 0.001011 | 0.0010221 | 0.0010287 | 0.0010355 | 0.0010351 | 0.0010539 | 0.0010861 | 0.0011152 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0.0011333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43985.3039 | 9317.9043 | 0 | 0 | 0 | 0 | 4952028.9853 | 0
| GL023-15402869 | 244 | GL023 | GL | South | 4436113.0361 | 0.0014706 | 0.0014586 | 0.0014456 | 0.0014308 | 0.0014122 | 0.0013997 | 0.0014214 | 0.0014459 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0.0014548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43985.3039 | 9317.9043 | 0 | 0 | 0 | 0 | 4629483.0361 | 0
| GL024-15402919 | 143 | GL024 | GL | South | 2599853.1318 | 0.001682 | 0.0016925 | 0.0016917 | 0.0016891 | 0.0016835 | 0.0016829 | 0.0016934 | 0.0017058 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0.0017078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43985.3039 | 9317.9043 | 0 | 0 | 0 | 0 | 2713180.6318 | 0
| GLE011-15406891 | 144 | GLE011 | GLE | South | 2618033.9229 | 0.0050627 | 0.0050348 | 0.0050306 | 0.0050028 | 0.0049471 | 0.0049471 | 0.0049749 | 0.0049889 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0.0049387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40890.8484 | 7387.56 | 0 | 0 | 0 | 0 | 2732153.9229 | 0
| GLE012-15406954 | 329 | GLE012 | GLE | South | 5981480.2823 | 0.0010193 | 0.0010293 | 0.0010486 | 0.0010821 | 0.0011159 | 0.0011543 | 0.001197 | 0.0012336 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.097214 | 0.0982 | 0.099186 | 0.10017 | 0.10116 | 0.10139 | 0.10163 | 0.10187 | 0.1021 | 0.10234 | 0.10258 | 0.10281 | 0.10305 | 0.10328 | 0.10352 | 0.10376 | 0.10399 | 0.10423 | 0.10447 | 0.1047 | 0.0027585 | 0.002814 | 0.0028954 | 0.0030177 | 0.0031427 | 0.0032584 | 0.0033867 | 0.0034983 | 0.0035885 | 0.0035968 | 0.0036051 | 0.0036134 | 0.0036217 | 0.0036301 | 0.0036384 | 0.0036467 | 0.003655 | 0.0036633 | 0.0036716 | 0.0036799 | 40890.8484 | 7387.56 | 1988.2142 | 359.2014 | 1860.6656 | 2411.8342 | 6242212.7823 | 1941.772
| GLE012-77546340 | 55 | GLE012 | GLE | South | 999943.5122 | 0.0010193 | 0.0010293 | 0.0010486 | 0.0010821 | 0.0011159 | 0.0011543 | 0.001197 | 0.0012336 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0.0012624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40890.8484 | 7387.56 | 0 | 0 | 0 | 0 | 1043531.0122 | 0
| GLE013-15407017 | 406 | GLE013 | GLE | South | 7381401.1994 | 0.0011594 | 0.0012539 | 0.0013605 | 0.0014636 | 0.0015617 | 0.0016736 | 0.0017909 | 0.0019018 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 0.0019977 | 100.8882 | 101.6641 | 102.44 | 103.2159 | 103.9918 | 104.0612 | 104.1306 | 104.1999 | 104.2693 | 104.3387 | 104.4081 | 104.4774 | 104.5468 | 104.6162 | 104.6856 | 104.7549 | 104.8243 | 104.8937 | 104.9631 | 105.0324 | 3.2564 | 3.5488 | 3.88 | 4.2058 | 4.5214 | 4.8485 | 5.1919 | 5.5171 | 5.7991 | 5.803 | 5.8069 | 5.8107 | 5.8146 | 5.8184 | 5.8223 | 5.8262 | 5.83 | 5.8339 | 5.8377 | 5.8416 | 40890.8484 | 7387.56 | 3009628.4668 | 543735.6204 | 1670921.8246 | 2165884.2277 | 7703156.1994 | 1743757.2439
| GLE021-15407054 | 77 | GLE021 | GLE | South | 1399920.9171 | 0.004649 | 0.0046896 | 0.0047494 | 0.0047635 | 0.0047369 | 0.0047867 | 0.0049029 | 0.0049942 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0.0049361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40890.8484 | 7387.56 | 0 | 0 | 0 | 0 | 1460943.4171 | 0
| GLE023-15407104 | 54 | GLE023 | GLE | South | 981762.7211 | 1.178 | 1.183 | 1.173 | 1.163 | 1.1495 | 1.1415 | 1.133 | 1.128 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 1.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40890.8484 | 7387.56 | 0 | 0 | 0 | 0 | 1024557.7211 | 0
| GLE024-15407167 | 484 | GLE024 | GLE | South | 8799502.9076 | 0.0011868 | 0.0012154 | 0.0012219 | 0.001226 | 0.0012239 | 0.0012228 | 0.0012348 | 0.0012591 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 26.9534 | 26.9705 | 26.9875 | 27.0046 | 27.0216 | 26.9806 | 26.9395 | 26.8984 | 26.8573 | 26.8163 | 26.7752 | 26.7341 | 26.693 | 26.652 | 26.6109 | 26.5698 | 26.5287 | 26.4877 | 26.4466 | 26.4055 | 0.89052 | 0.91261 | 0.91803 | 0.92169 | 0.92073 | 0.91849 | 0.92607 | 0.94291 | 0.9528 | 0.95134 | 0.94988 | 0.94843 | 0.94697 | 0.94551 | 0.94406 | 0.9426 | 0.94114 | 0.93968 | 0.93823 | 0.93677 | 40890.8484 | 7387.56 | 551100.6494 | 99564.7991 | 727849.3196 | 943453.6902 | 9183072.9076 | 759576.244
| GLE024-24612325 | 183 | GLE024 | GLE | South | 3327084.7771 | 0.0011868 | 0.0012154 | 0.0012219 | 0.001226 | 0.0012239 | 0.0012228 | 0.0012348 | 0.0012591 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 0.0012743 | 3.159 | 3.1649 | 3.1707 | 3.1765 | 3.1824 | 3.1698 | 3.1573 | 3.1448 | 3.1323 | 3.1198 | 3.1073 | 3.0947 | 3.0822 | 3.0697 | 3.0572 | 3.0447 | 3.0322 | 3.0196 | 3.0071 | 2.9946 | 0.10437 | 0.10709 | 0.10786 | 0.10842 | 0.10844 | 0.10791 | 0.10854 | 0.11024 | 0.11112 | 0.11068 | 0.11023 | 0.10979 | 0.10935 | 0.1089 | 0.10846 | 0.10801 | 0.10757 | 0.10713 | 0.10668 | 0.10624 | 40890.8484 | 7387.56 | 64045.867 | 11570.8698 | 110046.0783 | 142644.0554 | 3472112.2771 | 114842.9827
| GLE031-15407178 | 156 | GLE031 | GLE | South | 2836203.4165 | 0.0014722 | 0.0015074 | 0.0015122 | 0.0015152 | 0.0015187 | 0.001534 | 0.001559 | 0.0015799 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40890.8484 | 7387.56 | 0 | 0 | 0 | 0 | 2959833.4165 | 0
| GLE031-24612339 | 361 | GLE031 | GLE | South | 6563265.5985 | 0.0014722 | 0.0015074 | 0.0015122 | 0.0015152 | 0.0015187 | 0.001534 | 0.001559 | 0.0015799 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 0.0015892 | 2.2104 | 2.2148 | 2.2191 | 2.2235 | 2.2278 | 2.2185 | 2.2092 | 2.1999 | 2.1906 | 2.1814 | 2.1721 | 2.1628 | 2.1535 | 2.1442 | 2.1349 | 2.1256 | 2.1163 | 2.1071 | 2.0978 | 2.0885 | 0.090594 | 0.092944 | 0.093427 | 0.093791 | 0.09419 | 0.094743 | 0.095887 | 0.096763 | 0.096923 | 0.096512 | 0.096101 | 0.09569 | 0.095279 | 0.094869 | 0.094458 | 0.094047 | 0.093636 | 0.093225 | 0.092814 | 0.092403 | 40890.8484 | 7387.56 | 55804.0283 | 10081.855 | 132936.6376 | 172315.2828 | 6849358.0985 | 138731.3406
| GLE032-15407241 | 159 | GLE032 | GLE | South | 2890745.7899 | 0.0015868 | 0.0016211 | 0.0016441 | 0.0016645 | 0.001682 | 0.0017073 | 0.0017386 | 0.0017639 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 2.202 | 2.2092 | 2.2165 | 2.2238 | 2.2311 | 2.229 | 2.227 | 2.2249 | 2.2229 | 2.2208 | 2.2188 | 2.2167 | 2.2146 | 2.2126 | 2.2105 | 2.2085 | 2.2064 | 2.2044 | 2.2023 | 2.2003 | 0.097273 | 0.099707 | 0.10145 | 0.10305 | 0.10448 | 0.10595 | 0.10779 | 0.10926 | 0.10972 | 0.10962 | 0.10952 | 0.10941 | 0.10931 | 0.10921 | 0.10911 | 0.10901 | 0.10891 | 0.10881 | 0.1087 | 0.1086 | 40890.8484 | 7387.56 | 62882.8277 | 11360.7489 | 33485.7928 | 43404.9933 | 3016753.2899 | 34945.4373
| GLE032-24612713 | 148 | GLE032 | GLE | South | 2690757.0875 | 0.0015868 | 0.0016211 | 0.0016441 | 0.0016645 | 0.001682 | 0.0017073 | 0.0017386 | 0.0017639 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0.001773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40890.8484 | 7387.56 | 0 | 0 | 0 | 0 | 2808047.0875 | 0
| GLE033-15407304 | 147 | GLE033 | GLE | South | 2672576.2963 | 0.0035179 | 0.0035118 | 0.0035118 | 0.0035004 | 0.003483 | 0.0034856 | 0.0035118 | 0.0035292 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0.0035118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40890.8484 | 7387.56 | 0 | 0 | 0 | 0 | 2789073.7963 | 0
| GSB011-24597032 | 227 | GSB011 | GSB | South | 4127039.5868 | 0.0013801 | 0.0014127 | 0.0014506 | 0.0014906 | 0.0015298 | 0.0015781 | 0.0016355 | 0.0016851 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 16.5144 | 16.6367 | 16.7589 | 16.8812 | 17.0034 | 17.1171 | 17.2308 | 17.3445 | 17.4582 | 17.5718 | 17.6855 | 17.7992 | 17.9129 | 18.0266 | 18.1402 | 18.2539 | 18.3676 | 18.4813 | 18.595 | 18.7086 | 0.63453 | 0.65429 | 0.67683 | 0.70054 | 0.72416 | 0.75205 | 0.78457 | 0.81367 | 0.83614 | 0.84158 | 0.84703 | 0.85247 | 0.85792 | 0.86336 | 0.86881 | 0.87425 | 0.8797 | 0.88514 | 0.89059 | 0.89603 | 33248.4756 | 9067.2226 | 380206.1288 | 103686.3653 | 3954231.1846 | 5125558.1377 | 4306937.0868 | 4126595.9729
| GSB011-24613746 | 185 | GSB011 | GSB | South | 3363446.3593 | 0.0013801 | 0.0014127 | 0.0014506 | 0.0014906 | 0.0015298 | 0.0015781 | 0.0016355 | 0.0016851 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 42.2699 | 42.6493 | 43.0287 | 43.4081 | 43.7875 | 44.1582 | 44.5289 | 44.8996 | 45.2703 | 45.641 | 46.0117 | 46.3824 | 46.7531 | 47.1237 | 47.4944 | 47.8651 | 48.2358 | 48.6065 | 48.9772 | 49.3479 | 1.6241 | 1.6773 | 1.7378 | 1.8014 | 1.8649 | 1.9401 | 2.0275 | 2.1064 | 2.1682 | 2.1859 | 2.2037 | 2.2214 | 2.2392 | 2.2569 | 2.2747 | 2.2925 | 2.3102 | 2.328 | 2.3457 | 2.3635 | 33248.4756 | 9067.2226 | 987298.5733 | 269247.1079 | 1346273.1298 | 1745067.7196 | 3510058.8593 | 1404957.1248
| GSB011-74623144 | 0 | GSB011 | GSB | South | 0 | 0.0013801 | 0.0014127 | 0.0014506 | 0.0014906 | 0.0015298 | 0.0015781 | 0.0016355 | 0.0016851 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 14.6589 | 14.7379 | 14.8169 | 14.896 | 14.975 | 15.042 | 15.109 | 15.1759 | 15.2429 | 15.3099 | 15.3769 | 15.4438 | 15.5108 | 15.5778 | 15.6447 | 15.7117 | 15.7787 | 15.8457 | 15.9126 | 15.9796 | 0.56324 | 0.57962 | 0.5984 | 0.61816 | 0.63777 | 0.66088 | 0.68796 | 0.71194 | 0.73004 | 0.73325 | 0.73646 | 0.73967 | 0.74287 | 0.74608 | 0.74929 | 0.7525 | 0.7557 | 0.75891 | 0.76212 | 0.76533 | 33248.4756 | 9067.2226 | 0 | 0 | 0 | 0 | 0 | 0
| GSB011-74623154 | 65 | GSB011 | GSB | South | 1181751.4235 | 0.0013801 | 0.0014127 | 0.0014506 | 0.0014906 | 0.0015298 | 0.0015781 | 0.0016355 | 0.0016851 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 0.0017203 | 49.4531 | 49.8845 | 50.3159 | 50.7474 | 51.1788 | 51.617 | 52.0553 | 52.4935 | 52.9317 | 53.37 | 53.8082 | 54.2465 | 54.6847 | 55.123 | 55.5612 | 55.9994 | 56.4377 | 56.8759 | 57.3142 | 57.7524 | 1.9001 | 1.9619 | 2.0321 | 2.1059 | 2.1796 | 2.2678 | 2.3702 | 2.4626 | 2.5351 | 2.5561 | 2.5771 | 2.5981 | 2.6191 | 2.6401 | 2.661 | 2.682 | 2.703 | 2.724 | 2.745 | 2.766 | 33248.4756 | 9067.2226 | 1154676.7852 | 314892.975 | 542280.2752 | 702915.168 | 1233263.9235 | 565918.2519
| GSB012-181419068 | 0 | GSB012 | GSB | South | 0 | 0.0022813 | 0.0023496 | 0.002433 | 0.0025052 | 0.0025712 | 0.0026576 | 0.0027604 | 0.0028528 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33248.4756 | 9067.2226 | 0 | 0 | 0 | 0 | 0 | 0
| GSB012-24607348 | 403 | GSB012 | GSB | South | 7326858.826 | 0.0022813 | 0.0023496 | 0.002433 | 0.0025052 | 0.0025712 | 0.0026576 | 0.0027604 | 0.0028528 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 215.4672 | 216.967 | 218.4668 | 219.9666 | 221.4664 | 221.6852 | 221.9041 | 222.1229 | 222.3417 | 222.5606 | 222.7794 | 222.9983 | 223.2171 | 223.436 | 223.6548 | 223.8737 | 224.0925 | 224.3114 | 224.5302 | 224.749 | 13.6848 | 14.1927 | 14.7981 | 15.3414 | 15.8533 | 16.4018 | 17.053 | 17.6414 | 18.0216 | 18.0393 | 18.0571 | 18.0748 | 18.0925 | 18.1103 | 18.128 | 18.1458 | 18.1635 | 18.1812 | 18.199 | 18.2167 | 33248.4756 | 9067.2226 | 8104275.7174 | 2210124.5331 | 11863172.0117 | 15377294.6004 | 7646236.326 | 12380287.2324
| GSB012-24607362 | 196 | GSB012 | GSB | South | 3563435.0618 | 0.0022813 | 0.0023496 | 0.002433 | 0.0025052 | 0.0025712 | 0.0026576 | 0.0027604 | 0.0028528 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 2.5537 | 2.5762 | 2.5988 | 2.6213 | 2.6438 | 2.6433 | 2.6427 | 2.6421 | 2.6416 | 2.641 | 2.6404 | 2.6399 | 2.6393 | 2.6387 | 2.6382 | 2.6376 | 2.637 | 2.6365 | 2.6359 | 2.6353 | 0.16219 | 0.16852 | 0.17603 | 0.18282 | 0.18926 | 0.19557 | 0.20309 | 0.20984 | 0.21411 | 0.21406 | 0.21402 | 0.21397 | 0.21393 | 0.21388 | 0.21383 | 0.21379 | 0.21374 | 0.2137 | 0.21365 | 0.2136 | 33248.4756 | 9067.2226 | 96031.7375 | 26188.904 | 555748.4624 | 720372.9173 | 3718765.0618 | 579973.5169
| GSB012-72499030 | 20 | GSB012 | GSB | South | 363615.8226 | 0.0022813 | 0.0023496 | 0.002433 | 0.0025052 | 0.0025712 | 0.0026576 | 0.0027604 | 0.0028528 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.062535 | 0.06311 | 0.063685 | 0.06426 | 0.064835 | 0.065088 | 0.065341 | 0.065593 | 0.065846 | 0.066099 | 0.066351 | 0.066604 | 0.066857 | 0.067109 | 0.067362 | 0.067615 | 0.067867 | 0.06812 | 0.068372 | 0.068625 | 0.0039717 | 0.0041283 | 0.0043138 | 0.0044818 | 0.0046411 | 0.0048157 | 0.0050213 | 0.0052095 | 0.0053371 | 0.0053575 | 0.005378 | 0.0053985 | 0.005419 | 0.0054394 | 0.0054599 | 0.0054804 | 0.0055009 | 0.0055214 | 0.0055418 | 0.0055623 | 33248.4756 | 9067.2226 | 2406.5537 | 656.2935 | 26581.2851 | 34455.2242 | 379465.8226 | 27739.9623
| GSB012-72499395 | 45 | GSB012 | GSB | South | 818135.6009 | 0.0022813 | 0.0023496 | 0.002433 | 0.0025052 | 0.0025712 | 0.0026576 | 0.0027604 | 0.0028528 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.14122 | 0.1425 | 0.14378 | 0.14506 | 0.14634 | 0.1463 | 0.14627 | 0.14624 | 0.1462 | 0.14617 | 0.14613 | 0.1461 | 0.14607 | 0.14603 | 0.146 | 0.14597 | 0.14593 | 0.1459 | 0.14586 | 0.14583 | 0.0089689 | 0.0093212 | 0.0097389 | 0.010117 | 0.010475 | 0.010825 | 0.011241 | 0.011614 | 0.01185 | 0.011847 | 0.011845 | 0.011842 | 0.011839 | 0.011837 | 0.011834 | 0.011831 | 0.011828 | 0.011826 | 0.011823 | 0.01182 | 33248.4756 | 9067.2226 | 5314.233 | 1449.2494 | 71630.1967 | 92848.5768 | 853798.1009 | 74752.5543
| GSB012-74623277 | 140 | GSB012 | GSB | South | 2545310.7584 | 0.0022813 | 0.0023496 | 0.002433 | 0.0025052 | 0.0025712 | 0.0026576 | 0.0027604 | 0.0028528 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 101.9962 | 102.6794 | 103.3626 | 104.0457 | 104.7289 | 105.0405 | 105.3521 | 105.6638 | 105.9754 | 106.2871 | 106.5987 | 106.9104 | 107.222 | 107.5336 | 107.8453 | 108.1569 | 108.4686 | 108.7802 | 109.0919 | 109.4035 | 6.478 | 6.7167 | 7.0014 | 7.2566 | 7.4968 | 7.7716 | 8.0962 | 8.392 | 8.5897 | 8.6149 | 8.6402 | 8.6655 | 8.6907 | 8.716 | 8.7412 | 8.7665 | 8.7918 | 8.817 | 8.8423 | 8.8675 | 33248.4756 | 9067.2226 | 3873578.9281 | 1056367.2953 | 2173060.6562 | 2816767.2071 | 2656260.7584 | 2267784.2882
| GSB012-77736949 | 36 | GSB012 | GSB | South | 654508.4807 | 0.0022813 | 0.0023496 | 0.002433 | 0.0025052 | 0.0025712 | 0.0026576 | 0.0027604 | 0.0028528 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.33165 | 0.33424 | 0.33682 | 0.33941 | 0.342 | 0.34465 | 0.3473 | 0.34995 | 0.3526 | 0.35525 | 0.3579 | 0.36055 | 0.3632 | 0.36586 | 0.36851 | 0.37116 | 0.37381 | 0.37646 | 0.37911 | 0.38176 | 0.021064 | 0.021864 | 0.022815 | 0.023672 | 0.024481 | 0.0255 | 0.02669 | 0.027794 | 0.02858 | 0.028795 | 0.029009 | 0.029224 | 0.029439 | 0.029654 | 0.029869 | 0.030084 | 0.030298 | 0.030513 | 0.030728 | 0.030943 | 33248.4756 | 9067.2226 | 12960.7354 | 3534.5341 | 104575.2125 | 135552.6034 | 683038.4807 | 109133.6421
| GSB012-85320967 | 19 | GSB012 | GSB | South | 345435.0315 | 0.0022813 | 0.0023496 | 0.002433 | 0.0025052 | 0.0025712 | 0.0026576 | 0.0027604 | 0.0028528 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0012194 | 0.0012327 | 0.001246 | 0.0012594 | 0.0012727 | 0.0012775 | 0.0012824 | 0.0012872 | 0.001292 | 0.0012969 | 0.0013017 | 0.0013065 | 0.0013114 | 0.0013162 | 0.001321 | 0.0013259 | 0.0013307 | 0.0013355 | 0.0013403 | 0.0013452 | 7.7445e-05 | 8.0636e-05 | 8.4401e-05 | 8.7834e-05 | 9.1104e-05 | 9.4521e-05 | 9.8548e-05 | 0.00010223 | 0.00010472 | 0.00010512 | 0.00010551 | 0.0001059 | 0.00010629 | 0.00010668 | 0.00010707 | 0.00010747 | 0.00010786 | 0.00010825 | 0.00010864 | 0.00010903 | 33248.4756 | 9067.2226 | 47.1728 | 12.8645 | 494.9321 | 641.5415 | 360492.5315 | 516.5062
| GSB013-74623435 | 348 | GSB013 | GSB | South | 6326915.3137 | 0.0015692 | 0.0016079 | 0.0016287 | 0.0016696 | 0.0017178 | 0.0017754 | 0.0018417 | 0.0019028 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 0.0019452 | 192.0134 | 193.3737 | 194.734 | 196.0943 | 197.4546 | 198.0889 | 198.7231 | 199.3574 | 199.9917 | 200.626 | 201.2603 | 201.8946 | 202.5289 | 203.1631 | 203.7974 | 204.4317 | 205.066 | 205.7003 | 206.3346 | 206.9688 | 8.3883 | 8.6561 | 8.83 | 9.1145 | 9.4429 | 9.791 | 10.1889 | 10.5608 | 10.8305 | 10.8649 | 10.8992 | 10.9336 | 10.9679 | 11.0023 | 11.0366 | 11.071 | 11.1053 | 11.1397 | 11.174 | 11.2084 | 33248.4756 | 9067.2226 | 4897868.4049 | 1335702.2267 | 6456864.5806 | 8369524.5044 | 6602705.3137 | 6738319.0643
| GSB014-163179564 | 10 | GSB014 | GSB | South | 181807.9113 | 0.0013028 | 0.0013272 | 0.0013557 | 0.0013818 | 0.0014038 | 0.0014354 | 0.0014764 | 0.0015103 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0038196 | 0.0038622 | 0.0039049 | 0.0039476 | 0.0039902 | 0.0040148 | 0.0040393 | 0.0040638 | 0.0040884 | 0.0041129 | 0.0041374 | 0.004162 | 0.0041865 | 0.004211 | 0.0042356 | 0.0042601 | 0.0042846 | 0.0043091 | 0.0043337 | 0.0043582 | 0.00013854 | 0.00014271 | 0.00014738 | 0.00015186 | 0.00015595 | 0.00016043 | 0.00016603 | 0.00017087 | 0.00017379 | 0.00017484 | 0.00017588 | 0.00017692 | 0.00017796 | 0.00017901 | 0.00018005 | 0.00018109 | 0.00018214 | 0.00018318 | 0.00018422 | 0.00018526 | 33248.4756 | 9067.2226 | 80.1239 | 21.8507 | 2684.8812 | 3480.1999 | 189732.9113 | 2801.9151
| GSB014-194965507 | 235 | GSB014 | GSB | South | 4272485.9159 | 0.0013028 | 0.0013272 | 0.0013557 | 0.0013818 | 0.0014038 | 0.0014354 | 0.0014764 | 0.0015103 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 71.116 | 71.6541 | 72.1922 | 72.7303 | 73.2684 | 73.8213 | 74.3742 | 74.9271 | 75.48 | 76.0329 | 76.5858 | 77.1387 | 77.6915 | 78.2444 | 78.7973 | 79.3502 | 79.9031 | 80.456 | 81.0089 | 81.5618 | 2.5794 | 2.6477 | 2.7247 | 2.7979 | 2.8635 | 2.95 | 3.057 | 3.1505 | 3.2086 | 3.2321 | 3.2556 | 3.2791 | 3.3026 | 3.3261 | 3.3496 | 3.3731 | 3.3966 | 3.4201 | 3.4436 | 3.4671 | 33248.4756 | 9067.2226 | 1484590.7746 | 404864.1244 | 5613332.5346 | 7276120.4161 | 4458723.4159 | 5858017.4882
| GSB014-194965541 | 175 | GSB014 | GSB | South | 3181638.448 | 0.0013028 | 0.0013272 | 0.0013557 | 0.0013818 | 0.0014038 | 0.0014354 | 0.0014764 | 0.0015103 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 41.1881 | 41.4392 | 41.6904 | 41.9416 | 42.1927 | 42.3956 | 42.5984 | 42.8012 | 43.004 | 43.2068 | 43.4097 | 43.6125 | 43.8153 | 44.0181 | 44.2209 | 44.4238 | 44.6266 | 44.8294 | 45.0322 | 45.235 | 1.4939 | 1.5312 | 1.5735 | 1.6134 | 1.649 | 1.6942 | 1.7509 | 1.7997 | 1.8281 | 1.8367 | 1.8453 | 1.8539 | 1.8626 | 1.8712 | 1.8798 | 1.8884 | 1.897 | 1.9057 | 1.9143 | 1.9229 | 33248.4756 | 9067.2226 | 843769.203 | 230105.0804 | 1808468.4705 | 2344175.1008 | 3320325.948 | 1887299.5429
| GSB014-194965599 | 268 | GSB014 | GSB | South | 4872452.0232 | 0.0013028 | 0.0013272 | 0.0013557 | 0.0013818 | 0.0014038 | 0.0014354 | 0.0014764 | 0.0015103 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 18.7011 | 18.8541 | 19.0071 | 19.1601 | 19.3131 | 19.4706 | 19.628 | 19.7854 | 19.9429 | 20.1003 | 20.2577 | 20.4152 | 20.5726 | 20.73 | 20.8875 | 21.0449 | 21.2023 | 21.3597 | 21.5172 | 21.6746 | 0.6783 | 0.69667 | 0.71738 | 0.73707 | 0.75481 | 0.77806 | 0.80677 | 0.83192 | 0.84776 | 0.85445 | 0.86114 | 0.86783 | 0.87453 | 0.88122 | 0.88791 | 0.8946 | 0.9013 | 0.90799 | 0.91468 | 0.92137 | 33248.4756 | 9067.2226 | 392397.1773 | 107010.9975 | 2044457.3797 | 2650068.9187 | 5084842.0232 | 2133575.1998
| GSB014-73768594 | 15 | GSB014 | GSB | South | 272711.867 | 0.0013028 | 0.0013272 | 0.0013557 | 0.0013818 | 0.0014038 | 0.0014354 | 0.0014764 | 0.0015103 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.21609 | 0.21843 | 0.22077 | 0.22312 | 0.22546 | 0.22671 | 0.22795 | 0.2292 | 0.23045 | 0.2317 | 0.23295 | 0.2342 | 0.23545 | 0.23669 | 0.23794 | 0.23919 | 0.24044 | 0.24169 | 0.24294 | 0.24419 | 0.0078378 | 0.0080713 | 0.0083327 | 0.008583 | 0.0088115 | 0.0090594 | 0.0093696 | 0.0096373 | 0.0097963 | 0.0098494 | 0.0099025 | 0.0099556 | 0.010009 | 0.010062 | 0.010115 | 0.010168 | 0.010221 | 0.010274 | 0.010327 | 0.01038 | 33248.4756 | 9067.2226 | 4513.9061 | 1230.9915 | 33617.3334 | 43575.4989 | 284599.367 | 35082.7117
| GSB014-74623507 | 69 | GSB014 | GSB | South | 1254474.5881 | 0.0013028 | 0.0013272 | 0.0013557 | 0.0013818 | 0.0014038 | 0.0014354 | 0.0014764 | 0.0015103 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 0.0015269 | 24.1771 | 24.329 | 24.4809 | 24.6329 | 24.7848 | 24.902 | 25.0192 | 25.1365 | 25.2537 | 25.3709 | 25.4881 | 25.6054 | 25.7226 | 25.8398 | 25.957 | 26.0742 | 26.1915 | 26.3087 | 26.4259 | 26.5431 | 0.87692 | 0.89897 | 0.92398 | 0.9476 | 0.96866 | 0.99511 | 1.0284 | 1.0569 | 1.0735 | 1.0785 | 1.0835 | 1.0885 | 1.0934 | 1.0984 | 1.1034 | 1.1084 | 1.1134 | 1.1184 | 1.1233 | 1.1283 | 33248.4756 | 9067.2226 | 495397.913 | 135100.4234 | 893247.5356 | 1157846.3579 | 1309157.0881 | 932184.162
| HSM001-108341890 | 88 | HSM001 | HSM | North | 2073836.7049 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.31045 | 0.31252 | 0.31458 | 0.31665 | 0.31871 | 0.31896 | 0.31922 | 0.31947 | 0.31972 | 0.31998 | 0.32023 | 0.32048 | 0.32074 | 0.32099 | 0.32124 | 0.3215 | 0.32175 | 0.322 | 0.32226 | 0.32251 | 0.016955 | 0.016953 | 0.017014 | 0.016998 | 0.01689 | 0.016813 | 0.01685 | 0.016863 | 0.016602 | 0.016615 | 0.016629 | 0.016642 | 0.016655 | 0.016668 | 0.016681 | 0.016694 | 0.016708 | 0.016721 | 0.016734 | 0.016747 | 34455.2362 | 7106.5908 | 8365.076 | 1725.3451 | 180267.4392 | 180267.4392 | 2073836.7049 | 180267.4392
| HSM001-15416529 | 0 | HSM001 | HSM | North | 0 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34455.2362 | 7106.5908 | 0 | 0 | 0 | 0 | 0 | 0
| HSM001-15416542 | 196 | HSM001 | HSM | North | 4618999.9336 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 21.2253 | 21.2718 | 21.3182 | 21.3647 | 21.4112 | 21.3833 | 21.3554 | 21.3275 | 21.2996 | 21.2717 | 21.2438 | 21.2158 | 21.1879 | 21.16 | 21.1321 | 21.1042 | 21.0763 | 21.0484 | 21.0205 | 20.9926 | 1.1592 | 1.1539 | 1.153 | 1.1469 | 1.1347 | 1.1272 | 1.1273 | 1.1258 | 1.106 | 1.1046 | 1.1031 | 1.1017 | 1.1002 | 1.0988 | 1.0973 | 1.0959 | 1.0944 | 1.093 | 1.0915 | 1.0901 | 34455.2362 | 7106.5908 | 557768.7948 | 115043.0238 | 1569224.2248 | 1569224.2248 | 4618999.9336 | 1569224.2248
| HSM001-157535060 | 76 | HSM001 | HSM | North | 1791040.7906 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.18575 | 0.18757 | 0.1894 | 0.19122 | 0.19305 | 0.19327 | 0.1935 | 0.19373 | 0.19396 | 0.19419 | 0.19442 | 0.19465 | 0.19488 | 0.19511 | 0.19533 | 0.19556 | 0.19579 | 0.19602 | 0.19625 | 0.19648 | 0.010144 | 0.010175 | 0.010244 | 0.010265 | 0.01023 | 0.010188 | 0.010214 | 0.010226 | 0.010072 | 0.010084 | 0.010096 | 0.010107 | 0.010119 | 0.010131 | 0.010143 | 0.010155 | 0.010167 | 0.010179 | 0.010191 | 0.010203 | 34455.2362 | 7106.5908 | 5066.3907 | 1044.9722 | 185108.6581 | 185108.6581 | 1791040.7906 | 185108.6581
| HSM001-157535228 | 108 | HSM001 | HSM | North | 2545163.2287 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.21744 | 0.21922 | 0.221 | 0.22278 | 0.22457 | 0.22511 | 0.22566 | 0.2262 | 0.22675 | 0.22729 | 0.22784 | 0.22838 | 0.22893 | 0.22948 | 0.23002 | 0.23057 | 0.23111 | 0.23166 | 0.2322 | 0.23275 | 0.011875 | 0.011892 | 0.011953 | 0.011959 | 0.011901 | 0.011866 | 0.011911 | 0.01194 | 0.011774 | 0.011803 | 0.011831 | 0.011859 | 0.011888 | 0.011916 | 0.011944 | 0.011973 | 0.012001 | 0.012029 | 0.012058 | 0.012086 | 34455.2362 | 7106.5908 | 5936.0236 | 1224.339 | 320071.7863 | 320071.7863 | 2545163.2287 | 320071.7863
| HSM001-157577413 | 74 | HSM001 | HSM | North | 1743908.1382 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.13277 | 0.13377 | 0.13476 | 0.13576 | 0.13675 | 0.13699 | 0.13723 | 0.13747 | 0.13771 | 0.13795 | 0.13819 | 0.13843 | 0.13867 | 0.1389 | 0.13914 | 0.13938 | 0.13962 | 0.13986 | 0.1401 | 0.14034 | 0.0072511 | 0.0072562 | 0.0072886 | 0.0072875 | 0.007247 | 0.007221 | 0.0072437 | 0.0072564 | 0.0071508 | 0.0071632 | 0.0071756 | 0.0071881 | 0.0072005 | 0.0072129 | 0.0072253 | 0.0072378 | 0.0072502 | 0.0072626 | 0.007275 | 0.0072875 | 34455.2362 | 7106.5908 | 3604.2997 | 743.4076 | 76933.562 | 76933.562 | 1743908.1382 | 76933.562
| HSM001-157577658 | 107 | HSM001 | HSM | North | 2521596.9025 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.17247 | 0.1737 | 0.17492 | 0.17615 | 0.17738 | 0.17738 | 0.17739 | 0.17739 | 0.17739 | 0.17739 | 0.1774 | 0.1774 | 0.1774 | 0.17741 | 0.17741 | 0.17741 | 0.17741 | 0.17742 | 0.17742 | 0.17742 | 0.009419 | 0.0094222 | 0.0094609 | 0.009456 | 0.0094002 | 0.0093503 | 0.0093635 | 0.0093636 | 0.0092115 | 0.0092116 | 0.0092118 | 0.0092119 | 0.009212 | 0.0092122 | 0.0092123 | 0.0092125 | 0.0092126 | 0.0092128 | 0.0092129 | 0.009213 | 34455.2362 | 7106.5908 | 4636.2723 | 956.2578 | 321917.103 | 321917.103 | 2521596.9025 | 321917.103
| HSM001-157598665 | 34 | HSM001 | HSM | North | 801255.0905 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.037278 | 0.037648 | 0.038018 | 0.038388 | 0.038758 | 0.038793 | 0.038827 | 0.038862 | 0.038896 | 0.03893 | 0.038965 | 0.038999 | 0.039034 | 0.039068 | 0.039102 | 0.039137 | 0.039171 | 0.039206 | 0.03924 | 0.039275 | 0.0020359 | 0.0020422 | 0.0020562 | 0.0020607 | 0.002054 | 0.0020448 | 0.0020495 | 0.0020513 | 0.0020198 | 0.0020215 | 0.0020233 | 0.0020251 | 0.0020269 | 0.0020287 | 0.0020305 | 0.0020323 | 0.0020341 | 0.0020358 | 0.0020376 | 0.0020394 | 34455.2362 | 7106.5908 | 1015.6296 | 209.4795 | 37351.0922 | 37351.0922 | 801255.0905 | 37351.0922
| HSM001-157598865 | 58 | HSM001 | HSM | North | 1366846.9191 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.054295 | 0.054859 | 0.055424 | 0.055989 | 0.056554 | 0.056535 | 0.056516 | 0.056497 | 0.056478 | 0.056459 | 0.05644 | 0.056421 | 0.056402 | 0.056382 | 0.056363 | 0.056344 | 0.056325 | 0.056306 | 0.056287 | 0.056268 | 0.0029652 | 0.0029759 | 0.0029977 | 0.0030056 | 0.002997 | 0.0029801 | 0.0029832 | 0.0029822 | 0.0029327 | 0.0029317 | 0.0029308 | 0.0029298 | 0.0029288 | 0.0029278 | 0.0029268 | 0.0029258 | 0.0029248 | 0.0029238 | 0.0029228 | 0.0029218 | 34455.2362 | 7106.5908 | 1472.4983 | 303.7112 | 69278.8332 | 69278.8332 | 1366846.9191 | 69278.8332
| HSM001-157598965 | 45 | HSM001 | HSM | North | 1060484.6786 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.13598 | 0.13725 | 0.13851 | 0.13978 | 0.14104 | 0.14119 | 0.14134 | 0.14149 | 0.14163 | 0.14178 | 0.14193 | 0.14207 | 0.14222 | 0.14237 | 0.14251 | 0.14266 | 0.14281 | 0.14295 | 0.1431 | 0.14325 | 0.0074263 | 0.007445 | 0.0074916 | 0.0075035 | 0.0074745 | 0.0074425 | 0.0074606 | 0.0074684 | 0.0073545 | 0.0073622 | 0.0073698 | 0.0073774 | 0.007385 | 0.0073926 | 0.0074003 | 0.0074079 | 0.0074155 | 0.0074231 | 0.0074308 | 0.0074384 | 34455.2362 | 7106.5908 | 3700.1991 | 763.1874 | 120070.0975 | 120070.0975 | 1060484.6786 | 120070.0975
| HSM001-163581806 | 16 | HSM001 | HSM | North | 377061.2191 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0036009 | 0.0036321 | 0.0036632 | 0.0036943 | 0.0037255 | 0.003736 | 0.0037464 | 0.0037569 | 0.0037673 | 0.0037778 | 0.0037883 | 0.0037987 | 0.0038092 | 0.0038196 | 0.0038301 | 0.0038406 | 0.003851 | 0.0038615 | 0.0038719 | 0.0038824 | 0.00019666 | 0.00019702 | 0.00019813 | 0.00019832 | 0.00019743 | 0.00019693 | 0.00019776 | 0.00019831 | 0.00019563 | 0.00019617 | 0.00019671 | 0.00019726 | 0.0001978 | 0.00019834 | 0.00019889 | 0.00019943 | 0.00019997 | 0.00020052 | 0.00020106 | 0.0002016 | 34455.2362 | 7106.5908 | 98.6324 | 20.3435 | 2560.7403 | 2560.7403 | 377061.2191 | 2560.7403
| HSM001-163582048 | 18 | HSM001 | HSM | North | 424193.8715 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.011908 | 0.012011 | 0.012115 | 0.012219 | 0.012322 | 0.012341 | 0.012359 | 0.012377 | 0.012396 | 0.012414 | 0.012432 | 0.01245 | 0.012469 | 0.012487 | 0.012505 | 0.012524 | 0.012542 | 0.01256 | 0.012579 | 0.012597 | 0.00065033 | 0.00065156 | 0.00065525 | 0.00065591 | 0.00065301 | 0.0006505 | 0.00065237 | 0.00065334 | 0.00064366 | 0.00064462 | 0.00064557 | 0.00064652 | 0.00064747 | 0.00064842 | 0.00064937 | 0.00065032 | 0.00065128 | 0.00065223 | 0.00065318 | 0.00065413 | 34455.2362 | 7106.5908 | 324.104 | 66.8483 | 12620.7041 | 12620.7041 | 424193.8715 | 12620.7041
| HSM001-167869770 | 33 | HSM001 | HSM | North | 777688.7643 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.049673 | 0.050014 | 0.050354 | 0.050695 | 0.051035 | 0.051204 | 0.051373 | 0.051543 | 0.051712 | 0.051881 | 0.05205 | 0.052219 | 0.052388 | 0.052557 | 0.052726 | 0.052895 | 0.053064 | 0.053234 | 0.053403 | 0.053572 | 0.0027128 | 0.002713 | 0.0027234 | 0.0027213 | 0.0027046 | 0.0026991 | 0.0027118 | 0.0027207 | 0.0026852 | 0.002694 | 0.0027028 | 0.0027116 | 0.0027204 | 0.0027291 | 0.0027379 | 0.0027467 | 0.0027555 | 0.0027643 | 0.002773 | 0.0027818 | 34455.2362 | 7106.5908 | 1356.0442 | 279.6919 | 24204.303 | 24204.303 | 777688.7643 | 24204.303
| HSM001-167869862 | 76 | HSM001 | HSM | North | 1791040.7906 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.098679 | 0.099477 | 0.10028 | 0.10108 | 0.10187 | 0.1019 | 0.10193 | 0.10196 | 0.10199 | 0.10202 | 0.10205 | 0.10208 | 0.10211 | 0.10214 | 0.10217 | 0.1022 | 0.10223 | 0.10226 | 0.10229 | 0.10232 | 0.0053891 | 0.0053962 | 0.0054235 | 0.0054258 | 0.0053987 | 0.0053716 | 0.0053806 | 0.0053822 | 0.0052962 | 0.0052978 | 0.0052993 | 0.0053009 | 0.0053024 | 0.0053039 | 0.0053055 | 0.005307 | 0.0053086 | 0.0053101 | 0.0053117 | 0.0053132 | 34455.2362 | 7106.5908 | 2664.7236 | 549.6146 | 131423.6144 | 131423.6144 | 1791040.7906 | 131423.6144
| HSM001-192496053 | 2 | HSM001 | HSM | North | 47132.6524 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34455.2362 | 7106.5908 | 0 | 0 | 0 | 0 | 47132.6524 | 0
| HSM001-24613473 | 228 | HSM001 | HSM | North | 5373122.3717 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 6.4463 | 6.5044 | 6.5625 | 6.6206 | 6.6786 | 6.6806 | 6.6826 | 6.6846 | 6.6866 | 6.6886 | 6.6906 | 6.6926 | 6.6946 | 6.6966 | 6.6986 | 6.7006 | 6.7026 | 6.7046 | 6.7066 | 6.7086 | 0.35205 | 0.35283 | 0.35493 | 0.3554 | 0.35393 | 0.35215 | 0.35275 | 0.35285 | 0.34722 | 0.34732 | 0.34743 | 0.34753 | 0.34763 | 0.34774 | 0.34784 | 0.34794 | 0.34805 | 0.34815 | 0.34825 | 0.34836 | 34455.2362 | 7106.5908 | 174597.5868 | 36011.7571 | 1834373.3388 | 1834373.3388 | 5373122.3717 | 1834373.3388
| HSM001-41021978 | 236 | HSM001 | HSM | North | 5561652.9813 | 0.0019617 | 0.0019485 | 0.0019427 | 0.0019282 | 0.0019035 | 0.0018934 | 0.001896 | 0.001896 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 0.0018652 | 11.0669 | 11.1603 | 11.2538 | 11.3472 | 11.4407 | 11.4484 | 11.4562 | 11.4639 | 11.4717 | 11.4794 | 11.4872 | 11.4949 | 11.5027 | 11.5104 | 11.5182 | 11.5259 | 11.5337 | 11.5414 | 11.5492 | 11.5569 | 0.60439 | 0.60539 | 0.60867 | 0.60913 | 0.60629 | 0.60347 | 0.60472 | 0.60513 | 0.59569 | 0.59609 | 0.5965 | 0.5969 | 0.5973 | 0.5977 | 0.59811 | 0.59851 | 0.59891 | 0.59931 | 0.59972 | 0.60012 | 34455.2362 | 7106.5908 | 299760.7163 | 61827.3728 | 1586005.8597 | 1586005.8597 | 5561652.9813 | 1586005.8597
| HSM002-15416605 | 0 | HSM002 | HSM | North | 0 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34455.2362 | 7106.5908 | 0 | 0 | 0 | 0 | 0 | 0
| HSM002-15416618 | 69 | HSM002 | HSM | North | 1626076.5072 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 48.9981 | 49.2854 | 49.5728 | 49.8602 | 50.1475 | 50.0862 | 50.0249 | 49.9635 | 49.9022 | 49.8408 | 49.7795 | 49.7182 | 49.6568 | 49.5955 | 49.5341 | 49.4728 | 49.4115 | 49.3501 | 49.2888 | 49.2274 | 1.6122 | 1.6251 | 1.636 | 1.6371 | 1.6265 | 1.613 | 1.6125 | 1.6155 | 1.5971 | 1.5951 | 1.5931 | 1.5912 | 1.5892 | 1.5873 | 1.5853 | 1.5833 | 1.5814 | 1.5794 | 1.5774 | 1.5755 | 34455.2362 | 7106.5908 | 799185.9028 | 164836.6917 | 1064143.0018 | 1064143.0018 | 1626076.5072 | 1064143.0018
| HSM002-155422817 | 22 | HSM002 | HSM | North | 518459.1762 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.06223 | 0.06256 | 0.062889 | 0.063219 | 0.063548 | 0.063182 | 0.062816 | 0.06245 | 0.062084 | 0.061719 | 0.061353 | 0.060987 | 0.060621 | 0.060255 | 0.059889 | 0.059523 | 0.059157 | 0.058791 | 0.058425 | 0.058059 | 0.0020476 | 0.0020628 | 0.0020755 | 0.0020756 | 0.0020611 | 0.0020347 | 0.0020248 | 0.0020192 | 0.001987 | 0.0019752 | 0.0019635 | 0.0019518 | 0.0019401 | 0.0019284 | 0.0019167 | 0.001905 | 0.0018933 | 0.0018816 | 0.0018698 | 0.0018581 | 34455.2362 | 7106.5908 | 990.0322 | 204.1998 | 51220.2498 | 51220.2498 | 518459.1762 | 51220.2498
| HSM002-157400246 | 22 | HSM002 | HSM | North | 518459.1762 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0066118 | 0.0066567 | 0.0067015 | 0.0067464 | 0.0067912 | 0.006791 | 0.0067908 | 0.0067906 | 0.0067904 | 0.0067902 | 0.00679 | 0.0067898 | 0.0067896 | 0.0067894 | 0.0067892 | 0.006789 | 0.0067888 | 0.0067886 | 0.0067884 | 0.0067882 | 0.00021755 | 0.00021949 | 0.00022117 | 0.0002215 | 0.00022026 | 0.0002187 | 0.00021889 | 0.00021957 | 0.00021732 | 0.00021731 | 0.00021731 | 0.0002173 | 0.0002173 | 0.00021729 | 0.00021728 | 0.00021728 | 0.00021727 | 0.00021726 | 0.00021726 | 0.00021725 | 34455.2362 | 7106.5908 | 108.8153 | 22.4438 | 6335.1502 | 6335.1502 | 518459.1762 | 6335.1502
| HSM002-157400607 | 32 | HSM002 | HSM | North | 754122.4381 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0073592 | 0.0073953 | 0.0074314 | 0.0074674 | 0.0075035 | 0.0074948 | 0.0074861 | 0.0074775 | 0.0074688 | 0.0074601 | 0.0074515 | 0.0074428 | 0.0074341 | 0.0074255 | 0.0074168 | 0.0074081 | 0.0073995 | 0.0073908 | 0.0073821 | 0.0073735 | 0.00024214 | 0.00024384 | 0.00024525 | 0.00024518 | 0.00024336 | 0.00024136 | 0.00024131 | 0.00024177 | 0.00023903 | 0.00023875 | 0.00023848 | 0.0002382 | 0.00023792 | 0.00023764 | 0.00023737 | 0.00023709 | 0.00023681 | 0.00023654 | 0.00023626 | 0.00023598 | 34455.2362 | 7106.5908 | 119.6963 | 24.688 | 11583.3733 | 11583.3733 | 754122.4381 | 11583.3733
| HSM002-157400755 | 66 | HSM002 | HSM | North | 1555377.5287 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.083523 | 0.084154 | 0.084785 | 0.085416 | 0.086047 | 0.085929 | 0.085812 | 0.085694 | 0.085577 | 0.085459 | 0.085342 | 0.085224 | 0.085107 | 0.084989 | 0.084872 | 0.084754 | 0.084637 | 0.084519 | 0.084402 | 0.084284 | 0.0027481 | 0.0027748 | 0.0027981 | 0.0028044 | 0.0027908 | 0.0027672 | 0.002766 | 0.0027708 | 0.0027388 | 0.002735 | 0.0027313 | 0.0027275 | 0.0027238 | 0.00272 | 0.0027162 | 0.0027125 | 0.0027087 | 0.002705 | 0.0027012 | 0.0026974 | 34455.2362 | 7106.5908 | 1368.8306 | 282.3292 | 73558.4887 | 73558.4887 | 1555377.5287 | 73558.4887
| HSM002-157998943 | 41 | HSM002 | HSM | North | 966219.3739 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0045916 | 0.004615 | 0.0046383 | 0.0046617 | 0.0046851 | 0.0046599 | 0.0046346 | 0.0046094 | 0.0045841 | 0.0045589 | 0.0045336 | 0.0045084 | 0.0044831 | 0.0044578 | 0.0044326 | 0.0044073 | 0.0043821 | 0.0043568 | 0.0043316 | 0.0043063 | 0.00015107 | 0.00015217 | 0.00015308 | 0.00015306 | 0.00015195 | 0.00015007 | 0.00014939 | 0.00014904 | 0.00014671 | 0.0001459 | 0.00014509 | 0.00014429 | 0.00014348 | 0.00014267 | 0.00014186 | 0.00014105 | 0.00014024 | 0.00013944 | 0.00013863 | 0.00013782 | 34455.2362 | 7106.5908 | 73.1385 | 15.0852 | 3340.3742 | 3340.3742 | 966219.3739 | 3340.3742
| HSM002-157999372 | 77 | HSM002 | HSM | North | 1814607.1168 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.025115 | 0.025264 | 0.025414 | 0.025563 | 0.025713 | 0.025652 | 0.025591 | 0.02553 | 0.025469 | 0.025408 | 0.025347 | 0.025286 | 0.025225 | 0.025165 | 0.025104 | 0.025043 | 0.024982 | 0.024921 | 0.02486 | 0.024799 | 0.00082634 | 0.00083302 | 0.00083871 | 0.00083931 | 0.00083394 | 0.00082608 | 0.00082488 | 0.00082547 | 0.00081511 | 0.00081316 | 0.00081121 | 0.00080927 | 0.00080732 | 0.00080537 | 0.00080342 | 0.00080147 | 0.00079952 | 0.00079757 | 0.00079563 | 0.00079368 | 34455.2362 | 7106.5908 | 407.3918 | 84.0269 | 23715.3272 | 23715.3272 | 1814607.1168 | 23715.3272
| HSM002-157999534 | 43 | HSM002 | HSM | North | 1013352.0262 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.002863 | 0.00288 | 0.0028971 | 0.0029141 | 0.0029311 | 0.0029279 | 0.0029247 | 0.0029214 | 0.0029182 | 0.002915 | 0.0029117 | 0.0029085 | 0.0029053 | 0.0029021 | 0.0028988 | 0.0028956 | 0.0028924 | 0.0028891 | 0.0028859 | 0.0028827 | 9.42e-05 | 9.4962e-05 | 9.561e-05 | 9.5678e-05 | 9.5066e-05 | 9.4289e-05 | 9.4273e-05 | 9.446e-05 | 9.3394e-05 | 9.3291e-05 | 9.3188e-05 | 9.3084e-05 | 9.2981e-05 | 9.2877e-05 | 9.2774e-05 | 9.2671e-05 | 9.2567e-05 | 9.2464e-05 | 9.2361e-05 | 9.2257e-05 | 34455.2362 | 7106.5908 | 46.7383 | 9.6401 | 3545.4364 | 3545.4364 | 1013352.0262 | 3545.4364
| HSM002-158058496 | 104 | HSM002 | HSM | North | 2450897.9239 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0010209 | 0.0010233 | 0.0010257 | 0.001028 | 0.0010304 | 0.0010276 | 0.0010249 | 0.0010221 | 0.0010194 | 0.0010166 | 0.0010138 | 0.0010111 | 0.0010083 | 0.0010056 | 0.0010028 | 0.001 | 0.00099728 | 0.00099452 | 0.00099176 | 0.000989 | 3.3592e-05 | 3.3741e-05 | 3.385e-05 | 3.3753e-05 | 3.3419e-05 | 3.3094e-05 | 3.3036e-05 | 3.3049e-05 | 3.2624e-05 | 3.2535e-05 | 3.2447e-05 | 3.2359e-05 | 3.227e-05 | 3.2182e-05 | 3.2094e-05 | 3.2005e-05 | 3.1917e-05 | 3.1829e-05 | 3.174e-05 | 3.1652e-05 | 34455.2362 | 7106.5908 | 16.3392 | 3.3701 | 781.9233 | 781.9233 | 2450897.9239 | 781.9233
| HSM002-158058597 | 58 | HSM002 | HSM | North | 1366846.9191 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0079667 | 0.0080069 | 0.0080471 | 0.0080873 | 0.0081275 | 0.0081079 | 0.0080882 | 0.0080685 | 0.0080489 | 0.0080292 | 0.0080095 | 0.0079898 | 0.0079702 | 0.0079505 | 0.0079308 | 0.0079111 | 0.0078915 | 0.0078718 | 0.0078521 | 0.0078324 | 0.00026213 | 0.00026401 | 0.00026558 | 0.00026553 | 0.0002636 | 0.0002611 | 0.00026071 | 0.00026088 | 0.0002576 | 0.00025697 | 0.00025634 | 0.00025571 | 0.00025508 | 0.00025445 | 0.00025382 | 0.00025319 | 0.00025256 | 0.00025193 | 0.0002513 | 0.00025067 | 34455.2362 | 7106.5908 | 128.815 | 26.5688 | 7188.6975 | 7188.6975 | 1366846.9191 | 7188.6975
| HSM002-158110114 | 41 | HSM002 | HSM | North | 966219.3739 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.025669 | 0.025805 | 0.02594 | 0.026076 | 0.026212 | 0.026094 | 0.025976 | 0.025858 | 0.02574 | 0.025622 | 0.025504 | 0.025386 | 0.025268 | 0.02515 | 0.025032 | 0.024914 | 0.024796 | 0.024677 | 0.024559 | 0.024441 | 0.00084458 | 0.00085085 | 0.0008561 | 0.00085616 | 0.00085015 | 0.00084032 | 0.0008373 | 0.00083608 | 0.00082378 | 0.00082 | 0.00081622 | 0.00081245 | 0.00080867 | 0.00080489 | 0.00080111 | 0.00079733 | 0.00079356 | 0.00078978 | 0.000786 | 0.00078222 | 34455.2362 | 7106.5908 | 411 | 84.7711 | 32424.3145 | 32424.3145 | 966219.3739 | 32424.3145
| HSM002-158110202 | 20 | HSM002 | HSM | North | 471326.5238 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0023122 | 0.002324 | 0.0023358 | 0.0023477 | 0.0023595 | 0.0023478 | 0.0023361 | 0.0023245 | 0.0023128 | 0.0023011 | 0.0022894 | 0.0022777 | 0.0022661 | 0.0022544 | 0.0022427 | 0.002231 | 0.0022194 | 0.0022077 | 0.002196 | 0.0021843 | 7.6076e-05 | 7.6628e-05 | 7.7088e-05 | 7.7081e-05 | 7.6527e-05 | 7.5609e-05 | 7.5303e-05 | 7.5158e-05 | 7.4018e-05 | 7.3645e-05 | 7.3271e-05 | 7.2897e-05 | 7.2523e-05 | 7.215e-05 | 7.1776e-05 | 7.1402e-05 | 7.1028e-05 | 7.0654e-05 | 7.0281e-05 | 6.9907e-05 | 34455.2362 | 7106.5908 | 36.9163 | 7.6142 | 3125.4057 | 3125.4057 | 471326.5238 | 3125.4057
| HSM002-158110374 | 14 | HSM002 | HSM | North | 329928.5667 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.010632 | 0.010689 | 0.010745 | 0.010801 | 0.010858 | 0.010801 | 0.010743 | 0.010686 | 0.010629 | 0.010572 | 0.010515 | 0.010457 | 0.0104 | 0.010343 | 0.010286 | 0.010229 | 0.010171 | 0.010114 | 0.010057 | 0.0099999 | 0.00034983 | 0.00035243 | 0.00035461 | 0.00035464 | 0.00035215 | 0.00034782 | 0.0003463 | 0.00034552 | 0.00034017 | 0.00033834 | 0.00033651 | 0.00033468 | 0.00033285 | 0.00033102 | 0.00032919 | 0.00032736 | 0.00032553 | 0.0003237 | 0.00032187 | 0.00032004 | 34455.2362 | 7106.5908 | 169.5813 | 34.9771 | 10049.8185 | 10049.8185 | 329928.5667 | 10049.8185
| HSM002-158110591 | 35 | HSM002 | HSM | North | 824821.4167 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0048068 | 0.0048342 | 0.0048616 | 0.004889 | 0.0049163 | 0.0048899 | 0.0048635 | 0.0048371 | 0.0048107 | 0.0047843 | 0.0047578 | 0.0047314 | 0.004705 | 0.0046786 | 0.0046522 | 0.0046257 | 0.0045993 | 0.0045729 | 0.0045465 | 0.0045201 | 0.00015816 | 0.0001594 | 0.00016044 | 0.00016052 | 0.00015945 | 0.00015747 | 0.00015677 | 0.0001564 | 0.00015396 | 0.00015312 | 0.00015227 | 0.00015142 | 0.00015058 | 0.00014973 | 0.00014889 | 0.00014804 | 0.0001472 | 0.00014635 | 0.00014551 | 0.00014466 | 34455.2362 | 7106.5908 | 76.7239 | 15.8247 | 6315.0731 | 6315.0731 | 824821.4167 | 6315.0731
| HSM002-158110691 | 106 | HSM002 | HSM | North | 2498030.5763 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.17495 | 0.17591 | 0.17687 | 0.17784 | 0.1788 | 0.17881 | 0.17883 | 0.17884 | 0.17886 | 0.17887 | 0.17889 | 0.1789 | 0.17892 | 0.17893 | 0.17895 | 0.17896 | 0.17897 | 0.17899 | 0.179 | 0.17902 | 0.0057562 | 0.0058002 | 0.0058372 | 0.0058388 | 0.005799 | 0.0057585 | 0.0057643 | 0.0057826 | 0.0057242 | 0.0057246 | 0.0057251 | 0.0057256 | 0.005726 | 0.0057265 | 0.005727 | 0.0057274 | 0.0057279 | 0.0057284 | 0.0057289 | 0.0057293 | 34455.2362 | 7106.5908 | 2868.8178 | 591.7102 | 178828.2636 | 178828.2636 | 2498030.5763 | 178828.2636
| HSM002-158126654 | 14 | HSM002 | HSM | North | 329928.5667 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.035665 | 0.035916 | 0.036167 | 0.036418 | 0.036669 | 0.036671 | 0.036672 | 0.036674 | 0.036675 | 0.036677 | 0.036678 | 0.03668 | 0.036681 | 0.036682 | 0.036684 | 0.036685 | 0.036687 | 0.036688 | 0.03669 | 0.036691 | 0.0011735 | 0.0011842 | 0.0011936 | 0.0011957 | 0.0011893 | 0.0011809 | 0.0011821 | 0.0011858 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011739 | 0.0011739 | 0.001174 | 0.001174 | 0.0011741 | 0.0011741 | 0.0011742 | 0.0011742 | 0.0011743 | 34455.2362 | 7106.5908 | 587.6563 | 121.2075 | 15834.193 | 15834.193 | 329928.5667 | 15834.193
| HSM002-158165458 | 51 | HSM002 | HSM | North | 1201882.6358 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.63914 | 0.64201 | 0.64488 | 0.64775 | 0.65062 | 0.65007 | 0.64952 | 0.64897 | 0.64843 | 0.64788 | 0.64733 | 0.64678 | 0.64623 | 0.64568 | 0.64513 | 0.64459 | 0.64404 | 0.64349 | 0.64294 | 0.64239 | 0.02103 | 0.021169 | 0.021283 | 0.021267 | 0.021102 | 0.020935 | 0.020936 | 0.020984 | 0.020752 | 0.020735 | 0.020717 | 0.0207 | 0.020682 | 0.020664 | 0.020647 | 0.020629 | 0.020612 | 0.020594 | 0.020577 | 0.020559 | 34455.2362 | 7106.5908 | 10397.8034 | 2144.6068 | 374194.0627 | 374194.0627 | 1201882.6358 | 374194.0627
| HSM002-158165593 | 43 | HSM002 | HSM | North | 1013352.0262 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.00014512 | 0.00014608 | 0.00014704 | 0.000148 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 0.00014896 | 4.7748e-06 | 4.8166e-06 | 4.8527e-06 | 4.8593e-06 | 4.8313e-06 | 4.7971e-06 | 4.8015e-06 | 4.8164e-06 | 4.7673e-06 | 4.7673e-06 | 4.7673e-06 | 4.7673e-06 | 4.7673e-06 | 4.7673e-06 | 4.7673e-06 | 4.7673e-06 | 4.7673e-06 | 4.7673e-06 | 4.7673e-06 | 4.7673e-06 | 34455.2362 | 7106.5908 | 2.3874 | 0.49241 | 135.8327 | 135.8327 | 1013352.0262 | 135.8327
| HSM002-163503065 | 26 | HSM002 | HSM | North | 612724.481 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0044879 | 0.0045136 | 0.0045392 | 0.0045649 | 0.0045906 | 0.0045722 | 0.0045538 | 0.0045354 | 0.004517 | 0.0044986 | 0.0044802 | 0.0044618 | 0.0044435 | 0.0044251 | 0.0044067 | 0.0043883 | 0.0043699 | 0.0043515 | 0.0043331 | 0.0043147 | 0.00014766 | 0.00014882 | 0.00014981 | 0.00014988 | 0.00014889 | 0.00014724 | 0.00014679 | 0.00014665 | 0.00014456 | 0.00014397 | 0.00014339 | 0.0001428 | 0.00014221 | 0.00014162 | 0.00014103 | 0.00014044 | 0.00013985 | 0.00013927 | 0.00013868 | 0.00013809 | 34455.2362 | 7106.5908 | 72.1419 | 14.8797 | 1726.1682 | 1726.1682 | 612724.481 | 1726.1682
| HSM002-163560034 | 139 | HSM002 | HSM | North | 3275719.3407 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.27182 | 0.27324 | 0.27465 | 0.27607 | 0.27748 | 0.27606 | 0.27464 | 0.27323 | 0.27181 | 0.27039 | 0.26897 | 0.26755 | 0.26614 | 0.26472 | 0.2633 | 0.26188 | 0.26046 | 0.25905 | 0.25763 | 0.25621 | 0.0089437 | 0.0090093 | 0.0090642 | 0.009064 | 0.0089996 | 0.0088902 | 0.0088528 | 0.0088344 | 0.008699 | 0.0086536 | 0.0086082 | 0.0085628 | 0.0085174 | 0.008472 | 0.0084267 | 0.0083813 | 0.0083359 | 0.0082905 | 0.0082451 | 0.0081997 | 34455.2362 | 7106.5908 | 4337.5911 | 894.6531 | 202557.2649 | 202557.2649 | 3275719.3407 | 202557.2649
| HSM002-24600694 | 666 | HSM002 | HSM | North | 15695173.2437 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 9.2604 | 9.3085 | 9.3566 | 9.4047 | 9.4528 | 9.4295 | 9.4063 | 9.3831 | 9.3598 | 9.3366 | 9.3134 | 9.2901 | 9.2669 | 9.2437 | 9.2204 | 9.1972 | 9.1739 | 9.1507 | 9.1275 | 9.1042 | 0.30469 | 0.30693 | 0.30879 | 0.30878 | 0.30659 | 0.30367 | 0.3032 | 0.30339 | 0.29955 | 0.29881 | 0.29806 | 0.29732 | 0.29658 | 0.29583 | 0.29509 | 0.29435 | 0.2936 | 0.29286 | 0.29212 | 0.29137 | 34455.2362 | 7106.5908 | 149776.2656 | 30892.2167 | 4455824.0946 | 4455824.0946 | 15695173.2437 | 4455824.0946
| HSM002-24601420 | 462 | HSM002 | HSM | North | 10887642.7006 | 0.0011819 | 0.0011844 | 0.0011854 | 0.0011793 | 0.001165 | 0.0011567 | 0.0011578 | 0.0011614 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 0.0011496 | 17.6816 | 17.7643 | 17.8471 | 17.9298 | 18.0125 | 17.994 | 17.9754 | 17.9568 | 17.9382 | 17.9197 | 17.9011 | 17.8825 | 17.8639 | 17.8454 | 17.8268 | 17.8082 | 17.7896 | 17.771 | 17.7525 | 17.7339 | 0.58177 | 0.58574 | 0.589 | 0.58869 | 0.58421 | 0.57947 | 0.57941 | 0.58061 | 0.5741 | 0.5735 | 0.57291 | 0.57231 | 0.57172 | 0.57112 | 0.57053 | 0.56993 | 0.56934 | 0.56874 | 0.56815 | 0.56756 | 34455.2362 | 7106.5908 | 287558.1455 | 59310.5224 | 3127922.0923 | 3127922.0923 | 10887642.7006 | 3127922.0923
| HSM003-15416492 | 188 | HSM003 | HSM | North | 4430469.3241 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 41.2835 | 41.6346 | 41.9858 | 42.337 | 42.6882 | 42.7631 | 42.838 | 42.9129 | 42.9878 | 43.0626 | 43.1375 | 43.2124 | 43.2873 | 43.3622 | 43.4371 | 43.512 | 43.5868 | 43.6617 | 43.7366 | 43.8115 | 2.0611 | 2.1253 | 2.1495 | 2.1638 | 2.162 | 2.1536 | 2.1674 | 2.1861 | 2.1701 | 2.1739 | 2.1777 | 2.1815 | 2.1852 | 2.189 | 2.1928 | 2.1966 | 2.2004 | 2.2041 | 2.2079 | 2.2117 | 34455.2362 | 7106.5908 | 1079714.0544 | 222697.2374 | 1714068.7664 | 1714068.7664 | 4430469.3241 | 1714068.7664
| HSM003-160653285 | 133 | HSM003 | HSM | North | 3134321.3835 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.19408 | 0.19591 | 0.19774 | 0.19957 | 0.2014 | 0.20082 | 0.20023 | 0.19965 | 0.19906 | 0.19847 | 0.19789 | 0.1973 | 0.19671 | 0.19613 | 0.19554 | 0.19496 | 0.19437 | 0.19378 | 0.1932 | 0.19261 | 0.0096898 | 0.010001 | 0.010123 | 0.0102 | 0.010201 | 0.010113 | 0.010131 | 0.010171 | 0.010049 | 0.010019 | 0.0099898 | 0.0099602 | 0.0099306 | 0.009901 | 0.0098714 | 0.0098418 | 0.0098122 | 0.0097826 | 0.0097531 | 0.0097235 | 34455.2362 | 7106.5908 | 4972.5358 | 1025.6141 | 308258.9039 | 308258.9039 | 3134321.3835 | 308258.9039
| HSM003-160653643 | 112 | HSM003 | HSM | North | 2639428.5335 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.10268 | 0.10364 | 0.1046 | 0.10555 | 0.10651 | 0.10626 | 0.10602 | 0.10577 | 0.10552 | 0.10528 | 0.10503 | 0.10478 | 0.10454 | 0.10429 | 0.10404 | 0.1038 | 0.10355 | 0.1033 | 0.10306 | 0.10281 | 0.0051265 | 0.0052905 | 0.0053548 | 0.0053946 | 0.0053945 | 0.0053515 | 0.005364 | 0.0053883 | 0.0053271 | 0.0053146 | 0.0053022 | 0.0052898 | 0.0052773 | 0.0052649 | 0.0052524 | 0.00524 | 0.0052275 | 0.0052151 | 0.0052026 | 0.0051902 | 34455.2362 | 7106.5908 | 2637.8712 | 544.0761 | 181524.6672 | 181524.6672 | 2639428.5335 | 181524.6672
| HSM003-160677450 | 111 | HSM003 | HSM | North | 2615862.2073 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.1715 | 0.17325 | 0.17501 | 0.17676 | 0.17851 | 0.17787 | 0.17723 | 0.17659 | 0.17595 | 0.17531 | 0.17467 | 0.17403 | 0.17339 | 0.17275 | 0.17211 | 0.17147 | 0.17083 | 0.17019 | 0.16955 | 0.16891 | 0.0085622 | 0.008844 | 0.0089594 | 0.0090339 | 0.0090413 | 0.0089578 | 0.0089672 | 0.0089962 | 0.0088825 | 0.0088502 | 0.0088179 | 0.0087856 | 0.0087533 | 0.008721 | 0.0086887 | 0.0086564 | 0.0086241 | 0.0085918 | 0.0085594 | 0.0085271 | 34455.2362 | 7106.5908 | 4389.9933 | 905.4614 | 313652.421 | 313652.421 | 2615862.2073 | 313652.421
| HSM003-160677580 | 105 | HSM003 | HSM | North | 2474464.2501 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.074835 | 0.075761 | 0.076687 | 0.077613 | 0.078538 | 0.078349 | 0.07816 | 0.077971 | 0.077782 | 0.077593 | 0.077404 | 0.077215 | 0.077026 | 0.076836 | 0.076647 | 0.076458 | 0.076269 | 0.07608 | 0.075891 | 0.075702 | 0.0037362 | 0.0038674 | 0.003926 | 0.0039666 | 0.0039778 | 0.0039457 | 0.0039545 | 0.0039721 | 0.0039266 | 0.0039171 | 0.0039075 | 0.003898 | 0.0038884 | 0.0038789 | 0.0038693 | 0.0038598 | 0.0038502 | 0.0038407 | 0.0038311 | 0.0038216 | 34455.2362 | 7106.5908 | 1940.5358 | 400.2467 | 119748.3999 | 119748.3999 | 2474464.2501 | 119748.3999
| HSM003-160677831 | 98 | HSM003 | HSM | North | 2309499.9668 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.1195 | 0.12069 | 0.12187 | 0.12306 | 0.12425 | 0.12432 | 0.1244 | 0.12447 | 0.12455 | 0.12463 | 0.1247 | 0.12478 | 0.12486 | 0.12493 | 0.12501 | 0.12509 | 0.12516 | 0.12524 | 0.12532 | 0.12539 | 0.0059663 | 0.0061608 | 0.0062394 | 0.0062893 | 0.0062927 | 0.0062609 | 0.006294 | 0.0063411 | 0.0062876 | 0.0062915 | 0.0062953 | 0.0062992 | 0.006303 | 0.0063069 | 0.0063108 | 0.0063146 | 0.0063185 | 0.0063223 | 0.0063262 | 0.0063301 | 34455.2362 | 7106.5908 | 3121.9487 | 643.9199 | 114881.2188 | 114881.2188 | 2309499.9668 | 114881.2188
| HSM003-160683184 | 81 | HSM003 | HSM | North | 1908872.4215 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.10618 | 0.10733 | 0.10848 | 0.10963 | 0.11078 | 0.11034 | 0.1099 | 0.10946 | 0.10902 | 0.10858 | 0.10814 | 0.10771 | 0.10727 | 0.10683 | 0.10639 | 0.10595 | 0.10551 | 0.10508 | 0.10464 | 0.1042 | 0.0053012 | 0.0054789 | 0.0055536 | 0.0056028 | 0.0056105 | 0.0055567 | 0.0055604 | 0.0055762 | 0.0055037 | 0.0054815 | 0.0054594 | 0.0054373 | 0.0054151 | 0.005393 | 0.0053709 | 0.0053487 | 0.0053266 | 0.0053044 | 0.0052823 | 0.0052602 | 34455.2362 | 7106.5908 | 2717.9645 | 560.5958 | 156622.6827 | 156622.6827 | 1908872.4215 | 156622.6827
| HSM003-160683337 | 61 | HSM003 | HSM | North | 1437545.8977 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.11561 | 0.1167 | 0.11779 | 0.11888 | 0.11998 | 0.11975 | 0.11953 | 0.11931 | 0.11908 | 0.11886 | 0.11864 | 0.11841 | 0.11819 | 0.11797 | 0.11774 | 0.11752 | 0.1173 | 0.11707 | 0.11685 | 0.11663 | 0.0057718 | 0.0059572 | 0.0060303 | 0.0060759 | 0.0060764 | 0.0060308 | 0.0060476 | 0.0060778 | 0.0060116 | 0.0060003 | 0.005989 | 0.0059777 | 0.0059665 | 0.0059552 | 0.0059439 | 0.0059327 | 0.0059214 | 0.0059101 | 0.0058989 | 0.0058876 | 34455.2362 | 7106.5908 | 2978.0055 | 614.2308 | 94443.2117 | 94443.2117 | 1437545.8977 | 94443.2117
| HSM003-160683747 | 113 | HSM003 | HSM | North | 2662994.8597 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.17274 | 0.17464 | 0.17654 | 0.17845 | 0.18035 | 0.17981 | 0.17926 | 0.17872 | 0.17818 | 0.17764 | 0.1771 | 0.17655 | 0.17601 | 0.17547 | 0.17493 | 0.17439 | 0.17384 | 0.1733 | 0.17276 | 0.17222 | 0.0086242 | 0.008915 | 0.0090382 | 0.0091201 | 0.0091342 | 0.0090552 | 0.0090699 | 0.0091046 | 0.0089949 | 0.0089676 | 0.0089402 | 0.0089128 | 0.0088855 | 0.0088581 | 0.0088307 | 0.0088034 | 0.008776 | 0.0087486 | 0.0087213 | 0.0086939 | 34455.2362 | 7106.5908 | 4446.1565 | 917.0454 | 205794.1552 | 205794.1552 | 2662994.8597 | 205794.1552
| HSM003-160720939 | 111 | HSM003 | HSM | North | 2615862.2073 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.22693 | 0.22888 | 0.23084 | 0.23279 | 0.23475 | 0.23423 | 0.23372 | 0.2332 | 0.23268 | 0.23217 | 0.23165 | 0.23114 | 0.23062 | 0.2301 | 0.22959 | 0.22907 | 0.22855 | 0.22804 | 0.22752 | 0.22701 | 0.01133 | 0.011684 | 0.011818 | 0.011898 | 0.011889 | 0.011796 | 0.011825 | 0.01188 | 0.011746 | 0.01172 | 0.011694 | 0.011668 | 0.011642 | 0.011616 | 0.01159 | 0.011564 | 0.011538 | 0.011512 | 0.011486 | 0.01146 | 34455.2362 | 7106.5908 | 5819.8566 | 1200.3789 | 264611.371 | 264611.371 | 2615862.2073 | 264611.371
| HSM003-160721106 | 78 | HSM003 | HSM | North | 1838173.443 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.10868 | 0.10976 | 0.11084 | 0.11192 | 0.113 | 0.11264 | 0.11227 | 0.1119 | 0.11153 | 0.11116 | 0.11079 | 0.11042 | 0.11005 | 0.10968 | 0.10931 | 0.10894 | 0.10857 | 0.1082 | 0.10783 | 0.10746 | 0.0054261 | 0.0056032 | 0.0056747 | 0.0057202 | 0.0057234 | 0.0056724 | 0.0056801 | 0.0057003 | 0.0056301 | 0.0056115 | 0.0055928 | 0.0055742 | 0.0055555 | 0.0055369 | 0.0055182 | 0.0054996 | 0.0054809 | 0.0054623 | 0.0054436 | 0.005425 | 34455.2362 | 7106.5908 | 2784.0058 | 574.2172 | 139774.4974 | 139774.4974 | 1838173.443 | 139774.4974
| HSM003-160828901 | 82 | HSM003 | HSM | North | 1932438.7477 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.033292 | 0.03368 | 0.034069 | 0.034457 | 0.034845 | 0.034772 | 0.0347 | 0.034627 | 0.034554 | 0.034481 | 0.034409 | 0.034336 | 0.034263 | 0.034191 | 0.034118 | 0.034045 | 0.033972 | 0.0339 | 0.033827 | 0.033754 | 0.0016621 | 0.0017193 | 0.0017441 | 0.001761 | 0.0017648 | 0.0017512 | 0.0017556 | 0.001764 | 0.0017444 | 0.0017407 | 0.001737 | 0.0017334 | 0.0017297 | 0.001726 | 0.0017223 | 0.0017187 | 0.001715 | 0.0017113 | 0.0017077 | 0.001704 | 34455.2362 | 7106.5908 | 862.7426 | 177.9456 | 106252.8389 | 106252.8389 | 1932438.7477 | 106252.8389
| HSM003-160875785 | 112 | HSM003 | HSM | North | 2639428.5335 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.097049 | 0.097828 | 0.098607 | 0.099387 | 0.10017 | 0.10016 | 0.10015 | 0.10014 | 0.10013 | 0.10012 | 0.10011 | 0.10009 | 0.10008 | 0.10007 | 0.10006 | 0.10005 | 0.10004 | 0.10003 | 0.10002 | 0.10001 | 0.0048453 | 0.0049939 | 0.0050482 | 0.0050795 | 0.0050732 | 0.0050439 | 0.0050669 | 0.0051012 | 0.0050546 | 0.005054 | 0.0050535 | 0.005053 | 0.0050525 | 0.005052 | 0.0050515 | 0.005051 | 0.0050504 | 0.0050499 | 0.0050494 | 0.0050489 | 34455.2362 | 7106.5908 | 2510.7569 | 517.8581 | 152047.4206 | 152047.4206 | 2639428.5335 | 152047.4206
| HSM003-160931238 | 144 | HSM003 | HSM | North | 3393550.9716 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.16934 | 0.17118 | 0.17302 | 0.17486 | 0.17671 | 0.17605 | 0.17539 | 0.17474 | 0.17408 | 0.17342 | 0.17276 | 0.17211 | 0.17145 | 0.17079 | 0.17013 | 0.16948 | 0.16882 | 0.16816 | 0.16751 | 0.16685 | 0.0084543 | 0.0087382 | 0.0088579 | 0.008937 | 0.0089498 | 0.008866 | 0.008874 | 0.0089015 | 0.0087879 | 0.0087547 | 0.0087215 | 0.0086883 | 0.0086551 | 0.0086219 | 0.0085888 | 0.0085556 | 0.0085224 | 0.0084892 | 0.008456 | 0.0084229 | 34455.2362 | 7106.5908 | 4340.7987 | 895.3147 | 352047.6423 | 352047.6423 | 3393550.9716 | 352047.6423
| HSM003-161008360 | 88 | HSM003 | HSM | North | 2073836.7049 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.1509 | 0.15229 | 0.15367 | 0.15506 | 0.15645 | 0.1563 | 0.15615 | 0.156 | 0.15585 | 0.1557 | 0.15555 | 0.1554 | 0.15525 | 0.1551 | 0.15495 | 0.1548 | 0.15465 | 0.1545 | 0.15435 | 0.1542 | 0.0075338 | 0.0077738 | 0.0078673 | 0.0079248 | 0.0079236 | 0.0078712 | 0.0079003 | 0.007947 | 0.0078676 | 0.00786 | 0.0078525 | 0.0078449 | 0.0078374 | 0.0078299 | 0.0078223 | 0.0078148 | 0.0078072 | 0.0077997 | 0.0077921 | 0.0077846 | 34455.2362 | 7106.5908 | 3901.784 | 804.7654 | 145040.2938 | 145040.2938 | 2073836.7049 | 145040.2938
| HSM003-161008735 | 149 | HSM003 | HSM | North | 3511382.6026 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.069161 | 0.07002 | 0.07088 | 0.07174 | 0.0726 | 0.072426 | 0.072253 | 0.07208 | 0.071907 | 0.071734 | 0.071561 | 0.071388 | 0.071215 | 0.071041 | 0.070868 | 0.070695 | 0.070522 | 0.070349 | 0.070176 | 0.070003 | 0.0034529 | 0.0035744 | 0.0036287 | 0.0036665 | 0.003677 | 0.0036474 | 0.0036557 | 0.003672 | 0.00363 | 0.0036213 | 0.0036126 | 0.0036038 | 0.0035951 | 0.0035863 | 0.0035776 | 0.0035689 | 0.0035601 | 0.0035514 | 0.0035426 | 0.0035339 | 34455.2362 | 7106.5908 | 1793.9474 | 370.012 | 150546.7687 | 150546.7687 | 3511382.6026 | 150546.7687
| HSM003-161094121 | 21 | HSM003 | HSM | North | 494892.85 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 3.1274e-05 | 3.163e-05 | 3.1987e-05 | 3.2343e-05 | 3.27e-05 | 3.261e-05 | 3.252e-05 | 3.243e-05 | 3.234e-05 | 3.225e-05 | 3.216e-05 | 3.207e-05 | 3.198e-05 | 3.189e-05 | 3.18e-05 | 3.171e-05 | 3.162e-05 | 3.153e-05 | 3.144e-05 | 3.135e-05 | 1.5614e-06 | 1.6146e-06 | 1.6376e-06 | 1.653e-06 | 1.6562e-06 | 1.6423e-06 | 1.6454e-06 | 1.6521e-06 | 1.6326e-06 | 1.6281e-06 | 1.6235e-06 | 1.619e-06 | 1.6144e-06 | 1.6099e-06 | 1.6053e-06 | 1.6008e-06 | 1.5962e-06 | 1.5917e-06 | 1.5872e-06 | 1.5826e-06 | 34455.2362 | 7106.5908 | 0.80701 | 0.16645 | 76.3594 | 76.3594 | 494892.85 | 76.3594
| HSM003-161094233 | 50 | HSM003 | HSM | North | 1178316.3096 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.017985 | 0.01817 | 0.018355 | 0.018539 | 0.018724 | 0.018663 | 0.018602 | 0.018541 | 0.018479 | 0.018418 | 0.018357 | 0.018296 | 0.018235 | 0.018173 | 0.018112 | 0.018051 | 0.01799 | 0.017929 | 0.017867 | 0.017806 | 0.00089794 | 0.00092753 | 0.00093967 | 0.00094752 | 0.00094833 | 0.00093988 | 0.00094116 | 0.00094451 | 0.00093288 | 0.00092979 | 0.0009267 | 0.00092361 | 0.00092052 | 0.00091743 | 0.00091434 | 0.00091125 | 0.00090817 | 0.00090508 | 0.00090199 | 0.0008989 | 34455.2362 | 7106.5908 | 461.1998 | 95.1251 | 51950.5826 | 51950.5826 | 1178316.3096 | 51950.5826
| HSM003-163378469 | 116 | HSM003 | HSM | North | 2733693.8382 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.12136 | 0.12282 | 0.12429 | 0.12575 | 0.12721 | 0.12694 | 0.12668 | 0.12641 | 0.12615 | 0.12588 | 0.12562 | 0.12536 | 0.12509 | 0.12483 | 0.12456 | 0.1243 | 0.12403 | 0.12377 | 0.1235 | 0.12324 | 0.0060592 | 0.0062698 | 0.0063628 | 0.0064267 | 0.0064427 | 0.0063929 | 0.0064093 | 0.0064399 | 0.0063683 | 0.0063549 | 0.0063416 | 0.0063282 | 0.0063149 | 0.0063015 | 0.0062882 | 0.0062748 | 0.0062614 | 0.0062481 | 0.0062347 | 0.0062214 | 34455.2362 | 7106.5908 | 3148.9673 | 649.4926 | 214677.4078 | 214677.4078 | 2733693.8382 | 214677.4078
| HSM003-163378579 | 42 | HSM003 | HSM | North | 989785.7001 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.064971 | 0.065665 | 0.066359 | 0.067053 | 0.067747 | 0.067641 | 0.067534 | 0.067427 | 0.06732 | 0.067214 | 0.067107 | 0.067 | 0.066894 | 0.066787 | 0.06668 | 0.066573 | 0.066467 | 0.06636 | 0.066253 | 0.066146 | 0.0032438 | 0.003352 | 0.0033973 | 0.003427 | 0.0034312 | 0.0034064 | 0.0034169 | 0.0034349 | 0.0033985 | 0.0033931 | 0.0033877 | 0.0033823 | 0.0033769 | 0.0033716 | 0.0033662 | 0.0033608 | 0.0033554 | 0.00335 | 0.0033446 | 0.0033392 | 34455.2362 | 7106.5908 | 1682.771 | 347.0812 | 68239.5909 | 68239.5909 | 989785.7001 | 68239.5909
| HSM003-164469812 | 20 | HSM003 | HSM | North | 471326.5238 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0073203 | 0.007399 | 0.0074777 | 0.0075564 | 0.0076352 | 0.0076139 | 0.0075927 | 0.0075715 | 0.0075503 | 0.0075291 | 0.0075079 | 0.0074867 | 0.0074655 | 0.0074443 | 0.0074231 | 0.0074019 | 0.0073806 | 0.0073594 | 0.0073382 | 0.007317 | 0.00036548 | 0.0003777 | 0.00038282 | 0.0003862 | 0.0003867 | 0.00038344 | 0.00038416 | 0.00038572 | 0.00038116 | 0.00038009 | 0.00037902 | 0.00037795 | 0.00037687 | 0.0003758 | 0.00037473 | 0.00037366 | 0.00037259 | 0.00037152 | 0.00037045 | 0.00036938 | 34455.2362 | 7106.5908 | 188.4807 | 38.8752 | 8492.3985 | 8492.3985 | 471326.5238 | 8492.3985
| HSM003-164470113 | 9 | HSM003 | HSM | North | 212096.9357 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0051342 | 0.0051881 | 0.005242 | 0.0052958 | 0.0053497 | 0.0053294 | 0.0053091 | 0.0052888 | 0.0052685 | 0.0052482 | 0.0052279 | 0.0052076 | 0.0051873 | 0.005167 | 0.0051467 | 0.0051264 | 0.0051061 | 0.0050858 | 0.0050655 | 0.0050451 | 0.00025633 | 0.00026484 | 0.00026836 | 0.00027066 | 0.00027095 | 0.00026839 | 0.00026862 | 0.00026943 | 0.00026597 | 0.00026494 | 0.00026392 | 0.00026289 | 0.00026187 | 0.00026084 | 0.00025982 | 0.00025879 | 0.00025777 | 0.00025674 | 0.00025572 | 0.00025469 | 34455.2362 | 7106.5908 | 131.3959 | 27.1012 | 3196.9397 | 3196.9397 | 212096.9357 | 3196.9397
| HSM003-24600316 | 185 | HSM003 | HSM | North | 4359770.3455 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 4.7606 | 4.8023 | 4.844 | 4.8857 | 4.9273 | 4.9211 | 4.9148 | 4.9085 | 4.9022 | 4.896 | 4.8897 | 4.8834 | 4.8772 | 4.8709 | 4.8646 | 4.8583 | 4.8521 | 4.8458 | 4.8395 | 4.8332 | 0.23768 | 0.24514 | 0.24799 | 0.2497 | 0.24956 | 0.24783 | 0.24867 | 0.25005 | 0.24748 | 0.24716 | 0.24684 | 0.24653 | 0.24621 | 0.24589 | 0.24558 | 0.24526 | 0.24494 | 0.24463 | 0.24431 | 0.24399 | 34455.2362 | 7106.5908 | 122723.459 | 25312.4197 | 602798.8136 | 602798.8136 | 4359770.3455 | 602798.8136
| HSM003-24601084 | 392 | HSM003 | HSM | North | 9237999.8672 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 22.2997 | 22.4692 | 22.6387 | 22.8082 | 22.9777 | 22.901 | 22.8244 | 22.7477 | 22.6711 | 22.5944 | 22.5178 | 22.4411 | 22.3644 | 22.2878 | 22.2111 | 22.1345 | 22.0578 | 21.9812 | 21.9045 | 21.8279 | 1.1133 | 1.147 | 1.159 | 1.1657 | 1.1638 | 1.1533 | 1.1548 | 1.1588 | 1.1445 | 1.1406 | 1.1367 | 1.1329 | 1.129 | 1.1251 | 1.1213 | 1.1174 | 1.1135 | 1.1097 | 1.1058 | 1.1019 | 34455.2362 | 7106.5908 | 566720.9247 | 116889.4521 | 3942958.805 | 3942958.805 | 9237999.8672 | 3942958.805
| HSM003-24601658 | 91 | HSM003 | HSM | North | 2144535.6835 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.67565 | 0.68212 | 0.68859 | 0.69506 | 0.70154 | 0.69905 | 0.69656 | 0.69407 | 0.69159 | 0.6891 | 0.68661 | 0.68413 | 0.68164 | 0.67915 | 0.67667 | 0.67418 | 0.67169 | 0.66921 | 0.66672 | 0.66423 | 0.033732 | 0.03482 | 0.035252 | 0.035523 | 0.035531 | 0.035204 | 0.035243 | 0.035358 | 0.034913 | 0.034787 | 0.034662 | 0.034536 | 0.034411 | 0.034285 | 0.03416 | 0.034034 | 0.033909 | 0.033783 | 0.033657 | 0.033532 | 34455.2362 | 7106.5908 | 17262.6398 | 3560.5188 | 284282.9243 | 284282.9243 | 2144535.6835 | 284282.9243
| HSM003-24601840 | 297 | HSM003 | HSM | North | 6999198.879 | 0.0017933 | 0.0018336 | 0.0018389 | 0.0018358 | 0.0018192 | 0.0018089 | 0.0018174 | 0.0018298 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 0.0018133 | 4.0773 | 4.1085 | 4.1398 | 4.1711 | 4.2023 | 4.1866 | 4.1709 | 4.1551 | 4.1394 | 4.1236 | 4.1079 | 4.0921 | 4.0764 | 4.0606 | 4.0449 | 4.0291 | 4.0134 | 3.9976 | 3.9819 | 3.9661 | 0.20356 | 0.20973 | 0.21194 | 0.21318 | 0.21284 | 0.21084 | 0.21103 | 0.21167 | 0.20896 | 0.20817 | 0.20737 | 0.20658 | 0.20578 | 0.20499 | 0.20419 | 0.2034 | 0.2026 | 0.20181 | 0.20101 | 0.20022 | 34455.2362 | 7106.5908 | 103423.6353 | 21331.72 | 592923.1921 | 592923.1921 | 6999198.879 | 592923.1921
| HSM004-15416655 | 283 | HSM004 | HSM | North | 6669270.3123 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 71.0275 | 71.5909 | 72.1543 | 72.7178 | 73.2812 | 73.1893 | 73.0974 | 73.0054 | 72.9135 | 72.8215 | 72.7296 | 72.6377 | 72.5457 | 72.4538 | 72.3619 | 72.2699 | 72.178 | 72.0861 | 71.9941 | 71.9022 | 2.4323 | 2.4536 | 2.4695 | 2.4775 | 2.4605 | 2.4293 | 2.4248 | 2.4266 | 2.3891 | 2.3861 | 2.3831 | 2.3801 | 2.3771 | 2.3741 | 2.3711 | 2.3681 | 2.365 | 2.362 | 2.359 | 2.356 | 34455.2362 | 7106.5908 | 1200335.9246 | 247576.1923 | 4842604.9732 | 4842604.9732 | 6669270.3123 | 4842604.9732
| HSM004-155422230 | 61 | HSM004 | HSM | North | 1437545.8977 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.0078584 | 0.0079034 | 0.0079483 | 0.0079932 | 0.0080382 | 0.0079912 | 0.0079442 | 0.0078971 | 0.0078501 | 0.0078031 | 0.0077561 | 0.0077091 | 0.0076621 | 0.007615 | 0.007568 | 0.007521 | 0.007474 | 0.007427 | 0.00738 | 0.007333 | 0.00026911 | 0.00027086 | 0.00027203 | 0.00027233 | 0.0002699 | 0.00026524 | 0.00026352 | 0.0002625 | 0.00025722 | 0.00025568 | 0.00025414 | 0.0002526 | 0.00025106 | 0.00024952 | 0.00024798 | 0.00024644 | 0.0002449 | 0.00024336 | 0.00024182 | 0.00024028 | 34455.2362 | 7106.5908 | 128.8229 | 26.5705 | 7693.1156 | 7693.1156 | 1437545.8977 | 7693.1156
| HSM004-159429141 | 55 | HSM004 | HSM | North | 1296147.9405 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.096835 | 0.097572 | 0.098308 | 0.099045 | 0.099782 | 0.09991 | 0.10004 | 0.10017 | 0.10029 | 0.10042 | 0.10055 | 0.10068 | 0.10081 | 0.10094 | 0.10106 | 0.10119 | 0.10132 | 0.10145 | 0.10158 | 0.1017 | 0.0033161 | 0.003344 | 0.0033646 | 0.0033744 | 0.0033503 | 0.0033162 | 0.0033184 | 0.0033295 | 0.0032863 | 0.0032905 | 0.0032947 | 0.0032989 | 0.0033031 | 0.0033073 | 0.0033115 | 0.0033157 | 0.0033199 | 0.0033241 | 0.0033283 | 0.0033325 | 34455.2362 | 7106.5908 | 1655.5434 | 341.4654 | 56757.564 | 56757.564 | 1296147.9405 | 56757.564
| HSM004-159429252 | 102 | HSM004 | HSM | North | 2403765.2716 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.12528 | 0.12594 | 0.1266 | 0.12726 | 0.12791 | 0.1274 | 0.1269 | 0.12639 | 0.12588 | 0.12537 | 0.12487 | 0.12436 | 0.12385 | 0.12334 | 0.12283 | 0.12233 | 0.12182 | 0.12131 | 0.1208 | 0.1203 | 0.0042904 | 0.0043163 | 0.0043328 | 0.0043355 | 0.0042949 | 0.0042288 | 0.0042094 | 0.0042011 | 0.0041247 | 0.0041081 | 0.0040915 | 0.0040748 | 0.0040582 | 0.0040415 | 0.0040249 | 0.0040083 | 0.0039916 | 0.003975 | 0.0039583 | 0.0039417 | 34455.2362 | 7106.5908 | 2070.3496 | 427.0215 | 131578.327 | 131578.327 | 2403765.2716 | 131578.327
| HSM004-159452345 | 63 | HSM004 | HSM | North | 1484678.5501 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.22264 | 0.22403 | 0.22542 | 0.22682 | 0.22821 | 0.22805 | 0.22789 | 0.22773 | 0.22757 | 0.2274 | 0.22724 | 0.22708 | 0.22692 | 0.22676 | 0.2266 | 0.22644 | 0.22627 | 0.22611 | 0.22595 | 0.22579 | 0.0076242 | 0.007678 | 0.0077151 | 0.0077275 | 0.0076626 | 0.0075694 | 0.0075595 | 0.0075695 | 0.0074566 | 0.0074513 | 0.007446 | 0.0074407 | 0.0074355 | 0.0074302 | 0.0074249 | 0.0074196 | 0.0074143 | 0.007409 | 0.0074037 | 0.0073985 | 34455.2362 | 7106.5908 | 3752.3663 | 773.9471 | 167653.0421 | 167653.0421 | 1484678.5501 | 167653.0421
| HSM004-159452484 | 17 | HSM004 | HSM | North | 400627.5453 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.0089201 | 0.0089901 | 0.0090601 | 0.0091301 | 0.0092001 | 0.0092042 | 0.0092082 | 0.0092123 | 0.0092164 | 0.0092205 | 0.0092246 | 0.0092287 | 0.0092328 | 0.0092369 | 0.009241 | 0.009245 | 0.0092491 | 0.0092532 | 0.0092573 | 0.0092614 | 0.00030547 | 0.00030811 | 0.00031008 | 0.00031106 | 0.00030891 | 0.0003055 | 0.00030545 | 0.00030621 | 0.00030199 | 0.00030213 | 0.00030226 | 0.00030239 | 0.00030253 | 0.00030266 | 0.0003028 | 0.00030293 | 0.00030306 | 0.0003032 | 0.00030333 | 0.00030347 | 34455.2362 | 7106.5908 | 151.9866 | 31.3481 | 8857.5623 | 8857.5623 | 400627.5453 | 8857.5623
| HSM004-159452607 | 88 | HSM004 | HSM | North | 2073836.7049 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.027067 | 0.02716 | 0.027252 | 0.027345 | 0.027438 | 0.027327 | 0.027216 | 0.027105 | 0.026994 | 0.026882 | 0.026771 | 0.02666 | 0.026549 | 0.026438 | 0.026327 | 0.026216 | 0.026105 | 0.025994 | 0.025883 | 0.025772 | 0.0009269 | 0.00093081 | 0.0009327 | 0.00093163 | 0.00092127 | 0.00090703 | 0.00090279 | 0.00090094 | 0.00088449 | 0.00088085 | 0.00087721 | 0.00087357 | 0.00086993 | 0.00086629 | 0.00086265 | 0.00085901 | 0.00085537 | 0.00085173 | 0.00084809 | 0.00084445 | 34455.2362 | 7106.5908 | 444.4623 | 91.6729 | 25941.3732 | 25941.3732 | 2073836.7049 | 25941.3732
| HSM004-159452714 | 24 | HSM004 | HSM | North | 565591.8286 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.0066399 | 0.0066812 | 0.0067226 | 0.0067639 | 0.0068053 | 0.006812 | 0.0068188 | 0.0068256 | 0.0068323 | 0.0068391 | 0.0068458 | 0.0068526 | 0.0068593 | 0.0068661 | 0.0068729 | 0.0068796 | 0.0068864 | 0.0068931 | 0.0068999 | 0.0069067 | 0.00022738 | 0.00022898 | 0.00023008 | 0.00023044 | 0.0002285 | 0.00022611 | 0.00022619 | 0.00022688 | 0.00022387 | 0.00022409 | 0.00022432 | 0.00022454 | 0.00022476 | 0.00022498 | 0.0002252 | 0.00022542 | 0.00022564 | 0.00022587 | 0.00022609 | 0.00022631 | 34455.2362 | 7106.5908 | 112.8477 | 23.2755 | 6189.7936 | 6189.7936 | 565591.8286 | 6189.7936
| HSM004-160294257 | 108 | HSM004 | HSM | North | 2545163.2287 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.36802 | 0.37019 | 0.37236 | 0.37453 | 0.3767 | 0.37672 | 0.37674 | 0.37675 | 0.37677 | 0.37679 | 0.37681 | 0.37682 | 0.37684 | 0.37686 | 0.37687 | 0.37689 | 0.37691 | 0.37692 | 0.37694 | 0.37696 | 0.012603 | 0.012687 | 0.012744 | 0.01276 | 0.012648 | 0.012504 | 0.012497 | 0.012523 | 0.012346 | 0.012346 | 0.012347 | 0.012347 | 0.012348 | 0.012348 | 0.012349 | 0.012349 | 0.01235 | 0.012351 | 0.012351 | 0.012352 | 34455.2362 | 7106.5908 | 6218.6409 | 1282.6305 | 445595.8423 | 445595.8423 | 2545163.2287 | 445595.8423
| HSM004-160411068 | 61 | HSM004 | HSM | North | 1437545.8977 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.062204 | 0.06259 | 0.062976 | 0.063362 | 0.063748 | 0.063743 | 0.063739 | 0.063735 | 0.063731 | 0.063726 | 0.063722 | 0.063718 | 0.063714 | 0.06371 | 0.063705 | 0.063701 | 0.063697 | 0.063693 | 0.063688 | 0.063684 | 0.0021302 | 0.0021451 | 0.0021553 | 0.0021587 | 0.0021404 | 0.0021158 | 0.0021143 | 0.0021185 | 0.0020883 | 0.0020881 | 0.002088 | 0.0020878 | 0.0020877 | 0.0020876 | 0.0020874 | 0.0020873 | 0.0020871 | 0.002087 | 0.0020869 | 0.0020867 | 34455.2362 | 7106.5908 | 1051.562 | 216.8907 | 77606.5615 | 77606.5615 | 1437545.8977 | 77606.5615
| HSM004-160411194 | 81 | HSM004 | HSM | North | 1908872.4215 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.074037 | 0.074633 | 0.07523 | 0.075827 | 0.076424 | 0.075798 | 0.075173 | 0.074548 | 0.073922 | 0.073297 | 0.072672 | 0.072046 | 0.071421 | 0.070796 | 0.07017 | 0.069545 | 0.06892 | 0.068294 | 0.067669 | 0.067044 | 0.0025354 | 0.0025578 | 0.0025747 | 0.0025834 | 0.0025661 | 0.0025159 | 0.0024936 | 0.0024779 | 0.0024222 | 0.0024017 | 0.0023812 | 0.0023607 | 0.0023402 | 0.0023197 | 0.0022993 | 0.0022788 | 0.0022583 | 0.0022378 | 0.0022173 | 0.0021968 | 34455.2362 | 7106.5908 | 1208.2596 | 249.2105 | 54373.2753 | 54373.2753 | 1908872.4215 | 54373.2753
| HSM004-160424470 | 152 | HSM004 | HSM | North | 3582081.5812 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.59478 | 0.59843 | 0.60208 | 0.60572 | 0.60937 | 0.60946 | 0.60955 | 0.60964 | 0.60972 | 0.60981 | 0.6099 | 0.60999 | 0.61008 | 0.61017 | 0.61026 | 0.61035 | 0.61043 | 0.61052 | 0.61061 | 0.6107 | 0.020368 | 0.020509 | 0.020606 | 0.020637 | 0.020461 | 0.020229 | 0.02022 | 0.020264 | 0.019979 | 0.019982 | 0.019985 | 0.019987 | 0.01999 | 0.019993 | 0.019996 | 0.019999 | 0.020002 | 0.020005 | 0.020008 | 0.020011 | 34455.2362 | 7106.5908 | 10063.0387 | 2075.5596 | 524336.3432 | 524336.3432 | 3582081.5812 | 524336.3432
| HSM004-160437576 | 49 | HSM004 | HSM | North | 1154749.9834 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.057415 | 0.057822 | 0.058229 | 0.058635 | 0.059042 | 0.058731 | 0.05842 | 0.058109 | 0.057798 | 0.057487 | 0.057176 | 0.056865 | 0.056554 | 0.056243 | 0.055932 | 0.055621 | 0.05531 | 0.054999 | 0.054688 | 0.054377 | 0.0019662 | 0.0019817 | 0.0019929 | 0.0019977 | 0.0019824 | 0.0019494 | 0.0019379 | 0.0019315 | 0.0018939 | 0.0018837 | 0.0018735 | 0.0018633 | 0.0018531 | 0.0018429 | 0.0018327 | 0.0018225 | 0.0018123 | 0.0018021 | 0.001792 | 0.0017818 | 34455.2362 | 7106.5908 | 948.1902 | 195.5697 | 63683.7448 | 63683.7448 | 1154749.9834 | 63683.7448
| HSM004-160437658 | 85 | HSM004 | HSM | North | 2003137.7263 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.11257 | 0.11324 | 0.11392 | 0.1146 | 0.11528 | 0.11467 | 0.11407 | 0.11347 | 0.11286 | 0.11226 | 0.11166 | 0.11105 | 0.11045 | 0.10985 | 0.10924 | 0.10864 | 0.10804 | 0.10743 | 0.10683 | 0.10623 | 0.0038548 | 0.0038811 | 0.0038989 | 0.0039044 | 0.0038707 | 0.0038063 | 0.003784 | 0.0037716 | 0.0036982 | 0.0036785 | 0.0036587 | 0.0036389 | 0.0036191 | 0.0035994 | 0.0035796 | 0.0035598 | 0.0035401 | 0.0035203 | 0.0035005 | 0.0034808 | 34455.2362 | 7106.5908 | 1852.9329 | 382.1781 | 92519.0888 | 92519.0888 | 2003137.7263 | 92519.0888
| HSM004-160438050 | 95 | HSM004 | HSM | North | 2238800.9882 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.39154 | 0.39436 | 0.39717 | 0.39999 | 0.40281 | 0.40326 | 0.4037 | 0.40415 | 0.4046 | 0.40505 | 0.4055 | 0.40594 | 0.40639 | 0.40684 | 0.40729 | 0.40774 | 0.40818 | 0.40863 | 0.40908 | 0.40953 | 0.013408 | 0.013515 | 0.013593 | 0.013627 | 0.013525 | 0.013385 | 0.013392 | 0.013434 | 0.013257 | 0.013272 | 0.013287 | 0.013302 | 0.013316 | 0.013331 | 0.013346 | 0.01336 | 0.013375 | 0.01339 | 0.013404 | 0.013419 | 34455.2362 | 7106.5908 | 6679.308 | 1377.6457 | 343476.8569 | 343476.8569 | 2238800.9882 | 343476.8569
| HSM004-160438389 | 237 | HSM004 | HSM | North | 5585219.3075 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.13854 | 0.13943 | 0.14033 | 0.14122 | 0.14212 | 0.14155 | 0.14098 | 0.14041 | 0.13984 | 0.13928 | 0.13871 | 0.13814 | 0.13757 | 0.137 | 0.13644 | 0.13587 | 0.1353 | 0.13473 | 0.13416 | 0.1336 | 0.0047443 | 0.0047787 | 0.0048027 | 0.0048113 | 0.0047718 | 0.0046983 | 0.0046766 | 0.0046672 | 0.0045822 | 0.0045636 | 0.004545 | 0.0045264 | 0.0045078 | 0.0044892 | 0.0044706 | 0.004452 | 0.0044334 | 0.0044148 | 0.0043962 | 0.0043775 | 34455.2362 | 7106.5908 | 2298.0914 | 473.9946 | 399964.1324 | 399964.1324 | 5585219.3075 | 399964.1324
| HSM004-160438554 | 86 | HSM004 | HSM | North | 2026704.0525 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.19436 | 0.19551 | 0.19666 | 0.19781 | 0.19896 | 0.19765 | 0.19635 | 0.19505 | 0.19375 | 0.19245 | 0.19114 | 0.18984 | 0.18854 | 0.18724 | 0.18594 | 0.18464 | 0.18333 | 0.18203 | 0.18073 | 0.17943 | 0.0066557 | 0.0067003 | 0.0067305 | 0.0067391 | 0.0066803 | 0.0065605 | 0.0065133 | 0.0064833 | 0.0063485 | 0.0063059 | 0.0062632 | 0.0062206 | 0.0061779 | 0.0061353 | 0.0060926 | 0.00605 | 0.0060073 | 0.0059646 | 0.005922 | 0.0058793 | 34455.2362 | 7106.5908 | 3176.7818 | 655.2295 | 160470.6747 | 160470.6747 | 2026704.0525 | 160470.6747
| HSM004-160438797 | 36 | HSM004 | HSM | North | 848387.7429 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.00037173 | 0.00037419 | 0.00037666 | 0.00037913 | 0.0003816 | 0.0003792 | 0.0003768 | 0.0003744 | 0.000372 | 0.0003696 | 0.0003672 | 0.0003648 | 0.0003624 | 0.00036 | 0.0003576 | 0.0003552 | 0.0003528 | 0.0003504 | 0.000348 | 0.0003456 | 1.273e-05 | 1.2824e-05 | 1.2891e-05 | 1.2917e-05 | 1.2813e-05 | 1.2586e-05 | 1.2499e-05 | 1.2445e-05 | 1.2189e-05 | 1.2111e-05 | 1.2032e-05 | 1.1953e-05 | 1.1875e-05 | 1.1796e-05 | 1.1717e-05 | 1.1639e-05 | 1.156e-05 | 1.1481e-05 | 1.1403e-05 | 1.1324e-05 | 34455.2362 | 7106.5908 | 6.0981 | 1.2578 | 188.0525 | 188.0525 | 848387.7429 | 188.0525
| HSM004-160439137 | 92 | HSM004 | HSM | North | 2168102.0096 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.00047096 | 0.00047404 | 0.00047713 | 0.00048021 | 0.0004833 | 0.00048209 | 0.00048087 | 0.00047966 | 0.00047844 | 0.00047723 | 0.00047601 | 0.0004748 | 0.00047358 | 0.00047237 | 0.00047115 | 0.00046994 | 0.00046872 | 0.00046751 | 0.00046629 | 0.00046508 | 1.6128e-05 | 1.6246e-05 | 1.633e-05 | 1.6361e-05 | 1.6228e-05 | 1.6001e-05 | 1.5951e-05 | 1.5943e-05 | 1.5677e-05 | 1.5637e-05 | 1.5597e-05 | 1.5558e-05 | 1.5518e-05 | 1.5478e-05 | 1.5438e-05 | 1.5398e-05 | 1.5358e-05 | 1.5319e-05 | 1.5279e-05 | 1.5239e-05 | 34455.2362 | 7106.5908 | 7.8735 | 1.624 | 551.6995 | 551.6995 | 2168102.0096 | 551.6995
| HSM004-163582339 | 123 | HSM004 | HSM | North | 2898658.1216 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.49402 | 0.49769 | 0.50135 | 0.50501 | 0.50868 | 0.50591 | 0.50314 | 0.50038 | 0.49761 | 0.49485 | 0.49208 | 0.48931 | 0.48655 | 0.48378 | 0.48101 | 0.47825 | 0.47548 | 0.47272 | 0.46995 | 0.46718 | 0.016918 | 0.017057 | 0.017159 | 0.017205 | 0.01708 | 0.016792 | 0.01669 | 0.016632 | 0.016305 | 0.016215 | 0.016124 | 0.016033 | 0.015943 | 0.015852 | 0.015761 | 0.015671 | 0.01558 | 0.015489 | 0.015399 | 0.015308 | 34455.2362 | 7106.5908 | 8160.2048 | 1683.0892 | 606949.831 | 606949.831 | 2898658.1216 | 606949.831
| HSM004-163582585 | 6 | HSM004 | HSM | North | 141397.9572 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 3.7176e-05 | 3.7452e-05 | 3.7728e-05 | 3.8004e-05 | 3.828e-05 | 3.8046e-05 | 3.7812e-05 | 3.7578e-05 | 3.7344e-05 | 3.711e-05 | 3.6876e-05 | 3.6642e-05 | 3.6408e-05 | 3.6174e-05 | 3.594e-05 | 3.5706e-05 | 3.5472e-05 | 3.5238e-05 | 3.5004e-05 | 3.477e-05 | 1.2731e-06 | 1.2836e-06 | 1.2912e-06 | 1.2948e-06 | 1.2853e-06 | 1.2628e-06 | 1.2543e-06 | 1.2491e-06 | 1.2236e-06 | 1.216e-06 | 1.2083e-06 | 1.2006e-06 | 1.193e-06 | 1.1853e-06 | 1.1776e-06 | 1.17e-06 | 1.1623e-06 | 1.1546e-06 | 1.147e-06 | 1.1393e-06 | 34455.2362 | 7106.5908 | 0.61197 | 0.12622 | 12.5815 | 12.5815 | 141397.9572 | 12.5815
| HSM004-163582753 | 19 | HSM004 | HSM | North | 447760.1976 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 5.9206e-05 | 5.9654e-05 | 6.0103e-05 | 6.0551e-05 | 6.1e-05 | 6.09e-05 | 6.08e-05 | 6.07e-05 | 6.06e-05 | 6.05e-05 | 6.04e-05 | 6.03e-05 | 6.02e-05 | 6.01e-05 | 6e-05 | 5.99e-05 | 5.98e-05 | 5.97e-05 | 5.96e-05 | 5.95e-05 | 2.0275e-06 | 2.0445e-06 | 2.057e-06 | 2.063e-06 | 2.0482e-06 | 2.0214e-06 | 2.0168e-06 | 2.0176e-06 | 1.9857e-06 | 1.9824e-06 | 1.9791e-06 | 1.9758e-06 | 1.9726e-06 | 1.9693e-06 | 1.966e-06 | 1.9627e-06 | 1.9595e-06 | 1.9562e-06 | 1.9529e-06 | 1.9496e-06 | 34455.2362 | 7106.5908 | 0.99747 | 0.20573 | 77.9527 | 77.9527 | 447760.1976 | 77.9527
| HSM004-163606098 | 23 | HSM004 | HSM | North | 542025.5024 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.73464 | 0.73963 | 0.74462 | 0.74961 | 0.7546 | 0.75431 | 0.75402 | 0.75373 | 0.75345 | 0.75316 | 0.75287 | 0.75258 | 0.75229 | 0.75201 | 0.75172 | 0.75143 | 0.75114 | 0.75085 | 0.75057 | 0.75028 | 0.025158 | 0.025348 | 0.025484 | 0.025539 | 0.025337 | 0.025037 | 0.025012 | 0.025054 | 0.024688 | 0.024679 | 0.024669 | 0.02466 | 0.02465 | 0.024641 | 0.024631 | 0.024622 | 0.024613 | 0.024603 | 0.024594 | 0.024584 | 34455.2362 | 7106.5908 | 12423.347 | 2562.3868 | 146921.1427 | 146921.1427 | 542025.5024 | 146921.1427
| HSM004-163606269 | 20 | HSM004 | HSM | North | 471326.5238 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.0037363 | 0.003764 | 0.0037917 | 0.0038194 | 0.003847 | 0.0038496 | 0.0038522 | 0.0038547 | 0.0038573 | 0.0038598 | 0.0038624 | 0.003865 | 0.0038675 | 0.0038701 | 0.0038727 | 0.0038752 | 0.0038778 | 0.0038804 | 0.0038829 | 0.0038855 | 0.00012795 | 0.000129 | 0.00012977 | 0.00013012 | 0.00012917 | 0.00012778 | 0.00012778 | 0.00012813 | 0.00012639 | 0.00012648 | 0.00012656 | 0.00012664 | 0.00012673 | 0.00012681 | 0.0001269 | 0.00012698 | 0.00012706 | 0.00012715 | 0.00012723 | 0.00012732 | 34455.2362 | 7106.5908 | 63.6415 | 13.1264 | 3272.6146 | 3272.6146 | 471326.5238 | 3272.6146
| HSM004-163794865 | 64 | HSM004 | HSM | North | 1508244.8763 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.059069 | 0.059499 | 0.059928 | 0.060358 | 0.060787 | 0.060417 | 0.060046 | 0.059675 | 0.059305 | 0.058934 | 0.058563 | 0.058193 | 0.057822 | 0.057451 | 0.057081 | 0.05671 | 0.056339 | 0.055968 | 0.055598 | 0.055227 | 0.0020228 | 0.0020391 | 0.002051 | 0.0020564 | 0.002041 | 0.0020054 | 0.0019918 | 0.0019836 | 0.0019432 | 0.0019311 | 0.0019189 | 0.0019068 | 0.0018946 | 0.0018825 | 0.0018703 | 0.0018582 | 0.0018461 | 0.0018339 | 0.0018218 | 0.0018096 | 34455.2362 | 7106.5908 | 971.9539 | 200.4711 | 31971.9339 | 31971.9339 | 1508244.8763 | 31971.9339
| HSM004-163794980 | 57 | HSM004 | HSM | North | 1343280.5929 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.00060007 | 0.00060443 | 0.00060879 | 0.00061314 | 0.0006175 | 0.00061338 | 0.00060925 | 0.00060513 | 0.000601 | 0.00059688 | 0.00059275 | 0.00058863 | 0.0005845 | 0.00058038 | 0.00057625 | 0.00057213 | 0.000568 | 0.00056388 | 0.00055975 | 0.00055563 | 2.0549e-05 | 2.0715e-05 | 2.0835e-05 | 2.0889e-05 | 2.0734e-05 | 2.0359e-05 | 2.021e-05 | 2.0114e-05 | 1.9693e-05 | 1.9558e-05 | 1.9423e-05 | 1.9287e-05 | 1.9152e-05 | 1.9017e-05 | 1.8882e-05 | 1.8747e-05 | 1.8612e-05 | 1.8476e-05 | 1.8341e-05 | 1.8206e-05 | 34455.2362 | 7106.5908 | 9.844 | 2.0304 | 461.4152 | 461.4152 | 1343280.5929 | 461.4152
| HSM004-163795111 | 13 | HSM004 | HSM | North | 306362.2405 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.00018214 | 0.00018334 | 0.00018455 | 0.00018575 | 0.00018696 | 0.0001862 | 0.00018544 | 0.00018468 | 0.00018392 | 0.00018316 | 0.0001824 | 0.00018164 | 0.00018088 | 0.00018012 | 0.00017936 | 0.0001786 | 0.00017784 | 0.00017708 | 0.00017632 | 0.00017556 | 6.2373e-06 | 6.2836e-06 | 6.3161e-06 | 6.3286e-06 | 6.2775e-06 | 6.1804e-06 | 6.1514e-06 | 6.1386e-06 | 6.0265e-06 | 6.0016e-06 | 5.9767e-06 | 5.9518e-06 | 5.9269e-06 | 5.902e-06 | 5.8771e-06 | 5.8522e-06 | 5.8273e-06 | 5.8024e-06 | 5.7774e-06 | 5.7525e-06 | 34455.2362 | 7106.5908 | 3.0219 | 0.62328 | 21.2568 | 21.2568 | 306362.2405 | 21.2568
| HSM004-163795268 | 64 | HSM004 | HSM | North | 1508244.8763 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.0011363 | 0.0011443 | 0.0011522 | 0.0011602 | 0.0011682 | 0.0011661 | 0.001164 | 0.0011619 | 0.0011598 | 0.0011577 | 0.0011557 | 0.0011536 | 0.0011515 | 0.0011494 | 0.0011473 | 0.0011452 | 0.0011431 | 0.001141 | 0.0011389 | 0.0011369 | 3.8911e-05 | 3.9216e-05 | 3.9435e-05 | 3.9528e-05 | 3.9224e-05 | 3.8706e-05 | 3.8613e-05 | 3.8622e-05 | 3.8004e-05 | 3.7936e-05 | 3.7867e-05 | 3.7799e-05 | 3.773e-05 | 3.7662e-05 | 3.7593e-05 | 3.7525e-05 | 3.7456e-05 | 3.7388e-05 | 3.7319e-05 | 3.7251e-05 | 34455.2362 | 7106.5908 | 19.0949 | 3.9384 | 1142.3826 | 1142.3826 | 1508244.8763 | 1142.3826
| HSM004-24599744 | 180 | HSM004 | HSM | North | 4241938.7145 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 1.9493 | 1.9623 | 1.9753 | 1.9883 | 2.0013 | 1.9873 | 1.9732 | 1.9591 | 1.945 | 1.931 | 1.9169 | 1.9028 | 1.8887 | 1.8747 | 1.8606 | 1.8465 | 1.8324 | 1.8184 | 1.8043 | 1.7902 | 0.066755 | 0.067253 | 0.067605 | 0.067741 | 0.067198 | 0.065961 | 0.065454 | 0.065119 | 0.063733 | 0.063271 | 0.06281 | 0.062349 | 0.061888 | 0.061427 | 0.060966 | 0.060505 | 0.060044 | 0.059582 | 0.059121 | 0.05866 | 34455.2362 | 7106.5908 | 31859.4717 | 6571.1994 | 588609.6968 | 588609.6968 | 4241938.7145 | 588609.6968
| HSM004-24599758 | 354 | HSM004 | HSM | North | 8342479.4719 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 3.2515 | 3.2682 | 3.2848 | 3.3015 | 3.3182 | 3.3001 | 3.2821 | 3.264 | 3.246 | 3.2279 | 3.2099 | 3.1918 | 3.1738 | 3.1557 | 3.1377 | 3.1196 | 3.1016 | 3.0835 | 3.0655 | 3.0474 | 0.11135 | 0.11201 | 0.11242 | 0.11248 | 0.11141 | 0.10954 | 0.10887 | 0.10849 | 0.10636 | 0.10577 | 0.10518 | 0.10459 | 0.10399 | 0.1034 | 0.10281 | 0.10222 | 0.10163 | 0.10104 | 0.10045 | 0.099854 | 34455.2362 | 7106.5908 | 53310.6271 | 10995.6236 | 1162315.8384 | 1162315.8384 | 8342479.4719 | 1162315.8384
| HSM004-24604904 | 493 | HSM004 | HSM | North | 11618198.8125 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 31.2547 | 31.4601 | 31.6656 | 31.871 | 32.0765 | 32.1019 | 32.1274 | 32.1528 | 32.1783 | 32.2037 | 32.2292 | 32.2546 | 32.28 | 32.3055 | 32.3309 | 32.3564 | 32.3818 | 32.4073 | 32.4327 | 32.4581 | 1.0703 | 1.0782 | 1.0837 | 1.0858 | 1.077 | 1.0655 | 1.0657 | 1.0687 | 1.0544 | 1.0552 | 1.056 | 1.0569 | 1.0577 | 1.0585 | 1.0594 | 1.0602 | 1.061 | 1.0619 | 1.0627 | 1.0636 | 34455.2362 | 7106.5908 | 531259.7463 | 109575.38 | 5480850.7864 | 5480850.7864 | 11618198.8125 | 5480850.7864
| HSM004-76359867 | 49 | HSM004 | HSM | North | 1154749.9834 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.06271 | 0.063083 | 0.063455 | 0.063828 | 0.0642 | 0.063864 | 0.063527 | 0.06319 | 0.062853 | 0.062516 | 0.062179 | 0.061842 | 0.061505 | 0.061168 | 0.060831 | 0.060494 | 0.060157 | 0.05982 | 0.059483 | 0.059147 | 0.0021475 | 0.002162 | 0.0021717 | 0.0021746 | 0.0021556 | 0.0021198 | 0.0021073 | 0.0021004 | 0.0020595 | 0.0020484 | 0.0020374 | 0.0020264 | 0.0020153 | 0.0020043 | 0.0019932 | 0.0019822 | 0.0019712 | 0.0019601 | 0.0019491 | 0.001938 | 34455.2362 | 7106.5908 | 1031.9135 | 212.8381 | 49503.9342 | 49503.9342 | 1154749.9834 | 49503.9342
| HSM004-96221391 | 87 | HSM004 | HSM | North | 2050270.3787 | 0.0012301 | 0.001231 | 0.0012293 | 0.0012238 | 0.0012061 | 0.0011922 | 0.0011915 | 0.0011939 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.001177 | 0.43622 | 0.43888 | 0.44155 | 0.44421 | 0.44688 | 0.44657 | 0.44625 | 0.44594 | 0.44562 | 0.44531 | 0.445 | 0.44468 | 0.44437 | 0.44406 | 0.44374 | 0.44343 | 0.44312 | 0.4428 | 0.44249 | 0.44218 | 0.014938 | 0.015041 | 0.015112 | 0.015134 | 0.015005 | 0.014822 | 0.014803 | 0.014823 | 0.014602 | 0.014591 | 0.014581 | 0.014571 | 0.014561 | 0.01455 | 0.01454 | 0.01453 | 0.01452 | 0.014509 | 0.014499 | 0.014489 | 34455.2362 | 7106.5908 | 7348.7144 | 1515.7146 | 257823.849 | 257823.849 | 2050270.3787 | 257823.849
| HSM005-121050437 | 400 | HSM005 | HSM | North | 9426530.4767 | 0.0016797 | 0.0016998 | 0.001692 | 0.0016782 | 0.0016563 | 0.0016412 | 0.0016352 | 0.0016292 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 17.245 | 17.3921 | 17.5391 | 17.6861 | 17.8332 | 17.8554 | 17.8777 | 17.8999 | 17.9222 | 17.9445 | 17.9667 | 17.989 | 18.0112 | 18.0335 | 18.0557 | 18.078 | 18.1003 | 18.1225 | 18.1448 | 18.167 | 0.80641 | 0.82303 | 0.82618 | 0.8263 | 0.82229 | 0.81586 | 0.81389 | 0.81191 | 0.80498 | 0.80598 | 0.80698 | 0.80798 | 0.80898 | 0.80998 | 0.81098 | 0.81197 | 0.81297 | 0.81397 | 0.81497 | 0.81597 | 34455.2362 | 7106.5908 | 405551.0264 | 83647.2331 | 1896536.7049 | 1896536.7049 | 9426530.4767 | 1896536.7049
| HSM005-15416442 | 282 | HSM005 | HSM | North | 6645703.9861 | 0.0016797 | 0.0016998 | 0.001692 | 0.0016782 | 0.0016563 | 0.0016412 | 0.0016352 | 0.0016292 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 65.8701 | 66.3359 | 66.8016 | 67.2673 | 67.7331 | 67.7236 | 67.7142 | 67.7048 | 67.6954 | 67.6859 | 67.6765 | 67.6671 | 67.6577 | 67.6482 | 67.6388 | 67.6294 | 67.62 | 67.6105 | 67.6011 | 67.5917 | 3.0802 | 3.1392 | 3.1467 | 3.1428 | 3.1232 | 3.0945 | 3.0827 | 3.071 | 3.0405 | 3.0401 | 3.0397 | 3.0393 | 3.0389 | 3.0384 | 3.038 | 3.0376 | 3.0372 | 3.0367 | 3.0363 | 3.0359 | 34455.2362 | 7106.5908 | 1531203.0909 | 315819.4494 | 4442841.7848 | 4442841.7848 | 6645703.9861 | 4442841.7848
| HSM005-159947157 | 74 | HSM005 | HSM | North | 1743908.1382 | 0.0016797 | 0.0016998 | 0.001692 | 0.0016782 | 0.0016563 | 0.0016412 | 0.0016352 | 0.0016292 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.22153 | 0.22332 | 0.22511 | 0.22691 | 0.2287 | 0.22829 | 0.22789 | 0.22748 | 0.22708 | 0.22667 | 0.22627 | 0.22586 | 0.22546 | 0.22505 | 0.22465 | 0.22424 | 0.22383 | 0.22343 | 0.22302 | 0.22262 | 0.010359 | 0.010568 | 0.010604 | 0.010601 | 0.010545 | 0.010431 | 0.010375 | 0.010318 | 0.010199 | 0.010181 | 0.010163 | 0.010145 | 0.010126 | 0.010108 | 0.01009 | 0.010072 | 0.010054 | 0.010035 | 0.010017 | 0.0099989 | 34455.2362 | 7106.5908 | 5124.6521 | 1056.989 | 236900.6321 | 236900.6321 | 1743908.1382 | 236900.6321
| HSM005-160318639 | 162 | HSM005 | HSM | North | 3817744.8431 | 0.0016797 | 0.0016998 | 0.001692 | 0.0016782 | 0.0016563 | 0.0016412 | 0.0016352 | 0.0016292 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.1619 | 0.16347 | 0.16503 | 0.1666 | 0.16817 | 0.16775 | 0.16732 | 0.1669 | 0.16647 | 0.16605 | 0.16562 | 0.1652 | 0.16477 | 0.16435 | 0.16392 | 0.1635 | 0.16307 | 0.16265 | 0.16222 | 0.1618 | 0.0075706 | 0.0077355 | 0.0077739 | 0.0077837 | 0.0077544 | 0.0076647 | 0.0076173 | 0.0075701 | 0.0074771 | 0.007458 | 0.0074389 | 0.0074198 | 0.0074007 | 0.0073816 | 0.0073625 | 0.0073434 | 0.0073243 | 0.0073052 | 0.0072861 | 0.007267 | 34455.2362 | 7106.5908 | 3750.2321 | 773.507 | 569276.0877 | 569276.0877 | 3817744.8431 | 569276.0877
| HSM005-160319214 | 90 | HSM005 | HSM | North | 2120969.3573 | 0.0016797 | 0.0016998 | 0.001692 | 0.0016782 | 0.0016563 | 0.0016412 | 0.0016352 | 0.0016292 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.1429 | 0.14407 | 0.14524 | 0.14641 | 0.14757 | 0.14742 | 0.14726 | 0.14711 | 0.14695 | 0.1468 | 0.14664 | 0.14648 | 0.14633 | 0.14617 | 0.14602 | 0.14586 | 0.14571 | 0.14555 | 0.14539 | 0.14524 | 0.0066821 | 0.0068175 | 0.0068413 | 0.0068401 | 0.0068047 | 0.0067359 | 0.0067042 | 0.0066725 | 0.0066004 | 0.0065934 | 0.0065864 | 0.0065794 | 0.0065724 | 0.0065654 | 0.0065584 | 0.0065514 | 0.0065444 | 0.0065374 | 0.0065304 | 0.0065234 | 34455.2362 | 7106.5908 | 3318.5505 | 684.4701 | 223906.2365 | 223906.2365 | 2120969.3573 | 223906.2365
| HSM005-160415406 | 104 | HSM005 | HSM | North | 2450897.9239 | 0.0016797 | 0.0016998 | 0.001692 | 0.0016782 | 0.0016563 | 0.0016412 | 0.0016352 | 0.0016292 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.23499 | 0.23703 | 0.23907 | 0.24111 | 0.24315 | 0.24294 | 0.24273 | 0.24252 | 0.24231 | 0.2421 | 0.24189 | 0.24168 | 0.24147 | 0.24126 | 0.24105 | 0.24084 | 0.24063 | 0.24042 | 0.24021 | 0.24 | 0.010989 | 0.011217 | 0.011261 | 0.011265 | 0.011212 | 0.0111 | 0.01105 | 0.011 | 0.010883 | 0.010874 | 0.010864 | 0.010855 | 0.010846 | 0.010836 | 0.010827 | 0.010817 | 0.010808 | 0.010798 | 0.010789 | 0.010779 | 34455.2362 | 7106.5908 | 5471.2532 | 1128.4775 | 266615.5912 | 266615.5912 | 2450897.9239 | 266615.5912
| HSM005-160415504 | 41 | HSM005 | HSM | North | 966219.3739 | 0.0016797 | 0.0016998 | 0.001692 | 0.0016782 | 0.0016563 | 0.0016412 | 0.0016352 | 0.0016292 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.039394 | 0.03976 | 0.040126 | 0.040492 | 0.040858 | 0.040826 | 0.040794 | 0.040762 | 0.04073 | 0.040698 | 0.040666 | 0.040634 | 0.040601 | 0.040569 | 0.040537 | 0.040505 | 0.040473 | 0.040441 | 0.040409 | 0.040377 | 0.0018422 | 0.0018815 | 0.0018901 | 0.0018918 | 0.001884 | 0.0018654 | 0.0018572 | 0.0018489 | 0.0018294 | 0.0018279 | 0.0018265 | 0.0018251 | 0.0018236 | 0.0018222 | 0.0018207 | 0.0018193 | 0.0018179 | 0.0018164 | 0.001815 | 0.0018135 | 34455.2362 | 7106.5908 | 919.3811 | 189.6276 | 62800.0237 | 62800.0237 | 966219.3739 | 62800.0237
| HSM005-160419737 | 65 | HSM005 | HSM | North | 1531811.2025 | 0.0016797 | 0.0016998 | 0.001692 | 0.0016782 | 0.0016563 | 0.0016412 | 0.0016352 | 0.0016292 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.10056 | 0.10148 | 0.10239 | 0.10331 | 0.10422 | 0.10425 | 0.10427 | 0.1043 | 0.10432 | 0.10435 | 0.10437 | 0.1044 | 0.10442 | 0.10445 | 0.10447 | 0.1045 | 0.10453 | 0.10455 | 0.10458 | 0.1046 | 0.0047026 | 0.0048021 | 0.0048231 | 0.0048265 | 0.0048056 | 0.0047632 | 0.0047469 | 0.0047307 | 0.0046856 | 0.0046868 | 0.0046879 | 0.004689 | 0.0046902 | 0.0046913 | 0.0046925 | 0.0046936 | 0.0046948 | 0.0046959 | 0.004697 | 0.0046982 | 34455.2362 | 7106.5908 | 2357.4901 | 486.2459 | 120938.2755 | 120938.2755 | 1531811.2025 | 120938.2755
| HSM005-160419880 | 78 | HSM005 | HSM | North | 1838173.443 | 0.0016797 | 0.0016998 | 0.001692 | 0.0016782 | 0.0016563 | 0.0016412 | 0.0016352 | 0.0016292 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.075223 | 0.075882 | 0.076541 | 0.077199 | 0.077858 | 0.077933 | 0.078007 | 0.078082 | 0.078156 | 0.078231 | 0.078305 | 0.07838 | 0.078455 | 0.078529 | 0.078604 | 0.078678 | 0.078753 | 0.078828 | 0.078902 | 0.078977 | 0.0035176 | 0.0035909 | 0.0036054 | 0.0036068 | 0.00359 | 0.0035609 | 0.0035513 | 0.0035416 | 0.0035104 | 0.0035137 | 0.0035171 | 0.0035204 | 0.0035238 | 0.0035272 | 0.0035305 | 0.0035339 | 0.0035372 | 0.0035406 | 0.0035439 | 0.0035473 | 34455.2362 | 7106.5908 | 1767.802 | 364.6193 | 76584.0749 | 76584.0749 | 1838173.443 | 76584.0749
| HSM005-160419993 | 38 | HSM005 | HSM | North | 895520.3953 | 0.0016797 | 0.0016998 | 0.001692 | 0.0016782 | 0.0016563 | 0.0016412 | 0.0016352 | 0.0016292 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.041687 | 0.042073 | 0.042458 | 0.042843 | 0.043228 | 0.043308 | 0.043388 | 0.043469 | 0.043549 | 0.043629 | 0.043709 | 0.04379 | 0.04387 | 0.04395 | 0.04403 | 0.044111 | 0.044191 | 0.044271 | 0.044351 | 0.044431 | 0.0019494 | 0.001991 | 0.002 | 0.0020016 | 0.0019933 | 0.0019789 | 0.0019753 | 0.0019717 | 0.001956 | 0.0019596 | 0.0019632 | 0.0019668 | 0.0019704 | 0.001974 | 0.0019776 | 0.0019812 | 0.0019848 | 0.0019884 | 0.001992 | 0.0019956 | 34455.2362 | 7106.5908 | 985.579 | 203.2813 | 43205.3741 | 43205.3741 | 895520.3953 | 43205.3741
| HSM005-160647192 | 70 | HSM005 | HSM | North | 1649642.8334 | 0.0016797 | 0.0016998 | 0.001692 | 0.0016782 | 0.0016563 | 0.0016412 | 0.0016352 | 0.0016292 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.0016133 | 0.27996 | 0.28238 | 0.2848 | 0.28722 | 0.28964 | 0.28926 | 0.28888 | 0.2885 | 0.28812 | 0.28774 | 0.28735 | 0.28697 | 0.28659 | 0.28621 | 0.28583 | 0.28545 | 0.28507 | 0.28468 | 0.2843 | 0.28392 | 0.013091 | 0.013363 | 0.013415 | 0.013419 | 0.013355 | 0.013217 | 0.013151 | 0.013086 | 0.012941 | 0.012924 | 0.012907 | 0.012889 | 0.012872 | 0.012855 | 0.012838 | 0.012821 | 0.012804 | 0.012787 | 0.012769 | 0.012752 | 34455.2362 | 7106.5908 | 6502.7936 | 1341.2386 | 243747.7367 | 243747.7367 | 1649642.8334 | 243747.7367
| HSM006-153767042 | 101 | HSM006 | HSM | North | 2380198.9454 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.15441 | 0.15566 | 0.15692 | 0.15818 | 0.15943 | 0.15907 | 0.15872 | 0.15836 | 0.158 | 0.15764 | 0.15728 | 0.15692 | 0.15656 | 0.1562 | 0.15584 | 0.15548 | 0.15513 | 0.15477 | 0.15441 | 0.15405 | 0.0061823 | 0.0062296 | 0.0062523 | 0.0062526 | 0.0062241 | 0.0061548 | 0.0061356 | 0.0061315 | 0.006065 | 0.0060512 | 0.0060374 | 0.0060236 | 0.0060099 | 0.0059961 | 0.0059823 | 0.0059685 | 0.0059547 | 0.005941 | 0.0059272 | 0.0059134 | 34455.2362 | 7106.5908 | 3035.4353 | 626.076 | 269823.4284 | 269823.4284 | 2380198.9454 | 269823.4284
| HSM006-15416692 | 118 | HSM006 | HSM | North | 2780826.4906 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 4.8174 | 4.8604 | 4.9034 | 4.9464 | 4.9895 | 4.987 | 4.9846 | 4.9821 | 4.9797 | 4.9773 | 4.9748 | 4.9724 | 4.9699 | 4.9675 | 4.9651 | 4.9626 | 4.9602 | 4.9577 | 4.9553 | 4.9529 | 0.19288 | 0.19451 | 0.19537 | 0.19553 | 0.19478 | 0.19295 | 0.19269 | 0.19291 | 0.19115 | 0.19106 | 0.19097 | 0.19087 | 0.19078 | 0.19069 | 0.19059 | 0.1905 | 0.1904 | 0.19031 | 0.19022 | 0.19012 | 34455.2362 | 7106.5908 | 95790.4835 | 19757.3385 | 80348.0576 | 80348.0576 | 2780826.4906 | 80348.0576
| HSM006-15416703 | 0 | HSM006 | HSM | North | 0 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34455.2362 | 7106.5908 | 0 | 0 | 0 | 0 | 0 | 0
| HSM006-160434642 | 27 | HSM006 | HSM | North | 636290.8072 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.10495 | 0.1059 | 0.10684 | 0.10778 | 0.10872 | 0.10876 | 0.1088 | 0.10884 | 0.10887 | 0.10891 | 0.10895 | 0.10899 | 0.10902 | 0.10906 | 0.1091 | 0.10914 | 0.10918 | 0.10921 | 0.10925 | 0.10929 | 0.0042022 | 0.0042379 | 0.0042568 | 0.0042605 | 0.0042444 | 0.0042081 | 0.0042059 | 0.0042141 | 0.0041793 | 0.0041807 | 0.0041822 | 0.0041836 | 0.0041851 | 0.0041865 | 0.004188 | 0.0041894 | 0.0041909 | 0.0041923 | 0.0041937 | 0.0041952 | 34455.2362 | 7106.5908 | 2095.9944 | 432.3109 | 90573.421 | 90573.421 | 636290.8072 | 90573.421
| HSM006-160439280 | 46 | HSM006 | HSM | North | 1084051.0048 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.018696 | 0.018878 | 0.019061 | 0.019244 | 0.019427 | 0.019409 | 0.019391 | 0.019373 | 0.019355 | 0.019337 | 0.019319 | 0.019301 | 0.019283 | 0.019265 | 0.019247 | 0.019229 | 0.019211 | 0.019193 | 0.019175 | 0.019158 | 0.00074855 | 0.0007555 | 0.00075946 | 0.0007607 | 0.00075839 | 0.00075095 | 0.00074961 | 0.00075011 | 0.00074297 | 0.00074228 | 0.00074159 | 0.0007409 | 0.00074021 | 0.00073952 | 0.00073883 | 0.00073815 | 0.00073746 | 0.00073677 | 0.00073608 | 0.00073539 | 34455.2362 | 7106.5908 | 371.953 | 76.7174 | 17717.8312 | 17717.8312 | 1084051.0048 | 17717.8312
| HSM006-160439382 | 29 | HSM006 | HSM | North | 683423.4596 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.00036391 | 0.00036743 | 0.00037095 | 0.00037448 | 0.000378 | 0.00037868 | 0.00037935 | 0.00038003 | 0.0003807 | 0.00038138 | 0.00038205 | 0.00038273 | 0.0003834 | 0.00038408 | 0.00038475 | 0.00038543 | 0.0003861 | 0.00038678 | 0.00038745 | 0.00038813 | 1.457e-05 | 1.4704e-05 | 1.478e-05 | 1.4803e-05 | 1.4757e-05 | 1.4651e-05 | 1.4665e-05 | 1.4715e-05 | 1.4614e-05 | 1.464e-05 | 1.4666e-05 | 1.4691e-05 | 1.4717e-05 | 1.4743e-05 | 1.4769e-05 | 1.4795e-05 | 1.4821e-05 | 1.4847e-05 | 1.4873e-05 | 1.4899e-05 | 34455.2362 | 7106.5908 | 7.3362 | 1.5131 | 416.2076 | 416.2076 | 683423.4596 | 416.2076
| HSM006-160439464 | 75 | HSM006 | HSM | North | 1767474.4644 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.10833 | 0.10924 | 0.11015 | 0.11107 | 0.11198 | 0.11181 | 0.11164 | 0.11147 | 0.1113 | 0.11113 | 0.11096 | 0.11079 | 0.11062 | 0.11045 | 0.11028 | 0.11011 | 0.10994 | 0.10977 | 0.1096 | 0.10943 | 0.0043373 | 0.0043718 | 0.0043889 | 0.0043904 | 0.0043715 | 0.004326 | 0.0043157 | 0.004316 | 0.0042724 | 0.0042658 | 0.0042593 | 0.0042528 | 0.0042462 | 0.0042397 | 0.0042332 | 0.0042266 | 0.0042201 | 0.0042136 | 0.004207 | 0.0042005 | 34455.2362 | 7106.5908 | 2139.4397 | 441.2717 | 122806.5971 | 122806.5971 | 1767474.4644 | 122806.5971
| HSM006-160439562 | 175 | HSM006 | HSM | North | 4124107.0836 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.57445 | 0.57929 | 0.58414 | 0.58898 | 0.59382 | 0.59307 | 0.59232 | 0.59157 | 0.59082 | 0.59007 | 0.58933 | 0.58858 | 0.58783 | 0.58708 | 0.58633 | 0.58558 | 0.58483 | 0.58408 | 0.58333 | 0.58258 | 0.023 | 0.023183 | 0.023274 | 0.023282 | 0.023182 | 0.022947 | 0.022898 | 0.022906 | 0.02268 | 0.022651 | 0.022622 | 0.022593 | 0.022565 | 0.022536 | 0.022507 | 0.022478 | 0.022449 | 0.022421 | 0.022392 | 0.022363 | 34455.2362 | 7106.5908 | 11360.0527 | 2343.0762 | 555485.4404 | 555485.4404 | 4124107.0836 | 555485.4404
| HSM006-160439782 | 64 | HSM006 | HSM | North | 1508244.8763 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.009322 | 0.0094129 | 0.0095039 | 0.0095949 | 0.0096858 | 0.009688 | 0.0096902 | 0.0096924 | 0.0096946 | 0.0096968 | 0.0096989 | 0.0097011 | 0.0097033 | 0.0097055 | 0.0097077 | 0.0097099 | 0.0097121 | 0.0097143 | 0.0097164 | 0.0097186 | 0.00037324 | 0.0003767 | 0.00037867 | 0.00037928 | 0.00037812 | 0.00037484 | 0.0003746 | 0.00037529 | 0.00037214 | 0.00037222 | 0.00037231 | 0.00037239 | 0.00037248 | 0.00037256 | 0.00037264 | 0.00037273 | 0.00037281 | 0.0003729 | 0.00037298 | 0.00037306 | 34455.2362 | 7106.5908 | 186.5221 | 38.4713 | 11675.6255 | 11675.6255 | 1508244.8763 | 11675.6255
| HSM006-163605855 | 16 | HSM006 | HSM | North | 377061.2191 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.00016085 | 0.00016219 | 0.00016353 | 0.00016486 | 0.0001662 | 0.00016626 | 0.00016632 | 0.00016638 | 0.00016644 | 0.0001665 | 0.00016656 | 0.00016662 | 0.00016668 | 0.00016674 | 0.0001668 | 0.00016686 | 0.00016692 | 0.00016698 | 0.00016704 | 0.0001671 | 6.4403e-06 | 6.4907e-06 | 6.5154e-06 | 6.5169e-06 | 6.4883e-06 | 6.4328e-06 | 6.4296e-06 | 6.4422e-06 | 6.3891e-06 | 6.3914e-06 | 6.3937e-06 | 6.396e-06 | 6.3983e-06 | 6.4006e-06 | 6.4029e-06 | 6.4052e-06 | 6.4075e-06 | 6.4098e-06 | 6.4121e-06 | 6.4144e-06 | 34455.2362 | 7106.5908 | 3.2056 | 0.66118 | 150.4935 | 150.4935 | 377061.2191 | 150.4935
| HSM006-201967868 | 234 | HSM006 | HSM | North | 5514520.3289 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 32.9146 | 33.1817 | 33.4489 | 33.716 | 33.9832 | 33.9366 | 33.89 | 33.8434 | 33.7968 | 33.7502 | 33.7036 | 33.657 | 33.6104 | 33.5638 | 33.5172 | 33.4706 | 33.4241 | 33.3775 | 33.3309 | 33.2843 | 1.3179 | 1.3279 | 1.3327 | 1.3328 | 1.3267 | 1.313 | 1.3101 | 1.3104 | 1.2973 | 1.2956 | 1.2938 | 1.292 | 1.2902 | 1.2884 | 1.2866 | 1.2848 | 1.283 | 1.2812 | 1.2795 | 1.2777 | 34455.2362 | 7106.5908 | 649886.7863 | 134042.8897 | 2439092.8627 | 2439092.8627 | 5514520.3289 | 2439092.8627
| HSM006-24597826 | 72 | HSM006 | HSM | North | 1696775.4858 | 0.0014382 | 0.0014375 | 0.0014312 | 0.0014199 | 0.0014023 | 0.0013898 | 0.0013886 | 0.0013908 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 0.0013788 | 5.2381 | 5.2886 | 5.3391 | 5.3896 | 5.4401 | 5.4424 | 5.4448 | 5.4471 | 5.4495 | 5.4518 | 5.4542 | 5.4565 | 5.4589 | 5.4612 | 5.4636 | 5.4659 | 5.4683 | 5.4706 | 5.473 | 5.4753 | 0.20973 | 0.21165 | 0.21273 | 0.21305 | 0.21237 | 0.21057 | 0.21048 | 0.21091 | 0.20919 | 0.20928 | 0.20937 | 0.20946 | 0.20955 | 0.20964 | 0.20973 | 0.20982 | 0.20991 | 0.21 | 0.21009 | 0.21018 | 34455.2362 | 7106.5908 | 104876.271 | 21631.3345 | 251675.1813 | 251675.1813 | 1696775.4858 | 251675.1813
| HSM009-15416366 | 0 | HSM009 | HSM | North | 0 | 0.0011062 | 0.0011071 | 0.0011066 | 0.0011016 | 0.0010922 | 0.0010895 | 0.0010987 | 0.0011123 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34455.2362 | 7106.5908 | 0 | 0 | 0 | 0 | 0 | 0
| HSM009-15416379 | 252 | HSM009 | HSM | North | 5938714.2003 | 0.0011062 | 0.0011071 | 0.0011066 | 0.0011016 | 0.0010922 | 0.0010895 | 0.0010987 | 0.0011123 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 0.0011214 | 74.476 | 74.9296 | 75.3833 | 75.8369 | 76.2905 | 76.1503 | 76.0101 | 75.8699 | 75.7297 | 75.5895 | 75.4493 | 75.3091 | 75.1688 | 75.0286 | 74.8884 | 74.7482 | 74.608 | 74.4678 | 74.3276 | 74.1874 | 2.2936 | 2.3094 | 2.3225 | 2.3257 | 2.3197 | 2.3097 | 2.325 | 2.3495 | 2.3643 | 2.36 | 2.3556 | 2.3512 | 2.3468 | 2.3424 | 2.3381 | 2.3337 | 2.3293 | 2.3249 | 2.3206 | 2.3162 | 34455.2362 | 7106.5908 | 1161101.6753 | 239483.9026 | 1936157.6721 | 1936157.6721 | 5938714.2003 | 1936157.6721
| HSM010-15416755 | 224 | HSM010 | HSM | North | 5278857.067 | 0.0014484 | 0.0014388 | 0.0014343 | 0.001422 | 0.0014108 | 0.0014082 | 0.0014237 | 0.001434 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 0.0014278 | 148.0226 | 148.956 | 149.8895 | 150.8229 | 151.7564 | 151.6045 | 151.4527 | 151.3008 | 151.149 | 150.9971 | 150.8452 | 150.6934 | 150.5415 | 150.3897 | 150.2378 | 150.086 | 149.9341 | 149.7822 | 149.6304 | 149.4785 | 5.9689 | 5.9668 | 5.9854 | 5.9707 | 5.9605 | 5.9434 | 6.0028 | 6.0405 | 6.0083 | 6.0023 | 5.9963 | 5.9902 | 5.9842 | 5.9782 | 5.9721 | 5.9661 | 5.96 | 5.954 | 5.948 | 5.9419 | 34455.2362 | 7106.5908 | 2978243.7654 | 614279.9161 | 3554678.4036 | 3554678.4036 | 5278857.067 | 3554678.4036
| HTN011-155712659 | 71 | HTN011 | HTN | South | 1290836.1703 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.025267 | 0.025386 | 0.025506 | 0.025626 | 0.025746 | 0.025295 | 0.024844 | 0.024394 | 0.023943 | 0.023492 | 0.023042 | 0.022591 | 0.02214 | 0.02169 | 0.021239 | 0.020788 | 0.020337 | 0.019887 | 0.019436 | 0.018985 | 0.00060598 | 0.00061477 | 0.00062225 | 0.00062517 | 0.00062347 | 0.00061437 | 0.00061546 | 0.0006113 | 0.0005927 | 0.00058154 | 0.00057039 | 0.00055923 | 0.00054807 | 0.00053692 | 0.00052576 | 0.0005146 | 0.00050345 | 0.00049229 | 0.00048113 | 0.00046998 | 32583.1543 | 7511.9865 | 270.8487 | 62.4437 | 11494.9254 | 14899.9656 | 1347103.6703 | 11995.9888
| HTN011-156981207 | 47 | HTN011 | HTN | South | 854497.1832 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.069435 | 0.070117 | 0.070799 | 0.071481 | 0.072164 | 0.071127 | 0.070091 | 0.069054 | 0.068018 | 0.066981 | 0.065945 | 0.064908 | 0.063872 | 0.062835 | 0.061799 | 0.060762 | 0.059726 | 0.058689 | 0.057653 | 0.056616 | 0.0016653 | 0.001698 | 0.0017272 | 0.0017439 | 0.0017475 | 0.0017276 | 0.0017363 | 0.0017305 | 0.0016837 | 0.0016581 | 0.0016324 | 0.0016068 | 0.0015811 | 0.0015555 | 0.0015298 | 0.0015041 | 0.0014785 | 0.0014528 | 0.0014272 | 0.0014015 | 32583.1543 | 7511.9865 | 769.8621 | 177.4903 | 29347.7469 | 38041.1706 | 891744.6832 | 30627.0141
| HTN011-157405209 | 25 | HTN011 | HTN | South | 454519.7783 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.0016481 | 0.0016619 | 0.0016757 | 0.0016894 | 0.0017032 | 0.0016832 | 0.0016632 | 0.0016433 | 0.0016233 | 0.0016033 | 0.0015833 | 0.0015633 | 0.0015433 | 0.0015233 | 0.0015034 | 0.0014834 | 0.0014634 | 0.0014434 | 0.0014234 | 0.0014034 | 3.9527e-05 | 4.0245e-05 | 4.0879e-05 | 4.1215e-05 | 4.1246e-05 | 4.0883e-05 | 4.1203e-05 | 4.1179e-05 | 4.0184e-05 | 3.9689e-05 | 3.9194e-05 | 3.8699e-05 | 3.8205e-05 | 3.771e-05 | 3.7215e-05 | 3.672e-05 | 3.6226e-05 | 3.5731e-05 | 3.5236e-05 | 3.4741e-05 | 32583.1543 | 7511.9865 | 18.4502 | 4.2536 | 698.2808 | 905.1263 | 474332.2783 | 728.7188
| HTN011-157405424 | 35 | HTN011 | HTN | South | 636327.6896 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.0012188 | 0.0012296 | 0.0012403 | 0.0012511 | 0.0012618 | 0.0012486 | 0.0012353 | 0.0012221 | 0.0012089 | 0.0011956 | 0.0011824 | 0.0011692 | 0.001156 | 0.0011427 | 0.0011295 | 0.0011163 | 0.001103 | 0.0010898 | 0.0010766 | 0.0010634 | 2.9231e-05 | 2.9775e-05 | 3.0258e-05 | 3.052e-05 | 3.0556e-05 | 3.0326e-05 | 3.0603e-05 | 3.0626e-05 | 2.9925e-05 | 2.9598e-05 | 2.927e-05 | 2.8943e-05 | 2.8615e-05 | 2.8288e-05 | 2.796e-05 | 2.7633e-05 | 2.7305e-05 | 2.6978e-05 | 2.665e-05 | 2.6323e-05 | 32583.1543 | 7511.9865 | 13.7568 | 3.1716 | 607.3915 | 787.3137 | 664065.1896 | 633.8677
| HTN011-157405677 | 99 | HTN011 | HTN | South | 1799898.322 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.17743 | 0.1787 | 0.17998 | 0.18126 | 0.18253 | 0.18012 | 0.17771 | 0.1753 | 0.17288 | 0.17047 | 0.16806 | 0.16565 | 0.16323 | 0.16082 | 0.15841 | 0.156 | 0.15358 | 0.15117 | 0.14876 | 0.14635 | 0.0042553 | 0.0043276 | 0.0043908 | 0.0044219 | 0.0044203 | 0.0043748 | 0.0044023 | 0.0043928 | 0.0042797 | 0.0042199 | 0.0041602 | 0.0041005 | 0.0040408 | 0.0039811 | 0.0039213 | 0.0038616 | 0.0038019 | 0.0037422 | 0.0036825 | 0.0036227 | 32583.1543 | 7511.9865 | 1962.941 | 452.5524 | 91942.1435 | 119177.352 | 1878355.822 | 95949.8981
| HTN011-157406255 | 59 | HTN011 | HTN | South | 1072666.6768 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.062759 | 0.063303 | 0.063846 | 0.06439 | 0.064933 | 0.064327 | 0.063721 | 0.063115 | 0.062509 | 0.061903 | 0.061297 | 0.060691 | 0.060085 | 0.059479 | 0.058873 | 0.058267 | 0.057661 | 0.057055 | 0.056449 | 0.055843 | 0.0015052 | 0.001533 | 0.0015576 | 0.0015708 | 0.0015725 | 0.0015624 | 0.0015785 | 0.0015816 | 0.0015474 | 0.0015324 | 0.0015174 | 0.0015024 | 0.0014874 | 0.0014724 | 0.0014574 | 0.0014424 | 0.0014274 | 0.0014124 | 0.0013974 | 0.0013824 | 32583.1543 | 7511.9865 | 712.3889 | 164.2399 | 35346.2347 | 45816.5374 | 1119424.1768 | 36886.9758
| HTN011-157406464 | 50 | HTN011 | HTN | South | 909039.5566 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.034678 | 0.035013 | 0.035349 | 0.035684 | 0.036019 | 0.035652 | 0.035284 | 0.034916 | 0.034549 | 0.034181 | 0.033813 | 0.033446 | 0.033078 | 0.032711 | 0.032343 | 0.031975 | 0.031608 | 0.03124 | 0.030872 | 0.030505 | 0.00083169 | 0.0008479 | 0.00086236 | 0.00087054 | 0.00087226 | 0.00086592 | 0.00087408 | 0.00087499 | 0.00085524 | 0.00084614 | 0.00083704 | 0.00082794 | 0.00081884 | 0.00080974 | 0.00080064 | 0.00079154 | 0.00078244 | 0.00077334 | 0.00076424 | 0.00075514 | 32583.1543 | 7511.9865 | 393.0736 | 90.6224 | 22313.2217 | 28922.8702 | 948664.5566 | 23285.8542
| HTN011-157406612 | 32 | HTN011 | HTN | South | 581785.3162 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.032481 | 0.032793 | 0.033105 | 0.033417 | 0.033729 | 0.033256 | 0.032783 | 0.032309 | 0.031836 | 0.031363 | 0.03089 | 0.030416 | 0.029943 | 0.02947 | 0.028997 | 0.028523 | 0.02805 | 0.027577 | 0.027104 | 0.02663 | 0.00077899 | 0.00079413 | 0.00080762 | 0.00081524 | 0.0008168 | 0.00080773 | 0.00081211 | 0.00080966 | 0.00078809 | 0.00077638 | 0.00076466 | 0.00075295 | 0.00074123 | 0.00072952 | 0.0007178 | 0.00070609 | 0.00069437 | 0.00068266 | 0.00067094 | 0.00065923 | 32583.1543 | 7511.9865 | 360.54 | 83.1218 | 18715.1085 | 24258.9196 | 607145.3162 | 19530.8993
| HTN011-162645268 | 12 | HTN011 | HTN | South | 218169.4936 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 3.6818e-05 | 3.7138e-05 | 3.7459e-05 | 3.7779e-05 | 3.81e-05 | 3.7662e-05 | 3.7224e-05 | 3.6786e-05 | 3.6348e-05 | 3.591e-05 | 3.5472e-05 | 3.5034e-05 | 3.4596e-05 | 3.4158e-05 | 3.372e-05 | 3.3282e-05 | 3.2844e-05 | 3.2406e-05 | 3.1968e-05 | 3.153e-05 | 8.8301e-07 | 8.9936e-07 | 9.1384e-07 | 9.2166e-07 | 9.2265e-07 | 9.1474e-07 | 9.2213e-07 | 9.2184e-07 | 8.9978e-07 | 8.8894e-07 | 8.781e-07 | 8.6725e-07 | 8.5641e-07 | 8.4557e-07 | 8.3473e-07 | 8.2388e-07 | 8.1304e-07 | 8.022e-07 | 7.9136e-07 | 7.8051e-07 | 32583.1543 | 7511.9865 | 0.41316 | 0.095253 | 18.7638 | 24.3221 | 227679.4936 | 19.5817
| HTN011-162645611 | 19 | HTN011 | HTN | South | 345435.0315 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00066202 | 0.00066714 | 0.00067226 | 0.00067738 | 0.0006825 | 0.00067375 | 0.000665 | 0.00065625 | 0.0006475 | 0.00063875 | 0.00063 | 0.00062125 | 0.0006125 | 0.00060375 | 0.000595 | 0.00058625 | 0.0005775 | 0.00056875 | 0.00056 | 0.00055125 | 1.5877e-05 | 1.6156e-05 | 1.64e-05 | 1.6525e-05 | 1.6528e-05 | 1.6364e-05 | 1.6474e-05 | 1.6445e-05 | 1.6029e-05 | 1.5812e-05 | 1.5595e-05 | 1.5379e-05 | 1.5162e-05 | 1.4946e-05 | 1.4729e-05 | 1.4512e-05 | 1.4296e-05 | 1.4079e-05 | 1.3863e-05 | 1.3646e-05 | 32583.1543 | 7511.9865 | 7.3528 | 1.6952 | 453.2205 | 587.474 | 360492.5315 | 472.9764
| HTN011-190418895 | 0 | HTN011 | HTN | South | 0 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32583.1543 | 7511.9865 | 0 | 0 | 0 | 0 | 0 | 0
| HTN011-190418905 | 140 | HTN011 | HTN | South | 2545310.7584 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 7.2476 | 7.2886 | 7.3297 | 7.3707 | 7.4117 | 7.3635 | 7.3153 | 7.2671 | 7.2189 | 7.1707 | 7.1225 | 7.0743 | 7.0261 | 6.9779 | 6.9296 | 6.8814 | 6.8332 | 6.785 | 6.7368 | 6.6886 | 0.17382 | 0.17651 | 0.17881 | 0.17981 | 0.17949 | 0.17885 | 0.18122 | 0.18211 | 0.1787 | 0.17751 | 0.17631 | 0.17512 | 0.17393 | 0.17273 | 0.17154 | 0.17035 | 0.16915 | 0.16796 | 0.16677 | 0.16557 | 32583.1543 | 7511.9865 | 82700.2076 | 19066.3812 | 390755.6037 | 506505.6823 | 2656260.7584 | 407788.6257
| HTN011-24613192 | 839 | HTN011 | HTN | South | 15253683.7593 | 0.00086147 | 0.00086985 | 0.00087629 | 0.00087629 | 0.00086985 | 0.00087242 | 0.00088982 | 0.00090013 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 0.00088918 | 9.6938 | 9.7547 | 9.8156 | 9.8765 | 9.9374 | 9.8259 | 9.7143 | 9.6028 | 9.4912 | 9.3797 | 9.2681 | 9.1566 | 9.045 | 8.9335 | 8.8219 | 8.7104 | 8.5988 | 8.4873 | 8.3757 | 8.2642 | 0.23249 | 0.23622 | 0.23946 | 0.24095 | 0.24065 | 0.23865 | 0.24065 | 0.24064 | 0.23495 | 0.23219 | 0.22943 | 0.22667 | 0.22391 | 0.22115 | 0.21838 | 0.21562 | 0.21286 | 0.2101 | 0.20734 | 0.20458 | 32583.1543 | 7511.9865 | 108089.5349 | 24919.8441 | 3066263.1224 | 3974555.145 | 15918591.2593 | 3199921.4163
| HTN012-140933454 | 48 | HTN012 | HTN | South | 872677.9743 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.083297 | 0.083984 | 0.084672 | 0.085359 | 0.086047 | 0.085064 | 0.084081 | 0.083099 | 0.082116 | 0.081134 | 0.080151 | 0.079168 | 0.078186 | 0.077203 | 0.07622 | 0.075238 | 0.074255 | 0.073272 | 0.07229 | 0.071307 | 0.0019697 | 0.0019941 | 0.0020193 | 0.0020338 | 0.0020334 | 0.0020153 | 0.0020071 | 0.0019986 | 0.0019565 | 0.0019331 | 0.0019097 | 0.0018863 | 0.0018629 | 0.0018395 | 0.0018161 | 0.0017927 | 0.0017692 | 0.0017458 | 0.0017224 | 0.001699 | 32583.1543 | 7511.9865 | 904.5704 | 208.547 | 40710.7153 | 52770.0907 | 910717.9743 | 42485.2939
| HTN012-140933685 | 45 | HTN012 | HTN | South | 818135.6009 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.028279 | 0.028589 | 0.028899 | 0.029209 | 0.029519 | 0.028899 | 0.028279 | 0.027659 | 0.027039 | 0.026418 | 0.025798 | 0.025178 | 0.024558 | 0.023938 | 0.023318 | 0.022698 | 0.022078 | 0.021458 | 0.020838 | 0.020218 | 0.0006687 | 0.00067881 | 0.0006892 | 0.00069594 | 0.00069758 | 0.00068466 | 0.00067505 | 0.00066522 | 0.00064423 | 0.00062946 | 0.00061468 | 0.00059991 | 0.00058513 | 0.00057036 | 0.00055559 | 0.00054081 | 0.00052604 | 0.00051126 | 0.00049649 | 0.00048171 | 32583.1543 | 7511.9865 | 293.8149 | 67.7385 | 22138.568 | 28696.4803 | 853798.1009 | 23103.5873
| HTN012-140933990 | 34 | HTN012 | HTN | South | 618146.8985 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085731 | 0.00086799 | 0.00087866 | 0.00088933 | 0.0009 | 0.0008832 | 0.0008664 | 0.0008496 | 0.0008328 | 0.000816 | 0.0007992 | 0.0007824 | 0.0007656 | 0.0007488 | 0.000732 | 0.0007152 | 0.0006984 | 0.0006816 | 0.0006648 | 0.000648 | 2.0273e-05 | 2.061e-05 | 2.0955e-05 | 2.119e-05 | 2.1269e-05 | 2.0925e-05 | 2.0682e-05 | 2.0434e-05 | 1.9843e-05 | 1.9442e-05 | 1.9042e-05 | 1.8642e-05 | 1.8242e-05 | 1.7841e-05 | 1.7441e-05 | 1.7041e-05 | 1.664e-05 | 1.624e-05 | 1.584e-05 | 1.544e-05 | 32583.1543 | 7511.9865 | 9.0679 | 2.0906 | 481.8126 | 624.5357 | 645091.8985 | 502.8148
| HTN012-160319327 | 65 | HTN012 | HTN | South | 1181751.4235 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.17875 | 0.17946 | 0.18018 | 0.18089 | 0.18161 | 0.18077 | 0.17993 | 0.17909 | 0.17825 | 0.17742 | 0.17658 | 0.17574 | 0.1749 | 0.17406 | 0.17322 | 0.17239 | 0.17155 | 0.17071 | 0.16987 | 0.16903 | 0.0042269 | 0.0042612 | 0.0042971 | 0.0043101 | 0.0042917 | 0.0042827 | 0.0042952 | 0.0043074 | 0.0042472 | 0.0042272 | 0.0042072 | 0.0041873 | 0.0041673 | 0.0041473 | 0.0041273 | 0.0041074 | 0.0040874 | 0.0040674 | 0.0040474 | 0.0040275 | 32583.1543 | 7511.9865 | 1984.2515 | 457.4655 | 177832.6281 | 230510.4157 | 1233263.9235 | 185584.3457
| HTN012-160319432 | 33 | HTN012 | HTN | South | 599966.1073 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.020516 | 0.020696 | 0.020877 | 0.021057 | 0.021238 | 0.021045 | 0.020852 | 0.020659 | 0.020465 | 0.020272 | 0.020079 | 0.019886 | 0.019693 | 0.0195 | 0.019307 | 0.019114 | 0.018921 | 0.018727 | 0.018534 | 0.018341 | 0.00048513 | 0.00049141 | 0.00049789 | 0.00050172 | 0.00050189 | 0.00049858 | 0.00049776 | 0.00049686 | 0.00048762 | 0.00048302 | 0.00047842 | 0.00047382 | 0.00046921 | 0.00046461 | 0.00046001 | 0.00045541 | 0.00045081 | 0.00044621 | 0.00044161 | 0.00043701 | 32583.1543 | 7511.9865 | 225.9713 | 52.0973 | 19421.5063 | 25174.5675 | 626118.6073 | 20268.0891
| HTN012-160319528 | 34 | HTN012 | HTN | South | 618146.8985 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.0058903 | 0.0059438 | 0.0059972 | 0.0060507 | 0.0061042 | 0.0060553 | 0.0060064 | 0.0059575 | 0.0059086 | 0.0058597 | 0.0058108 | 0.0057619 | 0.005713 | 0.0056642 | 0.0056153 | 0.0055664 | 0.0055175 | 0.0054686 | 0.0054197 | 0.0053708 | 0.00013929 | 0.00014113 | 0.00014303 | 0.00014417 | 0.00014425 | 0.00014346 | 0.00014338 | 0.00014328 | 0.00014078 | 0.00013962 | 0.00013845 | 0.00013729 | 0.00013612 | 0.00013496 | 0.00013379 | 0.00013263 | 0.00013146 | 0.0001303 | 0.00012913 | 0.00012797 | 32583.1543 | 7511.9865 | 65.3098 | 15.0571 | 4731.7288 | 6133.367 | 645091.8985 | 4937.9847
| HTN012-160338385 | 38 | HTN012 | HTN | South | 690870.063 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.10083 | 0.10179 | 0.10275 | 0.10371 | 0.10467 | 0.1031 | 0.10152 | 0.099943 | 0.098366 | 0.096789 | 0.095212 | 0.093635 | 0.092058 | 0.090481 | 0.088904 | 0.087327 | 0.085751 | 0.084174 | 0.082597 | 0.08102 | 0.0023843 | 0.0024169 | 0.0024505 | 0.0024711 | 0.0024736 | 0.0024425 | 0.0024234 | 0.0024037 | 0.0023437 | 0.0023061 | 0.0022686 | 0.002231 | 0.0021934 | 0.0021559 | 0.0021183 | 0.0020807 | 0.0020431 | 0.0020056 | 0.001968 | 0.0019304 | 32583.1543 | 7511.9865 | 1077.9515 | 248.5197 | 30973.8807 | 40148.9995 | 720985.063 | 32324.0309
| HTN012-160338483 | 103 | HTN012 | HTN | South | 1872621.4865 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.093538 | 0.094519 | 0.095501 | 0.096483 | 0.097464 | 0.096425 | 0.095386 | 0.094347 | 0.093307 | 0.092268 | 0.091229 | 0.09019 | 0.08915 | 0.088111 | 0.087072 | 0.086033 | 0.084994 | 0.083954 | 0.082915 | 0.081876 | 0.0022119 | 0.0022443 | 0.0022776 | 0.0022988 | 0.0023033 | 0.0022845 | 0.002277 | 0.0022691 | 0.0022232 | 0.0021984 | 0.0021737 | 0.0021489 | 0.0021241 | 0.0020994 | 0.0020746 | 0.0020499 | 0.0020251 | 0.0020003 | 0.0019756 | 0.0019508 | 32583.1543 | 7511.9865 | 1027.2685 | 236.8349 | 60492.0702 | 78411.1014 | 1954248.9865 | 63128.9172
| HTN012-160338601 | 143 | HTN012 | HTN | South | 2599853.1318 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.093287 | 0.094322 | 0.095357 | 0.096392 | 0.097427 | 0.09574 | 0.094054 | 0.092368 | 0.090681 | 0.088995 | 0.087309 | 0.085622 | 0.083936 | 0.08225 | 0.080563 | 0.078877 | 0.077191 | 0.075504 | 0.073818 | 0.072131 | 0.0022059 | 0.0022396 | 0.0022742 | 0.0022967 | 0.0023024 | 0.0022683 | 0.0022452 | 0.0022215 | 0.0021606 | 0.0021204 | 0.0020803 | 0.0020401 | 0.0019999 | 0.0019597 | 0.0019195 | 0.0018794 | 0.0018392 | 0.001799 | 0.0017588 | 0.0017186 | 32583.1543 | 7511.9865 | 989.9645 | 228.2345 | 79010.7524 | 102415.4092 | 2713180.6318 | 82454.8281
| HTN012-160411348 | 32 | HTN012 | HTN | South | 581785.3162 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.0089633 | 0.0090569 | 0.0091505 | 0.0092441 | 0.0093378 | 0.0091916 | 0.0090455 | 0.0088994 | 0.0087533 | 0.0086072 | 0.008461 | 0.0083149 | 0.0081688 | 0.0080227 | 0.0078766 | 0.0077304 | 0.0075843 | 0.0074382 | 0.0072921 | 0.007146 | 0.00021195 | 0.00021505 | 0.00021823 | 0.00022026 | 0.00022067 | 0.00021777 | 0.00021593 | 0.00021404 | 0.00020856 | 0.00020508 | 0.0002016 | 0.00019812 | 0.00019463 | 0.00019115 | 0.00018767 | 0.00018419 | 0.00018071 | 0.00017723 | 0.00017374 | 0.00017026 | 32583.1543 | 7511.9865 | 95.7974 | 22.0859 | 5527.5878 | 7164.9763 | 607145.3162 | 5768.5352
| HTN012-160437866 | 102 | HTN012 | HTN | South | 1854440.6954 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.0081706 | 0.0082594 | 0.0083482 | 0.008437 | 0.0085258 | 0.0084252 | 0.0083246 | 0.008224 | 0.0081234 | 0.0080229 | 0.0079223 | 0.0078217 | 0.0077211 | 0.0076205 | 0.00752 | 0.0074194 | 0.0073188 | 0.0072182 | 0.0071176 | 0.0070171 | 0.00019321 | 0.00019611 | 0.00019909 | 0.00020102 | 0.00020148 | 0.00019961 | 0.00019872 | 0.0001978 | 0.00019355 | 0.00019116 | 0.00018876 | 0.00018636 | 0.00018397 | 0.00018157 | 0.00017917 | 0.00017678 | 0.00017438 | 0.00017198 | 0.00016959 | 0.00016719 | 32583.1543 | 7511.9865 | 89.294 | 20.5866 | 4542.434 | 5887.999 | 1935275.6954 | 4740.4385
| HTN012-162615153 | 1 | HTN012 | HTN | South | 18180.7911 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 5.7751e-06 | 5.8389e-06 | 5.9026e-06 | 5.9663e-06 | 6.03e-06 | 5.9185e-06 | 5.807e-06 | 5.6955e-06 | 5.584e-06 | 5.4725e-06 | 5.361e-06 | 5.2495e-06 | 5.138e-06 | 5.0265e-06 | 4.915e-06 | 4.8035e-06 | 4.692e-06 | 4.5805e-06 | 4.469e-06 | 4.3575e-06 | 1.3656e-07 | 1.3864e-07 | 1.4077e-07 | 1.4216e-07 | 1.425e-07 | 1.4022e-07 | 1.3862e-07 | 1.3698e-07 | 1.3305e-07 | 1.3039e-07 | 1.2773e-07 | 1.2508e-07 | 1.2242e-07 | 1.1976e-07 | 1.1711e-07 | 1.1445e-07 | 1.1179e-07 | 1.0914e-07 | 1.0648e-07 | 1.0382e-07 | 32583.1543 | 7511.9865 | 0.060872 | 0.014034 | 1.4269 | 1.8496 | 18973.2911 | 1.4891
| HTN012-162615767 | 25 | HTN012 | HTN | South | 454519.7783 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.0063188 | 0.0063759 | 0.006433 | 0.0064901 | 0.0065472 | 0.0064828 | 0.0064184 | 0.006354 | 0.0062896 | 0.0062252 | 0.0061608 | 0.0060963 | 0.0060319 | 0.0059675 | 0.0059031 | 0.0058387 | 0.0057743 | 0.0057099 | 0.0056455 | 0.0055811 | 0.00014942 | 0.00015139 | 0.00015342 | 0.00015464 | 0.00015472 | 0.00015359 | 0.00015322 | 0.00015282 | 0.00014986 | 0.00014832 | 0.00014679 | 0.00014525 | 0.00014372 | 0.00014219 | 0.00014065 | 0.00013912 | 0.00013758 | 0.00013605 | 0.00013451 | 0.00013298 | 32583.1543 | 7511.9865 | 69.3768 | 15.9947 | 3127.3104 | 4053.6859 | 474332.2783 | 3263.6297
| HTN012-162670168 | 5 | HTN012 | HTN | South | 90903.9557 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32583.1543 | 7511.9865 | 0 | 0 | 0 | 0 | 94866.4557 | 0
| HTN012-190418858 | 150 | HTN012 | HTN | South | 2727118.6697 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 1.2523 | 1.2598 | 1.2673 | 1.2748 | 1.2823 | 1.2735 | 1.2647 | 1.256 | 1.2472 | 1.2384 | 1.2296 | 1.2209 | 1.2121 | 1.2033 | 1.1946 | 1.1858 | 1.177 | 1.1683 | 1.1595 | 1.1507 | 0.029614 | 0.029913 | 0.030224 | 0.030373 | 0.030302 | 0.030171 | 0.030191 | 0.030207 | 0.029716 | 0.029507 | 0.029298 | 0.029089 | 0.02888 | 0.028671 | 0.028462 | 0.028253 | 0.028044 | 0.027836 | 0.027627 | 0.027418 | 32583.1543 | 7511.9865 | 13831.3533 | 3188.7931 | 28866.8522 | 37417.8247 | 2845993.6697 | 30125.1572
| HTN012-24597770 | 1484 | HTN012 | HTN | South | 26980294.0391 | 0.00084938 | 0.00085288 | 0.00085664 | 0.00085584 | 0.00084884 | 0.000851 | 0.00085745 | 0.00086391 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 0.00085584 | 25.5559 | 25.7846 | 26.0134 | 26.2422 | 26.471 | 26.105 | 25.739 | 25.373 | 25.007 | 24.641 | 24.2751 | 23.9091 | 23.5431 | 23.1771 | 22.8111 | 22.4451 | 22.0791 | 21.7132 | 21.3472 | 20.9812 | 0.60431 | 0.61223 | 0.62039 | 0.62526 | 0.62556 | 0.61847 | 0.61443 | 0.61025 | 0.59583 | 0.58711 | 0.57839 | 0.56967 | 0.56095 | 0.55223 | 0.54351 | 0.53479 | 0.52607 | 0.51735 | 0.50863 | 0.49991 | 32583.1543 | 7511.9865 | 274558.6594 | 63298.9955 | 8548909.9034 | 11081277.9219 | 28156364.0391 | 8921556.5638
| HTN013-100723362 | 265 | HTN013 | HTN | South | 4817909.6498 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 6.4193 | 6.4637 | 6.5081 | 6.5525 | 6.5969 | 6.5655 | 6.5341 | 6.5027 | 6.4713 | 6.4399 | 6.4085 | 6.3771 | 6.3457 | 6.3143 | 6.2829 | 6.2515 | 6.2201 | 6.1887 | 6.1573 | 6.1259 | 0.18657 | 0.18786 | 0.18818 | 0.18822 | 0.18695 | 0.18433 | 0.18307 | 0.18245 | 0.1796 | 0.17873 | 0.17786 | 0.17699 | 0.17612 | 0.17525 | 0.17437 | 0.1735 | 0.17263 | 0.17176 | 0.17089 | 0.17002 | 32583.1543 | 7511.9865 | 85013.8438 | 19599.7858 | 334696.4622 | 433840.6369 | 5027922.1498 | 349285.8684
| HTN013-142439156 | 48 | HTN013 | HTN | South | 872677.9743 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.20068 | 0.20176 | 0.20285 | 0.20394 | 0.20503 | 0.2039 | 0.20277 | 0.20164 | 0.20051 | 0.19938 | 0.19824 | 0.19711 | 0.19598 | 0.19485 | 0.19372 | 0.19259 | 0.19146 | 0.19033 | 0.1892 | 0.18807 | 0.0058324 | 0.005864 | 0.0058653 | 0.0058582 | 0.0058105 | 0.0057246 | 0.0056812 | 0.0056576 | 0.0055648 | 0.0055334 | 0.005502 | 0.0054707 | 0.0054393 | 0.0054079 | 0.0053765 | 0.0053451 | 0.0053137 | 0.0052823 | 0.005251 | 0.0052196 | 32583.1543 | 7511.9865 | 2634.6383 | 607.411 | 104432.4641 | 135367.5698 | 910717.9743 | 108984.6712
| HTN013-142439579 | 36 | HTN013 | HTN | South | 654508.4807 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.031189 | 0.031377 | 0.031566 | 0.031755 | 0.031943 | 0.031814 | 0.031685 | 0.031556 | 0.031426 | 0.031297 | 0.031168 | 0.031038 | 0.030909 | 0.03078 | 0.030651 | 0.030521 | 0.030392 | 0.030263 | 0.030134 | 0.030004 | 0.00090646 | 0.00091194 | 0.00091271 | 0.00091215 | 0.00090527 | 0.0008932 | 0.00088775 | 0.00088539 | 0.0008722 | 0.00086861 | 0.00086502 | 0.00086144 | 0.00085785 | 0.00085426 | 0.00085067 | 0.00084709 | 0.0008435 | 0.00083991 | 0.00083632 | 0.00083274 | 32583.1543 | 7511.9865 | 413.3855 | 95.3053 | 18436.2247 | 23897.4245 | 683038.4807 | 19239.859
| HTN013-142439718 | 89 | HTN013 | HTN | South | 1618090.4107 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.01803 | 0.018121 | 0.018212 | 0.018303 | 0.018395 | 0.018306 | 0.018217 | 0.018128 | 0.018039 | 0.01795 | 0.017861 | 0.017772 | 0.017683 | 0.017594 | 0.017505 | 0.017416 | 0.017327 | 0.017238 | 0.017149 | 0.01706 | 0.00052402 | 0.00052666 | 0.00052659 | 0.00052576 | 0.0005213 | 0.00051394 | 0.00051039 | 0.00050863 | 0.00050064 | 0.00049817 | 0.0004957 | 0.00049323 | 0.00049076 | 0.00048829 | 0.00048582 | 0.00048335 | 0.00048088 | 0.00047841 | 0.00047595 | 0.00047348 | 32583.1543 | 7511.9865 | 237.2486 | 54.6972 | 13500.003 | 17498.9896 | 1688622.9107 | 14088.4677
| HTN013-142440041 | 101 | HTN013 | HTN | South | 1836259.9043 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.11303 | 0.11385 | 0.11467 | 0.11549 | 0.11631 | 0.11578 | 0.11524 | 0.11471 | 0.11417 | 0.11364 | 0.1131 | 0.11257 | 0.11203 | 0.1115 | 0.11097 | 0.11043 | 0.1099 | 0.10936 | 0.10883 | 0.10829 | 0.0032851 | 0.003309 | 0.0033157 | 0.0033175 | 0.0032963 | 0.0032506 | 0.0032289 | 0.0032186 | 0.0031688 | 0.0031539 | 0.0031391 | 0.0031242 | 0.0031094 | 0.0030945 | 0.0030797 | 0.0030649 | 0.00305 | 0.0030352 | 0.0030203 | 0.0030055 | 32583.1543 | 7511.9865 | 1499.8266 | 345.7823 | 62553.1219 | 81082.6803 | 1916302.4043 | 65279.8101
| HTN013-153173736 | 261 | HTN013 | HTN | South | 4745186.4853 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 3.374 | 3.3945 | 3.4151 | 3.4356 | 3.4561 | 3.4392 | 3.4222 | 3.4052 | 3.3883 | 3.3713 | 3.3543 | 3.3374 | 3.3204 | 3.3034 | 3.2865 | 3.2695 | 3.2525 | 3.2356 | 3.2186 | 3.2016 | 0.098062 | 0.098658 | 0.098745 | 0.098687 | 0.097946 | 0.096556 | 0.095883 | 0.095545 | 0.094037 | 0.093566 | 0.093095 | 0.092624 | 0.092154 | 0.091683 | 0.091212 | 0.090741 | 0.09027 | 0.089799 | 0.089328 | 0.088857 | 32583.1543 | 7511.9865 | 44529.541 | 10266.204 | 402601.1618 | 521860.1454 | 4952028.9853 | 420150.5312
| HTN013-158639235 | 33 | HTN013 | HTN | South | 599966.1073 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.027194 | 0.02733 | 0.027466 | 0.027601 | 0.027737 | 0.027593 | 0.02745 | 0.027306 | 0.027162 | 0.027018 | 0.026875 | 0.026731 | 0.026587 | 0.026443 | 0.0263 | 0.026156 | 0.026012 | 0.025868 | 0.025725 | 0.025581 | 0.00079036 | 0.00079431 | 0.00079415 | 0.00079284 | 0.00078607 | 0.0007747 | 0.00076909 | 0.00076616 | 0.00075385 | 0.00074987 | 0.00074588 | 0.00074189 | 0.0007379 | 0.00073391 | 0.00072992 | 0.00072593 | 0.00072194 | 0.00071795 | 0.00071396 | 0.00070997 | 32583.1543 | 7511.9865 | 357.1345 | 82.3367 | 23358.0547 | 30277.2048 | 626118.6073 | 24376.2315
| HTN013-158639340 | 82 | HTN013 | HTN | South | 1490824.8728 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.02341 | 0.023577 | 0.023744 | 0.023911 | 0.024078 | 0.023966 | 0.023855 | 0.023744 | 0.023632 | 0.023521 | 0.023409 | 0.023298 | 0.023187 | 0.023075 | 0.022964 | 0.022853 | 0.022741 | 0.02263 | 0.022519 | 0.022407 | 0.00068038 | 0.00068523 | 0.00068654 | 0.00068683 | 0.00068236 | 0.00067287 | 0.00066837 | 0.00066621 | 0.00065588 | 0.00065279 | 0.0006497 | 0.00064661 | 0.00064352 | 0.00064043 | 0.00063734 | 0.00063425 | 0.00063116 | 0.00062807 | 0.00062498 | 0.00062188 | 32583.1543 | 7511.9865 | 310.4569 | 71.5753 | 18021.1733 | 23359.4262 | 1555809.8728 | 18806.7156
| HTN013-159365790 | 40 | HTN013 | HTN | South | 727231.6453 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0093106 | 0.0093553 | 0.0094 | 0.0094447 | 0.0094894 | 0.009429 | 0.0093686 | 0.0093082 | 0.0092478 | 0.0091874 | 0.009127 | 0.0090666 | 0.0090062 | 0.0089458 | 0.0088854 | 0.008825 | 0.0087646 | 0.0087042 | 0.0086437 | 0.0085833 | 0.0002706 | 0.0002719 | 0.00027179 | 0.0002713 | 0.00026893 | 0.00026472 | 0.00026249 | 0.00026117 | 0.00025666 | 0.00025499 | 0.00025331 | 0.00025163 | 0.00024996 | 0.00024828 | 0.0002466 | 0.00024493 | 0.00024325 | 0.00024157 | 0.0002399 | 0.00023822 | 32583.1543 | 7511.9865 | 121.4604 | 28.0025 | 5349.0341 | 6933.5312 | 758931.6453 | 5582.1983
| HTN013-159366167 | 44 | HTN013 | HTN | South | 799954.8098 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0066222 | 0.0066533 | 0.0066843 | 0.0067153 | 0.0067463 | 0.0067094 | 0.0066724 | 0.0066354 | 0.0065985 | 0.0065615 | 0.0065245 | 0.0064875 | 0.0064506 | 0.0064136 | 0.0063766 | 0.0063396 | 0.0063027 | 0.0062657 | 0.0062287 | 0.0061918 | 0.00019247 | 0.00019337 | 0.00019327 | 0.0001929 | 0.00019119 | 0.00018837 | 0.00018695 | 0.00018618 | 0.00018313 | 0.00018211 | 0.00018108 | 0.00018005 | 0.00017903 | 0.000178 | 0.00017698 | 0.00017595 | 0.00017492 | 0.0001739 | 0.00017287 | 0.00017184 | 32583.1543 | 7511.9865 | 86.7495 | 19.9999 | 3981.4854 | 5160.8856 | 834824.8098 | 4155.0382
| HTN013-159381071 | 33 | HTN013 | HTN | South | 599966.1073 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.039245 | 0.039422 | 0.0396 | 0.039777 | 0.039955 | 0.039738 | 0.039521 | 0.039305 | 0.039088 | 0.038871 | 0.038654 | 0.038437 | 0.03822 | 0.038004 | 0.037787 | 0.03757 | 0.037353 | 0.037136 | 0.03692 | 0.036703 | 0.0011406 | 0.0011458 | 0.001145 | 0.0011426 | 0.0011323 | 0.0011157 | 0.0011073 | 0.0011028 | 0.0010848 | 0.0010788 | 0.0010728 | 0.0010668 | 0.0010608 | 0.0010547 | 0.0010487 | 0.0010427 | 0.0010367 | 0.0010307 | 0.0010247 | 0.0010186 | 32583.1543 | 7511.9865 | 513.9683 | 118.4944 | 16807.3711 | 21786.0701 | 626118.6073 | 17540.0038
| HTN013-159381283 | 33 | HTN013 | HTN | South | 599966.1073 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.029744 | 0.029876 | 0.030009 | 0.030142 | 0.030275 | 0.030095 | 0.029916 | 0.029736 | 0.029557 | 0.029378 | 0.029198 | 0.029019 | 0.02884 | 0.02866 | 0.028481 | 0.028302 | 0.028122 | 0.027943 | 0.027764 | 0.027584 | 0.00086446 | 0.00086832 | 0.00086769 | 0.00086582 | 0.00085797 | 0.00084494 | 0.00083818 | 0.00083436 | 0.00082032 | 0.00081535 | 0.00081037 | 0.00080539 | 0.00080041 | 0.00079544 | 0.00079046 | 0.00078548 | 0.0007805 | 0.00077553 | 0.00077055 | 0.00076557 | 32583.1543 | 7511.9865 | 388.4683 | 89.5607 | 23096.2105 | 29937.7968 | 626118.6073 | 24102.9734
| HTN013-160286800 | 59 | HTN013 | HTN | South | 1072666.6768 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.10987 | 0.11047 | 0.11106 | 0.11165 | 0.11225 | 0.11167 | 0.1111 | 0.11052 | 0.10994 | 0.10937 | 0.10879 | 0.10822 | 0.10764 | 0.10707 | 0.10649 | 0.10592 | 0.10534 | 0.10477 | 0.10419 | 0.10362 | 0.0031933 | 0.0032106 | 0.0032112 | 0.0032072 | 0.003181 | 0.0031352 | 0.0031127 | 0.003101 | 0.0030514 | 0.0030354 | 0.0030195 | 0.0030035 | 0.0029875 | 0.0029715 | 0.0029556 | 0.0029396 | 0.0029236 | 0.0029077 | 0.0028917 | 0.0028757 | 32583.1543 | 7511.9865 | 1445.2662 | 333.2035 | 73479.8371 | 95246.1198 | 1119424.1768 | 76682.8204
| HTN013-160451212 | 50 | HTN013 | HTN | South | 909039.5566 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.021526 | 0.021693 | 0.02186 | 0.022027 | 0.022194 | 0.022105 | 0.022016 | 0.021928 | 0.021839 | 0.021751 | 0.021662 | 0.021573 | 0.021485 | 0.021396 | 0.021307 | 0.021219 | 0.02113 | 0.021042 | 0.020953 | 0.020864 | 0.00062561 | 0.00063047 | 0.00063206 | 0.00063271 | 0.00062897 | 0.00062061 | 0.00061686 | 0.00061526 | 0.00060612 | 0.00060366 | 0.0006012 | 0.00059874 | 0.00059628 | 0.00059382 | 0.00059136 | 0.0005889 | 0.00058644 | 0.00058398 | 0.00058152 | 0.00057906 | 32583.1543 | 7511.9865 | 286.9682 | 66.16 | 13543.6159 | 17555.5216 | 948664.5566 | 14133.9816
| HTN013-160451319 | 28 | HTN013 | HTN | South | 509062.1517 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.00011254 | 0.00011325 | 0.00011395 | 0.00011466 | 0.00011536 | 0.00011463 | 0.0001139 | 0.00011318 | 0.00011245 | 0.00011172 | 0.00011099 | 0.00011026 | 0.00010954 | 0.00010881 | 0.00010808 | 0.00010735 | 0.00010662 | 0.0001059 | 0.00010517 | 0.00010444 | 3.2709e-06 | 3.2914e-06 | 3.2948e-06 | 3.2935e-06 | 3.2693e-06 | 3.2184e-06 | 3.1914e-06 | 3.1755e-06 | 3.1209e-06 | 3.1007e-06 | 3.0805e-06 | 3.0602e-06 | 3.04e-06 | 3.0198e-06 | 2.9996e-06 | 2.9794e-06 | 2.9592e-06 | 2.939e-06 | 2.9188e-06 | 2.8986e-06 | 32583.1543 | 7511.9865 | 1.4755 | 0.34018 | 51.1745 | 66.3335 | 531252.1517 | 53.4052
| HTN013-160451462 | 53 | HTN013 | HTN | South | 963581.93 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.028471 | 0.028663 | 0.028856 | 0.029049 | 0.029241 | 0.029066 | 0.02889 | 0.028714 | 0.028539 | 0.028363 | 0.028187 | 0.028012 | 0.027836 | 0.02766 | 0.027485 | 0.027309 | 0.027133 | 0.026958 | 0.026782 | 0.026606 | 0.00082747 | 0.00083307 | 0.00083435 | 0.00083442 | 0.0008287 | 0.00081604 | 0.00080944 | 0.00080568 | 0.00079206 | 0.00078718 | 0.00078231 | 0.00077743 | 0.00077255 | 0.00076768 | 0.0007628 | 0.00075793 | 0.00075305 | 0.00074817 | 0.0007433 | 0.00073842 | 32583.1543 | 7511.9865 | 374.4712 | 86.3337 | 26223.0949 | 33990.9305 | 1005584.43 | 27366.1586
| HTN013-160772532 | 45 | HTN013 | HTN | South | 818135.6009 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.020762 | 0.020863 | 0.020963 | 0.021064 | 0.021164 | 0.021053 | 0.020942 | 0.020831 | 0.02072 | 0.020609 | 0.020499 | 0.020388 | 0.020277 | 0.020166 | 0.020055 | 0.019944 | 0.019833 | 0.019722 | 0.019611 | 0.0195 | 0.00060342 | 0.00060634 | 0.00060613 | 0.00060504 | 0.00059978 | 0.00059108 | 0.00058676 | 0.00058449 | 0.00057507 | 0.00057199 | 0.00056891 | 0.00056583 | 0.00056276 | 0.00055968 | 0.0005566 | 0.00055352 | 0.00055044 | 0.00054737 | 0.00054429 | 0.00054121 | 32583.1543 | 7511.9865 | 272.4477 | 62.8123 | 12788.806 | 16577.1209 | 853798.1009 | 13346.2695
| HTN013-162802647 | 8 | HTN013 | HTN | South | 145446.3291 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.00050392 | 0.00050619 | 0.00050846 | 0.00051072 | 0.00051299 | 0.00051026 | 0.00050754 | 0.00050481 | 0.00050208 | 0.00049935 | 0.00049662 | 0.00049389 | 0.00049117 | 0.00048844 | 0.00048571 | 0.00048298 | 0.00048025 | 0.00047752 | 0.0004748 | 0.00047207 | 1.4646e-05 | 1.4712e-05 | 1.4702e-05 | 1.467e-05 | 1.4538e-05 | 1.4326e-05 | 1.422e-05 | 1.4164e-05 | 1.3935e-05 | 1.3859e-05 | 1.3783e-05 | 1.3707e-05 | 1.3632e-05 | 1.3556e-05 | 1.348e-05 | 1.3405e-05 | 1.3329e-05 | 1.3253e-05 | 1.3177e-05 | 1.3102e-05 | 32583.1543 | 7511.9865 | 6.6027 | 1.5222 | 523.4371 | 678.4902 | 151786.3291 | 546.2537
| HTN013-162821734 | 98 | HTN013 | HTN | South | 1781717.5309 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.23015 | 0.23231 | 0.23447 | 0.23663 | 0.23879 | 0.23738 | 0.23596 | 0.23455 | 0.23313 | 0.23171 | 0.2303 | 0.22888 | 0.22747 | 0.22605 | 0.22464 | 0.22322 | 0.22181 | 0.22039 | 0.21898 | 0.21756 | 0.006689 | 0.0067518 | 0.0067795 | 0.0067972 | 0.0067673 | 0.0066645 | 0.0066112 | 0.006581 | 0.0064703 | 0.006431 | 0.0063917 | 0.0063524 | 0.0063131 | 0.0062738 | 0.0062346 | 0.0061953 | 0.006156 | 0.0061167 | 0.0060774 | 0.0060381 | 32583.1543 | 7511.9865 | 3054.0033 | 704.0949 | 121061.1613 | 156922.039 | 1859382.5309 | 126338.2127
| HTN013-162978763 | 27 | HTN013 | HTN | South | 490881.3605 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 6.0768e-05 | 6.1176e-05 | 6.1584e-05 | 6.1992e-05 | 6.24e-05 | 6.2091e-05 | 6.1782e-05 | 6.1473e-05 | 6.1164e-05 | 6.0855e-05 | 6.0546e-05 | 6.0237e-05 | 5.9928e-05 | 5.9619e-05 | 5.931e-05 | 5.9001e-05 | 5.8692e-05 | 5.8383e-05 | 5.8074e-05 | 5.7765e-05 | 1.7661e-06 | 1.778e-06 | 1.7807e-06 | 1.7807e-06 | 1.7684e-06 | 1.7432e-06 | 1.731e-06 | 1.7248e-06 | 1.6975e-06 | 1.689e-06 | 1.6804e-06 | 1.6718e-06 | 1.6632e-06 | 1.6547e-06 | 1.6461e-06 | 1.6375e-06 | 1.6289e-06 | 1.6204e-06 | 1.6118e-06 | 1.6032e-06 | 32583.1543 | 7511.9865 | 0.80346 | 0.18524 | 71.6625 | 92.8905 | 512278.8605 | 74.7863
| HTN013-163073376 | 123 | HTN013 | HTN | South | 2236237.3092 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.093578 | 0.094013 | 0.094447 | 0.094882 | 0.095317 | 0.094852 | 0.094387 | 0.093922 | 0.093457 | 0.092992 | 0.092527 | 0.092063 | 0.091598 | 0.091133 | 0.090668 | 0.090203 | 0.089738 | 0.089273 | 0.088809 | 0.088344 | 0.0027197 | 0.0027324 | 0.0027309 | 0.0027255 | 0.0027013 | 0.002663 | 0.0026445 | 0.0026353 | 0.0025938 | 0.0025809 | 0.002568 | 0.0025551 | 0.0025422 | 0.0025293 | 0.0025164 | 0.0025035 | 0.0024906 | 0.0024777 | 0.0024648 | 0.0024519 | 32583.1543 | 7511.9865 | 1229.4625 | 283.4503 | 96684.3029 | 125324.2394 | 2333714.8092 | 100898.768
| HTN013-163073497 | 31 | HTN013 | HTN | South | 563604.5251 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 1.9526e-05 | 1.9682e-05 | 1.9838e-05 | 1.9994e-05 | 2.015e-05 | 1.9994e-05 | 1.9838e-05 | 1.9682e-05 | 1.9526e-05 | 1.937e-05 | 1.9214e-05 | 1.9058e-05 | 1.8902e-05 | 1.8746e-05 | 1.859e-05 | 1.8434e-05 | 1.8278e-05 | 1.8122e-05 | 1.7966e-05 | 1.781e-05 | 5.675e-07 | 5.7203e-07 | 5.736e-07 | 5.7432e-07 | 5.7105e-07 | 5.6134e-07 | 5.5582e-07 | 5.5224e-07 | 5.4192e-07 | 5.3759e-07 | 5.3326e-07 | 5.2893e-07 | 5.246e-07 | 5.2027e-07 | 5.1594e-07 | 5.1161e-07 | 5.0728e-07 | 5.0295e-07 | 4.9863e-07 | 4.943e-07 | 32583.1543 | 7511.9865 | 0.25554 | 0.058914 | 12.0758 | 15.6529 | 588172.0251 | 12.6022
| HTN013-163073657 | 44 | HTN013 | HTN | South | 799954.8098 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.00026888 | 0.00027096 | 0.00027304 | 0.00027512 | 0.0002772 | 0.00027538 | 0.00027356 | 0.00027174 | 0.00026992 | 0.0002681 | 0.00026628 | 0.00026446 | 0.00026264 | 0.00026082 | 0.000259 | 0.00025718 | 0.00025536 | 0.00025354 | 0.00025172 | 0.0002499 | 7.8146e-06 | 7.8751e-06 | 7.8948e-06 | 7.9027e-06 | 7.8558e-06 | 7.7314e-06 | 7.6646e-06 | 7.6246e-06 | 7.4913e-06 | 7.4408e-06 | 7.3903e-06 | 7.3398e-06 | 7.2893e-06 | 7.2388e-06 | 7.1882e-06 | 7.1377e-06 | 7.0872e-06 | 7.0367e-06 | 6.9862e-06 | 6.9357e-06 | 32583.1543 | 7511.9865 | 3.5374 | 0.81555 | 220.3361 | 285.6044 | 834824.8098 | 229.9406
| HTN013-163073840 | 121 | HTN013 | HTN | South | 2199875.7269 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.098441 | 0.09897 | 0.099499 | 0.10003 | 0.10056 | 0.099908 | 0.099258 | 0.098609 | 0.09796 | 0.097311 | 0.096661 | 0.096012 | 0.095363 | 0.094714 | 0.094065 | 0.093415 | 0.092766 | 0.092117 | 0.091468 | 0.090818 | 0.0028611 | 0.0028764 | 0.0028769 | 0.0028733 | 0.0028498 | 0.002805 | 0.002781 | 0.0027668 | 0.0027188 | 0.0027007 | 0.0026827 | 0.0026647 | 0.0026467 | 0.0026287 | 0.0026107 | 0.0025926 | 0.0025746 | 0.0025566 | 0.0025386 | 0.0025206 | 32583.1543 | 7511.9865 | 1285.9881 | 296.4822 | 67037.8086 | 86895.8261 | 2295768.2269 | 69959.9841
| HTN013-163074070 | 7 | HTN013 | HTN | South | 127265.5379 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0013908 | 0.001399 | 0.0014073 | 0.0014156 | 0.0014239 | 0.0014183 | 0.0014127 | 0.0014071 | 0.0014016 | 0.001396 | 0.0013904 | 0.0013849 | 0.0013793 | 0.0013737 | 0.0013681 | 0.0013626 | 0.001357 | 0.0013514 | 0.0013459 | 0.0013403 | 4.0421e-05 | 4.0661e-05 | 4.0691e-05 | 4.0662e-05 | 4.0352e-05 | 3.9819e-05 | 3.9582e-05 | 3.9482e-05 | 3.8899e-05 | 3.8744e-05 | 3.859e-05 | 3.8435e-05 | 3.8281e-05 | 3.8126e-05 | 3.7971e-05 | 3.7817e-05 | 3.7662e-05 | 3.7507e-05 | 3.7353e-05 | 3.7198e-05 | 32583.1543 | 7511.9865 | 18.4402 | 4.2514 | 511.7184 | 663.3003 | 132813.0379 | 534.0242
| HTN013-171202197 | 80 | HTN013 | HTN | South | 1454463.2905 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.13694 | 0.13761 | 0.13828 | 0.13896 | 0.13963 | 0.13906 | 0.13849 | 0.13792 | 0.13735 | 0.13678 | 0.13621 | 0.13564 | 0.13507 | 0.1345 | 0.13393 | 0.13336 | 0.13279 | 0.13222 | 0.13165 | 0.13108 | 0.0039799 | 0.0039995 | 0.0039984 | 0.0039916 | 0.0039572 | 0.0039043 | 0.0038803 | 0.0038699 | 0.003812 | 0.0037962 | 0.0037804 | 0.0037646 | 0.0037487 | 0.0037329 | 0.0037171 | 0.0037012 | 0.0036854 | 0.0036696 | 0.0036537 | 0.0036379 | 32583.1543 | 7511.9865 | 1808.0272 | 416.8374 | 98859.9699 | 128144.385 | 1517863.2905 | 103169.2723
| HTN013-182145838 | 249 | HTN013 | HTN | South | 4527016.9917 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 2.2895 | 2.3036 | 2.3177 | 2.3319 | 2.346 | 2.3356 | 2.3253 | 2.315 | 2.3046 | 2.2943 | 2.2839 | 2.2736 | 2.2633 | 2.2529 | 2.2426 | 2.2322 | 2.2219 | 2.2116 | 2.2012 | 2.1909 | 0.066541 | 0.066951 | 0.067015 | 0.066982 | 0.066485 | 0.065574 | 0.06515 | 0.064954 | 0.063962 | 0.063675 | 0.063388 | 0.063101 | 0.062814 | 0.062527 | 0.06224 | 0.061953 | 0.061666 | 0.061379 | 0.061092 | 0.060805 | 32583.1543 | 7511.9865 | 30301.7514 | 6986.0132 | 783483.0106 | 1015567.2577 | 4724349.4917 | 817635.0055
| HTN013-190418811 | 224 | HTN013 | HTN | South | 4072497.2134 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 12.6042 | 12.7203 | 12.8364 | 12.9525 | 13.0685 | 12.9911 | 12.9136 | 12.8361 | 12.7586 | 12.6812 | 12.6037 | 12.5262 | 12.4488 | 12.3713 | 12.2938 | 12.2163 | 12.1389 | 12.0614 | 11.9839 | 11.9064 | 0.36632 | 0.3697 | 0.37115 | 0.37206 | 0.37036 | 0.36473 | 0.36181 | 0.36016 | 0.3541 | 0.35195 | 0.3498 | 0.34765 | 0.3455 | 0.34335 | 0.3412 | 0.33905 | 0.3369 | 0.33475 | 0.3326 | 0.33045 | 32583.1543 | 7511.9865 | 167157.4302 | 38537.839 | 485179.4361 | 628899.852 | 4250017.2134 | 506328.3894
| HTN013-192570901 | 73 | HTN013 | HTN | South | 1327197.7526 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.11169 | 0.11258 | 0.11348 | 0.11437 | 0.11527 | 0.11461 | 0.11395 | 0.11329 | 0.11263 | 0.11197 | 0.11131 | 0.11065 | 0.10999 | 0.10934 | 0.10868 | 0.10802 | 0.10736 | 0.1067 | 0.10604 | 0.10538 | 0.003246 | 0.0032721 | 0.0032812 | 0.0032854 | 0.0032667 | 0.0032178 | 0.0031927 | 0.0031788 | 0.003126 | 0.0031077 | 0.0030894 | 0.0030711 | 0.0030528 | 0.0030345 | 0.0030162 | 0.0029979 | 0.0029796 | 0.0029613 | 0.002943 | 0.0029247 | 32583.1543 | 7511.9865 | 1477.125 | 340.5485 | 53429.4049 | 69256.3252 | 1385050.2526 | 55758.3906
| HTN013-201063848 | 186 | HTN013 | HTN | South | 3381627.1505 | 0.001044 | 0.001044 | 0.0010386 | 0.0010318 | 0.001018 | 0.0010085 | 0.0010064 | 0.0010078 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 0.0009969 | 4.4674 | 4.4901 | 4.5127 | 4.5354 | 4.5581 | 4.5311 | 4.5041 | 4.4771 | 4.4502 | 4.4232 | 4.3962 | 4.3692 | 4.3422 | 4.3152 | 4.2882 | 4.2612 | 4.2342 | 4.2072 | 4.1802 | 4.1533 | 0.12984 | 0.1305 | 0.13048 | 0.13028 | 0.12918 | 0.12721 | 0.1262 | 0.12562 | 0.12351 | 0.12276 | 0.12201 | 0.12126 | 0.12051 | 0.11976 | 0.11901 | 0.11827 | 0.11752 | 0.11677 | 0.11602 | 0.11527 | 32583.1543 | 7511.9865 | 58464.0081 | 13478.7699 | 224492.147 | 290991.4715 | 3529032.1505 | 234277.7512
| HTN032-159373067 | 67 | HTN032 | HTN | South | 1218113.0058 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.09582 | 0.096825 | 0.09783 | 0.098836 | 0.099841 | 0.098977 | 0.098113 | 0.097249 | 0.096385 | 0.095521 | 0.094657 | 0.093793 | 0.092929 | 0.092065 | 0.091201 | 0.090337 | 0.089473 | 0.088609 | 0.087745 | 0.086881 | 0.0028634 | 0.0028891 | 0.0029472 | 0.0029912 | 0.003031 | 0.003035 | 0.0030612 | 0.0030753 | 0.0030397 | 0.0030125 | 0.0029852 | 0.002958 | 0.0029307 | 0.0029035 | 0.0028762 | 0.002849 | 0.0028217 | 0.0027945 | 0.0027673 | 0.00274 | 32583.1543 | 7511.9865 | 1384.9401 | 319.2954 | 49129.5581 | 63682.7728 | 1271210.5058 | 51271.1137
| HTN032-159377664 | 62 | HTN032 | HTN | South | 1127209.0502 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.096848 | 0.097602 | 0.098357 | 0.099112 | 0.099866 | 0.09926 | 0.098653 | 0.098047 | 0.09744 | 0.096834 | 0.096227 | 0.09562 | 0.095014 | 0.094407 | 0.093801 | 0.093194 | 0.092588 | 0.091981 | 0.091374 | 0.090768 | 0.0028942 | 0.0029123 | 0.0029631 | 0.0029996 | 0.0030318 | 0.0030436 | 0.0030781 | 0.0031005 | 0.003073 | 0.0030539 | 0.0030347 | 0.0030156 | 0.0029965 | 0.0029774 | 0.0029582 | 0.0029391 | 0.00292 | 0.0029008 | 0.0028817 | 0.0028626 | 32583.1543 | 7511.9865 | 1406.8351 | 324.3432 | 62796.6852 | 81398.3922 | 1176344.0502 | 65533.9903
| HTN032-159377774 | 147 | HTN032 | HTN | South | 2672576.2963 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.11256 | 0.11308 | 0.1136 | 0.11412 | 0.11464 | 0.11432 | 0.114 | 0.11369 | 0.11337 | 0.11305 | 0.11274 | 0.11242 | 0.1121 | 0.11179 | 0.11147 | 0.11116 | 0.11084 | 0.11052 | 0.11021 | 0.10989 | 0.0033636 | 0.0033741 | 0.0034222 | 0.0034537 | 0.0034802 | 0.0035055 | 0.0035571 | 0.0035951 | 0.0035754 | 0.0035654 | 0.0035555 | 0.0035455 | 0.0035355 | 0.0035255 | 0.0035155 | 0.0035055 | 0.0034956 | 0.0034856 | 0.0034756 | 0.0034656 | 32583.1543 | 7511.9865 | 1646.4523 | 379.5866 | 80653.0175 | 104544.148 | 2789073.7963 | 84168.6795
| HTN032-159443241 | 55 | HTN032 | HTN | South | 999943.5122 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0049219 | 0.0049283 | 0.0049348 | 0.0049413 | 0.0049477 | 0.0049395 | 0.0049312 | 0.004923 | 0.0049148 | 0.0049065 | 0.0048983 | 0.00489 | 0.0048818 | 0.0048735 | 0.0048653 | 0.004857 | 0.0048488 | 0.0048405 | 0.0048323 | 0.0048241 | 0.00014708 | 0.00014706 | 0.00014866 | 0.00014955 | 0.00015021 | 0.00015146 | 0.00015386 | 0.00015568 | 0.000155 | 0.00015474 | 0.00015448 | 0.00015422 | 0.00015396 | 0.0001537 | 0.00015344 | 0.00015318 | 0.00015292 | 0.00015266 | 0.0001524 | 0.00015214 | 32583.1543 | 7511.9865 | 71.6129 | 16.5102 | 3937.5012 | 5103.8723 | 1043531.0122 | 4109.1367
| HTN032-159443483 | 85 | HTN032 | HTN | South | 1545367.2462 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.28707 | 0.28847 | 0.28988 | 0.29128 | 0.29269 | 0.29152 | 0.29036 | 0.28919 | 0.28803 | 0.28686 | 0.2857 | 0.28453 | 0.28337 | 0.2822 | 0.28103 | 0.27987 | 0.2787 | 0.27754 | 0.27637 | 0.27521 | 0.0085786 | 0.0086077 | 0.0087328 | 0.0088156 | 0.0088857 | 0.0089391 | 0.0090596 | 0.009145 | 0.0090836 | 0.0090469 | 0.0090101 | 0.0089734 | 0.0089366 | 0.0088999 | 0.0088631 | 0.0088263 | 0.0087896 | 0.0087528 | 0.0087161 | 0.0086793 | 32583.1543 | 7511.9865 | 4176.3131 | 962.8413 | 187898.6054 | 243558.1484 | 1612729.7462 | 196089.0985
| HTN032-159944977 | 78 | HTN032 | HTN | South | 1418101.7083 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.15947 | 0.1608 | 0.16213 | 0.16346 | 0.16479 | 0.16408 | 0.16336 | 0.16265 | 0.16194 | 0.16123 | 0.16052 | 0.1598 | 0.15909 | 0.15838 | 0.15767 | 0.15695 | 0.15624 | 0.15553 | 0.15482 | 0.1541 | 0.0047654 | 0.004798 | 0.0048842 | 0.004947 | 0.0050028 | 0.0050312 | 0.0050972 | 0.0051435 | 0.0051072 | 0.0050847 | 0.0050622 | 0.0050398 | 0.0050173 | 0.0049948 | 0.0049724 | 0.0049499 | 0.0049275 | 0.004905 | 0.0048825 | 0.0048601 | 32583.1543 | 7511.9865 | 2342.1455 | 539.9773 | 156552.4373 | 202926.582 | 1479916.7083 | 163376.5521
| HTN032-160369507 | 56 | HTN032 | HTN | South | 1018124.3034 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.035622 | 0.035948 | 0.036273 | 0.036598 | 0.036924 | 0.036589 | 0.036255 | 0.03592 | 0.035586 | 0.035252 | 0.034917 | 0.034583 | 0.034248 | 0.033914 | 0.033579 | 0.033245 | 0.032911 | 0.032576 | 0.032242 | 0.031907 | 0.0010645 | 0.0010726 | 0.0010928 | 0.0011076 | 0.001121 | 0.001122 | 0.0011312 | 0.0011359 | 0.0011223 | 0.0011117 | 0.0011012 | 0.0010906 | 0.0010801 | 0.0010696 | 0.001059 | 0.0010485 | 0.0010379 | 0.0010274 | 0.0010168 | 0.0010063 | 32583.1543 | 7511.9865 | 511.5053 | 117.9266 | 39667.9118 | 51418.3867 | 1062504.3034 | 41397.0346
| HTN032-160369615 | 44 | HTN032 | HTN | South | 799954.8098 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.047715 | 0.048161 | 0.048606 | 0.049052 | 0.049498 | 0.04919 | 0.048882 | 0.048575 | 0.048267 | 0.047959 | 0.047652 | 0.047344 | 0.047036 | 0.046729 | 0.046421 | 0.046113 | 0.045806 | 0.045498 | 0.04519 | 0.044883 | 0.0014259 | 0.0014371 | 0.0014643 | 0.0014845 | 0.0015027 | 0.0015083 | 0.0015252 | 0.0015361 | 0.0015222 | 0.0015125 | 0.0015028 | 0.0014931 | 0.0014834 | 0.0014737 | 0.001464 | 0.0014543 | 0.0014446 | 0.0014349 | 0.0014252 | 0.0014155 | 32583.1543 | 7511.9865 | 696.0944 | 160.4833 | 36750.4206 | 47636.6728 | 834824.8098 | 38352.37
| HTN032-160369738 | 55 | HTN032 | HTN | South | 999943.5122 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.089588 | 0.090305 | 0.091023 | 0.091741 | 0.092458 | 0.091765 | 0.091071 | 0.090377 | 0.089683 | 0.08899 | 0.088296 | 0.087602 | 0.086908 | 0.086215 | 0.085521 | 0.084827 | 0.084133 | 0.08344 | 0.082746 | 0.082052 | 0.0026772 | 0.0026946 | 0.0027421 | 0.0027765 | 0.0028069 | 0.0028138 | 0.0028415 | 0.002858 | 0.0028284 | 0.0028065 | 0.0027846 | 0.0027627 | 0.0027409 | 0.002719 | 0.0026971 | 0.0026752 | 0.0026533 | 0.0026315 | 0.0026096 | 0.0025877 | 32583.1543 | 7511.9865 | 1292.442 | 297.9701 | 58162.8461 | 75391.9119 | 1043531.0122 | 60698.1624
| HTN032-162635166 | 14 | HTN032 | HTN | South | 254531.0758 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 9.1771e-05 | 9.2829e-05 | 9.3886e-05 | 9.4943e-05 | 9.6e-05 | 9.555e-05 | 9.51e-05 | 9.465e-05 | 9.42e-05 | 9.375e-05 | 9.33e-05 | 9.285e-05 | 9.24e-05 | 9.195e-05 | 9.15e-05 | 9.105e-05 | 9.06e-05 | 9.015e-05 | 8.97e-05 | 8.925e-05 | 2.7425e-06 | 2.7699e-06 | 2.8284e-06 | 2.8734e-06 | 2.9144e-06 | 2.9299e-06 | 2.9672e-06 | 2.9931e-06 | 2.9708e-06 | 2.9566e-06 | 2.9424e-06 | 2.9282e-06 | 2.9141e-06 | 2.8999e-06 | 2.8857e-06 | 2.8715e-06 | 2.8573e-06 | 2.8431e-06 | 2.8289e-06 | 2.8147e-06 | 32583.1543 | 7511.9865 | 1.3592 | 0.31337 | 68.4861 | 88.7731 | 265626.0758 | 71.4714
| HTN032-162645765 | 35 | HTN032 | HTN | South | 636327.6896 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.037144 | 0.037408 | 0.037671 | 0.037934 | 0.038198 | 0.037987 | 0.037777 | 0.037566 | 0.037356 | 0.037146 | 0.036935 | 0.036725 | 0.036514 | 0.036304 | 0.036094 | 0.035883 | 0.035673 | 0.035462 | 0.035252 | 0.035042 | 0.00111 | 0.0011162 | 0.0011349 | 0.0011481 | 0.0011596 | 0.0011648 | 0.0011787 | 0.0011879 | 0.0011781 | 0.0011715 | 0.0011648 | 0.0011582 | 0.0011516 | 0.0011449 | 0.0011383 | 0.0011317 | 0.001125 | 0.0011184 | 0.0011118 | 0.0011051 | 32583.1543 | 7511.9865 | 539.9414 | 124.4825 | 34012.7453 | 44088.0403 | 664065.1896 | 35495.3596
| HTN032-162671033 | 16 | HTN032 | HTN | South | 290892.6581 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.042211 | 0.042564 | 0.042918 | 0.043271 | 0.043625 | 0.043233 | 0.04284 | 0.042447 | 0.042055 | 0.041662 | 0.04127 | 0.040877 | 0.040485 | 0.040092 | 0.0397 | 0.039307 | 0.038914 | 0.038522 | 0.038129 | 0.037737 | 0.0012614 | 0.0012701 | 0.0012929 | 0.0013096 | 0.0013244 | 0.0013257 | 0.0013367 | 0.0013423 | 0.0013263 | 0.0013139 | 0.0013015 | 0.0012892 | 0.0012768 | 0.0012644 | 0.001252 | 0.0012396 | 0.0012273 | 0.0012149 | 0.0012025 | 0.0011901 | 32583.1543 | 7511.9865 | 604.8161 | 139.4393 | 9678.77 | 12545.8265 | 303572.6581 | 10100.6672
| HTN032-162671207 | 7 | HTN032 | HTN | South | 127265.5379 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0012124 | 0.0012234 | 0.0012344 | 0.0012454 | 0.0012563 | 0.0012504 | 0.0012445 | 0.0012386 | 0.0012327 | 0.0012268 | 0.0012208 | 0.0012149 | 0.001209 | 0.0012031 | 0.0011972 | 0.0011913 | 0.0011853 | 0.0011794 | 0.0011735 | 0.0011676 | 3.6231e-05 | 3.6505e-05 | 3.7186e-05 | 3.769e-05 | 3.8141e-05 | 3.8342e-05 | 3.883e-05 | 3.9167e-05 | 3.8875e-05 | 3.8689e-05 | 3.8502e-05 | 3.8316e-05 | 3.8129e-05 | 3.7942e-05 | 3.7756e-05 | 3.7569e-05 | 3.7383e-05 | 3.7196e-05 | 3.701e-05 | 3.6823e-05 | 32583.1543 | 7511.9865 | 17.8124 | 4.1066 | 747.9571 | 969.5178 | 132813.0379 | 780.5605
| HTN032-162798482 | 70 | HTN032 | HTN | South | 1272655.3792 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.11531 | 0.116 | 0.11669 | 0.11739 | 0.11808 | 0.11767 | 0.11726 | 0.11686 | 0.11645 | 0.11604 | 0.11563 | 0.11523 | 0.11482 | 0.11441 | 0.114 | 0.1136 | 0.11319 | 0.11278 | 0.11238 | 0.11197 | 0.0034459 | 0.0034614 | 0.0035155 | 0.0035526 | 0.0035847 | 0.0036082 | 0.0036587 | 0.0036953 | 0.0036725 | 0.0036596 | 0.0036468 | 0.0036339 | 0.0036211 | 0.0036082 | 0.0035954 | 0.0035826 | 0.0035697 | 0.0035569 | 0.003544 | 0.0035312 | 32583.1543 | 7511.9865 | 1688.3507 | 389.2462 | 66461.6278 | 86148.9683 | 1328130.3792 | 69358.6876
| HTN032-187419014 | 819 | HTN032 | HTN | South | 14890067.9367 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 24.1124 | 24.2972 | 24.4819 | 24.6667 | 24.8515 | 24.7216 | 24.5918 | 24.4619 | 24.3321 | 24.2022 | 24.0724 | 23.9425 | 23.8127 | 23.6828 | 23.553 | 23.4231 | 23.2933 | 23.1634 | 23.0335 | 22.9037 | 0.72057 | 0.725 | 0.73753 | 0.74653 | 0.75446 | 0.75805 | 0.76729 | 0.77355 | 0.76737 | 0.76327 | 0.75918 | 0.75508 | 0.75099 | 0.74689 | 0.7428 | 0.7387 | 0.73461 | 0.73051 | 0.72642 | 0.72232 | 32583.1543 | 7511.9865 | 351688.3451 | 81081.1031 | 6032925.2991 | 7820005.4366 | 15539125.4367 | 6295900.2855
| HTN032-190418526 | 556 | HTN032 | HTN | South | 10108519.8691 | 0.0010734 | 0.0010718 | 0.0010821 | 0.0010871 | 0.0010905 | 0.0011014 | 0.0011207 | 0.0011359 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 0.0011328 | 113.7442 | 114.3876 | 115.031 | 115.6744 | 116.3178 | 115.5806 | 114.8433 | 114.1061 | 113.3689 | 112.6317 | 111.8944 | 111.1572 | 110.42 | 109.6827 | 108.9455 | 108.2083 | 107.4711 | 106.7338 | 105.9966 | 105.2594 | 3.3991 | 3.4132 | 3.4654 | 3.5008 | 3.5313 | 3.5441 | 3.5833 | 3.6083 | 3.5754 | 3.5521 | 3.5289 | 3.5056 | 3.4824 | 3.4591 | 3.4359 | 3.4126 | 3.3894 | 3.3661 | 3.3429 | 3.3196 | 32583.1543 | 7511.9865 | 1638481.6466 | 377748.9391 | 5532466.961 | 7171300.7484 | 10549149.8691 | 5773626.9872
| HTN033-107035043 | 79 | HTN033 | HTN | South | 1436282.4994 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.066178 | 0.066589 | 0.067 | 0.067411 | 0.067822 | 0.067674 | 0.067526 | 0.067378 | 0.06723 | 0.067082 | 0.066934 | 0.066787 | 0.066639 | 0.066491 | 0.066343 | 0.066195 | 0.066047 | 0.0659 | 0.065752 | 0.065604 | 0.0020639 | 0.0020696 | 0.0020677 | 0.0020598 | 0.0020463 | 0.0020402 | 0.0020555 | 0.0020657 | 0.0020593 | 0.0020547 | 0.0020502 | 0.0020457 | 0.0020412 | 0.0020366 | 0.0020321 | 0.0020276 | 0.002023 | 0.0020185 | 0.002014 | 0.0020095 | 32583.1543 | 7511.9865 | 964.4792 | 222.3589 | 51386.52 | 66608.2947 | 1498889.9994 | 53626.4565
| HTN033-142434533 | 74 | HTN033 | HTN | South | 1345378.5437 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.097649 | 0.098338 | 0.099026 | 0.099714 | 0.1004 | 0.1001 | 0.0998 | 0.099498 | 0.099197 | 0.098895 | 0.098594 | 0.098292 | 0.097991 | 0.097689 | 0.097388 | 0.097086 | 0.096785 | 0.096483 | 0.096182 | 0.09588 | 0.0030454 | 0.0030563 | 0.0030561 | 0.0030469 | 0.0030294 | 0.0030178 | 0.0030379 | 0.0030505 | 0.0030384 | 0.0030292 | 0.0030199 | 0.0030107 | 0.0030015 | 0.0029922 | 0.002983 | 0.0029738 | 0.0029645 | 0.0029553 | 0.0029461 | 0.0029368 | 32583.1543 | 7511.9865 | 1421.0534 | 327.6213 | 66029.6238 | 85588.9956 | 1404023.5437 | 68907.8526
| HTN033-159363700 | 66 | HTN033 | HTN | South | 1199932.2147 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.035201 | 0.035481 | 0.035761 | 0.03604 | 0.03632 | 0.036067 | 0.035813 | 0.035559 | 0.035306 | 0.035052 | 0.034798 | 0.034545 | 0.034291 | 0.034037 | 0.033784 | 0.03353 | 0.033277 | 0.033023 | 0.032769 | 0.032516 | 0.0010978 | 0.0011027 | 0.0011036 | 0.0011012 | 0.0010959 | 0.0010873 | 0.0010902 | 0.0010902 | 0.0010814 | 0.0010737 | 0.0010659 | 0.0010581 | 0.0010503 | 0.0010426 | 0.0010348 | 0.001027 | 0.0010193 | 0.0010115 | 0.0010037 | 0.00099596 | 32583.1543 | 7511.9865 | 503.289 | 116.0324 | 14752.6205 | 19122.6589 | 1252237.2147 | 15395.6867
| HTN033-159373503 | 41 | HTN033 | HTN | South | 745412.4364 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.074138 | 0.074655 | 0.075171 | 0.075688 | 0.076204 | 0.075846 | 0.075487 | 0.075129 | 0.07477 | 0.074412 | 0.074053 | 0.073695 | 0.073336 | 0.072978 | 0.072619 | 0.072261 | 0.071902 | 0.071544 | 0.071185 | 0.070827 | 0.0023122 | 0.0023203 | 0.0023199 | 0.0023127 | 0.0022992 | 0.0022865 | 0.0022979 | 0.0023034 | 0.0022902 | 0.0022792 | 0.0022683 | 0.0022573 | 0.0022463 | 0.0022353 | 0.0022243 | 0.0022134 | 0.0022024 | 0.0021914 | 0.0021804 | 0.0021694 | 32583.1543 | 7511.9865 | 1069.2221 | 246.5072 | 42013.6055 | 54458.9245 | 777904.9364 | 43844.9769
| HTN033-159373599 | 64 | HTN033 | HTN | South | 1163570.6324 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.20431 | 0.2055 | 0.2067 | 0.20789 | 0.20908 | 0.20802 | 0.20695 | 0.20588 | 0.20481 | 0.20374 | 0.20267 | 0.20161 | 0.20054 | 0.19947 | 0.1984 | 0.19733 | 0.19626 | 0.1952 | 0.19413 | 0.19306 | 0.0063718 | 0.006387 | 0.0063789 | 0.0063523 | 0.0063085 | 0.0062711 | 0.0062996 | 0.0063121 | 0.0062734 | 0.0062407 | 0.006208 | 0.0061752 | 0.0061425 | 0.0061098 | 0.0060771 | 0.0060443 | 0.0060116 | 0.0059789 | 0.0059462 | 0.0059134 | 32583.1543 | 7511.9865 | 2929.665 | 675.4289 | 126450.7229 | 163908.1029 | 1214290.6324 | 131962.7052
| HTN033-159944283 | 83 | HTN033 | HTN | South | 1509005.6639 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.11995 | 0.12084 | 0.12173 | 0.12262 | 0.12351 | 0.12301 | 0.12251 | 0.12201 | 0.12152 | 0.12102 | 0.12052 | 0.12003 | 0.11953 | 0.11903 | 0.11853 | 0.11804 | 0.11754 | 0.11704 | 0.11655 | 0.11605 | 0.0037408 | 0.0037556 | 0.0037567 | 0.0037467 | 0.0037264 | 0.0037084 | 0.0037293 | 0.0037409 | 0.0037221 | 0.0037069 | 0.0036917 | 0.0036764 | 0.0036612 | 0.003646 | 0.0036307 | 0.0036155 | 0.0036003 | 0.003585 | 0.0035698 | 0.0035546 | 32583.1543 | 7511.9865 | 1738.4858 | 400.8047 | 77279.5793 | 100171.426 | 1574783.1639 | 80648.1933
| HTN033-159944367 | 45 | HTN033 | HTN | South | 818135.6009 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.044374 | 0.044784 | 0.045193 | 0.045603 | 0.046012 | 0.045648 | 0.045284 | 0.044919 | 0.044555 | 0.04419 | 0.043826 | 0.043462 | 0.043097 | 0.042733 | 0.042368 | 0.042004 | 0.04164 | 0.041275 | 0.040911 | 0.040546 | 0.0013839 | 0.0013919 | 0.0013947 | 0.0013934 | 0.0013883 | 0.0013762 | 0.0013784 | 0.0013772 | 0.0013647 | 0.0013536 | 0.0013424 | 0.0013312 | 0.0013201 | 0.0013089 | 0.0012978 | 0.0012866 | 0.0012754 | 0.0012643 | 0.0012531 | 0.0012419 | 32583.1543 | 7511.9865 | 633.9429 | 146.1544 | 25973.3156 | 33667.1613 | 853798.1009 | 27105.4914
| HTN033-159944491 | 73 | HTN033 | HTN | South | 1327197.7526 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.076408 | 0.076942 | 0.077476 | 0.07801 | 0.078545 | 0.078133 | 0.077721 | 0.077309 | 0.076896 | 0.076484 | 0.076072 | 0.07566 | 0.075248 | 0.074836 | 0.074424 | 0.074012 | 0.0736 | 0.073188 | 0.072776 | 0.072364 | 0.002383 | 0.0023914 | 0.002391 | 0.0023837 | 0.0023699 | 0.0023555 | 0.0023658 | 0.0023702 | 0.0023554 | 0.0023427 | 0.0023301 | 0.0023175 | 0.0023049 | 0.0022922 | 0.0022796 | 0.002267 | 0.0022544 | 0.0022418 | 0.0022291 | 0.0022165 | 32583.1543 | 7511.9865 | 1098.9594 | 253.3631 | 45650.5004 | 59173.1446 | 1385050.2526 | 47640.4039
| HTN033-159944618 | 41 | HTN033 | HTN | South | 745412.4364 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.045899 | 0.046233 | 0.046567 | 0.046901 | 0.047235 | 0.046933 | 0.04663 | 0.046327 | 0.046024 | 0.045721 | 0.045419 | 0.045116 | 0.044813 | 0.04451 | 0.044208 | 0.043905 | 0.043602 | 0.043299 | 0.042996 | 0.042694 | 0.0014315 | 0.0014369 | 0.0014371 | 0.0014331 | 0.0014252 | 0.0014149 | 0.0014194 | 0.0014203 | 0.0014097 | 0.0014005 | 0.0013912 | 0.0013819 | 0.0013726 | 0.0013634 | 0.0013541 | 0.0013448 | 0.0013355 | 0.0013263 | 0.001317 | 0.0013077 | 32583.1543 | 7511.9865 | 656.7872 | 151.4211 | 28843.6216 | 37387.7126 | 777904.9364 | 30100.9139
| HTN033-162626258 | 8 | HTN033 | HTN | South | 145446.3291 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0061631 | 0.0062155 | 0.0062678 | 0.0063202 | 0.0063726 | 0.0063289 | 0.0062852 | 0.0062415 | 0.0061978 | 0.0061542 | 0.0061105 | 0.0060668 | 0.0060231 | 0.0059794 | 0.0059358 | 0.0058921 | 0.0058484 | 0.0058047 | 0.0057611 | 0.0057174 | 0.00019221 | 0.00019318 | 0.00019343 | 0.00019312 | 0.00019227 | 0.0001908 | 0.00019132 | 0.00019136 | 0.00018984 | 0.0001885 | 0.00018717 | 0.00018583 | 0.00018449 | 0.00018315 | 0.00018181 | 0.00018048 | 0.00017914 | 0.0001778 | 0.00017646 | 0.00017512 | 32583.1543 | 7511.9865 | 88.3326 | 20.3649 | 4289.2739 | 5559.8475 | 151786.3291 | 4476.2431
| HTN033-162670429 | 8 | HTN033 | HTN | South | 145446.3291 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 1.0899e-05 | 1.0975e-05 | 1.105e-05 | 1.1125e-05 | 1.12e-05 | 1.116e-05 | 1.112e-05 | 1.108e-05 | 1.104e-05 | 1.1e-05 | 1.096e-05 | 1.092e-05 | 1.088e-05 | 1.084e-05 | 1.08e-05 | 1.076e-05 | 1.072e-05 | 1.068e-05 | 1.064e-05 | 1.06e-05 | 3.3992e-07 | 3.4109e-07 | 3.4101e-07 | 3.3993e-07 | 3.3793e-07 | 3.3644e-07 | 3.385e-07 | 3.397e-07 | 3.3816e-07 | 3.3693e-07 | 3.3571e-07 | 3.3448e-07 | 3.3326e-07 | 3.3203e-07 | 3.3081e-07 | 3.2958e-07 | 3.2836e-07 | 3.2713e-07 | 3.2591e-07 | 3.2468e-07 | 32583.1543 | 7511.9865 | 0.15807 | 0.036444 | 23.0273 | 29.8485 | 151786.3291 | 24.0311
| HTN033-162670652 | 9 | HTN033 | HTN | South | 163627.1202 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.00012382 | 0.00012386 | 0.00012391 | 0.00012395 | 0.000124 | 0.00012394 | 0.00012388 | 0.00012382 | 0.00012376 | 0.0001237 | 0.00012364 | 0.00012358 | 0.00012352 | 0.00012346 | 0.0001234 | 0.00012334 | 0.00012328 | 0.00012322 | 0.00012316 | 0.0001231 | 3.8615e-06 | 3.8497e-06 | 3.824e-06 | 3.7875e-06 | 3.7413e-06 | 3.7365e-06 | 3.7709e-06 | 3.7962e-06 | 3.7908e-06 | 3.789e-06 | 3.7871e-06 | 3.7853e-06 | 3.7834e-06 | 3.7816e-06 | 3.7798e-06 | 3.7779e-06 | 3.7761e-06 | 3.7743e-06 | 3.7724e-06 | 3.7706e-06 | 32583.1543 | 7511.9865 | 1.7854 | 0.41162 | 73.1463 | 94.8138 | 170759.6202 | 76.3348
| HTN033-182145786 | 690 | HTN033 | HTN | South | 12544745.8807 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 5.0374 | 5.046 | 5.0547 | 5.0633 | 5.072 | 5.0609 | 5.0498 | 5.0387 | 5.0276 | 5.0166 | 5.0055 | 4.9944 | 4.9833 | 4.9722 | 4.9611 | 4.95 | 4.939 | 4.9279 | 4.9168 | 4.9057 | 0.1571 | 0.15683 | 0.15599 | 0.15471 | 0.15303 | 0.15257 | 0.15372 | 0.15448 | 0.154 | 0.15366 | 0.15332 | 0.15298 | 0.15264 | 0.1523 | 0.15196 | 0.15162 | 0.15128 | 0.15094 | 0.1506 | 0.15026 | 32583.1543 | 7511.9865 | 72337.7518 | 16677.336 | 2080394.7191 | 2696651.6585 | 13091570.8807 | 2171079.0465
| HTN033-190418479 | 421 | HTN033 | HTN | South | 7654113.0663 | 0.0011202 | 0.0011164 | 0.0011085 | 0.0010976 | 0.0010838 | 0.0010829 | 0.0010934 | 0.0011013 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 0.0011002 | 31.612 | 31.9027 | 32.1935 | 32.4842 | 32.7749 | 32.4605 | 32.1461 | 31.8317 | 31.5173 | 31.2029 | 30.8885 | 30.5741 | 30.2597 | 29.9453 | 29.6309 | 29.3165 | 29.0021 | 28.6877 | 28.3733 | 28.0589 | 0.9859 | 0.99154 | 0.99353 | 0.99258 | 0.98889 | 0.9786 | 0.97854 | 0.97593 | 0.96538 | 0.95575 | 0.94612 | 0.93649 | 0.92686 | 0.91723 | 0.9076 | 0.89797 | 0.88834 | 0.87871 | 0.86908 | 0.85945 | 32583.1543 | 7511.9865 | 447597.7548 | 103192.8416 | 1048322.0961 | 1358857.2847 | 7987755.5663 | 1094018.4167
| HTN034-100723274 | 215 | HTN034 | HTN | South | 3908870.0933 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.34382 | 0.3456 | 0.34738 | 0.34916 | 0.35094 | 0.34881 | 0.34667 | 0.34453 | 0.3424 | 0.34026 | 0.33813 | 0.33599 | 0.33386 | 0.33172 | 0.32959 | 0.32745 | 0.32532 | 0.32318 | 0.32105 | 0.31891 | 0.0087815 | 0.0088685 | 0.0089403 | 0.0089521 | 0.0088923 | 0.0087779 | 0.008758 | 0.0087559 | 0.0085987 | 0.0085451 | 0.0084915 | 0.0084379 | 0.0083842 | 0.0083306 | 0.008277 | 0.0082234 | 0.0081698 | 0.0081161 | 0.0080625 | 0.0080089 | 32583.1543 | 7511.9865 | 4040.3713 | 931.5002 | 232751.9059 | 301697.9457 | 4079257.5933 | 242897.5527
| HTN034-108340859 | 635 | HTN034 | HTN | South | 11544802.3685 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 11.7966 | 11.8667 | 11.9367 | 12.0068 | 12.0769 | 12.0051 | 11.9333 | 11.8616 | 11.7898 | 11.7181 | 11.6463 | 11.5745 | 11.5028 | 11.431 | 11.3593 | 11.2875 | 11.2157 | 11.144 | 11.0722 | 11.0004 | 0.3013 | 0.30452 | 0.30721 | 0.30784 | 0.30601 | 0.30212 | 0.30148 | 0.30145 | 0.29608 | 0.29428 | 0.29247 | 0.29067 | 0.28887 | 0.28707 | 0.28527 | 0.28346 | 0.28166 | 0.27986 | 0.27806 | 0.27626 | 32583.1543 | 7511.9865 | 139073.1987 | 32063.071 | 4468937.1771 | 5792730.937 | 12048039.8685 | 4663737.9802
| HTN034-142233453 | 75 | HTN034 | HTN | South | 1363559.3349 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.18237 | 0.18375 | 0.18512 | 0.18649 | 0.18786 | 0.1851 | 0.18233 | 0.17956 | 0.17679 | 0.17402 | 0.17126 | 0.16849 | 0.16572 | 0.16295 | 0.16019 | 0.15742 | 0.15465 | 0.15188 | 0.14911 | 0.14635 | 0.0046581 | 0.0047152 | 0.0047643 | 0.0047814 | 0.0047602 | 0.0046581 | 0.0046062 | 0.0045633 | 0.0044398 | 0.0043703 | 0.0043008 | 0.0042313 | 0.0041618 | 0.0040923 | 0.0040228 | 0.0039532 | 0.0038837 | 0.0038142 | 0.0037447 | 0.0036752 | 32583.1543 | 7511.9865 | 2062.9488 | 475.6091 | 179579.7443 | 232775.0646 | 1422996.8349 | 187407.6185
| HTN034-142233590 | 62 | HTN034 | HTN | South | 1127209.0502 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.090139 | 0.090945 | 0.091751 | 0.092558 | 0.093364 | 0.092341 | 0.091318 | 0.090295 | 0.089273 | 0.08825 | 0.087227 | 0.086205 | 0.085182 | 0.084159 | 0.083137 | 0.082114 | 0.081091 | 0.080068 | 0.079046 | 0.078023 | 0.0023023 | 0.0023338 | 0.0023614 | 0.0023731 | 0.0023657 | 0.0023238 | 0.002307 | 0.0022947 | 0.0022419 | 0.0022162 | 0.0021905 | 0.0021649 | 0.0021392 | 0.0021135 | 0.0020878 | 0.0020621 | 0.0020365 | 0.0020108 | 0.0019851 | 0.0019594 | 32583.1543 | 7511.9865 | 1045.2265 | 240.9751 | 54973.8384 | 71258.2526 | 1176344.0502 | 57370.1459
| HTN034-142234012 | 69 | HTN034 | HTN | South | 1254474.5881 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.14392 | 0.14462 | 0.14531 | 0.146 | 0.1467 | 0.14581 | 0.14492 | 0.14403 | 0.14314 | 0.14226 | 0.14137 | 0.14048 | 0.13959 | 0.1387 | 0.13782 | 0.13693 | 0.13604 | 0.13515 | 0.13426 | 0.13338 | 0.003676 | 0.0037111 | 0.0037398 | 0.0037434 | 0.0037171 | 0.0036694 | 0.0036612 | 0.0036604 | 0.0035948 | 0.0035725 | 0.0035502 | 0.0035279 | 0.0035056 | 0.0034833 | 0.003461 | 0.0034387 | 0.0034164 | 0.0033941 | 0.0033718 | 0.0033495 | 32583.1543 | 7511.9865 | 1689.5903 | 389.5319 | 67675.9593 | 87723.0105 | 1309157.0881 | 70625.9518
| HTN034-157456094 | 45 | HTN034 | HTN | South | 818135.6009 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.0067868 | 0.0068253 | 0.0068637 | 0.0069022 | 0.0069407 | 0.0069013 | 0.0068619 | 0.0068225 | 0.0067831 | 0.0067438 | 0.0067044 | 0.006665 | 0.0066256 | 0.0065863 | 0.0065469 | 0.0065075 | 0.0064681 | 0.0064288 | 0.0063894 | 0.00635 | 0.00017334 | 0.00017515 | 0.00017665 | 0.00017697 | 0.00017587 | 0.00017368 | 0.00017335 | 0.00017338 | 0.00017035 | 0.00016936 | 0.00016837 | 0.00016738 | 0.00016639 | 0.0001654 | 0.00016441 | 0.00016342 | 0.00016243 | 0.00016145 | 0.00016046 | 0.00015947 | 32583.1543 | 7511.9865 | 80.0515 | 18.4557 | 3178.6182 | 4120.1922 | 853798.1009 | 3317.1741
| HTN034-157599634 | 77 | HTN034 | HTN | South | 1399920.9171 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.06419 | 0.064491 | 0.064791 | 0.065092 | 0.065393 | 0.065047 | 0.064701 | 0.064355 | 0.064009 | 0.063663 | 0.063317 | 0.062971 | 0.062625 | 0.062279 | 0.061933 | 0.061587 | 0.061241 | 0.060895 | 0.06055 | 0.060204 | 0.0016395 | 0.0016549 | 0.0016675 | 0.0016689 | 0.0016569 | 0.0016369 | 0.0016346 | 0.0016355 | 0.0016075 | 0.0015988 | 0.0015901 | 0.0015814 | 0.0015727 | 0.001564 | 0.0015553 | 0.0015466 | 0.001538 | 0.0015293 | 0.0015206 | 0.0015119 | 32583.1543 | 7511.9865 | 756.1979 | 174.34 | 45874.0019 | 59462.852 | 1460943.4171 | 47873.6479
| HTN034-157998388 | 52 | HTN034 | HTN | South | 945401.1388 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.043926 | 0.044171 | 0.044417 | 0.044662 | 0.044907 | 0.044595 | 0.044284 | 0.043972 | 0.04366 | 0.043349 | 0.043037 | 0.042726 | 0.042414 | 0.042102 | 0.041791 | 0.041479 | 0.041168 | 0.040856 | 0.040545 | 0.040233 | 0.0011219 | 0.0011335 | 0.0011431 | 0.0011451 | 0.0011379 | 0.0011223 | 0.0011188 | 0.0011175 | 0.0010964 | 0.0010886 | 0.0010808 | 0.001073 | 0.0010651 | 0.0010573 | 0.0010495 | 0.0010417 | 0.0010338 | 0.001026 | 0.0010182 | 0.0010104 | 32583.1543 | 7511.9865 | 514.5932 | 118.6385 | 31066.3877 | 40268.9091 | 986611.1388 | 32420.5703
| HTN034-157998738 | 28 | HTN034 | HTN | South | 509062.1517 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.012093 | 0.012164 | 0.012235 | 0.012305 | 0.012376 | 0.012259 | 0.012142 | 0.012026 | 0.011909 | 0.011792 | 0.011675 | 0.011559 | 0.011442 | 0.011325 | 0.011208 | 0.011092 | 0.010975 | 0.010858 | 0.010741 | 0.010625 | 0.00030888 | 0.00031214 | 0.00031487 | 0.00031549 | 0.00031358 | 0.00030851 | 0.00030676 | 0.00030561 | 0.00029907 | 0.00029614 | 0.0002932 | 0.00029027 | 0.00028734 | 0.00028441 | 0.00028148 | 0.00027855 | 0.00027561 | 0.00027268 | 0.00026975 | 0.00026682 | 32583.1543 | 7511.9865 | 139.9563 | 32.2667 | 7857.7348 | 10185.3621 | 531252.1517 | 8200.2531
| HTN034-157999069 | 47 | HTN034 | HTN | South | 854497.1832 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.061654 | 0.061987 | 0.062321 | 0.062655 | 0.062989 | 0.062576 | 0.062163 | 0.06175 | 0.061337 | 0.060924 | 0.060511 | 0.060098 | 0.059685 | 0.059272 | 0.058859 | 0.058446 | 0.058033 | 0.05762 | 0.057208 | 0.056795 | 0.0015747 | 0.0015907 | 0.0016039 | 0.0016064 | 0.001596 | 0.0015748 | 0.0015704 | 0.0015693 | 0.0015404 | 0.00153 | 0.0015196 | 0.0015093 | 0.0014989 | 0.0014885 | 0.0014781 | 0.0014678 | 0.0014574 | 0.001447 | 0.0014367 | 0.0014263 | 32583.1543 | 7511.9865 | 723.3104 | 166.7579 | 31245.9306 | 40501.6365 | 891744.6832 | 32607.9396
| HTN034-158085792 | 33 | HTN034 | HTN | South | 599966.1073 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.023577 | 0.023777 | 0.023977 | 0.024177 | 0.024377 | 0.024128 | 0.02388 | 0.023631 | 0.023383 | 0.023134 | 0.022885 | 0.022637 | 0.022388 | 0.02214 | 0.021891 | 0.021643 | 0.021394 | 0.021146 | 0.020897 | 0.020649 | 0.00060218 | 0.00061015 | 0.00061708 | 0.00061987 | 0.00061767 | 0.0006072 | 0.00060328 | 0.00060055 | 0.00058721 | 0.00058097 | 0.00057473 | 0.00056848 | 0.00056224 | 0.000556 | 0.00054976 | 0.00054352 | 0.00053728 | 0.00053103 | 0.00052479 | 0.00051855 | 32583.1543 | 7511.9865 | 274.0848 | 63.1897 | 10499.8427 | 13610.1183 | 626118.6073 | 10957.5305
| HTN034-158085879 | 131 | HTN034 | HTN | South | 2381683.6382 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.22967 | 0.23155 | 0.23343 | 0.2353 | 0.23718 | 0.23533 | 0.23348 | 0.23162 | 0.22977 | 0.22792 | 0.22606 | 0.22421 | 0.22236 | 0.22051 | 0.21865 | 0.2168 | 0.21495 | 0.21309 | 0.21124 | 0.20939 | 0.0058661 | 0.0059419 | 0.0060076 | 0.006033 | 0.0060099 | 0.0059222 | 0.0058984 | 0.0058864 | 0.0057703 | 0.0057237 | 0.0056772 | 0.0056306 | 0.0055841 | 0.0055376 | 0.005491 | 0.0054445 | 0.005398 | 0.0053514 | 0.0053049 | 0.0052584 | 32583.1543 | 7511.9865 | 2700.9566 | 622.7006 | 147260.4978 | 190882.1735 | 2485501.1382 | 153679.5774
| HTN034-158086014 | 12 | HTN034 | HTN | South | 218169.4936 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 3.2173e-05 | 3.2515e-05 | 3.2857e-05 | 3.3198e-05 | 3.354e-05 | 3.3221e-05 | 3.2903e-05 | 3.2584e-05 | 3.2266e-05 | 3.1947e-05 | 3.1629e-05 | 3.131e-05 | 3.0992e-05 | 3.0673e-05 | 3.0355e-05 | 3.0036e-05 | 2.9718e-05 | 2.9399e-05 | 2.9081e-05 | 2.8763e-05 | 8.2174e-07 | 8.3438e-07 | 8.4562e-07 | 8.5117e-07 | 8.4985e-07 | 8.3604e-07 | 8.3124e-07 | 8.2809e-07 | 8.103e-07 | 8.023e-07 | 7.943e-07 | 7.863e-07 | 7.783e-07 | 7.7031e-07 | 7.6231e-07 | 7.5431e-07 | 7.4631e-07 | 7.3831e-07 | 7.3031e-07 | 7.2232e-07 | 32583.1543 | 7511.9865 | 0.37798 | 0.087143 | 7.696 | 9.9757 | 227679.4936 | 8.0315
| HTN034-158095163 | 71 | HTN034 | HTN | South | 1290836.1703 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.043597 | 0.043796 | 0.043995 | 0.044194 | 0.044393 | 0.044197 | 0.044 | 0.043803 | 0.043607 | 0.04341 | 0.043213 | 0.043017 | 0.04282 | 0.042623 | 0.042427 | 0.04223 | 0.042033 | 0.041837 | 0.04164 | 0.041443 | 0.0011135 | 0.0011239 | 0.0011323 | 0.0011331 | 0.0011249 | 0.0011122 | 0.0011116 | 0.0011132 | 0.0010951 | 0.0010902 | 0.0010852 | 0.0010803 | 0.0010753 | 0.0010704 | 0.0010655 | 0.0010605 | 0.0010556 | 0.0010506 | 0.0010457 | 0.0010408 | 32583.1543 | 7511.9865 | 515.6736 | 118.8876 | 161537.7436 | 209388.6415 | 1347103.6703 | 168579.1677
| HTN034-158103724 | 59 | HTN034 | HTN | South | 1072666.6768 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.070113 | 0.070556 | 0.070998 | 0.07144 | 0.071883 | 0.071332 | 0.07078 | 0.070229 | 0.069677 | 0.069126 | 0.068575 | 0.068023 | 0.067472 | 0.066921 | 0.066369 | 0.065818 | 0.065266 | 0.064715 | 0.064164 | 0.063612 | 0.0017908 | 0.0018106 | 0.0018272 | 0.0018317 | 0.0018214 | 0.0017951 | 0.0017881 | 0.0017848 | 0.0017498 | 0.001736 | 0.0017221 | 0.0017083 | 0.0016944 | 0.0016806 | 0.0016667 | 0.0016529 | 0.001639 | 0.0016252 | 0.0016114 | 0.0015975 | 32583.1543 | 7511.9865 | 820.1919 | 189.0937 | 76244.4142 | 98829.6231 | 1119424.1768 | 79567.9053
| HTN034-158130464 | 58 | HTN034 | HTN | South | 1054485.8856 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.04311 | 0.043362 | 0.043613 | 0.043864 | 0.044115 | 0.04379 | 0.043465 | 0.04314 | 0.042815 | 0.04249 | 0.042166 | 0.041841 | 0.041516 | 0.041191 | 0.040866 | 0.040541 | 0.040216 | 0.039891 | 0.039566 | 0.039241 | 0.0011011 | 0.0011127 | 0.0011224 | 0.0011246 | 0.0011178 | 0.001102 | 0.0010981 | 0.0010963 | 0.0010752 | 0.0010671 | 0.0010589 | 0.0010507 | 0.0010426 | 0.0010344 | 0.0010263 | 0.0010181 | 0.0010099 | 0.0010018 | 0.00099363 | 0.00098547 | 32583.1543 | 7511.9865 | 504.319 | 116.2698 | 23896.8679 | 30975.6258 | 1100450.8856 | 24938.5314
| HTN034-158139663 | 48 | HTN034 | HTN | South | 872677.9743 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.010281 | 0.010334 | 0.010387 | 0.010441 | 0.010494 | 0.010432 | 0.010369 | 0.010307 | 0.010245 | 0.010182 | 0.01012 | 0.010057 | 0.009995 | 0.0099326 | 0.0098702 | 0.0098078 | 0.0097454 | 0.009683 | 0.0096206 | 0.0095582 | 0.00026258 | 0.00026518 | 0.00026733 | 0.00026769 | 0.00026591 | 0.00026252 | 0.00026196 | 0.00026194 | 0.00025727 | 0.00025571 | 0.00025414 | 0.00025257 | 0.000251 | 0.00024944 | 0.00024787 | 0.0002463 | 0.00024474 | 0.00024317 | 0.0002416 | 0.00024004 | 32583.1543 | 7511.9865 | 120.9041 | 27.8742 | 5566.0229 | 7214.7967 | 910717.9743 | 5808.6457
| HTN034-158494823 | 246 | HTN034 | HTN | South | 4472474.6183 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.41291 | 0.4162 | 0.41948 | 0.42277 | 0.42605 | 0.42082 | 0.41559 | 0.41036 | 0.40512 | 0.39989 | 0.39466 | 0.38943 | 0.38419 | 0.37896 | 0.37373 | 0.3685 | 0.36327 | 0.35803 | 0.3528 | 0.34757 | 0.010546 | 0.01068 | 0.010796 | 0.010839 | 0.010795 | 0.01059 | 0.010499 | 0.010429 | 0.010174 | 0.010042 | 0.0099111 | 0.0097797 | 0.0096483 | 0.0095169 | 0.0093855 | 0.0092541 | 0.0091227 | 0.0089913 | 0.0088599 | 0.0087286 | 32583.1543 | 7511.9865 | 4739.2663 | 1092.6291 | 485146.5491 | 628857.2233 | 4667429.6183 | 506294.0689
| HTN034-158495102 | 15 | HTN034 | HTN | South | 272711.867 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.008979 | 0.0090744 | 0.0091698 | 0.0092653 | 0.0093607 | 0.0092754 | 0.00919 | 0.0091047 | 0.0090194 | 0.008934 | 0.0088487 | 0.0087633 | 0.008678 | 0.0085926 | 0.0085073 | 0.008422 | 0.0083366 | 0.0082513 | 0.0081659 | 0.0080806 | 0.00022933 | 0.00023286 | 0.000236 | 0.00023755 | 0.00023719 | 0.00023342 | 0.00023217 | 0.00023138 | 0.0002265 | 0.00022436 | 0.00022222 | 0.00022007 | 0.00021793 | 0.00021579 | 0.00021364 | 0.0002115 | 0.00020936 | 0.00020722 | 0.00020507 | 0.00020293 | 32583.1543 | 7511.9865 | 105.7017 | 24.3693 | 3497.3182 | 4533.2979 | 284599.367 | 3649.7662
| HTN034-158495212 | 55 | HTN034 | HTN | South | 999943.5122 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.012514 | 0.012619 | 0.012724 | 0.012828 | 0.012933 | 0.0128 | 0.012666 | 0.012533 | 0.0124 | 0.012267 | 0.012134 | 0.012001 | 0.011868 | 0.011735 | 0.011602 | 0.011469 | 0.011336 | 0.011203 | 0.011069 | 0.010936 | 0.00031964 | 0.00032382 | 0.00032746 | 0.0003289 | 0.00032769 | 0.00032211 | 0.00032 | 0.00031852 | 0.00031141 | 0.00030807 | 0.00030473 | 0.00030138 | 0.00029804 | 0.0002947 | 0.00029136 | 0.00028801 | 0.00028467 | 0.00028133 | 0.00027799 | 0.00027465 | 32583.1543 | 7511.9865 | 145.3504 | 33.5103 | 6297.3303 | 8162.7328 | 1043531.0122 | 6571.8307
| HTN034-158638369 | 49 | HTN034 | HTN | South | 890858.7654 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.033658 | 0.033921 | 0.034185 | 0.034449 | 0.034713 | 0.034377 | 0.034041 | 0.033705 | 0.033369 | 0.033033 | 0.032697 | 0.032361 | 0.032025 | 0.031689 | 0.031353 | 0.031017 | 0.030681 | 0.030345 | 0.030009 | 0.029673 | 0.00085966 | 0.00087048 | 0.00087981 | 0.00088324 | 0.00087958 | 0.00086512 | 0.00085999 | 0.00085657 | 0.000838 | 0.00082957 | 0.00082113 | 0.00081269 | 0.00080425 | 0.00079582 | 0.00078738 | 0.00077894 | 0.0007705 | 0.00076207 | 0.00075363 | 0.00074519 | 32583.1543 | 7511.9865 | 391.537 | 90.2681 | 17631.9731 | 22854.9366 | 929691.2654 | 18400.5501
| HTN034-158638445 | 45 | HTN034 | HTN | South | 818135.6009 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.02186 | 0.022048 | 0.022237 | 0.022426 | 0.022615 | 0.022279 | 0.021943 | 0.021607 | 0.021271 | 0.020935 | 0.020598 | 0.020262 | 0.019926 | 0.01959 | 0.019254 | 0.018918 | 0.018582 | 0.018246 | 0.01791 | 0.017574 | 0.00055832 | 0.0005658 | 0.00057231 | 0.00057498 | 0.00057303 | 0.00056066 | 0.00055435 | 0.0005491 | 0.00053417 | 0.00052573 | 0.00051729 | 0.00050885 | 0.00050041 | 0.00049197 | 0.00048353 | 0.00047509 | 0.00046665 | 0.00045821 | 0.00044977 | 0.00044133 | 32583.1543 | 7511.9865 | 247.9773 | 57.1707 | 12951.9209 | 16788.554 | 853798.1009 | 13516.4947
| HTN034-158638542 | 62 | HTN034 | HTN | South | 1127209.0502 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.064722 | 0.065128 | 0.065533 | 0.065938 | 0.066343 | 0.065569 | 0.064795 | 0.064021 | 0.063247 | 0.062473 | 0.061699 | 0.060925 | 0.060151 | 0.059377 | 0.058603 | 0.057829 | 0.057055 | 0.056281 | 0.055507 | 0.054733 | 0.0016531 | 0.0016713 | 0.0016866 | 0.0016906 | 0.001681 | 0.0016501 | 0.0016369 | 0.001627 | 0.0015883 | 0.0015689 | 0.0015495 | 0.00153 | 0.0015106 | 0.0014911 | 0.0014717 | 0.0014523 | 0.0014328 | 0.0014134 | 0.001394 | 0.0013745 | 32583.1543 | 7511.9865 | 741.2458 | 170.8929 | 32696.2797 | 42381.6097 | 1176344.0502 | 34121.5093
| HTN034-158638725 | 33 | HTN034 | HTN | South | 599966.1073 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.027389 | 0.027638 | 0.027887 | 0.028137 | 0.028386 | 0.028143 | 0.0279 | 0.027656 | 0.027413 | 0.02717 | 0.026927 | 0.026684 | 0.02644 | 0.026197 | 0.025954 | 0.025711 | 0.025468 | 0.025224 | 0.024981 | 0.024738 | 0.00069954 | 0.00070923 | 0.00071772 | 0.00072139 | 0.00071926 | 0.00070823 | 0.00070483 | 0.00070285 | 0.00068843 | 0.00068232 | 0.00067621 | 0.00067011 | 0.000664 | 0.00065789 | 0.00065178 | 0.00064568 | 0.00063957 | 0.00063346 | 0.00062735 | 0.00062125 | 32583.1543 | 7511.9865 | 321.7801 | 74.1858 | 18017.5114 | 23354.6795 | 626118.6073 | 18802.894
| HTN034-158639522 | 29 | HTN034 | HTN | South | 527242.9428 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 6.2395e-05 | 6.2719e-05 | 6.3043e-05 | 6.3366e-05 | 6.369e-05 | 6.3354e-05 | 6.3019e-05 | 6.2683e-05 | 6.2348e-05 | 6.2012e-05 | 6.1677e-05 | 6.1341e-05 | 6.1006e-05 | 6.067e-05 | 6.0335e-05 | 5.9999e-05 | 5.9664e-05 | 5.9328e-05 | 5.8993e-05 | 5.8657e-05 | 1.5937e-06 | 1.6095e-06 | 1.6225e-06 | 1.6246e-06 | 1.6138e-06 | 1.5944e-06 | 1.5921e-06 | 1.593e-06 | 1.5658e-06 | 1.5573e-06 | 1.5489e-06 | 1.5405e-06 | 1.532e-06 | 1.5236e-06 | 1.5152e-06 | 1.5068e-06 | 1.4983e-06 | 1.4899e-06 | 1.4815e-06 | 1.4731e-06 | 32583.1543 | 7511.9865 | 0.73635 | 0.16976 | 42.8243 | 55.5097 | 550225.4428 | 44.691
| HTN034-158639644 | 47 | HTN034 | HTN | South | 854497.1832 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.037034 | 0.037368 | 0.037702 | 0.038036 | 0.03837 | 0.037988 | 0.037606 | 0.037225 | 0.036843 | 0.036461 | 0.036079 | 0.035697 | 0.035315 | 0.034933 | 0.034551 | 0.034169 | 0.033787 | 0.033405 | 0.033023 | 0.032641 | 0.00094589 | 0.00095891 | 0.00097032 | 0.00097521 | 0.00097225 | 0.00095601 | 0.00095007 | 0.00094601 | 0.00092523 | 0.00091564 | 0.00090605 | 0.00089645 | 0.00088686 | 0.00087727 | 0.00086768 | 0.00085808 | 0.00084849 | 0.0008389 | 0.00082931 | 0.00081971 | 32583.1543 | 7511.9865 | 431.8221 | 99.5558 | 23560.9261 | 30540.171 | 891744.6832 | 24587.946
| HTN034-158639828 | 32 | HTN034 | HTN | South | 581785.3162 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.018278 | 0.018385 | 0.018493 | 0.0186 | 0.018707 | 0.018537 | 0.018366 | 0.018196 | 0.018026 | 0.017855 | 0.017685 | 0.017514 | 0.017344 | 0.017174 | 0.017003 | 0.016833 | 0.016662 | 0.016492 | 0.016322 | 0.016151 | 0.00046684 | 0.00047179 | 0.00047594 | 0.00047688 | 0.00047401 | 0.00046649 | 0.00046399 | 0.00046242 | 0.00045268 | 0.0004484 | 0.00044412 | 0.00043984 | 0.00043556 | 0.00043128 | 0.000427 | 0.00042272 | 0.00041845 | 0.00041417 | 0.00040989 | 0.00040561 | 32583.1543 | 7511.9865 | 211.9134 | 48.8562 | 13597.5446 | 17625.425 | 607145.3162 | 14190.261
| HTN034-158639936 | 32 | HTN034 | HTN | South | 581785.3162 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.0047218 | 0.0047491 | 0.0047763 | 0.0048035 | 0.0048308 | 0.004778 | 0.0047253 | 0.0046725 | 0.0046198 | 0.004567 | 0.0045143 | 0.0044615 | 0.0044088 | 0.004356 | 0.0043033 | 0.0042505 | 0.0041978 | 0.004145 | 0.0040923 | 0.0040395 | 0.0001206 | 0.00012187 | 0.00012293 | 0.00012316 | 0.0001224 | 0.00012024 | 0.00011938 | 0.00011875 | 0.00011602 | 0.00011469 | 0.00011337 | 0.00011204 | 0.00011072 | 0.00010939 | 0.00010807 | 0.00010674 | 0.00010542 | 0.00010409 | 0.00010277 | 0.00010144 | 32583.1543 | 7511.9865 | 54.2062 | 12.4971 | 38257.3674 | 49590.0092 | 607145.3162 | 39925.0046
| HTN034-158640079 | 42 | HTN034 | HTN | South | 763593.2275 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00025262 | 0.00025426 | 0.00025591 | 0.00025755 | 0.0002592 | 0.00025776 | 0.00025632 | 0.00025488 | 0.00025344 | 0.000252 | 0.00025056 | 0.00024912 | 0.00024768 | 0.00024624 | 0.0002448 | 0.00024336 | 0.00024192 | 0.00024048 | 0.00023904 | 0.0002376 | 6.4522e-06 | 6.5248e-06 | 6.5862e-06 | 6.6034e-06 | 6.5677e-06 | 6.4867e-06 | 6.4755e-06 | 6.4774e-06 | 6.3647e-06 | 6.3285e-06 | 6.2923e-06 | 6.2562e-06 | 6.22e-06 | 6.1838e-06 | 6.1477e-06 | 6.1115e-06 | 6.0754e-06 | 6.0392e-06 | 6.003e-06 | 5.9669e-06 | 32583.1543 | 7511.9865 | 2.9897 | 0.68927 | 153.8878 | 199.4726 | 796878.2275 | 160.5958
| HTN034-158770728 | 153 | HTN034 | HTN | South | 2781661.0431 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.037099 | 0.037182 | 0.037264 | 0.037347 | 0.037429 | 0.037306 | 0.037182 | 0.037058 | 0.036935 | 0.036811 | 0.036688 | 0.036564 | 0.03644 | 0.036317 | 0.036193 | 0.036069 | 0.035946 | 0.035822 | 0.035698 | 0.035575 | 0.00094757 | 0.00095414 | 0.00095906 | 0.00095753 | 0.0009484 | 0.00093882 | 0.00093934 | 0.00094179 | 0.00092755 | 0.00092444 | 0.00092134 | 0.00091823 | 0.00091513 | 0.00091202 | 0.00090892 | 0.00090581 | 0.00090271 | 0.0008996 | 0.0008965 | 0.00089339 | 32583.1543 | 7511.9865 | 437.9641 | 100.9718 | 38901.3763 | 50424.7871 | 2902913.5431 | 40597.0858
| HTN034-158770892 | 249 | HTN034 | HTN | South | 4527016.9917 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.37099 | 0.37448 | 0.37797 | 0.38146 | 0.38495 | 0.37866 | 0.37237 | 0.36608 | 0.3598 | 0.35351 | 0.34722 | 0.34093 | 0.33464 | 0.32835 | 0.32207 | 0.31578 | 0.30949 | 0.3032 | 0.29691 | 0.29063 | 0.0094756 | 0.0096097 | 0.0097277 | 0.0097802 | 0.009754 | 0.0095292 | 0.0094074 | 0.0093035 | 0.0090356 | 0.0088777 | 0.0087198 | 0.0085618 | 0.0084039 | 0.008246 | 0.0080881 | 0.0079302 | 0.0077723 | 0.0076143 | 0.0074564 | 0.0072985 | 32583.1543 | 7511.9865 | 4185.1157 | 964.8707 | 410355.6723 | 531911.7061 | 4724349.4917 | 428243.0606
| HTN034-160807148 | 47 | HTN034 | HTN | South | 854497.1832 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.049932 | 0.050413 | 0.050894 | 0.051375 | 0.051856 | 0.051171 | 0.050486 | 0.049801 | 0.049117 | 0.048432 | 0.047747 | 0.047062 | 0.046378 | 0.045693 | 0.045008 | 0.044323 | 0.043638 | 0.042954 | 0.042269 | 0.041584 | 0.0012753 | 0.0012937 | 0.0013098 | 0.0013172 | 0.0013139 | 0.0012878 | 0.0012754 | 0.0012656 | 0.0012335 | 0.0012163 | 0.0011991 | 0.0011819 | 0.0011647 | 0.0011475 | 0.0011303 | 0.0011131 | 0.0010959 | 0.0010787 | 0.0010615 | 0.0010443 | 32583.1543 | 7511.9865 | 573.3312 | 132.1805 | 25838.6317 | 33492.5812 | 891744.6832 | 26964.9367
| HTN034-161079325 | 137 | HTN034 | HTN | South | 2490768.385 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.25807 | 0.25986 | 0.26166 | 0.26345 | 0.26525 | 0.26274 | 0.26024 | 0.25774 | 0.25524 | 0.25273 | 0.25023 | 0.24773 | 0.24522 | 0.24272 | 0.24022 | 0.23772 | 0.23521 | 0.23271 | 0.23021 | 0.2277 | 0.0065914 | 0.0066685 | 0.0067342 | 0.0067546 | 0.006721 | 0.0066121 | 0.0065746 | 0.0065501 | 0.0064098 | 0.0063469 | 0.0062841 | 0.0062212 | 0.0061583 | 0.0060955 | 0.0060326 | 0.0059698 | 0.0059069 | 0.0058441 | 0.0057812 | 0.0057184 | 32583.1543 | 7511.9865 | 2997.3695 | 691.0381 | 411701.0147 | 533655.5673 | 2599340.885 | 429647.0464
| HTN034-161093808 | 105 | HTN034 | HTN | South | 1908983.0688 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.21548 | 0.21691 | 0.21834 | 0.21977 | 0.22119 | 0.21982 | 0.21845 | 0.21707 | 0.2157 | 0.21432 | 0.21295 | 0.21157 | 0.2102 | 0.20882 | 0.20745 | 0.20607 | 0.2047 | 0.20332 | 0.20195 | 0.20057 | 0.0055036 | 0.0055661 | 0.0056192 | 0.0056345 | 0.0056047 | 0.0055319 | 0.0055187 | 0.0055165 | 0.0054168 | 0.0053823 | 0.0053477 | 0.0053132 | 0.0052787 | 0.0052442 | 0.0052096 | 0.0051751 | 0.0051406 | 0.0051061 | 0.0050716 | 0.005037 | 32583.1543 | 7511.9865 | 2542.454 | 586.1581 | 309942.1126 | 401753.5251 | 1992195.5688 | 323452.4776
| HTN034-162616477 | 11 | HTN034 | HTN | South | 199988.7024 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.0035 | 0.0035256 | 0.0035513 | 0.003577 | 0.0036026 | 0.0035746 | 0.0035467 | 0.0035187 | 0.0034907 | 0.0034627 | 0.0034348 | 0.0034068 | 0.0033788 | 0.0033508 | 0.0033229 | 0.0032949 | 0.0032669 | 0.0032389 | 0.003211 | 0.003183 | 8.9394e-05 | 9.0473e-05 | 9.1398e-05 | 9.1709e-05 | 9.1285e-05 | 8.9958e-05 | 8.96e-05 | 8.9422e-05 | 8.7663e-05 | 8.696e-05 | 8.6257e-05 | 8.5555e-05 | 8.4852e-05 | 8.415e-05 | 8.3447e-05 | 8.2745e-05 | 8.2042e-05 | 8.1339e-05 | 8.0637e-05 | 7.9934e-05 | 32583.1543 | 7511.9865 | 41.0582 | 9.4659 | 1423.1977 | 1844.779 | 208706.2024 | 1485.2348
| HTN034-162616681 | 12 | HTN034 | HTN | South | 218169.4936 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.0018983 | 0.0019087 | 0.0019191 | 0.0019296 | 0.00194 | 0.0019281 | 0.0019163 | 0.0019045 | 0.0018926 | 0.0018808 | 0.0018689 | 0.0018571 | 0.0018452 | 0.0018334 | 0.0018216 | 0.0018097 | 0.0017979 | 0.001786 | 0.0017742 | 0.0017623 | 4.8484e-05 | 4.898e-05 | 4.9392e-05 | 4.9472e-05 | 4.9156e-05 | 4.8523e-05 | 4.8412e-05 | 4.8399e-05 | 4.7529e-05 | 4.7232e-05 | 4.6935e-05 | 4.6637e-05 | 4.634e-05 | 4.6042e-05 | 4.5745e-05 | 4.5447e-05 | 4.515e-05 | 4.4853e-05 | 4.4555e-05 | 4.4258e-05 | 32583.1543 | 7511.9865 | 22.328 | 5.1477 | 1477.614 | 1915.3146 | 227679.4936 | 1542.0232
| HTN034-162616888 | 19 | HTN034 | HTN | South | 345435.0315 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.0029626 | 0.0029768 | 0.002991 | 0.0030053 | 0.0030195 | 0.0030046 | 0.0029897 | 0.0029748 | 0.0029599 | 0.002945 | 0.0029301 | 0.0029152 | 0.0029003 | 0.0028854 | 0.0028705 | 0.0028556 | 0.0028407 | 0.0028258 | 0.0028109 | 0.002796 | 7.5667e-05 | 7.6389e-05 | 7.6979e-05 | 7.7052e-05 | 7.651e-05 | 7.5614e-05 | 7.553e-05 | 7.5601e-05 | 7.4333e-05 | 7.3958e-05 | 7.3584e-05 | 7.321e-05 | 7.2836e-05 | 7.2461e-05 | 7.2087e-05 | 7.1713e-05 | 7.1339e-05 | 7.0964e-05 | 7.059e-05 | 7.0216e-05 | 32583.1543 | 7511.9865 | 34.9786 | 8.0642 | 4886.9565 | 6334.5765 | 360492.5315 | 5099.9788
| HTN034-162617230 | 28 | HTN034 | HTN | South | 509062.1517 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.0054866 | 0.0055227 | 0.0055588 | 0.0055949 | 0.005631 | 0.0055912 | 0.0055515 | 0.0055117 | 0.0054719 | 0.0054322 | 0.0053924 | 0.0053527 | 0.0053129 | 0.0052731 | 0.0052334 | 0.0051936 | 0.0051539 | 0.0051141 | 0.0050743 | 0.0050346 | 0.00014013 | 0.00014172 | 0.00014306 | 0.00014345 | 0.00014268 | 0.00014071 | 0.00014025 | 0.00014007 | 0.00013742 | 0.00013642 | 0.00013542 | 0.00013442 | 0.00013342 | 0.00013242 | 0.00013143 | 0.00013043 | 0.00012943 | 0.00012843 | 0.00012743 | 0.00012643 | 32583.1543 | 7511.9865 | 64.4427 | 14.8571 | 39802.5091 | 51592.8546 | 531252.1517 | 41537.499
| HTN034-162626507 | 21 | HTN034 | HTN | South | 381796.6138 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.0078586 | 0.0079518 | 0.008045 | 0.0081383 | 0.0082315 | 0.0080704 | 0.0079094 | 0.0077483 | 0.0075873 | 0.0074262 | 0.0072652 | 0.0071041 | 0.0069431 | 0.006782 | 0.0066209 | 0.0064599 | 0.0062988 | 0.0061378 | 0.0059767 | 0.0058157 | 0.00020072 | 0.00020406 | 0.00020705 | 0.00020866 | 0.00020857 | 0.0002031 | 0.00019982 | 0.00019691 | 0.00019054 | 0.0001865 | 0.00018245 | 0.00017841 | 0.00017436 | 0.00017032 | 0.00016627 | 0.00016223 | 0.00015818 | 0.00015414 | 0.00015009 | 0.00014605 | 32583.1543 | 7511.9865 | 87.7632 | 20.2336 | 6772.9253 | 8779.2091 | 398439.1138 | 7068.1568
| HTN034-162646056 | 72 | HTN034 | HTN | South | 1309016.9615 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.024438 | 0.024577 | 0.024716 | 0.024854 | 0.024993 | 0.02482 | 0.024647 | 0.024474 | 0.024301 | 0.024128 | 0.023955 | 0.023782 | 0.023608 | 0.023435 | 0.023262 | 0.023089 | 0.022916 | 0.022743 | 0.02257 | 0.022397 | 0.00062419 | 0.00063069 | 0.0006361 | 0.00063724 | 0.00063329 | 0.00062461 | 0.00062266 | 0.00062197 | 0.00061027 | 0.00060592 | 0.00060157 | 0.00059723 | 0.00059288 | 0.00058853 | 0.00058419 | 0.00057984 | 0.00057549 | 0.00057115 | 0.0005668 | 0.00056245 | 32583.1543 | 7511.9865 | 286.4017 | 66.0294 | 41351.6555 | 53600.891 | 1366076.9615 | 43154.1727
| HTN034-162671356 | 31 | HTN034 | HTN | South | 563604.5251 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.011841 | 0.011962 | 0.012084 | 0.012205 | 0.012327 | 0.012094 | 0.011861 | 0.011628 | 0.011396 | 0.011163 | 0.01093 | 0.010697 | 0.010465 | 0.010232 | 0.009999 | 0.0097662 | 0.0095335 | 0.0093007 | 0.009068 | 0.0088352 | 0.00030243 | 0.00030697 | 0.00031099 | 0.00031293 | 0.00031234 | 0.00030435 | 0.00029965 | 0.00029552 | 0.00028618 | 0.00028033 | 0.00027449 | 0.00026864 | 0.0002628 | 0.00025695 | 0.00025111 | 0.00024526 | 0.00023942 | 0.00023357 | 0.00022772 | 0.00022188 | 32583.1543 | 7511.9865 | 132.0688 | 30.4482 | 18054.8384 | 23403.0636 | 588172.0251 | 18841.8481
| HTN034-162794244 | 37 | HTN034 | HTN | South | 672689.2719 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00043283 | 0.00043573 | 0.00043862 | 0.00044151 | 0.0004444 | 0.00044264 | 0.00044088 | 0.00043912 | 0.00043736 | 0.0004356 | 0.00043384 | 0.00043208 | 0.00043032 | 0.00042856 | 0.0004268 | 0.00042504 | 0.00042328 | 0.00042152 | 0.00041976 | 0.000418 | 1.1055e-05 | 1.1181e-05 | 1.1289e-05 | 1.132e-05 | 1.126e-05 | 1.1139e-05 | 1.1138e-05 | 1.116e-05 | 1.0983e-05 | 1.0939e-05 | 1.0895e-05 | 1.0851e-05 | 1.0807e-05 | 1.0762e-05 | 1.0718e-05 | 1.0674e-05 | 1.063e-05 | 1.0586e-05 | 1.0541e-05 | 1.0497e-05 | 32583.1543 | 7511.9865 | 5.1674 | 1.1913 | 191.7253 | 248.5183 | 702011.7719 | 200.0826
| HTN034-162794768 | 10 | HTN034 | HTN | South | 181807.9113 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.010591 | 0.010648 | 0.010705 | 0.010763 | 0.01082 | 0.010753 | 0.010686 | 0.010619 | 0.010552 | 0.010485 | 0.010418 | 0.010351 | 0.010285 | 0.010218 | 0.010151 | 0.010084 | 0.010017 | 0.0099498 | 0.0098828 | 0.0098159 | 0.0002705 | 0.00027325 | 0.00027552 | 0.00027595 | 0.00027416 | 0.00027061 | 0.00026997 | 0.00026987 | 0.000265 | 0.00026332 | 0.00026164 | 0.00025996 | 0.00025828 | 0.00025659 | 0.00025491 | 0.00025323 | 0.00025155 | 0.00024987 | 0.00024819 | 0.00024651 | 32583.1543 | 7511.9865 | 124.4858 | 28.7 | 4576.7417 | 5932.4695 | 189732.9113 | 4776.2417
| HTN034-167870005 | 48 | HTN034 | HTN | South | 872677.9743 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.04585 | 0.046211 | 0.046571 | 0.046932 | 0.047293 | 0.046957 | 0.046621 | 0.046285 | 0.045949 | 0.045613 | 0.045277 | 0.044942 | 0.044606 | 0.04427 | 0.043934 | 0.043598 | 0.043262 | 0.042926 | 0.04259 | 0.042254 | 0.0011711 | 0.0011858 | 0.0011986 | 0.0012033 | 0.0011983 | 0.0011817 | 0.0011778 | 0.0011763 | 0.0011539 | 0.0011455 | 0.0011371 | 0.0011286 | 0.0011202 | 0.0011118 | 0.0011033 | 0.0010949 | 0.0010864 | 0.001078 | 0.0010696 | 0.0010611 | 32583.1543 | 7511.9865 | 540.6608 | 124.6484 | 27260.2416 | 35335.302 | 910717.9743 | 28448.5145
| HTN034-172348553 | 19 | HTN034 | HTN | South | 345435.0315 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00014568 | 0.00014636 | 0.00014704 | 0.00014772 | 0.0001484 | 0.00014756 | 0.00014672 | 0.00014588 | 0.00014504 | 0.0001442 | 0.00014336 | 0.00014252 | 0.00014168 | 0.00014084 | 0.00014 | 0.00013916 | 0.00013832 | 0.00013748 | 0.00013664 | 0.0001358 | 3.7209e-06 | 3.7558e-06 | 3.7843e-06 | 3.7874e-06 | 3.7602e-06 | 3.7134e-06 | 3.7066e-06 | 3.7073e-06 | 3.6424e-06 | 3.6213e-06 | 3.6002e-06 | 3.5791e-06 | 3.558e-06 | 3.5369e-06 | 3.5158e-06 | 3.4947e-06 | 3.4736e-06 | 3.4525e-06 | 3.4315e-06 | 3.4104e-06 | 32583.1543 | 7511.9865 | 1.7128 | 0.39489 | 102.5573 | 132.937 | 360492.5315 | 107.0278
| HTN034-182145724 | 484 | HTN034 | HTN | South | 8799502.9076 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 36.1574 | 36.3833 | 36.6091 | 36.835 | 37.0608 | 36.7024 | 36.3439 | 35.9855 | 35.627 | 35.2686 | 34.9101 | 34.5517 | 34.1932 | 33.8348 | 33.4763 | 33.1179 | 32.7595 | 32.401 | 32.0426 | 31.6841 | 0.92351 | 0.93365 | 0.94219 | 0.94441 | 0.93906 | 0.92364 | 0.91817 | 0.91452 | 0.8947 | 0.8857 | 0.8767 | 0.8677 | 0.8587 | 0.8497 | 0.84069 | 0.83169 | 0.82269 | 0.81369 | 0.80469 | 0.79569 | 32583.1543 | 7511.9865 | 418475.8189 | 96478.8327 | 3928851.5024 | 5092660.4566 | 9183072.9076 | 4100109.9913
| HTN034-182145744 | 224 | HTN034 | HTN | South | 4072497.2134 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 3.8509 | 3.8765 | 3.9021 | 3.9276 | 3.9532 | 3.921 | 3.8889 | 3.8567 | 3.8246 | 3.7924 | 3.7602 | 3.7281 | 3.6959 | 3.6637 | 3.6316 | 3.5994 | 3.5672 | 3.5351 | 3.5029 | 3.4707 | 0.098357 | 0.099476 | 0.10043 | 0.1007 | 0.10017 | 0.098676 | 0.098246 | 0.098013 | 0.096046 | 0.095239 | 0.094431 | 0.093623 | 0.092815 | 0.092008 | 0.0912 | 0.090392 | 0.089584 | 0.088777 | 0.087969 | 0.087161 | 32583.1543 | 7511.9865 | 44987.188 | 10371.7137 | 652359.3623 | 845602.0101 | 4250017.2134 | 680795.6823
| HTN034-182145765 | 419 | HTN034 | HTN | South | 7617751.4841 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 2.2378 | 2.251 | 2.2642 | 2.2773 | 2.2905 | 2.28 | 2.2696 | 2.2592 | 2.2487 | 2.2383 | 2.2279 | 2.2174 | 2.207 | 2.1966 | 2.1861 | 2.1757 | 2.1652 | 2.1548 | 2.1444 | 2.1339 | 0.057157 | 0.057764 | 0.058272 | 0.058388 | 0.058037 | 0.057379 | 0.057338 | 0.057414 | 0.056473 | 0.056211 | 0.055949 | 0.055686 | 0.055424 | 0.055162 | 0.0549 | 0.054638 | 0.054376 | 0.054114 | 0.053852 | 0.053589 | 32583.1543 | 7511.9865 | 26566.086 | 6124.7624 | 1585035.6869 | 2054556.7987 | 7949808.9841 | 1654127.3328
| HTN034-190418432 | 29 | HTN034 | HTN | South | 527242.9428 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 2.6455 | 2.6687 | 2.692 | 2.7152 | 2.7384 | 2.7122 | 2.6859 | 2.6597 | 2.6334 | 2.6072 | 2.5809 | 2.5547 | 2.5285 | 2.5022 | 2.476 | 2.4497 | 2.4235 | 2.3972 | 2.371 | 2.3447 | 0.06757 | 0.068484 | 0.069282 | 0.069614 | 0.069387 | 0.068253 | 0.067855 | 0.067592 | 0.066133 | 0.065474 | 0.064815 | 0.064156 | 0.063497 | 0.062838 | 0.062179 | 0.06152 | 0.060861 | 0.060202 | 0.059543 | 0.058884 | 32583.1543 | 7511.9865 | 30883.4675 | 7120.1268 | 27818.9835 | 36059.555 | 550225.4428 | 29031.6119
| HTN034-84443403 | 149 | HTN034 | HTN | South | 2708937.8786 | 0.00091743 | 0.00092175 | 0.00092445 | 0.00092094 | 0.00091015 | 0.00090394 | 0.00090745 | 0.00091284 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 0.00090205 | 2.5479 | 2.5602 | 2.5725 | 2.5847 | 2.597 | 2.582 | 2.5671 | 2.5521 | 2.5372 | 2.5222 | 2.5073 | 2.4923 | 2.4774 | 2.4625 | 2.4475 | 2.4326 | 2.4176 | 2.4027 | 2.3877 | 2.3728 | 0.065077 | 0.065698 | 0.066206 | 0.066269 | 0.065803 | 0.064979 | 0.064853 | 0.064859 | 0.063717 | 0.063341 | 0.062966 | 0.062591 | 0.062215 | 0.06184 | 0.061464 | 0.061089 | 0.060714 | 0.060338 | 0.059963 | 0.059588 | 32583.1543 | 7511.9865 | 29956.9833 | 6906.5276 | 180080.6749 | 233424.3815 | 2827020.3786 | 187930.3847
| HYT011-157370486 | 75 | HYT011 | HYTS | South | 1363559.3349 | 0.0076626 | 0.0077538 | 0.0079149 | 0.0079362 | 0.0078845 | 0.0079757 | 0.0081976 | 0.0083495 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.011504 | 0.011577 | 0.011649 | 0.011722 | 0.011795 | 0.011538 | 0.01128 | 0.011023 | 0.010766 | 0.010508 | 0.010251 | 0.0099934 | 0.009736 | 0.0094786 | 0.0092212 | 0.0089638 | 0.0087064 | 0.008449 | 0.0081916 | 0.0079342 | 0.002454 | 0.002499 | 0.002567 | 0.00259 | 0.0025891 | 0.0025619 | 0.0025744 | 0.0025623 | 0.0024497 | 0.0023911 | 0.0023325 | 0.0022739 | 0.0022154 | 0.0021568 | 0.0020982 | 0.0020397 | 0.0019811 | 0.0019225 | 0.0018639 | 0.0018054 | 30450.1443 | 4081.0322 | 1031.5179 | 138.2475 | 7927.6713 | 10276.0154 | 1422996.8349 | 8273.2382
| HYT011-157370579 | 42 | HYT011 | HYTS | South | 763593.2275 | 0.0076626 | 0.0077538 | 0.0079149 | 0.0079362 | 0.0078845 | 0.0079757 | 0.0081976 | 0.0083495 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.016975 | 0.017082 | 0.017189 | 0.017296 | 0.017404 | 0.017064 | 0.016724 | 0.016384 | 0.016043 | 0.015703 | 0.015363 | 0.015023 | 0.014683 | 0.014343 | 0.014003 | 0.013663 | 0.013323 | 0.012983 | 0.012643 | 0.012303 | 0.0036212 | 0.0036874 | 0.0037876 | 0.0038215 | 0.0038201 | 0.0037888 | 0.0038166 | 0.0038084 | 0.0036506 | 0.0035732 | 0.0034959 | 0.0034185 | 0.0033411 | 0.0032638 | 0.0031864 | 0.003109 | 0.0030317 | 0.0029543 | 0.0028769 | 0.0027996 | 30450.1443 | 4081.0322 | 1542.0217 | 206.667 | 14376.4526 | 18635.0621 | 796878.2275 | 15003.1216
| HYT011-162212996 | 11 | HYT011 | HYTS | South | 199988.7024 | 0.0076626 | 0.0077538 | 0.0079149 | 0.0079362 | 0.0078845 | 0.0079757 | 0.0081976 | 0.0083495 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0030107 | 0.0030318 | 0.0030529 | 0.0030741 | 0.0030952 | 0.003031 | 0.0029668 | 0.0029026 | 0.0028384 | 0.0027742 | 0.00271 | 0.0026458 | 0.0025816 | 0.0025175 | 0.0024533 | 0.0023891 | 0.0023249 | 0.0022607 | 0.0021965 | 0.0021323 | 0.00064226 | 0.00065446 | 0.00067271 | 0.00067919 | 0.00067941 | 0.00067301 | 0.00067708 | 0.00067471 | 0.00064586 | 0.00063126 | 0.00061665 | 0.00060204 | 0.00058744 | 0.00057283 | 0.00055822 | 0.00054362 | 0.00052901 | 0.00051441 | 0.0004998 | 0.00048519 | 30450.1443 | 4081.0322 | 272.2423 | 36.4868 | 1139.6773 | 1477.2739 | 208706.2024 | 1189.3558
| HYT011-162213233 | 12 | HYT011 | HYTS | South | 218169.4936 | 0.0076626 | 0.0077538 | 0.0079149 | 0.0079362 | 0.0078845 | 0.0079757 | 0.0081976 | 0.0083495 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30450.1443 | 4081.0322 | 0 | 0 | 0 | 0 | 227679.4936 | 0
| HYT011-41829518 | 290 | HYT011 | HYTS | South | 5272429.4281 | 0.0076626 | 0.0077538 | 0.0079149 | 0.0079362 | 0.0078845 | 0.0079757 | 0.0081976 | 0.0083495 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 2.3929 | 2.4069 | 2.4209 | 2.4349 | 2.4489 | 2.4237 | 2.3985 | 2.3733 | 2.3481 | 2.3228 | 2.2976 | 2.2724 | 2.2472 | 2.222 | 2.1968 | 2.1716 | 2.1463 | 2.1211 | 2.0959 | 2.0707 | 0.51048 | 0.51958 | 0.53345 | 0.53798 | 0.53755 | 0.53817 | 0.54739 | 0.55167 | 0.53429 | 0.52855 | 0.52281 | 0.51707 | 0.51134 | 0.5056 | 0.49986 | 0.49412 | 0.48839 | 0.48265 | 0.47691 | 0.47117 | 30450.1443 | 4081.0322 | 228443.4148 | 30616.7659 | 1137367.1153 | 1474279.3229 | 5502254.4281 | 1186944.905
| HYT011-82429866 | 36 | HYT011 | HYTS | South | 654508.4807 | 0.0076626 | 0.0077538 | 0.0079149 | 0.0079362 | 0.0078845 | 0.0079757 | 0.0081976 | 0.0083495 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.0081733 | 0.018752 | 0.018876 | 0.019001 | 0.019125 | 0.019249 | 0.018995 | 0.01874 | 0.018486 | 0.018231 | 0.017976 | 0.017722 | 0.017467 | 0.017213 | 0.016958 | 0.016703 | 0.016449 | 0.016194 | 0.01594 | 0.015685 | 0.01543 | 0.0040003 | 0.0040747 | 0.0041868 | 0.0042255 | 0.0042253 | 0.0042177 | 0.0042769 | 0.004297 | 0.0041484 | 0.0040904 | 0.0040325 | 0.0039746 | 0.0039166 | 0.0038587 | 0.0038008 | 0.0037428 | 0.0036849 | 0.003627 | 0.003569 | 0.0035111 | 30450.1443 | 4081.0322 | 1766.3549 | 236.7329 | 12092.3484 | 15674.3578 | 683038.4807 | 12619.4534
| KGT002-15430186 | 244 | KGT002 | KGTS | North | 5750183.5908 | 0.0014263 | 0.0014276 | 0.0014194 | 0.0014128 | 0.0013952 | 0.0013811 | 0.0013811 | 0.0013833 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 31.7503 | 31.9587 | 32.1672 | 32.3757 | 32.5842 | 32.7733 | 32.9624 | 33.1515 | 33.3406 | 33.5298 | 33.7189 | 33.908 | 34.0971 | 34.2862 | 34.4753 | 34.6644 | 34.8535 | 35.0426 | 35.2317 | 35.4208 | 1.2607 | 1.2702 | 1.2712 | 1.2734 | 1.2656 | 1.2601 | 1.2674 | 1.2767 | 1.2723 | 1.2795 | 1.2867 | 1.294 | 1.3012 | 1.3084 | 1.3156 | 1.3228 | 1.33 | 1.3373 | 1.3445 | 1.3517 | 26374.6861 | 4391.5243 | 491646.1588 | 81861.6772 | 1228906.4127 | 1228906.4127 | 5750183.5908 | 1228906.4127
| KGT002-24605712 | 65 | KGT002 | KGTS | North | 1531811.2025 | 0.0014263 | 0.0014276 | 0.0014194 | 0.0014128 | 0.0013952 | 0.0013811 | 0.0013811 | 0.0013833 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.0013707 | 0.29438 | 0.29603 | 0.29767 | 0.29931 | 0.30096 | 0.30226 | 0.30355 | 0.30485 | 0.30615 | 0.30745 | 0.30875 | 0.31005 | 0.31135 | 0.31265 | 0.31395 | 0.31525 | 0.31655 | 0.31785 | 0.31915 | 0.32045 | 0.011689 | 0.011765 | 0.011763 | 0.011773 | 0.01169 | 0.011622 | 0.011672 | 0.01174 | 0.011683 | 0.011733 | 0.011782 | 0.011832 | 0.011882 | 0.011931 | 0.011981 | 0.01203 | 0.01208 | 0.012129 | 0.012179 | 0.012229 | 26374.6861 | 4391.5243 | 4511.066 | 751.1163 | 169658.0673 | 169658.0673 | 1531811.2025 | 169658.0673
| KGT003-119555477 | 228 | KGT003 | KGTS | North | 5373122.3717 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 10.2407 | 10.2512 | 10.2616 | 10.2721 | 10.2826 | 10.2742 | 10.2658 | 10.2575 | 10.2491 | 10.2408 | 10.2324 | 10.2241 | 10.2157 | 10.2073 | 10.199 | 10.1906 | 10.1823 | 10.1739 | 10.1656 | 10.1572 | 0.43791 | 0.44306 | 0.44603 | 0.44725 | 0.44409 | 0.44153 | 0.44555 | 0.45142 | 0.44668 | 0.44632 | 0.44596 | 0.44559 | 0.44523 | 0.44486 | 0.4445 | 0.44413 | 0.44377 | 0.44341 | 0.44304 | 0.44268 | 26374.6861 | 4391.5243 | 169558.707 | 28232.4186 | 1197016.2009 | 1197016.2009 | 5373122.3717 | 1197016.2009
| KGT003-15424502 | 329 | KGT003 | KGTS | North | 7753321.3171 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 4.234 | 4.2626 | 4.2912 | 4.3198 | 4.3485 | 4.3781 | 4.4076 | 4.4372 | 4.4668 | 4.4964 | 4.526 | 4.5556 | 4.5852 | 4.6147 | 4.6443 | 4.6739 | 4.7035 | 4.7331 | 4.7627 | 4.7922 | 0.18105 | 0.18423 | 0.18652 | 0.18809 | 0.1878 | 0.18815 | 0.1913 | 0.19528 | 0.19468 | 0.19596 | 0.19725 | 0.19854 | 0.19983 | 0.20112 | 0.20241 | 0.2037 | 0.20499 | 0.20628 | 0.20757 | 0.20886 | 26374.6861 | 4391.5243 | 74209.2423 | 12356.23 | 894217.6887 | 894217.6887 | 7753321.3171 | 894217.6887
| KGT003-155046250 | 26 | KGT003 | KGTS | North | 612724.481 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.05669 | 0.057146 | 0.057602 | 0.058057 | 0.058513 | 0.058846 | 0.059178 | 0.059511 | 0.059844 | 0.060176 | 0.060509 | 0.060842 | 0.061175 | 0.061507 | 0.06184 | 0.062173 | 0.062505 | 0.062838 | 0.063171 | 0.063503 | 0.0024242 | 0.0024699 | 0.0025037 | 0.0025278 | 0.0025271 | 0.0025289 | 0.0025684 | 0.002619 | 0.0026081 | 0.0026226 | 0.0026371 | 0.0026516 | 0.0026661 | 0.0026806 | 0.0026951 | 0.0027096 | 0.0027241 | 0.0027386 | 0.0027531 | 0.0027676 | 26374.6861 | 4391.5243 | 992.338 | 165.2295 | 48230.7409 | 48230.7409 | 612724.481 | 48230.7409
| KGT003-155046371 | 6 | KGT003 | KGTS | North | 141397.9572 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.00022454 | 0.0002265 | 0.00022847 | 0.00023043 | 0.0002324 | 0.00023432 | 0.00023624 | 0.00023816 | 0.00024008 | 0.000242 | 0.00024392 | 0.00024584 | 0.00024776 | 0.00024968 | 0.0002516 | 0.00025352 | 0.00025544 | 0.00025736 | 0.00025928 | 0.0002612 | 9.6016e-06 | 9.7895e-06 | 9.9305e-06 | 1.0033e-05 | 1.0037e-05 | 1.007e-05 | 1.0253e-05 | 1.0481e-05 | 1.0463e-05 | 1.0547e-05 | 1.0631e-05 | 1.0714e-05 | 1.0798e-05 | 1.0882e-05 | 1.0965e-05 | 1.1049e-05 | 1.1133e-05 | 1.1216e-05 | 1.13e-05 | 1.1384e-05 | 26374.6861 | 4391.5243 | 3.9896 | 0.66429 | 123.052 | 123.052 | 141397.9572 | 123.052
| KGT003-155131479 | 65 | KGT003 | KGTS | North | 1531811.2025 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.013484 | 0.013587 | 0.013689 | 0.013791 | 0.013893 | 0.014024 | 0.014155 | 0.014286 | 0.014417 | 0.014548 | 0.01468 | 0.014811 | 0.014942 | 0.015073 | 0.015204 | 0.015335 | 0.015466 | 0.015597 | 0.015728 | 0.015859 | 0.00057662 | 0.00058721 | 0.00059498 | 0.00060045 | 0.00060001 | 0.00060269 | 0.00061435 | 0.00062872 | 0.00062834 | 0.00063406 | 0.00063977 | 0.00064548 | 0.0006512 | 0.00065691 | 0.00066262 | 0.00066834 | 0.00067405 | 0.00067976 | 0.00068548 | 0.00069119 | 26374.6861 | 4391.5243 | 240.0292 | 39.9661 | 17822.3773 | 17822.3773 | 1531811.2025 | 17822.3773
| KGT003-155165277 | 7 | KGT003 | KGTS | North | 164964.2833 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.012505 | 0.012587 | 0.01267 | 0.012752 | 0.012834 | 0.012956 | 0.013077 | 0.013198 | 0.013319 | 0.013441 | 0.013562 | 0.013683 | 0.013804 | 0.013925 | 0.014047 | 0.014168 | 0.014289 | 0.01441 | 0.014532 | 0.014653 | 0.00053473 | 0.00054402 | 0.00055069 | 0.00055522 | 0.00055429 | 0.00055677 | 0.00056755 | 0.00058083 | 0.00058049 | 0.00058577 | 0.00059106 | 0.00059634 | 0.00060162 | 0.00060691 | 0.00061219 | 0.00061747 | 0.00062276 | 0.00062804 | 0.00063332 | 0.00063861 | 26374.6861 | 4391.5243 | 221.8793 | 36.9441 | 5322.631 | 5322.631 | 164964.2833 | 5322.631
| KGT003-155165426 | 30 | KGT003 | KGTS | North | 706989.7858 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.089874 | 0.090476 | 0.091077 | 0.091678 | 0.092279 | 0.092963 | 0.093647 | 0.094331 | 0.095016 | 0.0957 | 0.096384 | 0.097068 | 0.097752 | 0.098436 | 0.09912 | 0.099804 | 0.10049 | 0.10117 | 0.10186 | 0.10254 | 0.0038432 | 0.0039104 | 0.0039587 | 0.0039917 | 0.0039854 | 0.0039951 | 0.0040644 | 0.0041514 | 0.004141 | 0.0041708 | 0.0042006 | 0.0042305 | 0.0042603 | 0.0042901 | 0.0043199 | 0.0043497 | 0.0043795 | 0.0044093 | 0.0044392 | 0.004469 | 26374.6861 | 4391.5243 | 1579.5628 | 263.0055 | 60899.4713 | 60899.4713 | 706989.7858 | 60899.4713
| KGT003-155165521 | 203 | KGT003 | KGTS | North | 4783964.2169 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.11391 | 0.11469 | 0.11548 | 0.11626 | 0.11705 | 0.11769 | 0.11834 | 0.11898 | 0.11963 | 0.12028 | 0.12092 | 0.12157 | 0.12221 | 0.12286 | 0.12351 | 0.12415 | 0.1248 | 0.12544 | 0.12609 | 0.12674 | 0.0048709 | 0.004957 | 0.0050192 | 0.005062 | 0.005055 | 0.0050578 | 0.0051361 | 0.0052364 | 0.0052138 | 0.005242 | 0.0052701 | 0.0052983 | 0.0053264 | 0.0053546 | 0.0053827 | 0.0054109 | 0.005439 | 0.0054672 | 0.0054953 | 0.0055235 | 26374.6861 | 4391.5243 | 1984.7577 | 330.4726 | 460275.814 | 460275.814 | 4783964.2169 | 460275.814
| KGT003-155165638 | 50 | KGT003 | KGTS | North | 1178316.3096 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.10593 | 0.10653 | 0.10714 | 0.10774 | 0.10834 | 0.10933 | 0.11032 | 0.11131 | 0.1123 | 0.11329 | 0.11428 | 0.11527 | 0.11625 | 0.11724 | 0.11823 | 0.11922 | 0.12021 | 0.1212 | 0.12219 | 0.12318 | 0.0045297 | 0.0046044 | 0.0046567 | 0.004691 | 0.0046792 | 0.0046986 | 0.0047881 | 0.0048987 | 0.0048943 | 0.0049374 | 0.0049805 | 0.0050236 | 0.0050667 | 0.0051098 | 0.0051528 | 0.0051959 | 0.005239 | 0.0052821 | 0.0053252 | 0.0053683 | 26374.6861 | 4391.5243 | 1871.1474 | 311.5559 | 120233.2495 | 120233.2495 | 1178316.3096 | 120233.2495
| KGT003-155165904 | 22 | KGT003 | KGTS | North | 518459.1762 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.092594 | 0.093269 | 0.093944 | 0.094619 | 0.095294 | 0.095858 | 0.096421 | 0.096985 | 0.097549 | 0.098113 | 0.098677 | 0.099241 | 0.099804 | 0.10037 | 0.10093 | 0.1015 | 0.10206 | 0.10262 | 0.10319 | 0.10375 | 0.0039595 | 0.0040311 | 0.0040833 | 0.0041197 | 0.0041156 | 0.0041195 | 0.0041848 | 0.0042682 | 0.0042514 | 0.004276 | 0.0043006 | 0.0043252 | 0.0043497 | 0.0043743 | 0.0043989 | 0.0044235 | 0.004448 | 0.0044726 | 0.0044972 | 0.0045218 | 26374.6861 | 4391.5243 | 1618.6771 | 269.5183 | 56327.8599 | 56327.8599 | 518459.1762 | 56327.8599
| KGT003-155166011 | 29 | KGT003 | KGTS | North | 683423.4596 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.011155 | 0.011237 | 0.011318 | 0.011399 | 0.01148 | 0.011575 | 0.011671 | 0.011766 | 0.011861 | 0.011956 | 0.012051 | 0.012146 | 0.012241 | 0.012336 | 0.012431 | 0.012526 | 0.012621 | 0.012716 | 0.012811 | 0.012906 | 0.00047702 | 0.00048565 | 0.00049194 | 0.00049632 | 0.00049582 | 0.00049746 | 0.00050652 | 0.00051779 | 0.00051692 | 0.00052106 | 0.0005252 | 0.00052934 | 0.00053348 | 0.00053763 | 0.00054177 | 0.00054591 | 0.00055005 | 0.00055419 | 0.00055834 | 0.00056248 | 26374.6861 | 4391.5243 | 197.2723 | 32.8469 | 14704.2408 | 14704.2408 | 683423.4596 | 14704.2408
| KGT003-155166153 | 13 | KGT003 | KGTS | North | 306362.2405 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.046158 | 0.046489 | 0.04682 | 0.047151 | 0.047482 | 0.047742 | 0.048002 | 0.048261 | 0.048521 | 0.048781 | 0.04904 | 0.0493 | 0.04956 | 0.04982 | 0.050079 | 0.050339 | 0.050599 | 0.050858 | 0.051118 | 0.051378 | 0.0019738 | 0.0020093 | 0.002035 | 0.002053 | 0.0020507 | 0.0020517 | 0.0020833 | 0.0021239 | 0.0021147 | 0.002126 | 0.0021373 | 0.0021486 | 0.0021599 | 0.0021713 | 0.0021826 | 0.0021939 | 0.0022052 | 0.0022165 | 0.0022279 | 0.0022392 | 26374.6861 | 4391.5243 | 804.824 | 134.0074 | 30734.9893 | 30734.9893 | 306362.2405 | 30734.9893
| KGT003-155166380 | 15 | KGT003 | KGTS | North | 353494.8929 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.044679 | 0.044954 | 0.04523 | 0.045506 | 0.045782 | 0.046233 | 0.046684 | 0.047136 | 0.047587 | 0.048038 | 0.048489 | 0.04894 | 0.049391 | 0.049842 | 0.050293 | 0.050744 | 0.051195 | 0.051646 | 0.052097 | 0.052548 | 0.0019105 | 0.0019429 | 0.001966 | 0.0019814 | 0.0019773 | 0.0019869 | 0.0020262 | 0.0020744 | 0.0020739 | 0.0020936 | 0.0021133 | 0.0021329 | 0.0021526 | 0.0021722 | 0.0021919 | 0.0022115 | 0.0022312 | 0.0022509 | 0.0022705 | 0.0022902 | 26374.6861 | 4391.5243 | 793.2275 | 132.0766 | 27183.6346 | 27183.6346 | 353494.8929 | 27183.6346
| KGT003-155177979 | 14 | KGT003 | KGTS | North | 329928.5667 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.21811 | 0.21988 | 0.22165 | 0.22342 | 0.2252 | 0.22589 | 0.22659 | 0.22729 | 0.22798 | 0.22868 | 0.22937 | 0.23007 | 0.23077 | 0.23146 | 0.23216 | 0.23285 | 0.23355 | 0.23425 | 0.23494 | 0.23564 | 0.0093267 | 0.0095033 | 0.0096342 | 0.0097279 | 0.0097259 | 0.0097078 | 0.0098343 | 0.010003 | 0.009936 | 0.0099664 | 0.0099967 | 0.010027 | 0.010057 | 0.010088 | 0.010118 | 0.010148 | 0.010179 | 0.010209 | 0.010239 | 0.01027 | 26374.6861 | 4391.5243 | 3770.2034 | 627.7587 | 83492.9786 | 83492.9786 | 329928.5667 | 83492.9786
| KGT003-155178122 | 10 | KGT003 | KGTS | North | 235663.2619 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.00044494 | 0.00044786 | 0.00045077 | 0.00045369 | 0.0004566 | 0.00046122 | 0.00046584 | 0.00047046 | 0.00047508 | 0.0004797 | 0.00048432 | 0.00048894 | 0.00049356 | 0.00049818 | 0.0005028 | 0.00050742 | 0.00051204 | 0.00051666 | 0.00052128 | 0.0005259 | 1.9027e-05 | 1.9356e-05 | 1.9593e-05 | 1.9753e-05 | 1.972e-05 | 1.9821e-05 | 2.0218e-05 | 2.0704e-05 | 2.0705e-05 | 2.0907e-05 | 2.1108e-05 | 2.1309e-05 | 2.1511e-05 | 2.1712e-05 | 2.1913e-05 | 2.2115e-05 | 2.2316e-05 | 2.2517e-05 | 2.2719e-05 | 2.292e-05 | 26374.6861 | 4391.5243 | 7.9195 | 1.3186 | 271.3965 | 271.3965 | 235663.2619 | 271.3965
| KGT003-155178538 | 18 | KGT003 | KGTS | North | 424193.8715 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.00032884 | 0.00033098 | 0.00033312 | 0.00033526 | 0.0003374 | 0.00034083 | 0.00034426 | 0.00034769 | 0.00035112 | 0.00035455 | 0.00035798 | 0.00036141 | 0.00036484 | 0.00036827 | 0.0003717 | 0.00037513 | 0.00037856 | 0.00038199 | 0.00038542 | 0.00038885 | 1.4062e-05 | 1.4305e-05 | 1.4479e-05 | 1.4597e-05 | 1.4572e-05 | 1.4647e-05 | 1.4941e-05 | 1.5301e-05 | 1.5303e-05 | 1.5452e-05 | 1.5602e-05 | 1.5751e-05 | 1.5901e-05 | 1.605e-05 | 1.62e-05 | 1.6349e-05 | 1.6499e-05 | 1.6648e-05 | 1.6798e-05 | 1.6947e-05 | 26374.6861 | 4391.5243 | 5.8535 | 0.97464 | 309.492 | 309.492 | 424193.8715 | 309.492
| KGT003-84636133 | 428 | KGT003 | KGTS | North | 10086387.6101 | 0.001536 | 0.0015525 | 0.0015613 | 0.0015639 | 0.0015513 | 0.0015436 | 0.001559 | 0.0015808 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 0.0015655 | 31.7614 | 31.967 | 32.1726 | 32.3781 | 32.5837 | 32.6763 | 32.7689 | 32.8615 | 32.9541 | 33.0467 | 33.1394 | 33.232 | 33.3246 | 33.4172 | 33.5098 | 33.6024 | 33.6951 | 33.7877 | 33.8803 | 33.9729 | 1.3582 | 1.3816 | 1.3984 | 1.4097 | 1.4072 | 1.4043 | 1.4222 | 1.4462 | 1.4362 | 1.4403 | 1.4443 | 1.4483 | 1.4524 | 1.4564 | 1.4604 | 1.4645 | 1.4685 | 1.4726 | 1.4766 | 1.4806 | 26374.6861 | 4391.5243 | 545382.1222 | 90808.9984 | 11904901.361 | 11904901.361 | 10086387.6101 | 11904901.361
| KGT004-15430149 | 74 | KGT004 | KGTS | North | 1743908.1382 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 2.4107 | 2.4277 | 2.4447 | 2.4617 | 2.4786 | 2.499 | 2.5193 | 2.5397 | 2.56 | 2.5804 | 2.6008 | 2.6211 | 2.6415 | 2.6618 | 2.6822 | 2.7025 | 2.7229 | 2.7433 | 2.7636 | 2.784 | 0.11689 | 0.11847 | 0.1193 | 0.1199 | 0.11902 | 0.11898 | 0.12033 | 0.12226 | 0.12204 | 0.12301 | 0.12398 | 0.12495 | 0.12592 | 0.12689 | 0.12786 | 0.12883 | 0.1298 | 0.13077 | 0.13174 | 0.13271 | 26374.6861 | 4391.5243 | 47006.3369 | 7826.8029 | 130813.3738 | 130813.3738 | 1743908.1382 | 130813.3738
| KGT004-154877585 | 79 | KGT004 | KGTS | North | 1861739.7692 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0005124 | 0.0005166 | 0.0005208 | 0.000525 | 0.0005292 | 0.00053498 | 0.00054075 | 0.00054653 | 0.0005523 | 0.00055808 | 0.00056385 | 0.00056963 | 0.0005754 | 0.00058118 | 0.00058695 | 0.00059273 | 0.0005985 | 0.00060428 | 0.00061005 | 0.00061583 | 2.4846e-05 | 2.521e-05 | 2.5415e-05 | 2.5571e-05 | 2.5411e-05 | 2.5472e-05 | 2.5828e-05 | 2.631e-05 | 2.6328e-05 | 2.6603e-05 | 2.6878e-05 | 2.7154e-05 | 2.7429e-05 | 2.7704e-05 | 2.7979e-05 | 2.8255e-05 | 2.853e-05 | 2.8805e-05 | 2.9081e-05 | 2.9356e-05 | 26374.6861 | 4391.5243 | 10.1596 | 1.6916 | 711.9956 | 711.9956 | 1861739.7692 | 711.9956
| KGT004-154878038 | 59 | KGT004 | KGTS | North | 1390413.2453 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.043159 | 0.043475 | 0.04379 | 0.044106 | 0.044421 | 0.044865 | 0.045309 | 0.045753 | 0.046196 | 0.04664 | 0.047084 | 0.047527 | 0.047971 | 0.048415 | 0.048859 | 0.049302 | 0.049746 | 0.05019 | 0.050633 | 0.051077 | 0.0020928 | 0.0021216 | 0.002137 | 0.0021482 | 0.002133 | 0.0021361 | 0.0021641 | 0.0022025 | 0.0022021 | 0.0022233 | 0.0022444 | 0.0022656 | 0.0022867 | 0.0023079 | 0.002329 | 0.0023502 | 0.0023713 | 0.0023925 | 0.0024136 | 0.0024348 | 26374.6861 | 4391.5243 | 849.5049 | 141.4471 | 66691.336 | 66691.336 | 1390413.2453 | 66691.336
| KGT004-154878151 | 86 | KGT004 | KGTS | North | 2026704.0525 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.12555 | 0.12625 | 0.12695 | 0.12765 | 0.12835 | 0.129 | 0.12966 | 0.13032 | 0.13098 | 0.13163 | 0.13229 | 0.13295 | 0.1336 | 0.13426 | 0.13492 | 0.13558 | 0.13623 | 0.13689 | 0.13755 | 0.1382 | 0.0060879 | 0.0061611 | 0.0061952 | 0.0062172 | 0.006163 | 0.0061423 | 0.0061931 | 0.0062736 | 0.0062435 | 0.0062749 | 0.0063062 | 0.0063375 | 0.0063688 | 0.0064002 | 0.0064315 | 0.0064628 | 0.0064941 | 0.0065255 | 0.0065568 | 0.0065881 | 26374.6861 | 4391.5243 | 2400.0129 | 399.6148 | 147860.0854 | 147860.0854 | 2026704.0525 | 147860.0854
| KGT004-154878281 | 62 | KGT004 | KGTS | North | 1461112.2239 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.068274 | 0.068787 | 0.069299 | 0.069811 | 0.070323 | 0.07098 | 0.071636 | 0.072293 | 0.072949 | 0.073606 | 0.074262 | 0.074919 | 0.075575 | 0.076232 | 0.076888 | 0.077545 | 0.078201 | 0.078858 | 0.079514 | 0.080171 | 0.0033106 | 0.0033568 | 0.0033818 | 0.0034002 | 0.0033768 | 0.0033795 | 0.0034216 | 0.0034802 | 0.0034774 | 0.0035087 | 0.00354 | 0.0035713 | 0.0036026 | 0.0036339 | 0.0036652 | 0.0036965 | 0.0037278 | 0.0037591 | 0.0037904 | 0.0038217 | 26374.6861 | 4391.5243 | 1340.4921 | 223.199 | 73724.007 | 73724.007 | 1461112.2239 | 73724.007
| KGT004-154878429 | 175 | KGT004 | KGTS | North | 4124107.0836 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.35261 | 0.35498 | 0.35734 | 0.3597 | 0.36206 | 0.36576 | 0.36945 | 0.37315 | 0.37684 | 0.38053 | 0.38423 | 0.38792 | 0.39162 | 0.39531 | 0.39901 | 0.4027 | 0.4064 | 0.41009 | 0.41378 | 0.41748 | 0.017098 | 0.017323 | 0.017438 | 0.017519 | 0.017385 | 0.017415 | 0.017646 | 0.017963 | 0.017964 | 0.01814 | 0.018316 | 0.018492 | 0.018668 | 0.018844 | 0.01902 | 0.019196 | 0.019373 | 0.019549 | 0.019725 | 0.019901 | 26374.6861 | 4391.5243 | 6933.6644 | 1154.4917 | 513721.8496 | 513721.8496 | 4124107.0836 | 513721.8496
| KGT004-154971301 | 24 | KGT004 | KGTS | North | 565591.8286 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0014143 | 0.0014249 | 0.0014356 | 0.0014462 | 0.0014568 | 0.0014719 | 0.001487 | 0.0015021 | 0.0015171 | 0.0015322 | 0.0015473 | 0.0015624 | 0.0015775 | 0.0015926 | 0.0016076 | 0.0016227 | 0.0016378 | 0.0016529 | 0.001668 | 0.0016831 | 6.8577e-05 | 6.9536e-05 | 7.0055e-05 | 7.0438e-05 | 6.9953e-05 | 7.0081e-05 | 7.1023e-05 | 7.231e-05 | 7.2321e-05 | 7.304e-05 | 7.3759e-05 | 7.4478e-05 | 7.5197e-05 | 7.5916e-05 | 7.6635e-05 | 7.7354e-05 | 7.8073e-05 | 7.8792e-05 | 7.9511e-05 | 8.023e-05 | 26374.6861 | 4391.5243 | 27.9048 | 4.6463 | 1247.5989 | 1247.5989 | 565591.8286 | 1247.5989
| KGT004-154971445 | 7 | KGT004 | KGTS | North | 164964.2833 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 5.332e-05 | 5.374e-05 | 5.416e-05 | 5.458e-05 | 5.5e-05 | 5.5635e-05 | 5.627e-05 | 5.6905e-05 | 5.754e-05 | 5.8175e-05 | 5.881e-05 | 5.9445e-05 | 6.008e-05 | 6.0715e-05 | 6.135e-05 | 6.1985e-05 | 6.262e-05 | 6.3255e-05 | 6.389e-05 | 6.4525e-05 | 2.5854e-06 | 2.6225e-06 | 2.643e-06 | 2.6584e-06 | 2.641e-06 | 2.6489e-06 | 2.6876e-06 | 2.7394e-06 | 2.7429e-06 | 2.7732e-06 | 2.8034e-06 | 2.8337e-06 | 2.864e-06 | 2.8942e-06 | 2.9245e-06 | 2.9548e-06 | 2.985e-06 | 3.0153e-06 | 3.0456e-06 | 3.0759e-06 | 26374.6861 | 4391.5243 | 1.0593 | 0.17637 | 138.1353 | 138.1353 | 164964.2833 | 138.1353
| KGT004-154971580 | 48 | KGT004 | KGTS | North | 1131183.6572 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0089672 | 0.0090361 | 0.009105 | 0.0091739 | 0.0092428 | 0.0093101 | 0.0093774 | 0.0094447 | 0.009512 | 0.0095793 | 0.0096466 | 0.0097139 | 0.0097812 | 0.0098485 | 0.0099158 | 0.009983 | 0.01005 | 0.010118 | 0.010185 | 0.010252 | 0.00043481 | 0.00044096 | 0.00044433 | 0.00044682 | 0.00044382 | 0.00044328 | 0.0004479 | 0.00045467 | 0.00045343 | 0.00045664 | 0.00045984 | 0.00046305 | 0.00046626 | 0.00046947 | 0.00047268 | 0.00047588 | 0.00047909 | 0.0004823 | 0.00048551 | 0.00048871 | 26374.6861 | 4391.5243 | 174.432 | 29.0438 | 11996.9725 | 11996.9725 | 1131183.6572 | 11996.9725
| KGT004-154971674 | 41 | KGT004 | KGTS | North | 966219.3739 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0021714 | 0.0021877 | 0.0022039 | 0.0022202 | 0.0022364 | 0.0022644 | 0.0022923 | 0.0023203 | 0.0023483 | 0.0023762 | 0.0024042 | 0.0024321 | 0.0024601 | 0.002488 | 0.002516 | 0.0025439 | 0.0025719 | 0.0025999 | 0.0026278 | 0.0026558 | 0.00010529 | 0.00010676 | 0.00010755 | 0.00010814 | 0.00010739 | 0.00010781 | 0.00010949 | 0.0001117 | 0.00011194 | 0.00011327 | 0.0001146 | 0.00011594 | 0.00011727 | 0.0001186 | 0.00011993 | 0.00012127 | 0.0001226 | 0.00012393 | 0.00012527 | 0.0001266 | 26374.6861 | 4391.5243 | 43.2775 | 7.2059 | 1502.5651 | 1502.5651 | 966219.3739 | 1502.5651
| KGT004-160450903 | 56 | KGT004 | KGTS | North | 1319714.2667 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.047562 | 0.04797 | 0.048377 | 0.048785 | 0.049192 | 0.049501 | 0.04981 | 0.050119 | 0.050428 | 0.050737 | 0.051046 | 0.051355 | 0.051664 | 0.051973 | 0.052282 | 0.052591 | 0.0529 | 0.053209 | 0.053518 | 0.053827 | 0.0023063 | 0.0023409 | 0.0023608 | 0.0023761 | 0.0023621 | 0.0023569 | 0.0023791 | 0.0024128 | 0.0024039 | 0.0024186 | 0.0024333 | 0.0024481 | 0.0024628 | 0.0024775 | 0.0024922 | 0.002507 | 0.0025217 | 0.0025364 | 0.0025512 | 0.0025659 | 26374.6861 | 4391.5243 | 923.3747 | 153.7468 | 48158.6596 | 48158.6596 | 1319714.2667 | 48158.6596
| KGT004-24604166 | 47 | KGT004 | KGTS | North | 1107617.331 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.41322 | 0.4166 | 0.41999 | 0.42338 | 0.42677 | 0.42844 | 0.43012 | 0.43179 | 0.43347 | 0.43514 | 0.43682 | 0.4385 | 0.44017 | 0.44185 | 0.44352 | 0.4452 | 0.44688 | 0.44855 | 0.45023 | 0.4519 | 0.020037 | 0.02033 | 0.020496 | 0.020621 | 0.020492 | 0.020399 | 0.020544 | 0.020787 | 0.020663 | 0.020743 | 0.020823 | 0.020903 | 0.020983 | 0.021063 | 0.021142 | 0.021222 | 0.021302 | 0.021382 | 0.021462 | 0.021542 | 26374.6861 | 4391.5243 | 7920.749 | 1318.8465 | 177789.6715 | 177789.6715 | 1107617.331 | 177789.6715
| KGT004-24604180 | 74 | KGT004 | KGTS | North | 1743908.1382 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 1.0059 | 1.013 | 1.0202 | 1.0273 | 1.0345 | 1.0431 | 1.0517 | 1.0603 | 1.0689 | 1.0775 | 1.0861 | 1.0947 | 1.1033 | 1.112 | 1.1206 | 1.1292 | 1.1378 | 1.1464 | 1.155 | 1.1636 | 0.048775 | 0.049436 | 0.049785 | 0.050036 | 0.049672 | 0.049663 | 0.050232 | 0.051043 | 0.050954 | 0.051364 | 0.051775 | 0.052185 | 0.052596 | 0.053006 | 0.053417 | 0.053827 | 0.054238 | 0.054648 | 0.055059 | 0.055469 | 26374.6861 | 4391.5243 | 19627.9958 | 3268.1648 | 178000.9979 | 178000.9979 | 1743908.1382 | 178000.9979
| KGT004-24605698 | 243 | KGT004 | KGTS | North | 5726617.2646 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 17.4823 | 17.5929 | 17.7035 | 17.8141 | 17.9248 | 18.0651 | 18.2055 | 18.3458 | 18.4862 | 18.6265 | 18.7669 | 18.9072 | 19.0475 | 19.1879 | 19.3282 | 19.4686 | 19.6089 | 19.7493 | 19.8896 | 20.03 | 0.8477 | 0.85854 | 0.86393 | 0.86765 | 0.86071 | 0.86013 | 0.86955 | 0.88317 | 0.88122 | 0.88791 | 0.8946 | 0.90129 | 0.90798 | 0.91467 | 0.92136 | 0.92805 | 0.93474 | 0.94143 | 0.94812 | 0.95481 | 26374.6861 | 4391.5243 | 339458.4211 | 56521.6166 | 1450112.4788 | 1450112.4788 | 5726617.2646 | 1450112.4788
| KGT004-24605978 | 154 | KGT004 | KGTS | North | 3629214.2335 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 2.0057 | 2.0081 | 2.0105 | 2.0129 | 2.0153 | 2.0134 | 2.0116 | 2.0097 | 2.0078 | 2.006 | 2.0041 | 2.0022 | 2.0004 | 1.9985 | 1.9967 | 1.9948 | 1.9929 | 1.9911 | 1.9892 | 1.9873 | 0.097256 | 0.097997 | 0.098113 | 0.09804 | 0.096769 | 0.095864 | 0.096079 | 0.096747 | 0.095711 | 0.095623 | 0.095534 | 0.095445 | 0.095356 | 0.095268 | 0.095179 | 0.09509 | 0.095001 | 0.094913 | 0.094824 | 0.094735 | 26374.6861 | 4391.5243 | 36676.625 | 6106.8514 | 643728.5528 | 643728.5528 | 3629214.2335 | 643728.5528
| KGT004-55202181 | 251 | KGT004 | KGTS | North | 5915147.8741 | 0.0017417 | 0.0017529 | 0.0017529 | 0.0017495 | 0.0017248 | 0.0017102 | 0.0017156 | 0.0017292 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 0.0017123 | 12.4087 | 12.5094 | 12.6102 | 12.7109 | 12.8116 | 12.8767 | 12.9419 | 13.007 | 13.0721 | 13.1373 | 13.2024 | 13.2676 | 13.3327 | 13.3978 | 13.463 | 13.5281 | 13.5933 | 13.6584 | 13.7235 | 13.7887 | 0.60169 | 0.61046 | 0.61538 | 0.61909 | 0.61518 | 0.61309 | 0.61815 | 0.62616 | 0.62314 | 0.62624 | 0.62935 | 0.63245 | 0.63556 | 0.63866 | 0.64177 | 0.64487 | 0.64798 | 0.65108 | 0.65419 | 0.65729 | 26374.6861 | 4391.5243 | 239148.6413 | 39819.5095 | 1487263.1672 | 1487263.1672 | 5915147.8741 | 1487263.1672
| KRT012-118960990 | 65 | KRT012 | KRT | South | 1181751.4235 | 0.0012863 | 0.0013002 | 0.0013201 | 0.0013256 | 0.0013243 | 0.0013332 | 0.0013645 | 0.0013869 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.031438 | 0.031716 | 0.031995 | 0.032273 | 0.032552 | 0.031921 | 0.03129 | 0.03066 | 0.030029 | 0.029399 | 0.028768 | 0.028137 | 0.027507 | 0.026876 | 0.026246 | 0.025615 | 0.024984 | 0.024354 | 0.023723 | 0.023093 | 0.0011258 | 0.0011481 | 0.0011758 | 0.001191 | 0.0012001 | 0.0011848 | 0.0011886 | 0.0011838 | 0.0011474 | 0.0011233 | 0.0010993 | 0.0010752 | 0.0010511 | 0.001027 | 0.0010029 | 0.00097877 | 0.00095468 | 0.00093058 | 0.00090649 | 0.00088239 | 32653.1012 | 4468.839 | 517.7485 | 70.858 | 18480.1744 | 23954.3931 | 1233263.9235 | 19285.7245
| KRT012-141850121 | 65 | KRT012 | KRT | South | 1181751.4235 | 0.0012863 | 0.0013002 | 0.0013201 | 0.0013256 | 0.0013243 | 0.0013332 | 0.0013645 | 0.0013869 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.045473 | 0.045917 | 0.04636 | 0.046803 | 0.047246 | 0.046504 | 0.045762 | 0.04502 | 0.044277 | 0.043535 | 0.042793 | 0.04205 | 0.041308 | 0.040566 | 0.039824 | 0.039081 | 0.038339 | 0.037597 | 0.036854 | 0.036112 | 0.0016284 | 0.0016621 | 0.0017038 | 0.0017272 | 0.0017419 | 0.001726 | 0.0017384 | 0.0017383 | 0.0016919 | 0.0016635 | 0.0016351 | 0.0016068 | 0.0015784 | 0.0015501 | 0.0015217 | 0.0014933 | 0.001465 | 0.0014366 | 0.0014082 | 0.0013799 | 32653.1012 | 4468.839 | 766.7067 | 104.93 | 30775.712 | 39892.1291 | 1233263.9235 | 32117.2241
| KRT012-141850552 | 104 | KRT012 | KRT | South | 1890802.2777 | 0.0012863 | 0.0013002 | 0.0013201 | 0.0013256 | 0.0013243 | 0.0013332 | 0.0013645 | 0.0013869 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.078113 | 0.078887 | 0.079662 | 0.080436 | 0.081211 | 0.079912 | 0.078613 | 0.077315 | 0.076016 | 0.074717 | 0.073419 | 0.07212 | 0.070822 | 0.069523 | 0.068224 | 0.066926 | 0.065627 | 0.064328 | 0.06303 | 0.061731 | 0.0027972 | 0.0028556 | 0.0029277 | 0.0029684 | 0.0029941 | 0.002966 | 0.0029863 | 0.0029852 | 0.0029046 | 0.002855 | 0.0028054 | 0.0027558 | 0.0027062 | 0.0026565 | 0.0026069 | 0.0025573 | 0.0025077 | 0.002458 | 0.0024084 | 0.0023588 | 32653.1012 | 4468.839 | 1315.6743 | 180.0606 | 65419.3747 | 84797.9778 | 1973222.2777 | 68271.0027
| KRT012-141850665 | 74 | KRT012 | KRT | South | 1345378.5437 | 0.0012863 | 0.0013002 | 0.0013201 | 0.0013256 | 0.0013243 | 0.0013332 | 0.0013645 | 0.0013869 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.052121 | 0.052242 | 0.052364 | 0.052485 | 0.052606 | 0.052455 | 0.052303 | 0.052152 | 0.052 | 0.051848 | 0.051697 | 0.051545 | 0.051393 | 0.051242 | 0.05109 | 0.050939 | 0.050787 | 0.050635 | 0.050484 | 0.050332 | 0.0018664 | 0.0018911 | 0.0019244 | 0.0019369 | 0.0019395 | 0.0019469 | 0.0019868 | 0.0020136 | 0.001987 | 0.0019812 | 0.0019754 | 0.0019696 | 0.0019638 | 0.001958 | 0.0019522 | 0.0019464 | 0.0019406 | 0.0019348 | 0.001929 | 0.0019232 | 32653.1012 | 4468.839 | 919.0102 | 125.7739 | 31468.0351 | 40789.533 | 1404023.5437 | 32839.7256
| KRT012-15397067 | 252 | KRT012 | KRT | South | 4581559.3651 | 0.0012863 | 0.0013002 | 0.0013201 | 0.0013256 | 0.0013243 | 0.0013332 | 0.0013645 | 0.0013869 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 2.6486 | 2.6667 | 2.6848 | 2.7029 | 2.721 | 2.6778 | 2.6346 | 2.5914 | 2.5483 | 2.5051 | 2.4619 | 2.4187 | 2.3755 | 2.3323 | 2.2891 | 2.2459 | 2.2027 | 2.1595 | 2.1163 | 2.0731 | 0.094845 | 0.096529 | 0.09867 | 0.099749 | 0.10032 | 0.099391 | 0.10008 | 0.10006 | 0.097371 | 0.095721 | 0.09407 | 0.09242 | 0.090769 | 0.089119 | 0.087468 | 0.085818 | 0.084168 | 0.082517 | 0.080867 | 0.079216 | 32653.1012 | 4468.839 | 44199.711 | 6049.0852 | 188356.0975 | 244151.1594 | 4781269.3651 | 196566.5327
| KRT012-160501273 | 35 | KRT012 | KRT | South | 636327.6896 | 0.0012863 | 0.0013002 | 0.0013201 | 0.0013256 | 0.0013243 | 0.0013332 | 0.0013645 | 0.0013869 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.013441 | 0.013561 | 0.013681 | 0.013801 | 0.013921 | 0.013638 | 0.013356 | 0.013073 | 0.012791 | 0.012508 | 0.012225 | 0.011943 | 0.01166 | 0.011378 | 0.011095 | 0.010812 | 0.01053 | 0.010247 | 0.0099645 | 0.0096819 | 0.0004813 | 0.00049087 | 0.00050279 | 0.00050931 | 0.00051325 | 0.00050621 | 0.00050735 | 0.00050477 | 0.00048874 | 0.00047794 | 0.00046714 | 0.00045634 | 0.00044555 | 0.00043475 | 0.00042395 | 0.00041315 | 0.00040235 | 0.00039155 | 0.00038075 | 0.00036995 | 32653.1012 | 4468.839 | 220.238 | 30.1413 | 4571.8976 | 5926.1904 | 664065.1896 | 4771.1864
| KRT012-163206103 | 15 | KRT012 | KRT | South | 272711.867 | 0.0012863 | 0.0013002 | 0.0013201 | 0.0013256 | 0.0013243 | 0.0013332 | 0.0013645 | 0.0013869 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.00021974 | 0.0002221 | 0.00022447 | 0.00022683 | 0.0002292 | 0.00022278 | 0.00021636 | 0.00020994 | 0.00020352 | 0.0001971 | 0.00019068 | 0.00018426 | 0.00017784 | 0.00017142 | 0.000165 | 0.00015858 | 0.00015216 | 0.00014574 | 0.00013932 | 0.0001329 | 7.8687e-06 | 8.0397e-06 | 8.2495e-06 | 8.3711e-06 | 8.4503e-06 | 8.2687e-06 | 8.2189e-06 | 8.106e-06 | 7.7767e-06 | 7.5314e-06 | 7.286e-06 | 7.0407e-06 | 6.7954e-06 | 6.5501e-06 | 6.3048e-06 | 6.0595e-06 | 5.8142e-06 | 5.5688e-06 | 5.3235e-06 | 5.0782e-06 | 32653.1012 | 4468.839 | 3.4616 | 0.47375 | 64.208 | 83.2278 | 284599.367 | 67.0069
| KRT012-163310215 | 21 | KRT012 | KRT | South | 381796.6138 | 0.0012863 | 0.0013002 | 0.0013201 | 0.0013256 | 0.0013243 | 0.0013332 | 0.0013645 | 0.0013869 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0033365 | 0.0033736 | 0.0034108 | 0.003448 | 0.0034851 | 0.0034237 | 0.0033622 | 0.0033007 | 0.0032392 | 0.0031777 | 0.0031162 | 0.0030547 | 0.0029932 | 0.0029317 | 0.0028702 | 0.0028087 | 0.0027472 | 0.0026857 | 0.0026242 | 0.0025627 | 0.00011948 | 0.00012212 | 0.00012535 | 0.00012724 | 0.00012849 | 0.00012707 | 0.00012772 | 0.00012744 | 0.00012377 | 0.00012142 | 0.00011907 | 0.00011672 | 0.00011437 | 0.00011202 | 0.00010967 | 0.00010732 | 0.00010497 | 0.00010262 | 0.00010027 | 9.7924e-05 | 32653.1012 | 4468.839 | 55.8957 | 7.6498 | 1739.9591 | 2255.3718 | 398439.1138 | 1815.8039
| KRT012-163310404 | 21 | KRT012 | KRT | South | 381796.6138 | 0.0012863 | 0.0013002 | 0.0013201 | 0.0013256 | 0.0013243 | 0.0013332 | 0.0013645 | 0.0013869 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.00048903 | 0.00049413 | 0.00049922 | 0.00050431 | 0.0005094 | 0.00050009 | 0.00049077 | 0.00048146 | 0.00047214 | 0.00046283 | 0.00045351 | 0.0004442 | 0.00043488 | 0.00042557 | 0.00041625 | 0.00040694 | 0.00039762 | 0.00038831 | 0.00037899 | 0.00036968 | 1.7512e-05 | 1.7886e-05 | 1.8347e-05 | 1.8611e-05 | 1.8781e-05 | 1.8561e-05 | 1.8643e-05 | 1.8589e-05 | 1.8041e-05 | 1.7685e-05 | 1.7329e-05 | 1.6973e-05 | 1.6617e-05 | 1.6261e-05 | 1.5905e-05 | 1.5549e-05 | 1.5193e-05 | 1.4837e-05 | 1.4482e-05 | 1.4126e-05 | 32653.1012 | 4468.839 | 8.1441 | 1.1146 | 281.7061 | 365.1534 | 398439.1138 | 293.9857
| KRT012-163313957 | 10 | KRT012 | KRT | South | 181807.9113 | 0.0012863 | 0.0013002 | 0.0013201 | 0.0013256 | 0.0013243 | 0.0013332 | 0.0013645 | 0.0013869 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.00014878 | 0.00015026 | 0.00015174 | 0.00015322 | 0.0001547 | 0.00015116 | 0.00014763 | 0.0001441 | 0.00014056 | 0.00013703 | 0.00013349 | 0.00012996 | 0.00012642 | 0.00012289 | 0.00011935 | 0.00011582 | 0.00011228 | 0.00010875 | 0.00010521 | 0.00010168 | 5.3277e-06 | 5.4391e-06 | 5.5766e-06 | 5.6545e-06 | 5.7036e-06 | 5.6107e-06 | 5.608e-06 | 5.5637e-06 | 5.3709e-06 | 5.2358e-06 | 5.1008e-06 | 4.9657e-06 | 4.8306e-06 | 4.6955e-06 | 4.5605e-06 | 4.4254e-06 | 4.2903e-06 | 4.1552e-06 | 4.0202e-06 | 3.8851e-06 | 32653.1012 | 4468.839 | 2.4101 | 0.32984 | 51.063 | 66.189 | 189732.9113 | 53.2889
| KRT012-24598034 | 448 | KRT012 | KRT | South | 8144994.4269 | 0.0012863 | 0.0013002 | 0.0013201 | 0.0013256 | 0.0013243 | 0.0013332 | 0.0013645 | 0.0013869 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 0.0013725 | 1.1403 | 1.151 | 1.1617 | 1.1725 | 1.1832 | 1.16 | 1.1368 | 1.1135 | 1.0903 | 1.0671 | 1.0438 | 1.0206 | 0.99738 | 0.97415 | 0.95092 | 0.9277 | 0.90447 | 0.88124 | 0.85801 | 0.83478 | 0.040833 | 0.041664 | 0.042695 | 0.043269 | 0.043624 | 0.043054 | 0.043182 | 0.042994 | 0.041661 | 0.040774 | 0.039886 | 0.038998 | 0.038111 | 0.037223 | 0.036336 | 0.035448 | 0.03456 | 0.033673 | 0.032785 | 0.031898 | 32653.1012 | 4468.839 | 18784.8195 | 2570.8533 | 249458.5028 | 323353.3901 | 8500034.4269 | 260332.3895
| KRT013-146237675 | 13 | KRT013 | KRT | South | 236350.2847 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.015024 | 0.015184 | 0.015344 | 0.015504 | 0.015664 | 0.015405 | 0.015146 | 0.014888 | 0.014629 | 0.01437 | 0.014112 | 0.013853 | 0.013594 | 0.013336 | 0.013077 | 0.012818 | 0.01256 | 0.012301 | 0.012042 | 0.011784 | 0.0005607 | 0.00056979 | 0.00057749 | 0.00058266 | 0.00058346 | 0.00057332 | 0.00057578 | 0.00057939 | 0.00057094 | 0.00056085 | 0.00055075 | 0.00054066 | 0.00053056 | 0.00052047 | 0.00051037 | 0.00050028 | 0.00049018 | 0.00048009 | 0.00046999 | 0.00045989 | 32653.1012 | 4468.839 | 257.9545 | 35.3031 | 5414.4425 | 7018.3149 | 246652.7847 | 5650.4578
| KRT013-15397117 | 372 | KRT013 | KRT | South | 6763254.3009 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 6.3035 | 6.3548 | 6.4061 | 6.4573 | 6.5086 | 6.4131 | 6.3176 | 6.222 | 6.1265 | 6.0309 | 5.9354 | 5.8399 | 5.7443 | 5.6488 | 5.5533 | 5.4577 | 5.3622 | 5.2666 | 5.1711 | 5.0756 | 0.23525 | 0.23847 | 0.24111 | 0.24268 | 0.24244 | 0.23867 | 0.24016 | 0.24214 | 0.2391 | 0.23538 | 0.23165 | 0.22792 | 0.22419 | 0.22046 | 0.21673 | 0.213 | 0.20928 | 0.20555 | 0.20182 | 0.19809 | 32653.1012 | 4468.839 | 108466.7474 | 14844.5449 | 249327.8942 | 323184.0925 | 7058064.3009 | 260196.0877
| KRT013-15397128 | 0 | KRT013 | KRT | South | 0 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 1.6237e-06 | 1.6363e-06 | 1.6489e-06 | 1.6614e-06 | 1.674e-06 | 1.6413e-06 | 1.6086e-06 | 1.5759e-06 | 1.5432e-06 | 1.5105e-06 | 1.4778e-06 | 1.4451e-06 | 1.4124e-06 | 1.3797e-06 | 1.347e-06 | 1.3143e-06 | 1.2816e-06 | 1.2489e-06 | 1.2162e-06 | 1.1835e-06 | 6.0599e-08 | 6.1404e-08 | 6.2058e-08 | 6.2439e-08 | 6.2355e-08 | 6.1083e-08 | 6.1149e-08 | 6.133e-08 | 6.0228e-08 | 5.8952e-08 | 5.7676e-08 | 5.6399e-08 | 5.5123e-08 | 5.3847e-08 | 5.2571e-08 | 5.1295e-08 | 5.0018e-08 | 4.8742e-08 | 4.7466e-08 | 4.619e-08 | 32653.1012 | 4468.839 | 0 | 0 | 0 | 0 | 0 | 0
| KRT013-157932507 | 57 | KRT013 | KRT | South | 1036305.0945 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.011486 | 0.011579 | 0.011673 | 0.011767 | 0.01186 | 0.01168 | 0.011499 | 0.011318 | 0.011137 | 0.010956 | 0.010775 | 0.010595 | 0.010414 | 0.010233 | 0.010052 | 0.0098714 | 0.0096906 | 0.0095098 | 0.009329 | 0.0091482 | 0.00042866 | 0.00043453 | 0.00043934 | 0.00044221 | 0.00044179 | 0.00043467 | 0.00043711 | 0.00044046 | 0.00043466 | 0.0004276 | 0.00042055 | 0.00041349 | 0.00040643 | 0.00039938 | 0.00039232 | 0.00038526 | 0.00037821 | 0.00037115 | 0.00036409 | 0.00035703 | 32653.1012 | 4468.839 | 197.0304 | 26.9652 | 7095.0205 | 9196.7157 | 1081477.5945 | 7404.2922
| KRT013-159317752 | 41 | KRT013 | KRT | South | 745412.4364 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0092225 | 0.0092961 | 0.0093697 | 0.0094433 | 0.0095168 | 0.0093753 | 0.0092338 | 0.0090923 | 0.0089508 | 0.0088093 | 0.0086678 | 0.0085263 | 0.0083848 | 0.0082433 | 0.0081018 | 0.0079603 | 0.0078188 | 0.0076773 | 0.0075358 | 0.0073943 | 0.0003442 | 0.00034885 | 0.00035265 | 0.00035489 | 0.0003545 | 0.00034891 | 0.00035102 | 0.00035385 | 0.00034933 | 0.00034381 | 0.00033829 | 0.00033277 | 0.00032724 | 0.00032172 | 0.0003162 | 0.00031068 | 0.00030515 | 0.00029963 | 0.00029411 | 0.00028858 | 32653.1012 | 4468.839 | 158.448 | 21.6849 | 2359.7707 | 3058.7847 | 777904.9364 | 2462.633
| KRT013-159427901 | 69 | KRT013 | KRT | South | 1254474.5881 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.012703 | 0.012777 | 0.012851 | 0.012925 | 0.012999 | 0.012766 | 0.012532 | 0.012298 | 0.012064 | 0.011831 | 0.011597 | 0.011363 | 0.01113 | 0.010896 | 0.010662 | 0.010429 | 0.010195 | 0.0099612 | 0.0097275 | 0.0094938 | 0.00047409 | 0.00047948 | 0.00048368 | 0.00048575 | 0.00048421 | 0.00047508 | 0.00047639 | 0.00047861 | 0.00047085 | 0.00046173 | 0.00045261 | 0.00044349 | 0.00043437 | 0.00042525 | 0.00041613 | 0.00040701 | 0.00039789 | 0.00038877 | 0.00037965 | 0.00037053 | 32653.1012 | 4468.839 | 212.9997 | 29.1507 | 7629.0896 | 9888.9874 | 1309157.0881 | 7961.6413
| KRT013-161097284 | 90 | KRT013 | KRT | South | 1636271.2018 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.078744 | 0.079341 | 0.079938 | 0.080535 | 0.081132 | 0.080209 | 0.079286 | 0.078363 | 0.07744 | 0.076517 | 0.075593 | 0.07467 | 0.073747 | 0.072824 | 0.071901 | 0.070978 | 0.070054 | 0.069131 | 0.068208 | 0.067285 | 0.0029388 | 0.0029774 | 0.0030087 | 0.0030267 | 0.0030221 | 0.0029851 | 0.003014 | 0.0030497 | 0.0030223 | 0.0029863 | 0.0029503 | 0.0029142 | 0.0028782 | 0.0028422 | 0.0028061 | 0.0027701 | 0.0027341 | 0.0026981 | 0.002662 | 0.002626 | 32653.1012 | 4468.839 | 1377.3166 | 188.4968 | 43915.1243 | 56923.7134 | 1707596.2018 | 45829.3829
| KRT013-161918444 | 33 | KRT013 | KRT | South | 599966.1073 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0038297 | 0.0038607 | 0.0038917 | 0.0039227 | 0.0039537 | 0.0039037 | 0.0038537 | 0.0038038 | 0.0037538 | 0.0037038 | 0.0036539 | 0.0036039 | 0.0035539 | 0.0035039 | 0.003454 | 0.003404 | 0.003354 | 0.003304 | 0.0032541 | 0.0032041 | 0.00014293 | 0.00014488 | 0.00014647 | 0.00014742 | 0.00014727 | 0.00014528 | 0.0001465 | 0.00014803 | 0.0001465 | 0.00014455 | 0.0001426 | 0.00014065 | 0.0001387 | 0.00013675 | 0.0001348 | 0.00013285 | 0.0001309 | 0.00012895 | 0.000127 | 0.00012505 | 32653.1012 | 4468.839 | 66.6354 | 9.1196 | 2903.9864 | 3764.2087 | 626118.6073 | 3030.5711
| KRT013-163312849 | 20 | KRT013 | KRT | South | 363615.8226 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0019939 | 0.002009 | 0.0020241 | 0.0020392 | 0.0020542 | 0.0020301 | 0.0020059 | 0.0019818 | 0.0019576 | 0.0019335 | 0.0019093 | 0.0018852 | 0.001861 | 0.0018369 | 0.0018127 | 0.0017886 | 0.0017644 | 0.0017403 | 0.0017161 | 0.0016919 | 7.4415e-05 | 7.539e-05 | 7.618e-05 | 7.6635e-05 | 7.6519e-05 | 7.5552e-05 | 7.6253e-05 | 7.7125e-05 | 7.6402e-05 | 7.546e-05 | 7.4517e-05 | 7.3574e-05 | 7.2632e-05 | 7.1689e-05 | 7.0747e-05 | 6.9804e-05 | 6.8861e-05 | 6.7919e-05 | 6.6976e-05 | 6.6033e-05 | 32653.1012 | 4468.839 | 34.8015 | 4.7629 | 1123.3668 | 1456.1318 | 379465.8226 | 1172.3343
| KRT013-163376810 | 76 | KRT013 | KRT | South | 1381740.126 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.015279 | 0.015414 | 0.015548 | 0.015683 | 0.015818 | 0.015624 | 0.01543 | 0.015236 | 0.015041 | 0.014847 | 0.014653 | 0.014459 | 0.014265 | 0.01407 | 0.013876 | 0.013682 | 0.013488 | 0.013294 | 0.013099 | 0.012905 | 0.00057022 | 0.00057842 | 0.0005852 | 0.00058941 | 0.00058921 | 0.00058146 | 0.00058655 | 0.00059293 | 0.00058704 | 0.00057946 | 0.00057188 | 0.0005643 | 0.00055672 | 0.00054914 | 0.00054156 | 0.00053398 | 0.0005264 | 0.00051882 | 0.00051125 | 0.00050367 | 32653.1012 | 4468.839 | 267.0036 | 36.5416 | 6550.3929 | 8490.7578 | 1441970.126 | 6835.9242
| KRT013-163377041 | 11 | KRT013 | KRT | South | 199988.7024 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.00020126 | 0.00020314 | 0.00020503 | 0.00020691 | 0.0002088 | 0.00020496 | 0.00020112 | 0.00019728 | 0.00019344 | 0.0001896 | 0.00018576 | 0.00018192 | 0.00017808 | 0.00017424 | 0.0001704 | 0.00016656 | 0.00016272 | 0.00015888 | 0.00015504 | 0.0001512 | 7.5112e-06 | 7.6232e-06 | 7.7167e-06 | 7.7762e-06 | 7.7777e-06 | 7.6278e-06 | 7.6454e-06 | 7.6776e-06 | 7.5496e-06 | 7.3997e-06 | 7.2499e-06 | 7.1e-06 | 6.9501e-06 | 6.8003e-06 | 6.6504e-06 | 6.5005e-06 | 6.3507e-06 | 6.2008e-06 | 6.0509e-06 | 5.901e-06 | 32653.1012 | 4468.839 | 3.4052 | 0.46603 | 45.3685 | 58.8076 | 208706.2024 | 47.3461
| KRT013-163377167 | 95 | KRT013 | KRT | South | 1727175.1575 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.014374 | 0.014516 | 0.014658 | 0.0148 | 0.014942 | 0.014742 | 0.014542 | 0.014342 | 0.014142 | 0.013942 | 0.013742 | 0.013542 | 0.013342 | 0.013142 | 0.012942 | 0.012742 | 0.012542 | 0.012342 | 0.012142 | 0.011942 | 0.00053647 | 0.00054474 | 0.00055168 | 0.0005562 | 0.00055656 | 0.00054862 | 0.00055278 | 0.00055814 | 0.00055192 | 0.00054412 | 0.00053631 | 0.00052851 | 0.0005207 | 0.0005129 | 0.00050509 | 0.00049729 | 0.00048948 | 0.00048168 | 0.00047387 | 0.00046607 | 32653.1012 | 4468.839 | 250.5098 | 34.2843 | 7682.856 | 9958.6806 | 1802462.6575 | 8017.7515
| KRT013-163377432 | 50 | KRT013 | KRT | South | 909039.5566 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0029747 | 0.0029983 | 0.0030218 | 0.0030453 | 0.0030689 | 0.0030237 | 0.0029786 | 0.0029334 | 0.0028883 | 0.0028431 | 0.002798 | 0.0027528 | 0.0027077 | 0.0026625 | 0.0026174 | 0.0025722 | 0.002527 | 0.0024819 | 0.0024367 | 0.0023916 | 0.00011102 | 0.00011251 | 0.00011373 | 0.00011445 | 0.00011431 | 0.00011253 | 0.00011323 | 0.00011416 | 0.00011272 | 0.00011096 | 0.0001092 | 0.00010744 | 0.00010567 | 0.00010391 | 0.00010215 | 0.00010039 | 9.8626e-05 | 9.6864e-05 | 9.5101e-05 | 9.3339e-05 | 32653.1012 | 4468.839 | 51.1408 | 6.999 | 7430.5502 | 9631.6364 | 948664.5566 | 7754.4476
| KRT013-163377643 | 22 | KRT013 | KRT | South | 399977.4049 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.00023749 | 0.00023987 | 0.00024225 | 0.00024462 | 0.000247 | 0.00024134 | 0.00023569 | 0.00023003 | 0.00022438 | 0.00021873 | 0.00021307 | 0.00020742 | 0.00020176 | 0.00019611 | 0.00019045 | 0.0001848 | 0.00017914 | 0.00017349 | 0.00016783 | 0.00016218 | 8.8635e-06 | 9.0014e-06 | 9.1174e-06 | 9.1934e-06 | 9.2006e-06 | 8.9819e-06 | 8.9595e-06 | 8.9523e-06 | 8.7571e-06 | 8.5364e-06 | 8.3157e-06 | 8.095e-06 | 7.8743e-06 | 7.6536e-06 | 7.4329e-06 | 7.2122e-06 | 6.9915e-06 | 6.7708e-06 | 6.5501e-06 | 6.3294e-06 | 32653.1012 | 4468.839 | 3.9237 | 0.53699 | 96.5523 | 125.1531 | 417412.4049 | 100.761
| KRT013-163377831 | 21 | KRT013 | KRT | South | 381796.6138 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0052015 | 0.0052415 | 0.0052815 | 0.0053216 | 0.0053616 | 0.0052735 | 0.0051854 | 0.0050974 | 0.0050093 | 0.0049212 | 0.0048332 | 0.0047451 | 0.004657 | 0.0045689 | 0.0044809 | 0.0043928 | 0.0043047 | 0.0042167 | 0.0041286 | 0.0040405 | 0.00019413 | 0.0001967 | 0.00019878 | 0.00019999 | 0.00019972 | 0.00019626 | 0.00019712 | 0.00019838 | 0.0001955 | 0.00019207 | 0.00018863 | 0.00018519 | 0.00018175 | 0.00017832 | 0.00017488 | 0.00017144 | 0.00016801 | 0.00016457 | 0.00016113 | 0.00015769 | 32653.1012 | 4468.839 | 88.5109 | 12.1134 | 2701.1055 | 3501.2302 | 398439.1138 | 2818.8466
| KRT013-24611768 | 280 | KRT013 | KRT | South | 5090621.5168 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.076167 | 0.076734 | 0.077301 | 0.077868 | 0.078434 | 0.077853 | 0.077271 | 0.076689 | 0.076107 | 0.075526 | 0.074944 | 0.074362 | 0.07378 | 0.073198 | 0.072617 | 0.072035 | 0.071453 | 0.070871 | 0.07029 | 0.069708 | 0.0028427 | 0.0028796 | 0.0029094 | 0.0029264 | 0.0029216 | 0.0028974 | 0.0029374 | 0.0029845 | 0.0029703 | 0.0029476 | 0.0029249 | 0.0029022 | 0.0028795 | 0.0028568 | 0.0028341 | 0.0028114 | 0.0027887 | 0.002766 | 0.0027433 | 0.0027206 | 32653.1012 | 4468.839 | 1360.3547 | 186.1755 | 117843.2527 | 152750.9178 | 5312521.5168 | 122980.0356
| KRT013-79724634 | 383 | KRT013 | KRT | South | 6963243.0034 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.29084 | 0.29339 | 0.29595 | 0.2985 | 0.30105 | 0.29842 | 0.2958 | 0.29318 | 0.29055 | 0.28793 | 0.28531 | 0.28268 | 0.28006 | 0.27743 | 0.27481 | 0.27219 | 0.26956 | 0.26694 | 0.26431 | 0.26169 | 0.010855 | 0.01101 | 0.011139 | 0.011218 | 0.011214 | 0.011106 | 0.011245 | 0.01141 | 0.01134 | 0.011237 | 0.011135 | 0.011033 | 0.01093 | 0.010828 | 0.010725 | 0.010623 | 0.01052 | 0.010418 | 0.010316 | 0.010213 | 32653.1012 | 4468.839 | 5180.8365 | 709.0391 | 53150.9046 | 68895.3273 | 7266770.5034 | 55467.7505
| KRT013-79724804 | 1028 | KRT013 | KRT | South | 18689853.2831 | 0.0013406 | 0.0013479 | 0.0013519 | 0.0013499 | 0.001338 | 0.0013368 | 0.0013654 | 0.0013979 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 0.0014019 | 5.251 | 5.2849 | 5.3189 | 5.3528 | 5.3867 | 5.2957 | 5.2047 | 5.1137 | 5.0227 | 4.9317 | 4.8407 | 4.7497 | 4.6587 | 4.5677 | 4.4767 | 4.3857 | 4.2947 | 4.2037 | 4.1127 | 4.0217 | 0.19597 | 0.19832 | 0.20019 | 0.20117 | 0.20065 | 0.19709 | 0.19785 | 0.19901 | 0.19603 | 0.19248 | 0.18893 | 0.18537 | 0.18182 | 0.17827 | 0.17472 | 0.17117 | 0.16762 | 0.16406 | 0.16051 | 0.15696 | 32653.1012 | 4468.839 | 88766.6171 | 12148.424 | 2177365.9291 | 2822347.7929 | 19504543.2831 | 2272277.2279
| KRT022-15396980 | 393 | KRT022 | KRT | South | 7145050.9147 | 0.0013202 | 0.0013329 | 0.001355 | 0.0013755 | 0.0013902 | 0.0014157 | 0.0014493 | 0.0014779 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 4.2357 | 4.2825 | 4.3292 | 4.3759 | 4.4227 | 4.3288 | 4.2348 | 4.1409 | 4.047 | 3.953 | 3.8591 | 3.7652 | 3.6713 | 3.5773 | 3.4834 | 3.3895 | 3.2956 | 3.2016 | 3.1077 | 3.0138 | 0.15568 | 0.15891 | 0.16331 | 0.16758 | 0.17117 | 0.17061 | 0.17087 | 0.17038 | 0.1678 | 0.1639 | 0.16001 | 0.15611 | 0.15222 | 0.14832 | 0.14443 | 0.14054 | 0.13664 | 0.13275 | 0.12885 | 0.12496 | 32653.1012 | 4468.839 | 73898.8846 | 10113.6554 | 140641.0299 | 182301.8791 | 7456503.4147 | 146771.5671
| KRT022-72389353 | 210 | KRT022 | KRT | South | 3817966.1376 | 0.0013202 | 0.0013329 | 0.001355 | 0.0013755 | 0.0013902 | 0.0014157 | 0.0014493 | 0.0014779 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 0.0014893 | 7.5883 | 7.6381 | 7.688 | 7.7378 | 7.7877 | 7.7366 | 7.6855 | 7.6344 | 7.5833 | 7.5322 | 7.4811 | 7.43 | 7.3789 | 7.3279 | 7.2768 | 7.2257 | 7.1746 | 7.1235 | 7.0724 | 7.0213 | 0.27891 | 0.28343 | 0.29001 | 0.29632 | 0.3014 | 0.30492 | 0.3101 | 0.31412 | 0.31442 | 0.3123 | 0.31018 | 0.30806 | 0.30595 | 0.30383 | 0.30171 | 0.29959 | 0.29747 | 0.29535 | 0.29324 | 0.29112 | 32653.1012 | 4468.839 | 141720.6528 | 19395.6087 | 172401.4912 | 223470.4611 | 3984391.1376 | 179916.4657
| KRT023-15396956 | 250 | KRT023 | KRT | South | 4545197.7829 | 0.002387 | 0.0023923 | 0.0024035 | 0.0024143 | 0.0024347 | 0.0024754 | 0.0025268 | 0.0025684 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.0025924 | 0.032666 | 0.032922 | 0.033178 | 0.033434 | 0.03369 | 0.033376 | 0.033062 | 0.032749 | 0.032435 | 0.032122 | 0.031808 | 0.031494 | 0.031181 | 0.030867 | 0.030554 | 0.03024 | 0.029926 | 0.029613 | 0.029299 | 0.028986 | 0.0021708 | 0.0021926 | 0.00222 | 0.0022472 | 0.0022836 | 0.0023002 | 0.0023258 | 0.0023416 | 0.0023409 | 0.0023183 | 0.0022956 | 0.002273 | 0.0022504 | 0.0022277 | 0.0022051 | 0.0021825 | 0.0021598 | 0.0021372 | 0.0021146 | 0.0020919 | 32653.1012 | 4468.839 | 1057.6434 | 144.747 | 1171.585 | 1518.6333 | 4743322.7829 | 1222.6543
| KRT031-15433128 | 98 | KRT031 | KRT | South | 1781717.5309 | 0.039319 | 0.039738 | 0.039319 | 0.038934 | 0.038557 | 0.038241 | 0.038024 | 0.037846 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.063374 | 0.064031 | 0.064688 | 0.065344 | 0.066001 | 0.064305 | 0.062609 | 0.060912 | 0.059216 | 0.05752 | 0.055824 | 0.054127 | 0.052431 | 0.050735 | 0.049039 | 0.047342 | 0.045646 | 0.04395 | 0.042254 | 0.040557 | 0.069372 | 0.070838 | 0.07081 | 0.070828 | 0.070848 | 0.068461 | 0.066277 | 0.06418 | 0.062 | 0.060224 | 0.058448 | 0.056672 | 0.054896 | 0.05312 | 0.051344 | 0.049568 | 0.047792 | 0.046016 | 0.04424 | 0.042464 | 32653.1012 | 4468.839 | 28686.8818 | 3926.03 | 9105.5269 | 11802.7767 | 1859382.5309 | 9502.4365
| KRT031-163356648 | 11 | KRT031 | KRT | South | 199988.7024 | 0.039319 | 0.039738 | 0.039319 | 0.038934 | 0.038557 | 0.038241 | 0.038024 | 0.037846 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.037608 | 0.0029829 | 0.0030138 | 0.0030448 | 0.0030757 | 0.0031066 | 0.0030269 | 0.0029472 | 0.0028675 | 0.0027878 | 0.0027081 | 0.0026283 | 0.0025486 | 0.0024689 | 0.0023892 | 0.0023095 | 0.0022298 | 0.00215 | 0.0020703 | 0.0019906 | 0.0019109 | 0.0032652 | 0.0033342 | 0.0033329 | 0.0033338 | 0.0033348 | 0.0032225 | 0.0031199 | 0.0030213 | 0.0029188 | 0.0028354 | 0.0027519 | 0.0026685 | 0.002585 | 0.0025015 | 0.0024181 | 0.0023346 | 0.0022511 | 0.0021677 | 0.0020842 | 0.0020008 | 32653.1012 | 4468.839 | 1350.5792 | 184.8376 | 970.8461 | 1258.4313 | 208706.2024 | 1013.1653
| KYM001-15421949 | 0 | KYM001 | KYM | North | 0 | 0.0057707 | 0.0058221 | 0.0057833 | 0.0057411 | 0.0056686 | 0.0056046 | 0.0055877 | 0.0055987 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28774.3421 | 3257.8197 | 0 | 0 | 0 | 0 | 0 | 0
| KYM001-15421988 | 828 | KYM001 | KYM | North | 19512918.0868 | 0.0057707 | 0.0058221 | 0.0057833 | 0.0057411 | 0.0056686 | 0.0056046 | 0.0055877 | 0.0055987 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 8.9784 | 9.0405 | 9.1026 | 9.1646 | 9.2267 | 9.2785 | 9.3303 | 9.382 | 9.4338 | 9.4855 | 9.5373 | 9.5891 | 9.6408 | 9.6926 | 9.7443 | 9.7961 | 9.8479 | 9.8996 | 9.9514 | 10.0032 | 1.4424 | 1.4653 | 1.4656 | 1.4648 | 1.4561 | 1.4477 | 1.4514 | 1.4623 | 1.4622 | 1.4702 | 1.4783 | 1.4863 | 1.4943 | 1.5023 | 1.5104 | 1.5184 | 1.5264 | 1.5344 | 1.5424 | 1.5505 | 28774.3421 | 3257.8197 | 616066.3203 | 69750.7858 | 4496675.2645 | 4496675.2645 | 19512918.0868 | 4496675.2645
| KYM001-155421580 | 15 | KYM001 | KYM | North | 353494.8929 | 0.0057707 | 0.0058221 | 0.0057833 | 0.0057411 | 0.0056686 | 0.0056046 | 0.0055877 | 0.0055987 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 5.3237e-05 | 5.3623e-05 | 5.4009e-05 | 5.4394e-05 | 5.478e-05 | 5.5371e-05 | 5.5962e-05 | 5.6553e-05 | 5.7144e-05 | 5.7735e-05 | 5.8326e-05 | 5.8917e-05 | 5.9508e-05 | 6.0099e-05 | 6.069e-05 | 6.1281e-05 | 6.1872e-05 | 6.2463e-05 | 6.3054e-05 | 6.3645e-05 | 8.5528e-06 | 8.6916e-06 | 8.6958e-06 | 8.694e-06 | 8.6451e-06 | 8.6396e-06 | 8.7055e-06 | 8.8147e-06 | 8.8572e-06 | 8.9488e-06 | 9.0404e-06 | 9.132e-06 | 9.2236e-06 | 9.3152e-06 | 9.4068e-06 | 9.4984e-06 | 9.59e-06 | 9.6816e-06 | 9.7732e-06 | 9.8648e-06 | 28774.3421 | 3257.8197 | 3.7488 | 0.42444 | 48.9776 | 48.9776 | 353494.8929 | 48.9776
| KYM001-155421922 | 28 | KYM001 | KYM | North | 659857.1334 | 0.0057707 | 0.0058221 | 0.0057833 | 0.0057411 | 0.0056686 | 0.0056046 | 0.0055877 | 0.0055987 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0055675 | 0.0036123 | 0.0036386 | 0.0036648 | 0.0036911 | 0.0037173 | 0.0037536 | 0.0037898 | 0.003826 | 0.0038623 | 0.0038985 | 0.0039347 | 0.0039709 | 0.0040072 | 0.0040434 | 0.0040796 | 0.0041158 | 0.0041521 | 0.0041883 | 0.0042245 | 0.0042607 | 0.00058033 | 0.00058976 | 0.00059006 | 0.00058996 | 0.00058665 | 0.00058567 | 0.00058955 | 0.00059635 | 0.00059864 | 0.00060426 | 0.00060987 | 0.00061549 | 0.0006211 | 0.00062672 | 0.00063233 | 0.00063795 | 0.00064356 | 0.00064918 | 0.00065479 | 0.00066041 | 28774.3421 | 3257.8197 | 253.1314 | 28.6594 | 3086.4894 | 3086.4894 | 659857.1334 | 3086.4894
| KYM002-15422060 | 0 | KYM002 | KYM | North | 0 | 0.0020817 | 0.0020719 | 0.002042 | 0.0020145 | 0.0019795 | 0.0019519 | 0.001937 | 0.0019249 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28774.3421 | 3257.8197 | 0 | 0 | 0 | 0 | 0 | 0
| KYM002-15422073 | 274 | KYM002 | KYM | North | 6457173.3765 | 0.0020817 | 0.0020719 | 0.002042 | 0.0020145 | 0.0019795 | 0.0019519 | 0.001937 | 0.0019249 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 1.2015 | 1.2047 | 1.2079 | 1.211 | 1.2142 | 1.2144 | 1.2146 | 1.2148 | 1.2149 | 1.2151 | 1.2153 | 1.2155 | 1.2157 | 1.2159 | 1.2161 | 1.2162 | 1.2164 | 1.2166 | 1.2168 | 1.217 | 0.069633 | 0.069488 | 0.068666 | 0.067918 | 0.066913 | 0.065992 | 0.065497 | 0.065097 | 0.064539 | 0.064549 | 0.064559 | 0.064568 | 0.064578 | 0.064588 | 0.064598 | 0.064608 | 0.064618 | 0.064628 | 0.064638 | 0.064648 | 28774.3421 | 3257.8197 | 27464.1298 | 3109.4779 | 105846.5398 | 105846.5398 | 6457173.3765 | 105846.5398
| KYM002-182106953 | 0 | KYM002 | KYM | North | 0 | 0.0020817 | 0.0020719 | 0.002042 | 0.0020145 | 0.0019795 | 0.0019519 | 0.001937 | 0.0019249 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0.0019081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28774.3421 | 3257.8197 | 0 | 0 | 0 | 0 | 0 | 0
| KYM003-15421938 | 452 | KYM003 | KYM | North | 10651979.4387 | 0.0019741 | 0.0019858 | 0.0019987 | 0.0020017 | 0.0019789 | 0.0019702 | 0.0019918 | 0.002019 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 6.2094 | 6.2471 | 6.2847 | 6.3223 | 6.3599 | 6.4122 | 6.4645 | 6.5167 | 6.569 | 6.6213 | 6.6736 | 6.7258 | 6.7781 | 6.8304 | 6.8827 | 6.9349 | 6.9872 | 7.0395 | 7.0917 | 7.144 | 0.34127 | 0.34536 | 0.3497 | 0.35233 | 0.35038 | 0.35172 | 0.35847 | 0.3663 | 0.36584 | 0.36875 | 0.37166 | 0.37458 | 0.37749 | 0.3804 | 0.38331 | 0.38622 | 0.38913 | 0.39204 | 0.39495 | 0.39786 | 28774.3421 | 3257.8197 | 152489.0083 | 17264.7454 | 945182.7729 | 945182.7729 | 10651979.4387 | 945182.7729
| KYM003-155504708 | 14 | KYM003 | KYM | North | 329928.5667 | 0.0019741 | 0.0019858 | 0.0019987 | 0.0020017 | 0.0019789 | 0.0019702 | 0.0019918 | 0.002019 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.046156 | 0.046461 | 0.046765 | 0.04707 | 0.047375 | 0.047814 | 0.048252 | 0.048691 | 0.049129 | 0.049568 | 0.050007 | 0.050445 | 0.050884 | 0.051323 | 0.051761 | 0.0522 | 0.052639 | 0.053077 | 0.053516 | 0.053955 | 0.0025367 | 0.0025685 | 0.0026022 | 0.0026231 | 0.00261 | 0.0026226 | 0.0026757 | 0.0027368 | 0.0027361 | 0.0027605 | 0.002785 | 0.0028094 | 0.0028338 | 0.0028583 | 0.0028827 | 0.0029071 | 0.0029316 | 0.002956 | 0.0029804 | 0.0030048 | 28774.3421 | 3257.8197 | 1141.2489 | 129.2118 | 15703.5056 | 15703.5056 | 329928.5667 | 15703.5056
| KYM003-163531836 | 14 | KYM003 | KYM | North | 329928.5667 | 0.0019741 | 0.0019858 | 0.0019987 | 0.0020017 | 0.0019789 | 0.0019702 | 0.0019918 | 0.002019 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0049822 | 0.0050132 | 0.0050443 | 0.0050753 | 0.0051064 | 0.0051683 | 0.0052303 | 0.0052922 | 0.0053541 | 0.0054161 | 0.005478 | 0.0055399 | 0.0056018 | 0.0056638 | 0.0057257 | 0.0057876 | 0.0058496 | 0.0059115 | 0.0059734 | 0.0060354 | 0.00027382 | 0.00027715 | 0.00028068 | 0.00028284 | 0.00028132 | 0.00028349 | 0.00029003 | 0.00029747 | 0.00029818 | 0.00030163 | 0.00030508 | 0.00030853 | 0.00031198 | 0.00031543 | 0.00031888 | 0.00032232 | 0.00032577 | 0.00032922 | 0.00033267 | 0.00033612 | 28774.3421 | 3257.8197 | 124.7438 | 14.1234 | 1980.4709 | 1980.4709 | 329928.5667 | 1980.4709
| KYM003-24602826 | 330 | KYM003 | KYM | North | 7776887.6433 | 0.0019741 | 0.0019858 | 0.0019987 | 0.0020017 | 0.0019789 | 0.0019702 | 0.0019918 | 0.002019 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 0.0020004 | 3.9436 | 3.963 | 3.9825 | 4.0019 | 4.0214 | 4.0557 | 4.09 | 4.1244 | 4.1587 | 4.1931 | 4.2274 | 4.2617 | 4.2961 | 4.3304 | 4.3647 | 4.3991 | 4.4334 | 4.4678 | 4.5021 | 4.5364 | 0.21674 | 0.21909 | 0.2216 | 0.22302 | 0.22154 | 0.22246 | 0.2268 | 0.23182 | 0.23161 | 0.23352 | 0.23543 | 0.23734 | 0.23926 | 0.24117 | 0.24308 | 0.24499 | 0.24691 | 0.24882 | 0.25073 | 0.25264 | 28774.3421 | 3257.8197 | 96633.723 | 10940.832 | 1182106.9871 | 1182106.9871 | 7776887.6433 | 1182106.9871
| KYM004-15422136 | 315 | KYM004 | KYM | North | 7423392.7504 | 0.0018858 | 0.0019031 | 0.0019139 | 0.0019116 | 0.001892 | 0.0018832 | 0.0019051 | 0.0019332 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 2.6636 | 2.6795 | 2.6954 | 2.7113 | 2.7271 | 2.7393 | 2.7515 | 2.7636 | 2.7758 | 2.7879 | 2.8001 | 2.8123 | 2.8244 | 2.8366 | 2.8487 | 2.8609 | 2.8731 | 2.8852 | 2.8974 | 2.9096 | 0.13984 | 0.14197 | 0.14362 | 0.14429 | 0.14365 | 0.14361 | 0.14593 | 0.14874 | 0.14831 | 0.14896 | 0.14961 | 0.15026 | 0.15091 | 0.15156 | 0.15221 | 0.15286 | 0.15351 | 0.15416 | 0.15481 | 0.15546 | 28774.3421 | 3257.8197 | 61503.7675 | 6963.4323 | 202287.4449 | 202287.4449 | 7423392.7504 | 202287.4449
| KYM004-24596780 | 314 | KYM004 | KYM | North | 7399826.4242 | 0.0018858 | 0.0019031 | 0.0019139 | 0.0019116 | 0.001892 | 0.0018832 | 0.0019051 | 0.0019332 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 1.3715 | 1.379 | 1.3864 | 1.3938 | 1.4013 | 1.411 | 1.4207 | 1.4304 | 1.4401 | 1.4498 | 1.4595 | 1.4692 | 1.479 | 1.4887 | 1.4984 | 1.5081 | 1.5178 | 1.5275 | 1.5372 | 1.5469 | 0.072006 | 0.073062 | 0.073873 | 0.07418 | 0.07381 | 0.073974 | 0.075351 | 0.076986 | 0.076945 | 0.077464 | 0.077983 | 0.078502 | 0.079021 | 0.079539 | 0.080058 | 0.080577 | 0.081096 | 0.081615 | 0.082134 | 0.082653 | 28774.3421 | 3257.8197 | 31999.0988 | 3622.9253 | 525928.2583 | 525928.2583 | 7399826.4242 | 525928.2583
| KYM004-24596836 | 143 | KYM004 | KYM | North | 3369984.6454 | 0.0018858 | 0.0019031 | 0.0019139 | 0.0019116 | 0.001892 | 0.0018832 | 0.0019051 | 0.0019332 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 0.0019192 | 2.0932 | 2.1058 | 2.1183 | 2.1308 | 2.1434 | 2.1553 | 2.1673 | 2.1793 | 2.1912 | 2.2032 | 2.2152 | 2.2271 | 2.2391 | 2.2511 | 2.263 | 2.275 | 2.2869 | 2.2989 | 2.3109 | 2.3228 | 0.1099 | 0.11157 | 0.11287 | 0.1134 | 0.1129 | 0.113 | 0.11495 | 0.11729 | 0.11708 | 0.11772 | 0.11836 | 0.119 | 0.11963 | 0.12027 | 0.12091 | 0.12155 | 0.12219 | 0.12283 | 0.12347 | 0.12411 | 28774.3421 | 3257.8197 | 48606.3887 | 5503.1962 | 676999.9216 | 676999.9216 | 3369984.6454 | 676999.9216
| KYM005-15421849 | 94 | KYM005 | KYM | North | 2215234.662 | 0.001368 | 0.0013712 | 0.0013705 | 0.0013656 | 0.0013508 | 0.0013427 | 0.0013434 | 0.0013483 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0.0013385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28774.3421 | 3257.8197 | 0 | 0 | 0 | 0 | 2215234.662 | 0
| KYM006-15422186 | 0 | KYM006 | KYM | North | 0 | 0.0069209 | 0.0069072 | 0.0068165 | 0.0067289 | 0.0066139 | 0.0065158 | 0.0064705 | 0.0064325 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28774.3421 | 3257.8197 | 0 | 0 | 0 | 0 | 0 | 0
| KYM006-15422212 | 364 | KYM006 | KYM | North | 8578142.7338 | 0.0069209 | 0.0069072 | 0.0068165 | 0.0067289 | 0.0066139 | 0.0065158 | 0.0064705 | 0.0064325 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 0.0063597 | 1.0713 | 1.079 | 1.0866 | 1.0943 | 1.1019 | 1.1118 | 1.1216 | 1.1315 | 1.1414 | 1.1512 | 1.1611 | 1.1709 | 1.1808 | 1.1906 | 1.2005 | 1.2104 | 1.2202 | 1.2301 | 1.2399 | 1.2498 | 0.20642 | 0.20749 | 0.20621 | 0.20499 | 0.2029 | 0.20168 | 0.20205 | 0.20263 | 0.20208 | 0.20383 | 0.20557 | 0.20732 | 0.20906 | 0.21081 | 0.21255 | 0.2143 | 0.21604 | 0.21779 | 0.21953 | 0.22128 | 28774.3421 | 3257.8197 | 86460.214 | 9788.9913 | 300613.7707 | 300613.7707 | 8578142.7338 | 300613.7707
| LV001-15406542 | 0 | LV001 | LV | South | 0 | 0.0011874 | 0.00084093 | 0.000848 | 0.00085357 | 0.00085498 | 0.0008594 | 0.0008685 | 0.00087858 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43164.5707 | 8808.5815 | 0 | 0 | 0 | 0 | 0 | 0
| LV001-15406555 | 150 | LV001 | LV | South | 2727118.6697 | 0.0011874 | 0.00084093 | 0.000848 | 0.00085357 | 0.00085498 | 0.0008594 | 0.0008685 | 0.00087858 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43164.5707 | 8808.5815 | 0 | 0 | 0 | 0 | 2845993.6697 | 0
| LV001-24613045 | 98 | LV001 | LV | South | 1781717.5309 | 0.0011874 | 0.00084093 | 0.000848 | 0.00085357 | 0.00085498 | 0.0008594 | 0.0008685 | 0.00087858 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0.00088556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43164.5707 | 8808.5815 | 0 | 0 | 0 | 0 | 1859382.5309 | 0
| LV002-15406265 | 157 | LV002 | LV | South | 2854384.2076 | 0.0011389 | 0.0011636 | 0.0011879 | 0.0012127 | 0.0012321 | 0.0012563 | 0.0013021 | 0.0013572 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 0.0014011 | 1.0447 | 1.053 | 1.0614 | 1.0697 | 1.078 | 1.0831 | 1.0882 | 1.0933 | 1.0983 | 1.1034 | 1.1085 | 1.1135 | 1.1186 | 1.1237 | 1.1288 | 1.1338 | 1.1389 | 1.144 | 1.1491 | 1.1541 | 0.033125 | 0.034112 | 0.035099 | 0.036116 | 0.036977 | 0.037883 | 0.039448 | 0.041309 | 0.04284 | 0.043038 | 0.043236 | 0.043434 | 0.043632 | 0.04383 | 0.044028 | 0.044226 | 0.044423 | 0.044621 | 0.044819 | 0.045017 | 43164.5707 | 8808.5815 | 25166.0175 | 5135.622 | 6895.5384 | 8938.1428 | 2978806.7076 | 7196.1147
| LV003-15406616 | 95 | LV003 | LV | South | 1727175.1575 | 0.0014465 | 0.0012689 | 0.0013171 | 0.0013587 | 0.001396 | 0.0014389 | 0.0014905 | 0.0015465 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 0.0015831 | 2.872 | 2.8945 | 2.9171 | 2.9397 | 2.9622 | 2.9705 | 2.9787 | 2.9869 | 2.9952 | 3.0034 | 3.0116 | 3.0198 | 3.0281 | 3.0363 | 3.0445 | 3.0528 | 3.061 | 3.0692 | 3.0774 | 3.0857 | 0.11566 | 0.10226 | 0.10697 | 0.1112 | 0.11513 | 0.11899 | 0.12361 | 0.1286 | 0.13201 | 0.13237 | 0.13273 | 0.1331 | 0.13346 | 0.13382 | 0.13418 | 0.13455 | 0.13491 | 0.13527 | 0.13564 | 0.136 | 43164.5707 | 8808.5815 | 77789.3327 | 15874.4468 | 15706.6973 | 20359.3534 | 1802462.6575 | 16391.3516
| LV004-15406315 | 159 | LV004 | LV | South | 2890745.7899 | 0.0012144 | 0.0012487 | 0.0012803 | 0.0013104 | 0.001337 | 0.0013651 | 0.0014023 | 0.0014421 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43164.5707 | 8808.5815 | 0 | 0 | 0 | 0 | 3016753.2899 | 0
| LV004-24612407 | 124 | LV004 | LV | South | 2254418.1003 | 0.0012144 | 0.0012487 | 0.0012803 | 0.0013104 | 0.001337 | 0.0013651 | 0.0014023 | 0.0014421 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0.0014882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43164.5707 | 8808.5815 | 0 | 0 | 94307.7617 | 122243.7164 | 2352688.1003 | 98418.6335
| LV005-15406664 | 4 | LV005 | LV | South | 72723.1645 | 0.00539 | 0.0057279 | 0.0059079 | 0.0060735 | 0.0062083 | 0.006519 | 0.0069153 | 0.0073016 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43164.5707 | 8808.5815 | 0 | 0 | 0 | 0 | 75893.1645 | 0
| LV005-15406790 | 6 | LV005 | LV | South | 109084.7468 | 0.00539 | 0.0057279 | 0.0059079 | 0.0060735 | 0.0062083 | 0.006519 | 0.0069153 | 0.0073016 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0.0076089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43164.5707 | 8808.5815 | 0 | 0 | 0 | 0 | 113839.7468 | 0
| LV006-15406376 | 371 | LV006 | LV | South | 6745073.5098 | 0.00035344 | 0.00038997 | 0.00040101 | 0.00041641 | 0.00043121 | 0.00044738 | 0.00046501 | 0.00048092 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 188.8733 | 190.6241 | 192.3748 | 194.1255 | 195.8763 | 195.7902 | 195.7041 | 195.618 | 195.532 | 195.4459 | 195.3598 | 195.2737 | 195.1876 | 195.1016 | 195.0155 | 194.9294 | 194.8433 | 194.7572 | 194.6712 | 194.5851 | 1.8585 | 2.0696 | 2.1477 | 2.2505 | 2.3515 | 2.4386 | 2.5335 | 2.6191 | 2.6892 | 2.688 | 2.6868 | 2.6857 | 2.6845 | 2.6833 | 2.6821 | 2.6809 | 2.6797 | 2.6785 | 2.6774 | 2.6762 | 43164.5707 | 8808.5815 | 1548396.1048 | 315980.7481 | 3242441.2403 | 4202920.9496 | 7039091.0098 | 3383779.1317
| LV006-160301671 | 104 | LV006 | LV | South | 1890802.2777 | 0.00035344 | 0.00038997 | 0.00040101 | 0.00041641 | 0.00043121 | 0.00044738 | 0.00046501 | 0.00048092 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0.00049401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43164.5707 | 8808.5815 | 0 | 0 | 0 | 0 | 1973222.2777 | 0
| LV007-15406690 | 75 | LV007 | LV | South | 1363559.3349 | 0.0015022 | 0.0016566 | 0.0017154 | 0.0017702 | 0.0018116 | 0.0018834 | 0.0019858 | 0.0020849 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 0.0021574 | 1.0054 | 1.0134 | 1.0214 | 1.0294 | 1.0375 | 1.0423 | 1.0472 | 1.0521 | 1.057 | 1.0619 | 1.0668 | 1.0716 | 1.0765 | 1.0814 | 1.0863 | 1.0912 | 1.096 | 1.1009 | 1.1058 | 1.1107 | 0.042047 | 0.046739 | 0.048778 | 0.050733 | 0.052325 | 0.054655 | 0.057894 | 0.061068 | 0.063486 | 0.063779 | 0.064072 | 0.064366 | 0.064659 | 0.064952 | 0.065245 | 0.065539 | 0.065832 | 0.066125 | 0.066418 | 0.066712 | 43164.5707 | 8808.5815 | 36435.2095 | 7435.3227 | 5995.3245 | 7771.2665 | 1422996.8349 | 6256.6605
| LV008-15406413 | 68 | LV008 | LV | South | 1236293.7969 | 0.0020294 | 0.0020449 | 0.0020524 | 0.0020552 | 0.002056 | 0.0020622 | 0.0020847 | 0.0021147 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43164.5707 | 8808.5815 | 0 | 0 | 0 | 0 | 1290183.7969 | 0
| LV008-24612803 | 43 | LV008 | LV | South | 781774.0187 | 0.0020294 | 0.0020449 | 0.0020524 | 0.0020552 | 0.002056 | 0.0020622 | 0.0020847 | 0.0021147 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.025564 | 0.025864 | 0.026164 | 0.026465 | 0.026765 | 0.026731 | 0.026696 | 0.026662 | 0.026628 | 0.026593 | 0.026559 | 0.026525 | 0.02649 | 0.026456 | 0.026422 | 0.026387 | 0.026353 | 0.026319 | 0.026285 | 0.02625 | 0.0014443 | 0.0014724 | 0.001495 | 0.0015142 | 0.001532 | 0.0015346 | 0.0015494 | 0.0015697 | 0.0015712 | 0.0015692 | 0.0015671 | 0.0015651 | 0.0015631 | 0.0015611 | 0.001559 | 0.001557 | 0.001555 | 0.001553 | 0.001551 | 0.0015489 | 43164.5707 | 8808.5815 | 959.0937 | 195.722 | 82.6031 | 107.0719 | 815851.5187 | 86.2038
| LV008-24612817 | 47 | LV008 | LV | South | 854497.1832 | 0.0020294 | 0.0020449 | 0.0020524 | 0.0020552 | 0.002056 | 0.0020622 | 0.0020847 | 0.0021147 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0021195 | 0.0099925 | 0.010055 | 0.010117 | 0.010179 | 0.010242 | 0.01028 | 0.010318 | 0.010356 | 0.010394 | 0.010432 | 0.01047 | 0.010508 | 0.010546 | 0.010584 | 0.010622 | 0.01066 | 0.010698 | 0.010736 | 0.010774 | 0.010812 | 0.00056455 | 0.0005724 | 0.00057807 | 0.00058242 | 0.00058621 | 0.00059017 | 0.00059881 | 0.00060968 | 0.0006133 | 0.00061555 | 0.00061779 | 0.00062004 | 0.00062228 | 0.00062453 | 0.00062678 | 0.00062902 | 0.00063127 | 0.00063351 | 0.00063576 | 0.000638 | 43164.5707 | 8808.5815 | 377.6849 | 77.074 | 371.0768 | 480.9976 | 891744.6832 | 387.252
| LV009-15406766 | 138 | LV009 | LV | South | 2508949.1761 | 0.001057 | 0.0010456 | 0.0010315 | 0.0010182 | 0.00099971 | 0.00098356 | 0.00097598 | 0.00096597 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43164.5707 | 8808.5815 | 0 | 0 | 0 | 0 | 2618314.1761 | 0
| LV009-155428316 | 194 | LV009 | LV | South | 3527073.4795 | 0.001057 | 0.0010456 | 0.0010315 | 0.0010182 | 0.00099971 | 0.00098356 | 0.00097598 | 0.00096597 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43164.5707 | 8808.5815 | 0 | 0 | 0 | 0 | 3680818.4795 | 0
| LV009-24611519 | 52 | LV009 | LV | South | 945401.1388 | 0.001057 | 0.0010456 | 0.0010315 | 0.0010182 | 0.00099971 | 0.00098356 | 0.00097598 | 0.00096597 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0.00095267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43164.5707 | 8808.5815 | 0 | 0 | 0 | 0 | 986611.1388 | 0
| LV010-15437621 | 21 | LV010 | LV | South | 381796.6138 | 0.0012741 | 0.0012643 | 0.0012563 | 0.0012489 | 0.0012402 | 0.0012354 | 0.0012391 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.0012471 | 0.020837 | 0.021004 | 0.02117 | 0.021337 | 0.021503 | 0.021604 | 0.021705 | 0.021807 | 0.021908 | 0.022009 | 0.02211 | 0.022211 | 0.022312 | 0.022414 | 0.022515 | 0.022616 | 0.022717 | 0.022818 | 0.02292 | 0.023021 | 0.00073913 | 0.0007393 | 0.00074046 | 0.00074188 | 0.00074245 | 0.00074305 | 0.00074877 | 0.0007571 | 0.00076061 | 0.00076412 | 0.00076763 | 0.00077115 | 0.00077466 | 0.00077817 | 0.00078169 | 0.0007852 | 0.00078871 | 0.00079222 | 0.00079574 | 0.00079925 | 43164.5707 | 8808.5815 | 475.3472 | 97.004 | 44.8133 | 58.0879 | 398439.1138 | 46.7667
| LVN021-15436461 | 74 | LVN021 | LVN | South | 1345378.5437 | 0.17319 | 0.18084 | 0.18764 | 0.19364 | 0.19804 | 0.20297 | 0.20925 | 0.21551 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.00066029 | 0.00066747 | 0.00067464 | 0.00068182 | 0.000689 | 0.00068847 | 0.00068794 | 0.00068741 | 0.00068688 | 0.00068635 | 0.00068582 | 0.00068529 | 0.00068476 | 0.00068423 | 0.0006837 | 0.00068317 | 0.00068264 | 0.00068211 | 0.00068158 | 0.00068105 | 0.0031836 | 0.0033604 | 0.0035243 | 0.0036757 | 0.0037987 | 0.0038904 | 0.0040075 | 0.0041243 | 0.0041956 | 0.0041924 | 0.0041892 | 0.0041859 | 0.0041827 | 0.0041795 | 0.0041762 | 0.004173 | 0.0041697 | 0.0041665 | 0.0041633 | 0.00416 | 33157.0777 | 2522.2471 | 1885.9237 | 143.4615 | 250.1781 | 324.2861 | 1404023.5437 | 261.0833
| LVN022-131932324 | 166 | LVN022 | LVN | South | 3018011.3278 | 0.0013971 | 0.0014102 | 0.0014187 | 0.0014225 | 0.0014182 | 0.0014198 | 0.001435 | 0.0014562 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.067567 | 0.068297 | 0.069026 | 0.069756 | 0.070485 | 0.070115 | 0.069745 | 0.069375 | 0.069005 | 0.068635 | 0.068265 | 0.067895 | 0.067525 | 0.067155 | 0.066785 | 0.066415 | 0.066045 | 0.065675 | 0.065305 | 0.064935 | 0.002628 | 0.0026814 | 0.0027263 | 0.0027625 | 0.0027829 | 0.0027715 | 0.0027863 | 0.0028126 | 0.0028065 | 0.0027915 | 0.0027764 | 0.0027614 | 0.0027463 | 0.0027313 | 0.0027162 | 0.0027012 | 0.0026862 | 0.0026711 | 0.0026561 | 0.002641 | 33157.0777 | 2522.2471 | 1311.0286 | 99.7295 | 1607.4439 | 2083.6028 | 3149566.3278 | 1677.5123
| LVN022-15436485 | 201 | LVN022 | LVN | South | 3654339.0174 | 0.0013971 | 0.0014102 | 0.0014187 | 0.0014225 | 0.0014182 | 0.0014198 | 0.001435 | 0.0014562 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.43606 | 0.44118 | 0.4463 | 0.45141 | 0.45653 | 0.45594 | 0.45535 | 0.45476 | 0.45417 | 0.45358 | 0.45299 | 0.4524 | 0.45181 | 0.45121 | 0.45062 | 0.45003 | 0.44944 | 0.44885 | 0.44826 | 0.44767 | 0.016961 | 0.017321 | 0.017627 | 0.017877 | 0.018025 | 0.018023 | 0.018191 | 0.018437 | 0.018472 | 0.018448 | 0.018424 | 0.0184 | 0.018376 | 0.018352 | 0.018328 | 0.018304 | 0.01828 | 0.018256 | 0.018231 | 0.018207 | 33157.0777 | 2522.2471 | 8663.3731 | 659.0197 | 5033.3784 | 6524.3716 | 3813631.5174 | 5252.7832
| LVN022-155325443 | 120 | LVN022 | LVN | South | 2181694.9358 | 0.0013971 | 0.0014102 | 0.0014187 | 0.0014225 | 0.0014182 | 0.0014198 | 0.001435 | 0.0014562 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0.0014609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33157.0777 | 2522.2471 | 0 | 0 | 0 | 0 | 2276794.9358 | 0
| LVN023-15436448 | 79 | LVN023 | LVN | South | 1436282.4994 | 0.041281 | 0.042139 | 0.043007 | 0.043632 | 0.044116 | 0.044768 | 0.045652 | 0.046464 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0.046877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33157.0777 | 2522.2471 | 0 | 0 | 0 | 0 | 1498889.9994 | 0
| LVN024-15436435 | 28 | LVN024 | LVN | South | 509062.1517 | 0.10655 | 0.11162 | 0.11607 | 0.12019 | 0.12375 | 0.12723 | 0.13111 | 0.13505 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.13836 | 0.0042597 | 0.0043058 | 0.0043519 | 0.0043981 | 0.0044442 | 0.0044418 | 0.0044393 | 0.0044369 | 0.0044345 | 0.004432 | 0.0044296 | 0.0044272 | 0.0044248 | 0.0044223 | 0.0044199 | 0.0044175 | 0.004415 | 0.0044126 | 0.0044102 | 0.0044077 | 0.012635 | 0.01338 | 0.014063 | 0.014717 | 0.015311 | 0.015733 | 0.016204 | 0.016681 | 0.017081 | 0.017072 | 0.017063 | 0.017053 | 0.017044 | 0.017035 | 0.017025 | 0.017016 | 0.017007 | 0.016997 | 0.016988 | 0.016979 | 33157.0777 | 2522.2471 | 7633.7914 | 580.6998 | 599.9747 | 777.7 | 531252.1517 | 626.1276
| LVN031-15432398 | 48 | LVN031 | LVN | South | 872677.9743 | 0.24551 | 0.25452 | 0.25794 | 0.26107 | 0.26319 | 0.26555 | 0.26878 | 0.27216 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0.27452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33157.0777 | 2522.2471 | 0 | 0 | 0 | 0 | 910717.9743 | 0
| LVN032-15432411 | 188 | LVN032 | LVN | South | 3417988.7327 | 0.032544 | 0.033762 | 0.034244 | 0.034692 | 0.035087 | 0.035502 | 0.036056 | 0.036665 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0.037133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33157.0777 | 2522.2471 | 0 | 0 | 0 | 0 | 3566978.7327 | 0
| LVN033-15432424 | 158 | LVN033 | LVN | South | 2872564.9988 | 0.027343 | 0.027797 | 0.02839 | 0.028644 | 0.028698 | 0.029162 | 0.029933 | 0.030505 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0.030365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33157.0777 | 2522.2471 | 0 | 0 | 0 | 0 | 2997779.9988 | 0
| LVN034-15432437 | 136 | LVN034 | LVN | South | 2472587.5939 | 0.050685 | 0.051338 | 0.051968 | 0.05238 | 0.052625 | 0.053088 | 0.05381 | 0.054514 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0.054806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33157.0777 | 2522.2471 | 0 | 0 | 0 | 0 | 2580367.5939 | 0
| MBN012-15419426 | 38 | MBN012 | MBN | North | 895520.3953 | 0.0020762 | 0.0021077 | 0.0021315 | 0.0021496 | 0.0021564 | 0.0021658 | 0.0021931 | 0.0022238 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 40.9228 | 41.1687 | 41.4146 | 41.6606 | 41.9065 | 41.8939 | 41.8813 | 41.8687 | 41.8561 | 41.8434 | 41.8308 | 41.8182 | 41.8056 | 41.793 | 41.7804 | 41.7678 | 41.7552 | 41.7426 | 41.73 | 41.7174 | 2.3654 | 2.4157 | 2.4576 | 2.4932 | 2.5158 | 2.5261 | 2.5571 | 2.5921 | 2.6084 | 2.6076 | 2.6068 | 2.606 | 2.6052 | 2.6044 | 2.6037 | 2.6029 | 2.6021 | 2.6013 | 2.6005 | 2.5997 | 26769.2377 | 4430.175 | 985677.1798 | 163124.6436 | 217447.8719 | 217447.8719 | 895520.3953 | 217447.8719
| MBN012-15419437 | 0 | MBN012 | MBN | North | 0 | 0.0020762 | 0.0021077 | 0.0021315 | 0.0021496 | 0.0021564 | 0.0021658 | 0.0021931 | 0.0022238 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0.0022384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26769.2377 | 4430.175 | 0 | 0 | 0 | 0 | 0 | 0
| MBN013-15419363 | 104 | MBN013 | MBN | North | 2450897.9239 | 0.0023136 | 0.0023291 | 0.0023308 | 0.0023308 | 0.0023061 | 0.0022947 | 0.0023061 | 0.0023251 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 1.226 | 1.2341 | 1.2422 | 1.2503 | 1.2584 | 1.2597 | 1.261 | 1.2623 | 1.2636 | 1.2649 | 1.2661 | 1.2674 | 1.2687 | 1.27 | 1.2713 | 1.2726 | 1.2739 | 1.2752 | 1.2764 | 1.2777 | 0.078971 | 0.080025 | 0.08061 | 0.081135 | 0.080795 | 0.080475 | 0.08096 | 0.081709 | 0.081125 | 0.081208 | 0.081291 | 0.081373 | 0.081456 | 0.081539 | 0.081621 | 0.081704 | 0.081786 | 0.081869 | 0.081952 | 0.082034 | 26769.2377 | 4430.175 | 31373.5623 | 5192.1677 | 61288.9474 | 61288.9474 | 2450897.9239 | 61288.9474
| MBN013-182964938 | 74 | MBN013 | MBN | North | 1743908.1382 | 0.0023136 | 0.0023291 | 0.0023308 | 0.0023308 | 0.0023061 | 0.0022947 | 0.0023061 | 0.0023251 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.45244 | 0.45567 | 0.4589 | 0.46213 | 0.46537 | 0.46483 | 0.4643 | 0.46377 | 0.46324 | 0.4627 | 0.46217 | 0.46164 | 0.46111 | 0.46058 | 0.46004 | 0.45951 | 0.45898 | 0.45845 | 0.45791 | 0.45738 | 0.029142 | 0.029547 | 0.029779 | 0.029988 | 0.029878 | 0.029695 | 0.02981 | 0.03002 | 0.029741 | 0.029707 | 0.029673 | 0.029639 | 0.029605 | 0.02957 | 0.029536 | 0.029502 | 0.029468 | 0.029434 | 0.0294 | 0.029365 | 26769.2377 | 4430.175 | 11472.1743 | 1898.5875 | 65243.3251 | 65243.3251 | 1743908.1382 | 65243.3251
| MBN013-24605754 | 80 | MBN013 | MBN | North | 1885306.0953 | 0.0023136 | 0.0023291 | 0.0023308 | 0.0023308 | 0.0023061 | 0.0022947 | 0.0023061 | 0.0023251 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 0.0023061 | 3.7178 | 3.7423 | 3.7668 | 3.7913 | 3.8158 | 3.8107 | 3.8056 | 3.8005 | 3.7954 | 3.7902 | 3.7851 | 3.78 | 3.7749 | 3.7698 | 3.7647 | 3.7596 | 3.7545 | 3.7494 | 3.7443 | 3.7392 | 0.23947 | 0.24266 | 0.24443 | 0.24602 | 0.24499 | 0.24344 | 0.24433 | 0.24601 | 0.24367 | 0.24335 | 0.24302 | 0.24269 | 0.24236 | 0.24203 | 0.24171 | 0.24138 | 0.24105 | 0.24072 | 0.24039 | 0.24007 | 26769.2377 | 4430.175 | 94006.4538 | 15557.598 | 294328.4173 | 294328.4173 | 1885306.0953 | 294328.4173
| MBN014-15419313 | 212 | MBN014 | MBN | North | 4996061.1527 | 0.0029253 | 0.0029521 | 0.0029713 | 0.0029713 | 0.0029459 | 0.0029349 | 0.002954 | 0.0029842 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 2.0916 | 2.1058 | 2.1199 | 2.1341 | 2.1483 | 2.1497 | 2.1511 | 2.1525 | 2.154 | 2.1554 | 2.1568 | 2.1583 | 2.1597 | 2.1611 | 2.1625 | 2.164 | 2.1654 | 2.1668 | 2.1683 | 2.1697 | 0.17034 | 0.17307 | 0.17536 | 0.17653 | 0.17619 | 0.17564 | 0.17691 | 0.17883 | 0.17752 | 0.17763 | 0.17775 | 0.17787 | 0.17799 | 0.17811 | 0.17822 | 0.17834 | 0.17846 | 0.17858 | 0.17869 | 0.17881 | 26769.2377 | 4430.175 | 68392.6134 | 11318.6355 | 154673.8868 | 154673.8868 | 4996061.1527 | 154673.8868
| MBN014-160652409 | 26 | MBN014 | MBN | North | 612724.481 | 0.0029253 | 0.0029521 | 0.0029713 | 0.0029713 | 0.0029459 | 0.0029349 | 0.002954 | 0.0029842 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0018281 | 0.001841 | 0.0018539 | 0.0018668 | 0.0018797 | 0.0018766 | 0.0018735 | 0.0018703 | 0.0018672 | 0.0018641 | 0.0018609 | 0.0018578 | 0.0018546 | 0.0018515 | 0.0018484 | 0.0018452 | 0.0018421 | 0.001839 | 0.0018358 | 0.0018327 | 0.00014888 | 0.00015131 | 0.00015336 | 0.00015442 | 0.00015416 | 0.00015333 | 0.00015407 | 0.00015539 | 0.00015388 | 0.00015362 | 0.00015336 | 0.00015311 | 0.00015285 | 0.00015259 | 0.00015233 | 0.00015207 | 0.00015181 | 0.00015155 | 0.0001513 | 0.00015104 | 26769.2377 | 4430.175 | 59.1303 | 9.7858 | 2054.8253 | 2054.8253 | 612724.481 | 2054.8253
| MBN014-24605768 | 145 | MBN014 | MBN | North | 3417117.2978 | 0.0029253 | 0.0029521 | 0.0029713 | 0.0029713 | 0.0029459 | 0.0029349 | 0.002954 | 0.0029842 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.0029602 | 0.3354 | 0.33777 | 0.34015 | 0.34253 | 0.3449 | 0.34448 | 0.34405 | 0.34362 | 0.34319 | 0.34276 | 0.34233 | 0.3419 | 0.34148 | 0.34105 | 0.34062 | 0.34019 | 0.33976 | 0.33933 | 0.3389 | 0.33848 | 0.027315 | 0.02776 | 0.028137 | 0.028334 | 0.028287 | 0.028146 | 0.028294 | 0.028548 | 0.028283 | 0.028248 | 0.028213 | 0.028177 | 0.028142 | 0.028107 | 0.028071 | 0.028036 | 0.028001 | 0.027966 | 0.02793 | 0.027895 | 26769.2377 | 4430.175 | 10872.8851 | 1799.4081 | 55009.5084 | 55009.5084 | 3417117.2978 | 55009.5084
| MBN023-94547225 | 0 | MBN023 | MBN | North | 0 | 0.0019337 | 0.0019351 | 0.0019254 | 0.0019121 | 0.0018903 | 0.0018736 | 0.001869 | 0.0018675 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.023042 | 0.0012405 | 0.0012414 | 0.0012351 | 0.0012266 | 0.0012126 | 0.0012019 | 0.001199 | 0.001198 | 0.0011899 | 0.0011899 | 0.0011899 | 0.0011899 | 0.0011899 | 0.0011899 | 0.0011899 | 0.0011899 | 0.0011899 | 0.0011899 | 0.0011899 | 0.0011899 | 26769.2377 | 4430.175 | 0 | 0 | 0 | 0 | 0 | 0
| MBN023-94547273 | 176 | MBN023 | MBN | North | 4147673.4098 | 0.0019337 | 0.0019351 | 0.0019254 | 0.0019121 | 0.0018903 | 0.0018736 | 0.001869 | 0.0018675 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 0.0018548 | 143.1799 | 144.1634 | 145.1469 | 146.1303 | 147.1138 | 147.0112 | 146.9087 | 146.8061 | 146.7035 | 146.6009 | 146.4984 | 146.3958 | 146.2932 | 146.1907 | 146.0881 | 145.9855 | 145.8829 | 145.7804 | 145.6778 | 145.5752 | 7.7081 | 7.7666 | 7.7802 | 7.779 | 7.7421 | 7.6681 | 7.6441 | 7.6325 | 7.5756 | 7.5703 | 7.565 | 7.5597 | 7.5544 | 7.5491 | 7.5438 | 7.5385 | 7.5332 | 7.5279 | 7.5226 | 7.5173 | 26769.2377 | 4430.175 | 2953492.1 | 488788.1714 | 2672648.861 | 2672648.861 | 4147673.4098 | 2672648.861
| MBN031-140147987 | 0 | MBN031 | MBN | North | 0 | 0.0042721 | 0.0043216 | 0.0043378 | 0.0043378 | 0.0043074 | 0.0042862 | 0.0043166 | 0.0043611 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26769.2377 | 4430.175 | 0 | 0 | 0 | 0 | 0 | 0
| MBN031-140148011 | 123 | MBN031 | MBN | North | 2898658.1216 | 0.0042721 | 0.0043216 | 0.0043378 | 0.0043378 | 0.0043074 | 0.0042862 | 0.0043166 | 0.0043611 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.60027 | 0.60461 | 0.60895 | 0.61328 | 0.61762 | 0.61694 | 0.61626 | 0.61558 | 0.61491 | 0.61423 | 0.61355 | 0.61287 | 0.6122 | 0.61152 | 0.61084 | 0.61016 | 0.60949 | 0.60881 | 0.60813 | 0.60745 | 0.071393 | 0.072742 | 0.073539 | 0.074063 | 0.074064 | 0.073618 | 0.074059 | 0.074741 | 0.074223 | 0.074141 | 0.074059 | 0.073977 | 0.073895 | 0.073814 | 0.073732 | 0.07365 | 0.073568 | 0.073487 | 0.073405 | 0.073323 | 26769.2377 | 4430.175 | 28502.5935 | 4717.0367 | 36840.7082 | 36840.7082 | 2898658.1216 | 36840.7082
| MBN031-162765180 | 6 | MBN031 | MBN | North | 141397.9572 | 0.0042721 | 0.0043216 | 0.0043378 | 0.0043378 | 0.0043074 | 0.0042862 | 0.0043166 | 0.0043611 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 1.37e-07 | 1.38e-07 | 1.39e-07 | 1.4e-07 | 1.41e-07 | 1.4105e-07 | 1.411e-07 | 1.4115e-07 | 1.412e-07 | 1.4125e-07 | 1.413e-07 | 1.4135e-07 | 1.414e-07 | 1.4145e-07 | 1.415e-07 | 1.4155e-07 | 1.416e-07 | 1.4165e-07 | 1.417e-07 | 1.4175e-07 | 1.6294e-08 | 1.6603e-08 | 1.6786e-08 | 1.6907e-08 | 1.6909e-08 | 1.6831e-08 | 1.6957e-08 | 1.7138e-08 | 1.7044e-08 | 1.705e-08 | 1.7056e-08 | 1.7062e-08 | 1.7068e-08 | 1.7074e-08 | 1.708e-08 | 1.7086e-08 | 1.7092e-08 | 1.7098e-08 | 1.7104e-08 | 1.711e-08 | 26769.2377 | 4430.175 | 0.0065548 | 0.0010848 | 0.28744 | 0.28744 | 141397.9572 | 0.28744
| MBN031-24605740 | 114 | MBN031 | MBN | North | 2686561.1859 | 0.0042721 | 0.0043216 | 0.0043378 | 0.0043378 | 0.0043074 | 0.0042862 | 0.0043166 | 0.0043611 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.30136 | 0.30338 | 0.3054 | 0.30742 | 0.30944 | 0.30913 | 0.30882 | 0.30851 | 0.3082 | 0.30789 | 0.30758 | 0.30727 | 0.30696 | 0.30665 | 0.30634 | 0.30603 | 0.30572 | 0.30541 | 0.3051 | 0.30479 | 0.035843 | 0.036501 | 0.036882 | 0.037126 | 0.037108 | 0.036888 | 0.037113 | 0.037458 | 0.037202 | 0.037164 | 0.037127 | 0.03709 | 0.037052 | 0.037015 | 0.036977 | 0.03694 | 0.036902 | 0.036865 | 0.036828 | 0.03679 | 26769.2377 | 4430.175 | 14292.1517 | 2365.2796 | 134547.0035 | 134547.0035 | 2686561.1859 | 134547.0035
| MBN031-52301620 | 129 | MBN031 | MBN | North | 3040056.0787 | 0.0042721 | 0.0043216 | 0.0043378 | 0.0043378 | 0.0043074 | 0.0042862 | 0.0043166 | 0.0043611 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.0043357 | 0.35891 | 0.36093 | 0.36296 | 0.36498 | 0.36701 | 0.36618 | 0.36535 | 0.36453 | 0.3637 | 0.36287 | 0.36204 | 0.36122 | 0.36039 | 0.35956 | 0.35873 | 0.3579 | 0.35708 | 0.35625 | 0.35542 | 0.35459 | 0.042687 | 0.043425 | 0.043833 | 0.044077 | 0.044011 | 0.043696 | 0.043906 | 0.044259 | 0.0439 | 0.043801 | 0.043701 | 0.043601 | 0.043501 | 0.043401 | 0.043301 | 0.043201 | 0.043101 | 0.043001 | 0.042901 | 0.042801 | 26769.2377 | 4430.175 | 16854.3006 | 2789.3025 | 178551.4484 | 178551.4484 | 3040056.0787 | 178551.4484
| MBN032-140148075 | 0 | MBN032 | MBN | North | 0 | 0.0023922 | 0.0024323 | 0.0024674 | 0.0024925 | 0.0025032 | 0.0025226 | 0.0025621 | 0.002605 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26769.2377 | 4430.175 | 0 | 0 | 0 | 0 | 0 | 0
| MBN032-140148099 | 232 | MBN032 | MBN | North | 5467387.6765 | 0.0023922 | 0.0024323 | 0.0024674 | 0.0024925 | 0.0025032 | 0.0025226 | 0.0025621 | 0.002605 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 0.0026223 | 5.0923 | 5.1281 | 5.1639 | 5.1998 | 5.2356 | 5.2417 | 5.2479 | 5.254 | 5.2602 | 5.2663 | 5.2724 | 5.2786 | 5.2847 | 5.2909 | 5.297 | 5.3032 | 5.3093 | 5.3154 | 5.3216 | 5.3277 | 0.33914 | 0.34725 | 0.35473 | 0.36081 | 0.36487 | 0.36813 | 0.37432 | 0.38104 | 0.38401 | 0.38446 | 0.38491 | 0.38535 | 0.3858 | 0.38625 | 0.3867 | 0.38715 | 0.3876 | 0.38805 | 0.38849 | 0.38894 | 26769.2377 | 4430.175 | 144644.8702 | 23938.0026 | 179034.635 | 179034.635 | 5467387.6765 | 179034.635
| MDA022-15412339 | 59 | MDA022 | MDA | North | 1390413.2453 | 0.0024062 | 0.0023788 | 0.0023299 | 0.0022811 | 0.0022237 | 0.0021754 | 0.0021508 | 0.0021299 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28168.2367 | 4041.4977 | 0 | 0 | 0 | 0 | 1390413.2453 | 0
| MDA022-15412350 | 0 | MDA022 | MDA | North | 0 | 0.0024062 | 0.0023788 | 0.0023299 | 0.0022811 | 0.0022237 | 0.0021754 | 0.0021508 | 0.0021299 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28168.2367 | 4041.4977 | 0 | 0 | 0 | 0 | 0 | 0
| MDA022-24605196 | 40 | MDA022 | MDA | North | 942653.0477 | 0.0024062 | 0.0023788 | 0.0023299 | 0.0022811 | 0.0022237 | 0.0021754 | 0.0021508 | 0.0021299 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0.0020952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28168.2367 | 4041.4977 | 0 | 0 | 0 | 0 | 942653.0477 | 0
| MDA023-15412302 | 303 | MDA023 | MDA | North | 7140596.8361 | 0.0026652 | 0.0027769 | 0.0027918 | 0.0028026 | 0.0027932 | 0.0027928 | 0.0028157 | 0.0028437 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 21.2679 | 21.3972 | 21.5264 | 21.6557 | 21.7849 | 21.7944 | 21.8038 | 21.8132 | 21.8226 | 21.832 | 21.8414 | 21.8508 | 21.8602 | 21.8696 | 21.8791 | 21.8885 | 21.8979 | 21.9073 | 21.9167 | 21.9261 | 1.5781 | 1.6542 | 1.6731 | 1.6897 | 1.6941 | 1.6945 | 1.7091 | 1.7269 | 1.7263 | 1.7271 | 1.7278 | 1.7286 | 1.7293 | 1.7301 | 1.7308 | 1.7315 | 1.7323 | 1.733 | 1.7338 | 1.7345 | 28168.2367 | 4041.4977 | 693685.8222 | 99528.0492 | 756015.5597 | 756015.5597 | 7140596.8361 | 756015.5597
| MDA023-24605266 | 304 | MDA023 | MDA | North | 7164163.1623 | 0.0026652 | 0.0027769 | 0.0027918 | 0.0028026 | 0.0027932 | 0.0027928 | 0.0028157 | 0.0028437 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 0.0028415 | 2.4921 | 2.5084 | 2.5247 | 2.5411 | 2.5574 | 2.5587 | 2.5599 | 2.5612 | 2.5625 | 2.5638 | 2.5651 | 2.5663 | 2.5676 | 2.5689 | 2.5702 | 2.5715 | 2.5727 | 2.574 | 2.5753 | 2.5766 | 0.18491 | 0.19392 | 0.19623 | 0.19827 | 0.19887 | 0.19894 | 0.20067 | 0.20277 | 0.20271 | 0.20281 | 0.20292 | 0.20302 | 0.20312 | 0.20322 | 0.20332 | 0.20342 | 0.20352 | 0.20362 | 0.20373 | 0.20383 | 28168.2367 | 4041.4977 | 81437.9943 | 11684.4895 | 354985.5556 | 354985.5556 | 7164163.1623 | 354985.5556
| MDA024-15412265 | 142 | MDA024 | MDA | North | 3346418.3192 | 0.0030291 | 0.0029887 | 0.0029172 | 0.0028685 | 0.0028163 | 0.0027759 | 0.0027608 | 0.002746 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 0.0027071 | 16.2463 | 16.3351 | 16.4238 | 16.5126 | 16.6013 | 16.6012 | 16.6011 | 16.601 | 16.6009 | 16.6008 | 16.6007 | 16.6006 | 16.6005 | 16.6004 | 16.6003 | 16.6002 | 16.6001 | 16.6 | 16.5999 | 16.5998 | 1.3701 | 1.3592 | 1.3339 | 1.3187 | 1.3017 | 1.283 | 1.276 | 1.2691 | 1.2511 | 1.2511 | 1.2511 | 1.2511 | 1.2511 | 1.2511 | 1.2511 | 1.2511 | 1.2511 | 1.2511 | 1.2511 | 1.2511 | 28168.2367 | 4041.4977 | 522479.5055 | 74963.8586 | 605004.9658 | 605004.9658 | 3346418.3192 | 605004.9658
| MDA031-15412215 | 108 | MDA031 | MDA | North | 2545163.2287 | 0.0015123 | 0.0014962 | 0.0014782 | 0.0014579 | 0.0014358 | 0.0014181 | 0.0014121 | 0.001411 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.001396 | 0.0087658 | 0.008827 | 0.0088883 | 0.0089495 | 0.0090108 | 0.0090079 | 0.0090051 | 0.0090022 | 0.0089994 | 0.0089965 | 0.0089937 | 0.0089908 | 0.008988 | 0.0089851 | 0.0089823 | 0.0089794 | 0.0089766 | 0.0089738 | 0.0089709 | 0.0089681 | 0.00036905 | 0.00036768 | 0.00036579 | 0.00036325 | 0.00036018 | 0.00035564 | 0.00035401 | 0.00035363 | 0.00034976 | 0.00034964 | 0.00034953 | 0.00034942 | 0.00034931 | 0.0003492 | 0.00034909 | 0.00034898 | 0.00034887 | 0.00034876 | 0.00034865 | 0.00034854 | 28168.2367 | 4041.4977 | 144.6656 | 20.7562 | 173.7441 | 173.7441 | 2545163.2287 | 173.7441
| MDA032-15412191 | 132 | MDA032 | MDA | North | 3110755.0573 | 0.0017563 | 0.0017594 | 0.0017554 | 0.001746 | 0.0017266 | 0.0017142 | 0.0017142 | 0.0017189 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.0017049 | 0.97221 | 0.97554 | 0.97886 | 0.98219 | 0.98552 | 0.98269 | 0.97987 | 0.97705 | 0.97423 | 0.97141 | 0.96859 | 0.96576 | 0.96294 | 0.96012 | 0.9573 | 0.95448 | 0.95166 | 0.94883 | 0.94601 | 0.94319 | 0.047537 | 0.047782 | 0.047837 | 0.047744 | 0.047373 | 0.046898 | 0.046763 | 0.046756 | 0.04624 | 0.046106 | 0.045972 | 0.045838 | 0.045705 | 0.045571 | 0.045437 | 0.045303 | 0.045169 | 0.045035 | 0.044901 | 0.044767 | 28168.2367 | 4041.4977 | 18911.1499 | 2713.3175 | 20388.7547 | 20388.7547 | 3110755.0573 | 20388.7547
| MDA033-15412154 | 32 | MDA033 | MDA | North | 754122.4381 | 0.0016825 | 0.0016985 | 0.0017146 | 0.0017226 | 0.0017266 | 0.0017399 | 0.0017599 | 0.001776 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0.00178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28168.2367 | 4041.4977 | 0 | 0 | 0 | 0 | 754122.4381 | 0
| MDA034-15433030 | 15 | MDA034 | MDA | North | 353494.8929 | 0.0017806 | 0.0018029 | 0.0018187 | 0.0018309 | 0.0018329 | 0.0018413 | 0.0018648 | 0.0018902 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0.0018986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28168.2367 | 4041.4977 | 0 | 0 | 0 | 0 | 353494.8929 | 0
| MLN011-196478975 | 115 | MLN011 | MLN | South | 2090790.9801 | 0.0010931 | 0.0011521 | 0.0012339 | 0.0013136 | 0.0013902 | 0.0014787 | 0.0015767 | 0.0016673 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43485.2798 | 9106.3944 | 0 | 0 | 0 | 0 | 2181928.4801 | 0
| MLN011-24613386 | 163 | MLN011 | MLN | South | 2963468.9544 | 0.0010931 | 0.0011521 | 0.0012339 | 0.0013136 | 0.0013902 | 0.0014787 | 0.0015767 | 0.0016673 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 0.0017411 | 2.6492 | 2.6722 | 2.6952 | 2.7181 | 2.7411 | 2.7496 | 2.758 | 2.7665 | 2.775 | 2.7835 | 2.7919 | 2.8004 | 2.8089 | 2.8173 | 2.8258 | 2.8343 | 2.8427 | 2.8512 | 2.8597 | 2.8681 | 0.080623 | 0.085707 | 0.092583 | 0.099402 | 0.10609 | 0.11319 | 0.12107 | 0.12841 | 0.13451 | 0.13492 | 0.13533 | 0.13574 | 0.13615 | 0.13656 | 0.13697 | 0.13738 | 0.13779 | 0.1382 | 0.13861 | 0.13903 | 43485.2798 | 9106.3944 | 75408.8026 | 15791.6036 | 27814.5084 | 36053.7544 | 3092646.4544 | 29026.9418
| MLN012-196479104 | 57 | MLN012 | MLN | South | 1036305.0945 | 0.0014518 | 0.0014921 | 0.00153 | 0.0015642 | 0.0015893 | 0.0016192 | 0.0016745 | 0.0017418 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43485.2798 | 9106.3944 | 0 | 0 | 0 | 0 | 1081477.5945 | 0
| MLN012-24607519 | 262 | MLN012 | MLN | South | 4763367.2764 | 0.0014518 | 0.0014921 | 0.00153 | 0.0015642 | 0.0015893 | 0.0016192 | 0.0016745 | 0.0017418 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 1.8353 | 1.8513 | 1.8672 | 1.8831 | 1.8991 | 1.8983 | 1.8976 | 1.8969 | 1.8962 | 1.8955 | 1.8947 | 1.894 | 1.8933 | 1.8926 | 1.8919 | 1.8912 | 1.8904 | 1.8897 | 1.889 | 1.8883 | 0.074181 | 0.076902 | 0.079534 | 0.082007 | 0.084024 | 0.085577 | 0.088461 | 0.091985 | 0.094689 | 0.094654 | 0.094618 | 0.094582 | 0.094546 | 0.09451 | 0.094474 | 0.094438 | 0.094402 | 0.094366 | 0.09433 | 0.094294 | 43485.2798 | 9106.3944 | 55739.3142 | 11672.5518 | 1272796.2639 | 1649825.4511 | 4971002.2764 | 1328277.405
| MLN012-76356455 | 115 | MLN012 | MLN | South | 2090790.9801 | 0.0014518 | 0.0014921 | 0.00153 | 0.0015642 | 0.0015893 | 0.0016192 | 0.0016745 | 0.0017418 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.084954 | 0.085574 | 0.086194 | 0.086814 | 0.087434 | 0.08792 | 0.088406 | 0.088891 | 0.089377 | 0.089863 | 0.090349 | 0.090834 | 0.09132 | 0.091806 | 0.092292 | 0.092777 | 0.093263 | 0.093749 | 0.094235 | 0.09472 | 0.0034336 | 0.0035547 | 0.0036714 | 0.0037806 | 0.0038685 | 0.0039634 | 0.0041212 | 0.0043105 | 0.0044632 | 0.0044875 | 0.0045117 | 0.004536 | 0.0045602 | 0.0045845 | 0.0046087 | 0.004633 | 0.0046573 | 0.0046815 | 0.0047058 | 0.00473 | 43485.2798 | 9106.3944 | 2649.7479 | 554.8924 | 1308.4781 | 1696.077 | 2181928.4801 | 1365.5146
| MLN012-84731779 | 202 | MLN012 | MLN | South | 3672519.8086 | 0.0014518 | 0.0014921 | 0.00153 | 0.0015642 | 0.0015893 | 0.0016192 | 0.0016745 | 0.0017418 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 0.0017937 | 6.637 | 6.693 | 6.7491 | 6.8051 | 6.8612 | 6.8796 | 6.898 | 6.9164 | 6.9348 | 6.9533 | 6.9717 | 6.9901 | 7.0085 | 7.0269 | 7.0454 | 7.0638 | 7.0822 | 7.1006 | 7.119 | 7.1374 | 0.26825 | 0.27803 | 0.28748 | 0.29635 | 0.30357 | 0.31013 | 0.32156 | 0.33539 | 0.3463 | 0.34722 | 0.34814 | 0.34906 | 0.34998 | 0.3509 | 0.35182 | 0.35274 | 0.35366 | 0.35458 | 0.3555 | 0.35642 | 43485.2798 | 9106.3944 | 204710.0476 | 42868.9995 | 1396539.9316 | 1810224.6118 | 3832604.8086 | 1457415.0546
| MLN013-196479162 | 226 | MLN013 | MLN | South | 4108858.7957 | 0.0013541 | 0.0014031 | 0.0014457 | 0.0014867 | 0.0015201 | 0.0015568 | 0.0016051 | 0.0016547 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 0.001694 | 81.1172 | 81.8503 | 82.5833 | 83.3164 | 84.0495 | 84.3238 | 84.598 | 84.8723 | 85.1465 | 85.4208 | 85.695 | 85.9693 | 86.2436 | 86.5178 | 86.7921 | 87.0663 | 87.3406 | 87.6148 | 87.8891 | 88.1634 | 3.0581 | 3.1972 | 3.3239 | 3.4484 | 3.5569 | 3.6546 | 3.7803 | 3.9098 | 4.0155 | 4.0285 | 4.0414 | 4.0543 | 4.0673 | 4.0802 | 4.0931 | 4.1061 | 4.119 | 4.1319 | 4.1449 | 4.1578 | 43485.2798 | 9106.3944 | 2380168.0396 | 498438.7605 | 1003496.1366 | 1300752.9274 | 4287963.7957 | 1047238.4954
| MLN014-196479219 | 192 | MLN014 | MLN | South | 3490711.8972 | 0.0011404 | 0.0011862 | 0.0012288 | 0.0012691 | 0.0013036 | 0.0013428 | 0.0014173 | 0.0014949 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 0.0015603 | 35.3664 | 35.606 | 35.8457 | 36.0853 | 36.3249 | 36.504 | 36.683 | 36.862 | 37.0411 | 37.2201 | 37.3991 | 37.5782 | 37.7572 | 37.9362 | 38.1153 | 38.2943 | 38.4733 | 38.6524 | 38.8314 | 39.0104 | 1.1229 | 1.1759 | 1.2262 | 1.275 | 1.3183 | 1.3647 | 1.4475 | 1.5341 | 1.609 | 1.6168 | 1.6245 | 1.6323 | 1.6401 | 1.6479 | 1.6556 | 1.6634 | 1.6712 | 1.679 | 1.6867 | 1.6945 | 43485.2798 | 9106.3944 | 929939.0908 | 194741.5813 | 402935.7865 | 522293.8931 | 3642871.8972 | 420499.7422
| MLN021-196479276 | 107 | MLN021 | MLN | South | 1945344.6511 | 0.0020048 | 0.0021405 | 0.0022581 | 0.0023736 | 0.0024819 | 0.0026013 | 0.0027485 | 0.0028974 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 39.6412 | 39.0339 | 38.4265 | 37.8192 | 37.2118 | 37.3722 | 37.5326 | 37.693 | 37.8534 | 38.0138 | 38.1742 | 38.3346 | 38.495 | 38.6554 | 38.8158 | 38.9762 | 39.1366 | 39.297 | 39.4574 | 39.6178 | 2.2125 | 2.3261 | 2.4157 | 2.4991 | 2.5712 | 2.7065 | 2.872 | 3.0404 | 3.1655 | 3.179 | 3.1924 | 3.2058 | 3.2192 | 3.2326 | 3.246 | 3.2594 | 3.2729 | 3.2863 | 3.2997 | 3.3131 | 43485.2798 | 9106.3944 | 1828430.6773 | 382897.638 | 246616.6715 | 319669.7483 | 2030142.1511 | 257366.6829
| MLN021-24600176 | 122 | MLN021 | MLN | South | 2218056.518 | 0.0020048 | 0.0021405 | 0.0022581 | 0.0023736 | 0.0024819 | 0.0026013 | 0.0027485 | 0.0028974 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 0.0030038 | 46.7863 | 47.1098 | 47.4332 | 47.7566 | 48.08 | 48.1754 | 48.2707 | 48.3661 | 48.4614 | 48.5568 | 48.6521 | 48.7474 | 48.8428 | 48.9381 | 49.0335 | 49.1288 | 49.2241 | 49.3195 | 49.4148 | 49.5102 | 2.6113 | 2.8074 | 2.982 | 3.1557 | 3.3222 | 3.4889 | 3.6937 | 3.9013 | 4.0526 | 4.0606 | 4.0686 | 4.0766 | 4.0845 | 4.0925 | 4.1005 | 4.1085 | 4.1164 | 4.1244 | 4.1324 | 4.1404 | 43485.2798 | 9106.3944 | 2305891.9848 | 482884.3694 | 480033.137 | 622229.1102 | 2314741.518 | 500957.7633
| MLN022-160532221 | 220 | MLN022 | MLN | South | 3999774.0489 | 0.0022974 | 0.0023717 | 0.0024369 | 0.0024953 | 0.0025371 | 0.0025843 | 0.0026621 | 0.0027558 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 92.3378 | 93.0814 | 93.8251 | 94.5687 | 95.3123 | 95.5441 | 95.7758 | 96.0076 | 96.2394 | 96.4712 | 96.7029 | 96.9347 | 97.1665 | 97.3983 | 97.63 | 97.8618 | 98.0936 | 98.3254 | 98.5572 | 98.7889 | 5.906 | 6.1461 | 6.3654 | 6.5697 | 6.7323 | 6.8742 | 7.0984 | 7.366 | 7.5772 | 7.5954 | 7.6137 | 7.6319 | 7.6502 | 7.6684 | 7.6867 | 7.7049 | 7.7232 | 7.7414 | 7.7597 | 7.7779 | 43485.2798 | 9106.3944 | 4496090.0756 | 941540.9026 | 4703958.0155 | 6097369.921 | 4174124.0489 | 4909003.3681
| MLN022-196479342 | 180 | MLN022 | MLN | South | 3272542.4037 | 0.0022974 | 0.0023717 | 0.0024369 | 0.0024953 | 0.0025371 | 0.0025843 | 0.0026621 | 0.0027558 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 31.6552 | 31.864 | 32.0728 | 32.2815 | 32.4903 | 32.6458 | 32.8013 | 32.9567 | 33.1122 | 33.2677 | 33.4231 | 33.5786 | 33.7341 | 33.8895 | 34.045 | 34.2005 | 34.3559 | 34.5114 | 34.6668 | 34.8223 | 2.0247 | 2.1039 | 2.1759 | 2.2426 | 2.2949 | 2.3488 | 2.431 | 2.5285 | 2.607 | 2.6192 | 2.6315 | 2.6437 | 2.656 | 2.6682 | 2.6804 | 2.6927 | 2.7049 | 2.7172 | 2.7294 | 2.7416 | 43485.2798 | 9106.3944 | 1552806.6929 | 325178.3195 | 1553078.7536 | 2013133.5455 | 3415192.4037 | 1620777.398
| MLN022-83935111 | 388 | MLN022 | MLN | South | 7054146.959 | 0.0022974 | 0.0023717 | 0.0024369 | 0.0024953 | 0.0025371 | 0.0025843 | 0.0026621 | 0.0027558 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 25.706 | 25.9277 | 26.1495 | 26.3712 | 26.5929 | 26.6625 | 26.7322 | 26.8018 | 26.8715 | 26.9411 | 27.0108 | 27.0804 | 27.1501 | 27.2198 | 27.2894 | 27.3591 | 27.4287 | 27.4984 | 27.568 | 27.6377 | 1.6442 | 1.712 | 1.7741 | 1.832 | 1.8784 | 1.9183 | 1.9812 | 2.0563 | 2.1157 | 2.1211 | 2.1266 | 2.1321 | 2.1376 | 2.1431 | 2.1486 | 2.154 | 2.1595 | 2.165 | 2.1705 | 2.176 | 43485.2798 | 9106.3944 | 1255292.7585 | 262874.9551 | 7447354.51 | 9653418.5108 | 7361636.959 | 7771984.4123
| MLN022-84622495 | 18 | MLN022 | MLN | South | 327254.2404 | 0.0022974 | 0.0023717 | 0.0024369 | 0.0024953 | 0.0025371 | 0.0025843 | 0.0026621 | 0.0027558 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.002828 | 0.25778 | 0.25965 | 0.26151 | 0.26338 | 0.26524 | 0.2657 | 0.26617 | 0.26663 | 0.2671 | 0.26756 | 0.26803 | 0.26849 | 0.26895 | 0.26942 | 0.26988 | 0.27035 | 0.27081 | 0.27128 | 0.27174 | 0.2722 | 0.016488 | 0.017144 | 0.017742 | 0.018297 | 0.018735 | 0.019117 | 0.019727 | 0.020457 | 0.021029 | 0.021066 | 0.021102 | 0.021139 | 0.021175 | 0.021212 | 0.021249 | 0.021285 | 0.021322 | 0.021358 | 0.021395 | 0.021431 | 43485.2798 | 9106.3944 | 12472.7297 | 2611.955 | 84019.1522 | 108907.403 | 341519.2404 | 87681.5438
| MLN023-196479399 | 109 | MLN023 | MLN | South | 1981706.2333 | 0.0013639 | 0.0014245 | 0.0014818 | 0.0015353 | 0.001583 | 0.0016345 | 0.0016976 | 0.0017629 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0.0018268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43485.2798 | 9106.3944 | 0 | 0 | 0 | 0 | 2068088.7333 | 0
| MLN024-196479455 | 138 | MLN024 | MLN | South | 2508949.1761 | 0.0027995 | 0.002877 | 0.0029263 | 0.0029715 | 0.0030044 | 0.0030432 | 0.0031036 | 0.00317 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0.0032246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43485.2798 | 9106.3944 | 0 | 0 | 0 | 0 | 2618314.1761 | 0
| MLN032-196479760 | 220 | MLN032 | MLN | South | 3999774.0489 | 0.0011738 | 0.0012139 | 0.0012528 | 0.0012881 | 0.0013196 | 0.0013537 | 0.0013981 | 0.0014442 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 0.0014859 | 40.087 | 40.3623 | 40.6375 | 40.9128 | 41.1881 | 41.397 | 41.6059 | 41.8147 | 42.0236 | 42.2324 | 42.4413 | 42.6502 | 42.859 | 43.0679 | 43.2768 | 43.4856 | 43.6945 | 43.9034 | 44.1122 | 44.3211 | 1.31 | 1.364 | 1.4173 | 1.4672 | 1.5132 | 1.5602 | 1.6194 | 1.6812 | 1.7385 | 1.7471 | 1.7557 | 1.7644 | 1.773 | 1.7817 | 1.7903 | 1.7989 | 1.8076 | 1.8162 | 1.8249 | 1.8335 | 43485.2798 | 9106.3944 | 1029419.0091 | 215573.9958 | 630435.7046 | 817184.101 | 4174124.0489 | 657916.3731
| MLN033-196479827 | 490 | MLN033 | MLN | South | 8908587.6544 | 0.0021387 | 0.0017387 | 0.0018746 | 0.0020369 | 0.0022026 | 0.002399 | 0.0026041 | 0.002801 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 0.0029794 | 82.3312 | 82.9077 | 83.4841 | 84.0606 | 84.6371 | 84.8953 | 85.1534 | 85.4116 | 85.6698 | 85.928 | 86.1861 | 86.4443 | 86.7025 | 86.9606 | 87.2188 | 87.477 | 87.7352 | 87.9933 | 88.2515 | 88.5097 | 4.9021 | 4.0131 | 4.3568 | 4.7669 | 5.1901 | 5.6699 | 6.1735 | 6.6605 | 7.106 | 7.1275 | 7.1489 | 7.1703 | 7.1917 | 7.2131 | 7.2345 | 7.2559 | 7.2774 | 7.2988 | 7.3202 | 7.3416 | 43485.2798 | 9106.3944 | 3911074.1197 | 819030.8012 | 3241247.7395 | 4201373.9086 | 9296912.6544 | 3382533.6063
| MNA013-15432110 | 1 | MNA013 | MNA | North | 23566.3262 | 0.0073978 | 0.007374 | 0.0072972 | 0.0072181 | 0.0071214 | 0.0070507 | 0.0070207 | 0.0069877 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 2.04e-06 | 4.2015e-07 | 4.188e-07 | 4.1444e-07 | 4.0994e-07 | 4.0445e-07 | 4.0043e-07 | 3.9873e-07 | 3.9686e-07 | 3.9293e-07 | 3.9293e-07 | 3.9293e-07 | 3.9293e-07 | 3.9293e-07 | 3.9293e-07 | 3.9293e-07 | 3.9293e-07 | 3.9293e-07 | 3.9293e-07 | 3.9293e-07 | 3.9293e-07 | 28893.9194 | 3452.2697 | 0.16733 | 0.019993 | 0.34756 | 0.34756 | 23566.3262 | 0.34756
| MNA013-15432136 | 250 | MNA013 | MNA | North | 5891581.5479 | 0.0073978 | 0.007374 | 0.0072972 | 0.0072181 | 0.0071214 | 0.0070507 | 0.0070207 | 0.0069877 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 0.0069186 | 2.3066 | 2.3189 | 2.3311 | 2.3434 | 2.3556 | 2.378 | 2.4003 | 2.4227 | 2.445 | 2.4674 | 2.4897 | 2.5121 | 2.5344 | 2.5568 | 2.5791 | 2.6015 | 2.6238 | 2.6462 | 2.6685 | 2.6909 | 0.47506 | 0.47605 | 0.47358 | 0.4709 | 0.46702 | 0.46677 | 0.46916 | 0.4713 | 0.47094 | 0.47525 | 0.47955 | 0.48386 | 0.48816 | 0.49247 | 0.49677 | 0.50107 | 0.50538 | 0.50968 | 0.51399 | 0.51829 | 28893.9194 | 3452.2697 | 201572.0216 | 24083.9938 | 322868.3202 | 322868.3202 | 5891581.5479 | 322868.3202
| MNA014-138630585 | 35 | MNA014 | MNA | North | 824821.4167 | 0.0033354 | 0.0033973 | 0.0034257 | 0.0034315 | 0.0033903 | 0.0033872 | 0.0034297 | 0.0034864 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28893.9194 | 3452.2697 | 0 | 0 | 0 | 0 | 824821.4167 | 0
| MNA014-15420920 | 225 | MNA014 | MNA | North | 5302423.3932 | 0.0033354 | 0.0033973 | 0.0034257 | 0.0034315 | 0.0033903 | 0.0033872 | 0.0034297 | 0.0034864 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 17.8755 | 17.9843 | 18.093 | 18.2018 | 18.3105 | 18.4496 | 18.5887 | 18.7278 | 18.8669 | 19.006 | 19.1451 | 19.2842 | 19.4232 | 19.5623 | 19.7014 | 19.8405 | 19.9796 | 20.1187 | 20.2578 | 20.3968 | 1.6599 | 1.701 | 1.7256 | 1.7389 | 1.7283 | 1.7398 | 1.7749 | 1.8178 | 1.8164 | 1.8297 | 1.8431 | 1.8565 | 1.8699 | 1.8833 | 1.8967 | 1.9101 | 1.9235 | 1.9369 | 1.9503 | 1.9636 | 28893.9194 | 3452.2697 | 756594.7625 | 90398.5752 | 982332.3684 | 982332.3684 | 5302423.3932 | 982332.3684
| MNA014-157238172 | 21 | MNA014 | MNA | North | 494892.85 | 0.0033354 | 0.0033973 | 0.0034257 | 0.0034315 | 0.0033903 | 0.0033872 | 0.0034297 | 0.0034864 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 6.1903e-05 | 6.2177e-05 | 6.2451e-05 | 6.2726e-05 | 6.3e-05 | 6.396e-05 | 6.492e-05 | 6.588e-05 | 6.684e-05 | 6.78e-05 | 6.876e-05 | 6.972e-05 | 7.068e-05 | 7.164e-05 | 7.26e-05 | 7.356e-05 | 7.452e-05 | 7.548e-05 | 7.644e-05 | 7.74e-05 | 5.7481e-06 | 5.8808e-06 | 5.9561e-06 | 5.9924e-06 | 5.9463e-06 | 6.0315e-06 | 6.1987e-06 | 6.3944e-06 | 6.4348e-06 | 6.5272e-06 | 6.6197e-06 | 6.7121e-06 | 6.8045e-06 | 6.8969e-06 | 6.9893e-06 | 7.0818e-06 | 7.1742e-06 | 7.2666e-06 | 7.359e-06 | 7.4514e-06 | 28893.9194 | 3452.2697 | 2.703 | 0.32296 | 24.2008 | 24.2008 | 494892.85 | 24.2008
| MNA014-157238287 | 21 | MNA014 | MNA | North | 494892.85 | 0.0033354 | 0.0033973 | 0.0034257 | 0.0034315 | 0.0033903 | 0.0033872 | 0.0034297 | 0.0034864 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.00026347 | 0.00026465 | 0.00026583 | 0.00026702 | 0.0002682 | 0.00027225 | 0.0002763 | 0.00028035 | 0.0002844 | 0.00028845 | 0.0002925 | 0.00029655 | 0.0003006 | 0.00030465 | 0.0003087 | 0.00031275 | 0.0003168 | 0.00032085 | 0.0003249 | 0.00032895 | 2.4465e-05 | 2.5031e-05 | 2.5353e-05 | 2.5509e-05 | 2.5314e-05 | 2.5673e-05 | 2.6382e-05 | 2.7211e-05 | 2.738e-05 | 2.777e-05 | 2.816e-05 | 2.8549e-05 | 2.8939e-05 | 2.9329e-05 | 2.9719e-05 | 3.0109e-05 | 3.0499e-05 | 3.0889e-05 | 3.1279e-05 | 3.1669e-05 | 28893.9194 | 3452.2697 | 11.4992 | 1.3739 | 114.3961 | 114.3961 | 494892.85 | 114.3961
| MNA014-157238460 | 26 | MNA014 | MNA | North | 612724.481 | 0.0033354 | 0.0033973 | 0.0034257 | 0.0034315 | 0.0033903 | 0.0033872 | 0.0034297 | 0.0034864 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.0046686 | 0.0046919 | 0.0047152 | 0.0047386 | 0.0047619 | 0.0048091 | 0.0048562 | 0.0049034 | 0.0049505 | 0.0049976 | 0.0050448 | 0.0050919 | 0.0051391 | 0.0051862 | 0.0052334 | 0.0052805 | 0.0053277 | 0.0053748 | 0.005422 | 0.0054691 | 0.00043351 | 0.00044377 | 0.0004497 | 0.00045269 | 0.00044946 | 0.0004535 | 0.00046368 | 0.00047593 | 0.00047659 | 0.00048113 | 0.00048567 | 0.00049021 | 0.00049475 | 0.00049929 | 0.00050383 | 0.00050837 | 0.0005129 | 0.00051744 | 0.00052198 | 0.00052652 | 28893.9194 | 3452.2697 | 199.1077 | 23.7896 | 2102.3561 | 2102.3561 | 612724.481 | 2102.3561
| MNA014-163873875 | 24 | MNA014 | MNA | North | 565591.8286 | 0.0033354 | 0.0033973 | 0.0034257 | 0.0034315 | 0.0033903 | 0.0033872 | 0.0034297 | 0.0034864 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.00059657 | 0.00060103 | 0.00060549 | 0.00060994 | 0.0006144 | 0.00062184 | 0.00062928 | 0.00063672 | 0.00064416 | 0.0006516 | 0.00065904 | 0.00066648 | 0.00067392 | 0.00068136 | 0.0006888 | 0.00069624 | 0.00070368 | 0.00071112 | 0.00071856 | 0.000726 | 5.5396e-05 | 5.6846e-05 | 5.7746e-05 | 5.827e-05 | 5.7991e-05 | 5.864e-05 | 6.0085e-05 | 6.1801e-05 | 6.2014e-05 | 6.2731e-05 | 6.3447e-05 | 6.4163e-05 | 6.488e-05 | 6.5596e-05 | 6.6312e-05 | 6.7028e-05 | 6.7745e-05 | 6.8461e-05 | 6.9177e-05 | 6.9893e-05 | 28893.9194 | 3452.2697 | 25.9263 | 3.0977 | 221.0879 | 221.0879 | 565591.8286 | 221.0879
| MNA014-164469721 | 12 | MNA014 | MNA | North | 282795.9143 | 0.0033354 | 0.0033973 | 0.0034257 | 0.0034315 | 0.0033903 | 0.0033872 | 0.0034297 | 0.0034864 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 1.9863e-05 | 1.9953e-05 | 2.0042e-05 | 2.0131e-05 | 2.022e-05 | 2.0526e-05 | 2.0832e-05 | 2.1138e-05 | 2.1444e-05 | 2.175e-05 | 2.2056e-05 | 2.2362e-05 | 2.2668e-05 | 2.2974e-05 | 2.328e-05 | 2.3586e-05 | 2.3892e-05 | 2.4198e-05 | 2.4504e-05 | 2.481e-05 | 1.8445e-06 | 1.8871e-06 | 1.9114e-06 | 1.9232e-06 | 1.9085e-06 | 1.9356e-06 | 1.9891e-06 | 2.0517e-06 | 2.0645e-06 | 2.0939e-06 | 2.1234e-06 | 2.1528e-06 | 2.1823e-06 | 2.2117e-06 | 2.2412e-06 | 2.2707e-06 | 2.3001e-06 | 2.3296e-06 | 2.359e-06 | 2.3885e-06 | 28893.9194 | 3452.2697 | 0.86708 | 0.1036 | 14.7871 | 14.7871 | 282795.9143 | 14.7871
| MNA014-167870808 | 13 | MNA014 | MNA | North | 306362.2405 | 0.0033354 | 0.0033973 | 0.0034257 | 0.0034315 | 0.0033903 | 0.0033872 | 0.0034297 | 0.0034864 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.00015557 | 0.00015673 | 0.00015789 | 0.00015904 | 0.0001602 | 0.00016218 | 0.00016416 | 0.00016614 | 0.00016812 | 0.0001701 | 0.00017208 | 0.00017406 | 0.00017604 | 0.00017802 | 0.00018 | 0.00018198 | 0.00018396 | 0.00018594 | 0.00018792 | 0.0001899 | 1.4446e-05 | 1.4824e-05 | 1.5058e-05 | 1.5194e-05 | 1.5121e-05 | 1.5294e-05 | 1.5674e-05 | 1.6126e-05 | 1.6185e-05 | 1.6376e-05 | 1.6566e-05 | 1.6757e-05 | 1.6948e-05 | 1.7138e-05 | 1.7329e-05 | 1.752e-05 | 1.771e-05 | 1.7901e-05 | 1.8091e-05 | 1.8282e-05 | 28893.9194 | 3452.2697 | 6.7683 | 0.80868 | 83.3685 | 83.3685 | 306362.2405 | 83.3685
| MNA014-184029858 | 195 | MNA014 | MNA | North | 4595433.6074 | 0.0033354 | 0.0033973 | 0.0034257 | 0.0034315 | 0.0033903 | 0.0033872 | 0.0034297 | 0.0034864 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 8.4319 | 8.4722 | 8.5126 | 8.5529 | 8.5933 | 8.6674 | 8.7415 | 8.8157 | 8.8898 | 8.964 | 9.0381 | 9.1123 | 9.1864 | 9.2606 | 9.3347 | 9.4089 | 9.483 | 9.5572 | 9.6313 | 9.7055 | 0.78295 | 0.80131 | 0.81185 | 0.81708 | 0.81108 | 0.81734 | 0.83466 | 0.85567 | 0.85584 | 0.86298 | 0.87012 | 0.87726 | 0.8844 | 0.89153 | 0.89867 | 0.90581 | 0.91295 | 0.92009 | 0.92722 | 0.93436 | 28893.9194 | 3452.2697 | 357143.0896 | 42671.7551 | 654145.4453 | 654145.4453 | 4595433.6074 | 654145.4453
| MNA014-187105725 | 50 | MNA014 | MNA | North | 1178316.3096 | 0.0033354 | 0.0033973 | 0.0034257 | 0.0034315 | 0.0033903 | 0.0033872 | 0.0034297 | 0.0034864 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003947 | 0.0039702 | 0.0039935 | 0.0040167 | 0.00404 | 0.0040859 | 0.0041319 | 0.0041778 | 0.0042238 | 0.0042697 | 0.0043157 | 0.0043616 | 0.0044076 | 0.0044535 | 0.0044995 | 0.0045454 | 0.0045914 | 0.0046373 | 0.0046832 | 0.0047292 | 0.00036651 | 0.00037551 | 0.00038086 | 0.00038373 | 0.00038132 | 0.00038531 | 0.00039452 | 0.00040551 | 0.00040663 | 0.00041105 | 0.00041548 | 0.0004199 | 0.00042432 | 0.00042875 | 0.00043317 | 0.00043759 | 0.00044202 | 0.00044644 | 0.00045086 | 0.00045529 | 28893.9194 | 3452.2697 | 170.0341 | 20.3158 | 128.8405 | 128.8405 | 1178316.3096 | 128.8405
| MNA014-203082790 | 99 | MNA014 | MNA | North | 2333066.293 | 0.0033354 | 0.0033973 | 0.0034257 | 0.0034315 | 0.0033903 | 0.0033872 | 0.0034297 | 0.0034864 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.003458 | 0.62421 | 0.62787 | 0.63154 | 0.6352 | 0.63886 | 0.64452 | 0.65018 | 0.65583 | 0.66149 | 0.66715 | 0.6728 | 0.67846 | 0.68411 | 0.68977 | 0.69543 | 0.70108 | 0.70674 | 0.7124 | 0.71805 | 0.72371 | 0.057962 | 0.059385 | 0.06023 | 0.060682 | 0.0603 | 0.060779 | 0.06208 | 0.063656 | 0.063683 | 0.064227 | 0.064772 | 0.065316 | 0.065861 | 0.066406 | 0.06695 | 0.067495 | 0.068039 | 0.068584 | 0.069128 | 0.069673 | 28893.9194 | 3452.2697 | 26563.6386 | 3173.8458 | 120898.5809 | 120898.5809 | 2333066.293 | 120898.5809
| MNA021-15421016 | 152 | MNA021 | MNA | North | 3582081.5812 | 0.0024088 | 0.002399 | 0.0023798 | 0.0023417 | 0.0023163 | 0.0022924 | 0.0022897 | 0.0022842 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 30.6782 | 30.8556 | 31.0329 | 31.2103 | 31.3877 | 31.524 | 31.6604 | 31.7968 | 31.9332 | 32.0696 | 32.206 | 32.3424 | 32.4788 | 32.6152 | 32.7516 | 32.8879 | 33.0243 | 33.1607 | 33.2971 | 33.4335 | 2.0573 | 2.0608 | 2.056 | 2.0347 | 2.024 | 2.0119 | 2.0182 | 2.0221 | 2.0074 | 2.0159 | 2.0245 | 2.0331 | 2.0417 | 2.0502 | 2.0588 | 2.0674 | 2.0759 | 2.0845 | 2.0931 | 2.1017 | 28893.9194 | 3452.2697 | 854018.8172 | 102038.8828 | 919705.911 | 919705.911 | 3582081.5812 | 919705.911
| MNA021-164301884 | 327 | MNA021 | MNA | North | 7706188.6647 | 0.0024088 | 0.002399 | 0.0023798 | 0.0023417 | 0.0023163 | 0.0022924 | 0.0022897 | 0.0022842 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 0.0022579 | 25.1118 | 25.2452 | 25.3786 | 25.5119 | 25.6453 | 25.8505 | 26.0557 | 26.2609 | 26.4661 | 26.6713 | 26.8765 | 27.0817 | 27.2869 | 27.4921 | 27.6973 | 27.9025 | 28.1077 | 28.3129 | 28.5181 | 28.7233 | 1.684 | 1.686 | 1.6814 | 1.6632 | 1.6537 | 1.6498 | 1.6609 | 1.67 | 1.6637 | 1.6766 | 1.6895 | 1.7024 | 1.7153 | 1.7282 | 1.7411 | 1.754 | 1.7669 | 1.7798 | 1.7927 | 1.8056 | 28893.9194 | 3452.2697 | 710365.6319 | 84875.08 | 1872666.6255 | 1872666.6255 | 7706188.6647 | 1872666.6255
| MNA022-15421040 | 177 | MNA022 | MNA | North | 4171239.7359 | 0.0014163 | 0.0014226 | 0.0014209 | 0.0014186 | 0.0014078 | 0.0014025 | 0.0014038 | 0.0014085 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.0014055 | 0.97304 | 0.97828 | 0.98352 | 0.98876 | 0.994 | 1.0066 | 1.0192 | 1.0318 | 1.0444 | 1.057 | 1.0696 | 1.0822 | 1.0948 | 1.1074 | 1.12 | 1.1326 | 1.1452 | 1.1578 | 1.1704 | 1.183 | 0.038367 | 0.038744 | 0.038907 | 0.039051 | 0.038957 | 0.039302 | 0.039833 | 0.040458 | 0.040865 | 0.041358 | 0.041851 | 0.042344 | 0.042837 | 0.04333 | 0.043823 | 0.044316 | 0.044809 | 0.045302 | 0.045795 | 0.046288 | 28893.9194 | 3452.2697 | 17268.7916 | 2063.2897 | 29384.4409 | 29384.4409 | 4171239.7359 | 29384.4409
| MNA024-15421140 | 178 | MNA024 | MNA | North | 4194806.0621 | 0.0016306 | 0.0016567 | 0.0016762 | 0.0016926 | 0.0016987 | 0.0017149 | 0.0017461 | 0.0017779 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 51.7764 | 52.0283 | 52.2801 | 52.5319 | 52.7837 | 53.14 | 53.4962 | 53.8524 | 54.2087 | 54.5649 | 54.9212 | 55.2774 | 55.6337 | 55.9899 | 56.3461 | 56.7024 | 57.0586 | 57.4149 | 57.7711 | 58.1273 | 2.3504 | 2.3997 | 2.4397 | 2.4754 | 2.4962 | 2.537 | 2.6005 | 2.6655 | 2.7117 | 2.7296 | 2.7474 | 2.7652 | 2.783 | 2.8008 | 2.8187 | 2.8365 | 2.8543 | 2.8721 | 2.8899 | 2.9078 | 28893.9194 | 3452.2697 | 1107266.8088 | 132297.1647 | 1288037.3381 | 1288037.3381 | 4194806.0621 | 1288037.3381
| MNA024-15421151 | 0 | MNA024 | MNA | North | 0 | 0.0016306 | 0.0016567 | 0.0016762 | 0.0016926 | 0.0016987 | 0.0017149 | 0.0017461 | 0.0017779 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 0.0017968 | 2.5076e-05 | 2.5212e-05 | 2.5348e-05 | 2.5484e-05 | 2.562e-05 | 2.5959e-05 | 2.6299e-05 | 2.6638e-05 | 2.6978e-05 | 2.7317e-05 | 2.7657e-05 | 2.7996e-05 | 2.8336e-05 | 2.8675e-05 | 2.9015e-05 | 2.9354e-05 | 2.9694e-05 | 3.0033e-05 | 3.0373e-05 | 3.0712e-05 | 1.1383e-06 | 1.1629e-06 | 1.1829e-06 | 1.2009e-06 | 1.2116e-06 | 1.2394e-06 | 1.2784e-06 | 1.3185e-06 | 1.3495e-06 | 1.3665e-06 | 1.3835e-06 | 1.4005e-06 | 1.4175e-06 | 1.4345e-06 | 1.4514e-06 | 1.4684e-06 | 1.4854e-06 | 1.5024e-06 | 1.5194e-06 | 1.5364e-06 | 28893.9194 | 3452.2697 | 0 | 0 | 0 | 0 | 0 | 0
| MNA034-15421279 | 232 | MNA034 | MNA | North | 5467387.6765 | 0.00176 | 0.0017754 | 0.0017824 | 0.0017832 | 0.0017716 | 0.001767 | 0.0017805 | 0.0018002 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 37.0543 | 37.2243 | 37.3943 | 37.5644 | 37.7344 | 37.9741 | 38.2138 | 38.4535 | 38.6931 | 38.9328 | 39.1725 | 39.4122 | 39.6518 | 39.8915 | 40.1312 | 40.3709 | 40.6105 | 40.8502 | 41.0899 | 41.3296 | 1.8156 | 1.8399 | 1.8556 | 1.8649 | 1.8611 | 1.8681 | 1.8942 | 1.9272 | 1.9296 | 1.9416 | 1.9535 | 1.9655 | 1.9774 | 1.9894 | 2.0013 | 2.0133 | 2.0252 | 2.0372 | 2.0492 | 2.0611 | 28893.9194 | 3452.2697 | 805916.4769 | 96291.5749 | 1798424.7906 | 1798424.7906 | 5467387.6765 | 1798424.7906
| MNA034-157168509 | 54 | MNA034 | MNA | North | 1272581.6144 | 0.00176 | 0.0017754 | 0.0017824 | 0.0017832 | 0.0017716 | 0.001767 | 0.0017805 | 0.0018002 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.12237 | 0.1232 | 0.12403 | 0.12487 | 0.1257 | 0.12672 | 0.12775 | 0.12878 | 0.1298 | 0.13083 | 0.13186 | 0.13288 | 0.13391 | 0.13494 | 0.13596 | 0.13699 | 0.13802 | 0.13904 | 0.14007 | 0.1411 | 0.0059957 | 0.0060893 | 0.0061547 | 0.0061989 | 0.0061996 | 0.006234 | 0.0063325 | 0.0064541 | 0.0064733 | 0.0065245 | 0.0065757 | 0.0066269 | 0.0066781 | 0.0067293 | 0.0067805 | 0.0068317 | 0.0068829 | 0.0069341 | 0.0069853 | 0.0070365 | 28893.9194 | 3452.2697 | 2704.8785 | 323.1811 | 85631.1859 | 85631.1859 | 1272581.6144 | 85631.1859
| MNA034-157168656 | 54 | MNA034 | MNA | North | 1272581.6144 | 0.00176 | 0.0017754 | 0.0017824 | 0.0017832 | 0.0017716 | 0.001767 | 0.0017805 | 0.0018002 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.14559 | 0.14664 | 0.14769 | 0.14875 | 0.1498 | 0.15088 | 0.15196 | 0.15305 | 0.15413 | 0.15521 | 0.15629 | 0.15737 | 0.15846 | 0.15954 | 0.16062 | 0.1617 | 0.16279 | 0.16387 | 0.16495 | 0.16603 | 0.0071334 | 0.0072479 | 0.0073288 | 0.0073844 | 0.0073882 | 0.0074223 | 0.0075327 | 0.0076703 | 0.0076863 | 0.0077403 | 0.0077943 | 0.0078483 | 0.0079023 | 0.0079562 | 0.0080102 | 0.0080642 | 0.0081182 | 0.0081722 | 0.0082261 | 0.0082801 | 28893.9194 | 3452.2697 | 3207.9066 | 383.2834 | 72913.1025 | 72913.1025 | 1272581.6144 | 72913.1025
| MNA034-157168875 | 78 | MNA034 | MNA | North | 1838173.443 | 0.00176 | 0.0017754 | 0.0017824 | 0.0017832 | 0.0017716 | 0.001767 | 0.0017805 | 0.0018002 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.012151 | 0.012238 | 0.012324 | 0.012411 | 0.012498 | 0.012558 | 0.012618 | 0.012678 | 0.012738 | 0.012799 | 0.012859 | 0.012919 | 0.012979 | 0.013039 | 0.013099 | 0.013159 | 0.013219 | 0.013279 | 0.013339 | 0.013399 | 0.00059536 | 0.00060486 | 0.00061157 | 0.00061616 | 0.00061643 | 0.00061779 | 0.00062549 | 0.00063542 | 0.00063527 | 0.00063826 | 0.00064126 | 0.00064425 | 0.00064724 | 0.00065024 | 0.00065323 | 0.00065623 | 0.00065922 | 0.00066222 | 0.00066521 | 0.0006682 | 28893.9194 | 3452.2697 | 264.496 | 31.6022 | 12543.6354 | 12543.6354 | 1838173.443 | 12543.6354
| MNA034-175612351 | 9 | MNA034 | MNA | North | 212096.9357 | 0.00176 | 0.0017754 | 0.0017824 | 0.0017832 | 0.0017716 | 0.001767 | 0.0017805 | 0.0018002 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 9.1351e-05 | 9.1913e-05 | 9.2475e-05 | 9.3038e-05 | 9.36e-05 | 9.476e-05 | 9.592e-05 | 9.708e-05 | 9.824e-05 | 9.94e-05 | 0.00010056 | 0.00010172 | 0.00010288 | 0.00010404 | 0.0001052 | 0.00010636 | 0.00010752 | 0.00010868 | 0.00010984 | 0.000111 | 4.476e-06 | 4.5429e-06 | 4.5888e-06 | 4.6188e-06 | 4.6165e-06 | 4.6616e-06 | 4.7547e-06 | 4.8655e-06 | 4.8992e-06 | 4.9571e-06 | 5.0149e-06 | 5.0728e-06 | 5.1306e-06 | 5.1885e-06 | 5.2463e-06 | 5.3042e-06 | 5.362e-06 | 5.4199e-06 | 5.4777e-06 | 5.5356e-06 | 28893.9194 | 3452.2697 | 2.0563 | 0.24569 | 37.9721 | 37.9721 | 212096.9357 | 37.9721
| MNA034-181657157 | 231 | MNA034 | MNA | North | 5443821.3503 | 0.00176 | 0.0017754 | 0.0017824 | 0.0017832 | 0.0017716 | 0.001767 | 0.0017805 | 0.0018002 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 25.755 | 25.8934 | 26.0318 | 26.1703 | 26.3087 | 26.4047 | 26.5007 | 26.5966 | 26.6926 | 26.7886 | 26.8846 | 26.9806 | 27.0766 | 27.1726 | 27.2686 | 27.3645 | 27.4605 | 27.5565 | 27.6525 | 27.7485 | 1.2619 | 1.2798 | 1.2918 | 1.2992 | 1.2976 | 1.2989 | 1.3136 | 1.333 | 1.3312 | 1.3359 | 1.3407 | 1.3455 | 1.3503 | 1.3551 | 1.3599 | 1.3647 | 1.3695 | 1.3742 | 1.379 | 1.3838 | 28893.9194 | 3452.2697 | 554180.7515 | 66213.9798 | 1635322.8522 | 1635322.8522 | 5443821.3503 | 1635322.8522
| MNA034-24605112 | 338 | MNA034 | MNA | North | 7965418.2528 | 0.00176 | 0.0017754 | 0.0017824 | 0.0017832 | 0.0017716 | 0.001767 | 0.0017805 | 0.0018002 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 0.0017913 | 35.4134 | 35.6322 | 35.851 | 36.0698 | 36.2887 | 36.4881 | 36.6876 | 36.8871 | 37.0865 | 37.286 | 37.4855 | 37.6849 | 37.8844 | 38.0838 | 38.2833 | 38.4828 | 38.6822 | 38.8817 | 39.0812 | 39.2806 | 1.7352 | 1.7612 | 1.779 | 1.7907 | 1.7898 | 1.795 | 1.8186 | 1.8487 | 1.8495 | 1.8595 | 1.8694 | 1.8793 | 1.8893 | 1.8992 | 1.9092 | 1.9191 | 1.9291 | 1.939 | 1.949 | 1.9589 | 28893.9194 | 3452.2697 | 771043.5465 | 92124.928 | 5478053.1966 | 5478053.1966 | 7965418.2528 | 5478053.1966
| MRO002-15420142 | 6 | MRO002 | MRO | North | 141397.9572 | 0.2425 | 0.2425 | 0.23925 | 0.235 | 0.23175 | 0.22925 | 0.22675 | 0.22425 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.00031106 | 0.00031137 | 0.00031168 | 0.00031199 | 0.0003123 | 0.00031203 | 0.00031176 | 0.00031148 | 0.00031121 | 0.00031093 | 0.00031066 | 0.00031039 | 0.00031011 | 0.00030984 | 0.00030956 | 0.00030929 | 0.00030902 | 0.00030874 | 0.00030847 | 0.00030819 | 0.0021001 | 0.0021021 | 0.002076 | 0.0020412 | 0.002015 | 0.0019915 | 0.001968 | 0.0019446 | 0.0019148 | 0.0019131 | 0.0019114 | 0.0019097 | 0.001908 | 0.0019063 | 0.0019046 | 0.0019029 | 0.0019013 | 0.0018996 | 0.0018979 | 0.0018962 | 34141.8711 | 6373.0788 | 971.5575 | 181.3554 | 317.6331 | 317.6331 | 141397.9572 | 317.6331
| MRO002-15420153 | 6 | MRO002 | MRO | North | 141397.9572 | 0.2425 | 0.2425 | 0.23925 | 0.235 | 0.23175 | 0.22925 | 0.22675 | 0.22425 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34141.8711 | 6373.0788 | 0 | 0 | 0 | 0 | 141397.9572 | 0
| MRO002-15420179 | 0 | MRO002 | MRO | North | 0 | 0.2425 | 0.2425 | 0.23925 | 0.235 | 0.23175 | 0.22925 | 0.22675 | 0.22425 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34141.8711 | 6373.0788 | 0 | 0 | 0 | 0 | 0 | 0
| MRO004-15420205 | 160 | MRO004 | MRO | North | 3770612.1907 | 0.0010686 | 0.0010702 | 0.0010668 | 0.0010614 | 0.0010515 | 0.0010461 | 0.0010442 | 0.0010469 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 0.0010416 | 69.4817 | 70.0373 | 70.5928 | 71.1483 | 71.7039 | 71.7394 | 71.775 | 71.8106 | 71.8462 | 71.8818 | 71.9174 | 71.953 | 71.9886 | 72.0242 | 72.0597 | 72.0953 | 72.1309 | 72.1665 | 72.2021 | 72.2377 | 2.0671 | 2.0868 | 2.0965 | 2.1024 | 2.099 | 2.0893 | 2.0866 | 2.093 | 2.0833 | 2.0843 | 2.0854 | 2.0864 | 2.0874 | 2.0885 | 2.0895 | 2.0905 | 2.0916 | 2.0926 | 2.0936 | 2.0947 | 34141.8711 | 6373.0788 | 1031315.5354 | 192510.1044 | 2090657.9312 | 2090657.9312 | 3770612.1907 | 2090657.9312
| MRO005-144335638 | 84 | MRO005 | MRO | North | 1979571.4001 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.16408 | 0.16568 | 0.16728 | 0.16887 | 0.17047 | 0.17017 | 0.16987 | 0.16957 | 0.16927 | 0.16897 | 0.16866 | 0.16836 | 0.16806 | 0.16776 | 0.16746 | 0.16716 | 0.16686 | 0.16656 | 0.16626 | 0.16596 | 0.0066504 | 0.0067183 | 0.0067468 | 0.0067541 | 0.0067342 | 0.0066614 | 0.0066247 | 0.0066021 | 0.0065256 | 0.006514 | 0.0065024 | 0.0064908 | 0.0064792 | 0.0064676 | 0.006456 | 0.0064443 | 0.0064327 | 0.0064211 | 0.0064095 | 0.0063979 | 34141.8711 | 6373.0788 | 3245.2855 | 605.7799 | 120149.7988 | 120149.7988 | 1979571.4001 | 120149.7988
| MRO005-144335959 | 81 | MRO005 | MRO | North | 1908872.4215 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0058938 | 0.0059616 | 0.0060293 | 0.0060971 | 0.0061649 | 0.0061784 | 0.006192 | 0.0062055 | 0.0062191 | 0.0062326 | 0.0062461 | 0.0062597 | 0.0062732 | 0.0062868 | 0.0063003 | 0.0063139 | 0.0063274 | 0.0063409 | 0.0063545 | 0.006368 | 0.00023888 | 0.00024174 | 0.00024318 | 0.00024385 | 0.00024353 | 0.00024186 | 0.00024148 | 0.00024161 | 0.00023976 | 0.00024028 | 0.0002408 | 0.00024132 | 0.00024185 | 0.00024237 | 0.00024289 | 0.00024341 | 0.00024393 | 0.00024446 | 0.00024498 | 0.0002455 | 34141.8711 | 6373.0788 | 119.5676 | 22.319 | 3881.839 | 3881.839 | 1908872.4215 | 3881.839
| MRO005-144336040 | 28 | MRO005 | MRO | North | 659857.1334 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.047919 | 0.048243 | 0.048567 | 0.048891 | 0.049215 | 0.049336 | 0.049456 | 0.049577 | 0.049697 | 0.049818 | 0.049938 | 0.050059 | 0.050179 | 0.050299 | 0.05042 | 0.05054 | 0.050661 | 0.050781 | 0.050902 | 0.051022 | 0.0019422 | 0.0019563 | 0.0019589 | 0.0019554 | 0.0019442 | 0.0019313 | 0.0019287 | 0.0019303 | 0.0019159 | 0.0019206 | 0.0019252 | 0.0019299 | 0.0019345 | 0.0019391 | 0.0019438 | 0.0019484 | 0.0019531 | 0.0019577 | 0.0019624 | 0.001967 | 34141.8711 | 6373.0788 | 958.5566 | 178.9286 | 39441.3944 | 39441.3944 | 659857.1334 | 39441.3944
| MRO005-144336270 | 12 | MRO005 | MRO | North | 282795.9143 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.011928 | 0.012024 | 0.01212 | 0.012216 | 0.012312 | 0.012316 | 0.01232 | 0.012324 | 0.012328 | 0.012332 | 0.012335 | 0.012339 | 0.012343 | 0.012347 | 0.012351 | 0.012355 | 0.012359 | 0.012363 | 0.012366 | 0.01237 | 0.00048347 | 0.00048759 | 0.00048885 | 0.00048859 | 0.00048637 | 0.00048212 | 0.00048047 | 0.00047983 | 0.00047526 | 0.00047541 | 0.00047556 | 0.00047571 | 0.00047586 | 0.000476 | 0.00047615 | 0.0004763 | 0.00047645 | 0.0004766 | 0.00047675 | 0.0004769 | 34141.8711 | 6373.0788 | 237.0942 | 44.2571 | 3135.3392 | 3135.3392 | 282795.9143 | 3135.3392
| MRO005-15420092 | 81 | MRO005 | MRO | North | 1908872.4215 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 72.0374 | 72.6041 | 73.1707 | 73.7373 | 74.3039 | 74.3473 | 74.3907 | 74.4342 | 74.4776 | 74.521 | 74.5644 | 74.6078 | 74.6512 | 74.6946 | 74.7381 | 74.7815 | 74.8249 | 74.8683 | 74.9117 | 74.9551 | 2.9198 | 2.9441 | 2.9512 | 2.9491 | 2.9353 | 2.9104 | 2.9012 | 2.8981 | 2.8713 | 2.8729 | 2.8746 | 2.8763 | 2.878 | 2.8796 | 2.8813 | 2.883 | 2.8847 | 2.8863 | 2.888 | 2.8897 | 34141.8711 | 6373.0788 | 1432943.1045 | 267479.7549 | 1082095.421 | 1082095.421 | 1908872.4215 | 1082095.421
| MRO005-155391758 | 85 | MRO005 | MRO | North | 2003137.7263 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.16409 | 0.16549 | 0.16688 | 0.16828 | 0.16968 | 0.17008 | 0.17047 | 0.17087 | 0.17126 | 0.17166 | 0.17206 | 0.17245 | 0.17285 | 0.17325 | 0.17364 | 0.17404 | 0.17444 | 0.17483 | 0.17523 | 0.17563 | 0.0066508 | 0.0067106 | 0.006731 | 0.0067304 | 0.0067029 | 0.0066577 | 0.0066482 | 0.0066528 | 0.0066026 | 0.0066179 | 0.0066332 | 0.0066485 | 0.0066638 | 0.006679 | 0.0066943 | 0.0067096 | 0.0067249 | 0.0067402 | 0.0067555 | 0.0067707 | 34141.8711 | 6373.0788 | 3299.3222 | 615.8667 | 123638.4469 | 123638.4469 | 2003137.7263 | 123638.4469
| MRO005-155391898 | 39 | MRO005 | MRO | North | 919086.7215 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.12837 | 0.12954 | 0.1307 | 0.13186 | 0.13302 | 0.13323 | 0.13343 | 0.13364 | 0.13385 | 0.13405 | 0.13426 | 0.13446 | 0.13467 | 0.13488 | 0.13508 | 0.13529 | 0.1355 | 0.1357 | 0.13591 | 0.13611 | 0.0052031 | 0.0052527 | 0.0052714 | 0.0052737 | 0.0052548 | 0.0052153 | 0.0052038 | 0.0052033 | 0.00516 | 0.005168 | 0.0051759 | 0.0051839 | 0.0051918 | 0.0051998 | 0.0052077 | 0.0052157 | 0.0052236 | 0.0052316 | 0.0052395 | 0.0052475 | 34141.8711 | 6373.0788 | 2575.6508 | 480.7828 | 110708.7016 | 110708.7016 | 919086.7215 | 110708.7016
| MRO005-155391999 | 57 | MRO005 | MRO | North | 1343280.5929 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.33731 | 0.34003 | 0.34275 | 0.34548 | 0.3482 | 0.34905 | 0.3499 | 0.35075 | 0.35161 | 0.35246 | 0.35331 | 0.35416 | 0.35501 | 0.35586 | 0.35672 | 0.35757 | 0.35842 | 0.35927 | 0.36012 | 0.36097 | 0.013671 | 0.013788 | 0.013824 | 0.013817 | 0.013755 | 0.013664 | 0.013646 | 0.013657 | 0.013555 | 0.013588 | 0.013621 | 0.013654 | 0.013686 | 0.013719 | 0.013752 | 0.013785 | 0.013818 | 0.013851 | 0.013883 | 0.013916 | 34141.8711 | 6373.0788 | 6776.0919 | 1264.8565 | 162171.3821 | 162171.3821 | 1343280.5929 | 162171.3821
| MRO005-155423773 | 50 | MRO005 | MRO | North | 1178316.3096 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.37866 | 0.38116 | 0.38367 | 0.38617 | 0.38867 | 0.38932 | 0.38997 | 0.39062 | 0.39128 | 0.39193 | 0.39258 | 0.39323 | 0.39388 | 0.39453 | 0.39518 | 0.39583 | 0.39648 | 0.39713 | 0.39778 | 0.39844 | 0.015348 | 0.015456 | 0.015474 | 0.015445 | 0.015354 | 0.01524 | 0.015209 | 0.015209 | 0.015084 | 0.01511 | 0.015135 | 0.01516 | 0.015185 | 0.01521 | 0.015235 | 0.01526 | 0.015285 | 0.01531 | 0.015335 | 0.015361 | 34141.8711 | 6373.0788 | 7542.0801 | 1407.8394 | 144555.8204 | 144555.8204 | 1178316.3096 | 144555.8204
| MRO005-155505168 | 56 | MRO005 | MRO | North | 1319714.2667 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.16994 | 0.17161 | 0.17327 | 0.17494 | 0.1766 | 0.17675 | 0.1769 | 0.17704 | 0.17719 | 0.17734 | 0.17748 | 0.17763 | 0.17778 | 0.17793 | 0.17807 | 0.17822 | 0.17837 | 0.17851 | 0.17866 | 0.17881 | 0.0068879 | 0.0069587 | 0.0069886 | 0.0069966 | 0.0069764 | 0.006919 | 0.0068988 | 0.0068932 | 0.0068311 | 0.0068367 | 0.0068424 | 0.0068481 | 0.0068537 | 0.0068594 | 0.0068651 | 0.0068707 | 0.0068764 | 0.0068821 | 0.0068877 | 0.0068934 | 34141.8711 | 6373.0788 | 3405.7668 | 635.7361 | 108486.4473 | 108486.4473 | 1319714.2667 | 108486.4473
| MRO005-155838268 | 46 | MRO005 | MRO | North | 1084051.0048 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.056527 | 0.057085 | 0.057644 | 0.058202 | 0.05876 | 0.058875 | 0.05899 | 0.059106 | 0.059221 | 0.059336 | 0.059451 | 0.059567 | 0.059682 | 0.059797 | 0.059912 | 0.060028 | 0.060143 | 0.060258 | 0.060373 | 0.060489 | 0.0022911 | 0.0023148 | 0.002325 | 0.0023278 | 0.0023212 | 0.0023047 | 0.0023006 | 0.0023013 | 0.0022831 | 0.0022875 | 0.002292 | 0.0022964 | 0.0023009 | 0.0023053 | 0.0023098 | 0.0023142 | 0.0023186 | 0.0023231 | 0.0023275 | 0.002332 | 34141.8711 | 6373.0788 | 1139.4751 | 212.6997 | 54373.0856 | 54373.0856 | 1084051.0048 | 54373.0856
| MRO005-163160444 | 19 | MRO005 | MRO | North | 447760.1976 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.026665 | 0.026939 | 0.027213 | 0.027487 | 0.027761 | 0.027739 | 0.027717 | 0.027695 | 0.027673 | 0.027651 | 0.027629 | 0.027607 | 0.027585 | 0.027563 | 0.02754 | 0.027518 | 0.027496 | 0.027474 | 0.027452 | 0.02743 | 0.0010807 | 0.0010924 | 0.0010976 | 0.0010993 | 0.0010967 | 0.0010859 | 0.0010809 | 0.0010783 | 0.0010669 | 0.001066 | 0.0010652 | 0.0010643 | 0.0010634 | 0.0010626 | 0.0010617 | 0.0010609 | 0.00106 | 0.0010592 | 0.0010583 | 0.0010575 | 34141.8711 | 6373.0788 | 530.8905 | 99.0985 | 29641.0891 | 29641.0891 | 447760.1976 | 29641.0891
| MRO005-163160605 | 18 | MRO005 | MRO | North | 424193.8715 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.043621 | 0.044019 | 0.044417 | 0.044816 | 0.045214 | 0.045334 | 0.045454 | 0.045574 | 0.045694 | 0.045814 | 0.045934 | 0.046054 | 0.046174 | 0.046294 | 0.046414 | 0.046534 | 0.046654 | 0.046773 | 0.046893 | 0.047013 | 0.001768 | 0.001785 | 0.0017915 | 0.0017924 | 0.0017861 | 0.0017746 | 0.0017727 | 0.0017744 | 0.0017616 | 0.0017662 | 0.0017708 | 0.0017755 | 0.0017801 | 0.0017847 | 0.0017893 | 0.001794 | 0.0017986 | 0.0018032 | 0.0018078 | 0.0018125 | 34141.8711 | 6373.0788 | 880.1912 | 164.3005 | 34925.6648 | 34925.6648 | 424193.8715 | 34925.6648
| MRO005-163160879 | 7 | MRO005 | MRO | North | 164964.2833 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34141.8711 | 6373.0788 | 0 | 0 | 0 | 0 | 164964.2833 | 0
| MRO005-163161051 | 15 | MRO005 | MRO | North | 353494.8929 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.017503 | 0.017674 | 0.017845 | 0.018016 | 0.018188 | 0.018246 | 0.018304 | 0.018362 | 0.01842 | 0.018478 | 0.018536 | 0.018594 | 0.018652 | 0.018711 | 0.018769 | 0.018827 | 0.018885 | 0.018943 | 0.019001 | 0.019059 | 0.0007094 | 0.00071668 | 0.00071975 | 0.00072057 | 0.00071848 | 0.00071425 | 0.00071383 | 0.00071493 | 0.00071013 | 0.00071237 | 0.00071461 | 0.00071685 | 0.00071909 | 0.00072133 | 0.00072357 | 0.00072581 | 0.00072805 | 0.00073029 | 0.00073253 | 0.00073477 | 34141.8711 | 6373.0788 | 354.8612 | 66.24 | 13410.9433 | 13410.9433 | 353494.8929 | 13410.9433
| MRO005-172349913 | 12 | MRO005 | MRO | North | 282795.9143 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.033897 | 0.03418 | 0.034463 | 0.034746 | 0.035029 | 0.035193 | 0.035357 | 0.035522 | 0.035686 | 0.03585 | 0.036014 | 0.036178 | 0.036342 | 0.036506 | 0.03667 | 0.036835 | 0.036999 | 0.037163 | 0.037327 | 0.037491 | 0.0013739 | 0.001386 | 0.00139 | 0.0013897 | 0.0013838 | 0.0013777 | 0.0013789 | 0.001383 | 0.0013758 | 0.0013821 | 0.0013884 | 0.0013947 | 0.0014011 | 0.0014074 | 0.0014137 | 0.0014201 | 0.0014264 | 0.0014327 | 0.001439 | 0.0014454 | 34141.8711 | 6373.0788 | 689.0671 | 128.6244 | 12153.5172 | 12153.5172 | 282795.9143 | 12153.5172
| MRO005-24606286 | 242 | MRO005 | MRO | North | 5703050.9384 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 10.4463 | 10.5185 | 10.5908 | 10.6631 | 10.7354 | 10.7517 | 10.768 | 10.7843 | 10.8006 | 10.8169 | 10.8332 | 10.8495 | 10.8659 | 10.8822 | 10.8985 | 10.9148 | 10.9311 | 10.9474 | 10.9637 | 10.98 | 0.4234 | 0.42653 | 0.42716 | 0.42647 | 0.42408 | 0.42088 | 0.41994 | 0.41989 | 0.41639 | 0.41702 | 0.41764 | 0.41827 | 0.4189 | 0.41953 | 0.42016 | 0.42079 | 0.42142 | 0.42204 | 0.42267 | 0.4233 | 34141.8711 | 6373.0788 | 208116.615 | 38848.0052 | 2888580.6759 | 2888580.6759 | 5703050.9384 | 2888580.6759
| MRO005-24606314 | 254 | MRO005 | MRO | North | 5985846.8527 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 17.481 | 17.6137 | 17.7464 | 17.8792 | 18.0119 | 18.0436 | 18.0753 | 18.1069 | 18.1386 | 18.1703 | 18.202 | 18.2336 | 18.2653 | 18.297 | 18.3287 | 18.3603 | 18.392 | 18.4237 | 18.4554 | 18.487 | 0.70852 | 0.71424 | 0.71577 | 0.71507 | 0.71153 | 0.70633 | 0.70492 | 0.705 | 0.69928 | 0.7005 | 0.70172 | 0.70295 | 0.70417 | 0.70539 | 0.70661 | 0.70783 | 0.70905 | 0.71027 | 0.71149 | 0.71271 | 34141.8711 | 6373.0788 | 349441.5127 | 65228.3611 | 1693262.3443 | 1693262.3443 | 5985846.8527 | 1693262.3443
| MRO005-24606328 | 249 | MRO005 | MRO | North | 5868015.2218 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 5.6964 | 5.7397 | 5.7831 | 5.8264 | 5.8698 | 5.8899 | 5.9101 | 5.9302 | 5.9503 | 5.9705 | 5.9906 | 6.0107 | 6.0309 | 6.051 | 6.0712 | 6.0913 | 6.1114 | 6.1316 | 6.1517 | 6.1718 | 0.23088 | 0.23275 | 0.23325 | 0.23303 | 0.23188 | 0.23057 | 0.23049 | 0.23089 | 0.2294 | 0.23017 | 0.23095 | 0.23173 | 0.2325 | 0.23328 | 0.23406 | 0.23483 | 0.23561 | 0.23639 | 0.23716 | 0.23794 | 34141.8711 | 6373.0788 | 114814.8672 | 21431.8715 | 1289190.7537 | 1289190.7537 | 5868015.2218 | 1289190.7537
| MRO005-24606858 | 220 | MRO005 | MRO | North | 5184591.7622 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 14.0051 | 14.1234 | 14.2417 | 14.3599 | 14.4782 | 14.4989 | 14.5196 | 14.5403 | 14.561 | 14.5817 | 14.6023 | 14.623 | 14.6437 | 14.6644 | 14.6851 | 14.7058 | 14.7265 | 14.7472 | 14.7678 | 14.7885 | 0.56764 | 0.57271 | 0.57441 | 0.57432 | 0.57194 | 0.56757 | 0.56625 | 0.56613 | 0.56136 | 0.56215 | 0.56295 | 0.56375 | 0.56455 | 0.56534 | 0.56614 | 0.56694 | 0.56774 | 0.56853 | 0.56933 | 0.57013 | 34141.8711 | 6373.0788 | 280277.3234 | 52317.8552 | 3295235.5417 | 3295235.5417 | 5184591.7622 | 3295235.5417
| MRO005-73766637 | 45 | MRO005 | MRO | North | 1060484.6786 | 0.0014559 | 0.0014565 | 0.0014488 | 0.0014366 | 0.0014189 | 0.0014061 | 0.0014008 | 0.0013985 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.0013848 | 0.34412 | 0.34688 | 0.34964 | 0.35241 | 0.35517 | 0.35599 | 0.3568 | 0.35762 | 0.35843 | 0.35925 | 0.36006 | 0.36088 | 0.36169 | 0.36251 | 0.36332 | 0.36414 | 0.36495 | 0.36577 | 0.36658 | 0.3674 | 0.013947 | 0.014066 | 0.014102 | 0.014094 | 0.01403 | 0.013935 | 0.013915 | 0.013924 | 0.013818 | 0.01385 | 0.013881 | 0.013913 | 0.013944 | 0.013975 | 0.014007 | 0.014038 | 0.01407 | 0.014101 | 0.014133 | 0.014164 | 34141.8711 | 6373.0788 | 6906.821 | 1289.259 | 144235.2477 | 144235.2477 | 1060484.6786 | 144235.2477
| MRO006-15420268 | 88 | MRO006 | MRO | North | 2073836.7049 | 0.0015108 | 0.0014911 | 0.0014773 | 0.0014604 | 0.0014435 | 0.0014357 | 0.0014357 | 0.0014357 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0.0014265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34141.8711 | 6373.0788 | 0 | 0 | 0 | 0 | 2073836.7049 | 0
| MRO007-122640081 | 430 | MRO007 | MRO | North | 10133520.2625 | 0.0012967 | 0.0013089 | 0.0013176 | 0.0013221 | 0.0013195 | 0.0013245 | 0.0013385 | 0.0013552 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 18.4105 | 18.5307 | 18.6509 | 18.7711 | 18.8913 | 18.9431 | 18.9949 | 19.0467 | 19.0984 | 19.1502 | 19.202 | 19.2538 | 19.3056 | 19.3574 | 19.4092 | 19.461 | 19.5128 | 19.5645 | 19.6163 | 19.6681 | 0.66462 | 0.67524 | 0.68416 | 0.69092 | 0.69395 | 0.69851 | 0.70784 | 0.71862 | 0.71917 | 0.72112 | 0.72307 | 0.72502 | 0.72697 | 0.72892 | 0.73087 | 0.73282 | 0.73477 | 0.73672 | 0.73867 | 0.74062 | 34141.8711 | 6373.0788 | 350701.9811 | 65463.6459 | 5480710.8916 | 5480710.8916 | 10133520.2625 | 5480710.8916
| MRO007-129258735 | 43 | MRO007 | MRO | North | 1013352.0262 | 0.0012967 | 0.0013089 | 0.0013176 | 0.0013221 | 0.0013195 | 0.0013245 | 0.0013385 | 0.0013552 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.31673 | 0.31935 | 0.32197 | 0.32459 | 0.32721 | 0.32858 | 0.32994 | 0.33131 | 0.33268 | 0.33404 | 0.33541 | 0.33678 | 0.33814 | 0.33951 | 0.34088 | 0.34224 | 0.34361 | 0.34498 | 0.34634 | 0.34771 | 0.011434 | 0.011637 | 0.011811 | 0.011947 | 0.01202 | 0.012116 | 0.012295 | 0.0125 | 0.012527 | 0.012579 | 0.01263 | 0.012682 | 0.012733 | 0.012785 | 0.012836 | 0.012888 | 0.012939 | 0.01299 | 0.013042 | 0.013093 | 34141.8711 | 6373.0788 | 6111.8852 | 1140.8726 | 202901.8414 | 202901.8414 | 1013352.0262 | 202901.8414
| MRO007-15420070 | 448 | MRO007 | MRO | North | 10557714.1339 | 0.0012967 | 0.0013089 | 0.0013176 | 0.0013221 | 0.0013195 | 0.0013245 | 0.0013385 | 0.0013552 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 35.9995 | 36.2758 | 36.5521 | 36.8284 | 37.1047 | 37.0865 | 37.0683 | 37.0501 | 37.0319 | 37.0137 | 36.9955 | 36.9773 | 36.9592 | 36.941 | 36.9228 | 36.9046 | 36.8864 | 36.8682 | 36.85 | 36.8318 | 1.2996 | 1.3219 | 1.3408 | 1.3556 | 1.363 | 1.3675 | 1.3814 | 1.3979 | 1.3945 | 1.3938 | 1.3931 | 1.3924 | 1.3917 | 1.391 | 1.3904 | 1.3897 | 1.389 | 1.3883 | 1.3876 | 1.3869 | 34141.8711 | 6373.0788 | 677154.1019 | 126400.7012 | 3962369.3164 | 3962369.3164 | 10557714.1339 | 3962369.3164
| MRO007-161151299 | 25 | MRO007 | MRO | North | 589158.1548 | 0.0012967 | 0.0013089 | 0.0013176 | 0.0013221 | 0.0013195 | 0.0013245 | 0.0013385 | 0.0013552 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.12276 | 0.12388 | 0.12501 | 0.12613 | 0.12726 | 0.12727 | 0.12729 | 0.12731 | 0.12733 | 0.12734 | 0.12736 | 0.12738 | 0.12739 | 0.12741 | 0.12743 | 0.12744 | 0.12746 | 0.12748 | 0.12749 | 0.12751 | 0.0044316 | 0.0045142 | 0.0045856 | 0.0046427 | 0.0046747 | 0.0046931 | 0.0047435 | 0.0048033 | 0.0047945 | 0.0047952 | 0.0047958 | 0.0047965 | 0.0047971 | 0.0047977 | 0.0047984 | 0.004799 | 0.0047996 | 0.0048003 | 0.0048009 | 0.0048016 | 34141.8711 | 6373.0788 | 2327.735 | 434.5057 | 82960.3686 | 82960.3686 | 589158.1548 | 82960.3686
| MRO007-24610986 | 173 | MRO007 | MRO | North | 4076974.4312 | 0.0012967 | 0.0013089 | 0.0013176 | 0.0013221 | 0.0013195 | 0.0013245 | 0.0013385 | 0.0013552 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 13.9572 | 14.092 | 14.2268 | 14.3616 | 14.4964 | 14.4883 | 14.4802 | 14.4722 | 14.4641 | 14.456 | 14.4479 | 14.4398 | 14.4317 | 14.4237 | 14.4156 | 14.4075 | 14.3994 | 14.3913 | 14.3833 | 14.3752 | 0.50385 | 0.5135 | 0.52187 | 0.52862 | 0.53251 | 0.53425 | 0.53961 | 0.54603 | 0.54466 | 0.54435 | 0.54405 | 0.54374 | 0.54344 | 0.54314 | 0.54283 | 0.54253 | 0.54222 | 0.54192 | 0.54161 | 0.54131 | 34141.8711 | 6373.0788 | 264148.8538 | 49307.2408 | 1573036.1572 | 1573036.1572 | 4076974.4312 | 1573036.1572
| MRO007-76446321 | 55 | MRO007 | MRO | North | 1296147.9405 | 0.0012967 | 0.0013089 | 0.0013176 | 0.0013221 | 0.0013195 | 0.0013245 | 0.0013385 | 0.0013552 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.46437 | 0.46837 | 0.47237 | 0.47638 | 0.48038 | 0.48062 | 0.48087 | 0.48111 | 0.48136 | 0.4816 | 0.48185 | 0.48209 | 0.48233 | 0.48258 | 0.48282 | 0.48307 | 0.48331 | 0.48356 | 0.4838 | 0.48405 | 0.016764 | 0.017067 | 0.017328 | 0.017534 | 0.017646 | 0.017723 | 0.01792 | 0.018152 | 0.018126 | 0.018135 | 0.018144 | 0.018154 | 0.018163 | 0.018172 | 0.018181 | 0.01819 | 0.0182 | 0.018209 | 0.018218 | 0.018227 | 34141.8711 | 6373.0788 | 8806.6028 | 1643.881 | 149608.049 | 149608.049 | 1296147.9405 | 149608.049
| MRO007-76446588 | 58 | MRO007 | MRO | North | 1366846.9191 | 0.0012967 | 0.0013089 | 0.0013176 | 0.0013221 | 0.0013195 | 0.0013245 | 0.0013385 | 0.0013552 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.15827 | 0.15981 | 0.16135 | 0.16289 | 0.16443 | 0.16445 | 0.16448 | 0.16451 | 0.16453 | 0.16456 | 0.16458 | 0.16461 | 0.16464 | 0.16466 | 0.16469 | 0.16472 | 0.16474 | 0.16477 | 0.1648 | 0.16482 | 0.0057134 | 0.0058232 | 0.0059186 | 0.0059955 | 0.00604 | 0.0060641 | 0.0061293 | 0.0062067 | 0.0061956 | 0.0061966 | 0.0061976 | 0.0061986 | 0.0061996 | 0.0062006 | 0.0062016 | 0.0062026 | 0.0062036 | 0.0062045 | 0.0062055 | 0.0062065 | 34141.8711 | 6373.0788 | 3007.0158 | 561.3034 | 62157.9534 | 62157.9534 | 1366846.9191 | 62157.9534
| MRO007-76547638 | 59 | MRO007 | MRO | North | 1390413.2453 | 0.0012967 | 0.0013089 | 0.0013176 | 0.0013221 | 0.0013195 | 0.0013245 | 0.0013385 | 0.0013552 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.20937 | 0.21065 | 0.21193 | 0.21321 | 0.21449 | 0.21504 | 0.2156 | 0.21615 | 0.2167 | 0.21725 | 0.2178 | 0.21835 | 0.21891 | 0.21946 | 0.22001 | 0.22056 | 0.22111 | 0.22167 | 0.22222 | 0.22277 | 0.0075581 | 0.0076758 | 0.0077741 | 0.0078478 | 0.0078791 | 0.0079295 | 0.0080342 | 0.0081552 | 0.00816 | 0.0081808 | 0.0082016 | 0.0082223 | 0.0082431 | 0.0082639 | 0.0082847 | 0.0083055 | 0.0083262 | 0.008347 | 0.0083678 | 0.0083886 | 34141.8711 | 6373.0788 | 3979.4763 | 742.8274 | 111562.0646 | 111562.0646 | 1390413.2453 | 111562.0646
| MRO007-76547903 | 43 | MRO007 | MRO | North | 1013352.0262 | 0.0012967 | 0.0013089 | 0.0013176 | 0.0013221 | 0.0013195 | 0.0013245 | 0.0013385 | 0.0013552 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0012963 | 0.0013108 | 0.0013252 | 0.0013397 | 0.0013542 | 0.0013555 | 0.0013568 | 0.0013581 | 0.0013594 | 0.0013607 | 0.001362 | 0.0013633 | 0.0013646 | 0.0013659 | 0.0013672 | 0.0013684 | 0.0013697 | 0.001371 | 0.0013723 | 0.0013736 | 4.6795e-05 | 4.7763e-05 | 4.8613e-05 | 4.9312e-05 | 4.9745e-05 | 4.9983e-05 | 5.0561e-05 | 5.124e-05 | 5.1189e-05 | 5.1237e-05 | 5.1286e-05 | 5.1335e-05 | 5.1384e-05 | 5.1433e-05 | 5.1481e-05 | 5.153e-05 | 5.1579e-05 | 5.1628e-05 | 5.1676e-05 | 5.1725e-05 | 34141.8711 | 6373.0788 | 24.8448 | 4.6376 | 535.0709 | 535.0709 | 1013352.0262 | 535.0709
| MRO007-76548012 | 58 | MRO007 | MRO | North | 1366846.9191 | 0.0012967 | 0.0013089 | 0.0013176 | 0.0013221 | 0.0013195 | 0.0013245 | 0.0013385 | 0.0013552 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.0013526 | 0.20285 | 0.20471 | 0.20657 | 0.20843 | 0.21028 | 0.21038 | 0.21047 | 0.21057 | 0.21066 | 0.21076 | 0.21086 | 0.21095 | 0.21105 | 0.21114 | 0.21124 | 0.21133 | 0.21143 | 0.21152 | 0.21162 | 0.21171 | 0.007323 | 0.0074595 | 0.0075775 | 0.0076717 | 0.0077246 | 0.0077576 | 0.0078433 | 0.0079447 | 0.0079328 | 0.0079364 | 0.00794 | 0.0079436 | 0.0079471 | 0.0079507 | 0.0079543 | 0.0079579 | 0.0079615 | 0.0079651 | 0.0079687 | 0.0079723 | 34141.8711 | 6373.0788 | 3852.7175 | 719.166 | 84514.68 | 84514.68 | 1366846.9191 | 84514.68
| MRO008-129258570 | 27 | MRO008 | MRO | North | 636290.8072 | 0.0010814 | 0.0010878 | 0.001088 | 0.0010868 | 0.00108 | 0.0010765 | 0.0010817 | 0.0010887 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.12701 | 0.12812 | 0.12922 | 0.13033 | 0.13143 | 0.1315 | 0.13157 | 0.13165 | 0.13172 | 0.13179 | 0.13186 | 0.13193 | 0.132 | 0.13207 | 0.13214 | 0.13221 | 0.13228 | 0.13235 | 0.13242 | 0.13249 | 0.0038236 | 0.00388 | 0.0039141 | 0.0039432 | 0.0039517 | 0.003941 | 0.0039623 | 0.0039901 | 0.0039839 | 0.003986 | 0.0039882 | 0.0039903 | 0.0039925 | 0.0039946 | 0.0039967 | 0.0039989 | 0.004001 | 0.0040032 | 0.0040053 | 0.0040074 | 34141.8711 | 6373.0788 | 1954.7085 | 364.8749 | 57418.4138 | 57418.4138 | 636290.8072 | 57418.4138
| MRO008-137134221 | 24 | MRO008 | MRO | North | 565591.8286 | 0.0010814 | 0.0010878 | 0.001088 | 0.0010868 | 0.00108 | 0.0010765 | 0.0010817 | 0.0010887 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.022179 | 0.022353 | 0.022527 | 0.022701 | 0.022874 | 0.022872 | 0.02287 | 0.022867 | 0.022865 | 0.022863 | 0.02286 | 0.022858 | 0.022855 | 0.022853 | 0.022851 | 0.022848 | 0.022846 | 0.022843 | 0.022841 | 0.022839 | 0.00066769 | 0.00067695 | 0.00068233 | 0.00068682 | 0.00068774 | 0.00068544 | 0.00068871 | 0.00069309 | 0.00069157 | 0.0006915 | 0.00069143 | 0.00069136 | 0.00069128 | 0.00069121 | 0.00069114 | 0.00069107 | 0.00069099 | 0.00069092 | 0.00069085 | 0.00069078 | 34141.8711 | 6373.0788 | 339.2732 | 63.3303 | 9791.1406 | 9791.1406 | 565591.8286 | 9791.1406
| MRO008-15411648 | 220 | MRO008 | MRO | North | 5184591.7622 | 0.0010814 | 0.0010878 | 0.001088 | 0.0010868 | 0.00108 | 0.0010765 | 0.0010817 | 0.0010887 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 93.9911 | 94.5572 | 95.1232 | 95.6893 | 96.2553 | 96.2655 | 96.2756 | 96.2857 | 96.2958 | 96.306 | 96.3161 | 96.3262 | 96.3364 | 96.3465 | 96.3566 | 96.3667 | 96.3769 | 96.387 | 96.3971 | 96.4073 | 2.8296 | 2.8637 | 2.8813 | 2.8952 | 2.894 | 2.8849 | 2.8993 | 2.9184 | 2.9126 | 2.9129 | 2.9132 | 2.9135 | 2.9138 | 2.9141 | 2.9144 | 2.9147 | 2.915 | 2.9153 | 2.9156 | 2.9159 | 34141.8711 | 6373.0788 | 1430794.3416 | 267078.657 | 2746918.8108 | 2746918.8108 | 5184591.7622 | 2746918.8108
| MRO008-156506029 | 365 | MRO008 | MRO | North | 8601709.06 | 0.0010814 | 0.0010878 | 0.001088 | 0.0010868 | 0.00108 | 0.0010765 | 0.0010817 | 0.0010887 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 53.4673 | 53.8964 | 54.3255 | 54.7547 | 55.1838 | 55.1509 | 55.118 | 55.0852 | 55.0523 | 55.0194 | 54.9865 | 54.9536 | 54.9208 | 54.8879 | 54.855 | 54.8221 | 54.7892 | 54.7563 | 54.7235 | 54.6906 | 1.6096 | 1.6323 | 1.6455 | 1.6566 | 1.6591 | 1.6528 | 1.6599 | 1.6696 | 1.6651 | 1.6641 | 1.6631 | 1.6621 | 1.6611 | 1.6601 | 1.6591 | 1.6582 | 1.6572 | 1.6562 | 1.6552 | 1.6542 | 34141.8711 | 6373.0788 | 816357.6119 | 152385.0691 | 5372786.8324 | 5372786.8324 | 8601709.06 | 5372786.8324
| MRO008-161918307 | 35 | MRO008 | MRO | North | 824821.4167 | 0.0010814 | 0.0010878 | 0.001088 | 0.0010868 | 0.00108 | 0.0010765 | 0.0010817 | 0.0010887 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.13682 | 0.13807 | 0.13932 | 0.14058 | 0.14183 | 0.14186 | 0.1419 | 0.14193 | 0.14196 | 0.14199 | 0.14202 | 0.14205 | 0.14208 | 0.14211 | 0.14214 | 0.14217 | 0.14221 | 0.14224 | 0.14227 | 0.1423 | 0.0041188 | 0.0041814 | 0.0042201 | 0.0042533 | 0.0042643 | 0.0042514 | 0.0042731 | 0.0043017 | 0.0042936 | 0.0042946 | 0.0042955 | 0.0042965 | 0.0042974 | 0.0042983 | 0.0042993 | 0.0043002 | 0.0043012 | 0.0043021 | 0.004303 | 0.004304 | 34141.8711 | 6373.0788 | 2105.3768 | 392.9993 | 41061.9356 | 41061.9356 | 824821.4167 | 41061.9356
| MRO008-24606830 | 225 | MRO008 | MRO | North | 5302423.3932 | 0.0010814 | 0.0010878 | 0.001088 | 0.0010868 | 0.00108 | 0.0010765 | 0.0010817 | 0.0010887 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 3.4696 | 3.5006 | 3.5316 | 3.5626 | 3.5936 | 3.5913 | 3.5889 | 3.5865 | 3.5842 | 3.5818 | 3.5795 | 3.5771 | 3.5748 | 3.5724 | 3.5701 | 3.5677 | 3.5654 | 3.563 | 3.5607 | 3.5583 | 0.10445 | 0.10602 | 0.10697 | 0.10779 | 0.10804 | 0.10762 | 0.10808 | 0.10871 | 0.10841 | 0.10834 | 0.10827 | 0.10819 | 0.10812 | 0.10805 | 0.10798 | 0.10791 | 0.10784 | 0.10777 | 0.1077 | 0.10763 | 34141.8711 | 6373.0788 | 53115.9845 | 9914.8741 | 1213598.1543 | 1213598.1543 | 5302423.3932 | 1213598.1543
| MRO008-24606844 | 91 | MRO008 | MRO | North | 2144535.6835 | 0.0010814 | 0.0010878 | 0.001088 | 0.0010868 | 0.00108 | 0.0010765 | 0.0010817 | 0.0010887 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 1.355 | 1.368 | 1.3809 | 1.3939 | 1.4068 | 1.4094 | 1.412 | 1.4146 | 1.4171 | 1.4197 | 1.4223 | 1.4249 | 1.4275 | 1.43 | 1.4326 | 1.4352 | 1.4378 | 1.4403 | 1.4429 | 1.4455 | 0.040792 | 0.041429 | 0.041828 | 0.042173 | 0.042298 | 0.042238 | 0.042522 | 0.042875 | 0.042863 | 0.042941 | 0.043019 | 0.043097 | 0.043175 | 0.043253 | 0.04333 | 0.043408 | 0.043486 | 0.043564 | 0.043642 | 0.04372 | 34141.8711 | 6373.0788 | 21048.246 | 3928.9625 | 497274.8886 | 497274.8886 | 2144535.6835 | 497274.8886
| MRO008-77241441 | 21 | MRO008 | MRO | North | 494892.85 | 0.0010814 | 0.0010878 | 0.001088 | 0.0010868 | 0.00108 | 0.0010765 | 0.0010817 | 0.0010887 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 3.124e-05 | 3.158e-05 | 3.192e-05 | 3.226e-05 | 3.26e-05 | 3.253e-05 | 3.246e-05 | 3.239e-05 | 3.232e-05 | 3.225e-05 | 3.218e-05 | 3.211e-05 | 3.204e-05 | 3.197e-05 | 3.19e-05 | 3.183e-05 | 3.176e-05 | 3.169e-05 | 3.162e-05 | 3.155e-05 | 9.4047e-07 | 9.564e-07 | 9.6685e-07 | 9.7605e-07 | 9.8015e-07 | 9.7487e-07 | 9.7752e-07 | 9.8172e-07 | 9.7755e-07 | 9.7544e-07 | 9.7332e-07 | 9.712e-07 | 9.6908e-07 | 9.6697e-07 | 9.6485e-07 | 9.6273e-07 | 9.6061e-07 | 9.585e-07 | 9.5638e-07 | 9.5426e-07 | 34141.8711 | 6373.0788 | 0.47763 | 0.089156 | 45.8319 | 45.8319 | 494892.85 | 45.8319
| MRO008-77241511 | 72 | MRO008 | MRO | North | 1696775.4858 | 0.0010814 | 0.0010878 | 0.001088 | 0.0010868 | 0.00108 | 0.0010765 | 0.0010817 | 0.0010887 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.0010864 | 0.26709 | 0.26928 | 0.27147 | 0.27366 | 0.27584 | 0.27546 | 0.27508 | 0.27469 | 0.27431 | 0.27392 | 0.27354 | 0.27315 | 0.27277 | 0.27238 | 0.272 | 0.27162 | 0.27123 | 0.27085 | 0.27046 | 0.27008 | 0.0080408 | 0.0081552 | 0.0082228 | 0.0082797 | 0.0082935 | 0.0082551 | 0.0082838 | 0.0083257 | 0.0082967 | 0.0082851 | 0.0082734 | 0.0082618 | 0.0082502 | 0.0082386 | 0.0082269 | 0.0082153 | 0.0082037 | 0.008192 | 0.0081804 | 0.0081688 | 34141.8711 | 6373.0788 | 4063.7649 | 758.5611 | 123793.0531 | 123793.0531 | 1696775.4858 | 123793.0531
| NHL015-115332434 | 220 | NHL015 | NHL | North | 5184591.7622 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 22.2739 | 22.4491 | 22.6243 | 22.7995 | 22.9747 | 22.9249 | 22.8751 | 22.8253 | 22.7755 | 22.7257 | 22.6759 | 22.6261 | 22.5763 | 22.5265 | 22.4766 | 22.4268 | 22.377 | 22.3272 | 22.2774 | 22.2276 | 0.69949 | 0.70499 | 0.70583 | 0.70515 | 0.69758 | 0.68371 | 0.67812 | 0.6746 | 0.66229 | 0.66084 | 0.65939 | 0.65794 | 0.65649 | 0.65505 | 0.6536 | 0.65215 | 0.6507 | 0.64925 | 0.6478 | 0.64636 | 27117.7471 | 4149.7923 | 264293.9383 | 40444.5449 | 2142691.7771 | 2142691.7771 | 5184591.7622 | 2142691.7771
| NHL015-154154899 | 423 | NHL015 | NHL | North | 9968555.9791 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.95657 | 0.96546 | 0.97436 | 0.98326 | 0.99216 | 0.98749 | 0.98283 | 0.97816 | 0.9735 | 0.96883 | 0.96417 | 0.9595 | 0.95483 | 0.95017 | 0.9455 | 0.94084 | 0.93617 | 0.93151 | 0.92684 | 0.92218 | 0.03004 | 0.03032 | 0.030398 | 0.030411 | 0.030125 | 0.029451 | 0.029135 | 0.028909 | 0.028308 | 0.028173 | 0.028037 | 0.027901 | 0.027766 | 0.02763 | 0.027494 | 0.027359 | 0.027223 | 0.027087 | 0.026952 | 0.026816 | 27117.7471 | 4149.7923 | 11258.563 | 1722.8827 | 3652231.0527 | 3652231.0527 | 9968555.9791 | 3652231.0527
| NHL015-15417078 | 0 | NHL015 | NHL | North | 0 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27117.7471 | 4149.7923 | 0 | 0 | 0 | 0 | 0 | 0
| NHL015-15417104 | 94 | NHL015 | NHL | North | 2215234.662 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 4.7196 | 4.7597 | 4.7999 | 4.8401 | 4.8803 | 4.8609 | 4.8416 | 4.8222 | 4.8028 | 4.7834 | 4.764 | 4.7447 | 4.7253 | 4.7059 | 4.6865 | 4.6671 | 4.6478 | 4.6284 | 4.609 | 4.5896 | 0.14821 | 0.14948 | 0.14975 | 0.1497 | 0.14818 | 0.14497 | 0.14353 | 0.14252 | 0.13966 | 0.1391 | 0.13853 | 0.13797 | 0.13741 | 0.13684 | 0.13628 | 0.13572 | 0.13515 | 0.13459 | 0.13402 | 0.13346 | 27117.7471 | 4149.7923 | 55613.1244 | 8510.4014 | 179508.8492 | 179508.8492 | 2215234.662 | 179508.8492
| NHL015-157413262 | 65 | NHL015 | NHL | North | 1531811.2025 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.090797 | 0.091794 | 0.092791 | 0.093788 | 0.094785 | 0.094443 | 0.094102 | 0.093761 | 0.093419 | 0.093078 | 0.092736 | 0.092395 | 0.092054 | 0.091712 | 0.091371 | 0.091029 | 0.090688 | 0.090347 | 0.090005 | 0.089664 | 0.0028514 | 0.0028827 | 0.0028949 | 0.0029007 | 0.0028779 | 0.0028167 | 0.0027896 | 0.0027711 | 0.0027165 | 0.0027066 | 0.0026967 | 0.0026867 | 0.0026768 | 0.0026669 | 0.002657 | 0.002647 | 0.0026371 | 0.0026272 | 0.0026173 | 0.0026073 | 27117.7471 | 4149.7923 | 1080.3678 | 165.3272 | 81873.7297 | 81873.7297 | 1531811.2025 | 81873.7297
| NHL015-157443574 | 92 | NHL015 | NHL | North | 2168102.0096 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.017682 | 0.017868 | 0.018054 | 0.018239 | 0.018425 | 0.018362 | 0.018299 | 0.018236 | 0.018172 | 0.018109 | 0.018046 | 0.017983 | 0.01792 | 0.017856 | 0.017793 | 0.01773 | 0.017667 | 0.017604 | 0.017541 | 0.017477 | 0.00055529 | 0.00056112 | 0.00056323 | 0.00056411 | 0.00055944 | 0.00054763 | 0.00054246 | 0.00053895 | 0.00052843 | 0.0005266 | 0.00052476 | 0.00052292 | 0.00052108 | 0.00051925 | 0.00051741 | 0.00051557 | 0.00051374 | 0.0005119 | 0.00051006 | 0.00050822 | 27117.7471 | 4149.7923 | 210.2594 | 32.1757 | 51256.9478 | 51256.9478 | 2168102.0096 | 51256.9478
| NHL015-157455075 | 89 | NHL015 | NHL | North | 2097403.0311 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.08564 | 0.086409 | 0.087177 | 0.087946 | 0.088714 | 0.08854 | 0.088367 | 0.088193 | 0.088019 | 0.087846 | 0.087672 | 0.087498 | 0.087324 | 0.087151 | 0.086977 | 0.086803 | 0.08663 | 0.086456 | 0.086282 | 0.086108 | 0.0026895 | 0.0027136 | 0.0027197 | 0.00272 | 0.0026936 | 0.0026406 | 0.0026196 | 0.0026065 | 0.0025595 | 0.0025545 | 0.0025494 | 0.0025444 | 0.0025393 | 0.0025343 | 0.0025292 | 0.0025241 | 0.0025191 | 0.002514 | 0.002509 | 0.0025039 | 27117.7471 | 4149.7923 | 1020.8643 | 156.2215 | 98096.2108 | 98096.2108 | 2097403.0311 | 98096.2108
| NHL015-157999738 | 128 | NHL015 | NHL | North | 3016489.7525 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.26574 | 0.26828 | 0.27081 | 0.27335 | 0.27589 | 0.27474 | 0.27359 | 0.27243 | 0.27128 | 0.27013 | 0.26898 | 0.26783 | 0.26668 | 0.26553 | 0.26438 | 0.26323 | 0.26207 | 0.26092 | 0.25977 | 0.25862 | 0.0083454 | 0.0084251 | 0.0084488 | 0.0084543 | 0.0083767 | 0.0081938 | 0.0081103 | 0.0080517 | 0.0078886 | 0.0078552 | 0.0078217 | 0.0077882 | 0.0077547 | 0.0077213 | 0.0076878 | 0.0076543 | 0.0076209 | 0.0075874 | 0.0075539 | 0.0075204 | 27117.7471 | 4149.7923 | 3138.5292 | 480.2849 | 325224.7524 | 325224.7524 | 3016489.7525 | 325224.7524
| NHL015-157999871 | 72 | NHL015 | NHL | North | 1696775.4858 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.066259 | 0.066949 | 0.067639 | 0.06833 | 0.06902 | 0.068718 | 0.068416 | 0.068114 | 0.067813 | 0.067511 | 0.067209 | 0.066907 | 0.066605 | 0.066303 | 0.066002 | 0.0657 | 0.065398 | 0.065096 | 0.064794 | 0.064492 | 0.0020808 | 0.0021025 | 0.0021102 | 0.0021133 | 0.0020956 | 0.0020495 | 0.0020282 | 0.0020131 | 0.0019719 | 0.0019631 | 0.0019544 | 0.0019456 | 0.0019368 | 0.001928 | 0.0019193 | 0.0019105 | 0.0019017 | 0.0018929 | 0.0018841 | 0.0018754 | 27117.7471 | 4149.7923 | 783.9331 | 119.9642 | 86578.3281 | 86578.3281 | 1696775.4858 | 86578.3281
| NHL015-158004096 | 36 | NHL015 | NHL | North | 848387.7429 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27117.7471 | 4149.7923 | 0 | 0 | 0 | 0 | 848387.7429 | 0
| NHL015-158004251 | 56 | NHL015 | NHL | North | 1319714.2667 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.040403 | 0.040781 | 0.041159 | 0.041537 | 0.041915 | 0.041767 | 0.041619 | 0.041471 | 0.041324 | 0.041176 | 0.041028 | 0.04088 | 0.040732 | 0.040585 | 0.040437 | 0.040289 | 0.040141 | 0.039993 | 0.039845 | 0.039698 | 0.0012688 | 0.0012807 | 0.0012841 | 0.0012847 | 0.0012727 | 0.0012457 | 0.0012338 | 0.0012257 | 0.0012016 | 0.0011973 | 0.0011931 | 0.0011888 | 0.0011845 | 0.0011802 | 0.0011759 | 0.0011716 | 0.0011673 | 0.001163 | 0.0011587 | 0.0011544 | 27117.7471 | 4149.7923 | 478.4399 | 73.215 | 60069.4278 | 60069.4278 | 1319714.2667 | 60069.4278
| NHL015-158004482 | 29 | NHL015 | NHL | North | 683423.4596 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.038235 | 0.038525 | 0.038815 | 0.039105 | 0.039396 | 0.039287 | 0.039179 | 0.03907 | 0.038962 | 0.038854 | 0.038745 | 0.038637 | 0.038529 | 0.03842 | 0.038312 | 0.038204 | 0.038095 | 0.037987 | 0.037879 | 0.03777 | 0.0012008 | 0.0012099 | 0.001211 | 0.0012095 | 0.0011962 | 0.0011717 | 0.0011614 | 0.0011547 | 0.001133 | 0.0011298 | 0.0011267 | 0.0011235 | 0.0011204 | 0.0011172 | 0.0011141 | 0.0011109 | 0.0011078 | 0.0011046 | 0.0011015 | 0.0010983 | 27117.7471 | 4149.7923 | 451.9625 | 69.1632 | 38203.0574 | 38203.0574 | 683423.4596 | 38203.0574
| NHL015-158005276 | 101 | NHL015 | NHL | North | 2380198.9454 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.030814 | 0.03112 | 0.031426 | 0.031733 | 0.032039 | 0.031933 | 0.031826 | 0.03172 | 0.031613 | 0.031507 | 0.0314 | 0.031294 | 0.031187 | 0.031081 | 0.030975 | 0.030868 | 0.030762 | 0.030655 | 0.030549 | 0.030442 | 0.00096768 | 0.0009773 | 0.00098043 | 0.00098144 | 0.0009728 | 0.00095236 | 0.00094347 | 0.00093747 | 0.00091928 | 0.00091618 | 0.00091309 | 0.00090999 | 0.0009069 | 0.0009038 | 0.00090071 | 0.00089761 | 0.00089451 | 0.00089142 | 0.00088832 | 0.00088523 | 27117.7471 | 4149.7923 | 365.9459 | 56.0002 | 41434.7749 | 41434.7749 | 2380198.9454 | 41434.7749
| NHL015-158007892 | 65 | NHL015 | NHL | North | 1531811.2025 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.035949 | 0.036256 | 0.036562 | 0.036868 | 0.037174 | 0.037082 | 0.03699 | 0.036898 | 0.036806 | 0.036714 | 0.036621 | 0.036529 | 0.036437 | 0.036345 | 0.036253 | 0.036161 | 0.036068 | 0.035976 | 0.035884 | 0.035792 | 0.001129 | 0.0011386 | 0.0011406 | 0.0011403 | 0.0011287 | 0.0011059 | 0.0010966 | 0.0010905 | 0.0010703 | 0.0010676 | 0.0010649 | 0.0010622 | 0.0010596 | 0.0010569 | 0.0010542 | 0.0010515 | 0.0010488 | 0.0010462 | 0.0010435 | 0.0010408 | 27117.7471 | 4149.7923 | 426.7958 | 65.312 | 47567.3793 | 47567.3793 | 1531811.2025 | 47567.3793
| NHL015-158008058 | 86 | NHL015 | NHL | North | 2026704.0525 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.35255 | 0.35534 | 0.35812 | 0.3609 | 0.36368 | 0.3629 | 0.36212 | 0.36134 | 0.36056 | 0.35978 | 0.359 | 0.35823 | 0.35745 | 0.35667 | 0.35589 | 0.35511 | 0.35433 | 0.35355 | 0.35277 | 0.35199 | 0.011072 | 0.011159 | 0.011172 | 0.011162 | 0.011042 | 0.010823 | 0.010735 | 0.010679 | 0.010485 | 0.010462 | 0.010439 | 0.010417 | 0.010394 | 0.010371 | 0.010349 | 0.010326 | 0.010303 | 0.010281 | 0.010258 | 0.010235 | 27117.7471 | 4149.7923 | 4184.1225 | 640.2906 | 476775.2378 | 476775.2378 | 2026704.0525 | 476775.2378
| NHL015-158050824 | 121 | NHL015 | NHL | North | 2851525.4692 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.11419 | 0.11515 | 0.11612 | 0.11708 | 0.11804 | 0.11789 | 0.11774 | 0.11759 | 0.11744 | 0.1173 | 0.11715 | 0.117 | 0.11685 | 0.1167 | 0.11655 | 0.1164 | 0.11625 | 0.1161 | 0.11596 | 0.11581 | 0.0035861 | 0.0036163 | 0.0036225 | 0.003621 | 0.003584 | 0.003516 | 0.0034904 | 0.0034754 | 0.0034151 | 0.0034108 | 0.0034065 | 0.0034022 | 0.0033978 | 0.0033935 | 0.0033892 | 0.0033848 | 0.0033805 | 0.0033762 | 0.0033719 | 0.0033675 | 27117.7471 | 4149.7923 | 1363.5283 | 208.6589 | 160329.9528 | 160329.9528 | 2851525.4692 | 160329.9528
| NHL015-158051013 | 86 | NHL015 | NHL | North | 2026704.0525 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.00056168 | 0.00056756 | 0.00057344 | 0.00057932 | 0.0005852 | 0.0005838 | 0.0005824 | 0.000581 | 0.0005796 | 0.0005782 | 0.0005768 | 0.0005754 | 0.000574 | 0.0005726 | 0.0005712 | 0.0005698 | 0.0005684 | 0.000567 | 0.0005656 | 0.0005642 | 1.7639e-05 | 1.7824e-05 | 1.789e-05 | 1.7917e-05 | 1.7768e-05 | 1.7411e-05 | 1.7265e-05 | 1.7171e-05 | 1.6854e-05 | 1.6813e-05 | 1.6773e-05 | 1.6732e-05 | 1.6691e-05 | 1.6651e-05 | 1.661e-05 | 1.6569e-05 | 1.6528e-05 | 1.6488e-05 | 1.6447e-05 | 1.6406e-05 | 27117.7471 | 4149.7923 | 6.713 | 1.0273 | 1202.1042 | 1202.1042 | 2026704.0525 | 1202.1042
| NHL015-158071333 | 110 | NHL015 | NHL | North | 2592295.8811 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.14499 | 0.14625 | 0.14751 | 0.14878 | 0.15004 | 0.14965 | 0.14926 | 0.14888 | 0.14849 | 0.1481 | 0.14772 | 0.14733 | 0.14694 | 0.14655 | 0.14617 | 0.14578 | 0.14539 | 0.14501 | 0.14462 | 0.14423 | 0.0045532 | 0.0045929 | 0.0046021 | 0.0046014 | 0.0045556 | 0.0044632 | 0.0044249 | 0.0044 | 0.0043179 | 0.0043067 | 0.0042954 | 0.0042842 | 0.0042729 | 0.0042616 | 0.0042504 | 0.0042391 | 0.0042279 | 0.0042166 | 0.0042053 | 0.0041941 | 27117.7471 | 4149.7923 | 1721.4886 | 263.4371 | 153326.2109 | 153326.2109 | 2592295.8811 | 153326.2109
| NHL015-158071498 | 18 | NHL015 | NHL | North | 424193.8715 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.030586 | 0.03068 | 0.030774 | 0.030868 | 0.030962 | 0.030855 | 0.030749 | 0.030642 | 0.030535 | 0.030428 | 0.030321 | 0.030215 | 0.030108 | 0.030001 | 0.029894 | 0.029787 | 0.029681 | 0.029574 | 0.029467 | 0.02936 | 0.00096052 | 0.00096348 | 0.00096008 | 0.0009547 | 0.0009401 | 0.00092023 | 0.00091153 | 0.00090561 | 0.00088792 | 0.00088482 | 0.00088171 | 0.00087861 | 0.0008755 | 0.0008724 | 0.00086929 | 0.00086618 | 0.00086308 | 0.00085997 | 0.00085687 | 0.00085376 | 27117.7471 | 4149.7923 | 355.0504 | 54.3329 | 20692.7283 | 20692.7283 | 424193.8715 | 20692.7283
| NHL015-158071668 | 130 | NHL015 | NHL | North | 3063622.4049 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.044599 | 0.045022 | 0.045444 | 0.045867 | 0.046289 | 0.046206 | 0.046122 | 0.046039 | 0.045956 | 0.045873 | 0.045789 | 0.045706 | 0.045623 | 0.045539 | 0.045456 | 0.045373 | 0.045289 | 0.045206 | 0.045123 | 0.045039 | 0.0014006 | 0.0014139 | 0.0014177 | 0.0014186 | 0.0014055 | 0.001378 | 0.0013673 | 0.0013607 | 0.0013363 | 0.0013339 | 0.0013315 | 0.0013291 | 0.0013267 | 0.0013242 | 0.0013218 | 0.0013194 | 0.001317 | 0.0013145 | 0.0013121 | 0.0013097 | 27117.7471 | 4149.7923 | 532.9108 | 81.5506 | 84151.0559 | 84151.0559 | 3063622.4049 | 84151.0559
| NHL015-158092505 | 66 | NHL015 | NHL | North | 1555377.5287 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.022575 | 0.022788 | 0.023002 | 0.023215 | 0.023429 | 0.023369 | 0.023309 | 0.02325 | 0.02319 | 0.023131 | 0.023071 | 0.023011 | 0.022952 | 0.022892 | 0.022832 | 0.022773 | 0.022713 | 0.022653 | 0.022594 | 0.022534 | 0.00070894 | 0.00071565 | 0.0007176 | 0.00071801 | 0.00071136 | 0.00069696 | 0.000691 | 0.00068714 | 0.00067435 | 0.00067261 | 0.00067088 | 0.00066914 | 0.00066741 | 0.00066567 | 0.00066394 | 0.0006622 | 0.00066047 | 0.00065873 | 0.000657 | 0.00065527 | 27117.7471 | 4149.7923 | 268.7282 | 41.1231 | 43083.412 | 43083.412 | 1555377.5287 | 43083.412
| NHL015-158092654 | 61 | NHL015 | NHL | North | 1437545.8977 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.15155 | 0.15304 | 0.15454 | 0.15603 | 0.15753 | 0.15691 | 0.15629 | 0.15567 | 0.15505 | 0.15443 | 0.15381 | 0.15319 | 0.15257 | 0.15195 | 0.15132 | 0.1507 | 0.15008 | 0.14946 | 0.14884 | 0.14822 | 0.0047593 | 0.0048062 | 0.0048212 | 0.0048258 | 0.004783 | 0.0046796 | 0.0046331 | 0.0046007 | 0.0045086 | 0.0044905 | 0.0044725 | 0.0044545 | 0.0044364 | 0.0044184 | 0.0044004 | 0.0043823 | 0.0043643 | 0.0043462 | 0.0043282 | 0.0043102 | 27117.7471 | 4149.7923 | 1793.7983 | 274.5025 | 132879.779 | 132879.779 | 1437545.8977 | 132879.779
| NHL015-158130266 | 15 | NHL015 | NHL | North | 353494.8929 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.01385 | 0.013978 | 0.014105 | 0.014233 | 0.01436 | 0.014313 | 0.014266 | 0.014218 | 0.014171 | 0.014123 | 0.014076 | 0.014028 | 0.013981 | 0.013934 | 0.013886 | 0.013839 | 0.013791 | 0.013744 | 0.013696 | 0.013649 | 0.00043495 | 0.00043895 | 0.00044005 | 0.0004402 | 0.00043602 | 0.00042687 | 0.0004229 | 0.00042021 | 0.00041207 | 0.00041069 | 0.00040931 | 0.00040793 | 0.00040655 | 0.00040517 | 0.0004038 | 0.00040242 | 0.00040104 | 0.00039966 | 0.00039828 | 0.0003969 | 27117.7471 | 4149.7923 | 164.1174 | 25.1147 | 7972.5 | 7972.5 | 353494.8929 | 7972.5
| NHL015-158130348 | 19 | NHL015 | NHL | North | 447760.1976 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.015015 | 0.015136 | 0.015258 | 0.015379 | 0.015501 | 0.015454 | 0.015408 | 0.015362 | 0.015316 | 0.01527 | 0.015224 | 0.015178 | 0.015132 | 0.015086 | 0.01504 | 0.014994 | 0.014948 | 0.014902 | 0.014856 | 0.01481 | 0.00047152 | 0.00047533 | 0.000476 | 0.00047565 | 0.00047064 | 0.00046092 | 0.00045678 | 0.00045403 | 0.00044538 | 0.00044404 | 0.0004427 | 0.00044137 | 0.00044003 | 0.00043869 | 0.00043735 | 0.00043601 | 0.00043467 | 0.00043333 | 0.00043199 | 0.00043065 | 27117.7471 | 4149.7923 | 177.5732 | 27.1738 | 19667.7279 | 19667.7279 | 447760.1976 | 19667.7279
| NHL015-158145995 | 78 | NHL015 | NHL | North | 1838173.443 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.28969 | 0.29231 | 0.29492 | 0.29754 | 0.30016 | 0.29895 | 0.29775 | 0.29654 | 0.29534 | 0.29413 | 0.29292 | 0.29172 | 0.29051 | 0.28931 | 0.2881 | 0.2869 | 0.28569 | 0.28448 | 0.28328 | 0.28207 | 0.0090974 | 0.0091796 | 0.0092009 | 0.0092025 | 0.0091137 | 0.008916 | 0.0088266 | 0.0087642 | 0.0085881 | 0.008553 | 0.0085179 | 0.0084829 | 0.0084478 | 0.0084128 | 0.0083777 | 0.0083426 | 0.0083076 | 0.0082725 | 0.0082375 | 0.0082024 | 27117.7471 | 4149.7923 | 3418.4643 | 523.123 | 222028.5351 | 222028.5351 | 1838173.443 | 222028.5351
| NHL015-158146107 | 87 | NHL015 | NHL | North | 2050270.3787 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.1887 | 0.19055 | 0.19239 | 0.19423 | 0.19608 | 0.1955 | 0.19493 | 0.19436 | 0.19379 | 0.19321 | 0.19264 | 0.19207 | 0.19149 | 0.19092 | 0.19035 | 0.18978 | 0.1892 | 0.18863 | 0.18806 | 0.18748 | 0.005926 | 0.005984 | 0.0060021 | 0.0060073 | 0.0059535 | 0.0058308 | 0.0057787 | 0.0057442 | 0.0056351 | 0.0056184 | 0.0056018 | 0.0055851 | 0.0055685 | 0.0055518 | 0.0055351 | 0.0055185 | 0.0055018 | 0.0054852 | 0.0054685 | 0.0054518 | 27117.7471 | 4149.7923 | 2244.3299 | 343.4468 | 271022.5536 | 271022.5536 | 2050270.3787 | 271022.5536
| NHL015-158377999 | 79 | NHL015 | NHL | North | 1861739.7692 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.078943 | 0.079691 | 0.08044 | 0.081188 | 0.081936 | 0.081779 | 0.081623 | 0.081467 | 0.08131 | 0.081154 | 0.080998 | 0.080841 | 0.080685 | 0.080529 | 0.080372 | 0.080216 | 0.08006 | 0.079903 | 0.079747 | 0.079591 | 0.0024792 | 0.0025026 | 0.0025095 | 0.002511 | 0.0024878 | 0.002439 | 0.0024197 | 0.0024077 | 0.0023644 | 0.0023599 | 0.0023553 | 0.0023508 | 0.0023462 | 0.0023417 | 0.0023371 | 0.0023326 | 0.0023281 | 0.0023235 | 0.002319 | 0.0023144 | 27117.7471 | 4149.7923 | 942.7891 | 144.2737 | 86849.8442 | 86849.8442 | 1861739.7692 | 86849.8442
| NHL015-164675628 | 12 | NHL015 | NHL | North | 282795.9143 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.027137 | 0.027374 | 0.027611 | 0.027848 | 0.028085 | 0.028018 | 0.027951 | 0.027884 | 0.027817 | 0.027751 | 0.027684 | 0.027617 | 0.02755 | 0.027483 | 0.027417 | 0.02735 | 0.027283 | 0.027216 | 0.027149 | 0.027083 | 0.00085222 | 0.00085966 | 0.0008614 | 0.00086129 | 0.00085273 | 0.00083561 | 0.0008286 | 0.00082411 | 0.0008089 | 0.00080696 | 0.00080502 | 0.00080307 | 0.00080113 | 0.00079919 | 0.00079725 | 0.0007953 | 0.00079336 | 0.00079142 | 0.00078948 | 0.00078753 | 27117.7471 | 4149.7923 | 322.5547 | 49.3601 | 14103.5192 | 14103.5192 | 282795.9143 | 14103.5192
| NHL015-24600722 | 200 | NHL015 | NHL | North | 4713265.2384 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 26.289 | 26.4891 | 26.6893 | 26.8894 | 27.0895 | 26.9846 | 26.8798 | 26.7749 | 26.6701 | 26.5652 | 26.4604 | 26.3555 | 26.2507 | 26.1458 | 26.041 | 25.9361 | 25.8313 | 25.7264 | 25.6216 | 25.5167 | 0.82558 | 0.83187 | 0.83264 | 0.83164 | 0.82251 | 0.80479 | 0.79684 | 0.79133 | 0.77554 | 0.77249 | 0.76944 | 0.76639 | 0.76334 | 0.76029 | 0.75724 | 0.7542 | 0.75115 | 0.7481 | 0.74505 | 0.742 | 27117.7471 | 4149.7923 | 309036.753 | 47291.4775 | 2015030.4763 | 2015030.4763 | 4713265.2384 | 2015030.4763
| NHL015-24600904 | 224 | NHL015 | NHL | North | 5278857.067 | 0.001128 | 0.001128 | 0.0011206 | 0.0011109 | 0.0010906 | 0.0010713 | 0.0010648 | 0.0010616 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 0.0010445 | 6.7627 | 6.8253 | 6.8878 | 6.9504 | 7.013 | 6.9837 | 6.9544 | 6.9252 | 6.8959 | 6.8666 | 6.8373 | 6.8081 | 6.7788 | 6.7495 | 6.7202 | 6.691 | 6.6617 | 6.6324 | 6.6032 | 6.5739 | 0.21238 | 0.21434 | 0.21488 | 0.21496 | 0.21293 | 0.20828 | 0.20616 | 0.20467 | 0.20052 | 0.19967 | 0.19882 | 0.19797 | 0.19712 | 0.19627 | 0.19542 | 0.19457 | 0.19372 | 0.19286 | 0.19201 | 0.19116 | 27117.7471 | 4149.7923 | 79795.0348 | 12210.9265 | 898625.0325 | 898625.0325 | 5278857.067 | 898625.0325
| NHL016-15417067 | 157 | NHL016 | NHL | North | 3699913.2121 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 15.9967 | 16.1199 | 16.2431 | 16.3664 | 16.4896 | 16.4415 | 16.3935 | 16.3454 | 16.2974 | 16.2493 | 16.2013 | 16.1532 | 16.1052 | 16.0571 | 16.0091 | 15.961 | 15.913 | 15.8649 | 15.8169 | 15.7688 | 0.58239 | 0.58364 | 0.58321 | 0.57941 | 0.57218 | 0.56061 | 0.55518 | 0.54912 | 0.5372 | 0.53561 | 0.53403 | 0.53244 | 0.53086 | 0.52928 | 0.52769 | 0.52611 | 0.52452 | 0.52294 | 0.52136 | 0.51977 | 27117.7471 | 4149.7923 | 215537.7658 | 32983.4536 | 659014.0127 | 659014.0127 | 3699913.2121 | 659014.0127
| NHL016-157284541 | 43 | NHL016 | NHL | North | 1013352.0262 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.063415 | 0.064001 | 0.064587 | 0.065172 | 0.065758 | 0.065563 | 0.065367 | 0.065171 | 0.064976 | 0.06478 | 0.064585 | 0.064389 | 0.064193 | 0.063998 | 0.063802 | 0.063606 | 0.063411 | 0.063215 | 0.06302 | 0.062824 | 0.0023087 | 0.0023172 | 0.002319 | 0.0023073 | 0.0022818 | 0.0022355 | 0.0022137 | 0.0021894 | 0.0021417 | 0.0021353 | 0.0021288 | 0.0021224 | 0.0021159 | 0.0021095 | 0.002103 | 0.0020966 | 0.0020902 | 0.0020837 | 0.0020773 | 0.0020708 | 27117.7471 | 4149.7923 | 858.3956 | 131.3591 | 55497.4227 | 55497.4227 | 1013352.0262 | 55497.4227
| NHL016-157284640 | 50 | NHL016 | NHL | North | 1178316.3096 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.049511 | 0.049958 | 0.050405 | 0.050853 | 0.0513 | 0.051157 | 0.051015 | 0.050872 | 0.05073 | 0.050587 | 0.050445 | 0.050303 | 0.05016 | 0.050018 | 0.049875 | 0.049733 | 0.04959 | 0.049448 | 0.049305 | 0.049163 | 0.0018025 | 0.0018088 | 0.0018098 | 0.0018003 | 0.0017801 | 0.0017443 | 0.0017277 | 0.001709 | 0.0016722 | 0.0016675 | 0.0016628 | 0.0016581 | 0.0016534 | 0.0016487 | 0.001644 | 0.0016393 | 0.0016346 | 0.0016299 | 0.0016252 | 0.0016205 | 27117.7471 | 4149.7923 | 670.4079 | 102.5916 | 45095.2224 | 45095.2224 | 1178316.3096 | 45095.2224
| NHL016-157284729 | 22 | NHL016 | NHL | North | 518459.1762 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.020893 | 0.02109 | 0.021288 | 0.021486 | 0.021683 | 0.02159 | 0.021496 | 0.021403 | 0.021309 | 0.021215 | 0.021122 | 0.021028 | 0.020935 | 0.020841 | 0.020748 | 0.020654 | 0.020561 | 0.020467 | 0.020373 | 0.02028 | 0.00076064 | 0.0007636 | 0.00076434 | 0.00076064 | 0.0007524 | 0.00073614 | 0.00072798 | 0.00071901 | 0.00070239 | 0.0006993 | 0.00069622 | 0.00069314 | 0.00069005 | 0.00068697 | 0.00068389 | 0.0006808 | 0.00067772 | 0.00067464 | 0.00067155 | 0.00066847 | 27117.7471 | 4149.7923 | 281.1182 | 43.0191 | 26341.6532 | 26341.6532 | 518459.1762 | 26341.6532
| NHL016-157284831 | 77 | NHL016 | NHL | North | 1814607.1168 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.083328 | 0.084191 | 0.085053 | 0.085916 | 0.086779 | 0.086456 | 0.086133 | 0.08581 | 0.085487 | 0.085165 | 0.084842 | 0.084519 | 0.084196 | 0.083874 | 0.083551 | 0.083228 | 0.082905 | 0.082582 | 0.08226 | 0.081937 | 0.0030337 | 0.0030482 | 0.0030538 | 0.0030416 | 0.0030112 | 0.0029479 | 0.002917 | 0.0028828 | 0.0028178 | 0.0028072 | 0.0027966 | 0.0027859 | 0.0027753 | 0.0027646 | 0.002754 | 0.0027434 | 0.0027327 | 0.0027221 | 0.0027115 | 0.0027008 | 27117.7471 | 4149.7923 | 1127.7542 | 172.5787 | 105687.2466 | 105687.2466 | 1814607.1168 | 105687.2466
| NHL016-157328241 | 35 | NHL016 | NHL | North | 824821.4167 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.030281 | 0.030596 | 0.03091 | 0.031225 | 0.03154 | 0.031362 | 0.031185 | 0.031007 | 0.030829 | 0.030651 | 0.030474 | 0.030296 | 0.030118 | 0.02994 | 0.029763 | 0.029585 | 0.029407 | 0.029229 | 0.029052 | 0.028874 | 0.0011024 | 0.0011077 | 0.0011098 | 0.0011055 | 0.0010944 | 0.0010694 | 0.0010561 | 0.0010417 | 0.0010162 | 0.0010103 | 0.0010045 | 0.00099862 | 0.00099276 | 0.0009869 | 0.00098104 | 0.00097518 | 0.00096932 | 0.00096346 | 0.0009576 | 0.00095174 | 27117.7471 | 4149.7923 | 405.9474 | 62.1216 | 24202.3943 | 24202.3943 | 824821.4167 | 24202.3943
| NHL016-157328461 | 45 | NHL016 | NHL | North | 1060484.6786 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.080587 | 0.081408 | 0.082228 | 0.083048 | 0.083869 | 0.083598 | 0.083328 | 0.083057 | 0.082787 | 0.082517 | 0.082246 | 0.081976 | 0.081705 | 0.081435 | 0.081164 | 0.080894 | 0.080623 | 0.080353 | 0.080082 | 0.079812 | 0.0029339 | 0.0029475 | 0.0029524 | 0.0029401 | 0.0029102 | 0.0028505 | 0.002822 | 0.0027903 | 0.0027288 | 0.0027199 | 0.002711 | 0.0027021 | 0.0026932 | 0.0026843 | 0.0026753 | 0.0026664 | 0.0026575 | 0.0026486 | 0.0026397 | 0.0026308 | 27117.7471 | 4149.7923 | 1092.7619 | 167.2239 | 83793.9309 | 83793.9309 | 1060484.6786 | 83793.9309
| NHL016-157328563 | 37 | NHL016 | NHL | North | 871954.0691 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.025074 | 0.025328 | 0.025581 | 0.025835 | 0.026089 | 0.025973 | 0.025856 | 0.02574 | 0.025624 | 0.025508 | 0.025391 | 0.025275 | 0.025159 | 0.025043 | 0.024926 | 0.02481 | 0.024694 | 0.024577 | 0.024461 | 0.024345 | 0.00091286 | 0.00091701 | 0.0009185 | 0.00091463 | 0.00090528 | 0.00088559 | 0.00087565 | 0.00086474 | 0.00084462 | 0.00084078 | 0.00083695 | 0.00083312 | 0.00082929 | 0.00082545 | 0.00082162 | 0.00081779 | 0.00081396 | 0.00081012 | 0.00080629 | 0.00080246 | 27117.7471 | 4149.7923 | 337.848 | 51.7004 | 18791.3861 | 18791.3861 | 871954.0691 | 18791.3861
| NHL016-162991101 | 47 | NHL016 | NHL | North | 1107617.331 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.022069 | 0.022297 | 0.022526 | 0.022754 | 0.022982 | 0.022865 | 0.022747 | 0.02263 | 0.022512 | 0.022395 | 0.022277 | 0.02216 | 0.022042 | 0.021925 | 0.021808 | 0.02169 | 0.021573 | 0.021455 | 0.021338 | 0.02122 | 0.00080347 | 0.0008073 | 0.00080878 | 0.00080554 | 0.00079746 | 0.00077961 | 0.00077035 | 0.00076024 | 0.00074205 | 0.00073818 | 0.00073431 | 0.00073044 | 0.00072657 | 0.0007227 | 0.00071883 | 0.00071495 | 0.00071108 | 0.00070721 | 0.00070334 | 0.00069947 | 27117.7471 | 4149.7923 | 296.5936 | 45.3873 | 59368.2111 | 59368.2111 | 1107617.331 | 59368.2111
| NHL016-163161231 | 51 | NHL016 | NHL | North | 1201882.6358 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.097223 | 0.098248 | 0.099272 | 0.1003 | 0.10132 | 0.10117 | 0.10103 | 0.10088 | 0.10073 | 0.10058 | 0.10044 | 0.10029 | 0.10014 | 0.099995 | 0.099847 | 0.0997 | 0.099553 | 0.099406 | 0.099258 | 0.099111 | 0.0035396 | 0.0035572 | 0.0035643 | 0.0035507 | 0.0035158 | 0.0034497 | 0.0034213 | 0.003389 | 0.0033203 | 0.0033155 | 0.0033106 | 0.0033057 | 0.0033009 | 0.003296 | 0.0032912 | 0.0032863 | 0.0032815 | 0.0032766 | 0.0032718 | 0.0032669 | 27117.7471 | 4149.7923 | 1331.5035 | 203.7582 | 124013.7137 | 124013.7137 | 1201882.6358 | 124013.7137
| NHL016-163161483 | 16 | NHL016 | NHL | North | 377061.2191 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.00033322 | 0.00033654 | 0.00033986 | 0.00034318 | 0.0003465 | 0.00034566 | 0.00034482 | 0.00034398 | 0.00034314 | 0.0003423 | 0.00034146 | 0.00034062 | 0.00033978 | 0.00033894 | 0.0003381 | 0.00033726 | 0.00033642 | 0.00033558 | 0.00033474 | 0.0003339 | 1.2132e-05 | 1.2185e-05 | 1.2203e-05 | 1.2149e-05 | 1.2023e-05 | 1.1786e-05 | 1.1678e-05 | 1.1556e-05 | 1.1311e-05 | 1.1283e-05 | 1.1255e-05 | 1.1228e-05 | 1.12e-05 | 1.1172e-05 | 1.1144e-05 | 1.1117e-05 | 1.1089e-05 | 1.1061e-05 | 1.1034e-05 | 1.1006e-05 | 27117.7471 | 4149.7923 | 4.5334 | 0.69374 | 264.8849 | 264.8849 | 377061.2191 | 264.8849
| NHL016-24601854 | 268 | NHL016 | NHL | North | 6315775.4194 | 0.0013077 | 0.0013005 | 0.0012897 | 0.0012716 | 0.0012464 | 0.0012247 | 0.0012165 | 0.0012067 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 0.001184 | 3.1142 | 3.1433 | 3.1725 | 3.2016 | 3.2307 | 3.2193 | 3.2079 | 3.1965 | 3.185 | 3.1736 | 3.1622 | 3.1507 | 3.1393 | 3.1279 | 3.1165 | 3.105 | 3.0936 | 3.0822 | 3.0708 | 3.0593 | 0.11338 | 0.11381 | 0.11391 | 0.11335 | 0.11211 | 0.10977 | 0.10864 | 0.10738 | 0.10499 | 0.10461 | 0.10423 | 0.10386 | 0.10348 | 0.1031 | 0.10273 | 0.10235 | 0.10197 | 0.1016 | 0.10122 | 0.10084 | 27117.7471 | 4149.7923 | 42052.0168 | 6435.1634 | 1646262.1339 | 1646262.1339 | 6315775.4194 | 1646262.1339
| NHL031-111738437 | 389 | NHL031 | NHL | North | 9167300.8886 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 4.4608 | 4.4945 | 4.5281 | 4.5618 | 4.5954 | 4.5671 | 4.5388 | 4.5105 | 4.4821 | 4.4538 | 4.4255 | 4.3972 | 4.3688 | 4.3405 | 4.3122 | 4.2839 | 4.2555 | 4.2272 | 4.1989 | 4.1706 | 0.18408 | 0.18355 | 0.18351 | 0.18203 | 0.17954 | 0.17625 | 0.17393 | 0.17125 | 0.16658 | 0.16553 | 0.16447 | 0.16342 | 0.16237 | 0.16132 | 0.16026 | 0.15921 | 0.15816 | 0.1571 | 0.15605 | 0.155 | 27117.7471 | 4149.7923 | 66701.272 | 10207.2057 | 1882648.4896 | 1882648.4896 | 9167300.8886 | 1882648.4896
| NHL031-15417259 | 164 | NHL031 | NHL | North | 3864877.4955 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 13.3092 | 13.4217 | 13.5343 | 13.6468 | 13.7594 | 13.7057 | 13.652 | 13.5982 | 13.5445 | 13.4908 | 13.4371 | 13.3834 | 13.3297 | 13.276 | 13.2222 | 13.1685 | 13.1148 | 13.0611 | 13.0074 | 12.9537 | 0.54921 | 0.54813 | 0.5485 | 0.54454 | 0.53757 | 0.52891 | 0.52315 | 0.51628 | 0.50338 | 0.50139 | 0.49939 | 0.49739 | 0.4954 | 0.4934 | 0.49141 | 0.48941 | 0.48741 | 0.48542 | 0.48342 | 0.48142 | 27117.7471 | 4149.7923 | 201868.5044 | 30891.6649 | 841090.7037 | 841090.7037 | 3864877.4955 | 841090.7037
| NHL031-158072303 | 76 | NHL031 | NHL | North | 1791040.7906 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.068217 | 0.068732 | 0.069247 | 0.069761 | 0.070276 | 0.070019 | 0.069761 | 0.069504 | 0.069246 | 0.068989 | 0.068731 | 0.068474 | 0.068216 | 0.067959 | 0.067701 | 0.067443 | 0.067186 | 0.066928 | 0.066671 | 0.066413 | 0.002815 | 0.0028069 | 0.0028063 | 0.0027836 | 0.0027457 | 0.0027021 | 0.0026733 | 0.0026388 | 0.0025735 | 0.002564 | 0.0025544 | 0.0025448 | 0.0025353 | 0.0025257 | 0.0025161 | 0.0025065 | 0.002497 | 0.0024874 | 0.0024778 | 0.0024683 | 27117.7471 | 4149.7923 | 1032.9118 | 158.0651 | 93561.1622 | 93561.1622 | 1791040.7906 | 93561.1622
| NHL031-158072703 | 55 | NHL031 | NHL | North | 1296147.9405 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.082801 | 0.083483 | 0.084165 | 0.084847 | 0.085529 | 0.084974 | 0.08442 | 0.083865 | 0.083311 | 0.082756 | 0.082202 | 0.081647 | 0.081092 | 0.080538 | 0.079983 | 0.079429 | 0.078874 | 0.078319 | 0.077765 | 0.07721 | 0.0034168 | 0.0034093 | 0.0034109 | 0.0033856 | 0.0033416 | 0.0032792 | 0.003235 | 0.0031841 | 0.0030962 | 0.0030756 | 0.003055 | 0.0030344 | 0.0030138 | 0.0029932 | 0.0029726 | 0.002952 | 0.0029314 | 0.0029108 | 0.0028901 | 0.0028695 | 27117.7471 | 4149.7923 | 1238.8282 | 189.5762 | 81173.5469 | 81173.5469 | 1296147.9405 | 81173.5469
| NHL031-158073136 | 24 | NHL031 | NHL | North | 565591.8286 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27117.7471 | 4149.7923 | 0 | 0 | 0 | 0 | 565591.8286 | 0
| NHL031-158078362 | 96 | NHL031 | NHL | North | 2262367.3144 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.088575 | 0.089344 | 0.090112 | 0.090881 | 0.09165 | 0.091066 | 0.090482 | 0.089898 | 0.089315 | 0.088731 | 0.088147 | 0.087563 | 0.086979 | 0.086395 | 0.085811 | 0.085227 | 0.084644 | 0.08406 | 0.083476 | 0.082892 | 0.0036551 | 0.0036487 | 0.003652 | 0.0036264 | 0.0035807 | 0.0035143 | 0.0034673 | 0.0034131 | 0.0033194 | 0.0032977 | 0.003276 | 0.0032543 | 0.0032326 | 0.0032109 | 0.0031892 | 0.0031675 | 0.0031458 | 0.0031241 | 0.0031024 | 0.0030807 | 27117.7471 | 4149.7923 | 1327.8507 | 203.1992 | 115422.4965 | 115422.4965 | 2262367.3144 | 115422.4965
| NHL031-158078443 | 43 | NHL031 | NHL | North | 1013352.0262 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.0083404 | 0.0084204 | 0.0085005 | 0.0085806 | 0.0086607 | 0.0086135 | 0.0085663 | 0.0085191 | 0.008472 | 0.0084248 | 0.0083776 | 0.0083304 | 0.0082832 | 0.008236 | 0.0081889 | 0.0081417 | 0.0080945 | 0.0080473 | 0.0080001 | 0.0079529 | 0.00034417 | 0.00034388 | 0.0003445 | 0.00034239 | 0.00033837 | 0.0003324 | 0.00032826 | 0.00032344 | 0.00031486 | 0.00031311 | 0.00031135 | 0.0003096 | 0.00030785 | 0.00030609 | 0.00030434 | 0.00030259 | 0.00030083 | 0.00029908 | 0.00029733 | 0.00029557 | 27117.7471 | 4149.7923 | 125.9861 | 19.2795 | 13628.1725 | 13628.1725 | 1013352.0262 | 13628.1725
| NHL031-158078533 | 60 | NHL031 | NHL | North | 1413979.5715 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.057494 | 0.058035 | 0.058575 | 0.059115 | 0.059656 | 0.059338 | 0.059019 | 0.058701 | 0.058383 | 0.058064 | 0.057746 | 0.057428 | 0.05711 | 0.056791 | 0.056473 | 0.056155 | 0.055837 | 0.055518 | 0.0552 | 0.054882 | 0.0023725 | 0.0023701 | 0.0023739 | 0.0023588 | 0.0023307 | 0.0022899 | 0.0022616 | 0.0022287 | 0.0021698 | 0.002158 | 0.0021461 | 0.0021343 | 0.0021225 | 0.0021107 | 0.0020988 | 0.002087 | 0.0020752 | 0.0020633 | 0.0020515 | 0.0020397 | 27117.7471 | 4149.7923 | 868.4186 | 132.8929 | 45373.2883 | 45373.2883 | 1413979.5715 | 45373.2883
| NHL031-158078653 | 66 | NHL031 | NHL | North | 1555377.5287 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.0014732 | 0.0014865 | 0.0014998 | 0.0015131 | 0.0015264 | 0.0015179 | 0.0015094 | 0.0015008 | 0.0014923 | 0.0014838 | 0.0014753 | 0.0014668 | 0.0014582 | 0.0014497 | 0.0014412 | 0.0014327 | 0.0014242 | 0.0014156 | 0.0014071 | 0.0013986 | 6.0792e-05 | 6.0707e-05 | 6.0782e-05 | 6.0376e-05 | 5.9636e-05 | 5.8576e-05 | 5.7839e-05 | 5.6982e-05 | 5.5462e-05 | 5.5146e-05 | 5.4829e-05 | 5.4512e-05 | 5.4196e-05 | 5.3879e-05 | 5.3562e-05 | 5.3246e-05 | 5.2929e-05 | 5.2612e-05 | 5.2296e-05 | 5.1979e-05 | 27117.7471 | 4149.7923 | 22.1979 | 3.3969 | 1382.0226 | 1382.0226 | 1555377.5287 | 1382.0226
| NHL031-158092744 | 36 | NHL031 | NHL | North | 848387.7429 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.023626 | 0.02385 | 0.024074 | 0.024299 | 0.024523 | 0.024433 | 0.024343 | 0.024253 | 0.024163 | 0.024073 | 0.023983 | 0.023893 | 0.023803 | 0.023713 | 0.023623 | 0.023533 | 0.023443 | 0.023353 | 0.023263 | 0.023173 | 0.00097495 | 0.00097402 | 0.00097566 | 0.00096957 | 0.00095809 | 0.00094288 | 0.00093282 | 0.00092079 | 0.00089801 | 0.00089467 | 0.00089132 | 0.00088798 | 0.00088463 | 0.00088129 | 0.00087794 | 0.0008746 | 0.00087125 | 0.00086791 | 0.00086456 | 0.00086122 | 27117.7471 | 4149.7923 | 359.9536 | 55.0832 | 29346.4402 | 29346.4402 | 848387.7429 | 29346.4402
| NHL031-158092870 | 31 | NHL031 | NHL | North | 730556.1119 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.019487 | 0.019654 | 0.019821 | 0.019988 | 0.020155 | 0.020028 | 0.019902 | 0.019775 | 0.019648 | 0.019521 | 0.019395 | 0.019268 | 0.019141 | 0.019015 | 0.018888 | 0.018761 | 0.018635 | 0.018508 | 0.018381 | 0.018254 | 0.00080413 | 0.00080264 | 0.00080327 | 0.00079756 | 0.00078745 | 0.00077291 | 0.00076264 | 0.00075078 | 0.00073023 | 0.00072552 | 0.00072081 | 0.0007161 | 0.00071139 | 0.00070668 | 0.00070197 | 0.00069726 | 0.00069256 | 0.00068785 | 0.00068314 | 0.00067843 | 27117.7471 | 4149.7923 | 292.1563 | 44.7083 | 29288.2118 | 29288.2118 | 730556.1119 | 29288.2118
| NHL031-158093033 | 496 | NHL031 | NHL | North | 11688897.7911 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.46747 | 0.47172 | 0.47597 | 0.48022 | 0.48446 | 0.48249 | 0.48051 | 0.47853 | 0.47655 | 0.47457 | 0.47259 | 0.47062 | 0.46864 | 0.46666 | 0.46468 | 0.4627 | 0.46072 | 0.45875 | 0.45677 | 0.45479 | 0.019291 | 0.019265 | 0.019289 | 0.019162 | 0.018928 | 0.01862 | 0.018413 | 0.018168 | 0.017711 | 0.017638 | 0.017564 | 0.01749 | 0.017417 | 0.017343 | 0.01727 | 0.017196 | 0.017123 | 0.017049 | 0.016976 | 0.016902 | 27117.7471 | 4149.7923 | 7098.3452 | 1086.2502 | 3066459.7367 | 3066459.7367 | 11688897.7911 | 3066459.7367
| NHL031-158103926 | 43 | NHL031 | NHL | North | 1013352.0262 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.078452 | 0.079131 | 0.079811 | 0.080491 | 0.081171 | 0.080865 | 0.080559 | 0.080253 | 0.079947 | 0.079641 | 0.079335 | 0.079029 | 0.078723 | 0.078417 | 0.078111 | 0.077805 | 0.077499 | 0.077193 | 0.076888 | 0.076582 | 0.0032374 | 0.0032316 | 0.0032345 | 0.0032118 | 0.0031713 | 0.0031207 | 0.003087 | 0.0030469 | 0.0029712 | 0.0029599 | 0.0029485 | 0.0029371 | 0.0029258 | 0.0029144 | 0.002903 | 0.0028916 | 0.0028803 | 0.0028689 | 0.0028575 | 0.0028462 | 27117.7471 | 4149.7923 | 1191.5192 | 182.3366 | 50446.0271 | 50446.0271 | 1013352.0262 | 50446.0271
| NHL031-158104228 | 28 | NHL031 | NHL | North | 659857.1334 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27117.7471 | 4149.7923 | 0 | 0 | 0 | 0 | 659857.1334 | 0
| NHL031-158104320 | 71 | NHL031 | NHL | North | 1673209.1596 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.00061975 | 0.00062601 | 0.00063227 | 0.00063854 | 0.0006448 | 0.00064032 | 0.00063584 | 0.00063136 | 0.00062688 | 0.0006224 | 0.00061792 | 0.00061344 | 0.00060896 | 0.00060448 | 0.0006 | 0.00059552 | 0.00059104 | 0.00058656 | 0.00058208 | 0.0005776 | 2.5574e-05 | 2.5566e-05 | 2.5624e-05 | 2.5479e-05 | 2.5192e-05 | 2.4711e-05 | 2.4366e-05 | 2.3971e-05 | 2.3298e-05 | 2.3132e-05 | 2.2965e-05 | 2.2799e-05 | 2.2632e-05 | 2.2466e-05 | 2.2299e-05 | 2.2133e-05 | 2.1966e-05 | 2.18e-05 | 2.1633e-05 | 2.1467e-05 | 27117.7471 | 4149.7923 | 9.3058 | 1.424 | 934.729 | 934.729 | 1673209.1596 | 934.729
| NHL031-158104465 | 28 | NHL031 | NHL | North | 659857.1334 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.033559 | 0.033889 | 0.034219 | 0.034549 | 0.034879 | 0.034745 | 0.034611 | 0.034477 | 0.034343 | 0.034209 | 0.034075 | 0.03394 | 0.033806 | 0.033672 | 0.033538 | 0.033404 | 0.03327 | 0.033136 | 0.033001 | 0.032867 | 0.0013848 | 0.001384 | 0.0013868 | 0.0013786 | 0.0013627 | 0.0013408 | 0.0013263 | 0.001309 | 0.0012764 | 0.0012714 | 0.0012664 | 0.0012614 | 0.0012564 | 0.0012514 | 0.0012464 | 0.0012415 | 0.0012365 | 0.0012315 | 0.0012265 | 0.0012215 | 27117.7471 | 4149.7923 | 511.4026 | 78.2593 | 19075.372 | 19075.372 | 659857.1334 | 19075.372
| NHL031-158118521 | 43 | NHL031 | NHL | North | 1013352.0262 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.04034 | 0.040707 | 0.041075 | 0.041443 | 0.04181 | 0.041681 | 0.041552 | 0.041423 | 0.041294 | 0.041165 | 0.041036 | 0.040907 | 0.040777 | 0.040648 | 0.040519 | 0.04039 | 0.040261 | 0.040132 | 0.040003 | 0.039874 | 0.0016646 | 0.0016624 | 0.0016646 | 0.0016537 | 0.0016335 | 0.0016085 | 0.0015923 | 0.0015727 | 0.0015347 | 0.0015299 | 0.0015251 | 0.0015203 | 0.0015155 | 0.0015107 | 0.0015059 | 0.0015011 | 0.0014963 | 0.0014915 | 0.0014867 | 0.0014819 | 27117.7471 | 4149.7923 | 615.6441 | 94.2112 | 33309.1942 | 33309.1942 | 1013352.0262 | 33309.1942
| NHL031-158118640 | 62 | NHL031 | NHL | North | 1461112.2239 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.025968 | 0.026174 | 0.026381 | 0.026587 | 0.026793 | 0.02662 | 0.026448 | 0.026275 | 0.026102 | 0.025929 | 0.025756 | 0.025584 | 0.025411 | 0.025238 | 0.025065 | 0.024892 | 0.02472 | 0.024547 | 0.024374 | 0.024201 | 0.0010716 | 0.0010689 | 0.0010691 | 0.0010609 | 0.0010468 | 0.0010273 | 0.0010135 | 0.00099756 | 0.00097008 | 0.00096366 | 0.00095724 | 0.00095082 | 0.0009444 | 0.00093797 | 0.00093155 | 0.00092513 | 0.00091871 | 0.00091229 | 0.00090586 | 0.00089944 | 27117.7471 | 4149.7923 | 388.227 | 59.4099 | 28675.7857 | 28675.7857 | 1461112.2239 | 28675.7857
| NHL031-159317140 | 187 | NHL031 | NHL | North | 4406902.9979 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.1982 | 0.20012 | 0.20203 | 0.20395 | 0.20586 | 0.20508 | 0.2043 | 0.20352 | 0.20274 | 0.20196 | 0.20118 | 0.2004 | 0.19962 | 0.19884 | 0.19806 | 0.19727 | 0.19649 | 0.19571 | 0.19493 | 0.19415 | 0.0081789 | 0.0081725 | 0.0081877 | 0.0081379 | 0.008043 | 0.0079143 | 0.0078289 | 0.0077269 | 0.0075348 | 0.0075058 | 0.0074768 | 0.0074478 | 0.0074188 | 0.0073898 | 0.0073607 | 0.0073317 | 0.0073027 | 0.0072737 | 0.0072447 | 0.0072157 | 27117.7471 | 4149.7923 | 3019.5176 | 462.0727 | 277985.8949 | 277985.8949 | 4406902.9979 | 277985.8949
| NHL031-159317397 | 50 | NHL031 | NHL | North | 1178316.3096 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.022088 | 0.022315 | 0.022543 | 0.02277 | 0.022997 | 0.022859 | 0.02272 | 0.022582 | 0.022443 | 0.022305 | 0.022166 | 0.022028 | 0.02189 | 0.021751 | 0.021613 | 0.021474 | 0.021336 | 0.021197 | 0.021059 | 0.02092 | 0.00091147 | 0.00091133 | 0.00091358 | 0.00090857 | 0.0008985 | 0.00088214 | 0.00087065 | 0.00085735 | 0.00083411 | 0.00082896 | 0.00082382 | 0.00081867 | 0.00081353 | 0.00080838 | 0.00080323 | 0.00079809 | 0.00079294 | 0.0007878 | 0.00078265 | 0.0007775 | 27117.7471 | 4149.7923 | 333.4177 | 51.0225 | 53916.6761 | 53916.6761 | 1178316.3096 | 53916.6761
| NHL031-159338407 | 18 | NHL031 | NHL | North | 424193.8715 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27117.7471 | 4149.7923 | 0 | 0 | 0 | 0 | 424193.8715 | 0
| NHL031-159449178 | 88 | NHL031 | NHL | North | 2073836.7049 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.070116 | 0.070658 | 0.071199 | 0.07174 | 0.072282 | 0.071985 | 0.071688 | 0.071391 | 0.071094 | 0.070798 | 0.070501 | 0.070204 | 0.069907 | 0.06961 | 0.069313 | 0.069017 | 0.06872 | 0.068423 | 0.068126 | 0.067829 | 0.0028934 | 0.0028856 | 0.0028855 | 0.0028626 | 0.002824 | 0.002778 | 0.0027471 | 0.0027105 | 0.0026422 | 0.0026312 | 0.0026202 | 0.0026091 | 0.0025981 | 0.0025871 | 0.002576 | 0.002565 | 0.002554 | 0.0025429 | 0.0025319 | 0.0025209 | 27117.7471 | 4149.7923 | 1059.9211 | 162.1983 | 96001.8306 | 96001.8306 | 2073836.7049 | 96001.8306
| NHL031-163378374 | 32 | NHL031 | NHL | North | 754122.4381 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.017963 | 0.018128 | 0.018294 | 0.018459 | 0.018624 | 0.01851 | 0.018396 | 0.018281 | 0.018167 | 0.018052 | 0.017938 | 0.017824 | 0.017709 | 0.017595 | 0.017481 | 0.017366 | 0.017252 | 0.017137 | 0.017023 | 0.016909 | 0.00074126 | 0.00074035 | 0.00074139 | 0.00073656 | 0.00072765 | 0.00071432 | 0.00070493 | 0.00069408 | 0.00067517 | 0.00067092 | 0.00066667 | 0.00066242 | 0.00065817 | 0.00065392 | 0.00064967 | 0.00064542 | 0.00064117 | 0.00063692 | 0.00063266 | 0.00062841 | 27117.7471 | 4149.7923 | 270.0526 | 41.3258 | 21736.5623 | 21736.5623 | 754122.4381 | 21736.5623
| NHL031-171331453 | 17 | NHL031 | NHL | North | 400627.5453 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27117.7471 | 4149.7923 | 0 | 0 | 0 | 0 | 400627.5453 | 0
| NHL031-187102650 | 106 | NHL031 | NHL | North | 2498030.5763 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 2.7649 | 2.7874 | 2.8099 | 2.8323 | 2.8548 | 2.8377 | 2.8207 | 2.8036 | 2.7865 | 2.7694 | 2.7524 | 2.7353 | 2.7182 | 2.7012 | 2.6841 | 2.667 | 2.6499 | 2.6329 | 2.6158 | 2.5987 | 0.1141 | 0.11383 | 0.11387 | 0.11302 | 0.11154 | 0.10951 | 0.10809 | 0.10644 | 0.10356 | 0.10293 | 0.10229 | 0.10166 | 0.10102 | 0.10039 | 0.099754 | 0.09912 | 0.098485 | 0.097851 | 0.097216 | 0.096582 | 27117.7471 | 4149.7923 | 41458.4251 | 6344.3269 | 191977.675 | 191977.675 | 2498030.5763 | 191977.675
| NHL031-202230824 | 191 | NHL031 | NHL | North | 4501168.3026 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 10.1395 | 10.23 | 10.3206 | 10.4111 | 10.5017 | 10.4248 | 10.348 | 10.2711 | 10.1942 | 10.1173 | 10.0405 | 9.9636 | 9.8867 | 9.8099 | 9.733 | 9.6561 | 9.5792 | 9.5024 | 9.4255 | 9.3486 | 0.41841 | 0.41778 | 0.41826 | 0.41543 | 0.4103 | 0.4023 | 0.39654 | 0.38996 | 0.37887 | 0.37601 | 0.37316 | 0.3703 | 0.36744 | 0.36458 | 0.36173 | 0.35887 | 0.35601 | 0.35316 | 0.3503 | 0.34744 | 27117.7471 | 4149.7923 | 151394.6738 | 23167.7227 | 792287.1811 | 792287.1811 | 4501168.3026 | 792287.1811
| NHL031-44808373 | 149 | NHL031 | NHL | North | 3511382.6026 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.53284 | 0.53738 | 0.54191 | 0.54645 | 0.55098 | 0.54712 | 0.54325 | 0.53938 | 0.53551 | 0.53164 | 0.52778 | 0.52391 | 0.52004 | 0.51617 | 0.51231 | 0.50844 | 0.50457 | 0.5007 | 0.49683 | 0.49297 | 0.021988 | 0.021946 | 0.021962 | 0.021805 | 0.021527 | 0.021114 | 0.020817 | 0.020478 | 0.019902 | 0.019759 | 0.019615 | 0.019471 | 0.019327 | 0.019184 | 0.01904 | 0.018896 | 0.018752 | 0.018609 | 0.018465 | 0.018321 | 27117.7471 | 4149.7923 | 7957.48 | 1217.7224 | 306601.8321 | 306601.8321 | 3511382.6026 | 306601.8321
| NHL031-47809173 | 72 | NHL031 | NHL | North | 1696775.4858 | 0.0014822 | 0.0014669 | 0.0014557 | 0.0014333 | 0.0014034 | 0.0013862 | 0.0013764 | 0.0013637 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.001335 | 0.201 | 0.20281 | 0.20462 | 0.20643 | 0.20824 | 0.20697 | 0.2057 | 0.20442 | 0.20315 | 0.20188 | 0.20061 | 0.19933 | 0.19806 | 0.19679 | 0.19552 | 0.19424 | 0.19297 | 0.1917 | 0.19043 | 0.18916 | 0.0082943 | 0.0082825 | 0.0082926 | 0.0082371 | 0.0081359 | 0.0079871 | 0.0078824 | 0.0077613 | 0.0075502 | 0.0075029 | 0.0074556 | 0.0074083 | 0.007361 | 0.0073137 | 0.0072664 | 0.0072191 | 0.0071718 | 0.0071246 | 0.0070773 | 0.00703 | 27117.7471 | 4149.7923 | 3020.3626 | 462.202 | 160898.5373 | 160898.5373 | 1696775.4858 | 160898.5373
| NKA001-111726711 | 45 | NKA001 | NKA | North | 1060484.6786 | 0.0013296 | 0.001345 | 0.0013553 | 0.0013604 | 0.0013537 | 0.0013501 | 0.0013656 | 0.0013861 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.00022565 | 0.00022731 | 0.00022897 | 0.00023064 | 0.0002323 | 0.00023472 | 0.00023713 | 0.00023955 | 0.00024196 | 0.00024438 | 0.00024679 | 0.00024921 | 0.00025162 | 0.00025404 | 0.00025645 | 0.00025887 | 0.00026128 | 0.0002637 | 0.00026611 | 0.00026853 | 8.3524e-06 | 8.5116e-06 | 8.6394e-06 | 8.7351e-06 | 8.7549e-06 | 8.8224e-06 | 9.015e-06 | 9.2439e-06 | 9.2921e-06 | 9.3848e-06 | 9.4776e-06 | 9.5703e-06 | 9.6631e-06 | 9.7558e-06 | 9.8486e-06 | 9.9413e-06 | 1.0034e-05 | 1.0127e-05 | 1.022e-05 | 1.0312e-05 | 27821.5406 | 3536.1598 | 3.7285 | 0.4739 | 162.2262 | 162.2262 | 1060484.6786 | 162.2262
| NKA001-138135636 | 55 | NKA001 | NKA | North | 1296147.9405 | 0.0013296 | 0.001345 | 0.0013553 | 0.0013604 | 0.0013537 | 0.0013501 | 0.0013656 | 0.0013861 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0031414 | 0.0031441 | 0.0031469 | 0.0031496 | 0.0031523 | 0.0031524 | 0.0031524 | 0.0031525 | 0.0031526 | 0.0031527 | 0.0031527 | 0.0031528 | 0.0031529 | 0.003153 | 0.003153 | 0.0031531 | 0.0031532 | 0.0031533 | 0.0031533 | 0.0031534 | 0.00011628 | 0.00011773 | 0.00011873 | 0.00011929 | 0.0001188 | 0.00011849 | 0.00011985 | 0.00012165 | 0.00012107 | 0.00012107 | 0.00012108 | 0.00012108 | 0.00012108 | 0.00012108 | 0.00012109 | 0.00012109 | 0.00012109 | 0.0001211 | 0.0001211 | 0.0001211 | 27821.5406 | 3536.1598 | 48.255 | 6.1333 | 2811.9292 | 2811.9292 | 1296147.9405 | 2811.9292
| NKA001-15424552 | 0 | NKA001 | NKA | North | 0 | 0.0013296 | 0.001345 | 0.0013553 | 0.0013604 | 0.0013537 | 0.0013501 | 0.0013656 | 0.0013861 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27821.5406 | 3536.1598 | 0 | 0 | 0 | 0 | 0 | 0
| NKA001-15424578 | 77 | NKA001 | NKA | North | 1814607.1168 | 0.0013296 | 0.001345 | 0.0013553 | 0.0013604 | 0.0013537 | 0.0013501 | 0.0013656 | 0.0013861 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 1.6522 | 1.6626 | 1.6729 | 1.6833 | 1.6936 | 1.7016 | 1.7096 | 1.7176 | 1.7256 | 1.7336 | 1.7416 | 1.7496 | 1.7576 | 1.7655 | 1.7735 | 1.7815 | 1.7895 | 1.7975 | 1.8055 | 1.8135 | 0.061157 | 0.062254 | 0.063121 | 0.063752 | 0.063828 | 0.063959 | 0.064994 | 0.066281 | 0.066268 | 0.066575 | 0.066882 | 0.067189 | 0.067496 | 0.067803 | 0.06811 | 0.068417 | 0.068724 | 0.069031 | 0.069338 | 0.069645 | 27821.5406 | 3536.1598 | 26454.7703 | 3362.4413 | 83455.7217 | 83455.7217 | 1814607.1168 | 83455.7217
| NKA001-161093990 | 33 | NKA001 | NKA | North | 777688.7643 | 0.0013296 | 0.001345 | 0.0013553 | 0.0013604 | 0.0013537 | 0.0013501 | 0.0013656 | 0.0013861 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.00035781 | 0.00036075 | 0.0003637 | 0.00036665 | 0.0003696 | 0.00037272 | 0.00037584 | 0.00037896 | 0.00038208 | 0.0003852 | 0.00038832 | 0.00039144 | 0.00039456 | 0.00039768 | 0.0004008 | 0.00040392 | 0.00040704 | 0.00041016 | 0.00041328 | 0.0004164 | 1.3244e-05 | 1.3508e-05 | 1.3723e-05 | 1.3887e-05 | 1.3929e-05 | 1.401e-05 | 1.4288e-05 | 1.4624e-05 | 1.4673e-05 | 1.4793e-05 | 1.4913e-05 | 1.5033e-05 | 1.5152e-05 | 1.5272e-05 | 1.5392e-05 | 1.5512e-05 | 1.5632e-05 | 1.5752e-05 | 1.5871e-05 | 1.5991e-05 | 27821.5406 | 3536.1598 | 5.8732 | 0.74649 | 179.6003 | 179.6003 | 777688.7643 | 179.6003
| NKA001-24606104 | 258 | NKA001 | NKA | North | 6080112.1575 | 0.0013296 | 0.001345 | 0.0013553 | 0.0013604 | 0.0013537 | 0.0013501 | 0.0013656 | 0.0013861 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 2.867 | 2.8823 | 2.8977 | 2.9131 | 2.9285 | 2.9398 | 2.9511 | 2.9625 | 2.9738 | 2.9851 | 2.9964 | 3.0077 | 3.019 | 3.0304 | 3.0417 | 3.053 | 3.0643 | 3.0756 | 3.0869 | 3.0982 | 0.10612 | 0.10793 | 0.10933 | 0.11033 | 0.11037 | 0.1105 | 0.11219 | 0.11432 | 0.1142 | 0.11464 | 0.11507 | 0.11551 | 0.11594 | 0.11638 | 0.11681 | 0.11725 | 0.11768 | 0.11811 | 0.11855 | 0.11898 | 27821.5406 | 3536.1598 | 45574.7429 | 5792.6187 | 706916.7129 | 706916.7129 | 6080112.1575 | 706916.7129
| NKA001-24606118 | 172 | NKA001 | NKA | North | 4053408.105 | 0.0013296 | 0.001345 | 0.0013553 | 0.0013604 | 0.0013537 | 0.0013501 | 0.0013656 | 0.0013861 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.50612 | 0.50989 | 0.51366 | 0.51743 | 0.5212 | 0.52477 | 0.52834 | 0.53192 | 0.53549 | 0.53906 | 0.54263 | 0.5462 | 0.54977 | 0.55334 | 0.55691 | 0.56048 | 0.56405 | 0.56763 | 0.5712 | 0.57477 | 0.018734 | 0.019093 | 0.019381 | 0.019597 | 0.019643 | 0.019725 | 0.020086 | 0.020526 | 0.020565 | 0.020702 | 0.020839 | 0.020976 | 0.021113 | 0.02125 | 0.021387 | 0.021525 | 0.021662 | 0.021799 | 0.021936 | 0.022073 | 27821.5406 | 3536.1598 | 8221.7506 | 1044.9969 | 96815.1293 | 96815.1293 | 4053408.105 | 96815.1293
| NKA001-96630054 | 103 | NKA001 | NKA | North | 2427331.5978 | 0.0013296 | 0.001345 | 0.0013553 | 0.0013604 | 0.0013537 | 0.0013501 | 0.0013656 | 0.0013861 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.0013794 | 0.90659 | 0.91281 | 0.91902 | 0.92524 | 0.93145 | 0.93675 | 0.94204 | 0.94733 | 0.95263 | 0.95792 | 0.96321 | 0.96851 | 0.9738 | 0.97909 | 0.98439 | 0.98968 | 0.99497 | 1.0003 | 1.0056 | 1.0109 | 0.033558 | 0.03418 | 0.034675 | 0.035042 | 0.035104 | 0.03521 | 0.035814 | 0.036557 | 0.036584 | 0.036787 | 0.036991 | 0.037194 | 0.037397 | 0.037601 | 0.037804 | 0.038007 | 0.03821 | 0.038414 | 0.038617 | 0.03882 | 27821.5406 | 3536.1598 | 14614.0511 | 1857.468 | 69686.5872 | 69686.5872 | 2427331.5978 | 69686.5872
| NKA002-15424741 | 366 | NKA002 | NKA | North | 8625275.3862 | 0.0016513 | 0.0016669 | 0.0016757 | 0.0016757 | 0.001661 | 0.0016501 | 0.001661 | 0.0016736 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 29.2387 | 29.3974 | 29.5561 | 29.7148 | 29.8735 | 30.0326 | 30.1916 | 30.3507 | 30.5098 | 30.6688 | 30.8279 | 30.987 | 31.146 | 31.3051 | 31.4642 | 31.6233 | 31.7823 | 31.9414 | 32.1005 | 32.2595 | 1.3441 | 1.3642 | 1.3788 | 1.3862 | 1.3814 | 1.3796 | 1.3961 | 1.4142 | 1.4126 | 1.4199 | 1.4273 | 1.4347 | 1.442 | 1.4494 | 1.4568 | 1.4641 | 1.4715 | 1.4789 | 1.4862 | 1.4936 | 27821.5406 | 3536.1598 | 569530.9662 | 72388.2461 | 2328630.0625 | 2328630.0625 | 8625275.3862 | 2328630.0625
| NKA002-15424752 | 0 | NKA002 | NKA | North | 0 | 0.0016513 | 0.0016669 | 0.0016757 | 0.0016757 | 0.001661 | 0.0016501 | 0.001661 | 0.0016736 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27821.5406 | 3536.1598 | 0 | 0 | 0 | 0 | 0 | 0
| NKA002-157269526 | 0 | NKA002 | NKA | North | 0 | 0.0016513 | 0.0016669 | 0.0016757 | 0.0016757 | 0.001661 | 0.0016501 | 0.001661 | 0.0016736 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27821.5406 | 3536.1598 | 0 | 0 | 0 | 0 | 0 | 0
| NKA002-160426606 | 21 | NKA002 | NKA | North | 494892.85 | 0.0016513 | 0.0016669 | 0.0016757 | 0.0016757 | 0.001661 | 0.0016501 | 0.001661 | 0.0016736 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 9.7436e-06 | 9.8172e-06 | 9.8908e-06 | 9.9644e-06 | 1.0038e-05 | 1.0141e-05 | 1.0244e-05 | 1.0347e-05 | 1.045e-05 | 1.0553e-05 | 1.0655e-05 | 1.0758e-05 | 1.0861e-05 | 1.0964e-05 | 1.1067e-05 | 1.117e-05 | 1.1273e-05 | 1.1376e-05 | 1.1479e-05 | 1.1582e-05 | 4.4793e-07 | 4.5557e-07 | 4.6142e-07 | 4.6485e-07 | 4.6417e-07 | 4.6586e-07 | 4.7369e-07 | 4.8209e-07 | 4.8381e-07 | 4.8857e-07 | 4.9333e-07 | 4.981e-07 | 5.0286e-07 | 5.0763e-07 | 5.1239e-07 | 5.1715e-07 | 5.2192e-07 | 5.2668e-07 | 5.3145e-07 | 5.3621e-07 | 27821.5406 | 3536.1598 | 0.19575 | 0.02488 | 5.37 | 5.37 | 494892.85 | 5.37
| NKA002-176883603 | 11 | NKA002 | NKA | North | 259229.5881 | 0.0016513 | 0.0016669 | 0.0016757 | 0.0016757 | 0.001661 | 0.0016501 | 0.001661 | 0.0016736 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.010129 | 0.010193 | 0.010257 | 0.010321 | 0.010385 | 0.010439 | 0.010493 | 0.010547 | 0.010601 | 0.010655 | 0.010709 | 0.010763 | 0.010817 | 0.010871 | 0.010925 | 0.010979 | 0.011033 | 0.011087 | 0.011141 | 0.011195 | 0.00046563 | 0.000473 | 0.00047849 | 0.00048147 | 0.0004802 | 0.00047954 | 0.0004852 | 0.00049142 | 0.00049081 | 0.00049331 | 0.00049581 | 0.00049831 | 0.00050081 | 0.00050331 | 0.00050582 | 0.00050832 | 0.00051082 | 0.00051332 | 0.00051582 | 0.00051833 | 27821.5406 | 3536.1598 | 197.7555 | 25.135 | 4420.3758 | 4420.3758 | 259229.5881 | 4420.3758
| NKA002-24606230 | 207 | NKA002 | NKA | North | 4878229.5217 | 0.0016513 | 0.0016669 | 0.0016757 | 0.0016757 | 0.001661 | 0.0016501 | 0.001661 | 0.0016736 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 1.2452 | 1.2531 | 1.261 | 1.2689 | 1.2768 | 1.284 | 1.2911 | 1.2982 | 1.3053 | 1.3125 | 1.3196 | 1.3267 | 1.3338 | 1.341 | 1.3481 | 1.3552 | 1.3623 | 1.3695 | 1.3766 | 1.3837 | 0.057245 | 0.058153 | 0.058829 | 0.059197 | 0.059043 | 0.058983 | 0.059702 | 0.060488 | 0.060435 | 0.060765 | 0.061095 | 0.061425 | 0.061755 | 0.062085 | 0.062415 | 0.062745 | 0.063074 | 0.063404 | 0.063734 | 0.064064 | 27821.5406 | 3536.1598 | 24359.3268 | 3096.1072 | 403356.9499 | 403356.9499 | 4878229.5217 | 403356.9499
| NKA002-24606244 | 142 | NKA002 | NKA | North | 3346418.3192 | 0.0016513 | 0.0016669 | 0.0016757 | 0.0016757 | 0.001661 | 0.0016501 | 0.001661 | 0.0016736 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 0.001663 | 6.4387 | 6.4721 | 6.5054 | 6.5388 | 6.5722 | 6.6244 | 6.6767 | 6.7289 | 6.7812 | 6.8334 | 6.8857 | 6.9379 | 6.9902 | 7.0424 | 7.0947 | 7.1469 | 7.1992 | 7.2514 | 7.3037 | 7.3559 | 0.296 | 0.30034 | 0.30349 | 0.30504 | 0.30391 | 0.30432 | 0.30874 | 0.31353 | 0.31396 | 0.31638 | 0.3188 | 0.32122 | 0.32364 | 0.32606 | 0.32848 | 0.33089 | 0.33331 | 0.33573 | 0.33815 | 0.34057 | 27821.5406 | 3536.1598 | 126929.8331 | 16132.9735 | 1026902.2668 | 1026902.2668 | 3346418.3192 | 1026902.2668
| NKA003-15422579 | 268 | NKA003 | NKA | North | 6315775.4194 | 0.0035246 | 0.0035223 | 0.0034839 | 0.0034432 | 0.0033894 | 0.0033487 | 0.0033257 | 0.0033026 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 7.0563 | 7.1002 | 7.1441 | 7.188 | 7.232 | 7.2765 | 7.321 | 7.3655 | 7.41 | 7.4545 | 7.4991 | 7.5436 | 7.5881 | 7.6326 | 7.6771 | 7.7217 | 7.7662 | 7.8107 | 7.8552 | 7.8997 | 0.6924 | 0.69625 | 0.69292 | 0.68903 | 0.68241 | 0.67837 | 0.67782 | 0.67722 | 0.67339 | 0.67744 | 0.68148 | 0.68553 | 0.68957 | 0.69362 | 0.69766 | 0.70171 | 0.70575 | 0.7098 | 0.71385 | 0.71789 | 27821.5406 | 3536.1598 | 277682.277 | 35293.8369 | 1041842.191 | 1041842.191 | 6315775.4194 | 1041842.191
| NKA003-161248298 | 29 | NKA003 | NKA | North | 683423.4596 | 0.0035246 | 0.0035223 | 0.0034839 | 0.0034432 | 0.0033894 | 0.0033487 | 0.0033257 | 0.0033026 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.0032642 | 0.00041166 | 0.00041474 | 0.00041783 | 0.00042091 | 0.000424 | 0.0004281 | 0.0004322 | 0.0004363 | 0.0004404 | 0.0004445 | 0.0004486 | 0.0004527 | 0.0004568 | 0.0004609 | 0.000465 | 0.0004691 | 0.0004732 | 0.0004773 | 0.0004814 | 0.0004855 | 4.0394e-05 | 4.067e-05 | 4.0526e-05 | 4.0348e-05 | 4.0009e-05 | 3.9911e-05 | 4.0016e-05 | 4.0115e-05 | 4.0022e-05 | 4.0394e-05 | 4.0767e-05 | 4.1139e-05 | 4.1512e-05 | 4.1885e-05 | 4.2257e-05 | 4.263e-05 | 4.3002e-05 | 4.3375e-05 | 4.3748e-05 | 4.412e-05 | 27821.5406 | 3536.1598 | 16.5408 | 2.1024 | 218.6619 | 218.6619 | 683423.4596 | 218.6619
| NKA004-15424817 | 237 | NKA004 | NKA | North | 5585219.3075 | 0.0020064 | 0.0020352 | 0.0020593 | 0.002068 | 0.0020553 | 0.0020527 | 0.00208 | 0.002116 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 48.998 | 49.2152 | 49.4324 | 49.6497 | 49.8669 | 50.0079 | 50.149 | 50.2901 | 50.4311 | 50.5722 | 50.7133 | 50.8543 | 50.9954 | 51.1364 | 51.2775 | 51.4186 | 51.5596 | 51.7007 | 51.8418 | 51.9828 | 2.737 | 2.7885 | 2.8341 | 2.8585 | 2.8534 | 2.8578 | 2.9041 | 2.9626 | 2.9512 | 2.9594 | 2.9677 | 2.9759 | 2.9842 | 2.9924 | 3.0007 | 3.009 | 3.0172 | 3.0255 | 3.0337 | 3.042 | 27821.5406 | 3536.1598 | 1175187.1576 | 149368.0629 | 1638287.8114 | 1638287.8114 | 5585219.3075 | 1638287.8114
| NKA004-162977911 | 16 | NKA004 | NKA | North | 377061.2191 | 0.0020064 | 0.0020352 | 0.0020593 | 0.002068 | 0.0020553 | 0.0020527 | 0.00208 | 0.002116 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.002102 | 0.00021864 | 0.00022023 | 0.00022182 | 0.00022341 | 0.000225 | 0.00022743 | 0.00022986 | 0.00023229 | 0.00023472 | 0.00023715 | 0.00023958 | 0.00024201 | 0.00024444 | 0.00024687 | 0.0002493 | 0.00025173 | 0.00025416 | 0.00025659 | 0.00025902 | 0.00026145 | 1.2213e-05 | 1.2478e-05 | 1.2717e-05 | 1.2862e-05 | 1.2874e-05 | 1.2997e-05 | 1.3311e-05 | 1.3684e-05 | 1.3736e-05 | 1.3878e-05 | 1.402e-05 | 1.4162e-05 | 1.4304e-05 | 1.4447e-05 | 1.4589e-05 | 1.4731e-05 | 1.4873e-05 | 1.5015e-05 | 1.5158e-05 | 1.53e-05 | 27821.5406 | 3536.1598 | 5.5053 | 0.69974 | 71.5291 | 71.5291 | 377061.2191 | 71.5291
| NKA005-154156915 | 28 | NKA005 | NKA | North | 659857.1334 | 0.0036922 | 0.0037281 | 0.0037448 | 0.0037473 | 0.0037231 | 0.0037089 | 0.0037448 | 0.0037807 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 1.6792 | 1.692 | 1.7048 | 1.7176 | 1.7304 | 1.7452 | 1.7601 | 1.7749 | 1.7898 | 1.8046 | 1.8195 | 1.8343 | 1.8492 | 1.864 | 1.8789 | 1.8937 | 1.9086 | 1.9234 | 1.9383 | 1.9531 | 0.17261 | 0.17561 | 0.17773 | 0.17919 | 0.17936 | 0.18021 | 0.1835 | 0.18682 | 0.1866 | 0.18814 | 0.18969 | 0.19124 | 0.19279 | 0.19434 | 0.19588 | 0.19743 | 0.19898 | 0.20053 | 0.20208 | 0.20363 | 27821.5406 | 3536.1598 | 75233.6881 | 9562.3154 | 69960.822 | 69960.822 | 659857.1334 | 69960.822
| NKA005-15422555 | 281 | NKA005 | NKA | North | 6622137.6599 | 0.0036922 | 0.0037281 | 0.0037448 | 0.0037473 | 0.0037231 | 0.0037089 | 0.0037448 | 0.0037807 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 2.1044 | 2.1186 | 2.1329 | 2.1471 | 2.1614 | 2.1748 | 2.1882 | 2.2016 | 2.215 | 2.2284 | 2.2418 | 2.2552 | 2.2686 | 2.282 | 2.2954 | 2.3088 | 2.3222 | 2.3356 | 2.349 | 2.3624 | 0.21631 | 0.21989 | 0.22236 | 0.224 | 0.22403 | 0.22456 | 0.22813 | 0.23172 | 0.23092 | 0.23232 | 0.23372 | 0.23512 | 0.23651 | 0.23791 | 0.23931 | 0.2407 | 0.2421 | 0.2435 | 0.2449 | 0.24629 | 27821.5406 | 3536.1598 | 92935.1901 | 11812.203 | 438363.2213 | 438363.2213 | 6622137.6599 | 438363.2213
| NKA005-24606900 | 150 | NKA005 | NKA | North | 3534948.9288 | 0.0036922 | 0.0037281 | 0.0037448 | 0.0037473 | 0.0037231 | 0.0037089 | 0.0037448 | 0.0037807 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 0.0037448 | 3.9638 | 3.9885 | 4.0131 | 4.0377 | 4.0623 | 4.0912 | 4.12 | 4.1489 | 4.1777 | 4.2066 | 4.2355 | 4.2643 | 4.2932 | 4.322 | 4.3509 | 4.3797 | 4.4086 | 4.4374 | 4.4663 | 4.4951 | 0.40745 | 0.41397 | 0.41838 | 0.42123 | 0.42107 | 0.42244 | 0.42953 | 0.43668 | 0.43555 | 0.43856 | 0.44157 | 0.44458 | 0.44758 | 0.45059 | 0.4536 | 0.45661 | 0.45962 | 0.46262 | 0.46563 | 0.46864 | 27821.5406 | 3536.1598 | 175503.8643 | 22306.8063 | 867257.7027 | 867257.7027 | 3534948.9288 | 867257.7027
| NKA006-152812929 | 226 | NKA006 | NKA | North | 5325989.7193 | 0.0032015 | 0.0032957 | 0.0033214 | 0.0033078 | 0.0032811 | 0.0032957 | 0.003343 | 0.0033686 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 9.0155 | 9.0762 | 9.1369 | 9.1976 | 9.2582 | 9.2963 | 9.3343 | 9.3723 | 9.4104 | 9.4484 | 9.4865 | 9.5245 | 9.5625 | 9.6006 | 9.6386 | 9.6767 | 9.7147 | 9.7527 | 9.7908 | 9.8288 | 0.80356 | 0.83277 | 0.84486 | 0.847 | 0.84569 | 0.85296 | 0.86873 | 0.87896 | 0.86564 | 0.86914 | 0.87263 | 0.87613 | 0.87963 | 0.88313 | 0.88663 | 0.89013 | 0.89363 | 0.89713 | 0.90063 | 0.90413 | 27821.5406 | 3536.1598 | 347952.6413 | 44225.3063 | 1376749.7108 | 1376749.7108 | 5325989.7193 | 1376749.7108
| NKA006-15424841 | 514 | NKA006 | NKA | North | 12113091.6626 | 0.0032015 | 0.0032957 | 0.0033214 | 0.0033078 | 0.0032811 | 0.0032957 | 0.003343 | 0.0033686 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 17.6018 | 17.7174 | 17.8331 | 17.9488 | 18.0645 | 18.1853 | 18.3062 | 18.4271 | 18.548 | 18.6688 | 18.7897 | 18.9106 | 19.0314 | 19.1523 | 19.2732 | 19.3941 | 19.5149 | 19.6358 | 19.7567 | 19.8776 | 1.5689 | 1.6256 | 1.649 | 1.6529 | 1.6501 | 1.6686 | 1.7037 | 1.7281 | 1.7062 | 1.7173 | 1.7284 | 1.7395 | 1.7507 | 1.7618 | 1.7729 | 1.784 | 1.7951 | 1.8062 | 1.8174 | 1.8285 | 27821.5406 | 3536.1598 | 687660.0192 | 87402.6272 | 2765164.2205 | 2765164.2205 | 12113091.6626 | 2765164.2205
| NKA006-15424865 | 0 | NKA006 | NKA | North | 0 | 0.0032015 | 0.0032957 | 0.0033214 | 0.0033078 | 0.0032811 | 0.0032957 | 0.003343 | 0.0033686 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27821.5406 | 3536.1598 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-160426703 | 24 | NKA006 | NKA | North | 565591.8286 | 0.0032015 | 0.0032957 | 0.0033214 | 0.0033078 | 0.0032811 | 0.0032957 | 0.003343 | 0.0033686 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0017716 | 0.0017855 | 0.0017994 | 0.0018133 | 0.0018272 | 0.0018475 | 0.0018678 | 0.0018882 | 0.0019085 | 0.0019288 | 0.0019491 | 0.0019694 | 0.0019898 | 0.0020101 | 0.0020304 | 0.0020507 | 0.002071 | 0.0020914 | 0.0021117 | 0.002132 | 0.00015791 | 0.00016383 | 0.00016639 | 0.00016699 | 0.0001669 | 0.00016951 | 0.00017384 | 0.00017708 | 0.00017556 | 0.00017743 | 0.00017929 | 0.00018116 | 0.00018303 | 0.0001849 | 0.00018677 | 0.00018864 | 0.00019051 | 0.00019238 | 0.00019425 | 0.00019612 | 27821.5406 | 3536.1598 | 71.0088 | 9.0253 | 490.7036 | 490.7036 | 565591.8286 | 490.7036
| NKA006-160426816 | 54 | NKA006 | NKA | North | 1272581.6144 | 0.0032015 | 0.0032957 | 0.0033214 | 0.0033078 | 0.0032811 | 0.0032957 | 0.003343 | 0.0033686 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.015711 | 0.015768 | 0.015824 | 0.015881 | 0.015938 | 0.015943 | 0.015948 | 0.015953 | 0.015958 | 0.015963 | 0.015968 | 0.015973 | 0.015978 | 0.015983 | 0.015988 | 0.015993 | 0.015998 | 0.016003 | 0.016008 | 0.016013 | 0.0014003 | 0.0014467 | 0.0014632 | 0.0014625 | 0.0014559 | 0.0014628 | 0.0014843 | 0.0014961 | 0.0014679 | 0.0014684 | 0.0014689 | 0.0014693 | 0.0014698 | 0.0014703 | 0.0014707 | 0.0014712 | 0.0014716 | 0.0014721 | 0.0014726 | 0.001473 | 27821.5406 | 3536.1598 | 588.8983 | 74.8499 | 20931.4968 | 20931.4968 | 1272581.6144 | 20931.4968
| NKA006-162978025 | 35 | NKA006 | NKA | North | 824821.4167 | 0.0032015 | 0.0032957 | 0.0033214 | 0.0033078 | 0.0032811 | 0.0032957 | 0.003343 | 0.0033686 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.033555 | 0.033777 | 0.034 | 0.034223 | 0.034445 | 0.034638 | 0.034831 | 0.035024 | 0.035217 | 0.035411 | 0.035604 | 0.035797 | 0.03599 | 0.036183 | 0.036376 | 0.036569 | 0.036762 | 0.036955 | 0.037148 | 0.037341 | 0.0029908 | 0.0030992 | 0.0031439 | 0.0031515 | 0.0031464 | 0.0031781 | 0.0032417 | 0.0032847 | 0.0032396 | 0.0032573 | 0.0032751 | 0.0032928 | 0.0033106 | 0.0033284 | 0.0033461 | 0.0033639 | 0.0033816 | 0.0033994 | 0.0034172 | 0.0034349 | 27821.5406 | 3536.1598 | 1304.2183 | 165.7681 | 28041.0387 | 28041.0387 | 824821.4167 | 28041.0387
| NKA006-163615273 | 0 | NKA006 | NKA | North | 0 | 0.0032015 | 0.0032957 | 0.0033214 | 0.0033078 | 0.0032811 | 0.0032957 | 0.003343 | 0.0033686 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27821.5406 | 3536.1598 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-181987048 | 0 | NKA006 | NKA | North | 0 | 0.0032015 | 0.0032957 | 0.0033214 | 0.0033078 | 0.0032811 | 0.0032957 | 0.003343 | 0.0033686 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27821.5406 | 3536.1598 | 0 | 0 | 0 | 0 | 0 | 0
| NKA006-192419289 | 127 | NKA006 | NKA | North | 2992923.4264 | 0.0032015 | 0.0032957 | 0.0033214 | 0.0033078 | 0.0032811 | 0.0032957 | 0.003343 | 0.0033686 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.31983 | 0.32173 | 0.32363 | 0.32554 | 0.32744 | 0.32981 | 0.33218 | 0.33456 | 0.33693 | 0.33931 | 0.34168 | 0.34405 | 0.34643 | 0.3488 | 0.35117 | 0.35355 | 0.35592 | 0.35829 | 0.36067 | 0.36304 | 0.028507 | 0.02952 | 0.029925 | 0.029978 | 0.02991 | 0.030261 | 0.030916 | 0.031376 | 0.030993 | 0.031212 | 0.03143 | 0.031648 | 0.031867 | 0.032085 | 0.032304 | 0.032522 | 0.03274 | 0.032959 | 0.033177 | 0.033395 | 27821.5406 | 3536.1598 | 12503.2193 | 1589.1781 | 166267.2878 | 166267.2878 | 2992923.4264 | 166267.2878
| NKA006-24605964 | 79 | NKA006 | NKA | North | 1861739.7692 | 0.0032015 | 0.0032957 | 0.0033214 | 0.0033078 | 0.0032811 | 0.0032957 | 0.003343 | 0.0033686 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.0033041 | 0.44741 | 0.45036 | 0.45331 | 0.45626 | 0.45921 | 0.46209 | 0.46497 | 0.46785 | 0.47073 | 0.47361 | 0.47649 | 0.47938 | 0.48226 | 0.48514 | 0.48802 | 0.4909 | 0.49378 | 0.49666 | 0.49954 | 0.50242 | 0.039878 | 0.041321 | 0.041916 | 0.042016 | 0.041946 | 0.042398 | 0.043274 | 0.043876 | 0.043301 | 0.043566 | 0.043831 | 0.044096 | 0.044361 | 0.044626 | 0.044892 | 0.045157 | 0.045422 | 0.045687 | 0.045952 | 0.046217 | 27821.5406 | 3536.1598 | 17444.7917 | 2217.2594 | 91533.9791 | 91533.9791 | 1861739.7692 | 91533.9791
| OYN001-15412732 | 267 | OYN001 | OYN | North | 6292209.0932 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.86746 | 0.8739 | 0.88033 | 0.88677 | 0.89321 | 0.8919 | 0.89059 | 0.88929 | 0.88798 | 0.88667 | 0.88537 | 0.88406 | 0.88275 | 0.88145 | 0.88014 | 0.87883 | 0.87753 | 0.87622 | 0.87491 | 0.87361 | 0.024748 | 0.025028 | 0.025074 | 0.025119 | 0.024881 | 0.024565 | 0.024431 | 0.024395 | 0.024039 | 0.024004 | 0.023969 | 0.023933 | 0.023898 | 0.023862 | 0.023827 | 0.023792 | 0.023756 | 0.023721 | 0.023686 | 0.02365 | 26869.1023 | 4575.9475 | 9445.1918 | 1608.5652 | 155269.3604 | 155269.3604 | 6292209.0932 | 155269.3604
| OYN001-15412756 | 0 | OYN001 | OYN | North | 0 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.0033287 | 0.0033582 | 0.0033877 | 0.0034172 | 0.0034468 | 0.0034463 | 0.0034459 | 0.0034454 | 0.003445 | 0.0034445 | 0.0034441 | 0.0034436 | 0.0034432 | 0.0034427 | 0.0034423 | 0.0034418 | 0.0034414 | 0.0034409 | 0.0034405 | 0.00344 | 9.4966e-05 | 9.6177e-05 | 9.6491e-05 | 9.6797e-05 | 9.6012e-05 | 9.4919e-05 | 9.4528e-05 | 9.4516e-05 | 9.3262e-05 | 9.325e-05 | 9.3237e-05 | 9.3225e-05 | 9.3213e-05 | 9.3201e-05 | 9.3189e-05 | 9.3177e-05 | 9.3164e-05 | 9.3152e-05 | 9.314e-05 | 9.3128e-05 | 26869.1023 | 4575.9475 | 0 | 0 | 0 | 0 | 0 | 0
| OYN001-157370670 | 37 | OYN001 | OYN | North | 871954.0691 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.015004 | 0.015111 | 0.015218 | 0.015326 | 0.015433 | 0.015394 | 0.015355 | 0.015316 | 0.015277 | 0.015238 | 0.015199 | 0.01516 | 0.015121 | 0.015083 | 0.015044 | 0.015005 | 0.014966 | 0.014927 | 0.014888 | 0.014849 | 0.00042805 | 0.00043277 | 0.00043346 | 0.00043412 | 0.0004299 | 0.00042399 | 0.00042123 | 0.00042016 | 0.00041359 | 0.00041253 | 0.00041148 | 0.00041042 | 0.00040937 | 0.00040831 | 0.00040726 | 0.0004062 | 0.00040515 | 0.00040409 | 0.00040304 | 0.00040198 | 26869.1023 | 4575.9475 | 162.3594 | 27.6506 | 21246.4622 | 21246.4622 | 871954.0691 | 21246.4622
| OYN001-157370765 | 19 | OYN001 | OYN | North | 447760.1976 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00040535 | 0.00040829 | 0.00041122 | 0.00041416 | 0.0004171 | 0.00041586 | 0.00041463 | 0.0004134 | 0.00041217 | 0.00041094 | 0.0004097 | 0.00040847 | 0.00040724 | 0.00040601 | 0.00040477 | 0.00040354 | 0.00040231 | 0.00040108 | 0.00039985 | 0.00039861 | 1.1565e-05 | 1.1693e-05 | 1.1713e-05 | 1.1731e-05 | 1.1618e-05 | 1.1454e-05 | 1.1374e-05 | 1.1341e-05 | 1.1158e-05 | 1.1125e-05 | 1.1091e-05 | 1.1058e-05 | 1.1025e-05 | 1.0991e-05 | 1.0958e-05 | 1.0925e-05 | 1.0891e-05 | 1.0858e-05 | 1.0825e-05 | 1.0791e-05 | 26869.1023 | 4575.9475 | 4.3782 | 0.74563 | 1323.8937 | 1323.8937 | 447760.1976 | 1323.8937
| OYN001-157425399 | 48 | OYN001 | OYN | North | 1131183.6572 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.003873 | 0.0038968 | 0.0039207 | 0.0039445 | 0.0039683 | 0.0039563 | 0.0039443 | 0.0039323 | 0.0039203 | 0.0039082 | 0.0038962 | 0.0038842 | 0.0038722 | 0.0038602 | 0.0038482 | 0.0038362 | 0.0038241 | 0.0038121 | 0.0038001 | 0.0037881 | 0.0001105 | 0.0001116 | 0.00011167 | 0.00011173 | 0.00011054 | 0.00010896 | 0.0001082 | 0.00010787 | 0.00010613 | 0.0001058 | 0.00010548 | 0.00010515 | 0.00010483 | 0.0001045 | 0.00010418 | 0.00010385 | 0.00010353 | 0.0001032 | 0.00010288 | 0.00010255 | 26869.1023 | 4575.9475 | 41.6693 | 7.0965 | 12732.3601 | 12732.3601 | 1131183.6572 | 12732.3601
| OYN001-157599093 | 38 | OYN001 | OYN | North | 895520.3953 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 4.6641e-05 | 4.6995e-05 | 4.735e-05 | 4.7705e-05 | 4.806e-05 | 4.8045e-05 | 4.803e-05 | 4.8015e-05 | 4.8e-05 | 4.7985e-05 | 4.797e-05 | 4.7955e-05 | 4.794e-05 | 4.7925e-05 | 4.791e-05 | 4.7895e-05 | 4.788e-05 | 4.7865e-05 | 4.785e-05 | 4.7835e-05 | 1.3306e-06 | 1.3459e-06 | 1.3487e-06 | 1.3513e-06 | 1.3387e-06 | 1.3233e-06 | 1.3176e-06 | 1.3172e-06 | 1.2995e-06 | 1.299e-06 | 1.2986e-06 | 1.2982e-06 | 1.2978e-06 | 1.2974e-06 | 1.297e-06 | 1.2966e-06 | 1.2962e-06 | 1.2958e-06 | 1.2954e-06 | 1.295e-06 | 26869.1023 | 4575.9475 | 0.51107 | 0.087038 | 103.0501 | 103.0501 | 895520.3953 | 103.0501
| OYN001-157599241 | 60 | OYN001 | OYN | North | 1413979.5715 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.0063088 | 0.0063605 | 0.0064123 | 0.006464 | 0.0065157 | 0.0065099 | 0.0065041 | 0.0064984 | 0.0064926 | 0.0064868 | 0.006481 | 0.0064752 | 0.0064694 | 0.0064636 | 0.0064578 | 0.006452 | 0.0064462 | 0.0064404 | 0.0064346 | 0.0064288 | 0.00017999 | 0.00018216 | 0.00018264 | 0.0001831 | 0.0001815 | 0.0001793 | 0.00017842 | 0.00017827 | 0.00017577 | 0.00017561 | 0.00017545 | 0.0001753 | 0.00017514 | 0.00017498 | 0.00017482 | 0.00017467 | 0.00017451 | 0.00017435 | 0.0001742 | 0.00017404 | 26869.1023 | 4575.9475 | 69.0633 | 11.7618 | 4255.5579 | 4255.5579 | 1413979.5715 | 4255.5579
| OYN001-157599335 | 74 | OYN001 | OYN | North | 1743908.1382 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.042468 | 0.042776 | 0.043083 | 0.043391 | 0.043698 | 0.043618 | 0.043537 | 0.043456 | 0.043376 | 0.043295 | 0.043215 | 0.043134 | 0.043053 | 0.042973 | 0.042892 | 0.042812 | 0.042731 | 0.04265 | 0.04257 | 0.042489 | 0.0012116 | 0.0012251 | 0.0012271 | 0.0012291 | 0.0012172 | 0.0012013 | 0.0011943 | 0.0011921 | 0.0011743 | 0.0011721 | 0.0011699 | 0.0011677 | 0.0011655 | 0.0011634 | 0.0011612 | 0.001159 | 0.0011568 | 0.0011546 | 0.0011524 | 0.0011503 | 26869.1023 | 4575.9475 | 461.258 | 78.5546 | 54327.7069 | 54327.7069 | 1743908.1382 | 54327.7069
| OYN001-157997774 | 68 | OYN001 | OYN | North | 1602510.181 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.016964 | 0.017091 | 0.017217 | 0.017344 | 0.017471 | 0.01744 | 0.017409 | 0.017378 | 0.017347 | 0.017316 | 0.017285 | 0.017254 | 0.017223 | 0.017192 | 0.017161 | 0.01713 | 0.0171 | 0.017069 | 0.017038 | 0.017007 | 0.00048397 | 0.00048946 | 0.0004904 | 0.00049129 | 0.00048667 | 0.00048034 | 0.00047757 | 0.00047672 | 0.00046962 | 0.00046878 | 0.00046795 | 0.00046711 | 0.00046627 | 0.00046543 | 0.00046459 | 0.00046375 | 0.00046292 | 0.00046208 | 0.00046124 | 0.0004604 | 26869.1023 | 4575.9475 | 184.4546 | 31.4136 | 24955.086 | 24955.086 | 1602510.181 | 24955.086
| OYN001-157997885 | 348 | OYN001 | OYN | North | 8201081.5147 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.064678 | 0.065132 | 0.065586 | 0.066041 | 0.066495 | 0.066373 | 0.066252 | 0.06613 | 0.066008 | 0.065886 | 0.065765 | 0.065643 | 0.065521 | 0.065399 | 0.065278 | 0.065156 | 0.065034 | 0.064913 | 0.064791 | 0.064669 | 0.0018452 | 0.0018653 | 0.0018681 | 0.0018707 | 0.0018523 | 0.0018281 | 0.0018174 | 0.0018141 | 0.001787 | 0.0017837 | 0.0017804 | 0.0017771 | 0.0017738 | 0.0017705 | 0.0017672 | 0.0017639 | 0.0017606 | 0.0017573 | 0.001754 | 0.0017507 | 26869.1023 | 4575.9475 | 702.0379 | 119.5607 | 648086.1609 | 648086.1609 | 8201081.5147 | 648086.1609
| OYN001-157997976 | 60 | OYN001 | OYN | North | 1413979.5715 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.0014223 | 0.0014329 | 0.0014435 | 0.0014541 | 0.0014647 | 0.001464 | 0.0014633 | 0.0014626 | 0.0014619 | 0.0014612 | 0.0014605 | 0.0014598 | 0.0014591 | 0.0014584 | 0.0014577 | 0.001457 | 0.0014563 | 0.0014556 | 0.0014549 | 0.0014542 | 4.0577e-05 | 4.1036e-05 | 4.1114e-05 | 4.1188e-05 | 4.0799e-05 | 4.0321e-05 | 4.0141e-05 | 4.0122e-05 | 3.9576e-05 | 3.9557e-05 | 3.9538e-05 | 3.9519e-05 | 3.95e-05 | 3.9481e-05 | 3.9463e-05 | 3.9444e-05 | 3.9425e-05 | 3.9406e-05 | 3.9387e-05 | 3.9368e-05 | 26869.1023 | 4575.9475 | 15.5642 | 2.6507 | 4247.2346 | 4247.2346 | 1413979.5715 | 4247.2346
| OYN001-157998086 | 128 | OYN001 | OYN | North | 3016489.7525 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.0054214 | 0.0054664 | 0.0055115 | 0.0055566 | 0.0056016 | 0.005604 | 0.0056063 | 0.0056087 | 0.005611 | 0.0056134 | 0.0056157 | 0.0056181 | 0.0056204 | 0.0056228 | 0.0056251 | 0.0056275 | 0.0056298 | 0.0056322 | 0.0056345 | 0.0056369 | 0.00015467 | 0.00015656 | 0.00015698 | 0.0001574 | 0.00015604 | 0.00015435 | 0.0001538 | 0.00015386 | 0.0001519 | 0.00015197 | 0.00015203 | 0.00015209 | 0.00015216 | 0.00015222 | 0.00015228 | 0.00015235 | 0.00015241 | 0.00015247 | 0.00015254 | 0.0001526 | 26869.1023 | 4575.9475 | 59.7576 | 10.177 | 22140.0283 | 22140.0283 | 3016489.7525 | 22140.0283
| OYN001-157998203 | 44 | OYN001 | OYN | North | 1036918.3524 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.012721 | 0.012823 | 0.012925 | 0.013026 | 0.013128 | 0.013123 | 0.013119 | 0.013114 | 0.013109 | 0.013104 | 0.013099 | 0.013094 | 0.01309 | 0.013085 | 0.01308 | 0.013075 | 0.01307 | 0.013066 | 0.013061 | 0.013056 | 0.00036293 | 0.00036724 | 0.00036813 | 0.00036899 | 0.00036569 | 0.00036145 | 0.00035987 | 0.00035974 | 0.00035488 | 0.00035475 | 0.00035462 | 0.00035449 | 0.00035436 | 0.00035423 | 0.0003541 | 0.00035397 | 0.00035384 | 0.00035371 | 0.00035358 | 0.00035345 | 26869.1023 | 4575.9475 | 139.5323 | 23.7631 | 24432.8493 | 24432.8493 | 1036918.3524 | 24432.8493
| OYN001-157998251 | 70 | OYN001 | OYN | North | 1649642.8334 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.0072511 | 0.0073071 | 0.007363 | 0.0074189 | 0.0074749 | 0.0074757 | 0.0074766 | 0.0074774 | 0.0074783 | 0.0074791 | 0.00748 | 0.0074808 | 0.0074817 | 0.0074825 | 0.0074834 | 0.0074842 | 0.0074851 | 0.0074859 | 0.0074868 | 0.0074876 | 0.00020687 | 0.00020927 | 0.00020972 | 0.00021015 | 0.00020822 | 0.0002059 | 0.0002051 | 0.00020512 | 0.00020245 | 0.00020247 | 0.0002025 | 0.00020252 | 0.00020254 | 0.00020257 | 0.00020259 | 0.00020261 | 0.00020264 | 0.00020266 | 0.00020268 | 0.0002027 | 26869.1023 | 4575.9475 | 79.6509 | 13.565 | 13655.1618 | 13655.1618 | 1649642.8334 | 13655.1618
| OYN001-157998623 | 102 | OYN001 | OYN | North | 2403765.2716 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.011559 | 0.011657 | 0.011755 | 0.011853 | 0.011951 | 0.011944 | 0.011937 | 0.01193 | 0.011924 | 0.011917 | 0.01191 | 0.011903 | 0.011896 | 0.011889 | 0.011882 | 0.011876 | 0.011869 | 0.011862 | 0.011855 | 0.011848 | 0.00032978 | 0.00033385 | 0.00033481 | 0.00033575 | 0.0003329 | 0.00032897 | 0.00032747 | 0.00032728 | 0.00032279 | 0.00032261 | 0.00032242 | 0.00032224 | 0.00032205 | 0.00032186 | 0.00032168 | 0.00032149 | 0.00032131 | 0.00032112 | 0.00032094 | 0.00032075 | 26869.1023 | 4575.9475 | 126.8503 | 21.6033 | 27462.1373 | 27462.1373 | 2403765.2716 | 27462.1373
| OYN001-159943098 | 63 | OYN001 | OYN | North | 1484678.5501 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.02945 | 0.029741 | 0.030033 | 0.030325 | 0.030616 | 0.030498 | 0.03038 | 0.030263 | 0.030145 | 0.030027 | 0.029909 | 0.029791 | 0.029673 | 0.029555 | 0.029437 | 0.029319 | 0.029202 | 0.029084 | 0.028966 | 0.028848 | 0.00084019 | 0.00085177 | 0.00085542 | 0.00085897 | 0.00085284 | 0.00083999 | 0.00083341 | 0.00083018 | 0.00081607 | 0.00081288 | 0.00080969 | 0.0008065 | 0.00080331 | 0.00080012 | 0.00079693 | 0.00079373 | 0.00079054 | 0.00078735 | 0.00078416 | 0.00078097 | 26869.1023 | 4575.9475 | 319.3684 | 54.3901 | 71156.9608 | 71156.9608 | 1484678.5501 | 71156.9608
| OYN001-159943284 | 43 | OYN001 | OYN | North | 1013352.0262 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.0044465 | 0.0044703 | 0.0044941 | 0.004518 | 0.0045418 | 0.0045302 | 0.0045186 | 0.0045071 | 0.0044955 | 0.0044839 | 0.0044724 | 0.0044608 | 0.0044492 | 0.0044376 | 0.0044261 | 0.0044145 | 0.0044029 | 0.0043914 | 0.0043798 | 0.0043682 | 0.00012686 | 0.00012803 | 0.000128 | 0.00012798 | 0.00012651 | 0.00012477 | 0.00012396 | 0.00012364 | 0.0001217 | 0.00012139 | 0.00012108 | 0.00012076 | 0.00012045 | 0.00012014 | 0.00011982 | 0.00011951 | 0.0001192 | 0.00011888 | 0.00011857 | 0.00011826 | 26869.1023 | 4575.9475 | 47.8313 | 8.1459 | 13093.1014 | 13093.1014 | 1013352.0262 | 13093.1014
| OYN001-161991346 | 124 | OYN001 | OYN | North | 2922224.4478 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.063837 | 0.064297 | 0.064758 | 0.065218 | 0.065678 | 0.065562 | 0.065446 | 0.06533 | 0.065214 | 0.065098 | 0.064981 | 0.064865 | 0.064749 | 0.064633 | 0.064517 | 0.064401 | 0.064284 | 0.064168 | 0.064052 | 0.063936 | 0.0018212 | 0.0018414 | 0.0018445 | 0.0018474 | 0.0018295 | 0.0018057 | 0.0017953 | 0.0017922 | 0.0017655 | 0.0017623 | 0.0017592 | 0.001756 | 0.0017529 | 0.0017497 | 0.0017466 | 0.0017434 | 0.0017403 | 0.0017372 | 0.001734 | 0.0017309 | 26869.1023 | 4575.9475 | 693.5457 | 118.1144 | 342203.9951 | 342203.9951 | 2922224.4478 | 342203.9951
| OYN001-161991484 | 7 | OYN001 | OYN | North | 164964.2833 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26869.1023 | 4575.9475 | 0 | 0 | 0 | 0 | 164964.2833 | 0
| OYN001-161991742 | 20 | OYN001 | OYN | North | 471326.5238 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00087929 | 0.00088671 | 0.00089414 | 0.00090157 | 0.000909 | 0.00090864 | 0.00090828 | 0.00090792 | 0.00090757 | 0.00090721 | 0.00090685 | 0.00090649 | 0.00090613 | 0.00090577 | 0.00090541 | 0.00090506 | 0.0009047 | 0.00090434 | 0.00090398 | 0.00090362 | 2.5086e-05 | 2.5395e-05 | 2.5468e-05 | 2.5538e-05 | 2.5321e-05 | 2.5026e-05 | 2.4916e-05 | 2.4907e-05 | 2.457e-05 | 2.456e-05 | 2.455e-05 | 2.454e-05 | 2.4531e-05 | 2.4521e-05 | 2.4511e-05 | 2.4502e-05 | 2.4492e-05 | 2.4482e-05 | 2.4472e-05 | 2.4463e-05 | 26869.1023 | 4575.9475 | 9.6571 | 1.6447 | 1229.8407 | 1229.8407 | 471326.5238 | 1229.8407
| OYN001-161991880 | 70 | OYN001 | OYN | North | 1649642.8334 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.0039547 | 0.0039905 | 0.0040263 | 0.0040621 | 0.004098 | 0.0040887 | 0.0040795 | 0.0040702 | 0.004061 | 0.0040517 | 0.0040425 | 0.0040332 | 0.004024 | 0.0040147 | 0.0040055 | 0.0039962 | 0.003987 | 0.0039777 | 0.0039685 | 0.0039592 | 0.00011283 | 0.00011429 | 0.00011468 | 0.00011506 | 0.00011415 | 0.00011261 | 0.00011191 | 0.00011166 | 0.00010994 | 0.00010969 | 0.00010944 | 0.00010919 | 0.00010894 | 0.00010869 | 0.00010844 | 0.00010818 | 0.00010793 | 0.00010768 | 0.00010743 | 0.00010718 | 26869.1023 | 4575.9475 | 43.1159 | 7.3429 | 19215.1385 | 19215.1385 | 1649642.8334 | 19215.1385
| OYN001-161991949 | 104 | OYN001 | OYN | North | 2450897.9239 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26869.1023 | 4575.9475 | 0 | 0 | 0 | 0 | 2450897.9239 | 0
| OYN001-24603328 | 384 | OYN001 | OYN | North | 9049469.2576 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.67701 | 0.68396 | 0.6909 | 0.69785 | 0.7048 | 0.70304 | 0.70128 | 0.69953 | 0.69777 | 0.69601 | 0.69426 | 0.6925 | 0.69074 | 0.68899 | 0.68723 | 0.68547 | 0.68372 | 0.68196 | 0.6802 | 0.67845 | 0.019315 | 0.019588 | 0.019679 | 0.019767 | 0.019633 | 0.019363 | 0.019238 | 0.01919 | 0.01889 | 0.018842 | 0.018795 | 0.018747 | 0.0187 | 0.018652 | 0.018605 | 0.018557 | 0.01851 | 0.018462 | 0.018414 | 0.018367 | 26869.1023 | 4575.9475 | 7400.8878 | 1260.4096 | 1081022.058 | 1081022.058 | 9049469.2576 | 1081022.058
| OYN001-24604668 | 921 | OYN001 | OYN | North | 21704586.4226 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 3.229 | 3.2492 | 3.2694 | 3.2896 | 3.3098 | 3.301 | 3.2921 | 3.2832 | 3.2743 | 3.2654 | 3.2565 | 3.2477 | 3.2388 | 3.2299 | 3.221 | 3.2121 | 3.2032 | 3.1944 | 3.1855 | 3.1766 | 0.092124 | 0.093056 | 0.093122 | 0.093182 | 0.092198 | 0.090915 | 0.090309 | 0.090066 | 0.088642 | 0.088401 | 0.088161 | 0.08792 | 0.08768 | 0.087439 | 0.087199 | 0.086958 | 0.086718 | 0.086477 | 0.086237 | 0.085996 | 26869.1023 | 4575.9475 | 34812.7092 | 5928.785 | 2335694.8494 | 2335694.8494 | 21704586.4226 | 2335694.8494
| OYN001-41898846 | 299 | OYN001 | OYN | North | 7046331.5313 | 0.0010248 | 0.0010287 | 0.0010231 | 0.0010175 | 0.0010006 | 0.0009893 | 0.00098536 | 0.00098536 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.00097241 | 0.26591 | 0.26785 | 0.26979 | 0.27174 | 0.27368 | 0.27312 | 0.27255 | 0.27199 | 0.27142 | 0.27086 | 0.2703 | 0.26973 | 0.26917 | 0.26861 | 0.26804 | 0.26748 | 0.26692 | 0.26635 | 0.26579 | 0.26523 | 0.0075863 | 0.0076711 | 0.0076845 | 0.0076972 | 0.0076235 | 0.0075222 | 0.0074768 | 0.0074613 | 0.007348 | 0.0073327 | 0.0073175 | 0.0073022 | 0.007287 | 0.0072717 | 0.0072564 | 0.0072412 | 0.0072259 | 0.0072107 | 0.0071954 | 0.0071802 | 26869.1023 | 4575.9475 | 2885.5995 | 491.4326 | 517410.2362 | 517410.2362 | 7046331.5313 | 517410.2362
| OYN003-15412682 | 173 | OYN003 | OYN | North | 4076974.4312 | 0.0010371 | 0.0010371 | 0.0010371 | 0.0010228 | 0.0010043 | 0.00099429 | 0.0010043 | 0.0010043 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.33787 | 0.34084 | 0.34381 | 0.34678 | 0.34976 | 0.3499 | 0.35003 | 0.35017 | 0.35031 | 0.35045 | 0.35059 | 0.35073 | 0.35086 | 0.351 | 0.35114 | 0.35128 | 0.35142 | 0.35156 | 0.3517 | 0.35183 | 0.0097552 | 0.009841 | 0.0099268 | 0.0098748 | 0.0097789 | 0.0096855 | 0.0097866 | 0.0097905 | 0.0095161 | 0.0095199 | 0.0095237 | 0.0095274 | 0.0095312 | 0.0095349 | 0.0095387 | 0.0095425 | 0.0095462 | 0.00955 | 0.0095538 | 0.0095575 | 26869.1023 | 4575.9475 | 3755.4499 | 639.5726 | 69618.7683 | 69618.7683 | 4076974.4312 | 69618.7683
| OYN003-157425942 | 11 | OYN003 | OYN | North | 259229.5881 | 0.0010371 | 0.0010371 | 0.0010371 | 0.0010228 | 0.0010043 | 0.00099429 | 0.0010043 | 0.0010043 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26869.1023 | 4575.9475 | 0 | 0 | 0 | 0 | 259229.5881 | 0
| OYN003-158041159 | 195 | OYN003 | OYN | North | 4595433.6074 | 0.0010371 | 0.0010371 | 0.0010371 | 0.0010228 | 0.0010043 | 0.00099429 | 0.0010043 | 0.0010043 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.022465 | 0.022672 | 0.022879 | 0.023087 | 0.023294 | 0.023313 | 0.023332 | 0.023351 | 0.023369 | 0.023388 | 0.023407 | 0.023426 | 0.023444 | 0.023463 | 0.023482 | 0.023501 | 0.023519 | 0.023538 | 0.023557 | 0.023576 | 0.00064861 | 0.0006546 | 0.00066059 | 0.00065741 | 0.00065129 | 0.00064533 | 0.00065234 | 0.00065286 | 0.00063482 | 0.00063533 | 0.00063584 | 0.00063635 | 0.00063686 | 0.00063737 | 0.00063788 | 0.00063839 | 0.0006389 | 0.00063941 | 0.00063992 | 0.00064043 | 26869.1023 | 4575.9475 | 250.5549 | 42.6708 | 49838.6608 | 49838.6608 | 4595433.6074 | 49838.6608
| OYN003-158109405 | 349 | OYN003 | OYN | North | 8224647.8409 | 0.0010371 | 0.0010371 | 0.0010371 | 0.0010228 | 0.0010043 | 0.00099429 | 0.0010043 | 0.0010043 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.020846 | 0.021039 | 0.021233 | 0.021426 | 0.02162 | 0.021631 | 0.021642 | 0.021653 | 0.021664 | 0.021675 | 0.021685 | 0.021696 | 0.021707 | 0.021718 | 0.021729 | 0.02174 | 0.021751 | 0.021762 | 0.021773 | 0.021784 | 0.00060187 | 0.00060746 | 0.00061305 | 0.00061013 | 0.00060447 | 0.00059877 | 0.00060509 | 0.00060539 | 0.00058849 | 0.00058879 | 0.00058908 | 0.00058938 | 0.00058968 | 0.00058997 | 0.00059027 | 0.00059057 | 0.00059086 | 0.00059116 | 0.00059146 | 0.00059175 | 26869.1023 | 4575.9475 | 232.1931 | 39.5437 | 320304.8722 | 320304.8722 | 8224647.8409 | 320304.8722
| OYN003-158109515 | 106 | OYN003 | OYN | North | 2498030.5763 | 0.0010371 | 0.0010371 | 0.0010371 | 0.0010228 | 0.0010043 | 0.00099429 | 0.0010043 | 0.0010043 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00010769 | 0.00010867 | 0.00010965 | 0.00011062 | 0.0001116 | 0.00011168 | 0.00011176 | 0.00011184 | 0.00011192 | 0.000112 | 0.00011208 | 0.00011216 | 0.00011224 | 0.00011232 | 0.0001124 | 0.00011248 | 0.00011256 | 0.00011264 | 0.00011272 | 0.0001128 | 3.1093e-06 | 3.1375e-06 | 3.1658e-06 | 3.15e-06 | 3.1202e-06 | 3.0914e-06 | 3.1247e-06 | 3.127e-06 | 3.0403e-06 | 3.0425e-06 | 3.0446e-06 | 3.0468e-06 | 3.049e-06 | 3.0512e-06 | 3.0533e-06 | 3.0555e-06 | 3.0577e-06 | 3.0598e-06 | 3.062e-06 | 3.0642e-06 | 26869.1023 | 4575.9475 | 1.2 | 0.20436 | 201.1097 | 201.1097 | 2498030.5763 | 201.1097
| OYN003-158109598 | 159 | OYN003 | OYN | North | 3747045.8645 | 0.0010371 | 0.0010371 | 0.0010371 | 0.0010228 | 0.0010043 | 0.00099429 | 0.0010043 | 0.0010043 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.01308 | 0.013197 | 0.013314 | 0.013432 | 0.013549 | 0.013566 | 0.013582 | 0.013599 | 0.013616 | 0.013632 | 0.013649 | 0.013666 | 0.013682 | 0.013699 | 0.013716 | 0.013733 | 0.013749 | 0.013766 | 0.013783 | 0.013799 | 0.00037764 | 0.00038103 | 0.00038442 | 0.00038247 | 0.00037882 | 0.00037551 | 0.00037975 | 0.00038022 | 0.00036987 | 0.00037032 | 0.00037078 | 0.00037123 | 0.00037168 | 0.00037214 | 0.00037259 | 0.00037304 | 0.00037349 | 0.00037395 | 0.0003744 | 0.00037485 | 26869.1023 | 4575.9475 | 146.0644 | 24.8755 | 33382.9058 | 33382.9058 | 3747045.8645 | 33382.9058
| OYN003-158109716 | 69 | OYN003 | OYN | North | 1626076.5072 | 0.0010371 | 0.0010371 | 0.0010371 | 0.0010228 | 0.0010043 | 0.00099429 | 0.0010043 | 0.0010043 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.0082236 | 0.0082927 | 0.0083617 | 0.0084308 | 0.0084998 | 0.0084923 | 0.0084847 | 0.0084772 | 0.0084696 | 0.0084621 | 0.0084545 | 0.0084469 | 0.0084394 | 0.0084318 | 0.0084243 | 0.0084167 | 0.0084092 | 0.0084016 | 0.0083941 | 0.0083865 | 0.00023744 | 0.00023943 | 0.00024143 | 0.00024007 | 0.00023765 | 0.00023508 | 0.00023723 | 0.00023701 | 0.00023008 | 0.00022987 | 0.00022967 | 0.00022946 | 0.00022925 | 0.00022905 | 0.00022884 | 0.00022864 | 0.00022843 | 0.00022823 | 0.00022802 | 0.00022782 | 26869.1023 | 4575.9475 | 90.709 | 15.4482 | 16490.3394 | 16490.3394 | 1626076.5072 | 16490.3394
| OYN003-158109850 | 76 | OYN003 | OYN | North | 1791040.7906 | 0.0010371 | 0.0010371 | 0.0010371 | 0.0010228 | 0.0010043 | 0.00099429 | 0.0010043 | 0.0010043 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.0069146 | 0.0069709 | 0.0070272 | 0.0070836 | 0.0071399 | 0.0071403 | 0.0071407 | 0.007141 | 0.0071414 | 0.0071418 | 0.0071422 | 0.0071425 | 0.0071429 | 0.0071433 | 0.0071437 | 0.0071441 | 0.0071444 | 0.0071448 | 0.0071452 | 0.0071456 | 0.00019964 | 0.00020127 | 0.00020289 | 0.00020171 | 0.00019963 | 0.00019765 | 0.00019965 | 0.00019966 | 0.000194 | 0.00019401 | 0.00019402 | 0.00019403 | 0.00019404 | 0.00019405 | 0.00019406 | 0.00019407 | 0.00019408 | 0.00019409 | 0.0001941 | 0.00019411 | 26869.1023 | 4575.9475 | 76.5653 | 13.0395 | 15332.4791 | 15332.4791 | 1791040.7906 | 15332.4791
| OYN003-158110054 | 135 | OYN003 | OYN | North | 3181454.0359 | 0.0010371 | 0.0010371 | 0.0010371 | 0.0010228 | 0.0010043 | 0.00099429 | 0.0010043 | 0.0010043 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.026781 | 0.027029 | 0.027276 | 0.027524 | 0.027771 | 0.027785 | 0.027798 | 0.027811 | 0.027824 | 0.027837 | 0.02785 | 0.027863 | 0.027876 | 0.027889 | 0.027902 | 0.027915 | 0.027928 | 0.027941 | 0.027954 | 0.027967 | 0.00077323 | 0.00078038 | 0.00078753 | 0.00078375 | 0.00077647 | 0.00076911 | 0.0007772 | 0.00077756 | 0.00075582 | 0.00075618 | 0.00075653 | 0.00075689 | 0.00075724 | 0.00075759 | 0.00075795 | 0.0007583 | 0.00075865 | 0.00075901 | 0.00075936 | 0.00075972 | 26869.1023 | 4575.9475 | 298.2134 | 50.7873 | 47149.1594 | 47149.1594 | 3181454.0359 | 47149.1594
| OYN003-161992042 | 22 | OYN003 | OYN | North | 518459.1762 | 0.0010371 | 0.0010371 | 0.0010371 | 0.0010228 | 0.0010043 | 0.00099429 | 0.0010043 | 0.0010043 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 0.00097575 | 4.892e-05 | 4.936e-05 | 4.98e-05 | 5.024e-05 | 5.068e-05 | 5.0645e-05 | 5.061e-05 | 5.0575e-05 | 5.054e-05 | 5.0505e-05 | 5.047e-05 | 5.0435e-05 | 5.04e-05 | 5.0365e-05 | 5.033e-05 | 5.0295e-05 | 5.026e-05 | 5.0225e-05 | 5.019e-05 | 5.0155e-05 | 1.4124e-06 | 1.4252e-06 | 1.4379e-06 | 1.4306e-06 | 1.417e-06 | 1.4019e-06 | 1.415e-06 | 1.414e-06 | 1.3729e-06 | 1.372e-06 | 1.371e-06 | 1.3701e-06 | 1.3691e-06 | 1.3682e-06 | 1.3672e-06 | 1.3663e-06 | 1.3653e-06 | 1.3644e-06 | 1.3634e-06 | 1.3625e-06 | 26869.1023 | 4575.9475 | 0.54117 | 0.092165 | 53.7759 | 53.7759 | 518459.1762 | 53.7759
| OYN005-15412808 | 288 | OYN005 | OYN | North | 6787101.9432 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 3.7139 | 3.7412 | 3.7684 | 3.7956 | 3.8228 | 3.8181 | 3.8134 | 3.8087 | 3.804 | 3.7992 | 3.7945 | 3.7898 | 3.7851 | 3.7804 | 3.7756 | 3.7709 | 3.7662 | 3.7615 | 3.7568 | 3.752 | 0.13193 | 0.13302 | 0.13345 | 0.13317 | 0.13192 | 0.13009 | 0.12939 | 0.12881 | 0.1267 | 0.12654 | 0.12639 | 0.12623 | 0.12607 | 0.12591 | 0.12576 | 0.1256 | 0.12544 | 0.12529 | 0.12513 | 0.12497 | 26869.1023 | 4575.9475 | 49979.7266 | 8511.8067 | 407304.929 | 407304.929 | 6787101.9432 | 407304.929
| OYN005-159372302 | 271 | OYN005 | OYN | North | 6386474.398 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.10332 | 0.10437 | 0.10543 | 0.10648 | 0.10754 | 0.10791 | 0.10829 | 0.10867 | 0.10904 | 0.10942 | 0.1098 | 0.11018 | 0.11055 | 0.11093 | 0.11131 | 0.11169 | 0.11206 | 0.11244 | 0.11282 | 0.1132 | 0.0036701 | 0.003711 | 0.0037335 | 0.003736 | 0.0037108 | 0.0036768 | 0.0036742 | 0.0036752 | 0.003632 | 0.0036446 | 0.0036572 | 0.0036697 | 0.0036823 | 0.0036949 | 0.0037075 | 0.00372 | 0.0037326 | 0.0037452 | 0.0037577 | 0.0037703 | 26869.1023 | 4575.9475 | 1436.4903 | 244.6417 | 669401.5811 | 669401.5811 | 6386474.398 | 669401.5811
| OYN005-159377479 | 27 | OYN005 | OYN | North | 636290.8072 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0082295 | 0.0083045 | 0.0083796 | 0.0084547 | 0.0085297 | 0.008553 | 0.0085762 | 0.0085994 | 0.0086226 | 0.0086459 | 0.0086691 | 0.0086923 | 0.0087156 | 0.0087388 | 0.008762 | 0.0087852 | 0.0088085 | 0.0088317 | 0.0088549 | 0.0088781 | 0.00029234 | 0.00029527 | 0.00029675 | 0.00029664 | 0.00029435 | 0.00029141 | 0.00029099 | 0.00029084 | 0.0002872 | 0.00028797 | 0.00028875 | 0.00028952 | 0.00029029 | 0.00029107 | 0.00029184 | 0.00029261 | 0.00029339 | 0.00029416 | 0.00029494 | 0.00029571 | 26869.1023 | 4575.9475 | 113.5844 | 19.344 | 11299.1289 | 11299.1289 | 636290.8072 | 11299.1289
| OYN005-160435471 | 53 | OYN005 | OYN | North | 1249015.2882 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.028558 | 0.028822 | 0.029085 | 0.029349 | 0.029613 | 0.029718 | 0.029823 | 0.029928 | 0.030033 | 0.030138 | 0.030243 | 0.030348 | 0.030452 | 0.030557 | 0.030662 | 0.030767 | 0.030872 | 0.030977 | 0.031082 | 0.031187 | 0.0010145 | 0.0010248 | 0.00103 | 0.0010298 | 0.0010219 | 0.0010125 | 0.0010119 | 0.0010122 | 0.0010003 | 0.0010038 | 0.0010073 | 0.0010108 | 0.0010143 | 0.0010178 | 0.0010213 | 0.0010248 | 0.0010283 | 0.0010318 | 0.0010353 | 0.0010388 | 26869.1023 | 4575.9475 | 395.8866 | 67.4215 | 41629.3612 | 41629.3612 | 1249015.2882 | 41629.3612
| OYN005-160491322 | 47 | OYN005 | OYN | North | 1107617.331 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.01547 | 0.015592 | 0.015714 | 0.015836 | 0.015958 | 0.016007 | 0.016055 | 0.016104 | 0.016153 | 0.016202 | 0.01625 | 0.016299 | 0.016348 | 0.016397 | 0.016446 | 0.016494 | 0.016543 | 0.016592 | 0.016641 | 0.016689 | 0.00054952 | 0.00055437 | 0.00055648 | 0.00055562 | 0.00055067 | 0.00054537 | 0.00054475 | 0.00054465 | 0.00053801 | 0.00053964 | 0.00054126 | 0.00054289 | 0.00054451 | 0.00054614 | 0.00054776 | 0.00054939 | 0.00055101 | 0.00055264 | 0.00055426 | 0.00055589 | 26869.1023 | 4575.9475 | 213.0112 | 36.2769 | 25820.2905 | 25820.2905 | 1107617.331 | 25820.2905
| OYN005-160578653 | 108 | OYN005 | OYN | North | 2545163.2287 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26869.1023 | 4575.9475 | 0 | 0 | 0 | 0 | 2545163.2287 | 0
| OYN005-160637132 | 58 | OYN005 | OYN | North | 1366846.9191 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.001495 | 0.0015104 | 0.0015258 | 0.0015413 | 0.0015567 | 0.0015584 | 0.0015601 | 0.0015618 | 0.0015635 | 0.0015652 | 0.0015669 | 0.0015686 | 0.0015703 | 0.001572 | 0.0015737 | 0.0015754 | 0.0015772 | 0.0015789 | 0.0015806 | 0.0015823 | 5.3107e-05 | 5.3704e-05 | 5.4036e-05 | 5.4078e-05 | 5.3718e-05 | 5.3097e-05 | 5.2934e-05 | 5.2821e-05 | 5.2077e-05 | 5.2134e-05 | 5.219e-05 | 5.2247e-05 | 5.2304e-05 | 5.2361e-05 | 5.2417e-05 | 5.2474e-05 | 5.2531e-05 | 5.2588e-05 | 5.2645e-05 | 5.2701e-05 | 26869.1023 | 4575.9475 | 20.5488 | 3.4996 | 6146.8206 | 6146.8206 | 1366846.9191 | 6146.8206
| OYN005-160827931 | 217 | OYN005 | OYN | North | 5113892.7836 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.092317 | 0.093114 | 0.09391 | 0.094707 | 0.095504 | 0.095509 | 0.095515 | 0.09552 | 0.095526 | 0.095531 | 0.095537 | 0.095542 | 0.095548 | 0.095553 | 0.095558 | 0.095564 | 0.095569 | 0.095575 | 0.09558 | 0.095586 | 0.0032794 | 0.0033107 | 0.0033257 | 0.0033229 | 0.0032957 | 0.0032541 | 0.0032408 | 0.0032305 | 0.0031817 | 0.0031819 | 0.0031821 | 0.0031823 | 0.0031825 | 0.0031826 | 0.0031828 | 0.003183 | 0.0031832 | 0.0031834 | 0.0031836 | 0.0031837 | 26869.1023 | 4575.9475 | 1255.5874 | 213.833 | 319319.4875 | 319319.4875 | 5113892.7836 | 319319.4875
| OYN005-160828059 | 129 | OYN005 | OYN | North | 3040056.0787 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.027127 | 0.02735 | 0.027574 | 0.027797 | 0.028021 | 0.02804 | 0.02806 | 0.02808 | 0.028099 | 0.028119 | 0.028138 | 0.028158 | 0.028178 | 0.028197 | 0.028217 | 0.028236 | 0.028256 | 0.028276 | 0.028295 | 0.028315 | 0.00096362 | 0.00097246 | 0.00097649 | 0.00097531 | 0.00096694 | 0.00095538 | 0.00095206 | 0.00094966 | 0.00093591 | 0.00093657 | 0.00093722 | 0.00093787 | 0.00093853 | 0.00093918 | 0.00093983 | 0.00094049 | 0.00094114 | 0.00094179 | 0.00094245 | 0.0009431 | 26869.1023 | 4575.9475 | 369.652 | 62.9537 | 72326.6717 | 72326.6717 | 3040056.0787 | 72326.6717
| OYN005-160828223 | 25 | OYN005 | OYN | North | 589158.1548 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 5.4137e-05 | 5.4603e-05 | 5.5069e-05 | 5.5534e-05 | 5.6e-05 | 5.59e-05 | 5.58e-05 | 5.57e-05 | 5.56e-05 | 5.55e-05 | 5.54e-05 | 5.53e-05 | 5.52e-05 | 5.51e-05 | 5.5e-05 | 5.49e-05 | 5.48e-05 | 5.47e-05 | 5.46e-05 | 5.45e-05 | 1.9231e-06 | 1.9414e-06 | 1.9502e-06 | 1.9485e-06 | 1.9325e-06 | 1.9046e-06 | 1.8933e-06 | 1.8838e-06 | 1.8519e-06 | 1.8486e-06 | 1.8452e-06 | 1.8419e-06 | 1.8386e-06 | 1.8352e-06 | 1.8319e-06 | 1.8286e-06 | 1.8253e-06 | 1.8219e-06 | 1.8186e-06 | 1.8153e-06 | 26869.1023 | 4575.9475 | 0.72953 | 0.12424 | 94.0315 | 94.0315 | 589158.1548 | 94.0315
| OYN005-160829369 | 119 | OYN005 | OYN | North | 2804392.8168 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.074525 | 0.075067 | 0.075608 | 0.07615 | 0.076692 | 0.076632 | 0.076572 | 0.076511 | 0.076451 | 0.076391 | 0.076331 | 0.07627 | 0.07621 | 0.07615 | 0.07609 | 0.07603 | 0.075969 | 0.075909 | 0.075849 | 0.075789 | 0.0026473 | 0.0026691 | 0.0026776 | 0.0026718 | 0.0026465 | 0.002611 | 0.0025981 | 0.0025877 | 0.0025464 | 0.0025444 | 0.0025424 | 0.0025404 | 0.0025384 | 0.0025364 | 0.0025344 | 0.0025324 | 0.0025304 | 0.0025283 | 0.0025263 | 0.0025243 | 26869.1023 | 4575.9475 | 1004.9524 | 171.1486 | 128460.7261 | 128460.7261 | 2804392.8168 | 128460.7261
| OYN005-160829541 | 61 | OYN005 | OYN | North | 1437545.8977 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.022692 | 0.022885 | 0.023078 | 0.023271 | 0.023465 | 0.023479 | 0.023494 | 0.023509 | 0.023524 | 0.023539 | 0.023554 | 0.023568 | 0.023583 | 0.023598 | 0.023613 | 0.023628 | 0.023642 | 0.023657 | 0.023672 | 0.023687 | 0.00080608 | 0.00081369 | 0.00081729 | 0.00081651 | 0.00080972 | 0.00079998 | 0.00079715 | 0.00079509 | 0.00078353 | 0.00078402 | 0.00078451 | 0.00078501 | 0.0007855 | 0.00078599 | 0.00078649 | 0.00078698 | 0.00078747 | 0.00078797 | 0.00078846 | 0.00078895 | 26869.1023 | 4575.9475 | 309.389 | 52.6906 | 37433.1378 | 37433.1378 | 1437545.8977 | 37433.1378
| OYN005-160930811 | 107 | OYN005 | OYN | North | 2521596.9025 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0211 | 0.021298 | 0.021496 | 0.021694 | 0.021892 | 0.021926 | 0.021961 | 0.021995 | 0.02203 | 0.022064 | 0.022099 | 0.022133 | 0.022168 | 0.022203 | 0.022237 | 0.022272 | 0.022306 | 0.022341 | 0.022375 | 0.02241 | 0.00074952 | 0.00075725 | 0.00076124 | 0.00076115 | 0.00075544 | 0.00074706 | 0.00074512 | 0.00074389 | 0.00073376 | 0.00073491 | 0.00073606 | 0.00073721 | 0.00073836 | 0.00073951 | 0.00074067 | 0.00074182 | 0.00074297 | 0.00074412 | 0.00074527 | 0.00074642 | 26869.1023 | 4575.9475 | 289.8363 | 49.3606 | 33322.7321 | 33322.7321 | 2521596.9025 | 33322.7321
| OYN005-160930950 | 123 | OYN005 | OYN | North | 2898658.1216 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.11732 | 0.11849 | 0.11966 | 0.12083 | 0.122 | 0.1224 | 0.12281 | 0.12321 | 0.12362 | 0.12402 | 0.12443 | 0.12484 | 0.12524 | 0.12565 | 0.12605 | 0.12646 | 0.12686 | 0.12727 | 0.12768 | 0.12808 | 0.0041677 | 0.004213 | 0.0042376 | 0.0042394 | 0.0042098 | 0.0041704 | 0.0041668 | 0.0041671 | 0.0041174 | 0.0041309 | 0.0041445 | 0.004158 | 0.0041715 | 0.004185 | 0.0041985 | 0.004212 | 0.0042256 | 0.0042391 | 0.0042526 | 0.0042661 | 26869.1023 | 4575.9475 | 1628.4551 | 277.3344 | 191343.0176 | 191343.0176 | 2898658.1216 | 191343.0176
| OYN005-160931147 | 60 | OYN005 | OYN | North | 1413979.5715 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.013047 | 0.01314 | 0.013232 | 0.013325 | 0.013418 | 0.01342 | 0.013422 | 0.013424 | 0.013426 | 0.013428 | 0.01343 | 0.013432 | 0.013434 | 0.013436 | 0.013438 | 0.01344 | 0.013442 | 0.013445 | 0.013447 | 0.013449 | 0.00046346 | 0.00046719 | 0.00046861 | 0.00046753 | 0.00046303 | 0.00045724 | 0.0004554 | 0.00045401 | 0.00044719 | 0.00044726 | 0.00044733 | 0.0004474 | 0.00044746 | 0.00044753 | 0.0004476 | 0.00044767 | 0.00044774 | 0.0004478 | 0.00044787 | 0.00044794 | 26869.1023 | 4575.9475 | 176.6619 | 30.0864 | 34161.135 | 34161.135 | 1413979.5715 | 34161.135
| OYN005-160960634 | 91 | OYN005 | OYN | North | 2144535.6835 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.11589 | 0.11701 | 0.11812 | 0.11924 | 0.12035 | 0.12053 | 0.1207 | 0.12087 | 0.12105 | 0.12122 | 0.12139 | 0.12157 | 0.12174 | 0.12191 | 0.12209 | 0.12226 | 0.12243 | 0.12261 | 0.12278 | 0.12295 | 0.0041167 | 0.0041602 | 0.0041832 | 0.0041837 | 0.0041532 | 0.0041066 | 0.0040953 | 0.004088 | 0.0040318 | 0.0040376 | 0.0040433 | 0.0040491 | 0.0040549 | 0.0040607 | 0.0040664 | 0.0040722 | 0.004078 | 0.0040837 | 0.0040895 | 0.0040953 | 26869.1023 | 4575.9475 | 1592.1074 | 271.1441 | 177912.5656 | 177912.5656 | 2144535.6835 | 177912.5656
| OYN005-160960891 | 46 | OYN005 | OYN | North | 1084051.0048 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0091114 | 0.0091927 | 0.0092741 | 0.0093554 | 0.0094368 | 0.009457 | 0.0094772 | 0.0094973 | 0.0095175 | 0.0095377 | 0.0095579 | 0.0095781 | 0.0095983 | 0.0096185 | 0.0096387 | 0.0096589 | 0.0096791 | 0.0096993 | 0.0097195 | 0.0097397 | 0.00032366 | 0.00032685 | 0.00032843 | 0.00032825 | 0.00032564 | 0.00032221 | 0.00032156 | 0.00032121 | 0.00031701 | 0.00031768 | 0.00031835 | 0.00031902 | 0.0003197 | 0.00032037 | 0.00032104 | 0.00032172 | 0.00032239 | 0.00032306 | 0.00032373 | 0.00032441 | 26869.1023 | 4575.9475 | 125.32 | 21.3427 | 24777.703 | 24777.703 | 1084051.0048 | 24777.703
| OYN005-161887259 | 283 | OYN005 | OYN | North | 6669270.3123 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 1.9234 | 1.9405 | 1.9577 | 1.9748 | 1.992 | 1.9966 | 2.0012 | 2.0058 | 2.0104 | 2.015 | 2.0197 | 2.0243 | 2.0289 | 2.0335 | 2.0381 | 2.0427 | 2.0474 | 2.052 | 2.0566 | 2.0612 | 0.068325 | 0.068998 | 0.069329 | 0.069289 | 0.068738 | 0.068026 | 0.0679 | 0.067837 | 0.066962 | 0.067116 | 0.06727 | 0.067424 | 0.067578 | 0.067731 | 0.067885 | 0.068039 | 0.068193 | 0.068347 | 0.0685 | 0.068654 | 26869.1023 | 4575.9475 | 26476.4763 | 4509.0813 | 636510.5672 | 636510.5672 | 6669270.3123 | 636510.5672
| OYN005-162206992 | 9 | OYN005 | OYN | North | 212096.9357 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26869.1023 | 4575.9475 | 0 | 0 | 0 | 0 | 212096.9357 | 0
| OYN005-162260630 | 2 | OYN005 | OYN | North | 47132.6524 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26869.1023 | 4575.9475 | 0 | 0 | 0 | 0 | 47132.6524 | 0
| OYN005-162551906 | 117 | OYN005 | OYN | North | 2757260.1644 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.023357 | 0.023558 | 0.023759 | 0.02396 | 0.024161 | 0.024255 | 0.024349 | 0.024443 | 0.024537 | 0.024631 | 0.024725 | 0.024819 | 0.024914 | 0.025008 | 0.025102 | 0.025196 | 0.02529 | 0.025384 | 0.025478 | 0.025572 | 0.00082972 | 0.00083762 | 0.00084139 | 0.00084066 | 0.00083374 | 0.0008264 | 0.00082615 | 0.00082667 | 0.00081727 | 0.00082041 | 0.00082354 | 0.00082667 | 0.00082981 | 0.00083294 | 0.00083608 | 0.00083921 | 0.00084235 | 0.00084548 | 0.00084862 | 0.00085175 | 26869.1023 | 4575.9475 | 323.6788 | 55.1242 | 54266.4554 | 54266.4554 | 2757260.1644 | 54266.4554
| OYN005-162690111 | 24 | OYN005 | OYN | North | 565591.8286 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26869.1023 | 4575.9475 | 0 | 0 | 0 | 0 | 565591.8286 | 0
| OYN005-162952933 | 7 | OYN005 | OYN | North | 164964.2833 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26869.1023 | 4575.9475 | 0 | 0 | 0 | 0 | 164964.2833 | 0
| OYN005-164254226 | 47 | OYN005 | OYN | North | 1107617.331 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.013119 | 0.013251 | 0.013382 | 0.013514 | 0.013645 | 0.01366 | 0.013674 | 0.013688 | 0.013702 | 0.013717 | 0.013731 | 0.013745 | 0.013759 | 0.013774 | 0.013788 | 0.013802 | 0.013817 | 0.013831 | 0.013845 | 0.013859 | 0.00046603 | 0.00047114 | 0.00047392 | 0.00047415 | 0.00047087 | 0.0004654 | 0.00046395 | 0.00046294 | 0.00045639 | 0.00045687 | 0.00045734 | 0.00045782 | 0.00045829 | 0.00045877 | 0.00045924 | 0.00045972 | 0.0004602 | 0.00046067 | 0.00046115 | 0.00046162 | 26869.1023 | 4575.9475 | 180.1117 | 30.674 | 24254.7632 | 24254.7632 | 1107617.331 | 24254.7632
| OYN005-164254377 | 59 | OYN005 | OYN | North | 1390413.2453 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.051799 | 0.052237 | 0.052674 | 0.053112 | 0.053549 | 0.05365 | 0.053751 | 0.053852 | 0.053953 | 0.054054 | 0.054155 | 0.054256 | 0.054357 | 0.054458 | 0.054559 | 0.05466 | 0.054761 | 0.054862 | 0.054963 | 0.055064 | 0.0018401 | 0.0018573 | 0.0018654 | 0.0018635 | 0.0018479 | 0.001828 | 0.0018238 | 0.0018213 | 0.0017971 | 0.0018004 | 0.0018038 | 0.0018072 | 0.0018105 | 0.0018139 | 0.0018172 | 0.0018206 | 0.001824 | 0.0018273 | 0.0018307 | 0.0018341 | 26869.1023 | 4575.9475 | 710.4685 | 120.9965 | 63586.598 | 63586.598 | 1390413.2453 | 63586.598
| OYN005-164276023 | 151 | OYN005 | OYN | North | 3558515.255 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.13197 | 0.13289 | 0.13381 | 0.13473 | 0.13565 | 0.13552 | 0.13538 | 0.13525 | 0.13511 | 0.13498 | 0.13484 | 0.13471 | 0.13457 | 0.13444 | 0.1343 | 0.13417 | 0.13403 | 0.1339 | 0.13376 | 0.13363 | 0.0046881 | 0.0047251 | 0.0047388 | 0.0047273 | 0.0046811 | 0.0046173 | 0.0045935 | 0.0045741 | 0.0045003 | 0.0044958 | 0.0044913 | 0.0044868 | 0.0044823 | 0.0044778 | 0.0044733 | 0.0044688 | 0.0044643 | 0.0044598 | 0.0044553 | 0.0044508 | 26869.1023 | 4575.9475 | 1776.0475 | 302.4701 | 238402.0757 | 238402.0757 | 3558515.255 | 238402.0757
| OYN005-164365790 | 11 | OYN005 | OYN | North | 259229.5881 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.050274 | 0.050748 | 0.051223 | 0.051697 | 0.052172 | 0.052192 | 0.052213 | 0.052233 | 0.052254 | 0.052274 | 0.052295 | 0.052315 | 0.052336 | 0.052356 | 0.052377 | 0.052397 | 0.052418 | 0.052438 | 0.052459 | 0.052479 | 0.0017859 | 0.0018044 | 0.001814 | 0.0018139 | 0.0018003 | 0.0017783 | 0.0017716 | 0.0017666 | 0.0017404 | 0.0017411 | 0.0017418 | 0.0017425 | 0.0017432 | 0.0017439 | 0.0017445 | 0.0017452 | 0.0017459 | 0.0017466 | 0.0017473 | 0.001748 | 26869.1023 | 4575.9475 | 686.6836 | 116.9458 | 7790.6639 | 7790.6639 | 259229.5881 | 7790.6639
| OYN005-164366490 | 52 | OYN005 | OYN | North | 1225448.962 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.00068215 | 0.00068927 | 0.00069638 | 0.00070349 | 0.0007106 | 0.00071231 | 0.00071402 | 0.00071573 | 0.00071744 | 0.00071915 | 0.00072086 | 0.00072257 | 0.00072428 | 0.00072599 | 0.0007277 | 0.00072941 | 0.00073112 | 0.00073283 | 0.00073454 | 0.00073625 | 2.4232e-05 | 2.4507e-05 | 2.4661e-05 | 2.4683e-05 | 2.4521e-05 | 2.4269e-05 | 2.4226e-05 | 2.4206e-05 | 2.3896e-05 | 2.3953e-05 | 2.401e-05 | 2.4067e-05 | 2.4124e-05 | 2.4181e-05 | 2.4238e-05 | 2.4295e-05 | 2.4352e-05 | 2.4409e-05 | 2.4466e-05 | 2.4523e-05 | 26869.1023 | 4575.9475 | 9.4401 | 1.6077 | 666.3315 | 666.3315 | 1225448.962 | 666.3315
| OYN005-164366901 | 9 | OYN005 | OYN | North | 212096.9357 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.010547 | 0.010661 | 0.010775 | 0.010889 | 0.011004 | 0.011022 | 0.01104 | 0.011058 | 0.011076 | 0.011094 | 0.011112 | 0.01113 | 0.011148 | 0.011166 | 0.011184 | 0.011202 | 0.01122 | 0.011238 | 0.011256 | 0.011274 | 0.00037465 | 0.00037905 | 0.00038159 | 0.00038207 | 0.00037971 | 0.00037552 | 0.00037457 | 0.00037398 | 0.00036891 | 0.00036951 | 0.00037011 | 0.00037071 | 0.00037131 | 0.00037191 | 0.00037251 | 0.00037311 | 0.00037371 | 0.00037431 | 0.00037491 | 0.00037551 | 26869.1023 | 4575.9475 | 145.5928 | 24.7952 | 4827.4596 | 4827.4596 | 212096.9357 | 4827.4596
| OYN005-203082808 | 102 | OYN005 | OYN | North | 2403765.2716 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.24552 | 0.2478 | 0.25008 | 0.25236 | 0.25464 | 0.25497 | 0.2553 | 0.25563 | 0.25596 | 0.25629 | 0.25662 | 0.25695 | 0.25728 | 0.25761 | 0.25794 | 0.25827 | 0.2586 | 0.25893 | 0.25926 | 0.25959 | 0.0087218 | 0.0088109 | 0.0088564 | 0.0088545 | 0.0087872 | 0.0086873 | 0.0086623 | 0.0086456 | 0.0085255 | 0.0085365 | 0.0085475 | 0.0085585 | 0.0085695 | 0.0085805 | 0.0085915 | 0.0086025 | 0.0086134 | 0.0086244 | 0.0086354 | 0.0086464 | 26869.1023 | 4575.9475 | 3366.8985 | 573.4003 | 164752.5521 | 164752.5521 | 2403765.2716 | 164752.5521
| OYN005-203102592 | 122 | OYN005 | OYN | North | 2875091.7954 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.075446 | 0.076169 | 0.076892 | 0.077615 | 0.078338 | 0.078466 | 0.078594 | 0.078721 | 0.078849 | 0.078977 | 0.079104 | 0.079232 | 0.07936 | 0.079487 | 0.079615 | 0.079742 | 0.07987 | 0.079998 | 0.080125 | 0.080253 | 0.0026801 | 0.0027083 | 0.0027231 | 0.0027233 | 0.0027033 | 0.0026735 | 0.0026667 | 0.0026624 | 0.0026263 | 0.0026305 | 0.0026348 | 0.002639 | 0.0026433 | 0.0026475 | 0.0026518 | 0.002656 | 0.0026603 | 0.0026645 | 0.0026688 | 0.002673 | 26869.1023 | 4575.9475 | 1037.297 | 176.6571 | 7366.2813 | 7366.2813 | 2875091.7954 | 7366.2813
| OYN005-24603468 | 127 | OYN005 | OYN | North | 2992923.4264 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.15855 | 0.16 | 0.16144 | 0.16289 | 0.16434 | 0.16432 | 0.16431 | 0.1643 | 0.16429 | 0.16428 | 0.16427 | 0.16426 | 0.16424 | 0.16423 | 0.16422 | 0.16421 | 0.1642 | 0.16419 | 0.16417 | 0.16416 | 0.0056322 | 0.0056888 | 0.0057173 | 0.0057152 | 0.0056709 | 0.0055988 | 0.0055751 | 0.0055568 | 0.0054721 | 0.0054717 | 0.0054713 | 0.0054709 | 0.0054706 | 0.0054702 | 0.0054698 | 0.0054694 | 0.005469 | 0.0054687 | 0.0054683 | 0.0054679 | 26869.1023 | 4575.9475 | 2158.4777 | 367.5999 | 152577.3254 | 152577.3254 | 2992923.4264 | 152577.3254
| OYN005-24603482 | 316 | OYN005 | OYN | North | 7446959.0766 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 4.393 | 4.4311 | 4.4692 | 4.5073 | 4.5454 | 4.5552 | 4.5651 | 4.5749 | 4.5847 | 4.5945 | 4.6044 | 4.6142 | 4.624 | 4.6338 | 4.6437 | 4.6535 | 4.6633 | 4.6731 | 4.683 | 4.6928 | 0.15605 | 0.15755 | 0.15827 | 0.15815 | 0.15685 | 0.1552 | 0.15489 | 0.15473 | 0.15271 | 0.15303 | 0.15336 | 0.15369 | 0.15401 | 0.15434 | 0.15467 | 0.155 | 0.15532 | 0.15565 | 0.15598 | 0.15631 | 26869.1023 | 4575.9475 | 60379.0396 | 10282.8637 | 1180056.2664 | 1180056.2664 | 7446959.0766 | 1180056.2664
| OYN005-84748828 | 93 | OYN005 | OYN | North | 2191668.3358 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 1.0334 | 1.0436 | 1.0538 | 1.064 | 1.0741 | 1.076 | 1.0778 | 1.0796 | 1.0814 | 1.0833 | 1.0851 | 1.0869 | 1.0888 | 1.0906 | 1.0924 | 1.0942 | 1.0961 | 1.0979 | 1.0997 | 1.1015 | 0.03671 | 0.037106 | 0.037318 | 0.037331 | 0.037066 | 0.03666 | 0.036569 | 0.036513 | 0.03602 | 0.036081 | 0.036142 | 0.036203 | 0.036264 | 0.036325 | 0.036385 | 0.036446 | 0.036507 | 0.036568 | 0.036629 | 0.03669 | 26869.1023 | 4575.9475 | 14225.5138 | 2422.6788 | 144946.4722 | 144946.4722 | 2191668.3358 | 144946.4722
| OYN005-88333607 | 130 | OYN005 | OYN | North | 3063622.4049 | 0.001276 | 0.0012771 | 0.0012721 | 0.0012603 | 0.0012395 | 0.0012238 | 0.0012187 | 0.0012148 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.0011964 | 0.024422 | 0.024631 | 0.024841 | 0.02505 | 0.02526 | 0.025263 | 0.025267 | 0.025271 | 0.025274 | 0.025278 | 0.025282 | 0.025285 | 0.025289 | 0.025293 | 0.025297 | 0.0253 | 0.025304 | 0.025308 | 0.025311 | 0.025315 | 0.00086755 | 0.00087579 | 0.00087971 | 0.00087892 | 0.00087166 | 0.00086076 | 0.0008573 | 0.00085467 | 0.00084183 | 0.00084195 | 0.00084207 | 0.0008422 | 0.00084232 | 0.00084244 | 0.00084257 | 0.00084269 | 0.00084281 | 0.00084293 | 0.00084306 | 0.00084318 | 26869.1023 | 4575.9475 | 332.2458 | 56.5832 | 50620.3091 | 50620.3091 | 3063622.4049 | 50620.3091
| OYN007-15412819 | 150 | OYN007 | OYN | North | 3534948.9288 | 0.0017094 | 0.0016842 | 0.001669 | 0.0016384 | 0.0016056 | 0.0015828 | 0.0015728 | 0.0015576 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.15455 | 0.15588 | 0.15722 | 0.15855 | 0.15988 | 0.15982 | 0.15975 | 0.15968 | 0.15962 | 0.15955 | 0.15948 | 0.15941 | 0.15935 | 0.15928 | 0.15921 | 0.15915 | 0.15908 | 0.15901 | 0.15895 | 0.15888 | 0.0073548 | 0.0073091 | 0.0073048 | 0.0072321 | 0.007147 | 0.0070422 | 0.0069951 | 0.0069244 | 0.0067859 | 0.006783 | 0.0067802 | 0.0067773 | 0.0067745 | 0.0067716 | 0.0067688 | 0.0067659 | 0.0067631 | 0.0067602 | 0.0067574 | 0.0067545 | 26869.1023 | 4575.9475 | 2706.5858 | 460.9456 | 12419.4913 | 12419.4913 | 3534948.9288 | 12419.4913
| OYN007-15412830 | 0 | OYN007 | OYN | North | 0 | 0.0017094 | 0.0016842 | 0.001669 | 0.0016384 | 0.0016056 | 0.0015828 | 0.0015728 | 0.0015576 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0.0015271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26869.1023 | 4575.9475 | 0 | 0 | 0 | 0 | 0 | 0
| PLD001-128232196 | 256 | PLD001 | PLD | South | 4654282.5297 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 1.54 | 1.5565 | 1.573 | 1.5895 | 1.6059 | 1.567 | 1.5282 | 1.4893 | 1.4504 | 1.4115 | 1.3726 | 1.3337 | 1.2948 | 1.2559 | 1.217 | 1.1781 | 1.1392 | 1.1003 | 1.0614 | 1.0225 | 0.04867 | 0.048854 | 0.049259 | 0.049317 | 0.049216 | 0.047799 | 0.046722 | 0.045533 | 0.043749 | 0.042576 | 0.041403 | 0.04023 | 0.039057 | 0.037883 | 0.03671 | 0.035537 | 0.034364 | 0.033191 | 0.032018 | 0.030844 | 34069.5054 | 6406.3237 | 21104.1212 | 3968.3532 | 103892.7263 | 134667.9503 | 4857162.5297 | 108421.4063
| PLD001-15398772 | 81 | PLD001 | PLD | South | 1472644.0816 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 7.9029 | 7.9808 | 8.0587 | 8.1366 | 8.2145 | 8.035 | 7.8555 | 7.676 | 7.4965 | 7.317 | 7.1375 | 6.958 | 6.7785 | 6.5989 | 6.4194 | 6.2399 | 6.0604 | 5.8809 | 5.7014 | 5.5219 | 0.24976 | 0.2505 | 0.25236 | 0.25246 | 0.25174 | 0.24509 | 0.24018 | 0.23469 | 0.22613 | 0.22071 | 0.2153 | 0.20988 | 0.20447 | 0.19905 | 0.19364 | 0.18822 | 0.18281 | 0.17739 | 0.17198 | 0.16656 | 34069.5054 | 6406.3237 | 109466.0219 | 20583.65 | 87869.5942 | 113898.4274 | 1536836.5816 | 91699.8265
| PLD001-159945085 | 36 | PLD001 | PLD | South | 654508.4807 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0037109 | 0.0037408 | 0.0037706 | 0.0038004 | 0.0038303 | 0.0037664 | 0.0037025 | 0.0036387 | 0.0035748 | 0.0035109 | 0.0034471 | 0.0033832 | 0.0033194 | 0.0032555 | 0.0031916 | 0.0031278 | 0.0030639 | 0.003 | 0.0029362 | 0.0028723 | 0.00011728 | 0.00011741 | 0.00011808 | 0.00011792 | 0.00011738 | 0.00011488 | 0.0001132 | 0.00011125 | 0.00010783 | 0.0001059 | 0.00010398 | 0.00010205 | 0.00010013 | 9.8199e-05 | 9.6273e-05 | 9.4346e-05 | 9.242e-05 | 9.0493e-05 | 8.8567e-05 | 8.6641e-05 | 34069.5054 | 6406.3237 | 52.5895 | 9.8888 | 1942.7572 | 2518.243 | 683038.4807 | 2027.4419
| PLD001-160255348 | 25 | PLD001 | PLD | South | 454519.7783 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0013898 | 0.0014 | 0.0014102 | 0.0014205 | 0.0014307 | 0.0014052 | 0.0013798 | 0.0013543 | 0.0013289 | 0.0013034 | 0.001278 | 0.0012525 | 0.001227 | 0.0012016 | 0.0011761 | 0.0011507 | 0.0011252 | 0.0010998 | 0.0010743 | 0.0010489 | 4.3922e-05 | 4.3942e-05 | 4.4162e-05 | 4.4073e-05 | 4.3845e-05 | 4.2863e-05 | 4.2186e-05 | 4.1407e-05 | 4.0084e-05 | 3.9316e-05 | 3.8548e-05 | 3.7781e-05 | 3.7013e-05 | 3.6245e-05 | 3.5477e-05 | 3.4709e-05 | 3.3942e-05 | 3.3174e-05 | 3.2406e-05 | 3.1638e-05 | 34069.5054 | 6406.3237 | 19.533 | 3.6729 | 709.8296 | 920.0962 | 474332.2783 | 740.7711
| PLD001-160255473 | 43 | PLD001 | PLD | South | 781774.0187 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0086248 | 0.0086846 | 0.0087444 | 0.0088041 | 0.0088639 | 0.0087596 | 0.0086553 | 0.008551 | 0.0084467 | 0.0083424 | 0.0082381 | 0.0081338 | 0.0080295 | 0.0079252 | 0.007821 | 0.0077167 | 0.0076124 | 0.0075081 | 0.0074038 | 0.0072995 | 0.00027257 | 0.00027259 | 0.00027383 | 0.00027317 | 0.00027165 | 0.00026719 | 0.00026463 | 0.00026144 | 0.00025479 | 0.00025164 | 0.0002485 | 0.00024535 | 0.0002422 | 0.00023906 | 0.00023591 | 0.00023277 | 0.00022962 | 0.00022647 | 0.00022333 | 0.00022018 | 34069.5054 | 6406.3237 | 125.0445 | 23.513 | 2759.6945 | 3577.1744 | 815851.5187 | 2879.9895
| PLD001-160255864 | 46 | PLD001 | PLD | South | 836316.392 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.00027287 | 0.00027615 | 0.00027943 | 0.00028272 | 0.000286 | 0.00027772 | 0.00026944 | 0.00026116 | 0.00025288 | 0.0002446 | 0.00023631 | 0.00022803 | 0.00021975 | 0.00021147 | 0.00020319 | 0.00019491 | 0.00018663 | 0.00017835 | 0.00017007 | 0.00016178 | 8.6235e-06 | 8.6676e-06 | 8.7506e-06 | 8.772e-06 | 8.7648e-06 | 8.4711e-06 | 8.2379e-06 | 7.9847e-06 | 7.6278e-06 | 7.378e-06 | 7.1282e-06 | 6.8784e-06 | 6.6286e-06 | 6.3789e-06 | 6.1291e-06 | 5.8793e-06 | 5.6295e-06 | 5.3797e-06 | 5.1299e-06 | 4.8801e-06 | 34069.5054 | 6406.3237 | 3.6537 | 0.68703 | 112.6686 | 146.0434 | 872771.392 | 117.5798
| PLD001-160255960 | 61 | PLD001 | PLD | South | 1109028.259 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.00018856 | 0.00018954 | 0.00019053 | 0.00019151 | 0.0001925 | 0.00018734 | 0.00018217 | 0.00017701 | 0.00017185 | 0.00016669 | 0.00016152 | 0.00015636 | 0.0001512 | 0.00014604 | 0.00014087 | 0.00013571 | 0.00013055 | 0.00012539 | 0.00012022 | 0.00011506 | 5.959e-06 | 5.9493e-06 | 5.9665e-06 | 5.9422e-06 | 5.8994e-06 | 5.7142e-06 | 5.5699e-06 | 5.412e-06 | 5.1837e-06 | 5.028e-06 | 4.8723e-06 | 4.7165e-06 | 4.5608e-06 | 4.4051e-06 | 4.2494e-06 | 4.0937e-06 | 3.9379e-06 | 3.7822e-06 | 3.6265e-06 | 3.4708e-06 | 34069.5054 | 6406.3237 | 2.5024 | 0.47054 | 106.4267 | 137.9526 | 1157370.759 | 111.0659
| PLD001-160286437 | 57 | PLD001 | PLD | South | 1036305.0945 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.00011647 | 0.00011761 | 0.00011874 | 0.00011987 | 0.000121 | 0.00011845 | 0.0001159 | 0.00011334 | 0.00011079 | 0.00010824 | 0.00010569 | 0.00010314 | 0.00010058 | 9.8032e-05 | 9.548e-05 | 9.2928e-05 | 9.0376e-05 | 8.7824e-05 | 8.5272e-05 | 8.272e-05 | 3.681e-06 | 3.6913e-06 | 3.7183e-06 | 3.7192e-06 | 3.7082e-06 | 3.6129e-06 | 3.5434e-06 | 3.4654e-06 | 3.342e-06 | 3.265e-06 | 3.188e-06 | 3.111e-06 | 3.034e-06 | 2.9571e-06 | 2.8801e-06 | 2.8031e-06 | 2.7261e-06 | 2.6491e-06 | 2.5722e-06 | 2.4952e-06 | 34069.5054 | 6406.3237 | 1.6195 | 0.30452 | 73.1756 | 94.8518 | 1081477.5945 | 76.3654
| PLD001-160286548 | 263 | PLD001 | PLD | South | 4781548.0676 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.040734 | 0.040867 | 0.041 | 0.041133 | 0.041266 | 0.041116 | 0.040967 | 0.040817 | 0.040668 | 0.040518 | 0.040369 | 0.04022 | 0.04007 | 0.039921 | 0.039771 | 0.039622 | 0.039473 | 0.039323 | 0.039174 | 0.039024 | 0.0012873 | 0.0012827 | 0.0012839 | 0.0012763 | 0.0012646 | 0.0012541 | 0.0012525 | 0.001248 | 0.0012267 | 0.0012222 | 0.0012177 | 0.0012132 | 0.0012087 | 0.0012042 | 0.0011997 | 0.0011952 | 0.0011907 | 0.0011862 | 0.0011816 | 0.0011771 | 34069.5054 | 6406.3237 | 608.7248 | 114.4627 | 99822.4685 | 129391.996 | 4989975.5676 | 104173.7261
| PLD001-160286649 | 85 | PLD001 | PLD | South | 1545367.2462 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.028071 | 0.02823 | 0.028389 | 0.028548 | 0.028707 | 0.028086 | 0.027465 | 0.026844 | 0.026223 | 0.025602 | 0.02498 | 0.024359 | 0.023738 | 0.023117 | 0.022496 | 0.021875 | 0.021254 | 0.020633 | 0.020012 | 0.019391 | 0.00088714 | 0.00088607 | 0.00088902 | 0.00088578 | 0.00087977 | 0.00085669 | 0.00083972 | 0.00082073 | 0.00079099 | 0.00077225 | 0.00075352 | 0.00073478 | 0.00071605 | 0.00069731 | 0.00067858 | 0.00065984 | 0.00064111 | 0.00062237 | 0.00060364 | 0.0005849 | 34069.5054 | 6406.3237 | 384.165 | 72.2372 | 16747.2955 | 21708.1989 | 1612729.7462 | 17477.3095
| PLD001-162206790 | 10 | PLD001 | PLD | South | 181807.9113 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34069.5054 | 6406.3237 | 0 | 0 | 0 | 0 | 189732.9113 | 0
| PLD001-162207166 | 9 | PLD001 | PLD | South | 163627.1202 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0001042 | 0.00010503 | 0.00010586 | 0.00010669 | 0.00010752 | 0.00010447 | 0.00010141 | 9.8358e-05 | 9.5304e-05 | 9.225e-05 | 8.9196e-05 | 8.6142e-05 | 8.3088e-05 | 8.0034e-05 | 7.698e-05 | 7.3926e-05 | 7.0872e-05 | 6.7818e-05 | 6.4764e-05 | 6.171e-05 | 3.2931e-06 | 3.2967e-06 | 3.3151e-06 | 3.3104e-06 | 3.2951e-06 | 3.1865e-06 | 3.1006e-06 | 3.0072e-06 | 2.8748e-06 | 2.7826e-06 | 2.6905e-06 | 2.5984e-06 | 2.5063e-06 | 2.4142e-06 | 2.322e-06 | 2.2299e-06 | 2.1378e-06 | 2.0457e-06 | 1.9536e-06 | 1.8614e-06 | 34069.5054 | 6406.3237 | 1.3821 | 0.25989 | 18.0668 | 23.4185 | 170759.6202 | 18.8543
| PLD001-162213349 | 10 | PLD001 | PLD | South | 181807.9113 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34069.5054 | 6406.3237 | 0 | 0 | 0 | 0 | 189732.9113 | 0
| PLD001-162290445 | 24 | PLD001 | PLD | South | 436338.9872 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0089372 | 0.0090108 | 0.0090845 | 0.0091581 | 0.0092317 | 0.0090229 | 0.008814 | 0.0086051 | 0.0083962 | 0.0081874 | 0.0079785 | 0.0077696 | 0.0075608 | 0.0073519 | 0.007143 | 0.0069342 | 0.0067253 | 0.0065164 | 0.0063076 | 0.0060987 | 0.00028245 | 0.00028283 | 0.00028448 | 0.00028415 | 0.00028292 | 0.00027522 | 0.00026948 | 0.0002631 | 0.00025327 | 0.00024697 | 0.00024067 | 0.00023436 | 0.00022806 | 0.00022176 | 0.00021546 | 0.00020916 | 0.00020286 | 0.00019656 | 0.00019026 | 0.00018396 | 34069.5054 | 6406.3237 | 122.6301 | 23.059 | 2138.3178 | 2771.7328 | 455358.9872 | 2231.527
| PLD001-162290662 | 10 | PLD001 | PLD | South | 181807.9113 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.00032784 | 0.00033058 | 0.00033332 | 0.00033606 | 0.0003388 | 0.00033082 | 0.00032284 | 0.00031486 | 0.00030688 | 0.0002989 | 0.00029092 | 0.00028294 | 0.00027496 | 0.00026698 | 0.000259 | 0.00025102 | 0.00024304 | 0.00023506 | 0.00022708 | 0.0002191 | 1.0361e-05 | 1.0376e-05 | 1.0438e-05 | 1.0427e-05 | 1.0383e-05 | 1.0091e-05 | 9.8706e-06 | 9.6266e-06 | 9.2568e-06 | 9.0161e-06 | 8.7754e-06 | 8.5347e-06 | 8.2939e-06 | 8.0532e-06 | 7.8125e-06 | 7.5718e-06 | 7.3311e-06 | 7.0904e-06 | 6.8497e-06 | 6.609e-06 | 34069.5054 | 6406.3237 | 4.4766 | 0.84176 | 111.5048 | 144.5349 | 189732.9113 | 116.3653
| PLD001-162291051 | 27 | PLD001 | PLD | South | 490881.3605 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.00085225 | 0.00085879 | 0.00086533 | 0.00087186 | 0.0008784 | 0.00085696 | 0.00083552 | 0.00081408 | 0.00079264 | 0.0007712 | 0.00074976 | 0.00072832 | 0.00070688 | 0.00068544 | 0.000664 | 0.00064256 | 0.00062112 | 0.00059968 | 0.00057824 | 0.0005568 | 2.6934e-05 | 2.6955e-05 | 2.7098e-05 | 2.7052e-05 | 2.692e-05 | 2.6139e-05 | 2.5545e-05 | 2.489e-05 | 2.3909e-05 | 2.3263e-05 | 2.2616e-05 | 2.1969e-05 | 2.1322e-05 | 2.0676e-05 | 2.0029e-05 | 1.9382e-05 | 1.8736e-05 | 1.8089e-05 | 1.7442e-05 | 1.6795e-05 | 34069.5054 | 6406.3237 | 11.5561 | 2.173 | 339.9884 | 440.7001 | 512278.8605 | 354.8085
| PLD001-162377877 | 18 | PLD001 | PLD | South | 327254.2404 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 3.9207e-05 | 3.9545e-05 | 3.9883e-05 | 4.0222e-05 | 4.056e-05 | 3.9504e-05 | 3.8448e-05 | 3.7392e-05 | 3.6336e-05 | 3.528e-05 | 3.4224e-05 | 3.3168e-05 | 3.2112e-05 | 3.1056e-05 | 3e-05 | 2.8944e-05 | 2.7888e-05 | 2.6832e-05 | 2.5776e-05 | 2.472e-05 | 1.2391e-06 | 1.2412e-06 | 1.249e-06 | 1.248e-06 | 1.243e-06 | 1.205e-06 | 1.1755e-06 | 1.1432e-06 | 1.096e-06 | 1.0642e-06 | 1.0323e-06 | 1.0005e-06 | 9.6863e-07 | 9.3678e-07 | 9.0493e-07 | 8.7307e-07 | 8.4122e-07 | 8.0937e-07 | 7.7751e-07 | 7.4566e-07 | 34069.5054 | 6406.3237 | 0.5283 | 0.09934 | 20.7216 | 26.8598 | 341519.2404 | 21.6249
| PLD001-163864241 | 98 | PLD001 | PLD | South | 1781717.5309 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.008484 | 0.0085536 | 0.0086232 | 0.0086928 | 0.0087624 | 0.0086062 | 0.00845 | 0.0082938 | 0.0081375 | 0.0079813 | 0.0078251 | 0.0076688 | 0.0075126 | 0.0073564 | 0.0072001 | 0.0070439 | 0.0068877 | 0.0067315 | 0.0065752 | 0.006419 | 0.00026812 | 0.00026848 | 0.00027004 | 0.00026972 | 0.00026854 | 0.00026251 | 0.00025835 | 0.00025358 | 0.00024546 | 0.00024075 | 0.00023604 | 0.00023132 | 0.00022661 | 0.0002219 | 0.00021719 | 0.00021247 | 0.00020776 | 0.00020305 | 0.00019834 | 0.00019362 | 34069.5054 | 6406.3237 | 119.5379 | 22.4775 | 5108.6094 | 6621.8876 | 1859382.5309 | 5331.2935
| PLD001-24597198 | 313 | PLD001 | PLD | South | 5690587.6241 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 2.0194 | 2.0318 | 2.0442 | 2.0566 | 2.069 | 2.0295 | 1.9901 | 1.9506 | 1.9112 | 1.8718 | 1.8323 | 1.7929 | 1.7534 | 1.714 | 1.6745 | 1.6351 | 1.5956 | 1.5562 | 1.5167 | 1.4773 | 0.063819 | 0.063772 | 0.064015 | 0.063811 | 0.063407 | 0.061906 | 0.060846 | 0.05964 | 0.05765 | 0.05646 | 0.05527 | 0.05408 | 0.05289 | 0.0517 | 0.050511 | 0.049321 | 0.048131 | 0.046941 | 0.045751 | 0.044561 | 34069.5054 | 6406.3237 | 28075.27 | 5279.1864 | 139260.534 | 180512.4511 | 5938640.1241 | 145330.8955
| PLD001-24611964 | 2 | PLD001 | PLD | South | 36361.5823 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34069.5054 | 6406.3237 | 0 | 0 | 0 | 0 | 37946.5823 | 0
| PLD001-95142888 | 57 | PLD001 | PLD | South | 1036305.0945 | 0.0011352 | 0.0011274 | 0.0011248 | 0.0011145 | 0.0011008 | 0.0010956 | 0.0010982 | 0.0010982 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.0010835 | 0.018994 | 0.019132 | 0.01927 | 0.019408 | 0.019546 | 0.019185 | 0.018824 | 0.018462 | 0.018101 | 0.01774 | 0.017379 | 0.017018 | 0.016657 | 0.016296 | 0.015935 | 0.015574 | 0.015213 | 0.014852 | 0.01449 | 0.014129 | 0.00060028 | 0.0006005 | 0.00060345 | 0.00060218 | 0.000599 | 0.00058518 | 0.00057552 | 0.00056448 | 0.00054601 | 0.00053512 | 0.00052423 | 0.00051334 | 0.00050244 | 0.00049155 | 0.00048066 | 0.00046977 | 0.00045888 | 0.00044799 | 0.00043709 | 0.0004262 | 34069.5054 | 6406.3237 | 265.8795 | 49.9951 | 4720.3525 | 6118.6207 | 1081477.5945 | 4926.1124
| PLD002-15398648 | 0 | PLD002 | PLD | South | 0 | 0.039062 | 0.038438 | 0.038031 | 0.037406 | 0.036687 | 0.036375 | 0.036062 | 0.035656 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34069.5054 | 6406.3237 | 0 | 0 | 0 | 0 | 0 | 0
| PLD002-15398661 | 36 | PLD002 | PLD | South | 654508.4807 | 0.039062 | 0.038438 | 0.038031 | 0.037406 | 0.036687 | 0.036375 | 0.036062 | 0.035656 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.03525 | 0.026565 | 0.026861 | 0.027157 | 0.027454 | 0.02775 | 0.027014 | 0.026278 | 0.025542 | 0.024806 | 0.024071 | 0.023335 | 0.022599 | 0.021863 | 0.021127 | 0.020391 | 0.019655 | 0.018919 | 0.018183 | 0.017447 | 0.016711 | 0.028889 | 0.028744 | 0.028754 | 0.02859 | 0.028343 | 0.027357 | 0.026383 | 0.025355 | 0.024344 | 0.023622 | 0.0229 | 0.022177 | 0.021455 | 0.020733 | 0.020011 | 0.019289 | 0.018567 | 0.017844 | 0.017122 | 0.0164 | 34069.5054 | 6406.3237 | 11901.4088 | 2237.9039 | 14112.0995 | 18292.402 | 683038.4807 | 14727.2454
| PLD003-110224899 | 12 | PLD003 | PLD | South | 218169.4936 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 1.5637e-05 | 1.5845e-05 | 1.6053e-05 | 1.6262e-05 | 1.647e-05 | 1.5891e-05 | 1.5312e-05 | 1.4733e-05 | 1.4153e-05 | 1.3574e-05 | 1.2995e-05 | 1.2416e-05 | 1.1837e-05 | 1.1258e-05 | 1.0678e-05 | 1.0099e-05 | 9.5202e-06 | 8.941e-06 | 8.3619e-06 | 7.7827e-06 | 4.4296e-07 | 4.4688e-07 | 4.5476e-07 | 4.5659e-07 | 4.5626e-07 | 4.4022e-07 | 4.2609e-07 | 4.1181e-07 | 3.8801e-07 | 3.7213e-07 | 3.5626e-07 | 3.4038e-07 | 3.245e-07 | 3.0863e-07 | 2.9275e-07 | 2.7687e-07 | 2.6099e-07 | 2.4512e-07 | 2.2924e-07 | 2.1336e-07 | 34069.5054 | 6406.3237 | 0.18361 | 0.034525 | 4.7053 | 6.0991 | 227679.4936 | 4.9104
| PLD003-147733185 | 66 | PLD003 | PLD | South | 1199932.2147 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.42175 | 0.42518 | 0.42861 | 0.43204 | 0.43547 | 0.4259 | 0.41633 | 0.40676 | 0.39719 | 0.38762 | 0.37805 | 0.36848 | 0.35892 | 0.34935 | 0.33978 | 0.33021 | 0.32064 | 0.31107 | 0.3015 | 0.29193 | 0.011947 | 0.011991 | 0.012141 | 0.012131 | 0.012064 | 0.011798 | 0.011585 | 0.01137 | 0.010889 | 0.010627 | 0.010364 | 0.010102 | 0.0098396 | 0.0095772 | 0.0093149 | 0.0090526 | 0.0087902 | 0.0085279 | 0.0082656 | 0.0080032 | 34069.5054 | 6406.3237 | 5263.5974 | 989.7505 | 15449.1284 | 20025.4871 | 1252237.2147 | 16122.5553
| PLD003-15398748 | 90 | PLD003 | PLD | South | 1636271.2018 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.5316 | 0.53759 | 0.54359 | 0.54958 | 0.55558 | 0.54044 | 0.52531 | 0.51018 | 0.49505 | 0.47992 | 0.46479 | 0.44966 | 0.43452 | 0.41939 | 0.40426 | 0.38913 | 0.374 | 0.35887 | 0.34374 | 0.3286 | 0.015059 | 0.015162 | 0.015399 | 0.015431 | 0.015391 | 0.014972 | 0.014618 | 0.014261 | 0.013572 | 0.013157 | 0.012742 | 0.012327 | 0.011912 | 0.011498 | 0.011083 | 0.010668 | 0.010253 | 0.0098383 | 0.0094234 | 0.0090086 | 34069.5054 | 6406.3237 | 6502.0919 | 1222.6331 | 18148.6869 | 23524.712 | 1707596.2018 | 18939.7874
| PLD003-160436494 | 37 | PLD003 | PLD | South | 672689.2719 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 5.6767e-05 | 5.7347e-05 | 5.7928e-05 | 5.8509e-05 | 5.909e-05 | 5.7257e-05 | 5.5423e-05 | 5.359e-05 | 5.1756e-05 | 4.9923e-05 | 4.8089e-05 | 4.6256e-05 | 4.4422e-05 | 4.2589e-05 | 4.0755e-05 | 3.8922e-05 | 3.7088e-05 | 3.5255e-05 | 3.3421e-05 | 3.1588e-05 | 1.6081e-06 | 1.6174e-06 | 1.641e-06 | 1.6428e-06 | 1.6369e-06 | 1.5861e-06 | 1.5423e-06 | 1.498e-06 | 1.4189e-06 | 1.3686e-06 | 1.3183e-06 | 1.2681e-06 | 1.2178e-06 | 1.1676e-06 | 1.1173e-06 | 1.067e-06 | 1.0168e-06 | 9.6649e-07 | 9.1623e-07 | 8.6596e-07 | 34069.5054 | 6406.3237 | 0.67685 | 0.12727 | 25.3398 | 32.8459 | 702011.7719 | 26.4443
| PLD003-160436674 | 111 | PLD003 | PLD | South | 2018067.8156 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.077075 | 0.077827 | 0.078578 | 0.07933 | 0.080082 | 0.078529 | 0.076977 | 0.075425 | 0.073872 | 0.07232 | 0.070768 | 0.069215 | 0.067663 | 0.066111 | 0.064558 | 0.063006 | 0.061454 | 0.059901 | 0.058349 | 0.056797 | 0.0021834 | 0.0021949 | 0.002226 | 0.0022274 | 0.0022185 | 0.0021754 | 0.0021421 | 0.0021083 | 0.0020252 | 0.0019826 | 0.0019401 | 0.0018975 | 0.001855 | 0.0018124 | 0.0017699 | 0.0017273 | 0.0016847 | 0.0016422 | 0.0015996 | 0.0015571 | 34069.5054 | 6406.3237 | 980.9422 | 184.4533 | 77585.739 | 100568.2767 | 2106035.3156 | 80967.6984
| PLD003-160451735 | 51 | PLD003 | PLD | South | 927220.3477 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.074015 | 0.074801 | 0.075587 | 0.076372 | 0.077158 | 0.075243 | 0.073329 | 0.071414 | 0.0695 | 0.067585 | 0.065671 | 0.063756 | 0.061842 | 0.059927 | 0.058013 | 0.056098 | 0.054184 | 0.052269 | 0.050355 | 0.04844 | 0.0020967 | 0.0021096 | 0.0021412 | 0.0021444 | 0.0021375 | 0.0020844 | 0.0020406 | 0.0019962 | 0.0019053 | 0.0018528 | 0.0018004 | 0.0017479 | 0.0016954 | 0.0016429 | 0.0015904 | 0.0015379 | 0.0014854 | 0.001433 | 0.0013805 | 0.001328 | 34069.5054 | 6406.3237 | 916.1266 | 172.2656 | 17619.5864 | 22838.8808 | 967637.8477 | 18387.6235
| PLD003-160519395 | 54 | PLD003 | PLD | South | 981762.7211 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.029157 | 0.029448 | 0.02974 | 0.030031 | 0.030322 | 0.029625 | 0.028928 | 0.02823 | 0.027533 | 0.026836 | 0.026139 | 0.025442 | 0.024744 | 0.024047 | 0.02335 | 0.022653 | 0.021955 | 0.021258 | 0.020561 | 0.019864 | 0.00082595 | 0.00083052 | 0.00084245 | 0.00084319 | 0.00084 | 0.00082068 | 0.00080498 | 0.00078911 | 0.00075482 | 0.0007357 | 0.00071659 | 0.00069747 | 0.00067836 | 0.00065924 | 0.00064013 | 0.00062102 | 0.0006019 | 0.00058279 | 0.00056367 | 0.00054456 | 34069.5054 | 6406.3237 | 363.9309 | 68.4324 | 47250.7353 | 61247.4029 | 1024557.7211 | 49310.393
| PLD003-160519570 | 84 | PLD003 | PLD | South | 1527186.455 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.045224 | 0.045733 | 0.046241 | 0.04675 | 0.047259 | 0.046133 | 0.045007 | 0.043881 | 0.042755 | 0.041629 | 0.040503 | 0.039377 | 0.038251 | 0.037125 | 0.036 | 0.034874 | 0.033748 | 0.032622 | 0.031496 | 0.03037 | 0.0012811 | 0.0012898 | 0.0013099 | 0.0013126 | 0.0013092 | 0.001278 | 0.0012524 | 0.0012266 | 0.0011721 | 0.0011413 | 0.0011104 | 0.0010795 | 0.0010487 | 0.0010178 | 0.00098692 | 0.00095605 | 0.00092519 | 0.00089432 | 0.00086345 | 0.00083258 | 34069.5054 | 6406.3237 | 564.0421 | 106.0607 | 60753.3501 | 78749.778 | 1593756.455 | 63401.5863
| PLD003-160519700 | 97 | PLD003 | PLD | South | 1763536.7398 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.0048157 | 0.0048523 | 0.0048888 | 0.0049253 | 0.0049619 | 0.0048596 | 0.0047573 | 0.004655 | 0.0045527 | 0.0044504 | 0.0043481 | 0.0042458 | 0.0041435 | 0.0040412 | 0.0039389 | 0.0038366 | 0.0037344 | 0.0036321 | 0.0035298 | 0.0034275 | 0.00013642 | 0.00013685 | 0.00013849 | 0.00013829 | 0.00013746 | 0.00013462 | 0.00013238 | 0.00013012 | 0.00012481 | 0.00012201 | 0.0001192 | 0.0001164 | 0.00011359 | 0.00011079 | 0.00010799 | 0.00010518 | 0.00010238 | 9.9572e-05 | 9.6768e-05 | 9.3963e-05 | 34069.5054 | 6406.3237 | 60.4563 | 11.368 | 3760.3418 | 4874.2346 | 1840409.2398 | 3924.2549
| PLD003-160519896 | 57 | PLD003 | PLD | South | 1036305.0945 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.014146 | 0.014274 | 0.014402 | 0.014531 | 0.014659 | 0.014258 | 0.013858 | 0.013457 | 0.013056 | 0.012655 | 0.012255 | 0.011854 | 0.011453 | 0.011053 | 0.010652 | 0.010251 | 0.0098505 | 0.0094498 | 0.0090491 | 0.0086484 | 0.00040071 | 0.00040256 | 0.00040799 | 0.00040799 | 0.00040609 | 0.00039499 | 0.00038562 | 0.00037615 | 0.00035793 | 0.00034695 | 0.00033596 | 0.00032498 | 0.00031399 | 0.00030301 | 0.00029202 | 0.00028104 | 0.00027005 | 0.00025906 | 0.00024808 | 0.00023709 | 34069.5054 | 6406.3237 | 171.7332 | 32.2922 | 7239.6439 | 9384.1796 | 1081477.5945 | 7555.2197
| PLD003-160520056 | 46 | PLD003 | PLD | South | 836316.392 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.0010978 | 0.0011085 | 0.0011192 | 0.00113 | 0.0011407 | 0.0011059 | 0.001071 | 0.0010362 | 0.0010013 | 0.00096645 | 0.0009316 | 0.00089675 | 0.0008619 | 0.00082705 | 0.0007922 | 0.00075735 | 0.0007225 | 0.00068765 | 0.0006528 | 0.00061795 | 3.1097e-05 | 3.1263e-05 | 3.1705e-05 | 3.1727e-05 | 3.16e-05 | 3.0635e-05 | 2.9803e-05 | 2.8963e-05 | 2.745e-05 | 2.6495e-05 | 2.554e-05 | 2.4584e-05 | 2.3629e-05 | 2.2673e-05 | 2.1718e-05 | 2.0763e-05 | 1.9807e-05 | 1.8852e-05 | 1.7896e-05 | 1.6941e-05 | 34069.5054 | 6406.3237 | 13.1076 | 2.4647 | 681.8751 | 883.8609 | 872771.392 | 711.598
| PLD003-160574293 | 114 | PLD003 | PLD | South | 2072610.189 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.12767 | 0.12888 | 0.1301 | 0.13131 | 0.13252 | 0.13017 | 0.12783 | 0.12548 | 0.12313 | 0.12078 | 0.11843 | 0.11609 | 0.11374 | 0.11139 | 0.10904 | 0.10669 | 0.10434 | 0.102 | 0.099649 | 0.0973 | 0.0036166 | 0.0036349 | 0.0036854 | 0.0036869 | 0.0036712 | 0.0036061 | 0.0035571 | 0.0035074 | 0.0033756 | 0.0033112 | 0.0032468 | 0.0031825 | 0.0031181 | 0.0030537 | 0.0029893 | 0.002925 | 0.0028606 | 0.0027962 | 0.0027318 | 0.0026675 | 34069.5054 | 6406.3237 | 1638.5738 | 308.1123 | 105709.0685 | 137022.3316 | 2162955.189 | 110316.9228
| PLD003-160574380 | 50 | PLD003 | PLD | South | 909039.5566 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.0019113 | 0.0019252 | 0.001939 | 0.0019528 | 0.0019666 | 0.0019389 | 0.0019112 | 0.0018836 | 0.0018559 | 0.0018282 | 0.0018005 | 0.0017728 | 0.0017452 | 0.0017175 | 0.0016898 | 0.0016621 | 0.0016344 | 0.0016068 | 0.0015791 | 0.0015514 | 5.4144e-05 | 5.4295e-05 | 5.4927e-05 | 5.4829e-05 | 5.4479e-05 | 5.3713e-05 | 5.3185e-05 | 5.265e-05 | 5.0878e-05 | 5.0119e-05 | 4.9361e-05 | 4.8602e-05 | 4.7843e-05 | 4.7084e-05 | 4.6325e-05 | 4.5567e-05 | 4.4808e-05 | 4.4049e-05 | 4.329e-05 | 4.2531e-05 | 34069.5054 | 6406.3237 | 24.8408 | 4.671 | 1327.886 | 1721.234 | 948664.5566 | 1385.7685
| PLD003-160574486 | 40 | PLD003 | PLD | South | 727231.6453 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.021203 | 0.021423 | 0.021643 | 0.021863 | 0.022082 | 0.021675 | 0.021268 | 0.020861 | 0.020454 | 0.020047 | 0.01964 | 0.019233 | 0.018826 | 0.018419 | 0.018012 | 0.017605 | 0.017198 | 0.016791 | 0.016384 | 0.015977 | 0.00060064 | 0.00060419 | 0.00061309 | 0.00061385 | 0.00061174 | 0.00060046 | 0.00059185 | 0.00058313 | 0.00056075 | 0.0005496 | 0.00053844 | 0.00052728 | 0.00051612 | 0.00050496 | 0.0004938 | 0.00048265 | 0.00047149 | 0.00046033 | 0.00044917 | 0.00043801 | 34069.5054 | 6406.3237 | 271.8082 | 51.11 | 16091.1199 | 20857.6501 | 758931.6453 | 16792.5312
| PLD003-160574588 | 58 | PLD003 | PLD | South | 1054485.8856 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.029054 | 0.029302 | 0.02955 | 0.029797 | 0.030045 | 0.029274 | 0.028503 | 0.027732 | 0.026961 | 0.026191 | 0.02542 | 0.024649 | 0.023878 | 0.023107 | 0.022336 | 0.021565 | 0.020794 | 0.020023 | 0.019252 | 0.018481 | 0.00082303 | 0.00082639 | 0.00083707 | 0.00083664 | 0.00083232 | 0.00081097 | 0.00079318 | 0.00077519 | 0.00073914 | 0.00071801 | 0.00069687 | 0.00067574 | 0.0006546 | 0.00063347 | 0.00061233 | 0.0005912 | 0.00057007 | 0.00054893 | 0.0005278 | 0.00050666 | 34069.5054 | 6406.3237 | 355.5445 | 66.8555 | 9442.298 | 12239.3065 | 1100450.8856 | 9853.8875
| PLD003-162199489 | 13 | PLD003 | PLD | South | 236350.2847 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34069.5054 | 6406.3237 | 0 | 0 | 0 | 0 | 246652.7847 | 0
| PLD003-162199732 | 15 | PLD003 | PLD | South | 272711.867 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34069.5054 | 6406.3237 | 0 | 0 | 0 | 0 | 284599.367 | 0
| PLD003-162199939 | 21 | PLD003 | PLD | South | 381796.6138 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00091829 | 0.00092677 | 0.00093525 | 0.00094372 | 0.0009522 | 0.00092598 | 0.00089976 | 0.00087354 | 0.00084732 | 0.0008211 | 0.00079488 | 0.00076866 | 0.00074244 | 0.00071622 | 0.00069 | 0.00066378 | 0.00063756 | 0.00061134 | 0.00058512 | 0.0005589 | 2.6013e-05 | 2.6137e-05 | 2.6493e-05 | 2.6497e-05 | 2.6378e-05 | 2.5652e-05 | 2.5038e-05 | 2.4418e-05 | 2.3229e-05 | 2.251e-05 | 2.1791e-05 | 2.1073e-05 | 2.0354e-05 | 1.9635e-05 | 1.8916e-05 | 1.8197e-05 | 1.7479e-05 | 1.676e-05 | 1.6041e-05 | 1.5322e-05 | 34069.5054 | 6406.3237 | 11.1409 | 2.0949 | 195.6003 | 253.5412 | 398439.1138 | 204.1265
| PLD003-162260412 | 13 | PLD003 | PLD | South | 236350.2847 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00049872 | 0.00050424 | 0.00050976 | 0.00051528 | 0.0005208 | 0.0005088 | 0.0004968 | 0.0004848 | 0.0004728 | 0.0004608 | 0.0004488 | 0.0004368 | 0.0004248 | 0.0004128 | 0.0004008 | 0.0003888 | 0.0003768 | 0.0003648 | 0.0003528 | 0.0003408 | 1.4128e-05 | 1.4221e-05 | 1.444e-05 | 1.4468e-05 | 1.4427e-05 | 1.4095e-05 | 1.3825e-05 | 1.3551e-05 | 1.2962e-05 | 1.2633e-05 | 1.2304e-05 | 1.1975e-05 | 1.1646e-05 | 1.1317e-05 | 1.0988e-05 | 1.0659e-05 | 1.033e-05 | 1.0001e-05 | 9.6719e-06 | 9.343e-06 | 34069.5054 | 6406.3237 | 6.2443 | 1.1742 | 260.2363 | 337.3238 | 246652.7847 | 271.58
| PLD003-162378154 | 7 | PLD003 | PLD | South | 127265.5379 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00071362 | 0.0007203 | 0.00072699 | 0.00073367 | 0.00074036 | 0.00071888 | 0.0006974 | 0.00067592 | 0.00065445 | 0.00063297 | 0.00061149 | 0.00059001 | 0.00056853 | 0.00054706 | 0.00052558 | 0.0005041 | 0.00048262 | 0.00046115 | 0.00043967 | 0.00041819 | 2.0215e-05 | 2.0315e-05 | 2.0594e-05 | 2.06e-05 | 2.051e-05 | 1.9915e-05 | 1.9407e-05 | 1.8894e-05 | 1.7941e-05 | 1.7353e-05 | 1.6764e-05 | 1.6175e-05 | 1.5586e-05 | 1.4997e-05 | 1.4409e-05 | 1.382e-05 | 1.3231e-05 | 1.2642e-05 | 1.2053e-05 | 1.1465e-05 | 34069.5054 | 6406.3237 | 8.5874 | 1.6147 | 192.6298 | 249.6908 | 132813.0379 | 201.0265
| PLD003-162378402 | 22 | PLD003 | PLD | South | 399977.4049 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.0013652 | 0.0013773 | 0.0013894 | 0.0014015 | 0.0014136 | 0.0013788 | 0.001344 | 0.0013093 | 0.0012745 | 0.0012397 | 0.0012049 | 0.0011701 | 0.0011354 | 0.0011006 | 0.0010658 | 0.001031 | 0.00099624 | 0.00096146 | 0.00092668 | 0.0008919 | 3.8673e-05 | 3.8844e-05 | 3.9359e-05 | 3.9351e-05 | 3.916e-05 | 3.8197e-05 | 3.7402e-05 | 3.6597e-05 | 3.494e-05 | 3.3986e-05 | 3.3033e-05 | 3.2079e-05 | 3.1126e-05 | 3.0172e-05 | 2.9219e-05 | 2.8265e-05 | 2.7312e-05 | 2.6358e-05 | 2.5405e-05 | 2.4451e-05 | 34069.5054 | 6406.3237 | 16.8254 | 3.1638 | 711.9068 | 922.7886 | 417412.4049 | 742.9388
| PLD003-163610230 | 24 | PLD003 | PLD | South | 436338.9872 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 3.7706e-06 | 3.8254e-06 | 3.8803e-06 | 3.9351e-06 | 3.99e-06 | 3.8455e-06 | 3.7009e-06 | 3.5564e-06 | 3.4119e-06 | 3.2674e-06 | 3.1229e-06 | 2.9783e-06 | 2.8338e-06 | 2.6893e-06 | 2.5448e-06 | 2.4002e-06 | 2.2557e-06 | 2.1112e-06 | 1.9667e-06 | 1.8221e-06 | 1.0681e-07 | 1.0789e-07 | 1.0992e-07 | 1.1049e-07 | 1.1053e-07 | 1.0653e-07 | 1.0299e-07 | 9.9411e-08 | 9.3536e-08 | 8.9574e-08 | 8.5612e-08 | 8.165e-08 | 7.7688e-08 | 7.3726e-08 | 6.9764e-08 | 6.5802e-08 | 6.184e-08 | 5.7877e-08 | 5.3915e-08 | 4.9953e-08 | 34069.5054 | 6406.3237 | 0.044154 | 0.0083025 | 1.3577 | 1.7599 | 455358.9872 | 1.4169
| PLD003-163610492 | 19 | PLD003 | PLD | South | 345435.0315 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.013381 | 0.013511 | 0.013641 | 0.013771 | 0.013901 | 0.013631 | 0.01336 | 0.013089 | 0.012818 | 0.012547 | 0.012276 | 0.012005 | 0.011734 | 0.011463 | 0.011192 | 0.010921 | 0.01065 | 0.01038 | 0.010109 | 0.0098377 | 0.00037904 | 0.00038104 | 0.00038642 | 0.00038666 | 0.0003851 | 0.0003776 | 0.00037176 | 0.00036586 | 0.0003514 | 0.00034397 | 0.00033654 | 0.00032912 | 0.00032169 | 0.00031426 | 0.00030683 | 0.00029941 | 0.00029198 | 0.00028455 | 0.00027713 | 0.0002697 | 34069.5054 | 6406.3237 | 170.1871 | 32.0015 | 7776.1901 | 10079.6622 | 360492.5315 | 8115.1539
| PLD003-24597170 | 262 | PLD003 | PLD | South | 4763367.2764 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.40494 | 0.40851 | 0.41209 | 0.41566 | 0.41924 | 0.4093 | 0.39935 | 0.38941 | 0.37946 | 0.36952 | 0.35957 | 0.34963 | 0.33968 | 0.32974 | 0.3198 | 0.30985 | 0.29991 | 0.28996 | 0.28002 | 0.27007 | 0.011471 | 0.011521 | 0.011674 | 0.011671 | 0.011614 | 0.011338 | 0.011113 | 0.010885 | 0.010403 | 0.01013 | 0.0098576 | 0.009585 | 0.0093124 | 0.0090398 | 0.0087671 | 0.0084945 | 0.0082219 | 0.0079493 | 0.0076766 | 0.007404 | 34069.5054 | 6406.3237 | 5015.2564 | 943.0532 | 88442.4809 | 114641.0153 | 4971002.2764 | 92297.6853
| PLD003-24597184 | 551 | PLD003 | PLD | South | 10017615.9134 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 7.4278 | 7.4828 | 7.5378 | 7.5928 | 7.6478 | 7.5372 | 7.4267 | 7.3161 | 7.2055 | 7.095 | 6.9844 | 6.8738 | 6.7633 | 6.6527 | 6.5422 | 6.4316 | 6.321 | 6.2105 | 6.0999 | 5.9893 | 0.21041 | 0.21103 | 0.21353 | 0.21319 | 0.21186 | 0.2088 | 0.20667 | 0.2045 | 0.19754 | 0.19451 | 0.19148 | 0.18844 | 0.18541 | 0.18238 | 0.17935 | 0.17632 | 0.17329 | 0.17026 | 0.16723 | 0.1642 | 34069.5054 | 6406.3237 | 96391.9748 | 18125.2469 | 2071818.7784 | 2685535.3428 | 10454283.4134 | 2162129.2809
| PLD003-24605460 | 96 | PLD003 | PLD | South | 1745355.9486 | 0.0010175 | 0.001013 | 0.0010175 | 0.0010085 | 0.00099506 | 0.00099506 | 0.00099955 | 0.001004 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.00098473 | 0.50618 | 0.51084 | 0.5155 | 0.52015 | 0.52481 | 0.51465 | 0.50448 | 0.49432 | 0.48415 | 0.47399 | 0.46382 | 0.45366 | 0.44349 | 0.43333 | 0.42317 | 0.413 | 0.40284 | 0.39267 | 0.38251 | 0.37234 | 0.014339 | 0.014407 | 0.014603 | 0.014605 | 0.014539 | 0.014257 | 0.014038 | 0.013817 | 0.013273 | 0.012994 | 0.012716 | 0.012437 | 0.012158 | 0.01188 | 0.011601 | 0.011322 | 0.011044 | 0.010765 | 0.010486 | 0.010208 | 34069.5054 | 6406.3237 | 6431.5901 | 1209.3762 | 18777.9479 | 24340.3734 | 1821435.9486 | 19596.4779
| PLD004-121146862 | 179 | PLD004 | PLD | South | 3254361.6125 | 0.0010788 | 0.0010812 | 0.0010892 | 0.0010957 | 0.0010999 | 0.0011103 | 0.0011282 | 0.0011409 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 3.3178 | 3.3483 | 3.3787 | 3.4091 | 3.4395 | 3.3737 | 3.3079 | 3.2421 | 3.1763 | 3.1105 | 3.0447 | 2.9789 | 2.9131 | 2.8473 | 2.7815 | 2.7157 | 2.65 | 2.5842 | 2.5184 | 2.4526 | 0.099648 | 0.10079 | 0.10246 | 0.10399 | 0.10532 | 0.10428 | 0.1039 | 0.10298 | 0.1012 | 0.099102 | 0.097005 | 0.094909 | 0.092813 | 0.090716 | 0.08862 | 0.086524 | 0.084428 | 0.082331 | 0.080235 | 0.078139 | 34069.5054 | 6406.3237 | 47522.8907 | 8936.0564 | 164429.2486 | 213136.6715 | 3396219.1125 | 171596.7133
| PLD004-15398624 | 130 | PLD004 | PLD | South | 2363502.8471 | 0.0010788 | 0.0010812 | 0.0010892 | 0.0010957 | 0.0010999 | 0.0011103 | 0.0011282 | 0.0011409 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 3.4688 | 3.5027 | 3.5365 | 3.5703 | 3.6041 | 3.5253 | 3.4464 | 3.3676 | 3.2888 | 3.2099 | 3.1311 | 3.0522 | 2.9734 | 2.8946 | 2.8157 | 2.7369 | 2.6581 | 2.5792 | 2.5004 | 2.4215 | 0.10418 | 0.10544 | 0.10724 | 0.10891 | 0.11036 | 0.10897 | 0.10825 | 0.10697 | 0.10478 | 0.10227 | 0.099757 | 0.097245 | 0.094733 | 0.092221 | 0.089709 | 0.087198 | 0.084686 | 0.082174 | 0.079662 | 0.07715 | 34069.5054 | 6406.3237 | 48998.9747 | 9213.6147 | 42782.5568 | 55455.6554 | 2466527.8471 | 44647.4468
| PLD004-72962767 | 116 | PLD004 | PLD | South | 2108971.7712 | 0.0010788 | 0.0010812 | 0.0010892 | 0.0010957 | 0.0010999 | 0.0011103 | 0.0011282 | 0.0011409 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0.0011444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34069.5054 | 6406.3237 | 0 | 0 | 0 | 0 | 2200901.7712 | 0
| PLD005-15398737 | 95 | PLD005 | PLD | South | 1727175.1575 | 0.0072092 | 0.0071232 | 0.0070372 | 0.006914 | 0.0067908 | 0.0067049 | 0.0066676 | 0.0066017 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.68351 | 0.69031 | 0.6971 | 0.7039 | 0.7107 | 0.69487 | 0.67904 | 0.66321 | 0.64739 | 0.63156 | 0.61573 | 0.5999 | 0.58407 | 0.56824 | 0.55241 | 0.53659 | 0.52076 | 0.50493 | 0.4891 | 0.47327 | 0.13718 | 0.13689 | 0.13657 | 0.13549 | 0.13436 | 0.12971 | 0.12605 | 0.12189 | 0.11743 | 0.11456 | 0.11169 | 0.10882 | 0.10595 | 0.10308 | 0.10021 | 0.097336 | 0.094465 | 0.091593 | 0.088722 | 0.085851 | 34069.5054 | 6406.3237 | 57758.1589 | 10860.6644 | 89951.7354 | 116597.343 | 1802462.6575 | 93872.7282
| PLD005-15398783 | 0 | PLD005 | PLD | South | 0 | 0.0072092 | 0.0071232 | 0.0070372 | 0.006914 | 0.0067908 | 0.0067049 | 0.0066676 | 0.0066017 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 0.0065158 | 2.0026e-06 | 2.0294e-06 | 2.0563e-06 | 2.0831e-06 | 2.11e-06 | 2.0358e-06 | 1.9615e-06 | 1.8873e-06 | 1.813e-06 | 1.7388e-06 | 1.6645e-06 | 1.5903e-06 | 1.516e-06 | 1.4418e-06 | 1.3675e-06 | 1.2933e-06 | 1.219e-06 | 1.1448e-06 | 1.0705e-06 | 9.9625e-07 | 4.0192e-07 | 4.0246e-07 | 4.0286e-07 | 4.0098e-07 | 3.9891e-07 | 3.8e-07 | 3.6411e-07 | 3.4686e-07 | 3.2888e-07 | 3.1541e-07 | 3.0194e-07 | 2.8847e-07 | 2.75e-07 | 2.6153e-07 | 2.4806e-07 | 2.3459e-07 | 2.2113e-07 | 2.0766e-07 | 1.9419e-07 | 1.8072e-07 | 34069.5054 | 6406.3237 | 0 | 0 | 0 | 0 | 0 | 0
| PLD006-15398587 | 126 | PLD006 | PLD | South | 2290779.6826 | 0.00073455 | 0.00074186 | 0.00075457 | 0.00076479 | 0.000774 | 0.00078714 | 0.00080511 | 0.00081826 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 6.9038 | 6.9674 | 7.0309 | 7.0945 | 7.1581 | 7.0144 | 6.8706 | 6.7269 | 6.5832 | 6.4394 | 6.2957 | 6.152 | 6.0083 | 5.8645 | 5.7208 | 5.5771 | 5.4334 | 5.2896 | 5.1459 | 5.0022 | 0.14118 | 0.1439 | 0.1477 | 0.15106 | 0.15424 | 0.15371 | 0.154 | 0.15324 | 0.15131 | 0.148 | 0.1447 | 0.1414 | 0.13809 | 0.13479 | 0.13149 | 0.12818 | 0.12488 | 0.12158 | 0.11827 | 0.11497 | 34069.5054 | 6406.3237 | 69836.0449 | 13131.7525 | 146208.5792 | 189518.6543 | 2390634.6826 | 152581.8057
| PLD006-161891725 | 36 | PLD006 | PLD | South | 654508.4807 | 0.00073455 | 0.00074186 | 0.00075457 | 0.00076479 | 0.000774 | 0.00078714 | 0.00080511 | 0.00081826 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.023666 | 0.02394 | 0.024215 | 0.024489 | 0.024764 | 0.024065 | 0.023366 | 0.022667 | 0.021968 | 0.021269 | 0.020571 | 0.019872 | 0.019173 | 0.018474 | 0.017775 | 0.017076 | 0.016378 | 0.015679 | 0.01498 | 0.014281 | 0.00048396 | 0.00049444 | 0.00050868 | 0.00052142 | 0.00053361 | 0.00052736 | 0.00052373 | 0.00051637 | 0.00050491 | 0.00048885 | 0.00047279 | 0.00045673 | 0.00044067 | 0.0004246 | 0.00040854 | 0.00039248 | 0.00037642 | 0.00036036 | 0.0003443 | 0.00032823 | 34069.5054 | 6406.3237 | 229.7857 | 43.2082 | 5865.5555 | 7603.0572 | 683038.4807 | 6121.2348
| PLD006-161892052 | 13 | PLD006 | PLD | South | 236350.2847 | 0.00073455 | 0.00074186 | 0.00075457 | 0.00076479 | 0.000774 | 0.00078714 | 0.00080511 | 0.00081826 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34069.5054 | 6406.3237 | 0 | 0 | 0 | 0 | 246652.7847 | 0
| PLD006-162198254 | 17 | PLD006 | PLD | South | 309073.4492 | 0.00073455 | 0.00074186 | 0.00075457 | 0.00076479 | 0.000774 | 0.00078714 | 0.00080511 | 0.00081826 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 3.253e-08 | 3.2948e-08 | 3.3365e-08 | 3.3783e-08 | 3.42e-08 | 3.2979e-08 | 3.1758e-08 | 3.0537e-08 | 2.9316e-08 | 2.8095e-08 | 2.6874e-08 | 2.5653e-08 | 2.4432e-08 | 2.3211e-08 | 2.199e-08 | 2.0769e-08 | 1.9548e-08 | 1.8327e-08 | 1.7106e-08 | 1.5885e-08 | 6.6524e-10 | 6.8048e-10 | 7.009e-10 | 7.1929e-10 | 7.3694e-10 | 7.227e-10 | 7.1183e-10 | 6.9565e-10 | 6.7379e-10 | 6.4573e-10 | 6.1767e-10 | 5.896e-10 | 5.6154e-10 | 5.3348e-10 | 5.0541e-10 | 4.7735e-10 | 4.4929e-10 | 4.2122e-10 | 3.9316e-10 | 3.651e-10 | 34069.5054 | 6406.3237 | 0.00030256 | 5.6893e-05 | 0.041402 | 0.053666 | 322545.9492 | 0.043207
| PLD006-162198466 | 17 | PLD006 | PLD | South | 309073.4492 | 0.00073455 | 0.00074186 | 0.00075457 | 0.00076479 | 0.000774 | 0.00078714 | 0.00080511 | 0.00081826 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.0039933 | 0.0040107 | 0.0040282 | 0.0040457 | 0.0040632 | 0.0040437 | 0.0040243 | 0.0040048 | 0.0039853 | 0.0039659 | 0.0039464 | 0.0039269 | 0.0039074 | 0.003888 | 0.0038685 | 0.003849 | 0.0038296 | 0.0038101 | 0.0037906 | 0.0037712 | 8.1662e-05 | 8.2835e-05 | 8.4621e-05 | 8.6141e-05 | 8.7554e-05 | 8.8615e-05 | 9.0201e-05 | 9.1231e-05 | 9.1598e-05 | 9.115e-05 | 9.0703e-05 | 9.0255e-05 | 8.9808e-05 | 8.936e-05 | 8.8913e-05 | 8.8465e-05 | 8.8018e-05 | 8.757e-05 | 8.7123e-05 | 8.6675e-05 | 34069.5054 | 6406.3237 | 43.2935 | 8.1408 | 1766.9655 | 2290.3781 | 322545.9492 | 1843.9875
| PLD006-162198656 | 29 | PLD006 | PLD | South | 527242.9428 | 0.00073455 | 0.00074186 | 0.00075457 | 0.00076479 | 0.000774 | 0.00078714 | 0.00080511 | 0.00081826 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.015927 | 0.016106 | 0.016285 | 0.016464 | 0.016643 | 0.016226 | 0.01581 | 0.015393 | 0.014976 | 0.014559 | 0.014142 | 0.013725 | 0.013309 | 0.012892 | 0.012475 | 0.012058 | 0.011641 | 0.011224 | 0.010808 | 0.010391 | 0.00032571 | 0.00033264 | 0.0003421 | 0.00035055 | 0.00035863 | 0.00035559 | 0.00035436 | 0.00035065 | 0.0003442 | 0.00033462 | 0.00032504 | 0.00031546 | 0.00030588 | 0.0002963 | 0.00028672 | 0.00027714 | 0.00026756 | 0.00025798 | 0.0002484 | 0.00023882 | 34069.5054 | 6406.3237 | 157.4727 | 29.6107 | 6876.353 | 8913.2743 | 550225.4428 | 7176.093
| PLD006-162260039 | 14 | PLD006 | PLD | South | 254531.0758 | 0.00073455 | 0.00074186 | 0.00075457 | 0.00076479 | 0.000774 | 0.00078714 | 0.00080511 | 0.00081826 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 5.1863e-05 | 5.2647e-05 | 5.3431e-05 | 5.4216e-05 | 5.5e-05 | 5.3215e-05 | 5.143e-05 | 4.9645e-05 | 4.786e-05 | 4.6075e-05 | 4.429e-05 | 4.2505e-05 | 4.072e-05 | 3.8935e-05 | 3.715e-05 | 3.5365e-05 | 3.358e-05 | 3.1795e-05 | 3.001e-05 | 2.8225e-05 | 1.0606e-06 | 1.0873e-06 | 1.1224e-06 | 1.1544e-06 | 1.1851e-06 | 1.1662e-06 | 1.1528e-06 | 1.1309e-06 | 1.1e-06 | 1.059e-06 | 1.018e-06 | 9.7692e-07 | 9.359e-07 | 8.9487e-07 | 8.5385e-07 | 8.1282e-07 | 7.7179e-07 | 7.3077e-07 | 6.8974e-07 | 6.4872e-07 | 34069.5054 | 6406.3237 | 0.49596 | 0.093259 | 33.5049 | 43.4297 | 265626.0758 | 34.9654
| PLD006-162260159 | 2 | PLD006 | PLD | South | 36361.5823 | 0.00073455 | 0.00074186 | 0.00075457 | 0.00076479 | 0.000774 | 0.00078714 | 0.00080511 | 0.00081826 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.0026231 | 0.0026564 | 0.0026897 | 0.0027229 | 0.0027562 | 0.0026808 | 0.0026053 | 0.0025298 | 0.0024544 | 0.0023789 | 0.0023034 | 0.0022279 | 0.0021525 | 0.002077 | 0.0020015 | 0.0019261 | 0.0018506 | 0.0017751 | 0.0016997 | 0.0016242 | 5.3642e-05 | 5.4863e-05 | 5.6502e-05 | 5.7976e-05 | 5.9391e-05 | 5.8746e-05 | 5.8396e-05 | 5.763e-05 | 5.641e-05 | 5.4676e-05 | 5.2941e-05 | 5.1207e-05 | 4.9472e-05 | 4.7737e-05 | 4.6003e-05 | 4.4268e-05 | 4.2534e-05 | 4.0799e-05 | 3.9065e-05 | 3.733e-05 | 34069.5054 | 6406.3237 | 25.6885 | 4.8304 | 1238.315 | 1605.1302 | 37946.5823 | 1292.2932
| PLD006-162260296 | 45 | PLD006 | PLD | South | 818135.6009 | 0.00073455 | 0.00074186 | 0.00075457 | 0.00076479 | 0.000774 | 0.00078714 | 0.00080511 | 0.00081826 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.0048984 | 0.0049253 | 0.0049521 | 0.004979 | 0.0050058 | 0.0049494 | 0.0048929 | 0.0048365 | 0.00478 | 0.0047236 | 0.0046671 | 0.0046107 | 0.0045542 | 0.0044978 | 0.0044413 | 0.0043849 | 0.0043284 | 0.004272 | 0.0042155 | 0.0041591 | 0.00010017 | 0.00010172 | 0.00010403 | 0.00010601 | 0.00010787 | 0.00010846 | 0.00010967 | 0.00011018 | 0.00010986 | 0.00010857 | 0.00010727 | 0.00010597 | 0.00010467 | 0.00010338 | 0.00010208 | 0.00010078 | 9.9483e-05 | 9.8186e-05 | 9.6889e-05 | 9.5591e-05 | 34069.5054 | 6406.3237 | 51.458 | 9.676 | 1987.618 | 2576.3925 | 853798.1009 | 2074.2581
| PLD006-202509382 | 500 | PLD006 | PLD | South | 9090395.5657 | 0.00073455 | 0.00074186 | 0.00075457 | 0.00076479 | 0.000774 | 0.00078714 | 0.00080511 | 0.00081826 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 5.3365 | 5.3502 | 5.3639 | 5.3775 | 5.3912 | 5.3626 | 5.334 | 5.3054 | 5.2768 | 5.2482 | 5.2196 | 5.191 | 5.1623 | 5.1337 | 5.1051 | 5.0765 | 5.0479 | 5.0193 | 4.9907 | 4.9621 | 0.10913 | 0.1105 | 0.11268 | 0.1145 | 0.11617 | 0.11752 | 0.11956 | 0.12086 | 0.12128 | 0.12062 | 0.11997 | 0.11931 | 0.11865 | 0.11799 | 0.11733 | 0.11668 | 0.11602 | 0.11536 | 0.1147 | 0.11405 | 34069.5054 | 6406.3237 | 57349.6852 | 10783.8563 | 248603.3969 | 322244.9838 | 9486645.5657 | 259440.0096
| PLD006-24597156 | 276 | PLD006 | PLD | South | 5017898.3523 | 0.00073455 | 0.00074186 | 0.00075457 | 0.00076479 | 0.000774 | 0.00078714 | 0.00080511 | 0.00081826 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 0.00082557 | 1.1646 | 1.1765 | 1.1883 | 1.2001 | 1.2119 | 1.1831 | 1.1544 | 1.1256 | 1.0968 | 1.068 | 1.0392 | 1.0104 | 0.98165 | 0.95286 | 0.92408 | 0.89529 | 0.86651 | 0.83773 | 0.80894 | 0.78016 | 0.023817 | 0.024298 | 0.024962 | 0.025552 | 0.026115 | 0.025927 | 0.025874 | 0.025641 | 0.025208 | 0.024547 | 0.023885 | 0.023224 | 0.022562 | 0.0219 | 0.021239 | 0.020577 | 0.019916 | 0.019254 | 0.018593 | 0.017931 | 34069.5054 | 6406.3237 | 11564.011 | 2174.4606 | 302100.4234 | 391588.9616 | 5236628.3523 | 315268.9694
| RCT011-15430907 | 198 | RCT011 | RCTS | North | 4666132.586 | 0.002454 | 0.0024929 | 0.0025194 | 0.0025379 | 0.0025379 | 0.0025503 | 0.002583 | 0.0026218 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 0.002628 | 17.9993 | 18.1069 | 18.2144 | 18.322 | 18.4296 | 18.4444 | 18.4593 | 18.4741 | 18.489 | 18.5038 | 18.5187 | 18.5335 | 18.5484 | 18.5632 | 18.5781 | 18.5929 | 18.6078 | 18.6226 | 18.6375 | 18.6523 | 1.2297 | 1.2567 | 1.2776 | 1.2946 | 1.3022 | 1.3096 | 1.3274 | 1.3485 | 1.3527 | 1.3538 | 1.3549 | 1.356 | 1.3571 | 1.3582 | 1.3592 | 1.3603 | 1.3614 | 1.3625 | 1.3636 | 1.3647 | 28932.3338 | 2806.8717 | 554490.3877 | 53793.9096 | 1533490.2189 | 1533490.2189 | 4666132.586 | 1533490.2189
| RCT012-109224809 | 3 | RCT012 | RCTS | North | 70698.9786 | 1.1645 | 1.1645 | 1.1495 | 1.1345 | 1.123 | 1.108 | 1.098 | 1.088 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 6.0094e-05 | 6.0546e-05 | 6.0997e-05 | 6.1449e-05 | 6.19e-05 | 6.2225e-05 | 6.255e-05 | 6.2875e-05 | 6.32e-05 | 6.3525e-05 | 6.385e-05 | 6.4175e-05 | 6.45e-05 | 6.4825e-05 | 6.515e-05 | 6.5475e-05 | 6.58e-05 | 6.6125e-05 | 6.645e-05 | 6.6775e-05 | 0.0019482 | 0.0019629 | 0.001952 | 0.0019408 | 0.0019353 | 0.0019194 | 0.001912 | 0.0019045 | 0.0018967 | 0.0019065 | 0.0019162 | 0.001926 | 0.0019357 | 0.0019455 | 0.0019553 | 0.001965 | 0.0019748 | 0.0019845 | 0.0019943 | 0.002004 | 28932.3338 | 2806.8717 | 812.0966 | 78.7856 | 64.6416 | 64.6416 | 70698.9786 | 64.6416
| RCT013-15430798 | 264 | RCT013 | RCTS | North | 6221510.1146 | 0.0087451 | 0.0092233 | 0.0091781 | 0.0091124 | 0.0089675 | 0.0088702 | 0.0089018 | 0.0089596 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 8.4806 | 8.5352 | 8.5898 | 8.6444 | 8.699 | 8.7128 | 8.7266 | 8.7404 | 8.7542 | 8.7681 | 8.7819 | 8.7957 | 8.8095 | 8.8233 | 8.8372 | 8.851 | 8.8648 | 8.8786 | 8.8924 | 8.9063 | 2.0647 | 2.1916 | 2.1949 | 2.193 | 2.1718 | 2.1516 | 2.1627 | 2.1802 | 2.1566 | 2.16 | 2.1634 | 2.1668 | 2.1702 | 2.1736 | 2.177 | 2.1804 | 2.1838 | 2.1872 | 2.1907 | 2.1941 | 28932.3338 | 2806.8717 | 907142.0176 | 88006.4231 | 1446388.1987 | 1446388.1987 | 6221510.1146 | 1446388.1987
| RCT013-24605168 | 61 | RCT013 | RCTS | North | 1437545.8977 | 0.0087451 | 0.0092233 | 0.0091781 | 0.0091124 | 0.0089675 | 0.0088702 | 0.0089018 | 0.0089596 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 10.0572 | 10.1097 | 10.1622 | 10.2148 | 10.2673 | 10.2572 | 10.2471 | 10.237 | 10.2269 | 10.2168 | 10.2067 | 10.1966 | 10.1865 | 10.1764 | 10.1663 | 10.1562 | 10.1461 | 10.136 | 10.1259 | 10.1158 | 2.4485 | 2.5959 | 2.5967 | 2.5914 | 2.5633 | 2.533 | 2.5395 | 2.5535 | 2.5194 | 2.5169 | 2.5144 | 2.5119 | 2.5094 | 2.507 | 2.5045 | 2.502 | 2.4995 | 2.497 | 2.4945 | 2.492 | 28932.3338 | 2806.8717 | 1057833.1853 | 102625.7335 | 1410923.4725 | 1410923.4725 | 1437545.8977 | 1410923.4725
| RCT013-24605182 | 160 | RCT013 | RCTS | North | 3770612.1907 | 0.0087451 | 0.0092233 | 0.0091781 | 0.0091124 | 0.0089675 | 0.0088702 | 0.0089018 | 0.0089596 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 0.0088488 | 1.5936 | 1.596 | 1.5985 | 1.601 | 1.6034 | 1.6 | 1.5965 | 1.5931 | 1.5896 | 1.5862 | 1.5827 | 1.5793 | 1.5758 | 1.5723 | 1.5689 | 1.5654 | 1.562 | 1.5585 | 1.5551 | 1.5516 | 0.38797 | 0.40982 | 0.40845 | 0.40615 | 0.4003 | 0.3951 | 0.39566 | 0.39737 | 0.3916 | 0.39075 | 0.3899 | 0.38905 | 0.3882 | 0.38735 | 0.3865 | 0.38565 | 0.3848 | 0.38395 | 0.3831 | 0.38224 | 28932.3338 | 2806.8717 | 164623.8453 | 15970.9897 | 315268.4959 | 315268.4959 | 3770612.1907 | 315268.4959
| RCT014-15430846 | 1 | RCT014 | RCTS | North | 23566.3262 | 0.01327 | 0.013395 | 0.013324 | 0.013234 | 0.013087 | 0.012983 | 0.012997 | 0.013044 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28932.3338 | 2806.8717 | 0 | 0 | 0 | 0 | 23566.3262 | 0
| RCT014-24605126 | 102 | RCT014 | RCTS | North | 2403765.2716 | 0.01327 | 0.013395 | 0.013324 | 0.013234 | 0.013087 | 0.012983 | 0.012997 | 0.013044 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.0055913 | 0.0056304 | 0.0056695 | 0.0057086 | 0.0057477 | 0.0057584 | 0.0057691 | 0.0057798 | 0.0057905 | 0.0058012 | 0.005812 | 0.0058227 | 0.0058334 | 0.0058441 | 0.0058548 | 0.0058655 | 0.0058762 | 0.0058869 | 0.0058976 | 0.0059084 | 0.0020656 | 0.0020997 | 0.002103 | 0.0021032 | 0.0020941 | 0.0020813 | 0.0020875 | 0.002099 | 0.0020838 | 0.0020876 | 0.0020915 | 0.0020953 | 0.0020992 | 0.002103 | 0.0021069 | 0.0021107 | 0.0021146 | 0.0021184 | 0.0021223 | 0.0021261 | 28932.3338 | 2806.8717 | 877.4973 | 85.1304 | 1686.9194 | 1686.9194 | 2403765.2716 | 1686.9194
| RCT014-24611042 | 204 | RCT014 | RCTS | North | 4807530.5431 | 0.01327 | 0.013395 | 0.013324 | 0.013234 | 0.013087 | 0.012983 | 0.012997 | 0.013044 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 0.012926 | 3.7814 | 3.8062 | 3.831 | 3.8558 | 3.8806 | 3.8869 | 3.8933 | 3.8996 | 3.9059 | 3.9122 | 3.9186 | 3.9249 | 3.9312 | 3.9376 | 3.9439 | 3.9502 | 3.9565 | 3.9629 | 3.9692 | 3.9755 | 1.397 | 1.4194 | 1.4211 | 1.4206 | 1.4139 | 1.4049 | 1.4087 | 1.4161 | 1.4056 | 1.4078 | 1.4101 | 1.4124 | 1.4147 | 1.4169 | 1.4192 | 1.4215 | 1.4238 | 1.4261 | 1.4283 | 1.4306 | 28932.3338 | 2806.8717 | 591930.7452 | 57426.1875 | 1278144.956 | 1278144.956 | 4807530.5431 | 1278144.956
| RCT015-15430944 | 25 | RCT015 | RCTS | North | 589158.1548 | 0.065925 | 0.066425 | 0.065925 | 0.06535 | 0.0646 | 0.0641 | 0.063775 | 0.063525 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.063025 | 0.054485 | 0.05489 | 0.055295 | 0.0557 | 0.056104 | 0.056323 | 0.056542 | 0.056761 | 0.05698 | 0.057199 | 0.057418 | 0.057637 | 0.057856 | 0.058074 | 0.058293 | 0.058512 | 0.058731 | 0.05895 | 0.059169 | 0.059388 | 0.1 | 0.10151 | 0.10149 | 0.10134 | 0.1009 | 0.10051 | 0.10039 | 0.10038 | 0.099978 | 0.10036 | 0.10075 | 0.10113 | 0.10151 | 0.1019 | 0.10228 | 0.10267 | 0.10305 | 0.10343 | 0.10382 | 0.1042 | 28932.3338 | 2806.8717 | 42418.1682 | 4115.2005 | 24251.5738 | 24251.5738 | 589158.1548 | 24251.5738
| RCT021-15430691 | 299 | RCT021 | RCTS | North | 7046331.5313 | 0.0046218 | 0.0046524 | 0.00467 | 0.00467 | 0.0046394 | 0.0046241 | 0.0046547 | 0.0046975 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 5.1603 | 5.1958 | 5.2313 | 5.2668 | 5.3022 | 5.3161 | 5.33 | 5.3439 | 5.3578 | 5.3717 | 5.3856 | 5.3995 | 5.4134 | 5.4273 | 5.4412 | 5.4551 | 5.469 | 5.4829 | 5.4968 | 5.5107 | 0.66399 | 0.67298 | 0.68013 | 0.68474 | 0.68484 | 0.68438 | 0.6907 | 0.69887 | 0.69578 | 0.69759 | 0.69939 | 0.7012 | 0.703 | 0.70481 | 0.70661 | 0.70842 | 0.71022 | 0.71203 | 0.71383 | 0.71564 | 28932.3338 | 2806.8717 | 290230.7322 | 28156.7474 | 837214.2238 | 837214.2238 | 7046331.5313 | 837214.2238
| RCT021-24612845 | 30 | RCT021 | RCTS | North | 706989.7858 | 0.0046218 | 0.0046524 | 0.00467 | 0.00467 | 0.0046394 | 0.0046241 | 0.0046547 | 0.0046975 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.0046646 | 0.081773 | 0.082282 | 0.08279 | 0.083299 | 0.083807 | 0.083957 | 0.084108 | 0.084258 | 0.084408 | 0.084558 | 0.084708 | 0.084859 | 0.085009 | 0.085159 | 0.085309 | 0.085459 | 0.08561 | 0.08576 | 0.08591 | 0.08606 | 0.010522 | 0.010657 | 0.010764 | 0.01083 | 0.010825 | 0.010808 | 0.010899 | 0.011019 | 0.010961 | 0.010981 | 0.011001 | 0.01102 | 0.01104 | 0.011059 | 0.011079 | 0.011098 | 0.011118 | 0.011137 | 0.011157 | 0.011176 | 28932.3338 | 2806.8717 | 4570.3009 | 443.3879 | 13246.1818 | 13246.1818 | 706989.7858 | 13246.1818
| RCT022-109224755 | 348 | RCT022 | RCTS | North | 8201081.5147 | 0.0050925 | 0.0051629 | 0.005253 | 0.0052774 | 0.0052321 | 0.0052566 | 0.0053819 | 0.005497 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 5.6175 | 5.6517 | 5.6858 | 5.7199 | 5.754 | 5.7641 | 5.7741 | 5.7842 | 5.7943 | 5.8043 | 5.8144 | 5.8244 | 5.8345 | 5.8445 | 5.8546 | 5.8646 | 5.8747 | 5.8847 | 5.8948 | 5.9048 | 0.79643 | 0.81234 | 0.83151 | 0.84039 | 0.83814 | 0.84353 | 0.86515 | 0.8852 | 0.87249 | 0.874 | 0.87552 | 0.87703 | 0.87854 | 0.88006 | 0.88157 | 0.88308 | 0.8846 | 0.88611 | 0.88762 | 0.88914 | 28932.3338 | 2806.8717 | 359497.3121 | 34876.6477 | 821181.3737 | 821181.3737 | 8201081.5147 | 821181.3737
| RCT022-160254089 | 35 | RCT022 | RCTS | North | 824821.4167 | 0.0050925 | 0.0051629 | 0.005253 | 0.0052774 | 0.0052321 | 0.0052566 | 0.0053819 | 0.005497 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0036283 | 0.0036523 | 0.0036762 | 0.0037001 | 0.003724 | 0.0037324 | 0.0037409 | 0.0037493 | 0.0037577 | 0.0037661 | 0.0037745 | 0.003783 | 0.0037914 | 0.0037998 | 0.0038082 | 0.0038167 | 0.0038251 | 0.0038335 | 0.0038419 | 0.0038503 | 0.00051441 | 0.00052496 | 0.00053761 | 0.00054363 | 0.00054245 | 0.00054621 | 0.0005605 | 0.00057378 | 0.00056583 | 0.0005671 | 0.00056837 | 0.00056963 | 0.0005709 | 0.00057217 | 0.00057344 | 0.00057471 | 0.00057597 | 0.00057724 | 0.00057851 | 0.00057978 | 28932.3338 | 2806.8717 | 233.2003 | 22.6239 | 11182.4549 | 11182.4549 | 824821.4167 | 11182.4549
| RCT022-160254223 | 67 | RCT022 | RCTS | North | 1578943.8548 | 0.0050925 | 0.0051629 | 0.005253 | 0.0052774 | 0.0052321 | 0.0052566 | 0.0053819 | 0.005497 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.021793 | 0.021952 | 0.022111 | 0.02227 | 0.022429 | 0.022431 | 0.022432 | 0.022434 | 0.022435 | 0.022437 | 0.022438 | 0.02244 | 0.022441 | 0.022443 | 0.022444 | 0.022446 | 0.022447 | 0.022449 | 0.02245 | 0.022452 | 0.0030898 | 0.0031553 | 0.0032336 | 0.003272 | 0.0032671 | 0.0032826 | 0.0033611 | 0.0034332 | 0.0033783 | 0.0033785 | 0.0033787 | 0.0033789 | 0.0033792 | 0.0033794 | 0.0033796 | 0.0033798 | 0.0033801 | 0.0033803 | 0.0033805 | 0.0033808 | 28932.3338 | 2806.8717 | 1388.3737 | 134.6931 | 101969.0413 | 101969.0413 | 1578943.8548 | 101969.0413
| RCT022-160652528 | 63 | RCT022 | RCTS | North | 1484678.5501 | 0.0050925 | 0.0051629 | 0.005253 | 0.0052774 | 0.0052321 | 0.0052566 | 0.0053819 | 0.005497 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 1.2617e-05 | 1.2692e-05 | 1.2766e-05 | 1.2841e-05 | 1.2915e-05 | 1.2948e-05 | 1.298e-05 | 1.3013e-05 | 1.3045e-05 | 1.3078e-05 | 1.311e-05 | 1.3143e-05 | 1.3175e-05 | 1.3208e-05 | 1.3241e-05 | 1.3273e-05 | 1.3306e-05 | 1.3338e-05 | 1.3371e-05 | 1.3403e-05 | 1.7888e-06 | 1.8243e-06 | 1.867e-06 | 1.8866e-06 | 1.8812e-06 | 1.8948e-06 | 1.9448e-06 | 1.9914e-06 | 1.9643e-06 | 1.9692e-06 | 1.9741e-06 | 1.979e-06 | 1.9839e-06 | 1.9888e-06 | 1.9937e-06 | 1.9986e-06 | 2.0035e-06 | 2.0084e-06 | 2.0133e-06 | 2.0182e-06 | 28932.3338 | 2806.8717 | 0.81014 | 0.078596 | 13.3193 | 13.3193 | 1484678.5501 | 13.3193
| RCT022-162765375 | 1 | RCT022 | RCTS | North | 23566.3262 | 0.0050925 | 0.0051629 | 0.005253 | 0.0052774 | 0.0052321 | 0.0052566 | 0.0053819 | 0.005497 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28932.3338 | 2806.8717 | 0 | 0 | 0 | 0 | 23566.3262 | 0
| RCT022-187104623 | 0 | RCT022 | RCTS | North | 0 | 0.0050925 | 0.0051629 | 0.005253 | 0.0052774 | 0.0052321 | 0.0052566 | 0.0053819 | 0.005497 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28932.3338 | 2806.8717 | 0 | 0 | 0 | 0 | 0 | 0
| RCT022-201142435 | 243 | RCT022 | RCTS | North | 5726617.2646 | 0.0050925 | 0.0051629 | 0.005253 | 0.0052774 | 0.0052321 | 0.0052566 | 0.0053819 | 0.005497 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.36781 | 0.36964 | 0.37147 | 0.3733 | 0.37513 | 0.37505 | 0.37497 | 0.37489 | 0.37481 | 0.37473 | 0.37464 | 0.37456 | 0.37448 | 0.3744 | 0.37432 | 0.37424 | 0.37416 | 0.37407 | 0.37399 | 0.37391 | 0.052146 | 0.05313 | 0.054325 | 0.054847 | 0.054643 | 0.054886 | 0.056182 | 0.057372 | 0.056438 | 0.056426 | 0.056413 | 0.056401 | 0.056389 | 0.056377 | 0.056364 | 0.056352 | 0.05634 | 0.056328 | 0.056315 | 0.056303 | 28932.3338 | 2806.8717 | 23219.8151 | 2252.6714 | 1088832.4426 | 1088832.4426 | 5726617.2646 | 1088832.4426
| RCT022-74940140 | 79 | RCT022 | RCTS | North | 1861739.7692 | 0.0050925 | 0.0051629 | 0.005253 | 0.0052774 | 0.0052321 | 0.0052566 | 0.0053819 | 0.005497 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.0054087 | 0.017635 | 0.01775 | 0.017865 | 0.01798 | 0.018095 | 0.018157 | 0.01822 | 0.018282 | 0.018345 | 0.018407 | 0.01847 | 0.018532 | 0.018595 | 0.018657 | 0.018719 | 0.018782 | 0.018844 | 0.018907 | 0.018969 | 0.019032 | 0.0025002 | 0.0025513 | 0.0026126 | 0.0026417 | 0.0026357 | 0.0026572 | 0.0027299 | 0.0027979 | 0.0027623 | 0.0027717 | 0.0027811 | 0.0027905 | 0.0027999 | 0.0028093 | 0.0028187 | 0.0028281 | 0.0028375 | 0.0028469 | 0.0028563 | 0.0028658 | 28932.3338 | 2806.8717 | 1139.9797 | 110.5952 | 9268.5224 | 9268.5224 | 1861739.7692 | 9268.5224
| RCT023-15430737 | 253 | RCT023 | RCTS | North | 5962280.5265 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 1.0513 | 1.0579 | 1.0644 | 1.071 | 1.0776 | 1.0797 | 1.0818 | 1.084 | 1.0861 | 1.0882 | 1.0904 | 1.0925 | 1.0946 | 1.0967 | 1.0989 | 1.101 | 1.1031 | 1.1053 | 1.1074 | 1.1095 | 0.059962 | 0.060897 | 0.061657 | 0.061983 | 0.061738 | 0.061567 | 0.062412 | 0.063375 | 0.063 | 0.063123 | 0.063247 | 0.06337 | 0.063494 | 0.063617 | 0.063741 | 0.063864 | 0.063988 | 0.064111 | 0.064235 | 0.064358 | 28932.3338 | 2806.8717 | 26213.9717 | 2543.1496 | 43671.889 | 43671.889 | 5962280.5265 | 43671.889
| RCT023-159364712 | 75 | RCT023 | RCTS | North | 1767474.4644 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.003974 | 0.0039974 | 0.0040209 | 0.0040443 | 0.0040678 | 0.0040661 | 0.0040644 | 0.0040628 | 0.0040611 | 0.0040595 | 0.0040578 | 0.0040561 | 0.0040545 | 0.0040528 | 0.0040512 | 0.0040495 | 0.0040478 | 0.0040462 | 0.0040445 | 0.0040429 | 0.00022666 | 0.00023011 | 0.00023291 | 0.00023406 | 0.00023306 | 0.00023186 | 0.00023448 | 0.00023753 | 0.00023557 | 0.00023547 | 0.00023538 | 0.00023528 | 0.00023518 | 0.00023509 | 0.00023499 | 0.00023489 | 0.0002348 | 0.0002347 | 0.00023461 | 0.00023451 | 28932.3338 | 2806.8717 | 97.795 | 9.4876 | 10334.8663 | 10334.8663 | 1767474.4644 | 10334.8663
| RCT023-159364841 | 127 | RCT023 | RCTS | North | 2992923.4264 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.02072 | 0.020827 | 0.020935 | 0.021043 | 0.02115 | 0.021142 | 0.021135 | 0.021127 | 0.021119 | 0.021112 | 0.021104 | 0.021097 | 0.021089 | 0.021081 | 0.021074 | 0.021066 | 0.021058 | 0.021051 | 0.021043 | 0.021035 | 0.0011818 | 0.0011989 | 0.0012126 | 0.0012178 | 0.0012118 | 0.0012056 | 0.0012193 | 0.0012352 | 0.0012251 | 0.0012246 | 0.0012242 | 0.0012237 | 0.0012233 | 0.0012228 | 0.0012224 | 0.0012219 | 0.0012215 | 0.0012211 | 0.0012206 | 0.0012202 | 28932.3338 | 2806.8717 | 508.8249 | 49.3637 | 32519.3385 | 32519.3385 | 2992923.4264 | 32519.3385
| RCT023-159364971 | 216 | RCT023 | RCTS | North | 5090326.4574 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.016804 | 0.016916 | 0.017029 | 0.017142 | 0.017254 | 0.017258 | 0.017262 | 0.017266 | 0.017269 | 0.017273 | 0.017277 | 0.017281 | 0.017285 | 0.017288 | 0.017292 | 0.017296 | 0.0173 | 0.017304 | 0.017308 | 0.017311 | 0.00095841 | 0.00097379 | 0.00098638 | 0.00099204 | 0.00098855 | 0.00098409 | 0.00099584 | 0.0010094 | 0.0010017 | 0.0010019 | 0.0010022 | 0.0010024 | 0.0010026 | 0.0010028 | 0.0010031 | 0.0010033 | 0.0010035 | 0.0010037 | 0.0010039 | 0.0010042 | 28932.3338 | 2806.8717 | 415.9299 | 40.3515 | 45210.2218 | 45210.2218 | 5090326.4574 | 45210.2218
| RCT023-159365116 | 69 | RCT023 | RCTS | North | 1626076.5072 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0015647 | 0.001575 | 0.0015853 | 0.0015956 | 0.0016059 | 0.0016055 | 0.0016052 | 0.0016049 | 0.0016046 | 0.0016043 | 0.001604 | 0.0016037 | 0.0016033 | 0.001603 | 0.0016027 | 0.0016024 | 0.0016021 | 0.0016018 | 0.0016014 | 0.0016011 | 8.924e-05 | 9.0662e-05 | 9.1824e-05 | 9.2341e-05 | 9.2006e-05 | 9.1552e-05 | 9.2607e-05 | 9.3833e-05 | 9.3076e-05 | 9.3058e-05 | 9.304e-05 | 9.3021e-05 | 9.3003e-05 | 9.2985e-05 | 9.2966e-05 | 9.2948e-05 | 9.293e-05 | 9.2911e-05 | 9.2893e-05 | 9.2875e-05 | 28932.3338 | 2806.8717 | 38.6321 | 3.7479 | 3129.9712 | 3129.9712 | 1626076.5072 | 3129.9712
| RCT023-159365240 | 87 | RCT023 | RCTS | North | 2050270.3787 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.00044509 | 0.00044767 | 0.00045025 | 0.00045282 | 0.0004554 | 0.00045562 | 0.00045584 | 0.00045606 | 0.00045628 | 0.0004565 | 0.00045672 | 0.00045694 | 0.00045716 | 0.00045738 | 0.0004576 | 0.00045782 | 0.00045804 | 0.00045826 | 0.00045848 | 0.0004587 | 2.5386e-05 | 2.577e-05 | 2.608e-05 | 2.6206e-05 | 2.6091e-05 | 2.5981e-05 | 2.6298e-05 | 2.6664e-05 | 2.6467e-05 | 2.648e-05 | 2.6492e-05 | 2.6505e-05 | 2.6518e-05 | 2.6531e-05 | 2.6543e-05 | 2.6556e-05 | 2.6569e-05 | 2.6582e-05 | 2.6594e-05 | 2.6607e-05 | 28932.3338 | 2806.8717 | 10.9987 | 1.067 | 1225.7087 | 1225.7087 | 2050270.3787 | 1225.7087
| RCT023-159365351 | 100 | RCT023 | RCTS | North | 2356632.6192 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0023996 | 0.0024135 | 0.0024273 | 0.0024412 | 0.002455 | 0.0024517 | 0.0024483 | 0.0024449 | 0.0024416 | 0.0024382 | 0.0024348 | 0.0024314 | 0.0024281 | 0.0024247 | 0.0024213 | 0.0024179 | 0.0024146 | 0.0024112 | 0.0024078 | 0.0024045 | 0.00013686 | 0.00013893 | 0.0001406 | 0.00014128 | 0.00014066 | 0.0001398 | 0.00014124 | 0.00014294 | 0.00014162 | 0.00014143 | 0.00014123 | 0.00014104 | 0.00014084 | 0.00014065 | 0.00014045 | 0.00014025 | 0.00014006 | 0.00013986 | 0.00013967 | 0.00013947 | 28932.3338 | 2806.8717 | 58.7384 | 5.6985 | 3941.2798 | 3941.2798 | 2356632.6192 | 3941.2798
| RCT023-159365509 | 41 | RCT023 | RCTS | North | 966219.3739 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 1.6285e-06 | 1.6399e-06 | 1.6513e-06 | 1.6626e-06 | 1.674e-06 | 1.6797e-06 | 1.6854e-06 | 1.6911e-06 | 1.6968e-06 | 1.7025e-06 | 1.7082e-06 | 1.7139e-06 | 1.7196e-06 | 1.7253e-06 | 1.731e-06 | 1.7367e-06 | 1.7424e-06 | 1.7481e-06 | 1.7538e-06 | 1.7595e-06 | 9.2883e-08 | 9.4399e-08 | 9.5647e-08 | 9.6222e-08 | 9.5909e-08 | 9.5781e-08 | 9.7232e-08 | 9.8872e-08 | 9.8424e-08 | 9.8755e-08 | 9.9085e-08 | 9.9416e-08 | 9.9747e-08 | 1.0008e-07 | 1.0041e-07 | 1.0074e-07 | 1.0107e-07 | 1.014e-07 | 1.0173e-07 | 1.0206e-07 | 28932.3338 | 2806.8717 | 0.040996 | 0.0039772 | 11.8411 | 11.8411 | 966219.3739 | 11.8411
| RCT023-160652906 | 123 | RCT023 | RCTS | North | 2898658.1216 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0018487 | 0.001861 | 0.0018732 | 0.0018855 | 0.0018978 | 0.001897 | 0.0018962 | 0.0018955 | 0.0018947 | 0.001894 | 0.0018932 | 0.0018925 | 0.0018917 | 0.001891 | 0.0018902 | 0.0018895 | 0.0018887 | 0.001888 | 0.0018872 | 0.0018865 | 0.00010544 | 0.00010713 | 0.0001085 | 0.00010912 | 0.00010873 | 0.00010817 | 0.0001094 | 0.00011082 | 0.00010991 | 0.00010986 | 0.00010982 | 0.00010977 | 0.00010973 | 0.00010969 | 0.00010964 | 0.0001096 | 0.00010956 | 0.00010951 | 0.00010947 | 0.00010943 | 28932.3338 | 2806.8717 | 45.6064 | 4.4245 | 19760.4343 | 19760.4343 | 2898658.1216 | 19760.4343
| RCT023-162905845 | 43 | RCT023 | RCTS | North | 1013352.0262 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.051598 | 0.051929 | 0.05226 | 0.05259 | 0.052921 | 0.052938 | 0.052956 | 0.052974 | 0.052992 | 0.053009 | 0.053027 | 0.053045 | 0.053062 | 0.05308 | 0.053098 | 0.053115 | 0.053133 | 0.053151 | 0.053169 | 0.053186 | 0.0029429 | 0.0029893 | 0.0030271 | 0.0030436 | 0.003032 | 0.0030187 | 0.0030551 | 0.0030972 | 0.0030738 | 0.0030748 | 0.0030759 | 0.0030769 | 0.0030779 | 0.003079 | 0.00308 | 0.003081 | 0.003082 | 0.0030831 | 0.0030841 | 0.0030851 | 28932.3338 | 2806.8717 | 1276.6751 | 123.8567 | 77351.6031 | 77351.6031 | 1013352.0262 | 77351.6031
| RCT023-162905960 | 20 | RCT023 | RCTS | North | 471326.5238 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0011439 | 0.0011519 | 0.0011599 | 0.0011679 | 0.0011759 | 0.0011745 | 0.0011731 | 0.0011717 | 0.0011703 | 0.001169 | 0.0011676 | 0.0011662 | 0.0011648 | 0.0011635 | 0.0011621 | 0.0011607 | 0.0011593 | 0.001158 | 0.0011566 | 0.0011552 | 6.5244e-05 | 6.6309e-05 | 6.7185e-05 | 6.7589e-05 | 6.7369e-05 | 6.6972e-05 | 6.7677e-05 | 6.8506e-05 | 6.7887e-05 | 6.7807e-05 | 6.7727e-05 | 6.7648e-05 | 6.7568e-05 | 6.7488e-05 | 6.7408e-05 | 6.7328e-05 | 6.7249e-05 | 6.7169e-05 | 6.7089e-05 | 6.7009e-05 | 28932.3338 | 2806.8717 | 28.141 | 2.7301 | 2643.4949 | 2643.4949 | 471326.5238 | 2643.4949
| RCT023-162906075 | 163 | RCT023 | RCTS | North | 3841311.1693 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.048675 | 0.048986 | 0.049297 | 0.049608 | 0.049919 | 0.049949 | 0.049979 | 0.050009 | 0.050039 | 0.050069 | 0.050098 | 0.050128 | 0.050158 | 0.050188 | 0.050218 | 0.050248 | 0.050278 | 0.050307 | 0.050337 | 0.050367 | 0.0027762 | 0.0028199 | 0.0028555 | 0.002871 | 0.0028601 | 0.0028482 | 0.0028833 | 0.0029238 | 0.0029025 | 0.0029043 | 0.002906 | 0.0029077 | 0.0029095 | 0.0029112 | 0.0029129 | 0.0029147 | 0.0029164 | 0.0029181 | 0.0029199 | 0.0029216 | 28932.3338 | 2806.8717 | 1205.8855 | 116.989 | 86549.0436 | 86549.0436 | 3841311.1693 | 86549.0436
| RCT023-24605614 | 21 | RCT023 | RCTS | North | 494892.85 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.7496 | 0.75414 | 0.75869 | 0.76324 | 0.76779 | 0.76889 | 0.76998 | 0.77107 | 0.77217 | 0.77326 | 0.77435 | 0.77545 | 0.77654 | 0.77764 | 0.77873 | 0.77982 | 0.78092 | 0.78201 | 0.7831 | 0.7842 | 0.042753 | 0.043412 | 0.043946 | 0.044172 | 0.04399 | 0.043844 | 0.044421 | 0.045082 | 0.04479 | 0.044854 | 0.044917 | 0.04498 | 0.045044 | 0.045107 | 0.045171 | 0.045234 | 0.045298 | 0.045361 | 0.045425 | 0.045488 | 28932.3338 | 2806.8717 | 18628.3248 | 1807.2278 | 19971.0834 | 19971.0834 | 494892.85 | 19971.0834
| RCT023-24605628 | 152 | RCT023 | RCTS | North | 3582081.5812 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 1.0162 | 1.0229 | 1.0297 | 1.0365 | 1.0432 | 1.0456 | 1.048 | 1.0504 | 1.0529 | 1.0553 | 1.0577 | 1.0601 | 1.0625 | 1.0649 | 1.0673 | 1.0697 | 1.0721 | 1.0745 | 1.0769 | 1.0793 | 0.057959 | 0.058886 | 0.059644 | 0.059984 | 0.05977 | 0.059624 | 0.060462 | 0.061415 | 0.061071 | 0.061211 | 0.061351 | 0.061491 | 0.06163 | 0.06177 | 0.06191 | 0.062049 | 0.062189 | 0.062329 | 0.062468 | 0.062608 | 28932.3338 | 2806.8717 | 25414.0553 | 2465.5457 | 175009.9981 | 175009.9981 | 3582081.5812 | 175009.9981
| RCT023-24606802 | 146 | RCT023 | RCTS | North | 3440683.624 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.92023 | 0.92495 | 0.92968 | 0.93441 | 0.93913 | 0.93845 | 0.93776 | 0.93708 | 0.93639 | 0.9357 | 0.93502 | 0.93433 | 0.93365 | 0.93296 | 0.93227 | 0.93159 | 0.9309 | 0.93022 | 0.92953 | 0.92884 | 0.052485 | 0.053245 | 0.053851 | 0.054077 | 0.053806 | 0.053513 | 0.0541 | 0.054787 | 0.054316 | 0.054276 | 0.054236 | 0.054197 | 0.054157 | 0.054117 | 0.054077 | 0.054038 | 0.053998 | 0.053958 | 0.053918 | 0.053878 | 28932.3338 | 2806.8717 | 22552.0617 | 2187.8893 | 405823.8645 | 405823.8645 | 3440683.624 | 405823.8645
| RCT023-24611339 | 25 | RCT023 | RCTS | North | 589158.1548 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28932.3338 | 2806.8717 | 0 | 0 | 0 | 0 | 589158.1548 | 0
| RCT023-85530600 | 27 | RCT023 | RCTS | North | 636290.8072 | 0.0020487 | 0.0020677 | 0.0020806 | 0.0020788 | 0.002058 | 0.0020482 | 0.0020722 | 0.0021001 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.0020835 | 0.022161 | 0.022299 | 0.022437 | 0.022574 | 0.022712 | 0.022769 | 0.022826 | 0.022884 | 0.022941 | 0.022998 | 0.023055 | 0.023112 | 0.023169 | 0.023226 | 0.023284 | 0.023341 | 0.023398 | 0.023455 | 0.023512 | 0.023569 | 0.001264 | 0.0012836 | 0.0012996 | 0.0013065 | 0.0013013 | 0.0012984 | 0.0013169 | 0.0013379 | 0.0013307 | 0.001334 | 0.0013373 | 0.0013406 | 0.001344 | 0.0013473 | 0.0013506 | 0.0013539 | 0.0013572 | 0.0013605 | 0.0013638 | 0.0013672 | 28932.3338 | 2806.8717 | 554.0166 | 53.7479 | 1968.3716 | 1968.3716 | 636290.8072 | 1968.3716
| RVL001-15418899 | 0 | RVL001 | RVL | North | 0 | 0.0047139 | 0.0050064 | 0.0050297 | 0.0050321 | 0.0050105 | 0.0050087 | 0.0050437 | 0.0050862 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 6.5257e-05 | 6.5843e-05 | 6.6429e-05 | 6.7014e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 6.76e-05 | 8.564e-06 | 9.1771e-06 | 9.3018e-06 | 9.3882e-06 | 9.4297e-06 | 9.4264e-06 | 9.4922e-06 | 9.5722e-06 | 9.5328e-06 | 9.5328e-06 | 9.5328e-06 | 9.5328e-06 | 9.5328e-06 | 9.5328e-06 | 9.5328e-06 | 9.5328e-06 | 9.5328e-06 | 9.5328e-06 | 9.5328e-06 | 9.5328e-06 | 28807.2259 | 3200.7764 | 0 | 0 | 0 | 0 | 0 | 0
| RVL001-15418912 | 393 | RVL001 | RVL | North | 9261566.1934 | 0.0047139 | 0.0050064 | 0.0050297 | 0.0050321 | 0.0050105 | 0.0050087 | 0.0050437 | 0.0050862 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 0.0050653 | 11.9531 | 12.0376 | 12.1221 | 12.2066 | 12.2911 | 12.27 | 12.2489 | 12.2277 | 12.2066 | 12.1855 | 12.1644 | 12.1433 | 12.1222 | 12.1011 | 12.08 | 12.0589 | 12.0378 | 12.0167 | 11.9956 | 11.9745 | 1.5687 | 1.6778 | 1.6974 | 1.71 | 1.7145 | 1.711 | 1.7199 | 1.7315 | 1.7213 | 1.7184 | 1.7154 | 1.7124 | 1.7094 | 1.7065 | 1.7035 | 1.7005 | 1.6975 | 1.6946 | 1.6916 | 1.6886 | 28807.2259 | 3200.7764 | 707061.7421 | 78561.7658 | 1895333.6378 | 1895333.6378 | 9261566.1934 | 1895333.6378
| RVL004-15418812 | 0 | RVL004 | RVL | North | 0 | 0.024872 | 0.025439 | 0.025734 | 0.025968 | 0.025909 | 0.025868 | 0.026249 | 0.026719 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28807.2259 | 3200.7764 | 0 | 0 | 0 | 0 | 0 | 0
| RVL004-15418838 | 117 | RVL004 | RVL | North | 2757260.1644 | 0.024872 | 0.025439 | 0.025734 | 0.025968 | 0.025909 | 0.025868 | 0.026249 | 0.026719 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 2.1817 | 2.1949 | 2.2081 | 2.2213 | 2.2345 | 2.2294 | 2.2244 | 2.2193 | 2.2143 | 2.2092 | 2.2042 | 2.1991 | 2.1941 | 2.189 | 2.184 | 2.1789 | 2.1739 | 2.1688 | 2.1638 | 2.1587 | 1.5107 | 1.5545 | 1.5819 | 1.6058 | 1.6117 | 1.6055 | 1.6255 | 1.6508 | 1.6477 | 1.644 | 1.6402 | 1.6365 | 1.6327 | 1.6289 | 1.6252 | 1.6214 | 1.6177 | 1.6139 | 1.6102 | 1.6064 | 28807.2259 | 3200.7764 | 670627.1797 | 74513.5146 | 381412.6372 | 381412.6372 | 2757260.1644 | 381412.6372
| RVL004-162771521 | 0 | RVL004 | RVL | North | 0 | 0.024872 | 0.025439 | 0.025734 | 0.025968 | 0.025909 | 0.025868 | 0.026249 | 0.026719 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0.026729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28807.2259 | 3200.7764 | 0 | 0 | 0 | 0 | 0 | 0
| RVL006-15418762 | 107 | RVL006 | RVL | North | 2521596.9025 | 0.0060761 | 0.0061411 | 0.0061437 | 0.0061608 | 0.0061317 | 0.0061146 | 0.0061343 | 0.0061685 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 0.0061771 | 2.5177 | 2.5338 | 2.5499 | 2.566 | 2.5821 | 2.5773 | 2.5725 | 2.5677 | 2.5629 | 2.5581 | 2.5533 | 2.5484 | 2.5436 | 2.5388 | 2.534 | 2.5292 | 2.5244 | 2.5196 | 2.5147 | 2.5099 | 0.42589 | 0.4332 | 0.43614 | 0.44012 | 0.44079 | 0.43874 | 0.43933 | 0.44096 | 0.44074 | 0.43991 | 0.43908 | 0.43826 | 0.43743 | 0.4366 | 0.43577 | 0.43494 | 0.43412 | 0.43329 | 0.43246 | 0.43163 | 28807.2259 | 3200.7764 | 181833.8824 | 20203.5976 | 158763.6955 | 158763.6955 | 2521596.9025 | 158763.6955
| RVL008-15418862 | 116 | RVL008 | RVL | North | 2733693.8382 | 0.016981 | 0.020056 | 0.020365 | 0.020519 | 0.020449 | 0.020449 | 0.020798 | 0.021214 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.46027 | 0.4639 | 0.46753 | 0.47116 | 0.47479 | 0.47458 | 0.47437 | 0.47416 | 0.47395 | 0.47374 | 0.47353 | 0.47332 | 0.47311 | 0.4729 | 0.47269 | 0.47248 | 0.47227 | 0.47206 | 0.47184 | 0.47163 | 0.2176 | 0.25902 | 0.26507 | 0.26914 | 0.2703 | 0.27018 | 0.27466 | 0.28004 | 0.2793 | 0.27917 | 0.27905 | 0.27893 | 0.2788 | 0.27868 | 0.27855 | 0.27843 | 0.27831 | 0.27818 | 0.27806 | 0.27793 | 28807.2259 | 3200.7764 | 112731.2227 | 12525.5878 | 116695.1664 | 116695.1664 | 2733693.8382 | 116695.1664
| RVL008-24613925 | 109 | RVL008 | RVL | North | 2568729.5549 | 0.016981 | 0.020056 | 0.020365 | 0.020519 | 0.020449 | 0.020449 | 0.020798 | 0.021214 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 0.021167 | 1.1356 | 1.1444 | 1.1531 | 1.1619 | 1.1707 | 1.1701 | 1.1695 | 1.1689 | 1.1683 | 1.1678 | 1.1672 | 1.1666 | 1.166 | 1.1654 | 1.1648 | 1.1643 | 1.1637 | 1.1631 | 1.1625 | 1.1619 | 0.53687 | 0.63896 | 0.65379 | 0.66372 | 0.66646 | 0.66612 | 0.67715 | 0.69036 | 0.6885 | 0.68816 | 0.68782 | 0.68747 | 0.68713 | 0.68679 | 0.68644 | 0.6861 | 0.68576 | 0.68541 | 0.68507 | 0.68473 | 28807.2259 | 3200.7764 | 277904.4408 | 30878.0157 | 324491.6528 | 324491.6528 | 2568729.5549 | 324491.6528
| SA001-15410791 | 256 | SA001 | SA | South | 4654282.5297 | 0.0010559 | 0.0010835 | 0.001118 | 0.001149 | 0.0011782 | 0.0012144 | 0.0012566 | 0.0012928 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 4857162.5297 | 0
| SA001-15410802 | 0 | SA001 | SA | South | 0 | 0.0010559 | 0.0010835 | 0.001118 | 0.001149 | 0.0011782 | 0.0012144 | 0.0012566 | 0.0012928 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 0 | 0
| SA001-15411152 | 0 | SA001 | SA | South | 0 | 0.0010559 | 0.0010835 | 0.001118 | 0.001149 | 0.0011782 | 0.0012144 | 0.0012566 | 0.0012928 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0.0013195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 0 | 0
| SA002-15410828 | 183 | SA002 | SA | South | 3327084.7771 | 0.0014203 | 0.0014248 | 0.001428 | 0.0014261 | 0.0014173 | 0.0014124 | 0.0014173 | 0.0014248 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.14115 | 0.14224 | 0.14333 | 0.14442 | 0.14551 | 0.14566 | 0.14581 | 0.14596 | 0.1461 | 0.14625 | 0.1464 | 0.14654 | 0.14669 | 0.14684 | 0.14698 | 0.14713 | 0.14728 | 0.14742 | 0.14757 | 0.14772 | 0.0055813 | 0.0056422 | 0.0056982 | 0.0057341 | 0.0057417 | 0.0057278 | 0.0057533 | 0.0057895 | 0.0057778 | 0.0057836 | 0.0057894 | 0.0057953 | 0.0058011 | 0.0058069 | 0.0058127 | 0.0058185 | 0.0058243 | 0.0058301 | 0.0058359 | 0.0058417 | 45022.6621 | 9967.7614 | 3747.9349 | 829.7715 | 2622.1618 | 3398.9016 | 3472112.2771 | 2736.4617
| SA002-24612976 | 133 | SA002 | SA | South | 2418045.2205 | 0.0014203 | 0.0014248 | 0.001428 | 0.0014261 | 0.0014173 | 0.0014124 | 0.0014173 | 0.0014248 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.0014205 | 0.095933 | 0.096663 | 0.097394 | 0.098124 | 0.098855 | 0.09896 | 0.099065 | 0.099171 | 0.099276 | 0.099381 | 0.099486 | 0.099591 | 0.099696 | 0.099802 | 0.099907 | 0.10001 | 0.10012 | 0.10022 | 0.10033 | 0.10043 | 0.0037933 | 0.0038343 | 0.0038719 | 0.0038958 | 0.0039006 | 0.0038913 | 0.0039089 | 0.0039337 | 0.003926 | 0.0039302 | 0.0039343 | 0.0039385 | 0.0039426 | 0.0039468 | 0.003951 | 0.0039551 | 0.0039593 | 0.0039634 | 0.0039676 | 0.0039718 | 45022.6621 | 9967.7614 | 2547.0224 | 563.8963 | 3123.6646 | 4048.9601 | 2523447.7205 | 3259.825
| SA003-15410891 | 161 | SA003 | SA | South | 2927107.3722 | 0.0012656 | 0.0012703 | 0.0012771 | 0.0012809 | 0.0012766 | 0.0012776 | 0.0012948 | 0.0013164 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 3054699.8722 | 0
| SA003-24613059 | 25 | SA003 | SA | South | 454519.7783 | 0.0012656 | 0.0012703 | 0.0012771 | 0.0012809 | 0.0012766 | 0.0012776 | 0.0012948 | 0.0013164 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0.0013166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 474332.2783 | 0
| SA004-15410928 | 339 | SA004 | SA | South | 6163288.1936 | 0.00094011 | 0.00095066 | 0.00095876 | 0.00096893 | 0.00097778 | 0.00099774 | 0.0010234 | 0.0010475 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0.0010652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 6431945.6936 | 0
| SA005-15411004 | 189 | SA005 | SA | South | 3436169.5238 | 0.0010538 | 0.0010667 | 0.0010738 | 0.0010791 | 0.0010822 | 0.0010871 | 0.0011156 | 0.0011436 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 3585952.0238 | 0
| SA005-24614201 | 6 | SA005 | SA | South | 109084.7468 | 0.0010538 | 0.0010667 | 0.0010738 | 0.0010791 | 0.0010822 | 0.0010871 | 0.0011156 | 0.0011436 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0.0011683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 113839.7468 | 0
| SA006-15411054 | 100 | SA006 | SA | South | 1818079.1131 | 0.0014454 | 0.0014484 | 0.0014431 | 0.0014385 | 0.0014264 | 0.0014188 | 0.0014188 | 0.0014211 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 1897329.1131 | 0
| SA006-24612920 | 50 | SA006 | SA | South | 909039.5566 | 0.0014454 | 0.0014484 | 0.0014431 | 0.0014385 | 0.0014264 | 0.0014188 | 0.0014188 | 0.0014211 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 0.0014135 | 1.4606 | 1.4735 | 1.4863 | 1.4992 | 1.5121 | 1.5116 | 1.5112 | 1.5108 | 1.5104 | 1.5099 | 1.5095 | 1.5091 | 1.5087 | 1.5082 | 1.5078 | 1.5074 | 1.5069 | 1.5065 | 1.5061 | 1.5057 | 0.058777 | 0.059417 | 0.059717 | 0.060042 | 0.060045 | 0.059709 | 0.059692 | 0.059771 | 0.059436 | 0.059419 | 0.059402 | 0.059385 | 0.059369 | 0.059352 | 0.059335 | 0.059318 | 0.059301 | 0.059285 | 0.059268 | 0.059251 | 45022.6621 | 9967.7614 | 38723.2271 | 8573.1023 | 23108.901 | 29954.2465 | 948664.5566 | 24116.2172
| SA007-111739222 | 58 | SA007 | SA | South | 1054485.8856 | 0.0011442 | 0.0011658 | 0.001187 | 0.001208 | 0.0012606 | 0.0013372 | 0.0014178 | 0.0014909 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 1100450.8856 | 0
| SA007-15411091 | 275 | SA007 | SA | South | 4999717.5612 | 0.0011442 | 0.0011658 | 0.001187 | 0.001208 | 0.0012606 | 0.0013372 | 0.0014178 | 0.0014909 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0.0015511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 5217655.0612 | 0
| SA009-15436559 | 0 | SA009 | SA | South | 0 | 0.0010691 | 0.0010953 | 0.0011161 | 0.0011371 | 0.0011501 | 0.0011909 | 0.0012618 | 0.001331 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 0 | 0
| SA009-15436572 | 176 | SA009 | SA | South | 3199819.2391 | 0.0010691 | 0.0010953 | 0.0011161 | 0.0011371 | 0.0011501 | 0.0011909 | 0.0012618 | 0.001331 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 3339299.2391 | 0
| SA009-76846685 | 2 | SA009 | SA | South | 36361.5823 | 0.0010691 | 0.0010953 | 0.0011161 | 0.0011371 | 0.0011501 | 0.0011909 | 0.0012618 | 0.001331 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0.0013902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 37946.5823 | 0
| SA010-15436583 | 97 | SA010 | SA | South | 1763536.7398 | 0.0012814 | 0.0012875 | 0.0012851 | 0.0012827 | 0.001271 | 0.0012667 | 0.0012741 | 0.0012853 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 1840409.2398 | 0
| SA010-24613811 | 27 | SA010 | SA | South | 490881.3605 | 0.0012814 | 0.0012875 | 0.0012851 | 0.0012827 | 0.001271 | 0.0012667 | 0.0012741 | 0.0012853 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0.0012829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 512278.8605 | 0
| SA011-15436594 | 85 | SA011 | SA | South | 1545367.2462 | 0.0014125 | 0.001439 | 0.0014591 | 0.0014777 | 0.0014896 | 0.0015068 | 0.0015809 | 0.0016585 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 0.0017257 | 21.2328 | 21.3794 | 21.5259 | 21.6725 | 21.819 | 21.8615 | 21.904 | 21.9465 | 21.989 | 22.0315 | 22.074 | 22.1165 | 22.159 | 22.2015 | 22.244 | 22.2865 | 22.329 | 22.3715 | 22.414 | 22.4565 | 0.83494 | 0.85652 | 0.87441 | 0.89157 | 0.90485 | 0.91709 | 0.96403 | 1.0133 | 1.0564 | 1.0585 | 1.0605 | 1.0625 | 1.0646 | 1.0666 | 1.0687 | 1.0707 | 1.0727 | 1.0748 | 1.0768 | 1.0789 | 45022.6621 | 9967.7614 | 642891.6216 | 142332.5499 | 120578.2159 | 156296.035 | 1612729.7462 | 125834.2158
| SA012-15437079 | 197 | SA012 | SA | South | 3581615.8529 | 0.015381 | 0.015389 | 0.015144 | 0.014893 | 0.01463 | 0.014379 | 0.014208 | 0.014037 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0.013834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45022.6621 | 9967.7614 | 0 | 0 | 0 | 0 | 3737738.3529 | 0
| SHL001-15428689 | 440 | SHL001 | SHL | North | 10369183.5244 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 5.1565 | 5.2038 | 5.2511 | 5.2983 | 5.3456 | 5.3697 | 5.3938 | 5.4178 | 5.4419 | 5.466 | 5.4901 | 5.5142 | 5.5383 | 5.5623 | 5.5864 | 5.6105 | 5.6346 | 5.6587 | 5.6828 | 5.7069 | 0.44201 | 0.43695 | 0.43237 | 0.42548 | 0.41992 | 0.41307 | 0.41053 | 0.40575 | 0.39803 | 0.39979 | 0.40155 | 0.40331 | 0.40507 | 0.40684 | 0.4086 | 0.41036 | 0.41212 | 0.41388 | 0.41564 | 0.41741 | 27985.8037 | 3928.7266 | 168061.5966 | 23592.9644 | 2882921.3594 | 2882921.3594 | 10369183.5244 | 2882921.3594
| SHL001-155492469 | 0 | SHL001 | SHL | North | 0 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27985.8037 | 3928.7266 | 0 | 0 | 0 | 0 | 0 | 0
| SHL001-160435720 | 41 | SHL001 | SHL | North | 966219.3739 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.038435 | 0.03877 | 0.039104 | 0.039439 | 0.039774 | 0.039949 | 0.040125 | 0.0403 | 0.040476 | 0.040651 | 0.040827 | 0.041002 | 0.041178 | 0.041354 | 0.041529 | 0.041705 | 0.04188 | 0.042056 | 0.042231 | 0.042407 | 0.0032946 | 0.0032554 | 0.0032198 | 0.0031671 | 0.0031244 | 0.0030731 | 0.003054 | 0.0030181 | 0.0029604 | 0.0029733 | 0.0029861 | 0.002999 | 0.0030118 | 0.0030246 | 0.0030375 | 0.0030503 | 0.0030632 | 0.003076 | 0.0030888 | 0.0031017 | 27985.8037 | 3928.7266 | 1250.293 | 175.5197 | 29731.8173 | 29731.8173 | 966219.3739 | 29731.8173
| SHL001-160435873 | 118 | SHL001 | SHL | North | 2780826.4906 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.1666 | 0.16803 | 0.16945 | 0.17087 | 0.17229 | 0.17319 | 0.17409 | 0.17499 | 0.17589 | 0.17679 | 0.17769 | 0.17859 | 0.17949 | 0.18039 | 0.18129 | 0.18219 | 0.1831 | 0.184 | 0.1849 | 0.1858 | 0.014281 | 0.014109 | 0.013952 | 0.013722 | 0.013534 | 0.013323 | 0.013251 | 0.013106 | 0.012865 | 0.012931 | 0.012997 | 0.013063 | 0.013128 | 0.013194 | 0.01326 | 0.013326 | 0.013392 | 0.013458 | 0.013523 | 0.013589 | 27985.8037 | 3928.7266 | 5437.5059 | 763.3325 | 220992.3713 | 220992.3713 | 2780826.4906 | 220992.3713
| SHL001-160436010 | 118 | SHL001 | SHL | North | 2780826.4906 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.14706 | 0.14853 | 0.15 | 0.15148 | 0.15295 | 0.15365 | 0.15434 | 0.15504 | 0.15574 | 0.15644 | 0.15714 | 0.15784 | 0.15854 | 0.15924 | 0.15994 | 0.16063 | 0.16133 | 0.16203 | 0.16273 | 0.16343 | 0.012606 | 0.012472 | 0.012351 | 0.012164 | 0.012015 | 0.011819 | 0.011748 | 0.011611 | 0.011391 | 0.011442 | 0.011493 | 0.011545 | 0.011596 | 0.011647 | 0.011698 | 0.011749 | 0.0118 | 0.011851 | 0.011902 | 0.011953 | 27985.8037 | 3928.7266 | 4807.3356 | 674.8674 | 231552.5328 | 231552.5328 | 2780826.4906 | 231552.5328
| SHL001-160450736 | 34 | SHL001 | SHL | North | 801255.0905 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.00033358 | 0.00033674 | 0.00033989 | 0.00034305 | 0.0003462 | 0.00034683 | 0.00034746 | 0.00034809 | 0.00034872 | 0.00034935 | 0.00034998 | 0.00035061 | 0.00035124 | 0.00035187 | 0.0003525 | 0.00035313 | 0.00035376 | 0.00035439 | 0.00035502 | 0.00035565 | 2.8594e-05 | 2.8275e-05 | 2.7987e-05 | 2.7548e-05 | 2.7196e-05 | 2.668e-05 | 2.6446e-05 | 2.6069e-05 | 2.5506e-05 | 2.5552e-05 | 2.5598e-05 | 2.5644e-05 | 2.569e-05 | 2.5736e-05 | 2.5782e-05 | 2.5828e-05 | 2.5874e-05 | 2.592e-05 | 2.5967e-05 | 2.6013e-05 | 27985.8037 | 3928.7266 | 10.7437 | 1.5082 | 670.5803 | 670.5803 | 801255.0905 | 670.5803
| SHL001-160450820 | 32 | SHL001 | SHL | North | 754122.4381 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0024001 | 0.0024234 | 0.0024467 | 0.00247 | 0.0024933 | 0.0024964 | 0.0024995 | 0.0025026 | 0.0025056 | 0.0025087 | 0.0025118 | 0.0025149 | 0.002518 | 0.0025211 | 0.0025242 | 0.0025273 | 0.0025304 | 0.0025335 | 0.0025366 | 0.0025396 | 0.00020573 | 0.00020349 | 0.00020146 | 0.00019835 | 0.00019586 | 0.00019204 | 0.00019024 | 0.00018742 | 0.00018327 | 0.00018349 | 0.00018372 | 0.00018394 | 0.00018417 | 0.0001844 | 0.00018462 | 0.00018485 | 0.00018507 | 0.0001853 | 0.00018553 | 0.00018575 | 27985.8037 | 3928.7266 | 77.146 | 10.83 | 3884.0941 | 3884.0941 | 754122.4381 | 3884.0941
| SHL001-160491672 | 32 | SHL001 | SHL | North | 754122.4381 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.053306 | 0.053326 | 0.053345 | 0.053365 | 0.053384 | 0.053369 | 0.053354 | 0.053339 | 0.053324 | 0.053308 | 0.053293 | 0.053278 | 0.053263 | 0.053248 | 0.053232 | 0.053217 | 0.053202 | 0.053187 | 0.053172 | 0.053156 | 0.0045693 | 0.0044776 | 0.0043924 | 0.0042854 | 0.0041936 | 0.0041055 | 0.0040609 | 0.0039946 | 0.0039001 | 0.003899 | 0.0038979 | 0.0038968 | 0.0038957 | 0.0038946 | 0.0038935 | 0.0038924 | 0.0038913 | 0.0038901 | 0.003889 | 0.0038879 | 27985.8037 | 3928.7266 | 1650.3811 | 231.6852 | 38741.4438 | 38741.4438 | 754122.4381 | 38741.4438
| SHL001-160682032 | 32 | SHL001 | SHL | North | 754122.4381 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.045042 | 0.04542 | 0.045798 | 0.046176 | 0.046553 | 0.046786 | 0.047019 | 0.047252 | 0.047484 | 0.047717 | 0.04795 | 0.048183 | 0.048415 | 0.048648 | 0.048881 | 0.049114 | 0.049346 | 0.049579 | 0.049812 | 0.050045 | 0.0038609 | 0.0038138 | 0.003771 | 0.0037081 | 0.003657 | 0.0035991 | 0.0035787 | 0.0035387 | 0.0034731 | 0.0034901 | 0.0035071 | 0.0035241 | 0.0035412 | 0.0035582 | 0.0035752 | 0.0035922 | 0.0036092 | 0.0036263 | 0.0036433 | 0.0036603 | 27985.8037 | 3928.7266 | 1467.7885 | 206.0523 | 28758.2895 | 28758.2895 | 754122.4381 | 28758.2895
| SHL001-162130935 | 22 | SHL001 | SHL | North | 518459.1762 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.00012428 | 0.00012538 | 0.00012649 | 0.00012759 | 0.0001287 | 0.00012939 | 0.00013008 | 0.00013077 | 0.00013146 | 0.00013215 | 0.00013284 | 0.00013353 | 0.00013422 | 0.00013491 | 0.0001356 | 0.00013629 | 0.00013698 | 0.00013767 | 0.00013836 | 0.00013905 | 1.0653e-05 | 1.0528e-05 | 1.0415e-05 | 1.0246e-05 | 1.011e-05 | 9.9535e-06 | 9.9007e-06 | 9.7935e-06 | 9.6151e-06 | 9.6656e-06 | 9.7161e-06 | 9.7665e-06 | 9.817e-06 | 9.8675e-06 | 9.9179e-06 | 9.9684e-06 | 1.0019e-05 | 1.0069e-05 | 1.012e-05 | 1.017e-05 | 27985.8037 | 3928.7266 | 4.0634 | 0.57043 | 328.4387 | 328.4387 | 518459.1762 | 328.4387
| SHL001-162641927 | 22 | SHL001 | SHL | North | 518459.1762 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.00022535 | 0.00022761 | 0.00022987 | 0.00023214 | 0.0002344 | 0.00023504 | 0.00023568 | 0.00023632 | 0.00023696 | 0.0002376 | 0.00023824 | 0.00023888 | 0.00023952 | 0.00024016 | 0.0002408 | 0.00024144 | 0.00024208 | 0.00024272 | 0.00024336 | 0.000244 | 1.9316e-05 | 1.9112e-05 | 1.8928e-05 | 1.8642e-05 | 1.8413e-05 | 1.8081e-05 | 1.7938e-05 | 1.7698e-05 | 1.7332e-05 | 1.7378e-05 | 1.7425e-05 | 1.7472e-05 | 1.7519e-05 | 1.7566e-05 | 1.7612e-05 | 1.7659e-05 | 1.7706e-05 | 1.7753e-05 | 1.78e-05 | 1.7846e-05 | 27985.8037 | 3928.7266 | 7.3031 | 1.0252 | 442.5253 | 442.5253 | 518459.1762 | 442.5253
| SHL001-162662602 | 64 | SHL001 | SHL | North | 1508244.8763 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.036518 | 0.036835 | 0.037152 | 0.037468 | 0.037785 | 0.037967 | 0.038149 | 0.038331 | 0.038513 | 0.038695 | 0.038877 | 0.039059 | 0.039241 | 0.039423 | 0.039605 | 0.039787 | 0.039969 | 0.040151 | 0.040333 | 0.040515 | 0.0031303 | 0.003093 | 0.003059 | 0.0030089 | 0.0029682 | 0.0029206 | 0.0029036 | 0.0028706 | 0.0028169 | 0.0028302 | 0.0028435 | 0.0028568 | 0.0028701 | 0.0028834 | 0.0028967 | 0.00291 | 0.0029234 | 0.0029367 | 0.00295 | 0.0029633 | 27985.8037 | 3928.7266 | 1190.0688 | 167.0652 | 64568.7278 | 64568.7278 | 1508244.8763 | 64568.7278
| SHL001-162662856 | 67 | SHL001 | SHL | North | 1578943.8548 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.089098 | 0.089939 | 0.09078 | 0.091622 | 0.092463 | 0.092651 | 0.092839 | 0.093027 | 0.093215 | 0.093403 | 0.093591 | 0.093779 | 0.093967 | 0.094155 | 0.094343 | 0.094531 | 0.094719 | 0.094907 | 0.095095 | 0.095283 | 0.0076373 | 0.007552 | 0.0074748 | 0.0073576 | 0.0072634 | 0.0071273 | 0.0070662 | 0.0069669 | 0.0068178 | 0.0068316 | 0.0068454 | 0.0068591 | 0.0068729 | 0.0068866 | 0.0069004 | 0.0069141 | 0.0069279 | 0.0069416 | 0.0069554 | 0.0069691 | 27985.8037 | 3928.7266 | 2872.3879 | 403.234 | 132491.0331 | 132491.0331 | 1578943.8548 | 132491.0331
| SHL001-162663030 | 14 | SHL001 | SHL | North | 329928.5667 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.013226 | 0.013348 | 0.013469 | 0.013591 | 0.013712 | 0.01375 | 0.013787 | 0.013824 | 0.013861 | 0.013898 | 0.013935 | 0.013973 | 0.01401 | 0.014047 | 0.014084 | 0.014121 | 0.014158 | 0.014196 | 0.014233 | 0.01427 | 0.0011337 | 0.0011208 | 0.0011091 | 0.0010914 | 0.0010772 | 0.0010577 | 0.0010493 | 0.0010353 | 0.0010138 | 0.0010165 | 0.0010192 | 0.001022 | 0.0010247 | 0.0010274 | 0.0010301 | 0.0010328 | 0.0010356 | 0.0010383 | 0.001041 | 0.0010437 | 27985.8037 | 3928.7266 | 427.4352 | 60.0046 | 13184.7051 | 13184.7051 | 329928.5667 | 13184.7051
| SHL001-162760066 | 13 | SHL001 | SHL | North | 306362.2405 | 0.0030789 | 0.0030161 | 0.0029576 | 0.0028845 | 0.0028216 | 0.0027632 | 0.0027339 | 0.0026901 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0.0026272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27985.8037 | 3928.7266 | 0 | 0 | 795.3876 | 795.3876 | 306362.2405 | 795.3876
| SHL002-15428854 | 98 | SHL002 | SHL | North | 2309499.9668 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 3.9279 | 3.9594 | 3.9909 | 4.0224 | 4.054 | 4.0639 | 4.0738 | 4.0837 | 4.0936 | 4.1035 | 4.1134 | 4.1234 | 4.1333 | 4.1432 | 4.1531 | 4.163 | 4.1729 | 4.1829 | 4.1928 | 4.2027 | 0.58775 | 0.5911 | 0.58974 | 0.58585 | 0.5789 | 0.5708 | 0.56768 | 0.56784 | 0.56019 | 0.56155 | 0.56291 | 0.56426 | 0.56562 | 0.56698 | 0.56834 | 0.56969 | 0.57105 | 0.57241 | 0.57376 | 0.57512 | 27985.8037 | 3928.7266 | 232125.7501 | 32586.4723 | 177284.6474 | 177284.6474 | 2309499.9668 | 177284.6474
| SHL002-160491442 | 106 | SHL002 | SHL | North | 2498030.5763 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0096716 | 0.0097587 | 0.0098458 | 0.0099328 | 0.01002 | 0.010023 | 0.010026 | 0.010029 | 0.010032 | 0.010035 | 0.010038 | 0.010041 | 0.010044 | 0.010047 | 0.010049 | 0.010052 | 0.010055 | 0.010058 | 0.010061 | 0.010064 | 0.0014472 | 0.0014569 | 0.0014549 | 0.0014467 | 0.0014308 | 0.0014078 | 0.0013971 | 0.0013945 | 0.0013728 | 0.0013732 | 0.0013736 | 0.001374 | 0.0013744 | 0.0013748 | 0.0013752 | 0.0013756 | 0.001376 | 0.0013764 | 0.0013768 | 0.0013773 | 27985.8037 | 3928.7266 | 567.3676 | 79.6487 | 30031.5635 | 30031.5635 | 2498030.5763 | 30031.5635
| SHL002-160491563 | 62 | SHL002 | SHL | North | 1461112.2239 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0069521 | 0.0070154 | 0.0070788 | 0.0071421 | 0.0072055 | 0.0072168 | 0.0072281 | 0.0072394 | 0.0072507 | 0.007262 | 0.0072733 | 0.0072846 | 0.0072959 | 0.0073071 | 0.0073184 | 0.0073297 | 0.007341 | 0.0073523 | 0.0073636 | 0.0073749 | 0.0010403 | 0.0010473 | 0.001046 | 0.0010402 | 0.0010289 | 0.0010136 | 0.0010072 | 0.0010066 | 0.00099222 | 0.00099377 | 0.00099531 | 0.00099686 | 0.00099841 | 0.00099995 | 0.0010015 | 0.001003 | 0.0010046 | 0.0010061 | 0.0010077 | 0.0010092 | 27985.8037 | 3928.7266 | 410.527 | 57.6309 | 6933.7869 | 6933.7869 | 1461112.2239 | 6933.7869
| SHL002-161866668 | 82 | SHL002 | SHL | North | 1932438.7477 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.011433 | 0.01154 | 0.011648 | 0.011755 | 0.011863 | 0.011884 | 0.011906 | 0.011928 | 0.011949 | 0.011971 | 0.011993 | 0.012014 | 0.012036 | 0.012057 | 0.012079 | 0.012101 | 0.012122 | 0.012144 | 0.012165 | 0.012187 | 0.0017107 | 0.0017229 | 0.0017212 | 0.0017121 | 0.001694 | 0.0016693 | 0.0016591 | 0.0016586 | 0.0016352 | 0.0016382 | 0.0016411 | 0.0016441 | 0.001647 | 0.00165 | 0.001653 | 0.0016559 | 0.0016589 | 0.0016618 | 0.0016648 | 0.0016677 | 27985.8037 | 3928.7266 | 676.5885 | 94.9814 | 12315.5218 | 12315.5218 | 1932438.7477 | 12315.5218
| SHL002-162436238 | 59 | SHL002 | SHL | North | 1390413.2453 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.00050214 | 0.00050686 | 0.00051157 | 0.00051629 | 0.000521 | 0.0005219 | 0.0005228 | 0.0005237 | 0.0005246 | 0.0005255 | 0.0005264 | 0.0005273 | 0.0005282 | 0.0005291 | 0.00053 | 0.0005309 | 0.0005318 | 0.0005327 | 0.0005336 | 0.0005345 | 7.5138e-05 | 7.5669e-05 | 7.5596e-05 | 7.5195e-05 | 7.4399e-05 | 7.3305e-05 | 7.2851e-05 | 7.2821e-05 | 7.1789e-05 | 7.1912e-05 | 7.2036e-05 | 7.2159e-05 | 7.2282e-05 | 7.2405e-05 | 7.2528e-05 | 7.2651e-05 | 7.2775e-05 | 7.2898e-05 | 7.3021e-05 | 7.3144e-05 | 27985.8037 | 3928.7266 | 29.7015 | 4.1696 | 1050.2746 | 1050.2746 | 1390413.2453 | 1050.2746
| SHL002-162436334 | 87 | SHL002 | SHL | North | 2050270.3787 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0044089 | 0.0044466 | 0.0044844 | 0.0045222 | 0.0045599 | 0.0045674 | 0.0045749 | 0.0045824 | 0.0045899 | 0.0045974 | 0.0046049 | 0.0046124 | 0.00462 | 0.0046275 | 0.004635 | 0.0046425 | 0.00465 | 0.0046575 | 0.004665 | 0.0046725 | 0.00065972 | 0.00066385 | 0.00066267 | 0.00065863 | 0.00065116 | 0.00064153 | 0.00063751 | 0.00063719 | 0.00062811 | 0.00062914 | 0.00063017 | 0.00063119 | 0.00063222 | 0.00063325 | 0.00063428 | 0.0006353 | 0.00063633 | 0.00063736 | 0.00063838 | 0.00063941 | 27985.8037 | 3928.7266 | 259.9895 | 36.4981 | 9682.8318 | 9682.8318 | 2050270.3787 | 9682.8318
| SHL002-162436442 | 5 | SHL002 | SHL | North | 117831.631 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.00031445 | 0.0003174 | 0.00032034 | 0.00032328 | 0.00032623 | 0.00032601 | 0.0003258 | 0.00032558 | 0.00032537 | 0.00032515 | 0.00032494 | 0.00032472 | 0.00032451 | 0.0003243 | 0.00032408 | 0.00032387 | 0.00032365 | 0.00032344 | 0.00032322 | 0.00032301 | 4.7053e-05 | 4.7384e-05 | 4.7337e-05 | 4.7085e-05 | 4.6585e-05 | 4.5791e-05 | 4.5399e-05 | 4.5273e-05 | 4.4525e-05 | 4.4496e-05 | 4.4467e-05 | 4.4437e-05 | 4.4408e-05 | 4.4378e-05 | 4.4349e-05 | 4.432e-05 | 4.429e-05 | 4.4261e-05 | 4.4232e-05 | 4.4202e-05 | 27985.8037 | 3928.7266 | 18.3814 | 2.5804 | 183.556 | 183.556 | 117831.631 | 183.556
| SHL002-162485158 | 11 | SHL002 | SHL | North | 259229.5881 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27985.8037 | 3928.7266 | 0 | 0 | 0 | 0 | 259229.5881 | 0
| SHL002-24604026 | 112 | SHL002 | SHL | North | 2639428.5335 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 11.7285 | 11.8276 | 11.9267 | 12.0258 | 12.1249 | 12.1467 | 12.1685 | 12.1903 | 12.2121 | 12.2339 | 12.2557 | 12.2775 | 12.2993 | 12.3211 | 12.3429 | 12.3647 | 12.3865 | 12.4083 | 12.4301 | 12.4519 | 1.755 | 1.7658 | 1.7624 | 1.7515 | 1.7314 | 1.7061 | 1.6957 | 1.6951 | 1.6712 | 1.6742 | 1.6771 | 1.6801 | 1.6831 | 1.6861 | 1.6891 | 1.6921 | 1.695 | 1.698 | 1.701 | 1.704 | 27985.8037 | 3928.7266 | 691883.4859 | 97128.5693 | 464586.7521 | 464586.7521 | 2639428.5335 | 464586.7521
| SHL002-24604040 | 34 | SHL002 | SHL | North | 801255.0905 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 1.8144 | 1.8288 | 1.8432 | 1.8575 | 1.8719 | 1.8731 | 1.8742 | 1.8754 | 1.8765 | 1.8777 | 1.8788 | 1.88 | 1.8811 | 1.8823 | 1.8834 | 1.8846 | 1.8857 | 1.8868 | 1.888 | 1.8891 | 0.2715 | 0.27302 | 0.27237 | 0.27054 | 0.26731 | 0.26308 | 0.26117 | 0.26077 | 0.25679 | 0.25695 | 0.25711 | 0.25726 | 0.25742 | 0.25758 | 0.25774 | 0.25789 | 0.25805 | 0.25821 | 0.25836 | 0.25852 | 27985.8037 | 3928.7266 | 106236.1005 | 14913.7256 | 83143.602 | 83143.602 | 801255.0905 | 83143.602
| SHL002-24614570 | 130 | SHL002 | SHL | North | 3063622.4049 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 4.2051 | 4.2272 | 4.2493 | 4.2714 | 4.2935 | 4.2852 | 4.2769 | 4.2686 | 4.2603 | 4.252 | 4.2437 | 4.2354 | 4.2271 | 4.2188 | 4.2105 | 4.2022 | 4.1939 | 4.1855 | 4.1772 | 4.1689 | 0.62923 | 0.63108 | 0.62793 | 0.62211 | 0.61311 | 0.60189 | 0.59598 | 0.59355 | 0.583 | 0.58187 | 0.58073 | 0.57959 | 0.57846 | 0.57732 | 0.57618 | 0.57505 | 0.57391 | 0.57277 | 0.57164 | 0.5705 | 27985.8037 | 3928.7266 | 241052.0763 | 33839.5753 | 877146.3873 | 877146.3873 | 3063622.4049 | 877146.3873
| SHL002-42163201 | 50 | SHL002 | SHL | North | 1178316.3096 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27985.8037 | 3928.7266 | 0 | 0 | 0 | 0 | 1178316.3096 | 0
| SHL002-54520142 | 181 | SHL002 | SHL | North | 4265505.0407 | 0.0053748 | 0.0053625 | 0.0053079 | 0.0052315 | 0.0051293 | 0.0050452 | 0.0050053 | 0.0049947 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.0049154 | 0.25346 | 0.25354 | 0.25361 | 0.25369 | 0.25376 | 0.25371 | 0.25365 | 0.25359 | 0.25353 | 0.25347 | 0.25341 | 0.25335 | 0.2533 | 0.25324 | 0.25318 | 0.25312 | 0.25306 | 0.253 | 0.25294 | 0.25289 | 0.037927 | 0.037851 | 0.037477 | 0.036949 | 0.036237 | 0.035635 | 0.035345 | 0.035262 | 0.034694 | 0.034686 | 0.034678 | 0.03467 | 0.034662 | 0.034654 | 0.034646 | 0.034638 | 0.03463 | 0.034622 | 0.034614 | 0.034606 | 27985.8037 | 3928.7266 | 14416.2503 | 2023.7942 | 185321.419 | 185321.419 | 4265505.0407 | 185321.419
| SHL004-15428865 | 187 | SHL004 | SHL | North | 4406902.9979 | 0.0029304 | 0.0029304 | 0.0029085 | 0.002875 | 0.0028242 | 0.0027825 | 0.002771 | 0.0027689 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 5.8017 | 5.8514 | 5.901 | 5.9506 | 6.0003 | 6.0189 | 6.0375 | 6.0561 | 6.0747 | 6.0934 | 6.112 | 6.1306 | 6.1492 | 6.1679 | 6.1865 | 6.2051 | 6.2237 | 6.2424 | 6.261 | 6.2796 | 0.47332 | 0.47737 | 0.47781 | 0.4763 | 0.47178 | 0.46624 | 0.46576 | 0.46684 | 0.4618 | 0.46322 | 0.46463 | 0.46605 | 0.46746 | 0.46888 | 0.4703 | 0.47171 | 0.47313 | 0.47454 | 0.47596 | 0.47737 | 27985.8037 | 3928.7266 | 190412.72 | 26730.6786 | 333791.222 | 333791.222 | 4406902.9979 | 333791.222
| SHL004-24604082 | 341 | SHL004 | SHL | North | 8036117.2314 | 0.0029304 | 0.0029304 | 0.0029085 | 0.002875 | 0.0028242 | 0.0027825 | 0.002771 | 0.0027689 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 12.548 | 12.665 | 12.782 | 12.899 | 13.016 | 13.0206 | 13.0253 | 13.03 | 13.0347 | 13.0394 | 13.044 | 13.0487 | 13.0534 | 13.0581 | 13.0628 | 13.0674 | 13.0721 | 13.0768 | 13.0815 | 13.0861 | 1.0237 | 1.0332 | 1.035 | 1.0324 | 1.0234 | 1.0086 | 1.0048 | 1.0044 | 0.99089 | 0.99125 | 0.9916 | 0.99196 | 0.99232 | 0.99267 | 0.99303 | 0.99338 | 0.99374 | 0.99409 | 0.99445 | 0.99481 | 27985.8037 | 3928.7266 | 407324.5617 | 57181.3791 | 2656392.3273 | 2656392.3273 | 8036117.2314 | 2656392.3273
| SHL004-24612892 | 229 | SHL004 | SHL | North | 5396688.6979 | 0.0029304 | 0.0029304 | 0.0029085 | 0.002875 | 0.0028242 | 0.0027825 | 0.002771 | 0.0027689 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 0.0027306 | 5.9086 | 5.9562 | 6.0038 | 6.0514 | 6.099 | 6.1048 | 6.1106 | 6.1165 | 6.1223 | 6.1281 | 6.1339 | 6.1397 | 6.1455 | 6.1513 | 6.1571 | 6.1629 | 6.1687 | 6.1745 | 6.1803 | 6.1861 | 0.48204 | 0.48592 | 0.48614 | 0.48436 | 0.47955 | 0.4729 | 0.4714 | 0.47149 | 0.46541 | 0.46585 | 0.46629 | 0.46674 | 0.46718 | 0.46762 | 0.46806 | 0.4685 | 0.46894 | 0.46938 | 0.46982 | 0.47026 | 27985.8037 | 3928.7266 | 191578.9711 | 26894.4002 | 1289280.0786 | 1289280.0786 | 5396688.6979 | 1289280.0786
| SHL005-15428600 | 1 | SHL005 | SHL | North | 23566.3262 | 0.0016944 | 0.0016931 | 0.0016843 | 0.0016729 | 0.0016467 | 0.0016292 | 0.0016261 | 0.0016292 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0027172 | 0.0027421 | 0.0027669 | 0.0027918 | 0.0028166 | 0.0028295 | 0.0028423 | 0.0028552 | 0.002868 | 0.0028809 | 0.0028937 | 0.0029065 | 0.0029194 | 0.0029322 | 0.0029451 | 0.0029579 | 0.0029708 | 0.0029836 | 0.0029965 | 0.0030093 | 0.00012818 | 0.00012925 | 0.00012975 | 0.00013003 | 0.00012912 | 0.00012833 | 0.00012867 | 0.0001295 | 0.00012833 | 0.00012891 | 0.00012948 | 0.00013006 | 0.00013063 | 0.00013121 | 0.00013178 | 0.00013236 | 0.00013293 | 0.00013351 | 0.00013408 | 0.00013466 | 27985.8037 | 3928.7266 | 52.6909 | 7.3969 | 65.0779 | 65.0779 | 23566.3262 | 65.0779
| SHL005-15428613 | 125 | SHL005 | SHL | North | 2945790.774 | 0.0016944 | 0.0016931 | 0.0016843 | 0.0016729 | 0.0016467 | 0.0016292 | 0.0016261 | 0.0016292 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 12.1134 | 12.2082 | 12.3031 | 12.398 | 12.4929 | 12.5358 | 12.5787 | 12.6216 | 12.6645 | 12.7074 | 12.7503 | 12.7931 | 12.836 | 12.8789 | 12.9218 | 12.9647 | 13.0076 | 13.0505 | 13.0934 | 13.1363 | 0.57141 | 0.57544 | 0.57691 | 0.57743 | 0.57272 | 0.56857 | 0.56944 | 0.57246 | 0.56669 | 0.56861 | 0.57053 | 0.57245 | 0.57437 | 0.57629 | 0.5782 | 0.58012 | 0.58204 | 0.58396 | 0.58588 | 0.5878 | 27985.8037 | 3928.7266 | 232616.2307 | 32655.3273 | 553067.9003 | 553067.9003 | 2945790.774 | 553067.9003
| SHL005-15428624 | 0 | SHL005 | SHL | North | 0 | 0.0016944 | 0.0016931 | 0.0016843 | 0.0016729 | 0.0016467 | 0.0016292 | 0.0016261 | 0.0016292 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27985.8037 | 3928.7266 | 0 | 0 | 0 | 0 | 0 | 0
| SHL005-24604390 | 141 | SHL005 | SHL | North | 3322851.993 | 0.0016944 | 0.0016931 | 0.0016843 | 0.0016729 | 0.0016467 | 0.0016292 | 0.0016261 | 0.0016292 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 3.1709 | 3.1969 | 3.2229 | 3.2489 | 3.2749 | 3.2853 | 3.2957 | 3.3061 | 3.3165 | 3.327 | 3.3374 | 3.3478 | 3.3582 | 3.3686 | 3.379 | 3.3894 | 3.3998 | 3.4102 | 3.4207 | 3.4311 | 0.14958 | 0.15069 | 0.15113 | 0.15132 | 0.15013 | 0.14901 | 0.1492 | 0.14995 | 0.1484 | 0.14887 | 0.14933 | 0.1498 | 0.15027 | 0.15073 | 0.1512 | 0.15166 | 0.15213 | 0.1526 | 0.15306 | 0.15353 | 27985.8037 | 3928.7266 | 60888.2963 | 8547.672 | 903601.1756 | 903601.1756 | 3322851.993 | 903601.1756
| SHL005-24613604 | 128 | SHL005 | SHL | North | 3016489.7525 | 0.0016944 | 0.0016931 | 0.0016843 | 0.0016729 | 0.0016467 | 0.0016292 | 0.0016261 | 0.0016292 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 0.0016073 | 2.3804 | 2.4003 | 2.4202 | 2.4401 | 2.46 | 2.471 | 2.482 | 2.493 | 2.504 | 2.515 | 2.5261 | 2.5371 | 2.5481 | 2.5591 | 2.5701 | 2.5811 | 2.5921 | 2.6031 | 2.6141 | 2.6252 | 0.11229 | 0.11314 | 0.11349 | 0.11365 | 0.11277 | 0.11207 | 0.11236 | 0.11307 | 0.11205 | 0.11254 | 0.11303 | 0.11352 | 0.11402 | 0.11451 | 0.115 | 0.1155 | 0.11599 | 0.11648 | 0.11697 | 0.11747 | 27985.8037 | 3928.7266 | 46022.8602 | 6460.8199 | 452841.0848 | 452841.0848 | 3016489.7525 | 452841.0848
| SHL007-15428576 | 89 | SHL007 | SHL | North | 2097403.0311 | 0.0020408 | 0.0020255 | 0.0019988 | 0.0019697 | 0.0019326 | 0.0019027 | 0.001885 | 0.0018712 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.81156 | 0.81956 | 0.82757 | 0.83558 | 0.84359 | 0.84557 | 0.84755 | 0.84953 | 0.85151 | 0.85349 | 0.85548 | 0.85746 | 0.85944 | 0.86142 | 0.8634 | 0.86538 | 0.86736 | 0.86935 | 0.87133 | 0.87331 | 0.046108 | 0.046215 | 0.046051 | 0.04582 | 0.045387 | 0.044791 | 0.044478 | 0.044255 | 0.043749 | 0.043851 | 0.043952 | 0.044054 | 0.044156 | 0.044258 | 0.04436 | 0.044461 | 0.044563 | 0.044665 | 0.044767 | 0.044869 | 27985.8037 | 3928.7266 | 18142.695 | 2546.9231 | 12481.8352 | 12481.8352 | 2097403.0311 | 12481.8352
| SHL007-181581220 | 61 | SHL007 | SHL | North | 1437545.8977 | 0.0020408 | 0.0020255 | 0.0019988 | 0.0019697 | 0.0019326 | 0.0019027 | 0.001885 | 0.0018712 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0.0018455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27985.8037 | 3928.7266 | 0 | 0 | 0 | 0 | 1437545.8977 | 0
| SHL008-15428954 | 59 | SHL008 | SHL | North | 1390413.2453 | 0.0018087 | 0.0017817 | 0.0017452 | 0.0017073 | 0.0016655 | 0.0016279 | 0.0016174 | 0.0016076 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.31074 | 0.31359 | 0.31644 | 0.31928 | 0.32213 | 0.32359 | 0.32506 | 0.32653 | 0.328 | 0.32946 | 0.33093 | 0.3324 | 0.33387 | 0.33533 | 0.3368 | 0.33827 | 0.33974 | 0.3412 | 0.34267 | 0.34414 | 0.015647 | 0.015555 | 0.015374 | 0.015176 | 0.014937 | 0.014665 | 0.014637 | 0.014614 | 0.014412 | 0.014477 | 0.014541 | 0.014606 | 0.01467 | 0.014734 | 0.014799 | 0.014863 | 0.014928 | 0.014992 | 0.015057 | 0.015121 | 27985.8037 | 3928.7266 | 6036.2396 | 847.3845 | 2563.3391 | 2563.3391 | 1390413.2453 | 2563.3391
| SHL008-181581109 | 124 | SHL008 | SHL | North | 2922224.4478 | 0.0018087 | 0.0017817 | 0.0017452 | 0.0017073 | 0.0016655 | 0.0016279 | 0.0016174 | 0.0016076 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 0.0015783 | 7.3688 | 7.4349 | 7.501 | 7.5671 | 7.6332 | 7.6657 | 7.6982 | 7.7307 | 7.7632 | 7.7957 | 7.8282 | 7.8607 | 7.8932 | 7.9257 | 7.9582 | 7.9907 | 8.0232 | 8.0557 | 8.0882 | 8.1207 | 0.37106 | 0.36879 | 0.36444 | 0.35967 | 0.35394 | 0.34741 | 0.34665 | 0.34598 | 0.34111 | 0.34254 | 0.34397 | 0.3454 | 0.34682 | 0.34825 | 0.34968 | 0.35111 | 0.35254 | 0.35397 | 0.35539 | 0.35682 | 27985.8037 | 3928.7266 | 142850.3177 | 20053.7334 | 221938.3662 | 221938.3662 | 2922224.4478 | 221938.3662
| SHN011-130746986 | 71 | SHN011 | SHN | North | 1673209.1596 | 0.0019182 | 0.0019389 | 0.0019595 | 0.00197 | 0.0019635 | 0.0019663 | 0.0019946 | 0.0020266 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.00035581 | 0.00035968 | 0.00036355 | 0.00036741 | 0.00037128 | 0.00037456 | 0.00037783 | 0.00038111 | 0.00038438 | 0.00038766 | 0.00039094 | 0.00039421 | 0.00039749 | 0.00040076 | 0.00040404 | 0.00040732 | 0.00041059 | 0.00041387 | 0.00041714 | 0.00042042 | 1.9002e-05 | 1.9415e-05 | 1.9833e-05 | 2.0151e-05 | 2.0296e-05 | 2.0504e-05 | 2.0981e-05 | 2.1502e-05 | 2.166e-05 | 2.1844e-05 | 2.2029e-05 | 2.2214e-05 | 2.2398e-05 | 2.2583e-05 | 2.2767e-05 | 2.2952e-05 | 2.3137e-05 | 2.3321e-05 | 2.3506e-05 | 2.3691e-05 | 28088.495 | 3881.5256 | 8.6975 | 1.2019 | 238.9464 | 238.9464 | 1673209.1596 | 238.9464
| SHN011-175612776 | 0 | SHN011 | SHN | North | 0 | 0.0019182 | 0.0019389 | 0.0019595 | 0.00197 | 0.0019635 | 0.0019663 | 0.0019946 | 0.0020266 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28088.495 | 3881.5256 | 0 | 0 | 0 | 0 | 0 | 0
| SHN011-200057131 | 17 | SHN011 | SHN | North | 400627.5453 | 0.0019182 | 0.0019389 | 0.0019595 | 0.00197 | 0.0019635 | 0.0019663 | 0.0019946 | 0.0020266 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28088.495 | 3881.5256 | 0 | 0 | 0 | 0 | 400627.5453 | 0
| SHN011-24605252 | 655 | SHN011 | SHN | North | 15435943.6556 | 0.0019182 | 0.0019389 | 0.0019595 | 0.00197 | 0.0019635 | 0.0019663 | 0.0019946 | 0.0020266 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 22.1274 | 22.2606 | 22.3938 | 22.527 | 22.6602 | 22.7855 | 22.9108 | 23.0362 | 23.1615 | 23.2869 | 23.4122 | 23.5375 | 23.6629 | 23.7882 | 23.9136 | 24.0389 | 24.1642 | 24.2896 | 24.4149 | 24.5403 | 1.1817 | 1.2016 | 1.2217 | 1.2355 | 1.2387 | 1.2473 | 1.2722 | 1.2997 | 1.3051 | 1.3122 | 1.3193 | 1.3263 | 1.3334 | 1.3405 | 1.3475 | 1.3546 | 1.3616 | 1.3687 | 1.3758 | 1.3828 | 28088.495 | 3881.5256 | 523742.8218 | 72375.5815 | 4377620.3544 | 4377620.3544 | 15435943.6556 | 4377620.3544
| SHN011-95830821 | 23 | SHN011 | SHN | North | 542025.5024 | 0.0019182 | 0.0019389 | 0.0019595 | 0.00197 | 0.0019635 | 0.0019663 | 0.0019946 | 0.0020266 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.0020241 | 0.00040073 | 0.00040293 | 0.00040512 | 0.00040731 | 0.0004095 | 0.00041145 | 0.0004134 | 0.00041535 | 0.0004173 | 0.00041925 | 0.0004212 | 0.00042315 | 0.0004251 | 0.00042705 | 0.000429 | 0.00043095 | 0.0004329 | 0.00043485 | 0.0004368 | 0.00043875 | 2.1401e-05 | 2.1749e-05 | 2.2101e-05 | 2.2339e-05 | 2.2385e-05 | 2.2524e-05 | 2.2956e-05 | 2.3434e-05 | 2.3515e-05 | 2.3625e-05 | 2.3734e-05 | 2.3844e-05 | 2.3954e-05 | 2.4064e-05 | 2.4174e-05 | 2.4284e-05 | 2.4394e-05 | 2.4504e-05 | 2.4614e-05 | 2.4723e-05 | 28088.495 | 3881.5256 | 9.4317 | 1.3034 | 251.9056 | 251.9056 | 542025.5024 | 251.9056
| SHN012-200057355 | 77 | SHN012 | SHN | North | 1814607.1168 | 0.0015455 | 0.0015811 | 0.0015958 | 0.0016067 | 0.0016078 | 0.0016142 | 0.0016309 | 0.0016529 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28088.495 | 3881.5256 | 0 | 0 | 0 | 0 | 1814607.1168 | 0
| SHN012-24613290 | 45 | SHN012 | SHN | North | 1060484.6786 | 0.0015455 | 0.0015811 | 0.0015958 | 0.0016067 | 0.0016078 | 0.0016142 | 0.0016309 | 0.0016529 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 0.0016573 | 3.7218 | 3.7453 | 3.7689 | 3.7924 | 3.816 | 3.8432 | 3.8704 | 3.8976 | 3.9248 | 3.952 | 3.9792 | 4.0064 | 4.0336 | 4.0608 | 4.088 | 4.1152 | 4.1424 | 4.1696 | 4.1968 | 4.224 | 0.16014 | 0.16486 | 0.16744 | 0.16963 | 0.17081 | 0.17271 | 0.17574 | 0.17935 | 0.18109 | 0.18235 | 0.1836 | 0.18486 | 0.18611 | 0.18737 | 0.18862 | 0.18988 | 0.19113 | 0.19239 | 0.19364 | 0.1949 | 28088.495 | 3881.5256 | 72638.109 | 10037.7994 | 47647.8488 | 47647.8488 | 1060484.6786 | 47647.8488
| SHN014-15423299 | 0 | SHN014 | SHN | North | 0 | 0.0068732 | 0.0069479 | 0.0069901 | 0.0069944 | 0.0069479 | 0.0069338 | 0.0070085 | 0.0070972 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28088.495 | 3881.5256 | 0 | 0 | 0 | 0 | 0 | 0
| SHN014-200219171 | 65 | SHN014 | SHN | North | 1531811.2025 | 0.0068732 | 0.0069479 | 0.0069901 | 0.0069944 | 0.0069479 | 0.0069338 | 0.0070085 | 0.0070972 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0.0070648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28088.495 | 3881.5256 | 0 | 0 | 0 | 0 | 1531811.2025 | 0
| SHN021-15423325 | 0 | SHN021 | SHN | North | 0 | 0.0014496 | 0.0014735 | 0.0014879 | 0.0015003 | 0.0015024 | 0.0015106 | 0.0015312 | 0.0015516 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28088.495 | 3881.5256 | 0 | 0 | 0 | 0 | 0 | 0
| SHN021-200219341 | 177 | SHN021 | SHN | North | 4171239.7359 | 0.0014496 | 0.0014735 | 0.0014879 | 0.0015003 | 0.0015024 | 0.0015106 | 0.0015312 | 0.0015516 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 0.0015605 | 51.5238 | 51.7391 | 51.9545 | 52.1699 | 52.3853 | 52.4873 | 52.5894 | 52.6914 | 52.7935 | 52.8955 | 52.9976 | 53.0996 | 53.2017 | 53.3037 | 53.4057 | 53.5078 | 53.6098 | 53.7119 | 53.8139 | 53.916 | 2.0794 | 2.1225 | 2.1522 | 2.1791 | 2.1911 | 2.2074 | 2.2418 | 2.2761 | 2.2935 | 2.298 | 2.3024 | 2.3068 | 2.3113 | 2.3157 | 2.3201 | 2.3246 | 2.329 | 2.3334 | 2.3379 | 2.3423 | 28088.495 | 3881.5256 | 913233.6505 | 126198.9927 | 1314261.9362 | 1314261.9362 | 4171239.7359 | 1314261.9362
| SHN022-200219453 | 96 | SHN022 | SHN | North | 2262367.3144 | 0.00087862 | 0.00091394 | 0.00091394 | 0.00091209 | 0.00090677 | 0.00090598 | 0.00090943 | 0.00091474 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0.00091288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28088.495 | 3881.5256 | 0 | 0 | 0 | 0 | 2262367.3144 | 0
| SHN023-200219561 | 33 | SHN023 | SHN | North | 777688.7643 | 0.0020638 | 0.0020589 | 0.0020369 | 0.002009 | 0.0020115 | 0.0020464 | 0.0020963 | 0.0021377 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.0021476 | 0.50556 | 0.5084 | 0.51124 | 0.51408 | 0.51692 | 0.51795 | 0.51898 | 0.52001 | 0.52104 | 0.52207 | 0.52309 | 0.52412 | 0.52515 | 0.52618 | 0.52721 | 0.52824 | 0.52927 | 0.5303 | 0.53133 | 0.53236 | 0.029048 | 0.029141 | 0.028991 | 0.028752 | 0.028947 | 0.029508 | 0.030287 | 0.030947 | 0.031153 | 0.031214 | 0.031276 | 0.031337 | 0.031399 | 0.03146 | 0.031522 | 0.031583 | 0.031645 | 0.031707 | 0.031768 | 0.03183 | 28088.495 | 3881.5256 | 12375.3422 | 1710.1382 | 5832.1878 | 5832.1878 | 777688.7643 | 5832.1878
| SHN024-159278517 | 35 | SHN024 | SHN | North | 824821.4167 | 0.0029278 | 0.0029772 | 0.0030186 | 0.0030447 | 0.0030461 | 0.0030648 | 0.0031202 | 0.0031836 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 8.9759e-05 | 9.0377e-05 | 9.0995e-05 | 9.1612e-05 | 9.223e-05 | 9.338e-05 | 9.453e-05 | 9.568e-05 | 9.683e-05 | 9.798e-05 | 9.913e-05 | 0.00010028 | 0.00010143 | 0.00010258 | 0.00010373 | 0.00010488 | 0.00010603 | 0.00010718 | 0.00010833 | 0.00010948 | 7.3162e-06 | 7.4908e-06 | 7.6471e-06 | 7.7656e-06 | 7.8215e-06 | 7.9675e-06 | 8.2115e-06 | 8.4802e-06 | 8.5495e-06 | 8.6511e-06 | 8.7526e-06 | 8.8541e-06 | 8.9557e-06 | 9.0572e-06 | 9.1587e-06 | 9.2603e-06 | 9.3618e-06 | 9.4634e-06 | 9.5649e-06 | 9.6664e-06 | 28088.495 | 3881.5256 | 3.4354 | 0.47474 | 50.6079 | 50.6079 | 824821.4167 | 50.6079
| SHN024-160253686 | 22 | SHN024 | SHN | North | 518459.1762 | 0.0029278 | 0.0029772 | 0.0030186 | 0.0030447 | 0.0030461 | 0.0030648 | 0.0031202 | 0.0031836 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 4.9817e-06 | 5.0263e-06 | 5.0709e-06 | 5.1154e-06 | 5.16e-06 | 5.2095e-06 | 5.259e-06 | 5.3085e-06 | 5.358e-06 | 5.4075e-06 | 5.457e-06 | 5.5065e-06 | 5.556e-06 | 5.6055e-06 | 5.655e-06 | 5.7045e-06 | 5.754e-06 | 5.8035e-06 | 5.853e-06 | 5.9025e-06 | 4.0606e-07 | 4.166e-07 | 4.2615e-07 | 4.3361e-07 | 4.3759e-07 | 4.4449e-07 | 4.5683e-07 | 4.705e-07 | 4.7308e-07 | 4.7745e-07 | 4.8182e-07 | 4.8619e-07 | 4.9056e-07 | 4.9493e-07 | 4.993e-07 | 5.0367e-07 | 5.0804e-07 | 5.1241e-07 | 5.1679e-07 | 5.2116e-07 | 28088.495 | 3881.5256 | 0.18931 | 0.026161 | 4.0325 | 4.0325 | 518459.1762 | 4.0325
| SHN024-164487380 | 12 | SHN024 | SHN | North | 282795.9143 | 0.0029278 | 0.0029772 | 0.0030186 | 0.0030447 | 0.0030461 | 0.0030648 | 0.0031202 | 0.0031836 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 1.5687e-05 | 1.5816e-05 | 1.5944e-05 | 1.6072e-05 | 1.62e-05 | 1.6365e-05 | 1.653e-05 | 1.6695e-05 | 1.686e-05 | 1.7025e-05 | 1.719e-05 | 1.7355e-05 | 1.752e-05 | 1.7685e-05 | 1.785e-05 | 1.8015e-05 | 1.818e-05 | 1.8345e-05 | 1.851e-05 | 1.8675e-05 | 1.2787e-06 | 1.3109e-06 | 1.3399e-06 | 1.3623e-06 | 1.3738e-06 | 1.3963e-06 | 1.4359e-06 | 1.4797e-06 | 1.4886e-06 | 1.5032e-06 | 1.5178e-06 | 1.5323e-06 | 1.5469e-06 | 1.5615e-06 | 1.576e-06 | 1.5906e-06 | 1.6052e-06 | 1.6198e-06 | 1.6343e-06 | 1.6489e-06 | 28088.495 | 3881.5256 | 0.59633 | 0.082406 | 4.619 | 4.619 | 282795.9143 | 4.619
| SHN024-200219667 | 177 | SHN024 | SHN | North | 4171239.7359 | 0.0029278 | 0.0029772 | 0.0030186 | 0.0030447 | 0.0030461 | 0.0030648 | 0.0031202 | 0.0031836 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.97048 | 0.97549 | 0.9805 | 0.9855 | 0.99051 | 0.99739 | 1.0043 | 1.0112 | 1.018 | 1.0249 | 1.0318 | 1.0387 | 1.0456 | 1.0525 | 1.0593 | 1.0662 | 1.0731 | 1.08 | 1.0869 | 1.0938 | 0.079103 | 0.080853 | 0.0824 | 0.083536 | 0.083999 | 0.085101 | 0.087238 | 0.089621 | 0.089887 | 0.090495 | 0.091103 | 0.091711 | 0.092319 | 0.092926 | 0.093534 | 0.094142 | 0.09475 | 0.095358 | 0.095966 | 0.096573 | 28088.495 | 3881.5256 | 35946.8689 | 4967.4677 | 64193.3066 | 64193.3066 | 4171239.7359 | 64193.3066
| SHN024-24605390 | 152 | SHN024 | SHN | North | 3582081.5812 | 0.0029278 | 0.0029772 | 0.0030186 | 0.0030447 | 0.0030461 | 0.0030648 | 0.0031202 | 0.0031836 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.0031715 | 0.85573 | 0.86135 | 0.86698 | 0.87261 | 0.87824 | 0.88529 | 0.89234 | 0.8994 | 0.90645 | 0.91351 | 0.92056 | 0.92761 | 0.93467 | 0.94172 | 0.94877 | 0.95583 | 0.96288 | 0.96993 | 0.97699 | 0.98404 | 0.06975 | 0.071393 | 0.07286 | 0.073967 | 0.074478 | 0.075536 | 0.077515 | 0.079715 | 0.080034 | 0.080657 | 0.08128 | 0.081903 | 0.082525 | 0.083148 | 0.083771 | 0.084394 | 0.085017 | 0.085639 | 0.086262 | 0.086885 | 28088.495 | 3881.5256 | 32017.1042 | 4424.4168 | 114410.101 | 114410.101 | 3582081.5812 | 114410.101
| SHP011-15432563 | 11 | SHP011 | SHP | North | 259229.5881 | 0.0054915 | 0.0054936 | 0.005437 | 0.0053831 | 0.0053201 | 0.0052705 | 0.0052472 | 0.005221 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 1.0881 | 1.092 | 1.0958 | 1.0997 | 1.1035 | 1.1058 | 1.108 | 1.1103 | 1.1125 | 1.1148 | 1.117 | 1.1192 | 1.1215 | 1.1237 | 1.126 | 1.1282 | 1.1305 | 1.1327 | 1.1349 | 1.1372 | 0.16636 | 0.16701 | 0.16587 | 0.16481 | 0.16345 | 0.16225 | 0.16186 | 0.16138 | 0.15973 | 0.16005 | 0.16038 | 0.1607 | 0.16102 | 0.16134 | 0.16166 | 0.16199 | 0.16231 | 0.16263 | 0.16295 | 0.16328 | 28781.8893 | 3190.6132 | 67740.977 | 7509.4186 | 6060.5053 | 6060.5053 | 259229.5881 | 6060.5053
| SHP011-164003814 | 29 | SHP011 | SHP | North | 683423.4596 | 0.0054915 | 0.0054936 | 0.005437 | 0.0053831 | 0.0053201 | 0.0052705 | 0.0052472 | 0.005221 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.00026835 | 0.00027057 | 0.00027278 | 0.00027499 | 0.0002772 | 0.00028035 | 0.0002835 | 0.00028665 | 0.0002898 | 0.00029295 | 0.0002961 | 0.00029925 | 0.0003024 | 0.00030555 | 0.0003087 | 0.00031185 | 0.000315 | 0.00031815 | 0.0003213 | 0.00032445 | 4.1027e-05 | 4.1381e-05 | 4.1289e-05 | 4.1212e-05 | 4.1057e-05 | 4.1136e-05 | 4.1414e-05 | 4.1665e-05 | 4.1609e-05 | 4.2061e-05 | 4.2513e-05 | 4.2965e-05 | 4.3418e-05 | 4.387e-05 | 4.4322e-05 | 4.4775e-05 | 4.5227e-05 | 4.5679e-05 | 4.6131e-05 | 4.6584e-05 | 28781.8893 | 3190.6132 | 17.7412 | 1.9667 | 160.0639 | 160.0639 | 683423.4596 | 160.0639
| SHP011-24602590 | 367 | SHP011 | SHP | North | 8648841.7124 | 0.0054915 | 0.0054936 | 0.005437 | 0.0053831 | 0.0053201 | 0.0052705 | 0.0052472 | 0.005221 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 0.0051572 | 1.4087 | 1.4175 | 1.4263 | 1.4352 | 1.444 | 1.4546 | 1.4652 | 1.4759 | 1.4865 | 1.4971 | 1.5077 | 1.5184 | 1.529 | 1.5396 | 1.5502 | 1.5609 | 1.5715 | 1.5821 | 1.5927 | 1.6034 | 0.21537 | 0.2168 | 0.2159 | 0.21508 | 0.21387 | 0.21344 | 0.21404 | 0.21452 | 0.21342 | 0.21495 | 0.21648 | 0.218 | 0.21953 | 0.22105 | 0.22258 | 0.2241 | 0.22563 | 0.22716 | 0.22868 | 0.23021 | 28781.8893 | 3190.6132 | 90791.8542 | 10064.7211 | 337963.1179 | 337963.1179 | 8648841.7124 | 337963.1179
| SHP012-153588795 | 79 | SHP012 | SHP | North | 1861739.7692 | 0.0016202 | 0.0016373 | 0.0016505 | 0.0016572 | 0.001645 | 0.0016428 | 0.0016627 | 0.0016855 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.43292 | 0.43556 | 0.4382 | 0.44083 | 0.44347 | 0.44724 | 0.451 | 0.45477 | 0.45854 | 0.4623 | 0.46607 | 0.46984 | 0.4736 | 0.47737 | 0.48114 | 0.4849 | 0.48867 | 0.49244 | 0.4962 | 0.49997 | 0.019528 | 0.019853 | 0.020135 | 0.020338 | 0.02031 | 0.020455 | 0.020877 | 0.021339 | 0.021423 | 0.021599 | 0.021775 | 0.021951 | 0.022127 | 0.022303 | 0.022479 | 0.022655 | 0.022831 | 0.023007 | 0.023183 | 0.023359 | 28781.8893 | 3190.6132 | 8884.6529 | 984.9072 | 158978.0882 | 158978.0882 | 1861739.7692 | 158978.0882
| SHP012-15432576 | 592 | SHP012 | SHP | North | 13951265.1055 | 0.0016202 | 0.0016373 | 0.0016505 | 0.0016572 | 0.001645 | 0.0016428 | 0.0016627 | 0.0016855 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 31.9051 | 32.1065 | 32.3078 | 32.5092 | 32.7105 | 32.9286 | 33.1467 | 33.3648 | 33.5829 | 33.8009 | 34.019 | 34.2371 | 34.4552 | 34.6733 | 34.8914 | 35.1095 | 35.3276 | 35.5457 | 35.7637 | 35.9818 | 1.4392 | 1.4635 | 1.4846 | 1.4998 | 1.498 | 1.506 | 1.5343 | 1.5656 | 1.569 | 1.5792 | 1.5894 | 1.5996 | 1.6097 | 1.6199 | 1.6301 | 1.6403 | 1.6505 | 1.6607 | 1.6709 | 1.6811 | 28781.8893 | 3190.6132 | 649417.9286 | 71991.1538 | 3516662.771 | 3516662.771 | 13951265.1055 | 3516662.771
| SHP012-160253286 | 34 | SHP012 | SHP | North | 801255.0905 | 0.0016202 | 0.0016373 | 0.0016505 | 0.0016572 | 0.001645 | 0.0016428 | 0.0016627 | 0.0016855 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 4.9765e-05 | 5.0081e-05 | 5.0397e-05 | 5.0714e-05 | 5.103e-05 | 5.1642e-05 | 5.2254e-05 | 5.2866e-05 | 5.3478e-05 | 5.409e-05 | 5.4702e-05 | 5.5314e-05 | 5.5926e-05 | 5.6538e-05 | 5.715e-05 | 5.7762e-05 | 5.8374e-05 | 5.8986e-05 | 5.9598e-05 | 6.021e-05 | 2.2448e-06 | 2.2828e-06 | 2.3158e-06 | 2.3397e-06 | 2.337e-06 | 2.3619e-06 | 2.4188e-06 | 2.4806e-06 | 2.4985e-06 | 2.5271e-06 | 2.5557e-06 | 2.5843e-06 | 2.6129e-06 | 2.6415e-06 | 2.67e-06 | 2.6986e-06 | 2.7272e-06 | 2.7558e-06 | 2.7844e-06 | 2.813e-06 | 28781.8893 | 3190.6132 | 1.0396 | 0.11525 | 69.3778 | 69.3778 | 801255.0905 | 69.3778
| SHP012-160253407 | 62 | SHP012 | SHP | North | 1461112.2239 | 0.0016202 | 0.0016373 | 0.0016505 | 0.0016572 | 0.001645 | 0.0016428 | 0.0016627 | 0.0016855 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.00054964 | 0.00055466 | 0.00055967 | 0.00056469 | 0.0005697 | 0.00057375 | 0.0005778 | 0.00058185 | 0.0005859 | 0.00058995 | 0.000594 | 0.00059805 | 0.0006021 | 0.00060615 | 0.0006102 | 0.00061425 | 0.0006183 | 0.00062235 | 0.0006264 | 0.00063045 | 2.4793e-05 | 2.5282e-05 | 2.5717e-05 | 2.6052e-05 | 2.6091e-05 | 2.6241e-05 | 2.6746e-05 | 2.7302e-05 | 2.7373e-05 | 2.7562e-05 | 2.7752e-05 | 2.7941e-05 | 2.813e-05 | 2.8319e-05 | 2.8509e-05 | 2.8698e-05 | 2.8887e-05 | 2.9076e-05 | 2.9265e-05 | 2.9455e-05 | 28781.8893 | 3190.6132 | 11.3163 | 1.2545 | 459.0995 | 459.0995 | 1461112.2239 | 459.0995
| SHP012-160253550 | 35 | SHP012 | SHP | North | 824821.4167 | 0.0016202 | 0.0016373 | 0.0016505 | 0.0016572 | 0.001645 | 0.0016428 | 0.0016627 | 0.0016855 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.00041284 | 0.00041656 | 0.00042027 | 0.00042399 | 0.0004277 | 0.00042932 | 0.00043095 | 0.00043258 | 0.0004342 | 0.00043583 | 0.00043745 | 0.00043908 | 0.0004407 | 0.00044233 | 0.00044395 | 0.00044558 | 0.0004472 | 0.00044883 | 0.00045045 | 0.00045208 | 1.8622e-05 | 1.8987e-05 | 1.9312e-05 | 1.9561e-05 | 1.9587e-05 | 1.9635e-05 | 1.9948e-05 | 2.0298e-05 | 2.0286e-05 | 2.0362e-05 | 2.0438e-05 | 2.0514e-05 | 2.059e-05 | 2.0665e-05 | 2.0741e-05 | 2.0817e-05 | 2.0893e-05 | 2.0969e-05 | 2.1045e-05 | 2.1121e-05 | 28781.8893 | 3190.6132 | 8.3581 | 0.92654 | 397.6156 | 397.6156 | 824821.4167 | 397.6156
| SHP012-163378080 | 0 | SHP012 | SHP | North | 0 | 0.0016202 | 0.0016373 | 0.0016505 | 0.0016572 | 0.001645 | 0.0016428 | 0.0016627 | 0.0016855 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28781.8893 | 3190.6132 | 0 | 0 | 0 | 0 | 0 | 0
| SHP012-164366336 | 38 | SHP012 | SHP | North | 895520.3953 | 0.0016202 | 0.0016373 | 0.0016505 | 0.0016572 | 0.001645 | 0.0016428 | 0.0016627 | 0.0016855 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 6.8894e-05 | 6.937e-05 | 6.9847e-05 | 7.0323e-05 | 7.08e-05 | 7.161e-05 | 7.242e-05 | 7.323e-05 | 7.404e-05 | 7.485e-05 | 7.566e-05 | 7.647e-05 | 7.728e-05 | 7.809e-05 | 7.89e-05 | 7.971e-05 | 8.052e-05 | 8.133e-05 | 8.214e-05 | 8.295e-05 | 3.1076e-06 | 3.162e-06 | 3.2095e-06 | 3.2444e-06 | 3.2424e-06 | 3.2751e-06 | 3.3523e-06 | 3.4362e-06 | 3.4591e-06 | 3.497e-06 | 3.5348e-06 | 3.5727e-06 | 3.6105e-06 | 3.6484e-06 | 3.6862e-06 | 3.7241e-06 | 3.7619e-06 | 3.7997e-06 | 3.8376e-06 | 3.8754e-06 | 28781.8893 | 3190.6132 | 1.4381 | 0.15942 | 80.4466 | 80.4466 | 895520.3953 | 80.4466
| SHP012-24603174 | 515 | SHP012 | SHP | North | 12136657.9888 | 0.0016202 | 0.0016373 | 0.0016505 | 0.0016572 | 0.001645 | 0.0016428 | 0.0016627 | 0.0016855 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 2.1694 | 2.183 | 2.1966 | 2.2101 | 2.2237 | 2.2371 | 2.2504 | 2.2638 | 2.2772 | 2.2905 | 2.3039 | 2.3172 | 2.3306 | 2.344 | 2.3573 | 2.3707 | 2.384 | 2.3974 | 2.4108 | 2.4241 | 0.097858 | 0.099504 | 0.10093 | 0.10197 | 0.10184 | 0.10231 | 0.10417 | 0.10622 | 0.10639 | 0.10701 | 0.10764 | 0.10826 | 0.10889 | 0.10951 | 0.11013 | 0.11076 | 0.11138 | 0.11201 | 0.11263 | 0.11326 | 28781.8893 | 3190.6132 | 44006.9433 | 4878.3849 | 532951.2163 | 532951.2163 | 12136657.9888 | 532951.2163
| SHP012-24612048 | 100 | SHP012 | SHP | North | 2356632.6192 | 0.0016202 | 0.0016373 | 0.0016505 | 0.0016572 | 0.001645 | 0.0016428 | 0.0016627 | 0.0016855 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 0.0016782 | 9.2632 | 9.3147 | 9.3662 | 9.4178 | 9.4693 | 9.5441 | 9.6189 | 9.6937 | 9.7685 | 9.8433 | 9.9181 | 9.993 | 10.0678 | 10.1426 | 10.2174 | 10.2922 | 10.367 | 10.4418 | 10.5166 | 10.5914 | 0.41784 | 0.42458 | 0.43039 | 0.43449 | 0.43366 | 0.4365 | 0.44525 | 0.45486 | 0.45639 | 0.45988 | 0.46338 | 0.46687 | 0.47037 | 0.47386 | 0.47736 | 0.48085 | 0.48435 | 0.48784 | 0.49134 | 0.49483 | 28781.8893 | 3190.6132 | 189222.4019 | 20976.2288 | 451954.0973 | 451954.0973 | 2356632.6192 | 451954.0973
| SHP014-15432602 | 154 | SHP014 | SHP | North | 3629214.2335 | 0.0015668 | 0.0015665 | 0.0015692 | 0.0015653 | 0.0015503 | 0.0015413 | 0.0015452 | 0.0015563 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 3.6972 | 3.7176 | 3.7381 | 3.7585 | 3.779 | 3.808 | 3.837 | 3.866 | 3.895 | 3.924 | 3.953 | 3.982 | 4.011 | 4.04 | 4.069 | 4.098 | 4.127 | 4.1559 | 4.1849 | 4.2139 | 0.16127 | 0.16213 | 0.1633 | 0.16379 | 0.16311 | 0.1634 | 0.16507 | 0.16751 | 0.16714 | 0.16838 | 0.16963 | 0.17087 | 0.17211 | 0.17336 | 0.1746 | 0.17585 | 0.17709 | 0.17834 | 0.17958 | 0.18082 | 28781.8893 | 3190.6132 | 70199.3164 | 7781.9376 | 165647.3966 | 165647.3966 | 3629214.2335 | 165647.3966
| SHP014-164366107 | 29 | SHP014 | SHP | North | 683423.4596 | 0.0015668 | 0.0015665 | 0.0015692 | 0.0015653 | 0.0015503 | 0.0015413 | 0.0015452 | 0.0015563 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.011733 | 0.011814 | 0.011894 | 0.011974 | 0.012055 | 0.012149 | 0.012243 | 0.012337 | 0.012431 | 0.012526 | 0.01262 | 0.012714 | 0.012808 | 0.012902 | 0.012996 | 0.013091 | 0.013185 | 0.013279 | 0.013373 | 0.013467 | 0.0005118 | 0.00051521 | 0.00051961 | 0.00052182 | 0.0005203 | 0.00052132 | 0.00052669 | 0.00053455 | 0.00053344 | 0.00053749 | 0.00054153 | 0.00054557 | 0.00054961 | 0.00055365 | 0.00055769 | 0.00056173 | 0.00056577 | 0.00056981 | 0.00057385 | 0.00057789 | 28781.8893 | 3190.6132 | 223.9004 | 24.8205 | 5359.6348 | 5359.6348 | 683423.4596 | 5359.6348
| SHP014-177037469 | 0 | SHP014 | SHP | North | 0 | 0.0015668 | 0.0015665 | 0.0015692 | 0.0015653 | 0.0015503 | 0.0015413 | 0.0015452 | 0.0015563 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28781.8893 | 3190.6132 | 0 | 0 | 0 | 0 | 0 | 0
| SHP014-24602550 | 341 | SHP014 | SHP | North | 8036117.2314 | 0.0015668 | 0.0015665 | 0.0015692 | 0.0015653 | 0.0015503 | 0.0015413 | 0.0015452 | 0.0015563 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 32.2263 | 32.3916 | 32.557 | 32.7224 | 32.8878 | 33.1043 | 33.3209 | 33.5375 | 33.754 | 33.9706 | 34.1871 | 34.4037 | 34.6203 | 34.8368 | 35.0534 | 35.2699 | 35.4865 | 35.7031 | 35.9196 | 36.1362 | 1.4057 | 1.4126 | 1.4223 | 1.426 | 1.4195 | 1.4205 | 1.4334 | 1.4531 | 1.4484 | 1.4577 | 1.467 | 1.4763 | 1.4856 | 1.4949 | 1.5042 | 1.5135 | 1.5228 | 1.5321 | 1.5413 | 1.5506 | 28781.8893 | 3190.6132 | 607869.0735 | 67385.26 | 3785674.7294 | 3785674.7294 | 8036117.2314 | 3785674.7294
| SHP014-24602854 | 180 | SHP014 | SHP | North | 4241938.7145 | 0.0015668 | 0.0015665 | 0.0015692 | 0.0015653 | 0.0015503 | 0.0015413 | 0.0015452 | 0.0015563 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.14921 | 0.14994 | 0.15067 | 0.1514 | 0.15213 | 0.15371 | 0.1553 | 0.15689 | 0.15847 | 0.16006 | 0.16165 | 0.16323 | 0.16482 | 0.16641 | 0.16799 | 0.16958 | 0.17117 | 0.17275 | 0.17434 | 0.17592 | 0.0065087 | 0.0065392 | 0.0065823 | 0.0065977 | 0.006566 | 0.0065961 | 0.006681 | 0.0067976 | 0.0068003 | 0.0068684 | 0.0069364 | 0.0070045 | 0.0070726 | 0.0071406 | 0.0072087 | 0.0072768 | 0.0073449 | 0.0074129 | 0.007481 | 0.0075491 | 28781.8893 | 3190.6132 | 2864.7016 | 317.5662 | 26106.595 | 26106.595 | 4241938.7145 | 26106.595
| SHP014-24602868 | 117 | SHP014 | SHP | North | 2757260.1644 | 0.0015668 | 0.0015665 | 0.0015692 | 0.0015653 | 0.0015503 | 0.0015413 | 0.0015452 | 0.0015563 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.0015413 | 0.5798 | 0.58341 | 0.58702 | 0.59063 | 0.59424 | 0.60119 | 0.60814 | 0.61509 | 0.62204 | 0.629 | 0.63595 | 0.6429 | 0.64985 | 0.6568 | 0.66375 | 0.6707 | 0.67765 | 0.6846 | 0.69155 | 0.6985 | 0.025291 | 0.025443 | 0.025645 | 0.025739 | 0.025648 | 0.025798 | 0.026162 | 0.026651 | 0.026693 | 0.026991 | 0.027289 | 0.027587 | 0.027886 | 0.028184 | 0.028482 | 0.02878 | 0.029079 | 0.029377 | 0.029675 | 0.029973 | 28781.8893 | 3190.6132 | 11248.5643 | 1246.9584 | 196754.6552 | 196754.6552 | 2757260.1644 | 196754.6552
| SHP021-120932535 | 34 | SHP021 | SHP | North | 801255.0905 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0024605 | 0.0024754 | 0.0024902 | 0.0025051 | 0.00252 | 0.0025329 | 0.0025458 | 0.0025586 | 0.0025715 | 0.0025844 | 0.0025973 | 0.0026102 | 0.002623 | 0.0026359 | 0.0026488 | 0.0026617 | 0.0026746 | 0.0026874 | 0.0027003 | 0.0027132 | 0.00018994 | 0.00018873 | 0.00018992 | 0.00018925 | 0.00018759 | 0.00018594 | 0.00018709 | 0.00018903 | 0.00018923 | 0.00019018 | 0.00019113 | 0.00019207 | 0.00019302 | 0.00019397 | 0.00019492 | 0.00019586 | 0.00019681 | 0.00019776 | 0.00019871 | 0.00019966 | 28781.8893 | 3190.6132 | 79.6389 | 8.8284 | 532.6994 | 532.6994 | 801255.0905 | 532.6994
| SHP021-129439859 | 38 | SHP021 | SHP | North | 895520.3953 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0011193 | 0.0011291 | 0.0011389 | 0.0011487 | 0.0011585 | 0.0011639 | 0.0011693 | 0.0011748 | 0.0011802 | 0.0011856 | 0.001191 | 0.0011965 | 0.0012019 | 0.0012073 | 0.0012127 | 0.0012182 | 0.0012236 | 0.001229 | 0.0012345 | 0.0012399 | 8.6405e-05 | 8.6088e-05 | 8.6857e-05 | 8.678e-05 | 8.6239e-05 | 8.5446e-05 | 8.5935e-05 | 8.679e-05 | 8.6847e-05 | 8.7246e-05 | 8.7646e-05 | 8.8045e-05 | 8.8444e-05 | 8.8843e-05 | 8.9242e-05 | 8.9642e-05 | 9.0041e-05 | 9.044e-05 | 9.0839e-05 | 9.1238e-05 | 28781.8893 | 3190.6132 | 36.4734 | 4.0433 | 436.2861 | 436.2861 | 895520.3953 | 436.2861
| SHP021-134953488 | 132 | SHP021 | SHP | North | 3110755.0573 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.063507 | 0.06399 | 0.064473 | 0.064956 | 0.06544 | 0.06577 | 0.066101 | 0.066432 | 0.066763 | 0.067094 | 0.067425 | 0.067756 | 0.068086 | 0.068417 | 0.068748 | 0.069079 | 0.06941 | 0.069741 | 0.070072 | 0.070403 | 0.0049025 | 0.0048789 | 0.004917 | 0.0049072 | 0.0048714 | 0.0048284 | 0.0048578 | 0.0049079 | 0.0049129 | 0.0049372 | 0.0049616 | 0.0049859 | 0.0050103 | 0.0050346 | 0.005059 | 0.0050833 | 0.0051077 | 0.005132 | 0.0051564 | 0.0051807 | 28781.8893 | 3190.6132 | 2065.4886 | 228.9695 | 58898.5036 | 58898.5036 | 3110755.0573 | 58898.5036
| SHP021-134953623 | 90 | SHP021 | SHP | North | 2120969.3573 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.21019 | 0.21159 | 0.21299 | 0.2144 | 0.2158 | 0.21679 | 0.21777 | 0.21875 | 0.21973 | 0.22072 | 0.2217 | 0.22268 | 0.22366 | 0.22464 | 0.22563 | 0.22661 | 0.22759 | 0.22857 | 0.22955 | 0.23054 | 0.016225 | 0.016133 | 0.016244 | 0.016197 | 0.016065 | 0.015915 | 0.016004 | 0.016161 | 0.016169 | 0.016242 | 0.016314 | 0.016386 | 0.016459 | 0.016531 | 0.016603 | 0.016675 | 0.016748 | 0.01682 | 0.016892 | 0.016964 | 28781.8893 | 3190.6132 | 6798.6875 | 753.6678 | 85329.6945 | 85329.6945 | 2120969.3573 | 85329.6945
| SHP021-137932835 | 20 | SHP021 | SHP | North | 471326.5238 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 7.8894e-06 | 7.957e-06 | 8.0247e-06 | 8.0923e-06 | 8.16e-06 | 8.2592e-06 | 8.3584e-06 | 8.4576e-06 | 8.5568e-06 | 8.656e-06 | 8.7552e-06 | 8.8544e-06 | 8.9536e-06 | 9.0528e-06 | 9.152e-06 | 9.2512e-06 | 9.3504e-06 | 9.4496e-06 | 9.5488e-06 | 9.648e-06 | 6.0902e-07 | 6.0668e-07 | 6.12e-07 | 6.1135e-07 | 6.0743e-07 | 6.0633e-07 | 6.1426e-07 | 6.2483e-07 | 6.2967e-07 | 6.3697e-07 | 6.4427e-07 | 6.5157e-07 | 6.5887e-07 | 6.6617e-07 | 6.7347e-07 | 6.8077e-07 | 6.8807e-07 | 6.9537e-07 | 7.0267e-07 | 7.0997e-07 | 28781.8893 | 3190.6132 | 0.26631 | 0.029522 | 3.6689 | 3.6689 | 471326.5238 | 3.6689
| SHP021-138133628 | 38 | SHP021 | SHP | North | 895520.3953 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.1549 | 0.15601 | 0.15712 | 0.15824 | 0.15935 | 0.15971 | 0.16008 | 0.16044 | 0.16081 | 0.16118 | 0.16154 | 0.16191 | 0.16227 | 0.16264 | 0.16301 | 0.16337 | 0.16374 | 0.16411 | 0.16447 | 0.16484 | 0.011958 | 0.011895 | 0.011983 | 0.011954 | 0.011862 | 0.011725 | 0.011764 | 0.011853 | 0.011834 | 0.01186 | 0.011887 | 0.011914 | 0.011941 | 0.011968 | 0.011995 | 0.012022 | 0.012049 | 0.012076 | 0.012103 | 0.01213 | 28781.8893 | 3190.6132 | 4963.2503 | 550.2006 | 53272.2386 | 53272.2386 | 895520.3953 | 53272.2386
| SHP021-15437442 | 0 | SHP021 | SHP | North | 0 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28781.8893 | 3190.6132 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-15437455 | 68 | SHP021 | SHP | North | 1602510.181 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.43584 | 0.43758 | 0.43932 | 0.44106 | 0.44281 | 0.44355 | 0.44429 | 0.44503 | 0.44576 | 0.4465 | 0.44724 | 0.44798 | 0.44872 | 0.44946 | 0.4502 | 0.45094 | 0.45168 | 0.45242 | 0.45316 | 0.4539 | 0.033644 | 0.033363 | 0.033504 | 0.033321 | 0.032963 | 0.032562 | 0.03265 | 0.032877 | 0.032802 | 0.032857 | 0.032911 | 0.032966 | 0.03302 | 0.033075 | 0.033129 | 0.033183 | 0.033238 | 0.033292 | 0.033347 | 0.033401 | 28781.8893 | 3190.6132 | 13777.8009 | 1527.3366 | 14380.6002 | 14380.6002 | 1602510.181 | 14380.6002
| SHP021-155422659 | 26 | SHP021 | SHP | North | 612724.481 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 7.4585e-05 | 7.5199e-05 | 7.5813e-05 | 7.6426e-05 | 7.704e-05 | 7.7964e-05 | 7.8888e-05 | 7.9812e-05 | 8.0736e-05 | 8.166e-05 | 8.2584e-05 | 8.3508e-05 | 8.4432e-05 | 8.5356e-05 | 8.628e-05 | 8.7204e-05 | 8.8128e-05 | 8.9052e-05 | 8.9976e-05 | 9.09e-05 | 5.7576e-06 | 5.7335e-06 | 5.7818e-06 | 5.7737e-06 | 5.7349e-06 | 5.7235e-06 | 5.7975e-06 | 5.8963e-06 | 5.9411e-06 | 6.0091e-06 | 6.0771e-06 | 6.1451e-06 | 6.2131e-06 | 6.2811e-06 | 6.3491e-06 | 6.4171e-06 | 6.4851e-06 | 6.5531e-06 | 6.621e-06 | 6.689e-06 | 28781.8893 | 3190.6132 | 2.5129 | 0.27857 | 60.0055 | 60.0055 | 612724.481 | 60.0055
| SHP021-157015365 | 55 | SHP021 | SHP | North | 1296147.9405 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0057081 | 0.0057482 | 0.0057884 | 0.0058285 | 0.0058687 | 0.0059246 | 0.0059806 | 0.0060365 | 0.0060925 | 0.0061484 | 0.0062044 | 0.0062604 | 0.0063163 | 0.0063723 | 0.0064282 | 0.0064842 | 0.0065402 | 0.0065961 | 0.0066521 | 0.006708 | 0.00044064 | 0.00043827 | 0.00044145 | 0.00044032 | 0.00043687 | 0.00043494 | 0.00043951 | 0.00044597 | 0.00044833 | 0.00045244 | 0.00045656 | 0.00046068 | 0.0004648 | 0.00046892 | 0.00047303 | 0.00047715 | 0.00048127 | 0.00048539 | 0.00048951 | 0.00049362 | 28781.8893 | 3190.6132 | 189.3439 | 20.9897 | 4590.2753 | 4590.2753 | 1296147.9405 | 4590.2753
| SHP021-157015736 | 45 | SHP021 | SHP | North | 1060484.6786 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.067216 | 0.067754 | 0.068292 | 0.068831 | 0.069369 | 0.069751 | 0.070132 | 0.070514 | 0.070896 | 0.071277 | 0.071659 | 0.072041 | 0.072422 | 0.072804 | 0.073186 | 0.073567 | 0.073949 | 0.074331 | 0.074712 | 0.075094 | 0.0051887 | 0.0051659 | 0.0052083 | 0.0051999 | 0.0051639 | 0.0051206 | 0.005154 | 0.0052094 | 0.005217 | 0.0052451 | 0.0052732 | 0.0053012 | 0.0053293 | 0.0053574 | 0.0053855 | 0.0054136 | 0.0054417 | 0.0054697 | 0.0054978 | 0.0055259 | 28781.8893 | 3190.6132 | 2193.7225 | 243.1849 | 43505.5222 | 43505.5222 | 1060484.6786 | 43505.5222
| SHP021-164271438 | 0 | SHP021 | SHP | North | 0 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28781.8893 | 3190.6132 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-164488411 | 11 | SHP021 | SHP | North | 259229.5881 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.045084 | 0.045386 | 0.045688 | 0.04599 | 0.046292 | 0.046505 | 0.046719 | 0.046932 | 0.047146 | 0.047359 | 0.047572 | 0.047786 | 0.047999 | 0.048213 | 0.048426 | 0.048639 | 0.048853 | 0.049066 | 0.04928 | 0.049493 | 0.0034803 | 0.0034604 | 0.0034844 | 0.0034744 | 0.003446 | 0.0034141 | 0.0034333 | 0.0034672 | 0.0034693 | 0.003485 | 0.0035007 | 0.0035164 | 0.0035321 | 0.0035478 | 0.0035635 | 0.0035792 | 0.0035949 | 0.0036106 | 0.0036263 | 0.003642 | 28781.8893 | 3190.6132 | 1458.783 | 161.7132 | 14732.0501 | 14732.0501 | 259229.5881 | 14732.0501
| SHP021-24614288 | 0 | SHP021 | SHP | North | 0 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0015656 | 0.0015781 | 0.0015907 | 0.0016033 | 0.0016158 | 0.0016304 | 0.0016449 | 0.0016594 | 0.001674 | 0.0016885 | 0.0017031 | 0.0017176 | 0.0017321 | 0.0017467 | 0.0017612 | 0.0017758 | 0.0017903 | 0.0018048 | 0.0018194 | 0.0018339 | 0.00012086 | 0.00012033 | 0.00012131 | 0.00012112 | 0.00012028 | 0.00011969 | 0.00012088 | 0.0001226 | 0.00012318 | 0.00012425 | 0.00012532 | 0.00012639 | 0.00012746 | 0.00012853 | 0.0001296 | 0.00013067 | 0.00013174 | 0.00013281 | 0.00013388 | 0.00013495 | 28781.8893 | 3190.6132 | 0 | 0 | 0 | 0 | 0 | 0
| SHP021-24614430 | 88 | SHP021 | SHP | North | 2073836.7049 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 3.9795 | 3.9968 | 4.0142 | 4.0315 | 4.0488 | 4.0668 | 4.0847 | 4.1027 | 4.1206 | 4.1386 | 4.1565 | 4.1745 | 4.1924 | 4.2104 | 4.2284 | 4.2463 | 4.2643 | 4.2822 | 4.3002 | 4.3181 | 0.3072 | 0.30474 | 0.30614 | 0.30456 | 0.3014 | 0.29855 | 0.30019 | 0.3031 | 0.30322 | 0.30455 | 0.30587 | 0.30719 | 0.30851 | 0.30983 | 0.31115 | 0.31247 | 0.31379 | 0.31512 | 0.31644 | 0.31776 | 28781.8893 | 3190.6132 | 127669.9163 | 14152.8347 | 245010.3295 | 245010.3295 | 2073836.7049 | 245010.3295
| SHP021-66719539 | 120 | SHP021 | SHP | North | 2827959.143 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.028692 | 0.02894 | 0.029187 | 0.029435 | 0.029682 | 0.029744 | 0.029806 | 0.029867 | 0.029929 | 0.029991 | 0.030053 | 0.030115 | 0.030176 | 0.030238 | 0.0303 | 0.030362 | 0.030424 | 0.030485 | 0.030547 | 0.030609 | 0.0022149 | 0.0022065 | 0.0022259 | 0.0022237 | 0.0022095 | 0.0021836 | 0.0021904 | 0.0022065 | 0.0022024 | 0.0022069 | 0.0022115 | 0.002216 | 0.0022206 | 0.0022251 | 0.0022297 | 0.0022342 | 0.0022388 | 0.0022433 | 0.0022479 | 0.0022524 | 28781.8893 | 3190.6132 | 922.6901 | 102.2847 | 14907.2872 | 14907.2872 | 2827959.143 | 14907.2872
| SHP021-85424826 | 136 | SHP021 | SHP | North | 3205020.3621 | 0.0027728 | 0.0027387 | 0.0027394 | 0.0027136 | 0.0026739 | 0.0026369 | 0.0026397 | 0.0026537 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.0026432 | 0.33438 | 0.33696 | 0.33954 | 0.34213 | 0.34471 | 0.34842 | 0.35214 | 0.35586 | 0.35957 | 0.36329 | 0.367 | 0.37072 | 0.37443 | 0.37815 | 0.38186 | 0.38558 | 0.38929 | 0.39301 | 0.39672 | 0.40044 | 0.025813 | 0.025692 | 0.025895 | 0.025846 | 0.02566 | 0.025579 | 0.025879 | 0.02629 | 0.02646 | 0.026733 | 0.027006 | 0.02728 | 0.027553 | 0.027827 | 0.0281 | 0.028373 | 0.028647 | 0.02892 | 0.029193 | 0.029467 | 28781.8893 | 3190.6132 | 11182.7406 | 1239.6615 | 127188.1427 | 127188.1427 | 3205020.3621 | 127188.1427
| SSE011-15435228 | 2 | SSE011 | SSE | South | 36361.5823 | 0.0053738 | 0.0054439 | 0.0054117 | 0.0053782 | 0.0053342 | 0.0053007 | 0.0052845 | 0.0052862 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 37946.5823 | 0
| SSE011-201930324 | 184 | SSE011 | SSE | South | 3345265.5682 | 0.0053738 | 0.0054439 | 0.0054117 | 0.0053782 | 0.0053342 | 0.0053007 | 0.0052845 | 0.0052862 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0.0052655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 3491085.5682 | 0
| SSE012-152773219 | 187 | SSE012 | SSE | South | 3399807.9416 | 0.00099418 | 0.001012 | 0.0010363 | 0.0010557 | 0.0010722 | 0.001099 | 0.0011349 | 0.0011636 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 3548005.4416 | 0
| SSE012-201930283 | 102 | SSE012 | SSE | South | 1854440.6954 | 0.00099418 | 0.001012 | 0.0010363 | 0.0010557 | 0.0010722 | 0.001099 | 0.0011349 | 0.0011636 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0.0011738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 1935275.6954 | 0
| SSE013-201930225 | 89 | SSE013 | SSE | South | 1618090.4107 | 0.0018348 | 0.0018334 | 0.0018176 | 0.0017975 | 0.0017807 | 0.0017732 | 0.0017833 | 0.0017949 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 1688622.9107 | 0
| SSE013-74144019 | 86 | SSE013 | SSE | South | 1563548.0373 | 0.0018348 | 0.0018334 | 0.0018176 | 0.0017975 | 0.0017807 | 0.0017732 | 0.0017833 | 0.0017949 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0.0017914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 1631703.0373 | 0
| SSE014-201930170 | 214 | SSE014 | SSE | South | 3890689.3021 | 0.0014428 | 0.0014589 | 0.0014806 | 0.0014914 | 0.0014964 | 0.0015127 | 0.0015425 | 0.0015673 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 4060284.3021 | 0
| SSE014-24597938 | 174 | SSE014 | SSE | South | 3163457.6569 | 0.0014428 | 0.0014589 | 0.0014806 | 0.0014914 | 0.0014964 | 0.0015127 | 0.0015425 | 0.0015673 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0.0015614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 3301352.6569 | 0
| SSE031-15437545 | 1 | SSE031 | SSE | South | 18180.7911 | 0.00092587 | 0.00093685 | 0.00094468 | 0.00098528 | 0.0010339 | 0.0010887 | 0.0011455 | 0.001195 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 18973.2911 | 0
| SSE031-201930106 | 223 | SSE031 | SSE | South | 4054316.4223 | 0.00092587 | 0.00093685 | 0.00094468 | 0.00098528 | 0.0010339 | 0.0010887 | 0.0011455 | 0.001195 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 4231043.9223 | 0
| SSE031-24597896 | 392 | SSE031 | SSE | South | 7126870.1235 | 0.00092587 | 0.00093685 | 0.00094468 | 0.00098528 | 0.0010339 | 0.0010887 | 0.0011455 | 0.001195 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 7437530.1235 | 0
| SSE031-24597910 | 32 | SSE031 | SSE | South | 581785.3162 | 0.00092587 | 0.00093685 | 0.00094468 | 0.00098528 | 0.0010339 | 0.0010887 | 0.0011455 | 0.001195 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0.0012354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 607145.3162 | 0
| SSE032-156444372 | 237 | SSE032 | SSE | South | 4308847.4982 | 0.0016787 | 0.0016791 | 0.0016721 | 0.0016774 | 0.0016745 | 0.0016865 | 0.0017251 | 0.0017525 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 2.6197 | 2.6371 | 2.6545 | 2.672 | 2.6894 | 2.6934 | 2.6973 | 2.7013 | 2.7053 | 2.7093 | 2.7132 | 2.7172 | 2.7212 | 2.7252 | 2.7291 | 2.7331 | 2.7371 | 2.7411 | 2.745 | 2.749 | 0.12243 | 0.12327 | 0.12357 | 0.12478 | 0.12537 | 0.12646 | 0.12954 | 0.13179 | 0.13186 | 0.13205 | 0.13225 | 0.13244 | 0.13263 | 0.13283 | 0.13302 | 0.13321 | 0.13341 | 0.1336 | 0.1338 | 0.13399 | 38767.6174 | 6056.3827 | 72521.8658 | 11329.5632 | 107196.005 | 138949.7301 | 4496669.9982 | 111868.6749
| SSE032-201929980 | 137 | SSE032 | SSE | South | 2490768.385 | 0.0016787 | 0.0016791 | 0.0016721 | 0.0016774 | 0.0016745 | 0.0016865 | 0.0017251 | 0.0017525 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0.0017508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 2599340.885 | 0
| SSE033-201929907 | 395 | SSE033 | SSE | South | 7181412.4969 | 0.001263 | 0.0012838 | 0.001297 | 0.0013076 | 0.0013119 | 0.0013192 | 0.0013383 | 0.0013595 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0.0013629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 7494449.9969 | 0
| SSE034-201929860 | 176 | SSE034 | SSE | South | 3199819.2391 | 0.0019492 | 0.0019911 | 0.0020225 | 0.0020443 | 0.0020429 | 0.0020514 | 0.0020963 | 0.0021487 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 3339299.2391 | 0
| SSE034-24597952 | 185 | SSE034 | SSE | South | 3363446.3593 | 0.0019492 | 0.0019911 | 0.0020225 | 0.0020443 | 0.0020429 | 0.0020514 | 0.0020963 | 0.0021487 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0.0021465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38767.6174 | 6056.3827 | 0 | 0 | 0 | 0 | 3510058.8593 | 0
| STL004-15415692 | 264 | STL004 | STL | North | 6221510.1146 | 0.0022054 | 0.002193 | 0.0021592 | 0.0021211 | 0.0020812 | 0.0020483 | 0.0020248 | 0.0020031 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 0.0019796 | 4.8872 | 4.9241 | 4.9609 | 4.9978 | 5.0347 | 5.0379 | 5.041 | 5.0442 | 5.0474 | 5.0506 | 5.0538 | 5.057 | 5.0602 | 5.0634 | 5.0666 | 5.0698 | 5.073 | 5.0761 | 5.0793 | 5.0825 | 0.30006 | 0.30063 | 0.29822 | 0.29513 | 0.29171 | 0.28729 | 0.28416 | 0.2813 | 0.27817 | 0.27834 | 0.27852 | 0.2787 | 0.27887 | 0.27905 | 0.27922 | 0.2794 | 0.27957 | 0.27975 | 0.27993 | 0.2801 | 33421.4206 | 4532.725 | 138075.7279 | 18726.2926 | 280151.1388 | 280151.1388 | 6221510.1146 | 280151.1388
| STL005-141432115 | 16 | STL005 | STL | North | 377061.2191 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0066498 | 0.0066958 | 0.0067417 | 0.0067876 | 0.0068335 | 0.0068504 | 0.0068673 | 0.0068842 | 0.0069011 | 0.006918 | 0.0069349 | 0.0069518 | 0.0069687 | 0.0069857 | 0.0070026 | 0.0070195 | 0.0070364 | 0.0070533 | 0.0070702 | 0.0070871 | 0.00024498 | 0.00024656 | 0.00024642 | 0.00024588 | 0.00024434 | 0.00024222 | 0.00024196 | 0.00024206 | 0.00024029 | 0.00024088 | 0.00024147 | 0.00024206 | 0.00024265 | 0.00024323 | 0.00024382 | 0.00024441 | 0.000245 | 0.00024559 | 0.00024618 | 0.00024677 | 33421.4206 | 4532.725 | 117.832 | 15.9808 | 1788.2879 | 1788.2879 | 377061.2191 | 1788.2879
| STL005-142032974 | 82 | STL005 | STL | North | 1932438.7477 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.07131 | 0.071902 | 0.072494 | 0.073086 | 0.073677 | 0.073622 | 0.073566 | 0.073511 | 0.073455 | 0.073399 | 0.073344 | 0.073288 | 0.073232 | 0.073177 | 0.073121 | 0.073066 | 0.07301 | 0.072954 | 0.072899 | 0.072843 | 0.0026271 | 0.0026477 | 0.0026498 | 0.0026475 | 0.0026344 | 0.0026031 | 0.002592 | 0.0025848 | 0.0025576 | 0.0025557 | 0.0025538 | 0.0025518 | 0.0025499 | 0.0025479 | 0.002546 | 0.0025441 | 0.0025421 | 0.0025402 | 0.0025383 | 0.0025363 | 33421.4206 | 4532.725 | 1249.1951 | 169.42 | 78459.8056 | 78459.8056 | 1932438.7477 | 78459.8056
| STL005-143031921 | 24 | STL005 | STL | North | 565591.8286 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.062711 | 0.063146 | 0.06358 | 0.064015 | 0.064449 | 0.06456 | 0.064671 | 0.064781 | 0.064892 | 0.065002 | 0.065113 | 0.065224 | 0.065334 | 0.065445 | 0.065556 | 0.065666 | 0.065777 | 0.065888 | 0.065998 | 0.066109 | 0.0023103 | 0.0023253 | 0.002324 | 0.0023189 | 0.0023045 | 0.0022827 | 0.0022785 | 0.0022779 | 0.0022595 | 0.0022633 | 0.0022672 | 0.002271 | 0.0022749 | 0.0022787 | 0.0022826 | 0.0022864 | 0.0022903 | 0.0022941 | 0.002298 | 0.0023019 | 33421.4206 | 4532.725 | 1107.1736 | 150.1586 | 12908.9563 | 12908.9563 | 565591.8286 | 12908.9563
| STL005-15415831 | 185 | STL005 | STL | North | 4359770.3455 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 14.1009 | 14.2211 | 14.3412 | 14.4613 | 14.5814 | 14.5979 | 14.6144 | 14.6309 | 14.6474 | 14.6639 | 14.6804 | 14.6969 | 14.7134 | 14.7299 | 14.7464 | 14.7629 | 14.7794 | 14.7959 | 14.8124 | 14.829 | 0.51948 | 0.52368 | 0.52419 | 0.52386 | 0.52137 | 0.51616 | 0.51491 | 0.51446 | 0.51001 | 0.51058 | 0.51116 | 0.51173 | 0.51231 | 0.51288 | 0.51346 | 0.51403 | 0.51461 | 0.51518 | 0.51576 | 0.51633 | 33421.4206 | 4532.725 | 249518.2665 | 33840.5029 | 393362.2122 | 393362.2122 | 4359770.3455 | 393362.2122
| STL005-155503897 | 20 | STL005 | STL | North | 471326.5238 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.00011604 | 0.00011688 | 0.00011772 | 0.00011856 | 0.0001194 | 0.00011995 | 0.0001205 | 0.00012105 | 0.0001216 | 0.00012215 | 0.0001227 | 0.00012325 | 0.0001238 | 0.00012435 | 0.0001249 | 0.00012545 | 0.000126 | 0.00012655 | 0.0001271 | 0.00012765 | 4.275e-06 | 4.304e-06 | 4.3029e-06 | 4.2948e-06 | 4.2693e-06 | 4.2412e-06 | 4.2456e-06 | 4.2564e-06 | 4.234e-06 | 4.2531e-06 | 4.2723e-06 | 4.2915e-06 | 4.3106e-06 | 4.3298e-06 | 4.3489e-06 | 4.3681e-06 | 4.3872e-06 | 4.4064e-06 | 4.4255e-06 | 4.4447e-06 | 33421.4206 | 4532.725 | 2.0799 | 0.28209 | 41.4381 | 41.4381 | 471326.5238 | 41.4381
| STL005-164675419 | 15 | STL005 | STL | North | 353494.8929 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33421.4206 | 4532.725 | 0 | 0 | 0 | 0 | 353494.8929 | 0
| STL005-24599604 | 140 | STL005 | STL | North | 3299285.6668 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 9.1934 | 9.2542 | 9.3151 | 9.3759 | 9.4368 | 9.4436 | 9.4504 | 9.4572 | 9.464 | 9.4708 | 9.4776 | 9.4845 | 9.4913 | 9.4981 | 9.5049 | 9.5117 | 9.5185 | 9.5253 | 9.5321 | 9.5389 | 0.33869 | 0.34078 | 0.34048 | 0.33964 | 0.33742 | 0.33391 | 0.33297 | 0.33254 | 0.32953 | 0.32977 | 0.33 | 0.33024 | 0.33048 | 0.33071 | 0.33095 | 0.33119 | 0.33143 | 0.33166 | 0.3319 | 0.33214 | 33421.4206 | 4532.725 | 161352.7566 | 21883.2012 | 632990.2528 | 632990.2528 | 3299285.6668 | 632990.2528
| STL005-24613578 | 128 | STL005 | STL | North | 3016489.7525 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 2.6849 | 2.703 | 2.7211 | 2.7393 | 2.7574 | 2.7567 | 2.756 | 2.7553 | 2.7546 | 2.7539 | 2.7532 | 2.7524 | 2.7517 | 2.751 | 2.7503 | 2.7496 | 2.7489 | 2.7482 | 2.7475 | 2.7467 | 0.098911 | 0.099535 | 0.099462 | 0.09923 | 0.098595 | 0.097473 | 0.097102 | 0.096882 | 0.095912 | 0.095887 | 0.095862 | 0.095837 | 0.095813 | 0.095788 | 0.095763 | 0.095738 | 0.095714 | 0.095689 | 0.095664 | 0.095639 | 33421.4206 | 4532.725 | 46914.4721 | 6362.6978 | 478064.7095 | 478064.7095 | 3016489.7525 | 478064.7095
| STL005-78736488 | 53 | STL005 | STL | North | 1249015.2882 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.021259 | 0.021408 | 0.021557 | 0.021706 | 0.021855 | 0.021814 | 0.021772 | 0.021731 | 0.02169 | 0.021649 | 0.021608 | 0.021567 | 0.021526 | 0.021485 | 0.021443 | 0.021402 | 0.021361 | 0.02132 | 0.021279 | 0.021238 | 0.00078319 | 0.00078832 | 0.00078794 | 0.00078629 | 0.00078144 | 0.00077129 | 0.00076711 | 0.00076412 | 0.00075523 | 0.0007538 | 0.00075237 | 0.00075094 | 0.0007495 | 0.00074807 | 0.00074664 | 0.00074521 | 0.00074377 | 0.00074234 | 0.00074091 | 0.00073948 | 33421.4206 | 4532.725 | 368.772 | 50.0141 | 55598.0447 | 55598.0447 | 1249015.2882 | 55598.0447
| STL005-78747550 | 52 | STL005 | STL | North | 1225448.962 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.012788 | 0.012888 | 0.012988 | 0.013089 | 0.013189 | 0.01318 | 0.013171 | 0.013162 | 0.013152 | 0.013143 | 0.013134 | 0.013125 | 0.013115 | 0.013106 | 0.013097 | 0.013088 | 0.013079 | 0.013069 | 0.01306 | 0.013051 | 0.0004711 | 0.00047459 | 0.00047475 | 0.00047414 | 0.00047159 | 0.00046602 | 0.00046405 | 0.00046279 | 0.00045795 | 0.00045763 | 0.00045731 | 0.00045699 | 0.00045667 | 0.00045635 | 0.00045603 | 0.00045571 | 0.00045539 | 0.00045507 | 0.00045475 | 0.00045442 | 33421.4206 | 4532.725 | 223.7495 | 30.3457 | 8581.7443 | 8581.7443 | 1225448.962 | 8581.7443
| STL005-78747613 | 48 | STL005 | STL | North | 1131183.6572 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.09081 | 0.091606 | 0.092402 | 0.093198 | 0.093993 | 0.093806 | 0.093619 | 0.093432 | 0.093245 | 0.093058 | 0.092871 | 0.092684 | 0.092497 | 0.09231 | 0.092123 | 0.091936 | 0.091749 | 0.091562 | 0.091375 | 0.091188 | 0.0033455 | 0.0033733 | 0.0033774 | 0.0033761 | 0.0033608 | 0.0033168 | 0.0032985 | 0.0032853 | 0.0032467 | 0.0032402 | 0.0032337 | 0.0032272 | 0.0032207 | 0.0032141 | 0.0032076 | 0.0032011 | 0.0031946 | 0.0031881 | 0.0031816 | 0.0031751 | 33421.4206 | 4532.725 | 1583.358 | 214.7403 | 44512.2098 | 44512.2098 | 1131183.6572 | 44512.2098
| STL005-84921818 | 71 | STL005 | STL | North | 1673209.1596 | 0.0013233 | 0.0013227 | 0.0013129 | 0.0013012 | 0.0012843 | 0.0012701 | 0.0012656 | 0.001263 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 0.0012507 | 5.5743 | 5.618 | 5.6618 | 5.7055 | 5.7493 | 5.7465 | 5.7436 | 5.7408 | 5.738 | 5.7351 | 5.7323 | 5.7295 | 5.7266 | 5.7238 | 5.721 | 5.7181 | 5.7153 | 5.7125 | 5.7097 | 5.7068 | 0.20536 | 0.20688 | 0.20695 | 0.20668 | 0.20557 | 0.20319 | 0.20237 | 0.20186 | 0.19979 | 0.19969 | 0.19959 | 0.1995 | 0.1994 | 0.1993 | 0.1992 | 0.1991 | 0.199 | 0.1989 | 0.1988 | 0.19871 | 33421.4206 | 4532.725 | 97634.7962 | 13241.558 | 208901.5246 | 208901.5246 | 1673209.1596 | 208901.5246
| STL006-144106192 | 87 | STL006 | STL | North | 2050270.3787 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.025824 | 0.026041 | 0.026257 | 0.026473 | 0.026689 | 0.02666 | 0.026632 | 0.026603 | 0.026574 | 0.026546 | 0.026517 | 0.026488 | 0.02646 | 0.026431 | 0.026402 | 0.026374 | 0.026345 | 0.026316 | 0.026288 | 0.026259 | 0.0013064 | 0.0013375 | 0.0013495 | 0.0013583 | 0.0013587 | 0.001352 | 0.0013574 | 0.0013629 | 0.0013469 | 0.0013454 | 0.001344 | 0.0013425 | 0.0013411 | 0.0013396 | 0.0013382 | 0.0013367 | 0.0013353 | 0.0013338 | 0.0013324 | 0.0013309 | 33421.4206 | 4532.725 | 648.9915 | 88.0184 | 16653.4266 | 16653.4266 | 2050270.3787 | 16653.4266
| STL006-144106506 | 86 | STL006 | STL | North | 2026704.0525 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.001126 | 0.001136 | 0.0011459 | 0.0011559 | 0.0011658 | 0.001168 | 0.0011702 | 0.0011723 | 0.0011745 | 0.0011767 | 0.0011789 | 0.001181 | 0.0011832 | 0.0011854 | 0.0011876 | 0.0011897 | 0.0011919 | 0.0011941 | 0.0011963 | 0.0011984 | 5.6965e-05 | 5.8345e-05 | 5.8895e-05 | 5.9306e-05 | 5.9351e-05 | 5.9229e-05 | 5.9643e-05 | 6.0059e-05 | 5.9529e-05 | 5.9639e-05 | 5.9749e-05 | 5.986e-05 | 5.997e-05 | 6.008e-05 | 6.019e-05 | 6.0301e-05 | 6.0411e-05 | 6.0521e-05 | 6.0631e-05 | 6.0741e-05 | 33421.4206 | 4532.725 | 28.7622 | 3.9008 | 1182.4588 | 1182.4588 | 2026704.0525 | 1182.4588
| STL006-144106734 | 67 | STL006 | STL | North | 1578943.8548 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.75626 | 0.76223 | 0.7682 | 0.77417 | 0.78014 | 0.77945 | 0.77876 | 0.77807 | 0.77738 | 0.77668 | 0.77599 | 0.7753 | 0.77461 | 0.77392 | 0.77323 | 0.77253 | 0.77184 | 0.77115 | 0.77046 | 0.76977 | 0.038259 | 0.039149 | 0.039482 | 0.039722 | 0.039717 | 0.039526 | 0.039694 | 0.039861 | 0.039401 | 0.039366 | 0.039331 | 0.039296 | 0.039261 | 0.039226 | 0.039191 | 0.039155 | 0.03912 | 0.039085 | 0.03905 | 0.039015 | 33421.4206 | 4532.725 | 18994.2503 | 2576.0638 | 289208.5704 | 289208.5704 | 1578943.8548 | 289208.5704
| STL006-144631935 | 72 | STL006 | STL | North | 1696775.4858 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.1497 | 0.15112 | 0.15253 | 0.15394 | 0.15536 | 0.15528 | 0.1552 | 0.15512 | 0.15504 | 0.15496 | 0.15488 | 0.1548 | 0.15472 | 0.15464 | 0.15456 | 0.15448 | 0.1544 | 0.15431 | 0.15423 | 0.15415 | 0.0075732 | 0.0077614 | 0.0078394 | 0.0078987 | 0.0079093 | 0.0078743 | 0.0079106 | 0.0079468 | 0.007858 | 0.0078539 | 0.0078499 | 0.0078458 | 0.0078417 | 0.0078376 | 0.0078336 | 0.0078295 | 0.0078254 | 0.0078214 | 0.0078173 | 0.0078132 | 33421.4206 | 4532.725 | 3785.9593 | 513.4645 | 130304.2095 | 130304.2095 | 1696775.4858 | 130304.2095
| STL006-144632294 | 341 | STL006 | STL | North | 8036117.2314 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.52136 | 0.52618 | 0.53101 | 0.53583 | 0.54066 | 0.54037 | 0.54008 | 0.5398 | 0.53951 | 0.53922 | 0.53894 | 0.53865 | 0.53836 | 0.53807 | 0.53779 | 0.5375 | 0.53721 | 0.53693 | 0.53664 | 0.53635 | 0.026375 | 0.027025 | 0.027291 | 0.027493 | 0.027525 | 0.027402 | 0.027528 | 0.027654 | 0.027345 | 0.02733 | 0.027316 | 0.027301 | 0.027287 | 0.027272 | 0.027257 | 0.027243 | 0.027228 | 0.027214 | 0.027199 | 0.027185 | 33421.4206 | 4532.725 | 13175.9892 | 1786.9718 | 1519152.8937 | 1519152.8937 | 8036117.2314 | 1519152.8937
| STL006-15415768 | 56 | STL006 | STL | North | 1319714.2667 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 15.1284 | 15.2229 | 15.3174 | 15.4119 | 15.5064 | 15.5014 | 15.4965 | 15.4915 | 15.4865 | 15.4815 | 15.4765 | 15.4715 | 15.4665 | 15.4616 | 15.4566 | 15.4516 | 15.4466 | 15.4416 | 15.4366 | 15.4316 | 0.76533 | 0.78186 | 0.78725 | 0.79077 | 0.78943 | 0.78609 | 0.78986 | 0.79364 | 0.78492 | 0.78467 | 0.78442 | 0.78417 | 0.78391 | 0.78366 | 0.78341 | 0.78315 | 0.7829 | 0.78265 | 0.7824 | 0.78214 | 33421.4206 | 4532.725 | 379006.9826 | 51402.1963 | 270763.0443 | 270763.0443 | 1319714.2667 | 270763.0443
| STL006-155132358 | 150 | STL006 | STL | North | 3534948.9288 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.2099 | 0.21177 | 0.21363 | 0.2155 | 0.21736 | 0.21794 | 0.21851 | 0.21908 | 0.21966 | 0.22023 | 0.2208 | 0.22138 | 0.22195 | 0.22252 | 0.2231 | 0.22367 | 0.22424 | 0.22481 | 0.22539 | 0.22596 | 0.010619 | 0.010877 | 0.01098 | 0.011057 | 0.011066 | 0.011052 | 0.011138 | 0.011224 | 0.011133 | 0.011162 | 0.011191 | 0.01122 | 0.011249 | 0.011278 | 0.011307 | 0.011337 | 0.011366 | 0.011395 | 0.011424 | 0.011453 | 33421.4206 | 4532.725 | 5383.1761 | 730.0844 | 196391.862 | 196391.862 | 3534948.9288 | 196391.862
| STL006-155132567 | 42 | STL006 | STL | North | 989785.7001 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 6.3707e-05 | 6.4291e-05 | 6.4874e-05 | 6.5457e-05 | 6.604e-05 | 6.6228e-05 | 6.6417e-05 | 6.6605e-05 | 6.6794e-05 | 6.6982e-05 | 6.7171e-05 | 6.7359e-05 | 6.7548e-05 | 6.7736e-05 | 6.7925e-05 | 6.8113e-05 | 6.8302e-05 | 6.849e-05 | 6.8679e-05 | 6.8867e-05 | 3.2229e-06 | 3.302e-06 | 3.3342e-06 | 3.3585e-06 | 3.3621e-06 | 3.3585e-06 | 3.3853e-06 | 3.4123e-06 | 3.3854e-06 | 3.395e-06 | 3.4045e-06 | 3.4141e-06 | 3.4236e-06 | 3.4332e-06 | 3.4427e-06 | 3.4523e-06 | 3.4618e-06 | 3.4714e-06 | 3.481e-06 | 3.4905e-06 | 33421.4206 | 4532.725 | 1.637 | 0.22202 | 73.3217 | 73.3217 | 989785.7001 | 73.3217
| STL006-155132685 | 131 | STL006 | STL | North | 3087188.7311 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.31421 | 0.31646 | 0.31872 | 0.32097 | 0.32322 | 0.32357 | 0.32392 | 0.32426 | 0.32461 | 0.32496 | 0.32531 | 0.32565 | 0.326 | 0.32635 | 0.32669 | 0.32704 | 0.32739 | 0.32773 | 0.32808 | 0.32843 | 0.015896 | 0.016254 | 0.016381 | 0.016469 | 0.016455 | 0.016408 | 0.01651 | 0.016612 | 0.016453 | 0.01647 | 0.016488 | 0.016505 | 0.016523 | 0.016541 | 0.016558 | 0.016576 | 0.016593 | 0.016611 | 0.016629 | 0.016646 | 33421.4206 | 4532.725 | 7951.1024 | 1078.3551 | 360990.0158 | 360990.0158 | 3087188.7311 | 360990.0158
| STL006-155132926 | 43 | STL006 | STL | North | 1013352.0262 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.091004 | 0.091826 | 0.092649 | 0.093471 | 0.094293 | 0.094491 | 0.094689 | 0.094888 | 0.095086 | 0.095284 | 0.095482 | 0.09568 | 0.095878 | 0.096077 | 0.096275 | 0.096473 | 0.096671 | 0.096869 | 0.097067 | 0.097266 | 0.0046038 | 0.0047163 | 0.0047617 | 0.0047959 | 0.0048004 | 0.0047917 | 0.0048264 | 0.0048612 | 0.0048194 | 0.0048294 | 0.0048395 | 0.0048495 | 0.0048595 | 0.0048696 | 0.0048796 | 0.0048897 | 0.0048997 | 0.0049098 | 0.0049198 | 0.0049299 | 33421.4206 | 4532.725 | 2328.8105 | 315.8411 | 81661.7725 | 81661.7725 | 1013352.0262 | 81661.7725
| STL006-155133021 | 37 | STL006 | STL | North | 871954.0691 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33421.4206 | 4532.725 | 0 | 0 | 0 | 0 | 871954.0691 | 0
| STL006-155133103 | 48 | STL006 | STL | North | 1131183.6572 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.038535 | 0.038841 | 0.039147 | 0.039453 | 0.039759 | 0.03973 | 0.0397 | 0.03967 | 0.039641 | 0.039611 | 0.039582 | 0.039552 | 0.039522 | 0.039493 | 0.039463 | 0.039433 | 0.039404 | 0.039374 | 0.039345 | 0.039315 | 0.0019494 | 0.0019949 | 0.002012 | 0.0020243 | 0.0020241 | 0.0020147 | 0.0020235 | 0.0020323 | 0.0020092 | 0.0020077 | 0.0020062 | 0.0020047 | 0.0020032 | 0.0020017 | 0.0020002 | 0.0019987 | 0.0019972 | 0.0019957 | 0.0019942 | 0.0019927 | 33421.4206 | 4532.725 | 968.6859 | 131.3764 | 26857.0315 | 26857.0315 | 1131183.6572 | 26857.0315
| STL006-155133222 | 31 | STL006 | STL | North | 730556.1119 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33421.4206 | 4532.725 | 0 | 0 | 0 | 0 | 730556.1119 | 0
| STL006-155178765 | 45 | STL006 | STL | North | 1060484.6786 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33421.4206 | 4532.725 | 0 | 0 | 0 | 0 | 1060484.6786 | 0
| STL006-155178849 | 51 | STL006 | STL | North | 1201882.6358 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.055197 | 0.055747 | 0.056297 | 0.056847 | 0.057397 | 0.057359 | 0.057322 | 0.057284 | 0.057247 | 0.057209 | 0.057171 | 0.057134 | 0.057096 | 0.057059 | 0.057021 | 0.056984 | 0.056946 | 0.056908 | 0.056871 | 0.056833 | 0.0027924 | 0.0028632 | 0.0028934 | 0.0029168 | 0.0029221 | 0.0029087 | 0.0029217 | 0.0029347 | 0.0029015 | 0.0028996 | 0.0028977 | 0.0028958 | 0.0028939 | 0.002892 | 0.0028901 | 0.0028882 | 0.0028863 | 0.0028844 | 0.0028825 | 0.0028806 | 33421.4206 | 4532.725 | 1397.2928 | 189.5055 | 61742.6363 | 61742.6363 | 1201882.6358 | 61742.6363
| STL006-155178947 | 56 | STL006 | STL | North | 1319714.2667 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.046629 | 0.047095 | 0.047561 | 0.048027 | 0.048493 | 0.04842 | 0.048346 | 0.048273 | 0.0482 | 0.048126 | 0.048053 | 0.047979 | 0.047906 | 0.047832 | 0.047759 | 0.047686 | 0.047612 | 0.047539 | 0.047465 | 0.047392 | 0.0023589 | 0.0024188 | 0.0024444 | 0.0024642 | 0.0024688 | 0.0024554 | 0.0024642 | 0.0024731 | 0.002443 | 0.0024392 | 0.0024355 | 0.0024318 | 0.0024281 | 0.0024244 | 0.0024206 | 0.0024169 | 0.0024132 | 0.0024095 | 0.0024058 | 0.002402 | 33421.4206 | 4532.725 | 1175.3863 | 159.4098 | 60830.1829 | 60830.1829 | 1319714.2667 | 60830.1829
| STL006-155179094 | 82 | STL006 | STL | North | 1932438.7477 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.015848 | 0.015994 | 0.016141 | 0.016288 | 0.016435 | 0.016412 | 0.016389 | 0.016367 | 0.016344 | 0.016321 | 0.016299 | 0.016276 | 0.016253 | 0.016231 | 0.016208 | 0.016185 | 0.016163 | 0.01614 | 0.016117 | 0.016095 | 0.00080171 | 0.00082148 | 0.00082958 | 0.00083571 | 0.00083669 | 0.00083226 | 0.00083538 | 0.00083848 | 0.00082839 | 0.00082724 | 0.00082609 | 0.00082494 | 0.00082379 | 0.00082265 | 0.0008215 | 0.00082035 | 0.0008192 | 0.00081805 | 0.0008169 | 0.00081576 | 33421.4206 | 4532.725 | 398.8014 | 54.0868 | 22666.3987 | 22666.3987 | 1932438.7477 | 22666.3987
| STL006-155189552 | 95 | STL006 | STL | North | 2238800.9882 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.064189 | 0.064851 | 0.065514 | 0.066176 | 0.066839 | 0.066839 | 0.066838 | 0.066838 | 0.066838 | 0.066838 | 0.066838 | 0.066838 | 0.066837 | 0.066837 | 0.066837 | 0.066837 | 0.066837 | 0.066836 | 0.066836 | 0.066836 | 0.0032473 | 0.0033308 | 0.0033671 | 0.0033954 | 0.0034028 | 0.0033894 | 0.0034068 | 0.0034242 | 0.0033876 | 0.0033876 | 0.0033876 | 0.0033876 | 0.0033876 | 0.0033876 | 0.0033876 | 0.0033876 | 0.0033876 | 0.0033876 | 0.0033876 | 0.0033875 | 33421.4206 | 4532.725 | 1632.1565 | 221.3585 | 107475.0618 | 107475.0618 | 2238800.9882 | 107475.0618
| STL006-155189674 | 50 | STL006 | STL | North | 1178316.3096 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33421.4206 | 4532.725 | 0 | 0 | 0 | 0 | 1178316.3096 | 0
| STL006-155189763 | 32 | STL006 | STL | North | 754122.4381 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33421.4206 | 4532.725 | 0 | 0 | 0 | 0 | 754122.4381 | 0
| STL006-155189877 | 75 | STL006 | STL | North | 1767474.4644 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.00055296 | 0.00055872 | 0.00056448 | 0.00057024 | 0.000576 | 0.00057798 | 0.00057996 | 0.00058194 | 0.00058392 | 0.0005859 | 0.00058788 | 0.00058986 | 0.00059184 | 0.00059382 | 0.0005958 | 0.00059778 | 0.00059976 | 0.00060174 | 0.00060372 | 0.0006057 | 2.7974e-05 | 2.8696e-05 | 2.9012e-05 | 2.9258e-05 | 2.9324e-05 | 2.931e-05 | 2.9561e-05 | 2.9813e-05 | 2.9596e-05 | 2.9696e-05 | 2.9796e-05 | 2.9897e-05 | 2.9997e-05 | 3.0097e-05 | 3.0198e-05 | 3.0298e-05 | 3.0398e-05 | 3.0499e-05 | 3.0599e-05 | 3.07e-05 | 33421.4206 | 4532.725 | 14.3086 | 1.9406 | 413.266 | 413.266 | 1767474.4644 | 413.266
| STL006-155190011 | 23 | STL006 | STL | North | 542025.5024 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33421.4206 | 4532.725 | 0 | 0 | 0 | 0 | 542025.5024 | 0
| STL006-155190105 | 33 | STL006 | STL | North | 777688.7643 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.016198 | 0.016309 | 0.01642 | 0.016532 | 0.016643 | 0.016649 | 0.016656 | 0.016662 | 0.016668 | 0.016674 | 0.01668 | 0.016687 | 0.016693 | 0.016699 | 0.016705 | 0.016711 | 0.016718 | 0.016724 | 0.01673 | 0.016736 | 0.00081942 | 0.00083765 | 0.00084394 | 0.00084823 | 0.0008473 | 0.0008443 | 0.00084894 | 0.0008536 | 0.00084481 | 0.00084512 | 0.00084544 | 0.00084575 | 0.00084607 | 0.00084638 | 0.0008467 | 0.00084701 | 0.00084733 | 0.00084764 | 0.00084796 | 0.00084827 | 33421.4206 | 4532.725 | 408.0525 | 55.3414 | 18667.3029 | 18667.3029 | 777688.7643 | 18667.3029
| STL006-155193804 | 6 | STL006 | STL | North | 141397.9572 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33421.4206 | 4532.725 | 0 | 0 | 0 | 0 | 141397.9572 | 0
| STL006-155193946 | 63 | STL006 | STL | North | 1484678.5501 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33421.4206 | 4532.725 | 0 | 0 | 0 | 0 | 1484678.5501 | 0
| STL006-155249643 | 57 | STL006 | STL | North | 1343280.5929 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.037207 | 0.037536 | 0.037865 | 0.038194 | 0.038523 | 0.038508 | 0.038493 | 0.038478 | 0.038463 | 0.038448 | 0.038433 | 0.038418 | 0.038402 | 0.038387 | 0.038372 | 0.038357 | 0.038342 | 0.038327 | 0.038312 | 0.038297 | 0.0018823 | 0.0019279 | 0.0019461 | 0.0019597 | 0.0019612 | 0.0019528 | 0.001962 | 0.0019712 | 0.0019495 | 0.0019487 | 0.0019479 | 0.0019472 | 0.0019464 | 0.0019456 | 0.0019449 | 0.0019441 | 0.0019433 | 0.0019426 | 0.0019418 | 0.0019411 | 33421.4206 | 4532.725 | 939.7197 | 127.4479 | 41252.3744 | 41252.3744 | 1343280.5929 | 41252.3744
| STL006-155249816 | 82 | STL006 | STL | North | 1932438.7477 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.054235 | 0.054739 | 0.055242 | 0.055745 | 0.056249 | 0.056434 | 0.056619 | 0.056805 | 0.05699 | 0.057176 | 0.057361 | 0.057547 | 0.057732 | 0.057918 | 0.058103 | 0.058289 | 0.058474 | 0.058659 | 0.058845 | 0.05903 | 0.0027437 | 0.0028114 | 0.0028392 | 0.0028602 | 0.0028636 | 0.0028618 | 0.0028859 | 0.0029102 | 0.0028885 | 0.0028979 | 0.0029073 | 0.0029167 | 0.0029261 | 0.0029355 | 0.0029449 | 0.0029543 | 0.0029637 | 0.0029731 | 0.0029825 | 0.0029919 | 33421.4206 | 4532.725 | 1397.2695 | 189.5024 | 75639.3708 | 75639.3708 | 1932438.7477 | 75639.3708
| STL006-155250434 | 38 | STL006 | STL | North | 895520.3953 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0070497 | 0.0071141 | 0.0071785 | 0.0072429 | 0.0073074 | 0.0073046 | 0.0073019 | 0.0072992 | 0.0072964 | 0.0072937 | 0.007291 | 0.0072883 | 0.0072855 | 0.0072828 | 0.0072801 | 0.0072774 | 0.0072746 | 0.0072719 | 0.0072692 | 0.0072665 | 0.00035664 | 0.00036539 | 0.00036894 | 0.00037163 | 0.00037202 | 0.00037042 | 0.00037218 | 0.00037394 | 0.00036982 | 0.00036968 | 0.00036954 | 0.0003694 | 0.00036926 | 0.00036913 | 0.00036899 | 0.00036885 | 0.00036871 | 0.00036857 | 0.00036843 | 0.0003683 | 33421.4206 | 4532.725 | 178.2371 | 24.1731 | 7824.3679 | 7824.3679 | 895520.3953 | 7824.3679
| STL006-155392225 | 41 | STL006 | STL | North | 966219.3739 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33421.4206 | 4532.725 | 0 | 0 | 0 | 0 | 966219.3739 | 0
| STL006-182934752 | 101 | STL006 | STL | North | 2380198.9454 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.040716 | 0.041139 | 0.041563 | 0.041986 | 0.04241 | 0.042398 | 0.042386 | 0.042375 | 0.042363 | 0.042352 | 0.04234 | 0.042329 | 0.042317 | 0.042305 | 0.042294 | 0.042282 | 0.042271 | 0.042259 | 0.042247 | 0.042236 | 0.0020598 | 0.002113 | 0.0021361 | 0.0021543 | 0.0021591 | 0.00215 | 0.0021605 | 0.0021709 | 0.0021472 | 0.0021466 | 0.002146 | 0.0021454 | 0.0021448 | 0.0021442 | 0.0021436 | 0.002143 | 0.0021425 | 0.0021419 | 0.0021413 | 0.0021407 | 33421.4206 | 4532.725 | 1034.1514 | 140.2551 | 2916.3156 | 2916.3156 | 2380198.9454 | 2916.3156
| STL006-24599342 | 97 | STL006 | STL | North | 2285933.6406 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.54779 | 0.55266 | 0.55753 | 0.5624 | 0.56727 | 0.56873 | 0.57018 | 0.57164 | 0.5731 | 0.57456 | 0.57602 | 0.57748 | 0.57894 | 0.58039 | 0.58185 | 0.58331 | 0.58477 | 0.58623 | 0.58769 | 0.58914 | 0.027712 | 0.028385 | 0.028654 | 0.028856 | 0.028879 | 0.02884 | 0.029063 | 0.029286 | 0.029047 | 0.029121 | 0.029195 | 0.029269 | 0.029343 | 0.029417 | 0.029491 | 0.029565 | 0.029639 | 0.029713 | 0.029787 | 0.02986 | 33421.4206 | 4532.725 | 14044.1534 | 1904.7151 | 117132.0656 | 117132.0656 | 2285933.6406 | 117132.0656
| STL006-24601812 | 297 | STL006 | STL | North | 6999198.879 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 1.816 | 1.8317 | 1.8473 | 1.863 | 1.8787 | 1.8776 | 1.8766 | 1.8756 | 1.8746 | 1.8736 | 1.8726 | 1.8716 | 1.8706 | 1.8696 | 1.8686 | 1.8676 | 1.8666 | 1.8656 | 1.8646 | 1.8636 | 0.091871 | 0.094077 | 0.094945 | 0.095588 | 0.095642 | 0.095216 | 0.095653 | 0.09609 | 0.095014 | 0.094963 | 0.094912 | 0.094861 | 0.09481 | 0.094759 | 0.094708 | 0.094657 | 0.094606 | 0.094555 | 0.094504 | 0.094453 | 33421.4206 | 4532.725 | 45800.132 | 6211.5673 | 448325.5516 | 448325.5516 | 6999198.879 | 448325.5516
| STL006-24613426 | 134 | STL006 | STL | North | 3157887.7097 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 10.4113 | 10.4947 | 10.5782 | 10.6616 | 10.7451 | 10.752 | 10.7589 | 10.7659 | 10.7728 | 10.7797 | 10.7866 | 10.7936 | 10.8005 | 10.8074 | 10.8143 | 10.8212 | 10.8282 | 10.8351 | 10.842 | 10.8489 | 0.52669 | 0.53902 | 0.54367 | 0.54704 | 0.54703 | 0.54524 | 0.54839 | 0.55154 | 0.54601 | 0.54636 | 0.54671 | 0.54706 | 0.54742 | 0.54777 | 0.54812 | 0.54847 | 0.54882 | 0.54917 | 0.54952 | 0.54987 | 33421.4206 | 4532.725 | 263616.7198 | 35752.5824 | 377278.6373 | 377278.6373 | 3157887.7097 | 377278.6373
| STL006-56211052 | 27 | STL006 | STL | North | 636290.8072 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.079468 | 0.079604 | 0.07974 | 0.079875 | 0.080011 | 0.079967 | 0.079922 | 0.079877 | 0.079833 | 0.079788 | 0.079744 | 0.079699 | 0.079654 | 0.07961 | 0.079565 | 0.079521 | 0.079476 | 0.079432 | 0.079387 | 0.079342 | 0.0040202 | 0.0040885 | 0.0040983 | 0.0040983 | 0.0040734 | 0.0040551 | 0.0040737 | 0.0040922 | 0.0040463 | 0.004044 | 0.0040418 | 0.0040395 | 0.0040372 | 0.004035 | 0.0040327 | 0.0040305 | 0.0040282 | 0.0040259 | 0.0040237 | 0.0040214 | 33421.4206 | 4532.725 | 1959.01 | 265.6875 | 13047.9702 | 13047.9702 | 636290.8072 | 13047.9702
| STL006-82629266 | 49 | STL006 | STL | North | 1154749.9834 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.040102 | 0.04042 | 0.040738 | 0.041056 | 0.041374 | 0.041344 | 0.041313 | 0.041283 | 0.041253 | 0.041222 | 0.041192 | 0.041162 | 0.041131 | 0.041101 | 0.041071 | 0.04104 | 0.04101 | 0.040979 | 0.040949 | 0.040919 | 0.0020287 | 0.002076 | 0.0020938 | 0.0021065 | 0.0021064 | 0.0020966 | 0.0021058 | 0.002115 | 0.0020909 | 0.0020893 | 0.0020878 | 0.0020863 | 0.0020847 | 0.0020832 | 0.0020816 | 0.0020801 | 0.0020786 | 0.002077 | 0.0020755 | 0.0020739 | 33421.4206 | 4532.725 | 1008.0977 | 136.7216 | 40280.5051 | 40280.5051 | 1154749.9834 | 40280.5051
| STL006-83365075 | 43 | STL006 | STL | North | 1013352.0262 | 0.0018171 | 0.0018449 | 0.0018461 | 0.001843 | 0.0018287 | 0.0018215 | 0.0018308 | 0.0018402 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.0018206 | 0.082261 | 0.082911 | 0.083561 | 0.084211 | 0.084861 | 0.084768 | 0.084675 | 0.084582 | 0.084489 | 0.084396 | 0.084303 | 0.08421 | 0.084117 | 0.084025 | 0.083932 | 0.083839 | 0.083746 | 0.083653 | 0.08356 | 0.083467 | 0.0041615 | 0.0042584 | 0.0042947 | 0.0043208 | 0.0043203 | 0.0042986 | 0.0043159 | 0.0043332 | 0.0042823 | 0.0042776 | 0.0042729 | 0.0042682 | 0.0042634 | 0.0042587 | 0.004254 | 0.0042493 | 0.0042446 | 0.0042399 | 0.0042352 | 0.0042305 | 33421.4206 | 4532.725 | 2063.9345 | 279.9177 | 32376.0153 | 32376.0153 | 1013352.0262 | 32376.0153
| STL007-143136191 | 1 | STL007 | STL | North | 23566.3262 | 0.0071108 | 0.0071188 | 0.0070524 | 0.006989 | 0.0069117 | 0.0068666 | 0.0068264 | 0.0067801 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0003417 | 0.000345 | 0.0003483 | 0.0003516 | 0.0003549 | 0.0003556 | 0.0003563 | 0.000357 | 0.0003577 | 0.0003584 | 0.0003591 | 0.0003598 | 0.0003605 | 0.0003612 | 0.0003619 | 0.0003626 | 0.0003633 | 0.000364 | 0.0003647 | 0.0003654 | 6.7645e-05 | 6.8374e-05 | 6.8385e-05 | 6.8413e-05 | 6.829e-05 | 6.7979e-05 | 6.7714e-05 | 6.7387e-05 | 6.6961e-05 | 6.7092e-05 | 6.7223e-05 | 6.7354e-05 | 6.7485e-05 | 6.7616e-05 | 6.7747e-05 | 6.7879e-05 | 6.801e-05 | 6.8141e-05 | 6.8272e-05 | 6.8403e-05 | 33421.4206 | 4532.725 | 32.7761 | 4.4452 | 1.7341 | 1.7341 | 23566.3262 | 1.7341
| STL007-143136451 | 140 | STL007 | STL | North | 3299285.6668 | 0.0071108 | 0.0071188 | 0.0070524 | 0.006989 | 0.0069117 | 0.0068666 | 0.0068264 | 0.0067801 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.11923 | 0.1205 | 0.12176 | 0.12303 | 0.1243 | 0.12427 | 0.12423 | 0.1242 | 0.12417 | 0.12414 | 0.1241 | 0.12407 | 0.12404 | 0.12401 | 0.12397 | 0.12394 | 0.12391 | 0.12388 | 0.12385 | 0.12381 | 0.023603 | 0.023881 | 0.023907 | 0.023939 | 0.023918 | 0.023756 | 0.02361 | 0.023444 | 0.023244 | 0.023238 | 0.023232 | 0.023226 | 0.02322 | 0.023214 | 0.023208 | 0.023202 | 0.023196 | 0.02319 | 0.023184 | 0.023178 | 33421.4206 | 4532.725 | 11346.1352 | 1538.8009 | 96427.5685 | 96427.5685 | 3299285.6668 | 96427.5685
| STL007-15415881 | 119 | STL007 | STL | North | 2804392.8168 | 0.0071108 | 0.0071188 | 0.0070524 | 0.006989 | 0.0069117 | 0.0068666 | 0.0068264 | 0.0067801 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 4.9021 | 4.9356 | 4.9692 | 5.0027 | 5.0362 | 5.0384 | 5.0406 | 5.0429 | 5.0451 | 5.0473 | 5.0495 | 5.0517 | 5.054 | 5.0562 | 5.0584 | 5.0606 | 5.0628 | 5.065 | 5.0673 | 5.0695 | 0.97045 | 0.97817 | 0.97564 | 0.9734 | 0.96908 | 0.96318 | 0.95796 | 0.95189 | 0.94444 | 0.94485 | 0.94527 | 0.94568 | 0.9461 | 0.94651 | 0.94693 | 0.94734 | 0.94776 | 0.94817 | 0.94859 | 0.949 | 33421.4206 | 4532.725 | 462434.747 | 62716.9491 | 334733.125 | 334733.125 | 2804392.8168 | 334733.125
| STL007-155179441 | 5 | STL007 | STL | North | 117831.631 | 0.0071108 | 0.0071188 | 0.0070524 | 0.006989 | 0.0069117 | 0.0068666 | 0.0068264 | 0.0067801 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.00038423 | 0.00038817 | 0.00039211 | 0.00039606 | 0.0004 | 0.0004002 | 0.0004004 | 0.0004006 | 0.0004008 | 0.000401 | 0.0004012 | 0.0004014 | 0.0004016 | 0.0004018 | 0.000402 | 0.0004022 | 0.0004024 | 0.0004026 | 0.0004028 | 0.000403 | 7.6064e-05 | 7.693e-05 | 7.6987e-05 | 7.7063e-05 | 7.6969e-05 | 7.6505e-05 | 7.6095e-05 | 7.5617e-05 | 7.503e-05 | 7.5067e-05 | 7.5104e-05 | 7.5142e-05 | 7.5179e-05 | 7.5217e-05 | 7.5254e-05 | 7.5292e-05 | 7.5329e-05 | 7.5366e-05 | 7.5404e-05 | 7.5441e-05 | 33421.4206 | 4532.725 | 36.6594 | 4.9719 | 67.8787 | 67.8787 | 117831.631 | 67.8787
| STL007-155179565 | 103 | STL007 | STL | North | 2427331.5978 | 0.0071108 | 0.0071188 | 0.0070524 | 0.006989 | 0.0069117 | 0.0068666 | 0.0068264 | 0.0067801 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.065502 | 0.065969 | 0.066437 | 0.066904 | 0.067371 | 0.067493 | 0.067615 | 0.067737 | 0.067859 | 0.06798 | 0.068102 | 0.068224 | 0.068346 | 0.068467 | 0.068589 | 0.068711 | 0.068833 | 0.068954 | 0.069076 | 0.069198 | 0.012967 | 0.013074 | 0.013044 | 0.013018 | 0.012964 | 0.012902 | 0.01285 | 0.012786 | 0.012703 | 0.012726 | 0.012749 | 0.012771 | 0.012794 | 0.012817 | 0.01284 | 0.012863 | 0.012885 | 0.012908 | 0.012931 | 0.012954 | 33421.4206 | 4532.725 | 6226.8646 | 844.5082 | 67862.8258 | 67862.8258 | 2427331.5978 | 67862.8258
| STL007-155179964 | 32 | STL007 | STL | North | 754122.4381 | 0.0071108 | 0.0071188 | 0.0070524 | 0.006989 | 0.0069117 | 0.0068666 | 0.0068264 | 0.0067801 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0039759 | 0.0040112 | 0.0040465 | 0.0040818 | 0.0041171 | 0.0041211 | 0.004125 | 0.004129 | 0.0041329 | 0.0041369 | 0.0041408 | 0.0041448 | 0.0041487 | 0.0041527 | 0.0041566 | 0.0041606 | 0.0041645 | 0.0041685 | 0.0041724 | 0.0041764 | 0.0007871 | 0.00079497 | 0.00079449 | 0.00079422 | 0.00079223 | 0.00078782 | 0.00078396 | 0.00077939 | 0.00077368 | 0.00077442 | 0.00077516 | 0.0007759 | 0.00077664 | 0.00077738 | 0.00077812 | 0.00077886 | 0.0007796 | 0.00078034 | 0.00078108 | 0.00078182 | 33421.4206 | 4532.725 | 378.5202 | 51.3362 | 2638.5849 | 2638.5849 | 754122.4381 | 2638.5849
| STL007-162910244 | 76 | STL007 | STL | North | 1791040.7906 | 0.0071108 | 0.0071188 | 0.0070524 | 0.006989 | 0.0069117 | 0.0068666 | 0.0068264 | 0.0067801 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.36296 | 0.36606 | 0.36916 | 0.37227 | 0.37537 | 0.37626 | 0.37714 | 0.37803 | 0.37892 | 0.3798 | 0.38069 | 0.38157 | 0.38246 | 0.38335 | 0.38423 | 0.38512 | 0.386 | 0.38689 | 0.38777 | 0.38866 | 0.071853 | 0.072548 | 0.072481 | 0.072434 | 0.07223 | 0.071928 | 0.071675 | 0.071357 | 0.070933 | 0.071099 | 0.071265 | 0.07143 | 0.071596 | 0.071762 | 0.071928 | 0.072094 | 0.07226 | 0.072425 | 0.072591 | 0.072757 | 33421.4206 | 4532.725 | 34757.1373 | 4713.8794 | 244581.7019 | 244581.7019 | 1791040.7906 | 244581.7019
| STL007-183308767 | 12 | STL007 | STL | North | 282795.9143 | 0.0071108 | 0.0071188 | 0.0070524 | 0.006989 | 0.0069117 | 0.0068666 | 0.0068264 | 0.0067801 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.00076009 | 0.00076731 | 0.00077454 | 0.00078177 | 0.000789 | 0.00079035 | 0.0007917 | 0.00079305 | 0.0007944 | 0.00079575 | 0.0007971 | 0.00079845 | 0.0007998 | 0.00080115 | 0.0008025 | 0.00080385 | 0.0008052 | 0.00080655 | 0.0008079 | 0.00080925 | 0.00015047 | 0.00015207 | 0.00015207 | 0.00015211 | 0.00015182 | 0.00015109 | 0.00015046 | 0.0001497 | 0.00014871 | 0.00014896 | 0.00014922 | 0.00014947 | 0.00014972 | 0.00014997 | 0.00015023 | 0.00015048 | 0.00015073 | 0.00015099 | 0.00015124 | 0.00015149 | 33421.4206 | 4532.725 | 72.7795 | 9.8706 | 323.4472 | 323.4472 | 282795.9143 | 323.4472
| STL007-76065702 | 37 | STL007 | STL | North | 871954.0691 | 0.0071108 | 0.0071188 | 0.0070524 | 0.006989 | 0.0069117 | 0.0068666 | 0.0068264 | 0.0067801 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.076736 | 0.077307 | 0.077878 | 0.078448 | 0.079019 | 0.078923 | 0.078826 | 0.07873 | 0.078633 | 0.078536 | 0.07844 | 0.078343 | 0.078247 | 0.07815 | 0.078053 | 0.077957 | 0.07786 | 0.077764 | 0.077667 | 0.077571 | 0.015191 | 0.015321 | 0.01529 | 0.015264 | 0.015205 | 0.015087 | 0.014981 | 0.014861 | 0.01472 | 0.014702 | 0.014684 | 0.014666 | 0.014648 | 0.01463 | 0.014612 | 0.014593 | 0.014575 | 0.014557 | 0.014539 | 0.014521 | 33421.4206 | 4532.725 | 7193.1535 | 975.5596 | 25266.5505 | 25266.5505 | 871954.0691 | 25266.5505
| STL007-85224567 | 166 | STL007 | STL | North | 3912010.1478 | 0.0071108 | 0.0071188 | 0.0070524 | 0.006989 | 0.0069117 | 0.0068666 | 0.0068264 | 0.0067801 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 1.5876 | 1.6 | 1.6124 | 1.6248 | 1.6372 | 1.6388 | 1.6405 | 1.6421 | 1.6438 | 1.6454 | 1.647 | 1.6487 | 1.6503 | 1.652 | 1.6536 | 1.6553 | 1.6569 | 1.6585 | 1.6602 | 1.6618 | 0.3143 | 0.3171 | 0.31658 | 0.31615 | 0.31503 | 0.31329 | 0.31177 | 0.30997 | 0.30771 | 0.30802 | 0.30833 | 0.30863 | 0.30894 | 0.30925 | 0.30956 | 0.30986 | 0.31017 | 0.31048 | 0.31079 | 0.31109 | 33421.4206 | 4532.725 | 150655.9582 | 20432.4656 | 192927.3956 | 192927.3956 | 3912010.1478 | 192927.3956
| STL007-87836091 | 422 | STL007 | STL | North | 9944989.6529 | 0.0071108 | 0.0071188 | 0.0070524 | 0.006989 | 0.0069117 | 0.0068666 | 0.0068264 | 0.0067801 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 0.0067241 | 7.0539 | 7.093 | 7.132 | 7.171 | 7.2101 | 7.2133 | 7.2166 | 7.2199 | 7.2232 | 7.2265 | 7.2298 | 7.2331 | 7.2364 | 7.2397 | 7.243 | 7.2463 | 7.2496 | 7.2529 | 7.2561 | 7.2594 | 1.3964 | 1.4057 | 1.4003 | 1.3953 | 1.3874 | 1.379 | 1.3715 | 1.3628 | 1.3522 | 1.3528 | 1.3534 | 1.354 | 1.3546 | 1.3553 | 1.3559 | 1.3565 | 1.3571 | 1.3577 | 1.3583 | 1.359 | 33421.4206 | 4532.725 | 662656.6912 | 89871.7197 | 2278424.12 | 2278424.12 | 9944989.6529 | 2278424.12
| STN011-130745907 | 120 | STN011 | STN | North | 2827959.143 | 0.0027852 | 0.0027966 | 0.0028197 | 0.0028281 | 0.0028217 | 0.0028448 | 0.0028892 | 0.0029187 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.071531 | 0.072038 | 0.072546 | 0.073053 | 0.07356 | 0.073708 | 0.073857 | 0.074006 | 0.074154 | 0.074303 | 0.074452 | 0.0746 | 0.074749 | 0.074898 | 0.075046 | 0.075195 | 0.075344 | 0.075492 | 0.075641 | 0.07579 | 0.0055466 | 0.0056086 | 0.0056949 | 0.0057517 | 0.0057785 | 0.0058377 | 0.0059406 | 0.0060135 | 0.005989 | 0.006001 | 0.006013 | 0.006025 | 0.006037 | 0.006049 | 0.006061 | 0.006073 | 0.006085 | 0.006097 | 0.006109 | 0.006121 | 29204.052 | 3430.9349 | 2495.4628 | 293.1706 | 58167.5613 | 58167.5613 | 2827959.143 | 58167.5613
| STN011-160424610 | 94 | STN011 | STN | North | 2215234.662 | 0.0027852 | 0.0027966 | 0.0028197 | 0.0028281 | 0.0028217 | 0.0028448 | 0.0028892 | 0.0029187 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.051784 | 0.052149 | 0.052514 | 0.052879 | 0.053244 | 0.053331 | 0.053418 | 0.053505 | 0.053592 | 0.053679 | 0.053766 | 0.053853 | 0.05394 | 0.054027 | 0.054113 | 0.0542 | 0.054287 | 0.054374 | 0.054461 | 0.054548 | 0.0040154 | 0.0040601 | 0.0041224 | 0.0041634 | 0.0041826 | 0.0042238 | 0.0042966 | 0.0043476 | 0.0043283 | 0.0043353 | 0.0043423 | 0.0043493 | 0.0043563 | 0.0043634 | 0.0043704 | 0.0043774 | 0.0043844 | 0.0043915 | 0.0043985 | 0.0044055 | 29204.052 | 3430.9349 | 1802.7749 | 211.7926 | 53490.9867 | 53490.9867 | 2215234.662 | 53490.9867
| STN011-164271487 | 37 | STN011 | STN | North | 871954.0691 | 0.0027852 | 0.0027966 | 0.0028197 | 0.0028281 | 0.0028217 | 0.0028448 | 0.0028892 | 0.0029187 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 2.4167e-05 | 2.4313e-05 | 2.4459e-05 | 2.4604e-05 | 2.475e-05 | 2.496e-05 | 2.517e-05 | 2.538e-05 | 2.559e-05 | 2.58e-05 | 2.601e-05 | 2.622e-05 | 2.643e-05 | 2.664e-05 | 2.685e-05 | 2.706e-05 | 2.727e-05 | 2.748e-05 | 2.769e-05 | 2.79e-05 | 1.8739e-06 | 1.8929e-06 | 1.92e-06 | 1.9372e-06 | 1.9442e-06 | 1.9768e-06 | 2.0245e-06 | 2.0623e-06 | 2.0667e-06 | 2.0837e-06 | 2.1007e-06 | 2.1176e-06 | 2.1346e-06 | 2.1515e-06 | 2.1685e-06 | 2.1855e-06 | 2.2024e-06 | 2.2194e-06 | 2.2363e-06 | 2.2533e-06 | 29204.052 | 3430.9349 | 0.86756 | 0.10192 | 21.6085 | 21.6085 | 871954.0691 | 21.6085
| STN011-184475628 | 1 | STN011 | STN | North | 23566.3262 | 0.0027852 | 0.0027966 | 0.0028197 | 0.0028281 | 0.0028217 | 0.0028448 | 0.0028892 | 0.0029187 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29204.052 | 3430.9349 | 0 | 0 | 0 | 0 | 23566.3262 | 0
| STN011-200055388 | 553 | STN011 | STN | North | 13032178.3841 | 0.0027852 | 0.0027966 | 0.0028197 | 0.0028281 | 0.0028217 | 0.0028448 | 0.0028892 | 0.0029187 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 0.002901 | 3.4132 | 3.4337 | 3.4541 | 3.4745 | 3.495 | 3.5143 | 3.5337 | 3.5531 | 3.5724 | 3.5918 | 3.6111 | 3.6305 | 3.6499 | 3.6692 | 3.6886 | 3.7079 | 3.7273 | 3.7466 | 3.766 | 3.7854 | 0.26466 | 0.26733 | 0.27115 | 0.27356 | 0.27455 | 0.27834 | 0.28423 | 0.28871 | 0.28852 | 0.29008 | 0.29165 | 0.29321 | 0.29477 | 0.29634 | 0.2979 | 0.29947 | 0.30103 | 0.30259 | 0.30416 | 0.30572 | 29204.052 | 3430.9349 | 120749.6119 | 14185.8416 | 694052.785 | 694052.785 | 13032178.3841 | 694052.785
| STN012-200055438 | 93 | STN012 | STN | North | 2191668.3358 | 0.0016301 | 0.0016594 | 0.0016863 | 0.0017067 | 0.0017188 | 0.0017379 | 0.0017696 | 0.0018018 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29204.052 | 3430.9349 | 0 | 0 | 0 | 0 | 2191668.3358 | 0
| STN012-72075245 | 26 | STN012 | STN | North | 612724.481 | 0.0016301 | 0.0016594 | 0.0016863 | 0.0017067 | 0.0017188 | 0.0017379 | 0.0017696 | 0.0018018 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.0018224 | 0.11408 | 0.11477 | 0.11546 | 0.11615 | 0.11683 | 0.11845 | 0.12006 | 0.12167 | 0.12329 | 0.1249 | 0.12651 | 0.12813 | 0.12974 | 0.13135 | 0.13297 | 0.13458 | 0.13619 | 0.13781 | 0.13942 | 0.14103 | 0.0051774 | 0.0053023 | 0.0054203 | 0.0055185 | 0.0055907 | 0.0057308 | 0.0059148 | 0.0061035 | 0.0062549 | 0.0063368 | 0.0064186 | 0.0065005 | 0.0065823 | 0.0066642 | 0.006746 | 0.0068279 | 0.0069097 | 0.0069916 | 0.0070734 | 0.0071552 | 29204.052 | 3430.9349 | 2592.637 | 304.5868 | 550.3232 | 550.3232 | 612724.481 | 550.3232
| STN013-15421517 | 0 | STN013 | STN | North | 0 | 1.0678 | 1.0688 | 1.0622 | 1.0538 | 1.0438 | 1.0367 | 1.0317 | 1.0283 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29204.052 | 3430.9349 | 0 | 0 | 0 | 0 | 0 | 0
| STN013-200055508 | 2 | STN013 | STN | North | 47132.6524 | 1.0678 | 1.0688 | 1.0622 | 1.0538 | 1.0438 | 1.0367 | 1.0317 | 1.0283 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29204.052 | 3430.9349 | 0 | 0 | 0 | 0 | 47132.6524 | 0
| STN014-200055610 | 8 | STN014 | STN | North | 188530.6095 | 0.0055014 | 0.0056387 | 0.0056749 | 0.0056792 | 0.0056553 | 0.0056553 | 0.0056886 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0.0057269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29204.052 | 3430.9349 | 0 | 0 | 0 | 0 | 188530.6095 | 0
| STN021-164443076 | 28 | STN021 | STN | North | 659857.1334 | 0.0014927 | 0.0015076 | 0.0015151 | 0.00152 | 0.0015183 | 0.0015225 | 0.0015357 | 0.0015532 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29204.052 | 3430.9349 | 0 | 0 | 0 | 0 | 659857.1334 | 0
| STN021-164443183 | 38 | STN021 | STN | North | 895520.3953 | 0.0014927 | 0.0015076 | 0.0015151 | 0.00152 | 0.0015183 | 0.0015225 | 0.0015357 | 0.0015532 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.01948 | 0.019608 | 0.019736 | 0.019864 | 0.019991 | 0.020136 | 0.02028 | 0.020424 | 0.020568 | 0.020713 | 0.020857 | 0.021001 | 0.021145 | 0.02129 | 0.021434 | 0.021578 | 0.021722 | 0.021866 | 0.022011 | 0.022155 | 0.00080949 | 0.00082296 | 0.00083244 | 0.00084059 | 0.00084503 | 0.0008535 | 0.00086707 | 0.00088315 | 0.00089366 | 0.00089993 | 0.0009062 | 0.00091246 | 0.00091873 | 0.000925 | 0.00093126 | 0.00093753 | 0.0009438 | 0.00095006 | 0.00095633 | 0.0009626 | 29204.052 | 3430.9349 | 373.8776 | 43.9237 | 5807.5275 | 5807.5275 | 895520.3953 | 5807.5275
| STN021-193604803 | 253 | STN021 | STN | North | 5962280.5265 | 0.0014927 | 0.0015076 | 0.0015151 | 0.00152 | 0.0015183 | 0.0015225 | 0.0015357 | 0.0015532 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 9.5758 | 9.6326 | 9.6894 | 9.7463 | 9.8031 | 9.8764 | 9.9496 | 10.0228 | 10.096 | 10.1693 | 10.2425 | 10.3157 | 10.3889 | 10.4622 | 10.5354 | 10.6086 | 10.6819 | 10.7551 | 10.8283 | 10.9015 | 0.39792 | 0.40429 | 0.4087 | 0.41245 | 0.41437 | 0.41863 | 0.42539 | 0.43339 | 0.43866 | 0.44184 | 0.44502 | 0.4482 | 0.45138 | 0.45457 | 0.45775 | 0.46093 | 0.46411 | 0.46729 | 0.47047 | 0.47365 | 29204.052 | 3430.9349 | 183635.6566 | 21573.7864 | 976725.0708 | 976725.0708 | 5962280.5265 | 976725.0708
| STN021-200055789 | 35 | STN021 | STN | North | 824821.4167 | 0.0014927 | 0.0015076 | 0.0015151 | 0.00152 | 0.0015183 | 0.0015225 | 0.0015357 | 0.0015532 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0.0015606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29204.052 | 3430.9349 | 0 | 0 | 0 | 0 | 824821.4167 | 0
| STN022-200055843 | 154 | STN022 | STN | North | 3629214.2335 | 0.0012971 | 0.001305 | 0.0013017 | 0.0012988 | 0.0012902 | 0.0012846 | 0.001288 | 0.0012919 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0012873 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.0062175 | 0.00022452 | 0.00022588 | 0.00022532 | 0.00022481 | 0.00022333 | 0.00022235 | 0.00022294 | 0.00022363 | 0.00022283 | 0.00022283 | 0.00022283 | 0.00022283 | 0.00022283 | 0.00022283 | 0.00022283 | 0.00022283 | 0.00022283 | 0.00022283 | 0.00022283 | 0.00022283 | 29204.052 | 3430.9349 | 94.3638 | 11.086 | 111.7712 | 111.7712 | 3629214.2335 | 111.7712
| STN023-200055989 | 24 | STN023 | STN | North | 565591.8286 | 0.0068352 | 0.0068165 | 0.0067172 | 0.006618 | 0.0064925 | 0.0063933 | 0.0063502 | 0.0062996 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0.0062378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29204.052 | 3430.9349 | 0 | 0 | 0 | 0 | 565591.8286 | 0
| STN024-138232567 | 62 | STN024 | STN | North | 1461112.2239 | 0.0046304 | 0.0046758 | 0.0046963 | 0.0046856 | 0.0046381 | 0.0046291 | 0.0047233 | 0.0048052 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.026344 | 0.026524 | 0.026703 | 0.026882 | 0.027061 | 0.027202 | 0.027342 | 0.027482 | 0.027623 | 0.027763 | 0.027904 | 0.028044 | 0.028185 | 0.028325 | 0.028466 | 0.028606 | 0.028746 | 0.028887 | 0.029027 | 0.029168 | 0.003396 | 0.0034527 | 0.0034912 | 0.0035067 | 0.0034943 | 0.0035056 | 0.0035954 | 0.0036765 | 0.0036449 | 0.0036634 | 0.003682 | 0.0037005 | 0.003719 | 0.0037376 | 0.0037561 | 0.0037746 | 0.0037932 | 0.0038117 | 0.0038302 | 0.0038488 | 29204.052 | 3430.9349 | 1531.9211 | 179.9723 | 17700.3581 | 17700.3581 | 1461112.2239 | 17700.3581
| STN024-160253800 | 17 | STN024 | STN | North | 400627.5453 | 0.0046304 | 0.0046758 | 0.0046963 | 0.0046856 | 0.0046381 | 0.0046291 | 0.0047233 | 0.0048052 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 1.7604e-05 | 1.7748e-05 | 1.7892e-05 | 1.8036e-05 | 1.818e-05 | 1.8369e-05 | 1.8558e-05 | 1.8747e-05 | 1.8936e-05 | 1.9125e-05 | 1.9314e-05 | 1.9503e-05 | 1.9692e-05 | 1.9881e-05 | 2.007e-05 | 2.0259e-05 | 2.0448e-05 | 2.0637e-05 | 2.0826e-05 | 2.1015e-05 | 2.2693e-06 | 2.3103e-06 | 2.3393e-06 | 2.3528e-06 | 2.3475e-06 | 2.3673e-06 | 2.4403e-06 | 2.5079e-06 | 2.4986e-06 | 2.5236e-06 | 2.5485e-06 | 2.5735e-06 | 2.5984e-06 | 2.6233e-06 | 2.6483e-06 | 2.6732e-06 | 2.6982e-06 | 2.7231e-06 | 2.748e-06 | 2.773e-06 | 29204.052 | 3430.9349 | 1.0548 | 0.12392 | 18.3768 | 18.3768 | 400627.5453 | 18.3768
| STN024-160253882 | 49 | STN024 | STN | North | 1154749.9834 | 0.0046304 | 0.0046758 | 0.0046963 | 0.0046856 | 0.0046381 | 0.0046291 | 0.0047233 | 0.0048052 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 2.7813e-05 | 2.803e-05 | 2.8247e-05 | 2.8464e-05 | 2.8681e-05 | 2.8972e-05 | 2.9264e-05 | 2.9555e-05 | 2.9847e-05 | 3.0138e-05 | 3.043e-05 | 3.0721e-05 | 3.1013e-05 | 3.1304e-05 | 3.1596e-05 | 3.1887e-05 | 3.2178e-05 | 3.247e-05 | 3.2761e-05 | 3.3053e-05 | 3.5853e-06 | 3.6488e-06 | 3.6931e-06 | 3.7131e-06 | 3.7035e-06 | 3.7338e-06 | 3.8481e-06 | 3.9538e-06 | 3.9384e-06 | 3.9768e-06 | 4.0153e-06 | 4.0537e-06 | 4.0922e-06 | 4.1306e-06 | 4.1691e-06 | 4.2076e-06 | 4.246e-06 | 4.2845e-06 | 4.3229e-06 | 4.3614e-06 | 29204.052 | 3430.9349 | 1.6626 | 0.19532 | 17.2734 | 17.2734 | 1154749.9834 | 17.2734
| STN024-200056045 | 87 | STN024 | STN | North | 2050270.3787 | 0.0046304 | 0.0046758 | 0.0046963 | 0.0046856 | 0.0046381 | 0.0046291 | 0.0047233 | 0.0048052 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29204.052 | 3430.9349 | 0 | 0 | 0 | 0 | 2050270.3787 | 0
| STN024-24605670 | 264 | STN024 | STN | North | 6221510.1146 | 0.0046304 | 0.0046758 | 0.0046963 | 0.0046856 | 0.0046381 | 0.0046291 | 0.0047233 | 0.0048052 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.82165 | 0.82766 | 0.83367 | 0.83968 | 0.84569 | 0.84883 | 0.85196 | 0.8551 | 0.85824 | 0.86138 | 0.86451 | 0.86765 | 0.87079 | 0.87393 | 0.87706 | 0.8802 | 0.88334 | 0.88648 | 0.88961 | 0.89275 | 0.10592 | 0.10774 | 0.109 | 0.10953 | 0.1092 | 0.10939 | 0.11203 | 0.11439 | 0.11325 | 0.11366 | 0.11407 | 0.11449 | 0.1149 | 0.11532 | 0.11573 | 0.11614 | 0.11656 | 0.11697 | 0.11739 | 0.1178 | 29204.052 | 3430.9349 | 47509.19 | 5581.4494 | 169586.2991 | 169586.2991 | 6221510.1146 | 169586.2991
| STN024-24611992 | 53 | STN024 | STN | North | 1249015.2882 | 0.0046304 | 0.0046758 | 0.0046963 | 0.0046856 | 0.0046381 | 0.0046291 | 0.0047233 | 0.0048052 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.0047397 | 0.00046818 | 0.00047196 | 0.00047574 | 0.00047952 | 0.0004833 | 0.00048829 | 0.00049329 | 0.00049828 | 0.00050328 | 0.00050827 | 0.00051327 | 0.00051826 | 0.00052326 | 0.00052825 | 0.00053325 | 0.00053824 | 0.00054324 | 0.00054823 | 0.00055323 | 0.00055822 | 6.0353e-05 | 6.1437e-05 | 6.22e-05 | 6.2552e-05 | 6.2407e-05 | 6.2929e-05 | 6.4866e-05 | 6.6658e-05 | 6.6409e-05 | 6.7068e-05 | 6.7727e-05 | 6.8386e-05 | 6.9045e-05 | 6.9704e-05 | 7.0364e-05 | 7.1023e-05 | 7.1682e-05 | 7.2341e-05 | 7.3e-05 | 7.3659e-05 | 29204.052 | 3430.9349 | 28.0345 | 3.2935 | 338.3828 | 338.3828 | 1249015.2882 | 338.3828
| STN031-200777976 | 1 | STN031 | STN | North | 23566.3262 | 0.011499 | 0.011395 | 0.011199 | 0.010998 | 0.010769 | 0.010574 | 0.010448 | 0.010363 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29204.052 | 3430.9349 | 0 | 0 | 0 | 0 | 23566.3262 | 0
| STN031-200778008 | 66 | STN031 | STN | North | 1555377.5287 | 0.011499 | 0.011395 | 0.011199 | 0.010998 | 0.010769 | 0.010574 | 0.010448 | 0.010363 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0.010212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29204.052 | 3430.9349 | 0 | 0 | 67037.3253 | 67037.3253 | 1555377.5287 | 67037.3253
| SU011-94649597 | 29 | SU011 | SU | South | 527242.9428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 550225.4428 | 0
| SU012-24612934 | 22 | SU012 | SU | South | 399977.4049 | 0.0018379 | 0.0018434 | 0.0018507 | 0.0018585 | 0.0018624 | 0.0018726 | 0.0018952 | 0.0019204 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 417412.4049 | 0
| SU012-24613115 | 11 | SU012 | SU | South | 199988.7024 | 0.0018379 | 0.0018434 | 0.0018507 | 0.0018585 | 0.0018624 | 0.0018726 | 0.0018952 | 0.0019204 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 208706.2024 | 0
| SU012-94649646 | 202 | SU012 | SU | South | 3672519.8086 | 0.0018379 | 0.0018434 | 0.0018507 | 0.0018585 | 0.0018624 | 0.0018726 | 0.0018952 | 0.0019204 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0.0019313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 3832604.8086 | 0
| SU013-94649695 | 121 | SU013 | SU | South | 2199875.7269 | 0.04918 | 0.049895 | 0.050145 | 0.05026 | 0.05026 | 0.05031 | 0.050675 | 0.05119 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0.051405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 2295768.2269 | 0
| SU015-24612538 | 122 | SU015 | SU | South | 2218056.518 | 0.0010972 | 0.0011204 | 0.0011443 | 0.0011653 | 0.0011963 | 0.0012555 | 0.0013273 | 0.0013902 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.74157 | 0.74285 | 0.74413 | 0.74541 | 0.74669 | 0.74776 | 0.74883 | 0.7499 | 0.75097 | 0.75205 | 0.75312 | 0.75419 | 0.75526 | 0.75633 | 0.7574 | 0.75848 | 0.75955 | 0.76062 | 0.76169 | 0.76276 | 0.022653 | 0.02317 | 0.023706 | 0.024183 | 0.024867 | 0.026137 | 0.027671 | 0.029024 | 0.030049 | 0.030092 | 0.030135 | 0.030178 | 0.030221 | 0.030264 | 0.030306 | 0.030349 | 0.030392 | 0.030435 | 0.030478 | 0.030521 | 38519.1568 | 5878.1174 | 15442.9088 | 2356.6256 | 11185.0206 | 14498.2604 | 2314741.518 | 11672.5752
| SU015-94649793 | 139 | SU015 | SU | South | 2527129.9673 | 0.0010972 | 0.0011204 | 0.0011443 | 0.0011653 | 0.0011963 | 0.0012555 | 0.0013273 | 0.0013902 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 2637287.4673 | 0
| SU015-98840126 | 1 | SU015 | SU | South | 18180.7911 | 0.0010972 | 0.0011204 | 0.0011443 | 0.0011653 | 0.0011963 | 0.0012555 | 0.0013273 | 0.0013902 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0.0014373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 18973.2911 | 0
| SU021-40665700 | 266 | SU021 | SU | South | 4836090.441 | 0.0013978 | 0.0014074 | 0.0014101 | 0.0014109 | 0.0014095 | 0.0014113 | 0.0014235 | 0.0014375 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 1.8677 | 1.8787 | 1.8896 | 1.9006 | 1.9116 | 1.9207 | 1.9297 | 1.9388 | 1.9478 | 1.9569 | 1.966 | 1.975 | 1.9841 | 1.9932 | 2.0022 | 2.0113 | 2.0204 | 2.0294 | 2.0385 | 2.0476 | 0.07268 | 0.073612 | 0.074181 | 0.074656 | 0.075013 | 0.075466 | 0.076475 | 0.077589 | 0.078701 | 0.079068 | 0.079434 | 0.0798 | 0.080167 | 0.080533 | 0.080899 | 0.081265 | 0.081632 | 0.081998 | 0.082364 | 0.08273 | 38519.1568 | 5878.1174 | 43330.2689 | 6612.3049 | 84009.0884 | 108894.3581 | 5046895.441 | 87671.0414
| SU021-94649866 | 103 | SU021 | SU | South | 1872621.4865 | 0.0013978 | 0.0014074 | 0.0014101 | 0.0014109 | 0.0014095 | 0.0014113 | 0.0014235 | 0.0014375 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0.0014513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 1954248.9865 | 0
| SU022-186913526 | 94 | SU022 | SU | South | 1708994.3664 | 0.0012399 | 0.0012623 | 0.0012846 | 0.001303 | 0.0013197 | 0.0013426 | 0.0014252 | 0.0015049 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 1783489.3664 | 0
| SU022-94649915 | 104 | SU022 | SU | South | 1890802.2777 | 0.0012399 | 0.0012623 | 0.0012846 | 0.001303 | 0.0013197 | 0.0013426 | 0.0014252 | 0.0015049 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0.001572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 1973222.2777 | 0
| SU023-94649964 | 14 | SU023 | SU | South | 254531.0758 | 0.0036055 | 0.003643 | 0.0036772 | 0.0037004 | 0.003715 | 0.0037506 | 0.0038145 | 0.0038689 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0.0038908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 265626.0758 | 0
| SU024-94650013 | 65 | SU024 | SU | South | 1181751.4235 | 1.5895 | 1.6075 | 1.6157 | 1.6235 | 1.621 | 1.6233 | 1.6355 | 1.6515 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 1.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 1233263.9235 | 0
| SU034-94650323 | 177 | SU034 | SU | South | 3218000.0303 | 0.062716 | 0.064342 | 0.0652 | 0.065994 | 0.066529 | 0.06711 | 0.067987 | 0.069039 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.069684 | 0.00016097 | 0.00016226 | 0.00016355 | 0.00016485 | 0.00016614 | 0.00016661 | 0.00016708 | 0.00016754 | 0.00016801 | 0.00016848 | 0.00016895 | 0.00016942 | 0.00016988 | 0.00017035 | 0.00017082 | 0.00017129 | 0.00017176 | 0.00017222 | 0.00017269 | 0.00017316 | 0.00028106 | 0.00029066 | 0.00029688 | 0.00030287 | 0.00030772 | 0.00031128 | 0.00031623 | 0.00032203 | 0.00032594 | 0.00032685 | 0.00032776 | 0.00032867 | 0.00032957 | 0.00033048 | 0.00033139 | 0.0003323 | 0.00033321 | 0.00033411 | 0.00033502 | 0.00033593 | 38519.1568 | 5878.1174 | 176.5726 | 26.9454 | 100.0021 | 129.6249 | 3358272.5303 | 104.3612
| SU035-183159191 | 114 | SU035 | SU | South | 2072610.189 | 0.0018972 | 0.001942 | 0.0019731 | 0.0019993 | 0.0020138 | 0.0020334 | 0.0020718 | 0.0021109 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.97951 | 0.98705 | 0.99458 | 1.0021 | 1.0097 | 1.016 | 1.0223 | 1.0286 | 1.0349 | 1.0412 | 1.0475 | 1.0538 | 1.0601 | 1.0664 | 1.0727 | 1.0791 | 1.0854 | 1.0917 | 1.098 | 1.1043 | 0.051737 | 0.053364 | 0.054634 | 0.05578 | 0.056606 | 0.057514 | 0.058965 | 0.060448 | 0.06132 | 0.061694 | 0.062068 | 0.062442 | 0.062816 | 0.063189 | 0.063563 | 0.063937 | 0.064311 | 0.064685 | 0.065058 | 0.065432 | 38519.1568 | 5878.1174 | 33244.7269 | 5073.2265 | 7766.5286 | 10067.1387 | 2162955.189 | 8105.0713
| SU035-24612255 | 109 | SU035 | SU | South | 1981706.2333 | 0.0018972 | 0.001942 | 0.0019731 | 0.0019993 | 0.0020138 | 0.0020334 | 0.0020718 | 0.0021109 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 2068088.7333 | 0
| SU035-94650372 | 33 | SU035 | SU | South | 599966.1073 | 0.0018972 | 0.001942 | 0.0019731 | 0.0019993 | 0.0020138 | 0.0020334 | 0.0020718 | 0.0021109 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0.0021283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.1568 | 5878.1174 | 0 | 0 | 0 | 0 | 626118.6073 | 0
| TNA011-155056985 | 315 | TNA011 | TNA | South | 5726949.2064 | 0.0016141 | 0.0010245 | 0.0010743 | 0.0011199 | 0.0011599 | 0.0012034 | 0.0012587 | 0.0013156 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 0.0013586 | 154.352 | 155.7221 | 157.0923 | 158.4624 | 159.8326 | 160.7141 | 161.5955 | 162.4769 | 163.3584 | 164.2398 | 165.1213 | 166.0027 | 166.8842 | 167.7656 | 168.6471 | 169.5285 | 170.41 | 171.2914 | 172.1728 | 173.0543 | 6.936 | 4.4414 | 4.6983 | 4.9406 | 5.1614 | 5.3845 | 5.6628 | 5.951 | 6.179 | 6.2123 | 6.2456 | 6.279 | 6.3123 | 6.3457 | 6.379 | 6.4123 | 6.4457 | 6.479 | 6.5124 | 6.5457 | 38594.8523 | 5980.7106 | 3285506.9904 | 509126.6107 | 1853786.8091 | 2402917.6903 | 5976586.7064 | 1934593.3062
| TNA012-182581784 | 169 | TNA012 | TNA | South | 3072553.7012 | 0.0013584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2279 | 52.68 | 53.132 | 53.584 | 54.036 | 54.2642 | 54.4924 | 54.7205 | 54.9487 | 55.1768 | 55.405 | 55.6331 | 55.8613 | 56.0895 | 56.3176 | 56.5458 | 56.7739 | 57.0021 | 57.2302 | 57.4584 | 1.9752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38594.8523 | 5980.7106 | 74930.7342 | 11611.368 | 351291.4166 | 455351.368 | 3206486.2012 | 366604.1962
| TNA014-154750885 | 80 | TNA014 | TNA | South | 1454463.2905 | 0.10134 | 0.10487 | 0.10702 | 0.10884 | 0.10963 | 0.11069 | 0.11296 | 0.11571 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38594.8523 | 5980.7106 | 0 | 0 | 0 | 0 | 1517863.2905 | 0
| TNA021-154751071 | 135 | TNA021 | TNA | South | 2454406.8027 | 0.0032379 | 0.003378 | 0.0033584 | 0.0033247 | 0.0032796 | 0.0032524 | 0.0032768 | 0.0033033 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 35.5923 | 35.9204 | 36.2486 | 36.5767 | 36.9049 | 37.1159 | 37.327 | 37.5381 | 37.7492 | 37.9602 | 38.1713 | 38.3824 | 38.5935 | 38.8046 | 39.0156 | 39.2267 | 39.4378 | 39.6489 | 39.8599 | 40.071 | 3.2084 | 3.3781 | 3.3892 | 3.3855 | 3.3696 | 3.3607 | 3.4052 | 3.4521 | 3.4774 | 3.4969 | 3.5163 | 3.5358 | 3.5552 | 3.5746 | 3.5941 | 3.6135 | 3.633 | 3.6524 | 3.6719 | 3.6913 | 38594.8523 | 5980.7106 | 1938680.9963 | 300420.6315 | 543218.8162 | 704131.7247 | 2561394.3027 | 566897.7039
| TNA021-158086216 | 75 | TNA021 | TNA | South | 1363559.3349 | 0.0032379 | 0.003378 | 0.0033584 | 0.0033247 | 0.0032796 | 0.0032524 | 0.0032768 | 0.0033033 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.0033089 | 0.5294 | 0.53452 | 0.53964 | 0.54477 | 0.54989 | 0.55318 | 0.55646 | 0.55975 | 0.56304 | 0.56633 | 0.56961 | 0.5729 | 0.57619 | 0.57948 | 0.58276 | 0.58605 | 0.58934 | 0.59263 | 0.59591 | 0.5992 | 0.047722 | 0.050269 | 0.050455 | 0.050424 | 0.050207 | 0.050088 | 0.050764 | 0.051476 | 0.051867 | 0.05217 | 0.052472 | 0.052775 | 0.053078 | 0.053381 | 0.053684 | 0.053987 | 0.054289 | 0.054592 | 0.054895 | 0.055198 | 38594.8523 | 5980.7106 | 28915.5348 | 4480.7904 | 5961.6388 | 7727.6024 | 1422996.8349 | 6221.5064
| TNA022-182581504 | 220 | TNA022 | TNA | South | 3999774.0489 | 0.0011243 | 0.00088223 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 66.276 | 66.8162 | 67.3564 | 67.8966 | 68.4368 | 68.7128 | 68.9887 | 69.2646 | 69.5406 | 69.8165 | 70.0925 | 70.3684 | 70.6444 | 70.9203 | 71.1963 | 71.4722 | 71.7481 | 72.0241 | 72.3 | 72.576 | 2.0744 | 1.6411 | 1.6556 | 1.6689 | 1.6822 | 1.689 | 1.6958 | 1.7025 | 1.7093 | 1.7161 | 1.7229 | 1.7297 | 1.7365 | 1.7432 | 1.75 | 1.7568 | 1.7636 | 1.7704 | 1.7772 | 1.7839 | 38594.8523 | 5980.7106 | 969725.7003 | 150270.0072 | 929003.6813 | 1204194.2305 | 4174124.0489 | 969498.9167
| TNA022-184844358 | 129 | TNA022 | TNA | South | 2345322.056 | 0.0011243 | 0.00088223 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 42.3569 | 42.6954 | 43.0338 | 43.3722 | 43.7106 | 43.9177 | 44.1247 | 44.3317 | 44.5388 | 44.7458 | 44.9528 | 45.1599 | 45.3669 | 45.5739 | 45.781 | 45.988 | 46.195 | 46.402 | 46.6091 | 46.8161 | 1.3258 | 1.0487 | 1.0578 | 1.0661 | 1.0744 | 1.0795 | 1.0846 | 1.0897 | 1.0948 | 1.0999 | 1.105 | 1.11 | 1.1151 | 1.1202 | 1.1253 | 1.1304 | 1.1355 | 1.1406 | 1.1457 | 1.1508 | 38594.8523 | 5980.7106 | 621551.593 | 96316.4762 | 315842.1655 | 409401.2985 | 2447554.556 | 329609.7136
| TNA022-187163239 | 180 | TNA022 | TNA | South | 3272542.4037 | 0.0011243 | 0.00088223 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 2.1879 | 2.2115 | 2.2352 | 2.2589 | 2.2825 | 2.289 | 2.2954 | 2.3019 | 2.3084 | 2.3149 | 2.3213 | 2.3278 | 2.3343 | 2.3407 | 2.3472 | 2.3537 | 2.3602 | 2.3666 | 2.3731 | 2.3796 | 0.068481 | 0.054319 | 0.054942 | 0.055523 | 0.056105 | 0.056264 | 0.056423 | 0.056582 | 0.056741 | 0.0569 | 0.057059 | 0.057218 | 0.057377 | 0.057536 | 0.057695 | 0.057854 | 0.058013 | 0.058173 | 0.058332 | 0.058491 | 38594.8523 | 5980.7106 | 32097.5528 | 4973.8802 | 28891.4127 | 37449.6605 | 3415192.4037 | 30150.7882
| TNA022-194840439 | 115 | TNA022 | TNA | South | 2090790.9801 | 0.0011243 | 0.00088223 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 0.00088291 | 6.1872 | 6.236 | 6.2847 | 6.3335 | 6.3823 | 6.3958 | 6.4093 | 6.4228 | 6.4363 | 6.4498 | 6.4633 | 6.4769 | 6.4904 | 6.5039 | 6.5174 | 6.5309 | 6.5444 | 6.5579 | 6.5714 | 6.5849 | 0.19366 | 0.15316 | 0.15448 | 0.15568 | 0.15688 | 0.15721 | 0.15754 | 0.15787 | 0.15821 | 0.15854 | 0.15887 | 0.1592 | 0.15953 | 0.15987 | 0.1602 | 0.16053 | 0.16086 | 0.1612 | 0.16153 | 0.16186 | 38594.8523 | 5980.7106 | 89608.6876 | 13885.8835 | 126481.7845 | 163948.3656 | 2181928.4801 | 131995.1207
| TNA023-154633087 | 9 | TNA023 | TNA | South | 163627.1202 | 0.0059272 | 0.0058809 | 0.0063983 | 0.0069444 | 0.0074642 | 0.0080338 | 0.0086265 | 0.0091877 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38594.8523 | 5980.7106 | 0 | 0 | 0 | 0 | 170759.6202 | 0
| TNA023-154751161 | 83 | TNA023 | TNA | South | 1509005.6639 | 0.0059272 | 0.0058809 | 0.0063983 | 0.0069444 | 0.0074642 | 0.0080338 | 0.0086265 | 0.0091877 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.0096588 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.57679 | 0.095178 | 0.094436 | 0.10274 | 0.11151 | 0.11986 | 0.12901 | 0.13852 | 0.14754 | 0.1551 | 0.1551 | 0.1551 | 0.1551 | 0.1551 | 0.1551 | 0.1551 | 0.1551 | 0.1551 | 0.1551 | 0.1551 | 0.1551 | 38594.8523 | 5980.7106 | 75974.5138 | 11773.1135 | 2582.045 | 3346.9013 | 1574783.1639 | 2694.5962
| TNA024-154751243 | 39 | TNA024 | TNA | South | 709050.8541 | 0.01633 | 0.016774 | 0.017232 | 0.017594 | 0.017919 | 0.018422 | 0.01909 | 0.019678 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0.019918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38594.8523 | 5980.7106 | 0 | 0 | 0 | 0 | 739958.3541 | 0
| TNA031-188490107 | 244 | TNA031 | TNA | South | 4436113.0361 | 0.003744 | 0.0026354 | 0.002695 | 0.0027528 | 0.0027965 | 0.0028738 | 0.003006 | 0.0031452 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 0.0032572 | 1.3108 | 1.3227 | 1.3346 | 1.3466 | 1.3585 | 1.3645 | 1.3705 | 1.3764 | 1.3824 | 1.3884 | 1.3944 | 1.4003 | 1.4063 | 1.4123 | 1.4182 | 1.4242 | 1.4302 | 1.4362 | 1.4421 | 1.4481 | 0.13663 | 0.097048 | 0.10014 | 0.1032 | 0.10577 | 0.10917 | 0.11469 | 0.12053 | 0.12536 | 0.1259 | 0.12644 | 0.12698 | 0.12752 | 0.12807 | 0.12861 | 0.12915 | 0.12969 | 0.13023 | 0.13077 | 0.13131 | 38594.8523 | 5980.7106 | 66849.7729 | 10359.1313 | 31481.9154 | 40807.525 | 4629483.0361 | 32854.2109
| TNA033-153234693 | 49 | TNA033 | TNA | South | 890858.7654 | 0.0012007 | 0.0012597 | 0.0013214 | 0.0013906 | 0.0014962 | 0.0016105 | 0.0017303 | 0.0018367 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38594.8523 | 5980.7106 | 0 | 0 | 0 | 0 | 929691.2654 | 0
| TNA033-178283696 | 5 | TNA033 | TNA | South | 90903.9557 | 0.0012007 | 0.0012597 | 0.0013214 | 0.0013906 | 0.0014962 | 0.0016105 | 0.0017303 | 0.0018367 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38594.8523 | 5980.7106 | 0 | 0 | 0 | 0 | 94866.4557 | 0
| TNA033-188490077 | 213 | TNA033 | TNA | South | 3872508.511 | 0.0012007 | 0.0012597 | 0.0013214 | 0.0013906 | 0.0014962 | 0.0016105 | 0.0017303 | 0.0018367 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.0019268 | 0.69714 | 0.70532 | 0.71349 | 0.72167 | 0.72984 | 0.72892 | 0.72799 | 0.72707 | 0.72615 | 0.72522 | 0.7243 | 0.72338 | 0.72245 | 0.72153 | 0.7206 | 0.71968 | 0.71876 | 0.71783 | 0.71691 | 0.71599 | 0.023304 | 0.024735 | 0.026249 | 0.02794 | 0.030402 | 0.032682 | 0.035068 | 0.037177 | 0.038953 | 0.038903 | 0.038854 | 0.038804 | 0.038754 | 0.038705 | 0.038655 | 0.038606 | 0.038556 | 0.038507 | 0.038457 | 0.038408 | 38594.8523 | 5980.7106 | 19067.2261 | 2954.6832 | 5822.7496 | 7547.5712 | 4041311.011 | 6076.563
| TQY021-185165057 | 182 | TQY021 | TQY | South | 3308903.9859 | 0.0023964 | 0.0024154 | 0.0024428 | 0.0024538 | 0.0024566 | 0.0024703 | 0.0024928 | 0.0025087 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 32.0833 | 32.367 | 32.6508 | 32.9346 | 33.2183 | 33.1287 | 33.0392 | 32.9496 | 32.86 | 32.7704 | 32.6809 | 32.5913 | 32.5017 | 32.4121 | 32.3225 | 32.233 | 32.1434 | 32.0538 | 31.9642 | 31.8747 | 2.1404 | 2.1765 | 2.2205 | 2.2498 | 2.2718 | 2.2784 | 2.2929 | 2.3013 | 2.2835 | 2.2772 | 2.271 | 2.2648 | 2.2586 | 2.2523 | 2.2461 | 2.2399 | 2.2337 | 2.2274 | 2.2212 | 2.215 | 35123.8703 | 8144.7687 | 1140029.7791 | 264358.0788 | 593538.0214 | 769356.5434 | 3453138.9859 | 619410.3214
| TQY021-187647017 | 236 | TQY021 | TQY | South | 4290666.707 | 0.0023964 | 0.0024154 | 0.0024428 | 0.0024538 | 0.0024566 | 0.0024703 | 0.0024928 | 0.0025087 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 36.7014 | 37.0335 | 37.3657 | 37.6978 | 38.03 | 37.8062 | 37.5824 | 37.3585 | 37.1347 | 36.9109 | 36.6871 | 36.4633 | 36.2395 | 36.0157 | 35.7919 | 35.568 | 35.3442 | 35.1204 | 34.8966 | 34.6728 | 2.4485 | 2.4903 | 2.5412 | 2.5752 | 2.6009 | 2.6001 | 2.6082 | 2.6092 | 2.5805 | 2.565 | 2.5494 | 2.5339 | 2.5183 | 2.5028 | 2.4872 | 2.4716 | 2.4561 | 2.4405 | 2.425 | 2.4094 | 35123.8703 | 8144.7687 | 1283506.0959 | 297628.3706 | 713206.7359 | 924473.6633 | 4477696.707 | 744295.3906
| TQY021-192995237 | 545 | TQY021 | TQY | South | 9908531.1666 | 0.0023964 | 0.0024154 | 0.0024428 | 0.0024538 | 0.0024566 | 0.0024703 | 0.0024928 | 0.0025087 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 34.7884 | 35.1261 | 35.4637 | 35.8013 | 36.1389 | 36.1121 | 36.0852 | 36.0583 | 36.0314 | 36.0046 | 35.9777 | 35.9508 | 35.924 | 35.8971 | 35.8702 | 35.8433 | 35.8165 | 35.7896 | 35.7627 | 35.7358 | 2.3209 | 2.362 | 2.4118 | 2.4457 | 2.4716 | 2.4836 | 2.5043 | 2.5184 | 2.5038 | 2.502 | 2.5001 | 2.4982 | 2.4964 | 2.4945 | 2.4926 | 2.4908 | 2.4889 | 2.487 | 2.4852 | 2.4833 | 35123.8703 | 8144.7687 | 1252124.0894 | 290351.2915 | 1472326.6973 | 1908461.0212 | 10340443.6666 | 1536505.3625
| TQY021-24613536 | 275 | TQY021 | TQY | South | 4999717.5612 | 0.0023964 | 0.0024154 | 0.0024428 | 0.0024538 | 0.0024566 | 0.0024703 | 0.0024928 | 0.0025087 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 0.0024961 | 10.5566 | 10.572 | 10.5875 | 10.6029 | 10.6183 | 10.5716 | 10.5249 | 10.4782 | 10.4315 | 10.3848 | 10.3381 | 10.2914 | 10.2447 | 10.198 | 10.1513 | 10.1046 | 10.0579 | 10.0112 | 9.9645 | 9.9179 | 0.70428 | 0.7109 | 0.72004 | 0.72431 | 0.7262 | 0.72705 | 0.73043 | 0.73183 | 0.72489 | 0.72165 | 0.7184 | 0.71516 | 0.71191 | 0.70867 | 0.70542 | 0.70218 | 0.69893 | 0.69569 | 0.69244 | 0.6892 | 35123.8703 | 8144.7687 | 362901.8484 | 84152.2188 | 433730.3102 | 562210.4064 | 5217655.0612 | 452636.5981
| TQY022-192995279 | 150 | TQY022 | TQY | South | 2727118.6697 | 0.0024397 | 0.0025292 | 0.002579 | 0.0026234 | 0.002653 | 0.0026916 | 0.0027407 | 0.002804 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 13.3301 | 13.3956 | 13.4611 | 13.5265 | 13.592 | 13.5863 | 13.5807 | 13.575 | 13.5693 | 13.5637 | 13.558 | 13.5523 | 13.5467 | 13.541 | 13.5353 | 13.5297 | 13.524 | 13.5183 | 13.5127 | 13.507 | 0.90539 | 0.94323 | 0.96648 | 0.98792 | 1.0039 | 1.0181 | 1.0362 | 1.0597 | 1.0712 | 1.0707 | 1.0703 | 1.0698 | 1.0694 | 1.0689 | 1.0685 | 1.068 | 1.0676 | 1.0671 | 1.0667 | 1.0663 | 35123.8703 | 8144.7687 | 522585.7437 | 121180.8373 | 318184.0535 | 412436.9033 | 2845993.6697 | 332053.6844
| TQY022-88336509 | 39 | TQY022 | TQY | South | 709050.8541 | 0.0024397 | 0.0025292 | 0.002579 | 0.0026234 | 0.002653 | 0.0026916 | 0.0027407 | 0.002804 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 0.0028355 | 17.2971 | 17.4391 | 17.5811 | 17.7231 | 17.8651 | 17.8256 | 17.7861 | 17.7466 | 17.7071 | 17.6675 | 17.628 | 17.5885 | 17.549 | 17.5095 | 17.4699 | 17.4304 | 17.3909 | 17.3514 | 17.3119 | 17.2724 | 1.1748 | 1.2279 | 1.2623 | 1.2944 | 1.3195 | 1.3357 | 1.3571 | 1.3853 | 1.3978 | 1.3947 | 1.3916 | 1.3885 | 1.3853 | 1.3822 | 1.3791 | 1.376 | 1.3729 | 1.3697 | 1.3666 | 1.3635 | 35123.8703 | 8144.7687 | 679127.3438 | 157480.7984 | 60014.7823 | 77792.4309 | 739958.3541 | 62630.8244
| TQY031-156447550 | 388 | TQY031 | TQY | South | 7054146.959 | 0.0027672 | 0.0028191 | 0.002857 | 0.0028963 | 0.0029186 | 0.0029514 | 0.0029865 | 0.0030264 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 28.9671 | 29.0318 | 29.0965 | 29.1611 | 29.2258 | 29.054 | 28.8822 | 28.7104 | 28.5387 | 28.3669 | 28.1951 | 28.0233 | 27.8515 | 27.6797 | 27.5079 | 27.3362 | 27.1644 | 26.9926 | 26.8208 | 26.649 | 2.2316 | 2.2785 | 2.3143 | 2.3514 | 2.3747 | 2.3873 | 2.4014 | 2.419 | 2.4203 | 2.4058 | 2.3912 | 2.3766 | 2.3621 | 2.3475 | 2.3329 | 2.3184 | 2.3038 | 2.2892 | 2.2747 | 2.2601 | 35123.8703 | 8144.7687 | 1190018.4946 | 275949.8118 | 1400181.8738 | 1814945.3744 | 7361636.959 | 1461215.7489
| TQY031-192995335 | 329 | TQY031 | TQY | South | 5981480.2823 | 0.0027672 | 0.0028191 | 0.002857 | 0.0028963 | 0.0029186 | 0.0029514 | 0.0029865 | 0.0030264 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 0.0030463 | 12.275 | 12.3131 | 12.3513 | 12.3894 | 12.4276 | 12.3277 | 12.2279 | 12.128 | 12.0282 | 11.9283 | 11.8285 | 11.7286 | 11.6288 | 11.5289 | 11.4291 | 11.3293 | 11.2294 | 11.1296 | 11.0297 | 10.9299 | 0.94565 | 0.96637 | 0.98239 | 0.999 | 1.0098 | 1.0129 | 1.0167 | 1.0219 | 1.0201 | 1.0116 | 1.0032 | 0.9947 | 0.98623 | 0.97776 | 0.96929 | 0.96083 | 0.95236 | 0.94389 | 0.93542 | 0.92695 | 35123.8703 | 8144.7687 | 499956.907 | 115933.5044 | 622541.8015 | 806951.8568 | 6242212.7823 | 649678.3751
| TQY032-192995307 | 236 | TQY032 | TQY | South | 4290666.707 | 0.0032212 | 0.0034425 | 0.0034238 | 0.0033955 | 0.0033743 | 0.0033566 | 0.0033634 | 0.003392 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 0.00342 | 8.5957 | 8.6413 | 8.6868 | 8.7324 | 8.778 | 8.729 | 8.68 | 8.631 | 8.582 | 8.533 | 8.484 | 8.435 | 8.386 | 8.337 | 8.288 | 8.239 | 8.19 | 8.141 | 8.092 | 8.043 | 0.77086 | 0.82816 | 0.82802 | 0.82549 | 0.82461 | 0.8157 | 0.81278 | 0.81505 | 0.81712 | 0.81246 | 0.80779 | 0.80313 | 0.79846 | 0.7938 | 0.78913 | 0.78447 | 0.7798 | 0.77514 | 0.77047 | 0.7658 | 35123.8703 | 8144.7687 | 408140.2019 | 94642.4046 | 3317287.8153 | 4299938.664 | 4477696.707 | 3461888.2661
| TRG002-154491390 | 9 | TRG002 | TRG | South | 163627.1202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 21.378 | 27.7106 | 170759.6202 | 22.3099
| TRG002-158166546 | 6 | TRG002 | TRG | South | 109084.7468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 15.4252 | 19.9945 | 113839.7468 | 16.0976
| TRG002-158166806 | 3 | TRG002 | TRG | South | 54542.3734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0.3405 | 0.44137 | 56919.8734 | 0.35535
| TRG002-158205190 | 4 | TRG002 | TRG | South | 72723.1645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 10.3164 | 13.3723 | 75893.1645 | 10.7661
| TRG002-158205316 | 5 | TRG002 | TRG | South | 90903.9557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 7.9285 | 10.277 | 94866.4557 | 8.2741
| TRG002-158205503 | 4 | TRG002 | TRG | South | 72723.1645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0 | 0 | 75893.1645 | 0
| TRG002-158205673 | 2 | TRG002 | TRG | South | 36361.5823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 4.9424 | 6.4064 | 37946.5823 | 5.1578
| TRG002-158205847 | 5 | TRG002 | TRG | South | 90903.9557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0.94368 | 1.2232 | 94866.4557 | 0.98481
| TRG002-163035708 | 3 | TRG002 | TRG | South | 54542.3734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 1.7928 | 2.3239 | 56919.8734 | 1.871
| TRG002-163036120 | 7 | TRG002 | TRG | South | 127265.5379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 2121.513 | 2749.9501 | 132813.0379 | 2213.9897
| TRG002-24598160 | 59 | TRG002 | TRG | South | 1072666.6768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 1965.5636 | 2547.8051 | 1119424.1768 | 2051.2424
| TRG002-24598202 | 18 | TRG002 | TRG | South | 327254.2404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 14.5738 | 18.8909 | 341519.2404 | 15.2091
| TRG003-162785300 | 3 | TRG003 | TRG | South | 54542.3734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0 | 0 | 56919.8734 | 0
| TRG003-162785510 | 3 | TRG003 | TRG | South | 54542.3734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0 | 0 | 56919.8734 | 0
| TRG003-163036413 | 3 | TRG003 | TRG | South | 54542.3734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 15.4571 | 20.0358 | 56919.8734 | 16.1309
| TRG003-163036890 | 2 | TRG003 | TRG | South | 36361.5823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0 | 0 | 37946.5823 | 0
| TRG003-163037137 | 4 | TRG003 | TRG | South | 72723.1645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 2.0441 | 2.6495 | 75893.1645 | 2.1332
| TRG003-163066379 | 3 | TRG003 | TRG | South | 54542.3734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0.9924 | 1.2864 | 56919.8734 | 1.0357
| TRG003-60700569 | 14 | TRG003 | TRG | South | 254531.0758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0.26352 | 0.34158 | 265626.0758 | 0.27501
| TRG004-158007081 | 3 | TRG004 | TRG | South | 54542.3734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0.060093 | 0.077894 | 56919.8734 | 0.062713
| TRG004-162802539 | 8 | TRG004 | TRG | South | 145446.3291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 24.8938 | 32.2678 | 151786.3291 | 25.9789
| TRG004-24598258 | 21 | TRG004 | TRG | South | 381796.6138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 6.6177 | 8.578 | 398439.1138 | 6.9062
| TRG005-117365806 | 4 | TRG005 | TRG | South | 72723.1645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 1.3821 | 1.7915 | 75893.1645 | 1.4424
| TRG005-158041024 | 8 | TRG005 | TRG | South | 145446.3291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 4.703 | 6.0961 | 151786.3291 | 4.908
| TRG005-162822850 | 3 | TRG005 | TRG | South | 54542.3734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 1.5752 | 2.0418 | 56919.8734 | 1.6439
| TRG005-162823024 | 2 | TRG005 | TRG | South | 36361.5823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0 | 0 | 37946.5823 | 0
| TRG005-24598286 | 15 | TRG005 | TRG | South | 272711.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 602.1817 | 780.5607 | 284599.367 | 628.4308
| TRG005-60700588 | 14 | TRG005 | TRG | South | 254531.0758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 8.7979 | 11.404 | 265626.0758 | 9.1814
| TRG005-74127795 | 60 | TRG005 | TRG | South | 1090847.4679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0 | 0 | 1138397.4679 | 0
| TRG011-185851173 | 662 | TRG011 | TRG | South | 12035683.729 | 0.0016578 | 0.0016925 | 0.0017075 | 0.0017191 | 0.0017075 | 0.001696 | 0.0017272 | 0.0017572 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 0.0017538 | 1.5685 | 1.5833 | 1.5981 | 1.6129 | 1.6277 | 1.6117 | 1.5958 | 1.5798 | 1.5639 | 1.5479 | 1.532 | 1.5161 | 1.5001 | 1.4842 | 1.4682 | 1.4523 | 1.4364 | 1.4204 | 1.4045 | 1.3885 | 0.072393 | 0.074604 | 0.075969 | 0.077191 | 0.077374 | 0.076097 | 0.076731 | 0.077287 | 0.076356 | 0.075578 | 0.074799 | 0.074021 | 0.073243 | 0.072464 | 0.071686 | 0.070908 | 0.070129 | 0.069351 | 0.068573 | 0.067794 | 31361.1981 | 5633.8693 | 33586.2317 | 6033.5845 | 618075.5524 | 801162.6102 | 12560318.729 | 645017.4424
| TRG013-162785300 | 5 | TRG013 | TRG | South | 90903.9557 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0 | 0 | 94866.4557 | 0
| TRG013-162785510 | 19 | TRG013 | TRG | South | 345435.0315 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 3.227e-05 | 3.2562e-05 | 3.2855e-05 | 3.3147e-05 | 3.344e-05 | 3.3024e-05 | 3.2608e-05 | 3.2192e-05 | 3.1776e-05 | 3.136e-05 | 3.0944e-05 | 3.0528e-05 | 3.0112e-05 | 2.9696e-05 | 2.928e-05 | 2.8864e-05 | 2.8448e-05 | 2.8032e-05 | 2.7616e-05 | 2.72e-05 | 1.5867e-06 | 1.6008e-06 | 1.6181e-06 | 1.6199e-06 | 1.6136e-06 | 1.5879e-06 | 1.5822e-06 | 1.5688e-06 | 1.5207e-06 | 1.5008e-06 | 1.4809e-06 | 1.461e-06 | 1.4411e-06 | 1.4211e-06 | 1.4012e-06 | 1.3813e-06 | 1.3614e-06 | 1.3415e-06 | 1.3216e-06 | 1.3017e-06 | 31361.1981 | 5633.8693 | 0.68276 | 0.12265 | 9.7266 | 12.6078 | 360492.5315 | 10.1506
| TRG013-162806327 | 9 | TRG013 | TRG | South | 163627.1202 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.00086314 | 0.00087686 | 0.00089057 | 0.00090429 | 0.000918 | 0.00090425 | 0.0008905 | 0.00087675 | 0.000863 | 0.00084925 | 0.0008355 | 0.00082175 | 0.000808 | 0.00079425 | 0.0007805 | 0.00076675 | 0.000753 | 0.00073925 | 0.0007255 | 0.00071175 | 4.2441e-05 | 4.3108e-05 | 4.3862e-05 | 4.4192e-05 | 4.4297e-05 | 4.348e-05 | 4.3208e-05 | 4.2726e-05 | 4.13e-05 | 4.0642e-05 | 3.9984e-05 | 3.9326e-05 | 3.8668e-05 | 3.801e-05 | 3.7352e-05 | 3.6694e-05 | 3.6036e-05 | 3.5378e-05 | 3.472e-05 | 3.4062e-05 | 31361.1981 | 5633.8693 | 18.4058 | 3.3065 | 198.7175 | 257.5818 | 170759.6202 | 207.3796
| TRG013-162823585 | 31 | TRG013 | TRG | South | 563604.5251 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.011334 | 0.011436 | 0.011537 | 0.011639 | 0.011741 | 0.011619 | 0.011497 | 0.011376 | 0.011254 | 0.011132 | 0.011011 | 0.010889 | 0.010768 | 0.010646 | 0.010524 | 0.010403 | 0.010281 | 0.010159 | 0.010038 | 0.0099162 | 0.00055728 | 0.00056219 | 0.00056822 | 0.00056879 | 0.00056653 | 0.00055868 | 0.00055786 | 0.00055436 | 0.00053858 | 0.00053276 | 0.00052694 | 0.00052112 | 0.0005153 | 0.00050948 | 0.00050366 | 0.00049784 | 0.00049202 | 0.0004862 | 0.00048038 | 0.00047456 | 31361.1981 | 5633.8693 | 242.3926 | 43.5445 | 3756.3798 | 4869.099 | 588172.0251 | 3920.1202
| TRG013-162823910 | 20 | TRG013 | TRG | South | 363615.8226 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.00012013 | 0.00012151 | 0.00012288 | 0.00012426 | 0.00012564 | 0.00012371 | 0.00012179 | 0.00011986 | 0.00011794 | 0.00011601 | 0.00011408 | 0.00011216 | 0.00011023 | 0.00010831 | 0.00010638 | 0.00010445 | 0.00010253 | 0.0001006 | 9.8676e-05 | 9.675e-05 | 5.9066e-06 | 5.9734e-06 | 6.0521e-06 | 6.0727e-06 | 6.0626e-06 | 5.9486e-06 | 5.9093e-06 | 5.8411e-06 | 5.644e-06 | 5.5518e-06 | 5.4597e-06 | 5.3675e-06 | 5.2753e-06 | 5.1832e-06 | 5.091e-06 | 4.9988e-06 | 4.9066e-06 | 4.8145e-06 | 4.7223e-06 | 4.6301e-06 | 31361.1981 | 5633.8693 | 2.5216 | 0.45298 | 33.6075 | 43.5628 | 379465.8226 | 35.0725
| TRG013-162824119 | 36 | TRG013 | TRG | South | 654508.4807 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 2.9007e-06 | 2.954e-06 | 3.0073e-06 | 3.0607e-06 | 3.114e-06 | 3.0456e-06 | 2.9772e-06 | 2.9088e-06 | 2.8404e-06 | 2.772e-06 | 2.7036e-06 | 2.6352e-06 | 2.5668e-06 | 2.4984e-06 | 2.43e-06 | 2.3616e-06 | 2.2932e-06 | 2.2248e-06 | 2.1564e-06 | 2.088e-06 | 1.4263e-07 | 1.4522e-07 | 1.4811e-07 | 1.4957e-07 | 1.5026e-07 | 1.4644e-07 | 1.4446e-07 | 1.4175e-07 | 1.3593e-07 | 1.3266e-07 | 1.2939e-07 | 1.2611e-07 | 1.2284e-07 | 1.1956e-07 | 1.1629e-07 | 1.1302e-07 | 1.0974e-07 | 1.0647e-07 | 1.032e-07 | 9.9925e-08 | 31361.1981 | 5633.8693 | 0.059962 | 0.010772 | 1.4382 | 1.8642 | 683038.4807 | 1.5008
| TRG013-163036413 | 8 | TRG013 | TRG | South | 145446.3291 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 6.4594e-07 | 6.5246e-07 | 6.5897e-07 | 6.6549e-07 | 6.72e-07 | 6.6435e-07 | 6.567e-07 | 6.4905e-07 | 6.414e-07 | 6.3375e-07 | 6.261e-07 | 6.1845e-07 | 6.108e-07 | 6.0315e-07 | 5.955e-07 | 5.8785e-07 | 5.802e-07 | 5.7255e-07 | 5.649e-07 | 5.5725e-07 | 3.1761e-08 | 3.2076e-08 | 3.2455e-08 | 3.2522e-08 | 3.2427e-08 | 3.1944e-08 | 3.1864e-08 | 3.163e-08 | 3.0695e-08 | 3.0329e-08 | 2.9963e-08 | 2.9597e-08 | 2.9231e-08 | 2.8865e-08 | 2.8499e-08 | 2.8132e-08 | 2.7766e-08 | 2.74e-08 | 2.7034e-08 | 2.6668e-08 | 31361.1981 | 5633.8693 | 0.013789 | 0.0024771 | 0.44114 | 0.57181 | 151786.3291 | 0.46037
| TRG013-163036626 | 3 | TRG013 | TRG | South | 54542.3734 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 3.3597e-07 | 3.4247e-07 | 3.4898e-07 | 3.5549e-07 | 3.62e-07 | 3.56e-07 | 3.5e-07 | 3.44e-07 | 3.38e-07 | 3.32e-07 | 3.26e-07 | 3.2e-07 | 3.14e-07 | 3.08e-07 | 3.02e-07 | 2.96e-07 | 2.9e-07 | 2.84e-07 | 2.78e-07 | 2.72e-07 | 1.6519e-08 | 1.6837e-08 | 1.7188e-08 | 1.7373e-08 | 1.7468e-08 | 1.7118e-08 | 1.6982e-08 | 1.6764e-08 | 1.6176e-08 | 1.5888e-08 | 1.5601e-08 | 1.5314e-08 | 1.5027e-08 | 1.474e-08 | 1.4453e-08 | 1.4166e-08 | 1.3878e-08 | 1.3591e-08 | 1.3304e-08 | 1.3017e-08 | 31361.1981 | 5633.8693 | 0.0071789 | 0.0012897 | 0.12917 | 0.16744 | 56919.8734 | 0.1348
| TRG013-163036890 | 13 | TRG013 | TRG | South | 236350.2847 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 5.2806e-06 | 5.3554e-06 | 5.4303e-06 | 5.5051e-06 | 5.58e-06 | 5.489e-06 | 5.398e-06 | 5.307e-06 | 5.216e-06 | 5.125e-06 | 5.034e-06 | 4.943e-06 | 4.852e-06 | 4.761e-06 | 4.67e-06 | 4.579e-06 | 4.488e-06 | 4.397e-06 | 4.306e-06 | 4.215e-06 | 2.5965e-07 | 2.6328e-07 | 2.6745e-07 | 2.6904e-07 | 2.6926e-07 | 2.6393e-07 | 2.6192e-07 | 2.5862e-07 | 2.4962e-07 | 2.4527e-07 | 2.4091e-07 | 2.3656e-07 | 2.322e-07 | 2.2785e-07 | 2.2349e-07 | 2.1914e-07 | 2.1478e-07 | 2.1043e-07 | 2.0607e-07 | 2.0172e-07 | 31361.1981 | 5633.8693 | 0.11119 | 0.019975 | 1.7339 | 2.2475 | 246652.7847 | 1.8095
| TRG013-163037137 | 8 | TRG013 | TRG | South | 145446.3291 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.0022992 | 0.0023176 | 0.002336 | 0.0023544 | 0.0023728 | 0.0023503 | 0.0023278 | 0.0023052 | 0.0022827 | 0.0022602 | 0.0022377 | 0.0022151 | 0.0021926 | 0.0021701 | 0.0021476 | 0.002125 | 0.0021025 | 0.00208 | 0.0020574 | 0.0020349 | 0.00011305 | 0.00011394 | 0.00011505 | 0.00011506 | 0.0001145 | 0.00011301 | 0.00011295 | 0.00011234 | 0.00010924 | 0.00010817 | 0.00010709 | 0.00010601 | 0.00010493 | 0.00010385 | 0.00010277 | 0.0001017 | 0.00010062 | 9.954e-05 | 9.8462e-05 | 9.7384e-05 | 31361.1981 | 5633.8693 | 49.2441 | 8.8464 | 945.3373 | 1225.3662 | 151786.3291 | 986.5445
| TRG013-163037241 | 19 | TRG013 | TRG | South | 345435.0315 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.0020909 | 0.0021082 | 0.0021254 | 0.0021427 | 0.0021599 | 0.0021387 | 0.0021175 | 0.0020963 | 0.0020751 | 0.0020539 | 0.0020328 | 0.0020116 | 0.0019904 | 0.0019692 | 0.001948 | 0.0019268 | 0.0019056 | 0.0018844 | 0.0018632 | 0.001842 | 0.00010281 | 0.00010364 | 0.00010468 | 0.00010471 | 0.00010422 | 0.00010284 | 0.00010274 | 0.00010216 | 9.9309e-05 | 9.8295e-05 | 9.7281e-05 | 9.6266e-05 | 9.5252e-05 | 9.4238e-05 | 9.3224e-05 | 9.221e-05 | 9.1196e-05 | 9.0182e-05 | 8.9168e-05 | 8.8154e-05 | 31361.1981 | 5633.8693 | 44.7433 | 8.0379 | 2549.9349 | 3305.2796 | 360492.5315 | 2661.0864
| TRG013-163065605 | 25 | TRG013 | TRG | South | 454519.7783 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.00010577 | 0.00010691 | 0.00010806 | 0.0001092 | 0.00011034 | 0.00010876 | 0.00010719 | 0.00010561 | 0.00010404 | 0.00010247 | 0.00010089 | 9.9315e-05 | 9.774e-05 | 9.6165e-05 | 9.459e-05 | 9.3015e-05 | 9.144e-05 | 8.9865e-05 | 8.829e-05 | 8.6715e-05 | 5.2009e-06 | 5.2561e-06 | 5.3219e-06 | 5.3365e-06 | 5.3243e-06 | 5.2298e-06 | 5.201e-06 | 5.1468e-06 | 4.979e-06 | 4.9036e-06 | 4.8283e-06 | 4.7529e-06 | 4.6775e-06 | 4.6021e-06 | 4.5268e-06 | 4.4514e-06 | 4.376e-06 | 4.3006e-06 | 4.2253e-06 | 4.1499e-06 | 31361.1981 | 5633.8693 | 2.2282 | 0.40029 | 37.1237 | 48.1205 | 474332.2783 | 38.7419
| TRG013-163065814 | 24 | TRG013 | TRG | South | 436338.9872 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.0002388 | 0.0002406 | 0.0002424 | 0.0002442 | 0.000246 | 0.000243 | 0.00024 | 0.000237 | 0.000234 | 0.000231 | 0.000228 | 0.000225 | 0.000222 | 0.000219 | 0.000216 | 0.000213 | 0.00021 | 0.000207 | 0.000204 | 0.000201 | 1.1742e-05 | 1.1828e-05 | 1.1938e-05 | 1.1934e-05 | 1.187e-05 | 1.1684e-05 | 1.1645e-05 | 1.155e-05 | 1.1198e-05 | 1.1055e-05 | 1.0911e-05 | 1.0768e-05 | 1.0624e-05 | 1.0481e-05 | 1.0337e-05 | 1.0193e-05 | 1.005e-05 | 9.9063e-06 | 9.7627e-06 | 9.6192e-06 | 31361.1981 | 5633.8693 | 5.0344 | 0.90441 | 144.9497 | 187.8869 | 455358.9872 | 151.2681
| TRG013-163066137 | 18 | TRG013 | TRG | South | 327254.2404 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.0074077 | 0.0075102 | 0.0076128 | 0.0077153 | 0.0078178 | 0.007687 | 0.0075562 | 0.0074254 | 0.0072946 | 0.0071638 | 0.007033 | 0.0069022 | 0.0067714 | 0.0066406 | 0.0065098 | 0.006379 | 0.0062482 | 0.0061174 | 0.0059866 | 0.0058558 | 0.00036424 | 0.00036922 | 0.00037494 | 0.00037705 | 0.00037724 | 0.00036962 | 0.00036664 | 0.00036186 | 0.0003491 | 0.00034284 | 0.00033658 | 0.00033032 | 0.00032406 | 0.0003178 | 0.00031154 | 0.00030528 | 0.00029902 | 0.00029276 | 0.0002865 | 0.00028024 | 31361.1981 | 5633.8693 | 155.4608 | 27.9277 | 2097.8043 | 2719.2184 | 341519.2404 | 2189.2476
| TRG013-163066379 | 10 | TRG013 | TRG | South | 181807.9113 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0 | 0 | 189732.9113 | 0
| TRG013-163066765 | 28 | TRG013 | TRG | South | 509062.1517 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.00038643 | 0.00039153 | 0.00039662 | 0.00040171 | 0.0004068 | 0.00040032 | 0.00039384 | 0.00038736 | 0.00038088 | 0.0003744 | 0.00036792 | 0.00036144 | 0.00035496 | 0.00034848 | 0.000342 | 0.00033552 | 0.00032904 | 0.00032256 | 0.00031608 | 0.0003096 | 1.9001e-05 | 1.9248e-05 | 1.9534e-05 | 1.9631e-05 | 1.963e-05 | 1.9249e-05 | 1.911e-05 | 1.8877e-05 | 1.8228e-05 | 1.7918e-05 | 1.7607e-05 | 1.7297e-05 | 1.6987e-05 | 1.6677e-05 | 1.6367e-05 | 1.6057e-05 | 1.5747e-05 | 1.5437e-05 | 1.5127e-05 | 1.4816e-05 | 31361.1981 | 5633.8693 | 8.1285 | 1.4602 | 303.3428 | 393.1993 | 531252.1517 | 316.5655
| TRG013-176898414 | 787 | TRG013 | TRG | South | 14308282.6205 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.81098 | 0.81968 | 0.82838 | 0.83707 | 0.84577 | 0.83276 | 0.81975 | 0.80674 | 0.79373 | 0.78071 | 0.7677 | 0.75469 | 0.74168 | 0.72867 | 0.71565 | 0.70264 | 0.68963 | 0.67662 | 0.66361 | 0.65059 | 0.039876 | 0.040297 | 0.040798 | 0.040908 | 0.040812 | 0.040042 | 0.039775 | 0.039314 | 0.037985 | 0.037362 | 0.03674 | 0.036117 | 0.035494 | 0.034871 | 0.034249 | 0.033626 | 0.033003 | 0.032381 | 0.031758 | 0.031135 | 31361.1981 | 5633.8693 | 16977.834 | 3049.9759 | 358139.8465 | 464228.4477 | 14931980.1205 | 373751.1489
| TRG013-176898441 | 267 | TRG013 | TRG | South | 4854271.2321 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.47264 | 0.47667 | 0.48069 | 0.48471 | 0.48873 | 0.48373 | 0.47874 | 0.47374 | 0.46874 | 0.46374 | 0.45875 | 0.45375 | 0.44875 | 0.44375 | 0.43876 | 0.43376 | 0.42876 | 0.42376 | 0.41876 | 0.41377 | 0.02324 | 0.023434 | 0.023674 | 0.023688 | 0.023583 | 0.02326 | 0.023229 | 0.023086 | 0.022432 | 0.022193 | 0.021954 | 0.021715 | 0.021476 | 0.021236 | 0.020997 | 0.020758 | 0.020519 | 0.02028 | 0.020041 | 0.019801 | 31361.1981 | 5633.8693 | 10100.4379 | 1814.4889 | 38511.943 | 49919.9954 | 5065868.7321 | 40190.6771
| TRG013-185851126 | 626 | TRG013 | TRG | South | 11381175.2483 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 4.0416 | 4.0755 | 4.1094 | 4.1434 | 4.1773 | 4.1387 | 4.1 | 4.0613 | 4.0227 | 3.984 | 3.9453 | 3.9067 | 3.868 | 3.8293 | 3.7906 | 3.752 | 3.7133 | 3.6746 | 3.636 | 3.5973 | 0.19872 | 0.20036 | 0.20239 | 0.20249 | 0.20157 | 0.199 | 0.19894 | 0.19792 | 0.19251 | 0.19066 | 0.18881 | 0.18696 | 0.18511 | 0.18326 | 0.18141 | 0.17956 | 0.17771 | 0.17586 | 0.17401 | 0.17216 | 31361.1981 | 5633.8693 | 86779.3803 | 15589.4455 | 409707.5365 | 531071.5787 | 11877280.2483 | 427566.6726
| TRG013-60700569 | 106 | TRG013 | TRG | South | 1927163.8599 | 0.0017662 | 0.0017659 | 0.0017691 | 0.0017554 | 0.0017333 | 0.0017271 | 0.0017429 | 0.0017504 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.001719 | 0.45797 | 0.45893 | 0.45988 | 0.46083 | 0.46178 | 0.45973 | 0.45767 | 0.45561 | 0.45355 | 0.45149 | 0.44943 | 0.44737 | 0.44531 | 0.44325 | 0.44119 | 0.43913 | 0.43707 | 0.43501 | 0.43295 | 0.43089 | 0.022519 | 0.022562 | 0.02265 | 0.022521 | 0.022283 | 0.022105 | 0.022207 | 0.022203 | 0.021705 | 0.021607 | 0.021508 | 0.02141 | 0.021311 | 0.021212 | 0.021114 | 0.021015 | 0.020917 | 0.020818 | 0.02072 | 0.020621 | 31361.1981 | 5633.8693 | 9875.7284 | 1774.1211 | 32884.5495 | 42625.649 | 2011168.8599 | 34317.9858
| TRG014-158007081 | 35 | TRG014 | TRG | South | 636327.6896 | 0.0012382 | 0.0012361 | 0.0012422 | 0.0012361 | 0.0012228 | 0.0012228 | 0.0012351 | 0.0012422 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 9.4025e-05 | 9.4999e-05 | 9.5973e-05 | 9.6946e-05 | 9.792e-05 | 9.6112e-05 | 9.4304e-05 | 9.2496e-05 | 9.0688e-05 | 8.888e-05 | 8.7072e-05 | 8.5264e-05 | 8.3456e-05 | 8.1648e-05 | 7.984e-05 | 7.8032e-05 | 7.6224e-05 | 7.4416e-05 | 7.2608e-05 | 7.08e-05 | 3.2412e-06 | 3.2691e-06 | 3.3191e-06 | 3.3361e-06 | 3.3335e-06 | 3.2719e-06 | 3.2427e-06 | 3.1988e-06 | 3.0896e-06 | 3.028e-06 | 2.9664e-06 | 2.9048e-06 | 2.8432e-06 | 2.7816e-06 | 2.72e-06 | 2.6584e-06 | 2.5968e-06 | 2.5352e-06 | 2.4737e-06 | 2.4121e-06 | 31361.1981 | 5633.8693 | 1.3688 | 0.2459 | 50.7184 | 65.7423 | 664065.1896 | 52.9292
| TRG014-162802339 | 25 | TRG014 | TRG | South | 454519.7783 | 0.0012382 | 0.0012361 | 0.0012422 | 0.0012361 | 0.0012228 | 0.0012228 | 0.0012351 | 0.0012422 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.000975 | 0.0009822 | 0.0009894 | 0.0009966 | 0.0010038 | 0.00099029 | 0.00097678 | 0.00096327 | 0.00094976 | 0.00093625 | 0.00092274 | 0.00090923 | 0.00089572 | 0.00088221 | 0.0008687 | 0.00085519 | 0.00084168 | 0.00082817 | 0.00081466 | 0.00080115 | 3.361e-05 | 3.3799e-05 | 3.4217e-05 | 3.4295e-05 | 3.4172e-05 | 3.3712e-05 | 3.3588e-05 | 3.3313e-05 | 3.2357e-05 | 3.1897e-05 | 3.1436e-05 | 3.0976e-05 | 3.0516e-05 | 3.0056e-05 | 2.9595e-05 | 2.9135e-05 | 2.8675e-05 | 2.8215e-05 | 2.7754e-05 | 2.7294e-05 | 31361.1981 | 5633.8693 | 14.4506 | 2.596 | 437.1326 | 566.6205 | 474332.2783 | 456.1872
| TRG014-162802539 | 16 | TRG014 | TRG | South | 290892.6581 | 0.0012382 | 0.0012361 | 0.0012422 | 0.0012361 | 0.0012228 | 0.0012228 | 0.0012351 | 0.0012422 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0013975 | 0.0014117 | 0.0014259 | 0.00144 | 0.0014542 | 0.0014382 | 0.0014222 | 0.0014062 | 0.0013902 | 0.0013741 | 0.0013581 | 0.0013421 | 0.0013261 | 0.0013101 | 0.0012941 | 0.0012781 | 0.0012621 | 0.001246 | 0.00123 | 0.001214 | 4.8175e-05 | 4.8579e-05 | 4.9311e-05 | 4.9554e-05 | 4.9505e-05 | 4.896e-05 | 4.8903e-05 | 4.863e-05 | 4.7361e-05 | 4.6815e-05 | 4.627e-05 | 4.5724e-05 | 4.5179e-05 | 4.4633e-05 | 4.4087e-05 | 4.3542e-05 | 4.2996e-05 | 4.2451e-05 | 4.1905e-05 | 4.136e-05 | 31361.1981 | 5633.8693 | 21.1725 | 3.8035 | 819.8552 | 1062.7136 | 303572.6581 | 855.5926
| TRG014-182935203 | 25 | TRG014 | TRG | South | 454519.7783 | 0.0012382 | 0.0012361 | 0.0012422 | 0.0012361 | 0.0012228 | 0.0012228 | 0.0012351 | 0.0012422 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 5.6746e-05 | 5.723e-05 | 5.7713e-05 | 5.8197e-05 | 5.868e-05 | 5.796e-05 | 5.724e-05 | 5.652e-05 | 5.58e-05 | 5.508e-05 | 5.436e-05 | 5.364e-05 | 5.292e-05 | 5.22e-05 | 5.148e-05 | 5.076e-05 | 5.004e-05 | 4.932e-05 | 4.86e-05 | 4.788e-05 | 1.9561e-06 | 1.9694e-06 | 1.9959e-06 | 2.0026e-06 | 1.9976e-06 | 1.9731e-06 | 1.9683e-06 | 1.9547e-06 | 1.901e-06 | 1.8765e-06 | 1.852e-06 | 1.8274e-06 | 1.8029e-06 | 1.7784e-06 | 1.7539e-06 | 1.7293e-06 | 1.7048e-06 | 1.6803e-06 | 1.6557e-06 | 1.6312e-06 | 31361.1981 | 5633.8693 | 0.84953 | 0.15261 | 19.9881 | 25.909 | 474332.2783 | 20.8594
| TRG014-185851238 | 197 | TRG014 | TRG | South | 3581615.8529 | 0.0012382 | 0.0012361 | 0.0012422 | 0.0012361 | 0.0012228 | 0.0012228 | 0.0012351 | 0.0012422 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 2.5736 | 2.5982 | 2.6228 | 2.6474 | 2.672 | 2.6487 | 2.6254 | 2.6021 | 2.5788 | 2.5556 | 2.5323 | 2.509 | 2.4857 | 2.4624 | 2.4391 | 2.4158 | 2.3925 | 2.3693 | 2.346 | 2.3227 | 0.088717 | 0.089409 | 0.090705 | 0.091101 | 0.090962 | 0.090169 | 0.090278 | 0.08999 | 0.087857 | 0.087064 | 0.086271 | 0.085477 | 0.084684 | 0.083891 | 0.083097 | 0.082304 | 0.08151 | 0.080717 | 0.079924 | 0.07913 | 31361.1981 | 5633.8693 | 39393.9103 | 7076.9025 | 81426.8296 | 105547.1796 | 3737738.3529 | 84976.2221
| TRG014-24598258 | 595 | TRG014 | TRG | South | 10817570.7232 | 0.0012382 | 0.0012361 | 0.0012422 | 0.0012361 | 0.0012228 | 0.0012228 | 0.0012351 | 0.0012422 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 0.0012237 | 1.1033 | 1.1106 | 1.1178 | 1.1251 | 1.1324 | 1.1241 | 1.1158 | 1.1075 | 1.0992 | 1.0909 | 1.0826 | 1.0743 | 1.0659 | 1.0576 | 1.0493 | 1.041 | 1.0327 | 1.0244 | 1.0161 | 1.0078 | 0.038032 | 0.038216 | 0.038658 | 0.038717 | 0.03855 | 0.038267 | 0.038367 | 0.0383 | 0.037447 | 0.037164 | 0.036881 | 0.036598 | 0.036315 | 0.036032 | 0.035749 | 0.035466 | 0.035183 | 0.0349 | 0.034618 | 0.034335 | 31361.1981 | 5633.8693 | 16848.8934 | 3026.8124 | 343062.9846 | 444685.5002 | 11289108.2232 | 358017.0871
| TRG022-142033811 | 111 | TRG022 | TRG | South | 2018067.8156 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.053664 | 0.054231 | 0.054798 | 0.055365 | 0.055932 | 0.055428 | 0.054924 | 0.054419 | 0.053915 | 0.053411 | 0.052907 | 0.052403 | 0.051898 | 0.051394 | 0.05089 | 0.050386 | 0.049882 | 0.049378 | 0.048873 | 0.048369 | 0.0019553 | 0.0019873 | 0.0020347 | 0.0020519 | 0.0020601 | 0.0020516 | 0.0020699 | 0.0020736 | 0.0020169 | 0.0019981 | 0.0019792 | 0.0019604 | 0.0019415 | 0.0019226 | 0.0019038 | 0.0018849 | 0.001866 | 0.0018472 | 0.0018283 | 0.0018095 | 31361.1981 | 5633.8693 | 895.5628 | 160.883 | 25788.136 | 33427.1276 | 2106035.3156 | 26912.2399
| TRG022-154491351 | 78 | TRG022 | TRG | South | 1418101.7083 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.014618 | 0.01474 | 0.014863 | 0.014985 | 0.015108 | 0.015033 | 0.014958 | 0.014884 | 0.014809 | 0.014734 | 0.01466 | 0.014585 | 0.01451 | 0.014436 | 0.014361 | 0.014286 | 0.014212 | 0.014137 | 0.014062 | 0.013988 | 0.00053263 | 0.00054016 | 0.00055187 | 0.00055538 | 0.00055646 | 0.00055642 | 0.00056373 | 0.00056712 | 0.00055399 | 0.0005512 | 0.00054841 | 0.00054562 | 0.00054282 | 0.00054003 | 0.00053724 | 0.00053445 | 0.00053165 | 0.00052886 | 0.00052607 | 0.00052327 | 31361.1981 | 5633.8693 | 247.4785 | 44.4582 | 14306.3107 | 18544.1427 | 1479916.7083 | 14929.9223
| TRG022-154491390 | 108 | TRG022 | TRG | South | 1963525.4422 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.010601 | 0.010681 | 0.010761 | 0.010842 | 0.010922 | 0.010899 | 0.010877 | 0.010855 | 0.010832 | 0.01081 | 0.010787 | 0.010765 | 0.010743 | 0.01072 | 0.010698 | 0.010675 | 0.010653 | 0.010631 | 0.010608 | 0.010586 | 0.00038627 | 0.00039142 | 0.00039959 | 0.00040181 | 0.00040229 | 0.00040343 | 0.00040993 | 0.0004136 | 0.00040523 | 0.00040439 | 0.00040355 | 0.00040271 | 0.00040187 | 0.00040104 | 0.0004002 | 0.00039936 | 0.00039852 | 0.00039768 | 0.00039685 | 0.00039601 | 31361.1981 | 5633.8693 | 181.6937 | 32.6403 | 12215.4606 | 15833.9385 | 2049115.4422 | 12747.9321
| TRG022-158166546 | 31 | TRG022 | TRG | South | 563604.5251 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0010236 | 0.0010318 | 0.00104 | 0.0010481 | 0.0010563 | 0.0010479 | 0.0010394 | 0.0010309 | 0.0010224 | 0.0010139 | 0.0010055 | 0.00099699 | 0.00098851 | 0.00098003 | 0.00097155 | 0.00096307 | 0.00095459 | 0.00094611 | 0.00093764 | 0.00092916 | 3.7296e-05 | 3.7809e-05 | 3.8615e-05 | 3.8846e-05 | 3.8908e-05 | 3.8785e-05 | 3.9171e-05 | 3.9281e-05 | 3.8248e-05 | 3.7931e-05 | 3.7614e-05 | 3.7297e-05 | 3.6979e-05 | 3.6662e-05 | 3.6345e-05 | 3.6028e-05 | 3.5711e-05 | 3.5394e-05 | 3.5076e-05 | 3.4759e-05 | 31361.1981 | 5633.8693 | 17.0302 | 3.0594 | 1643.4719 | 2130.303 | 588172.0251 | 1715.1107
| TRG022-158166693 | 31 | TRG022 | TRG | South | 563604.5251 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.010384 | 0.010493 | 0.010603 | 0.010712 | 0.010821 | 0.010669 | 0.010516 | 0.010363 | 0.01021 | 0.010057 | 0.0099043 | 0.0097515 | 0.0095986 | 0.0094458 | 0.0092929 | 0.0091401 | 0.0089872 | 0.0088344 | 0.0086815 | 0.0085287 | 0.00037836 | 0.00038453 | 0.00039369 | 0.00039701 | 0.00039858 | 0.00039488 | 0.00039631 | 0.00039486 | 0.00038195 | 0.00037623 | 0.00037051 | 0.0003648 | 0.00035908 | 0.00035336 | 0.00034764 | 0.00034192 | 0.00033621 | 0.00033049 | 0.00032477 | 0.00031905 | 31361.1981 | 5633.8693 | 168.5577 | 30.2805 | 4519.0928 | 5857.7437 | 588172.0251 | 4716.0799
| TRG022-158166806 | 32 | TRG022 | TRG | South | 581785.3162 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.032746 | 0.033022 | 0.033298 | 0.033574 | 0.033849 | 0.033541 | 0.033232 | 0.032924 | 0.032615 | 0.032307 | 0.031998 | 0.03169 | 0.031381 | 0.031072 | 0.030764 | 0.030455 | 0.030147 | 0.029838 | 0.02953 | 0.029221 | 0.0011932 | 0.0012101 | 0.0012364 | 0.0012443 | 0.0012468 | 0.0012415 | 0.0012524 | 0.0012545 | 0.0012201 | 0.0012086 | 0.001197 | 0.0011855 | 0.0011739 | 0.0011624 | 0.0011509 | 0.0011393 | 0.0011278 | 0.0011162 | 0.0011047 | 0.0010931 | 31361.1981 | 5633.8693 | 542.4279 | 97.4442 | 7719.4469 | 10006.1105 | 607145.3162 | 8055.9373
| TRG022-158204991 | 109 | TRG022 | TRG | South | 1981706.2333 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.063089 | 0.063571 | 0.064052 | 0.064534 | 0.065016 | 0.064555 | 0.064094 | 0.063633 | 0.063172 | 0.062711 | 0.06225 | 0.061789 | 0.061327 | 0.060866 | 0.060405 | 0.059944 | 0.059483 | 0.059022 | 0.058561 | 0.0581 | 0.0022988 | 0.0023296 | 0.0023784 | 0.0023918 | 0.0023947 | 0.0023894 | 0.0024155 | 0.0024247 | 0.0023632 | 0.002346 | 0.0023287 | 0.0023115 | 0.0022942 | 0.002277 | 0.0022597 | 0.0022425 | 0.0022252 | 0.002208 | 0.0021907 | 0.0021735 | 31361.1981 | 5633.8693 | 1053.6091 | 189.2752 | 49653.0228 | 64361.2989 | 2068088.7333 | 51817.3962
| TRG022-158205190 | 108 | TRG022 | TRG | South | 1963525.4422 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.031438 | 0.031612 | 0.031787 | 0.031961 | 0.032136 | 0.032017 | 0.031899 | 0.03178 | 0.031662 | 0.031543 | 0.031425 | 0.031306 | 0.031187 | 0.031069 | 0.03095 | 0.030832 | 0.030713 | 0.030595 | 0.030476 | 0.030358 | 0.0011455 | 0.0011584 | 0.0011803 | 0.0011846 | 0.0011837 | 0.0011851 | 0.0012022 | 0.0012109 | 0.0011844 | 0.00118 | 0.0011756 | 0.0011711 | 0.0011667 | 0.0011623 | 0.0011578 | 0.0011534 | 0.001149 | 0.0011445 | 0.0011401 | 0.0011357 | 31361.1981 | 5633.8693 | 530.7909 | 95.3537 | 21760.8549 | 28206.8806 | 2049115.4422 | 22709.4097
| TRG022-158205316 | 117 | TRG022 | TRG | South | 2127152.5624 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.078029 | 0.078773 | 0.079517 | 0.080261 | 0.081004 | 0.079982 | 0.07896 | 0.077938 | 0.076916 | 0.075894 | 0.074872 | 0.07385 | 0.072828 | 0.071806 | 0.070784 | 0.069762 | 0.06874 | 0.067718 | 0.066696 | 0.065674 | 0.0028432 | 0.0028867 | 0.0029526 | 0.0029746 | 0.0029836 | 0.0029604 | 0.0029758 | 0.0029697 | 0.0028774 | 0.0028392 | 0.0028009 | 0.0027627 | 0.0027245 | 0.0026862 | 0.002648 | 0.0026098 | 0.0025715 | 0.0025333 | 0.0024951 | 0.0024568 | 31361.1981 | 5633.8693 | 1272.9841 | 228.6847 | 53918.7193 | 69890.585 | 2219875.0624 | 56269.0343
| TRG022-158205503 | 95 | TRG022 | TRG | South | 1727175.1575 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.10711 | 0.10829 | 0.10948 | 0.11066 | 0.11184 | 0.11082 | 0.1098 | 0.10878 | 0.10776 | 0.10674 | 0.10572 | 0.10469 | 0.10367 | 0.10265 | 0.10163 | 0.10061 | 0.099589 | 0.098568 | 0.097547 | 0.096526 | 0.0039027 | 0.0039684 | 0.004065 | 0.0041012 | 0.0041195 | 0.0041019 | 0.004138 | 0.0041449 | 0.0040311 | 0.0039929 | 0.0039547 | 0.0039165 | 0.0038784 | 0.0038402 | 0.003802 | 0.0037638 | 0.0037256 | 0.0036874 | 0.0036492 | 0.003611 | 31361.1981 | 5633.8693 | 1789.1333 | 321.4081 | 66139.039 | 85730.8219 | 1802462.6575 | 69022.0372
| TRG022-158205673 | 58 | TRG022 | TRG | South | 1054485.8856 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0012302 | 0.0012442 | 0.0012583 | 0.0012723 | 0.0012864 | 0.0012656 | 0.0012449 | 0.0012241 | 0.0012034 | 0.0011826 | 0.0011618 | 0.0011411 | 0.0011203 | 0.0010996 | 0.0010788 | 0.001058 | 0.0010373 | 0.0010165 | 0.00099576 | 0.000975 | 4.4824e-05 | 4.5595e-05 | 4.6722e-05 | 4.7156e-05 | 4.7382e-05 | 4.6846e-05 | 4.6916e-05 | 4.6644e-05 | 4.5017e-05 | 4.424e-05 | 4.3464e-05 | 4.2687e-05 | 4.191e-05 | 4.1134e-05 | 4.0357e-05 | 3.9581e-05 | 3.8804e-05 | 3.8027e-05 | 3.7251e-05 | 3.6474e-05 | 31361.1981 | 5633.8693 | 19.8051 | 3.5579 | 745.1223 | 965.8433 | 1100450.8856 | 777.6021
| TRG022-158205847 | 69 | TRG022 | TRG | South | 1254474.5881 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.00089003 | 0.00089983 | 0.00090962 | 0.00091941 | 0.0009292 | 0.00091816 | 0.00090712 | 0.00089608 | 0.00088504 | 0.000874 | 0.00086296 | 0.00085192 | 0.00084088 | 0.00082984 | 0.0008188 | 0.00080776 | 0.00079672 | 0.00078568 | 0.00077464 | 0.0007636 | 3.243e-05 | 3.2975e-05 | 3.3776e-05 | 3.4075e-05 | 3.4225e-05 | 3.3984e-05 | 3.4187e-05 | 3.4144e-05 | 3.3109e-05 | 3.2696e-05 | 3.2283e-05 | 3.187e-05 | 3.1457e-05 | 3.1044e-05 | 3.0631e-05 | 3.0218e-05 | 2.9805e-05 | 2.9392e-05 | 2.8979e-05 | 2.8566e-05 | 31361.1981 | 5633.8693 | 14.6469 | 2.6312 | 683.991 | 886.6036 | 1309157.0881 | 713.8061
| TRG022-158206040 | 49 | TRG022 | TRG | South | 890858.7654 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.00019668 | 0.00019896 | 0.00020124 | 0.00020352 | 0.0002058 | 0.00020342 | 0.00020104 | 0.00019866 | 0.00019628 | 0.0001939 | 0.00019152 | 0.00018914 | 0.00018676 | 0.00018438 | 0.000182 | 0.00017962 | 0.00017724 | 0.00017486 | 0.00017248 | 0.0001701 | 7.1665e-06 | 7.291e-06 | 7.4724e-06 | 7.5429e-06 | 7.5802e-06 | 7.5293e-06 | 7.5766e-06 | 7.5697e-06 | 7.3427e-06 | 7.2537e-06 | 7.1646e-06 | 7.0756e-06 | 6.9866e-06 | 6.8975e-06 | 6.8085e-06 | 6.7195e-06 | 6.6304e-06 | 6.5414e-06 | 6.4524e-06 | 6.3633e-06 | 31361.1981 | 5633.8693 | 3.2483 | 0.58355 | 176.9731 | 229.3962 | 929691.2654 | 184.6873
| TRG022-160930593 | 74 | TRG022 | TRG | South | 1345378.5437 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.029562 | 0.029839 | 0.030117 | 0.030395 | 0.030673 | 0.030352 | 0.030031 | 0.02971 | 0.029388 | 0.029067 | 0.028746 | 0.028425 | 0.028103 | 0.027782 | 0.027461 | 0.02714 | 0.026818 | 0.026497 | 0.026176 | 0.025855 | 0.0010771 | 0.0010935 | 0.0011183 | 0.0011265 | 0.0011298 | 0.0011234 | 0.0011318 | 0.001132 | 0.0010994 | 0.0010874 | 0.0010754 | 0.0010633 | 0.0010513 | 0.0010393 | 0.0010273 | 0.0010153 | 0.0010033 | 0.00099124 | 0.00097922 | 0.0009672 | 31361.1981 | 5633.8693 | 487.6765 | 87.6084 | 16521.852 | 21415.9742 | 1404023.5437 | 17242.0389
| TRG022-163035515 | 15 | TRG022 | TRG | South | 272711.867 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 3.028e-05 | 3.064e-05 | 3.1e-05 | 3.136e-05 | 3.172e-05 | 3.13e-05 | 3.088e-05 | 3.046e-05 | 3.004e-05 | 2.962e-05 | 2.92e-05 | 2.878e-05 | 2.836e-05 | 2.794e-05 | 2.752e-05 | 2.71e-05 | 2.668e-05 | 2.626e-05 | 2.584e-05 | 2.542e-05 | 1.1033e-06 | 1.1228e-06 | 1.1511e-06 | 1.1623e-06 | 1.1683e-06 | 1.1585e-06 | 1.1638e-06 | 1.1606e-06 | 1.1238e-06 | 1.1081e-06 | 1.0924e-06 | 1.0766e-06 | 1.0609e-06 | 1.0452e-06 | 1.0295e-06 | 1.0138e-06 | 9.9808e-07 | 9.8237e-07 | 9.6666e-07 | 9.5095e-07 | 31361.1981 | 5633.8693 | 0.49604 | 0.089111 | 28.9564 | 37.534 | 284599.367 | 30.2187
| TRG022-163035708 | 21 | TRG022 | TRG | South | 381796.6138 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.00013267 | 0.00013445 | 0.00013623 | 0.00013802 | 0.0001398 | 0.00013782 | 0.00013584 | 0.00013386 | 0.00013188 | 0.0001299 | 0.00012792 | 0.00012594 | 0.00012396 | 0.00012198 | 0.00012 | 0.00011802 | 0.00011604 | 0.00011406 | 0.00011208 | 0.0001101 | 4.8341e-06 | 4.927e-06 | 5.0586e-06 | 5.1152e-06 | 5.1492e-06 | 5.1012e-06 | 5.1194e-06 | 5.1006e-06 | 4.9335e-06 | 4.8595e-06 | 4.7854e-06 | 4.7113e-06 | 4.6373e-06 | 4.5632e-06 | 4.4891e-06 | 4.4151e-06 | 4.341e-06 | 4.2669e-06 | 4.1928e-06 | 4.1188e-06 | 31361.1981 | 5633.8693 | 2.1731 | 0.39038 | 118.3977 | 153.4697 | 398439.1138 | 123.5587
| TRG022-163035922 | 7 | TRG022 | TRG | South | 127265.5379 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0040632 | 0.0041042 | 0.0041452 | 0.0041861 | 0.0042271 | 0.0041763 | 0.0041254 | 0.0040746 | 0.0040238 | 0.0039729 | 0.0039221 | 0.0038713 | 0.0038204 | 0.0037696 | 0.0037188 | 0.0036679 | 0.0036171 | 0.0035663 | 0.0035154 | 0.0034646 | 0.00014805 | 0.0001504 | 0.00015392 | 0.00015515 | 0.0001557 | 0.00015458 | 0.00015548 | 0.00015526 | 0.00015053 | 0.00014863 | 0.00014672 | 0.00014482 | 0.00014292 | 0.00014102 | 0.00013912 | 0.00013722 | 0.00013531 | 0.00013341 | 0.00013151 | 0.00012961 | 31361.1981 | 5633.8693 | 66.6185 | 11.9676 | 1814.7737 | 2352.3481 | 132813.0379 | 1893.8796
| TRG022-163036120 | 19 | TRG022 | TRG | South | 345435.0315 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 5.3789e-05 | 5.4341e-05 | 5.4894e-05 | 5.5447e-05 | 5.6e-05 | 5.5642e-05 | 5.5285e-05 | 5.4927e-05 | 5.457e-05 | 5.4213e-05 | 5.3855e-05 | 5.3498e-05 | 5.314e-05 | 5.2783e-05 | 5.2425e-05 | 5.2068e-05 | 5.171e-05 | 5.1353e-05 | 5.0995e-05 | 5.0638e-05 | 1.9599e-06 | 1.9914e-06 | 2.0383e-06 | 2.055e-06 | 2.0626e-06 | 2.0595e-06 | 2.0835e-06 | 2.0929e-06 | 2.0414e-06 | 2.0281e-06 | 2.0147e-06 | 2.0013e-06 | 1.9879e-06 | 1.9746e-06 | 1.9612e-06 | 1.9478e-06 | 1.9344e-06 | 1.9211e-06 | 1.9077e-06 | 1.8943e-06 | 31361.1981 | 5633.8693 | 0.90937 | 0.16336 | 53.7834 | 69.7152 | 360492.5315 | 56.1279
| TRG022-163036215 | 31 | TRG022 | TRG | South | 563604.5251 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 1.6875e-05 | 1.7082e-05 | 1.7288e-05 | 1.7494e-05 | 1.77e-05 | 1.7447e-05 | 1.7194e-05 | 1.6942e-05 | 1.6689e-05 | 1.6436e-05 | 1.6183e-05 | 1.5931e-05 | 1.5678e-05 | 1.5425e-05 | 1.5172e-05 | 1.492e-05 | 1.4667e-05 | 1.4414e-05 | 1.4161e-05 | 1.3909e-05 | 6.1489e-07 | 6.2596e-07 | 6.4192e-07 | 6.4836e-07 | 6.5194e-07 | 6.4578e-07 | 6.4801e-07 | 6.4554e-07 | 6.2432e-07 | 6.1487e-07 | 6.0541e-07 | 5.9596e-07 | 5.865e-07 | 5.7705e-07 | 5.6759e-07 | 5.5814e-07 | 5.4868e-07 | 5.3923e-07 | 5.2977e-07 | 5.2032e-07 | 31361.1981 | 5633.8693 | 0.27517 | 0.049433 | 8.8528 | 11.4751 | 588172.0251 | 9.2387
| TRG022-171344186 | 5 | TRG022 | TRG | South | 90903.9557 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0 | 0 | 94866.4557 | 0
| TRG022-176898220 | 742 | TRG022 | TRG | South | 13490147.0195 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 9.2372 | 9.3155 | 9.3938 | 9.4721 | 9.5504 | 9.469 | 9.3876 | 9.3063 | 9.2249 | 9.1435 | 9.0621 | 8.9808 | 8.8994 | 8.818 | 8.7366 | 8.6553 | 8.5739 | 8.4925 | 8.4111 | 8.3298 | 0.33658 | 0.34137 | 0.34881 | 0.35106 | 0.35177 | 0.35048 | 0.35379 | 0.3546 | 0.3451 | 0.34205 | 0.33901 | 0.33596 | 0.33292 | 0.32988 | 0.32683 | 0.32379 | 0.32074 | 0.3177 | 0.31466 | 0.31161 | 31361.1981 | 5633.8693 | 153522.0533 | 27579.405 | 1252649.7994 | 1623711.1775 | 14078182.0195 | 1307252.7569
| TRG022-176898350 | 452 | TRG022 | TRG | South | 8217717.5914 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.95794 | 0.95977 | 0.96159 | 0.96341 | 0.96524 | 0.96333 | 0.96143 | 0.95953 | 0.95763 | 0.95573 | 0.95383 | 0.95193 | 0.95003 | 0.94813 | 0.94623 | 0.94433 | 0.94243 | 0.94053 | 0.93862 | 0.93672 | 0.034905 | 0.035171 | 0.035705 | 0.035706 | 0.035552 | 0.035656 | 0.036234 | 0.036562 | 0.035824 | 0.035753 | 0.035682 | 0.035611 | 0.03554 | 0.035469 | 0.035398 | 0.035327 | 0.035256 | 0.035184 | 0.035113 | 0.035042 | 31361.1981 | 5633.8693 | 16121.7948 | 2896.1931 | 350559.8463 | 454403.091 | 8575927.5914 | 365840.7368
| TRG022-176898385 | 150 | TRG022 | TRG | South | 2727118.6697 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.58159 | 0.58605 | 0.59051 | 0.59496 | 0.59942 | 0.59358 | 0.58774 | 0.5819 | 0.57605 | 0.57021 | 0.56437 | 0.55853 | 0.55269 | 0.54684 | 0.541 | 0.53516 | 0.52932 | 0.52348 | 0.51763 | 0.51179 | 0.021191 | 0.021476 | 0.021926 | 0.022051 | 0.022079 | 0.021971 | 0.02215 | 0.022172 | 0.02155 | 0.021331 | 0.021113 | 0.020894 | 0.020676 | 0.020457 | 0.020239 | 0.02002 | 0.019801 | 0.019583 | 0.019364 | 0.019146 | 31361.1981 | 5633.8693 | 9578.0597 | 1720.6465 | 64892.991 | 84115.6682 | 2845993.6697 | 67721.674
| TRG022-185851624 | 73 | TRG022 | TRG | South | 1327197.7526 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 2.2361 | 2.2618 | 2.2876 | 2.3134 | 2.3391 | 2.3124 | 2.2856 | 2.2588 | 2.232 | 2.2052 | 2.1784 | 2.1517 | 2.1249 | 2.0981 | 2.0713 | 2.0445 | 2.0178 | 1.991 | 1.9642 | 1.9374 | 0.081476 | 0.082886 | 0.084942 | 0.085738 | 0.086157 | 0.085588 | 0.086137 | 0.086069 | 0.083498 | 0.082496 | 0.081494 | 0.080492 | 0.07949 | 0.078489 | 0.077487 | 0.076485 | 0.075483 | 0.074481 | 0.073479 | 0.072477 | 31361.1981 | 5633.8693 | 36945.4226 | 6637.045 | 35380.8435 | 45861.3981 | 1385050.2526 | 36923.0932
| TRG022-24598160 | 362 | TRG022 | TRG | South | 6581446.3896 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.86191 | 0.8686 | 0.8753 | 0.88199 | 0.88868 | 0.87922 | 0.86975 | 0.86028 | 0.85082 | 0.84135 | 0.83189 | 0.82242 | 0.81295 | 0.80349 | 0.79402 | 0.78455 | 0.77509 | 0.76562 | 0.75616 | 0.74669 | 0.031406 | 0.03183 | 0.032501 | 0.032688 | 0.032733 | 0.032543 | 0.032778 | 0.03278 | 0.031829 | 0.031474 | 0.03112 | 0.030766 | 0.030412 | 0.030058 | 0.029704 | 0.02935 | 0.028996 | 0.028641 | 0.028287 | 0.027933 | 31361.1981 | 5633.8693 | 14130.5491 | 2538.4766 | 376304.6215 | 487774.0135 | 6868331.3896 | 392707.7258
| TRG022-24598202 | 336 | TRG022 | TRG | South | 6108745.8202 | 0.0013088 | 0.0013163 | 0.0013337 | 0.0013313 | 0.001323 | 0.0013295 | 0.0013537 | 0.0013687 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.0013437 | 0.65409 | 0.66095 | 0.66782 | 0.67469 | 0.68156 | 0.67546 | 0.66936 | 0.66326 | 0.65716 | 0.65106 | 0.64496 | 0.63887 | 0.63277 | 0.62667 | 0.62057 | 0.61447 | 0.60837 | 0.60227 | 0.59618 | 0.59008 | 0.023833 | 0.024221 | 0.024797 | 0.025005 | 0.025104 | 0.025001 | 0.025226 | 0.025273 | 0.024584 | 0.024356 | 0.024128 | 0.0239 | 0.023671 | 0.023443 | 0.023215 | 0.022987 | 0.022759 | 0.022531 | 0.022303 | 0.022074 | 31361.1981 | 5633.8693 | 10917.1528 | 1961.2073 | 270867.9464 | 351104.764 | 6375025.8202 | 282675.07
| TRG024-117365806 | 17 | TRG024 | TRG | South | 309073.4492 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0 | 0 | 322545.9492 | 0
| TRG024-158041024 | 47 | TRG024 | TRG | South | 854497.1832 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.015839 | 0.015943 | 0.016047 | 0.016152 | 0.016256 | 0.016121 | 0.015986 | 0.015852 | 0.015717 | 0.015583 | 0.015448 | 0.015313 | 0.015179 | 0.015044 | 0.014909 | 0.014775 | 0.01464 | 0.014505 | 0.014371 | 0.014236 | 0.0014873 | 0.00153 | 0.0015609 | 0.0015877 | 0.0015912 | 0.0015766 | 0.0015904 | 0.0016126 | 0.0015912 | 0.0015776 | 0.001564 | 0.0015503 | 0.0015367 | 0.0015231 | 0.0015094 | 0.0014958 | 0.0014822 | 0.0014685 | 0.0014549 | 0.0014413 | 31361.1981 | 5633.8693 | 699.4172 | 125.6465 | 5807.3191 | 7527.5699 | 891744.6832 | 6060.4599
| TRG024-158742698 | 1 | TRG024 | TRG | South | 18180.7911 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0 | 0 | 18973.2911 | 0
| TRG024-162822011 | 10 | TRG024 | TRG | South | 181807.9113 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0037931 | 0.0038289 | 0.0038647 | 0.0039005 | 0.0039362 | 0.0038699 | 0.0038035 | 0.0037371 | 0.0036707 | 0.0036043 | 0.0035379 | 0.0034716 | 0.0034052 | 0.0033388 | 0.0032724 | 0.003206 | 0.0031396 | 0.0030733 | 0.0030069 | 0.0029405 | 0.00035618 | 0.00036743 | 0.00037592 | 0.00038342 | 0.0003853 | 0.00037847 | 0.00037838 | 0.00038018 | 0.00037163 | 0.00036491 | 0.00035819 | 0.00035147 | 0.00034475 | 0.00033803 | 0.00033131 | 0.00032458 | 0.00031786 | 0.00031114 | 0.00030442 | 0.0002977 | 31361.1981 | 5633.8693 | 161.2755 | 28.9723 | 1344.1669 | 1742.3375 | 189732.9113 | 1402.759
| TRG024-162822186 | 10 | TRG024 | TRG | South | 181807.9113 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 5.6054e-06 | 5.695e-06 | 5.7847e-06 | 5.8743e-06 | 5.964e-06 | 5.8227e-06 | 5.6814e-06 | 5.5401e-06 | 5.3988e-06 | 5.2575e-06 | 5.1162e-06 | 4.9749e-06 | 4.8336e-06 | 4.6923e-06 | 4.551e-06 | 4.4097e-06 | 4.2684e-06 | 4.1271e-06 | 3.9858e-06 | 3.8445e-06 | 5.2635e-07 | 5.4651e-07 | 5.6268e-07 | 5.7745e-07 | 5.8379e-07 | 5.6945e-07 | 5.652e-07 | 5.6361e-07 | 5.4659e-07 | 5.3228e-07 | 5.1797e-07 | 5.0367e-07 | 4.8936e-07 | 4.7506e-07 | 4.6075e-07 | 4.4645e-07 | 4.3214e-07 | 4.1784e-07 | 4.0353e-07 | 3.8923e-07 | 31361.1981 | 5633.8693 | 0.23396 | 0.042031 | 2.2763 | 2.9505 | 189732.9113 | 2.3755
| TRG024-162822411 | 8 | TRG024 | TRG | South | 145446.3291 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31361.1981 | 5633.8693 | 0 | 0 | 0 | 0 | 151786.3291 | 0
| TRG024-162822646 | 11 | TRG024 | TRG | South | 199988.7024 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 5.7036e-07 | 5.7582e-07 | 5.8128e-07 | 5.8674e-07 | 5.922e-07 | 5.7883e-07 | 5.6546e-07 | 5.5209e-07 | 5.3872e-07 | 5.2535e-07 | 5.1198e-07 | 4.9861e-07 | 4.8524e-07 | 4.7187e-07 | 4.585e-07 | 4.4513e-07 | 4.3176e-07 | 4.1839e-07 | 4.0502e-07 | 3.9165e-07 | 5.3558e-08 | 5.5258e-08 | 5.6541e-08 | 5.7677e-08 | 5.7968e-08 | 5.6609e-08 | 5.6253e-08 | 5.6165e-08 | 5.4541e-08 | 5.3188e-08 | 5.1834e-08 | 5.048e-08 | 4.9127e-08 | 4.7773e-08 | 4.6419e-08 | 4.5066e-08 | 4.3712e-08 | 4.2359e-08 | 4.1005e-08 | 3.9651e-08 | 31361.1981 | 5633.8693 | 0.023482 | 0.0042184 | 0.21541 | 0.27922 | 208706.2024 | 0.2248
| TRG024-162822850 | 23 | TRG024 | TRG | South | 418158.196 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0090488 | 0.0091401 | 0.0092314 | 0.0093227 | 0.009414 | 0.0092603 | 0.0091066 | 0.0089529 | 0.0087992 | 0.0086455 | 0.0084918 | 0.0083382 | 0.0081845 | 0.0080308 | 0.0078771 | 0.0077234 | 0.0075697 | 0.007416 | 0.0072623 | 0.0071086 | 0.0008497 | 0.00087712 | 0.00089794 | 0.00091643 | 0.0009215 | 0.00090564 | 0.00090595 | 0.0009108 | 0.00089085 | 0.00087529 | 0.00085973 | 0.00084417 | 0.00082861 | 0.00081305 | 0.00079749 | 0.00078193 | 0.00076637 | 0.00075081 | 0.00073525 | 0.00071969 | 31361.1981 | 5633.8693 | 386.7162 | 69.4715 | 2470.8878 | 3202.8171 | 436385.696 | 2578.5937
| TRG024-162823024 | 7 | TRG024 | TRG | South | 127265.5379 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 2.8546e-05 | 2.879e-05 | 2.9033e-05 | 2.9277e-05 | 2.952e-05 | 2.916e-05 | 2.88e-05 | 2.844e-05 | 2.808e-05 | 2.772e-05 | 2.736e-05 | 2.7e-05 | 2.664e-05 | 2.628e-05 | 2.592e-05 | 2.556e-05 | 2.52e-05 | 2.484e-05 | 2.448e-05 | 2.412e-05 | 2.6805e-06 | 2.7628e-06 | 2.8241e-06 | 2.8779e-06 | 2.8896e-06 | 2.8518e-06 | 2.8651e-06 | 2.8933e-06 | 2.8429e-06 | 2.8064e-06 | 2.77e-06 | 2.7335e-06 | 2.6971e-06 | 2.6606e-06 | 2.6242e-06 | 2.5877e-06 | 2.5513e-06 | 2.5149e-06 | 2.4784e-06 | 2.442e-06 | 31361.1981 | 5633.8693 | 1.242 | 0.22311 | 8.4499 | 10.9529 | 132813.0379 | 8.8182
| TRG024-162823256 | 19 | TRG024 | TRG | South | 345435.0315 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 2.1966e-05 | 2.2212e-05 | 2.2458e-05 | 2.2704e-05 | 2.295e-05 | 2.2519e-05 | 2.2089e-05 | 2.1658e-05 | 2.1228e-05 | 2.0797e-05 | 2.0367e-05 | 1.9936e-05 | 1.9506e-05 | 1.9075e-05 | 1.8645e-05 | 1.8214e-05 | 1.7784e-05 | 1.7353e-05 | 1.6923e-05 | 1.6492e-05 | 2.0626e-06 | 2.1315e-06 | 2.1845e-06 | 2.2318e-06 | 2.2465e-06 | 2.2024e-06 | 2.1975e-06 | 2.2034e-06 | 2.1492e-06 | 2.1056e-06 | 2.062e-06 | 2.0184e-06 | 1.9748e-06 | 1.9312e-06 | 1.8877e-06 | 1.8441e-06 | 1.8005e-06 | 1.7569e-06 | 1.7133e-06 | 1.6697e-06 | 31361.1981 | 5633.8693 | 0.92923 | 0.16693 | 6.868 | 8.9025 | 360492.5315 | 7.1674
| TRG024-185851718 | 48 | TRG024 | TRG | South | 872677.9743 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.00019585 | 0.00019842 | 0.00020099 | 0.00020356 | 0.00020613 | 0.00020372 | 0.00020131 | 0.00019889 | 0.00019648 | 0.00019407 | 0.00019166 | 0.00018924 | 0.00018683 | 0.00018442 | 0.000182 | 0.00017959 | 0.00017718 | 0.00017477 | 0.00017235 | 0.00016994 | 1.8391e-05 | 1.9041e-05 | 1.9551e-05 | 2.001e-05 | 2.0178e-05 | 1.9923e-05 | 2.0027e-05 | 2.0234e-05 | 1.9892e-05 | 1.9648e-05 | 1.9404e-05 | 1.9159e-05 | 1.8915e-05 | 1.8671e-05 | 1.8426e-05 | 1.8182e-05 | 1.7938e-05 | 1.7694e-05 | 1.7449e-05 | 1.7205e-05 | 31361.1981 | 5633.8693 | 8.6709 | 1.5577 | 10.0411 | 13.0155 | 910717.9743 | 10.4788
| TRG024-24598286 | 257 | TRG024 | TRG | South | 4672463.3208 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.090495 | 0.091294 | 0.092094 | 0.092894 | 0.093694 | 0.092199 | 0.090704 | 0.089209 | 0.087714 | 0.086219 | 0.084724 | 0.083229 | 0.081734 | 0.080239 | 0.078744 | 0.077249 | 0.075754 | 0.074259 | 0.072764 | 0.07127 | 0.0084976 | 0.0087609 | 0.008958 | 0.0091316 | 0.0091714 | 0.0090169 | 0.0090235 | 0.0090755 | 0.0088804 | 0.008729 | 0.0085777 | 0.0084263 | 0.008275 | 0.0081236 | 0.0079722 | 0.0078209 | 0.0076695 | 0.0075182 | 0.0073668 | 0.0072155 | 31361.1981 | 5633.8693 | 3859.9342 | 693.4163 | 16233.1671 | 21041.7747 | 4876135.8208 | 16940.7702
| TRG024-60700588 | 199 | TRG024 | TRG | South | 3617977.4352 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.57057 | 0.57681 | 0.58306 | 0.5893 | 0.59555 | 0.5851 | 0.57465 | 0.56421 | 0.55376 | 0.54331 | 0.53286 | 0.52242 | 0.51197 | 0.50152 | 0.49107 | 0.48063 | 0.47018 | 0.45973 | 0.44928 | 0.43884 | 0.053577 | 0.055353 | 0.056714 | 0.057929 | 0.058296 | 0.057222 | 0.057168 | 0.057398 | 0.056064 | 0.055006 | 0.053948 | 0.05289 | 0.051833 | 0.050775 | 0.049717 | 0.04866 | 0.047602 | 0.046544 | 0.045486 | 0.044429 | 31361.1981 | 5633.8693 | 24284.0972 | 4362.5065 | 66971.3191 | 86809.641 | 3775684.9352 | 69890.5964
| TRG024-74127795 | 703 | TRG024 | TRG | South | 12781096.1654 | 0.0033729 | 0.003447 | 0.0034939 | 0.0035309 | 0.003516 | 0.0035129 | 0.0035734 | 0.0036542 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 0.0036366 | 1.7966 | 1.8153 | 1.8339 | 1.8525 | 1.8712 | 1.8534 | 1.8356 | 1.8179 | 1.8001 | 1.7823 | 1.7645 | 1.7468 | 1.729 | 1.7112 | 1.6934 | 1.6757 | 1.6579 | 1.6401 | 1.6224 | 1.6046 | 0.16871 | 0.1742 | 0.17838 | 0.18211 | 0.18316 | 0.18126 | 0.18261 | 0.18493 | 0.18224 | 0.18044 | 0.17865 | 0.17685 | 0.17505 | 0.17325 | 0.17145 | 0.16965 | 0.16785 | 0.16605 | 0.16425 | 0.16245 | 31361.1981 | 5633.8693 | 79795.6031 | 14334.8477 | 391869.6895 | 507949.784 | 13338223.6654 | 408951.2745
| WBE011-203216132 | 271 | WBE011 | WBE | South | 4926994.3966 | 0.0014169 | 0.0014049 | 0.0013915 | 0.0013741 | 0.00135 | 0.0013416 | 0.0013666 | 0.0013869 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 7.1367 | 7.1712 | 7.2057 | 7.2403 | 7.2748 | 7.2862 | 7.2977 | 7.3091 | 7.3206 | 7.332 | 7.3435 | 7.3549 | 7.3663 | 7.3778 | 7.3892 | 7.4007 | 7.4121 | 7.4236 | 7.435 | 7.4464 | 0.28151 | 0.28048 | 0.27915 | 0.27697 | 0.27341 | 0.27215 | 0.27765 | 0.28221 | 0.2817 | 0.28214 | 0.28258 | 0.28302 | 0.28346 | 0.2839 | 0.28434 | 0.28478 | 0.28522 | 0.28566 | 0.2861 | 0.28654 | 42369.9203 | 8385.8779 | 172195.2628 | 34080.9808 | 211936.845 | 274717.0233 | 5141761.8966 | 221175.1641
| WBE011-41045910 | 1 | WBE011 | WBE | South | 18180.7911 | 0.0014169 | 0.0014049 | 0.0013915 | 0.0013741 | 0.00135 | 0.0013416 | 0.0013666 | 0.0013869 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0.0013822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42369.9203 | 8385.8779 | 0 | 0 | 0 | 0 | 18973.2911 | 0
| WBE012-203216204 | 58 | WBE012 | WBE | South | 1054485.8856 | 0.00099665 | 0.001004 | 0.0010101 | 0.0010145 | 0.0010145 | 0.0010177 | 0.0010279 | 0.0010476 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0.0010671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42369.9203 | 8385.8779 | 0 | 0 | 0 | 0 | 1100450.8856 | 0
| WBE013-203216284 | 298 | WBE013 | WBE | South | 5417875.7572 | 0.0014497 | 0.0015403 | 0.0015839 | 0.001623 | 0.0016562 | 0.0016972 | 0.0017617 | 0.001845 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0.0019177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42369.9203 | 8385.8779 | 0 | 0 | 0 | 0 | 5654040.7572 | 0
| WBE014-203216348 | 129 | WBE014 | WBE | South | 2345322.056 | 0.0010644 | 0.00056049 | 0.00058645 | 0.00061109 | 0.00063288 | 0.00065729 | 0.0006858 | 0.00071454 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 0.00073841 | 7.8515 | 7.9026 | 7.9537 | 8.0047 | 8.0558 | 8.0802 | 8.1046 | 8.129 | 8.1534 | 8.1778 | 8.2022 | 8.2266 | 8.2509 | 8.2753 | 8.2997 | 8.3241 | 8.3485 | 8.3729 | 8.3973 | 8.4217 | 0.23267 | 0.12331 | 0.12986 | 0.13618 | 0.14194 | 0.14786 | 0.15474 | 0.16171 | 0.16761 | 0.16811 | 0.16861 | 0.16912 | 0.16962 | 0.17012 | 0.17062 | 0.17112 | 0.17162 | 0.17212 | 0.17263 | 0.17313 | 42369.9203 | 8385.8779 | 99515.6386 | 19696.1898 | 42675.5352 | 55316.9318 | 2447554.556 | 44535.7602
| WBE021-203216532 | 165 | WBE021 | WBE | South | 2999830.5367 | 0.0018081 | 0.00053347 | 0.00052005 | 0.00050814 | 0.00049639 | 0.00048633 | 0.00048079 | 0.00047509 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0.00046955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42369.9203 | 8385.8779 | 0 | 0 | 0 | 0 | 3130593.0367 | 0
| WBE022-203216606 | 193 | WBE022 | WBE | South | 3508892.6884 | 0.0027856 | 0.0030412 | 0.0030131 | 0.0029781 | 0.0029281 | 0.0028823 | 0.0028604 | 0.0028581 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 0.002881 | 9.0139 | 9.082 | 9.1501 | 9.2183 | 9.2864 | 9.3012 | 9.316 | 9.3308 | 9.3456 | 9.3604 | 9.3752 | 9.39 | 9.4048 | 9.4196 | 9.4344 | 9.4491 | 9.4639 | 9.4787 | 9.4935 | 9.5083 | 0.69902 | 0.76894 | 0.76755 | 0.76429 | 0.75701 | 0.74636 | 0.74187 | 0.74245 | 0.74958 | 0.75077 | 0.75196 | 0.75314 | 0.75433 | 0.75552 | 0.7567 | 0.75789 | 0.75908 | 0.76026 | 0.76145 | 0.76264 | 42369.9203 | 8385.8779 | 460711.1043 | 91184.1944 | 308917.5004 | 400425.4011 | 3661845.1884 | 322383.2026
| WBE023-139765778 | 486 | WBE023 | WBE | South | 8835864.4899 | 0.0011307 | 0.0011551 | 0.0011811 | 0.0012043 | 0.0012253 | 0.0012513 | 0.0012912 | 0.0013486 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 5.8197 | 5.8591 | 5.8985 | 5.9379 | 5.9774 | 5.9959 | 6.0145 | 6.0331 | 6.0517 | 6.0703 | 6.0889 | 6.1075 | 6.1261 | 6.1446 | 6.1632 | 6.1818 | 6.2004 | 6.219 | 6.2376 | 6.2562 | 0.1832 | 0.18842 | 0.19395 | 0.19908 | 0.2039 | 0.20888 | 0.21621 | 0.22652 | 0.23493 | 0.23565 | 0.23638 | 0.2371 | 0.23782 | 0.23854 | 0.23926 | 0.23998 | 0.24071 | 0.24143 | 0.24215 | 0.24287 | 42369.9203 | 8385.8779 | 135172.0662 | 26753.3294 | 1084649.5125 | 1405945.6505 | 9221019.4899 | 1131929.3438
| WBE023-203216893 | 10 | WBE023 | WBE | South | 181807.9113 | 0.0011307 | 0.0011551 | 0.0011811 | 0.0012043 | 0.0012253 | 0.0012513 | 0.0012912 | 0.0013486 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0.0013944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42369.9203 | 8385.8779 | 0 | 0 | 0 | 0 | 189732.9113 | 0
| WBE024-203216929 | 291 | WBE024 | WBE | South | 5290610.2193 | 0.0024181 | 0.0024599 | 0.0024912 | 0.0025236 | 0.0025433 | 0.0025802 | 0.0026517 | 0.002723 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 0.0027668 | 4.7817 | 4.82 | 4.8584 | 4.8967 | 4.935 | 4.9584 | 4.9818 | 5.0052 | 5.0286 | 5.052 | 5.0754 | 5.0988 | 5.1222 | 5.1457 | 5.1691 | 5.1925 | 5.2159 | 5.2393 | 5.2627 | 5.2861 | 0.3219 | 0.33009 | 0.33695 | 0.34403 | 0.34943 | 0.35618 | 0.36778 | 0.37943 | 0.38734 | 0.38914 | 0.39094 | 0.39275 | 0.39455 | 0.39635 | 0.39816 | 0.39996 | 0.40176 | 0.40356 | 0.40537 | 0.40717 | 42369.9203 | 8385.8779 | 228192.0175 | 45163.8892 | 110447.3653 | 143164.2121 | 5521227.7193 | 115261.7618
| WBE031-15425070 | 1 | WBE031 | WBE | South | 18180.7911 | 0.00090735 | 0.00093367 | 0.00095998 | 0.0010042 | 0.0010607 | 0.0011233 | 0.0011887 | 0.0012485 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42369.9203 | 8385.8779 | 0 | 0 | 0 | 0 | 18973.2911 | 0
| WBE031-203217123 | 75 | WBE031 | WBE | South | 1363559.3349 | 0.00090735 | 0.00093367 | 0.00095998 | 0.0010042 | 0.0010607 | 0.0011233 | 0.0011887 | 0.0012485 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42369.9203 | 8385.8779 | 0 | 0 | 0 | 0 | 1422996.8349 | 0
| WBE031-24612962 | 274 | WBE031 | WBE | South | 4981536.77 | 0.00090735 | 0.00093367 | 0.00095998 | 0.0010042 | 0.0010607 | 0.0011233 | 0.0011887 | 0.0012485 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0.0012938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42369.9203 | 8385.8779 | 0 | 0 | 0 | 0 | 5198681.77 | 0
| WBE032-203217195 | 159 | WBE032 | WBE | South | 2890745.7899 | 0.0011294 | 0.00078031 | 0.00079238 | 0.00080487 | 0.00081424 | 0.00082496 | 0.00084119 | 0.00085847 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42369.9203 | 8385.8779 | 0 | 0 | 0 | 0 | 3016753.2899 | 0
| WBE032-24612505 | 80 | WBE032 | WBE | South | 1454463.2905 | 0.0011294 | 0.00078031 | 0.00079238 | 0.00080487 | 0.00081424 | 0.00082496 | 0.00084119 | 0.00085847 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 0.00086919 | 22.544 | 22.6807 | 22.8174 | 22.9541 | 23.0908 | 23.1312 | 23.1717 | 23.2121 | 23.2525 | 23.2929 | 23.3333 | 23.3737 | 23.4141 | 23.4545 | 23.4949 | 23.5354 | 23.5758 | 23.6162 | 23.6566 | 23.697 | 0.70881 | 0.49271 | 0.50335 | 0.51435 | 0.52343 | 0.53125 | 0.54265 | 0.55476 | 0.56267 | 0.56364 | 0.56462 | 0.5656 | 0.56658 | 0.56756 | 0.56853 | 0.56951 | 0.57049 | 0.57147 | 0.57244 | 0.57342 | 42369.9203 | 8385.8779 | 341966.716 | 67682.2399 | 162281.4005 | 210352.5854 | 1517863.2905 | 169355.2407
| WBE033-203217267 | 506 | WBE033 | WBE | South | 9199480.3125 | 0.002104 | 0.0021674 | 0.0022288 | 0.0022837 | 0.0023217 | 0.0023689 | 0.0024405 | 0.0025193 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 39.5177 | 39.7879 | 40.058 | 40.3282 | 40.5984 | 40.766 | 40.9336 | 41.1012 | 41.2689 | 41.4365 | 41.6041 | 41.7717 | 41.9393 | 42.1069 | 42.2746 | 42.4422 | 42.6098 | 42.7774 | 42.945 | 43.1126 | 2.3147 | 2.4008 | 2.4856 | 2.564 | 2.6241 | 2.6886 | 2.7811 | 2.8827 | 2.9582 | 2.9702 | 2.9823 | 2.9943 | 3.0063 | 3.0183 | 3.0303 | 3.0423 | 3.0543 | 3.0664 | 3.0784 | 3.0904 | 42369.9203 | 8385.8779 | 1719163.1863 | 340257.7204 | 1085767.6175 | 1407394.9619 | 9600485.3125 | 1133096.187
| WBE033-65838252 | 0 | WBE033 | WBE | South | 0 | 0.002104 | 0.0021674 | 0.0022288 | 0.0022837 | 0.0023217 | 0.0023689 | 0.0024405 | 0.0025193 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0.0025748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42369.9203 | 8385.8779 | 0 | 0 | 0 | 0 | 0 | 0
| WBE034-182145993 | 72 | WBE034 | WBE | South | 1309016.9615 | 0.0015544 | 0.0016164 | 0.0016728 | 0.0017242 | 0.0017666 | 0.0018141 | 0.0018717 | 0.001935 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.027051 | 0.027264 | 0.027476 | 0.027689 | 0.027902 | 0.027978 | 0.028054 | 0.02813 | 0.028206 | 0.028282 | 0.028358 | 0.028434 | 0.02851 | 0.028586 | 0.028662 | 0.028739 | 0.028815 | 0.028891 | 0.028967 | 0.029043 | 0.0011706 | 0.0012269 | 0.0012796 | 0.0013291 | 0.0013723 | 0.001413 | 0.0014619 | 0.0015154 | 0.0015544 | 0.0015586 | 0.0015628 | 0.001567 | 0.0015712 | 0.0015754 | 0.0015796 | 0.0015838 | 0.001588 | 0.0015922 | 0.0015964 | 0.0016006 | 42369.9203 | 8385.8779 | 894.7409 | 177.0876 | 315.0102 | 408.3228 | 1366076.9615 | 328.7415
| WBE034-203217365 | 259 | WBE034 | WBE | South | 4708824.903 | 0.0015544 | 0.0016164 | 0.0016728 | 0.0017242 | 0.0017666 | 0.0018141 | 0.0018717 | 0.001935 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.00638 | 0.0064416 | 0.0065032 | 0.0065648 | 0.0066264 | 0.0066455 | 0.0066646 | 0.0066837 | 0.0067029 | 0.006722 | 0.0067411 | 0.0067603 | 0.0067794 | 0.0067985 | 0.0068177 | 0.0068368 | 0.0068559 | 0.006875 | 0.0068942 | 0.0069133 | 0.00027608 | 0.00028987 | 0.00030287 | 0.00031512 | 0.0003259 | 0.00033563 | 0.00034729 | 0.00036006 | 0.0003694 | 0.00037045 | 0.00037151 | 0.00037256 | 0.00037362 | 0.00037467 | 0.00037572 | 0.00037678 | 0.00037783 | 0.00037889 | 0.00037994 | 0.000381 | 42369.9203 | 8385.8779 | 212.4714 | 42.0525 | 199.1494 | 258.1417 | 4914082.403 | 207.8304
| WBE034-24612477 | 406 | WBE034 | WBE | South | 7381401.1994 | 0.0015544 | 0.0016164 | 0.0016728 | 0.0017242 | 0.0017666 | 0.0018141 | 0.0018717 | 0.001935 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0.0019795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42369.9203 | 8385.8779 | 0 | 0 | 0 | 0 | 7703156.1994 | 0
| WBL002-15395911 | 732 | WBL002 | WBL | South | 13308339.1082 | 0.0035222 | 0.0035367 | 0.0035459 | 0.0035385 | 0.0035179 | 0.0035217 | 0.0035602 | 0.0035865 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.30296 | 0.30529 | 0.30762 | 0.30995 | 0.31228 | 0.30937 | 0.30646 | 0.30355 | 0.30064 | 0.29773 | 0.29483 | 0.29192 | 0.28901 | 0.2861 | 0.28319 | 0.28028 | 0.27738 | 0.27447 | 0.27156 | 0.26865 | 0.029708 | 0.03006 | 0.030368 | 0.030534 | 0.030584 | 0.030332 | 0.030375 | 0.030309 | 0.029741 | 0.029453 | 0.029166 | 0.028878 | 0.02859 | 0.028302 | 0.028015 | 0.027727 | 0.027439 | 0.027151 | 0.026864 | 0.026576 | 33070.0773 | 4814.9063 | 13981.7643 | 2035.7039 | 29103.4702 | 37724.534 | 13888449.1082 | 30372.0894
| WBL002-15395961 | 0 | WBL002 | WBL | South | 0 | 0.0035222 | 0.0035367 | 0.0035459 | 0.0035385 | 0.0035179 | 0.0035217 | 0.0035602 | 0.0035865 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 0 | 0
| WBL002-163162028 | 4 | WBL002 | WBL | South | 72723.1645 | 0.0035222 | 0.0035367 | 0.0035459 | 0.0035385 | 0.0035179 | 0.0035217 | 0.0035602 | 0.0035865 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 0.0035533 | 6.8229e-07 | 6.8871e-07 | 6.9514e-07 | 7.0157e-07 | 7.08e-07 | 6.933e-07 | 6.786e-07 | 6.639e-07 | 6.492e-07 | 6.345e-07 | 6.198e-07 | 6.051e-07 | 5.904e-07 | 5.757e-07 | 5.61e-07 | 5.463e-07 | 5.316e-07 | 5.169e-07 | 5.022e-07 | 4.875e-07 | 6.6903e-08 | 6.7813e-08 | 6.8623e-08 | 6.9113e-08 | 6.9339e-08 | 6.7974e-08 | 6.726e-08 | 6.6289e-08 | 6.4222e-08 | 6.2767e-08 | 6.1313e-08 | 5.9859e-08 | 5.8405e-08 | 5.6951e-08 | 5.5497e-08 | 5.4042e-08 | 5.2588e-08 | 5.1134e-08 | 4.968e-08 | 4.8226e-08 | 33070.0773 | 4814.9063 | 0.029738 | 0.0043298 | 0.2208 | 0.2862 | 75893.1645 | 0.23042
| WBL003-15396013 | 0 | WBL003 | WBL | South | 0 | 0.0015333 | 0.0015252 | 0.0015063 | 0.0014844 | 0.0014856 | 0.0014952 | 0.0015297 | 0.0015607 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 0 | 0
| WBL003-15396026 | 0 | WBL003 | WBL | South | 0 | 0.0015333 | 0.0015252 | 0.0015063 | 0.0014844 | 0.0014856 | 0.0014952 | 0.0015297 | 0.0015607 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 0 | 0
| WBL003-15396039 | 130 | WBL003 | WBL | South | 2363502.8471 | 0.0015333 | 0.0015252 | 0.0015063 | 0.0014844 | 0.0014856 | 0.0014952 | 0.0015297 | 0.0015607 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0.0015745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 2466527.8471 | 0
| WBL004-15395887 | 94 | WBL004 | WBL | South | 1708994.3664 | 0.0026283 | 0.0026127 | 0.0025867 | 0.0025677 | 0.0025507 | 0.0025424 | 0.0025391 | 0.0025351 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 1783489.3664 | 0
| WBL004-24598022 | 125 | WBL004 | WBL | South | 2272598.8914 | 0.0026283 | 0.0026127 | 0.0025867 | 0.0025677 | 0.0025507 | 0.0025424 | 0.0025391 | 0.0025351 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0.0025231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 2371661.3914 | 0
| WBL005-153526296 | 460 | WBL005 | WBL | South | 8363163.9205 | 0.0010666 | 0.0010781 | 0.0010883 | 0.0011112 | 0.0011327 | 0.0011694 | 0.001216 | 0.0012567 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 1.7972 | 1.8127 | 1.8282 | 1.8437 | 1.8592 | 1.8296 | 1.8 | 1.7704 | 1.7408 | 1.7112 | 1.6816 | 1.652 | 1.6224 | 1.5928 | 1.5631 | 1.5335 | 1.5039 | 1.4743 | 1.4447 | 1.4151 | 0.053368 | 0.054409 | 0.055391 | 0.05704 | 0.058629 | 0.059568 | 0.060936 | 0.061943 | 0.062048 | 0.060993 | 0.059938 | 0.058882 | 0.057827 | 0.056771 | 0.055716 | 0.054661 | 0.053605 | 0.05255 | 0.051494 | 0.050439 | 33070.0773 | 4814.9063 | 27274.5812 | 3971.0991 | 314777.2988 | 408020.9958 | 8727713.9205 | 328498.4294
| WBL005-15396050 | 147 | WBL005 | WBL | South | 2672576.2963 | 0.0010666 | 0.0010781 | 0.0010883 | 0.0011112 | 0.0011327 | 0.0011694 | 0.001216 | 0.0012567 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.50436 | 0.50646 | 0.50857 | 0.51068 | 0.51279 | 0.51018 | 0.50756 | 0.50495 | 0.50234 | 0.49973 | 0.49711 | 0.4945 | 0.49189 | 0.48928 | 0.48666 | 0.48405 | 0.48144 | 0.47883 | 0.47621 | 0.4736 | 0.014977 | 0.015201 | 0.015408 | 0.015799 | 0.01617 | 0.01661 | 0.017182 | 0.017667 | 0.017905 | 0.017812 | 0.017719 | 0.017626 | 0.017533 | 0.01744 | 0.017346 | 0.017253 | 0.01716 | 0.017067 | 0.016974 | 0.016881 | 33070.0773 | 4814.9063 | 8017.0517 | 1167.2592 | 7491.9278 | 9711.1953 | 2789073.7963 | 7818.5006
| WBL005-158638825 | 78 | WBL005 | WBL | South | 1418101.7083 | 0.0010666 | 0.0010781 | 0.0010883 | 0.0011112 | 0.0011327 | 0.0011694 | 0.001216 | 0.0012567 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.01544 | 0.015612 | 0.015784 | 0.015956 | 0.016128 | 0.015892 | 0.015655 | 0.015418 | 0.015181 | 0.014944 | 0.014707 | 0.01447 | 0.014233 | 0.013996 | 0.013759 | 0.013522 | 0.013286 | 0.013049 | 0.012812 | 0.012575 | 0.00045849 | 0.00046859 | 0.00047822 | 0.00049364 | 0.00050859 | 0.00051739 | 0.00052995 | 0.00053943 | 0.0005411 | 0.00053265 | 0.00052421 | 0.00051577 | 0.00050732 | 0.00049888 | 0.00049043 | 0.00048199 | 0.00047354 | 0.0004651 | 0.00045666 | 0.00044821 | 33070.0773 | 4814.9063 | 237.9478 | 34.6445 | 9806.0199 | 12710.7704 | 1479916.7083 | 10233.4639
| WBL005-158639092 | 48 | WBL005 | WBL | South | 872677.9743 | 0.0010666 | 0.0010781 | 0.0010883 | 0.0011112 | 0.0011327 | 0.0011694 | 0.001216 | 0.0012567 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.002411 | 0.0024295 | 0.0024479 | 0.0024664 | 0.0024849 | 0.0024446 | 0.0024044 | 0.0023641 | 0.0023239 | 0.0022836 | 0.0022433 | 0.0022031 | 0.0021628 | 0.0021226 | 0.0020823 | 0.002042 | 0.0020018 | 0.0019615 | 0.0019213 | 0.001881 | 7.1594e-05 | 7.292e-05 | 7.4166e-05 | 7.6303e-05 | 7.8359e-05 | 7.9591e-05 | 8.1394e-05 | 8.2716e-05 | 8.2831e-05 | 8.1396e-05 | 7.9961e-05 | 7.8526e-05 | 7.7091e-05 | 7.5655e-05 | 7.422e-05 | 7.2785e-05 | 7.135e-05 | 6.9915e-05 | 6.848e-05 | 6.7045e-05 | 33070.0773 | 4814.9063 | 36.4153 | 5.302 | 868.1806 | 1125.354 | 910717.9743 | 906.0245
| WBL005-158702306 | 44 | WBL005 | WBL | South | 799954.8098 | 0.0010666 | 0.0010781 | 0.0010883 | 0.0011112 | 0.0011327 | 0.0011694 | 0.001216 | 0.0012567 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.062577 | 0.062654 | 0.062731 | 0.062808 | 0.062884 | 0.062789 | 0.062693 | 0.062597 | 0.062502 | 0.062406 | 0.06231 | 0.062215 | 0.062119 | 0.062023 | 0.061928 | 0.061832 | 0.061737 | 0.061641 | 0.061545 | 0.06145 | 0.0018582 | 0.0018805 | 0.0019006 | 0.0019431 | 0.001983 | 0.0020442 | 0.0021223 | 0.0021901 | 0.0022278 | 0.0022244 | 0.002221 | 0.0022176 | 0.0022141 | 0.0022107 | 0.0022073 | 0.0022039 | 0.0022005 | 0.0021971 | 0.0021937 | 0.0021903 | 33070.0773 | 4814.9063 | 1004.0461 | 146.1862 | 31357.1034 | 40645.741 | 834824.8098 | 32723.9584
| WBL005-163161673 | 13 | WBL005 | WBL | South | 236350.2847 | 0.0010666 | 0.0010781 | 0.0010883 | 0.0011112 | 0.0011327 | 0.0011694 | 0.001216 | 0.0012567 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.00010996 | 0.00011134 | 0.00011273 | 0.00011411 | 0.0001155 | 0.00011392 | 0.00011235 | 0.00011077 | 0.0001092 | 0.00010763 | 0.00010605 | 0.00010448 | 0.0001029 | 0.00010133 | 9.975e-05 | 9.8175e-05 | 9.66e-05 | 9.5025e-05 | 9.345e-05 | 9.1875e-05 | 3.2652e-06 | 3.3419e-06 | 3.4154e-06 | 3.5303e-06 | 3.6422e-06 | 3.7091e-06 | 3.8033e-06 | 3.8758e-06 | 3.8923e-06 | 3.8361e-06 | 3.78e-06 | 3.7239e-06 | 3.6677e-06 | 3.6116e-06 | 3.5554e-06 | 3.4993e-06 | 3.4432e-06 | 3.387e-06 | 3.3309e-06 | 3.2747e-06 | 33070.0773 | 4814.9063 | 1.7129 | 0.2494 | 72.9127 | 94.511 | 246652.7847 | 76.091
| WBL005-163161826 | 2 | WBL005 | WBL | South | 36361.5823 | 0.0010666 | 0.0010781 | 0.0010883 | 0.0011112 | 0.0011327 | 0.0011694 | 0.001216 | 0.0012567 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0.0012803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 37946.5823 | 0
| WBL006-15435914 | 219 | WBL006 | WBL | South | 3981593.2578 | 0.00079006 | 0.00080959 | 0.00083296 | 0.00085894 | 0.00088806 | 0.00092345 | 0.00096059 | 0.0009925 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.0010169 | 0.00026023 | 0.00026243 | 0.00026463 | 0.00026682 | 0.00026902 | 0.00026628 | 0.00026354 | 0.0002608 | 0.00025806 | 0.00025532 | 0.00025258 | 0.00024985 | 0.00024711 | 0.00024437 | 0.00024163 | 0.00023889 | 0.00023615 | 0.00023341 | 0.00023067 | 0.00022793 | 5.7239e-06 | 5.9149e-06 | 6.1365e-06 | 6.3805e-06 | 6.6511e-06 | 6.8458e-06 | 7.0478e-06 | 7.2063e-06 | 7.306e-06 | 7.2284e-06 | 7.1509e-06 | 7.0734e-06 | 6.9958e-06 | 6.9183e-06 | 6.8407e-06 | 6.7632e-06 | 6.6856e-06 | 6.6081e-06 | 6.5306e-06 | 6.453e-06 | 33070.0773 | 4814.9063 | 3.1977 | 0.46558 | 5.095 | 6.6042 | 4155150.7578 | 5.317
| WBL008-15395863 | 200 | WBL008 | WBL | South | 3636158.2263 | 0.0010826 | 0.0010724 | 0.0010528 | 0.0010337 | 0.0010356 | 0.0010458 | 0.0010707 | 0.001092 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 0.001102 | 1.133 | 1.1358 | 1.1385 | 1.1413 | 1.1441 | 1.1407 | 1.1373 | 1.1339 | 1.1305 | 1.1271 | 1.1237 | 1.1203 | 1.1169 | 1.1135 | 1.1101 | 1.1067 | 1.1033 | 1.0999 | 1.0965 | 1.0931 | 0.03415 | 0.03391 | 0.033371 | 0.032843 | 0.032984 | 0.033211 | 0.033901 | 0.034472 | 0.034684 | 0.03458 | 0.034476 | 0.034371 | 0.034267 | 0.034163 | 0.034059 | 0.033954 | 0.03385 | 0.033746 | 0.033642 | 0.033538 | 33070.0773 | 4814.9063 | 16203.43 | 2359.1719 | 25194.9426 | 32658.2178 | 3794658.2263 | 26293.1892
| WBL010-15395826 | 98 | WBL010 | WBL | South | 1781717.5309 | 0.002965 | 0.0029079 | 0.0028322 | 0.0027707 | 0.0027366 | 0.0027207 | 0.0027357 | 0.0027446 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0.0027313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 1859382.5309 | 0
| WBL012-153865449 | 21 | WBL012 | WBL | South | 381796.6138 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 398439.1138 | 0
| WBL012-162960471 | 7 | WBL012 | WBL | South | 127265.5379 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 2.4908e-06 | 2.5138e-06 | 2.5369e-06 | 2.5599e-06 | 2.583e-06 | 2.5426e-06 | 2.5023e-06 | 2.462e-06 | 2.4216e-06 | 2.3813e-06 | 2.3409e-06 | 2.3006e-06 | 2.2602e-06 | 2.2199e-06 | 2.1795e-06 | 2.1392e-06 | 2.0988e-06 | 2.0585e-06 | 2.0181e-06 | 1.9778e-06 | 1.1178e-07 | 1.1398e-07 | 1.1575e-07 | 1.1697e-07 | 1.1709e-07 | 1.15e-07 | 1.1459e-07 | 1.146e-07 | 1.1221e-07 | 1.1034e-07 | 1.0847e-07 | 1.066e-07 | 1.0473e-07 | 1.0286e-07 | 1.0099e-07 | 9.912e-08 | 9.725e-08 | 9.538e-08 | 9.3511e-08 | 9.1641e-08 | 33070.0773 | 4814.9063 | 0.051931 | 0.007561 | 1.4508 | 1.8805 | 132813.0379 | 1.514
| WBL012-162960671 | 16 | WBL012 | WBL | South | 290892.6581 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 2.7216e-05 | 2.7552e-05 | 2.7888e-05 | 2.8224e-05 | 2.856e-05 | 2.7978e-05 | 2.7396e-05 | 2.6814e-05 | 2.6232e-05 | 2.565e-05 | 2.5068e-05 | 2.4486e-05 | 2.3904e-05 | 2.3322e-05 | 2.274e-05 | 2.2158e-05 | 2.1576e-05 | 2.0994e-05 | 2.0412e-05 | 1.983e-05 | 1.2214e-06 | 1.2493e-06 | 1.2725e-06 | 1.2896e-06 | 1.2947e-06 | 1.2654e-06 | 1.2546e-06 | 1.2481e-06 | 1.2155e-06 | 1.1885e-06 | 1.1616e-06 | 1.1346e-06 | 1.1076e-06 | 1.0806e-06 | 1.0537e-06 | 1.0267e-06 | 9.9975e-07 | 9.7278e-07 | 9.4581e-07 | 9.1884e-07 | 33070.0773 | 4814.9063 | 0.55793 | 0.081233 | 8.9084 | 11.5473 | 303572.6581 | 9.2967
| WBL012-162960865 | 16 | WBL012 | WBL | South | 290892.6581 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 5.9277e-05 | 5.9907e-05 | 6.0538e-05 | 6.1169e-05 | 6.18e-05 | 6.0366e-05 | 5.8932e-05 | 5.7498e-05 | 5.6064e-05 | 5.463e-05 | 5.3196e-05 | 5.1762e-05 | 5.0328e-05 | 4.8894e-05 | 4.746e-05 | 4.6026e-05 | 4.4592e-05 | 4.3158e-05 | 4.1724e-05 | 4.029e-05 | 2.6603e-06 | 2.7163e-06 | 2.7622e-06 | 2.7949e-06 | 2.8015e-06 | 2.7303e-06 | 2.6988e-06 | 2.6764e-06 | 2.5978e-06 | 2.5313e-06 | 2.4649e-06 | 2.3984e-06 | 2.332e-06 | 2.2656e-06 | 2.1991e-06 | 2.1327e-06 | 2.0662e-06 | 1.9998e-06 | 1.9333e-06 | 1.8669e-06 | 33070.0773 | 4814.9063 | 1.1892 | 0.17315 | 18.9913 | 24.617 | 303572.6581 | 19.8192
| WBL012-163034361 | 9 | WBL012 | WBL | South | 163627.1202 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 2.3079e-05 | 2.3385e-05 | 2.369e-05 | 2.3995e-05 | 2.43e-05 | 2.3883e-05 | 2.3466e-05 | 2.3049e-05 | 2.2632e-05 | 2.2215e-05 | 2.1798e-05 | 2.1381e-05 | 2.0964e-05 | 2.0547e-05 | 2.013e-05 | 1.9713e-05 | 1.9296e-05 | 1.8879e-05 | 1.8462e-05 | 1.8045e-05 | 1.0358e-06 | 1.0603e-06 | 1.0809e-06 | 1.0964e-06 | 1.1016e-06 | 1.0802e-06 | 1.0746e-06 | 1.0729e-06 | 1.0487e-06 | 1.0294e-06 | 1.01e-06 | 9.9071e-07 | 9.7139e-07 | 9.5207e-07 | 9.3274e-07 | 9.1342e-07 | 8.941e-07 | 8.7478e-07 | 8.5546e-07 | 8.3613e-07 | 33070.0773 | 4814.9063 | 0.48314 | 0.070343 | 8.6769 | 11.2472 | 170759.6202 | 9.0552
| WBL012-163034588 | 6 | WBL012 | WBL | South | 109084.7468 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 113839.7468 | 0
| WBL012-163150328 | 5 | WBL012 | WBL | South | 90903.9557 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 94866.4557 | 0
| WBL012-163162276 | 12 | WBL012 | WBL | South | 218169.4936 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 227679.4936 | 0
| WBL012-163162391 | 14 | WBL012 | WBL | South | 254531.0758 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.00087727 | 0.00088537 | 0.00089348 | 0.00090159 | 0.0009097 | 0.00089694 | 0.00088418 | 0.00087142 | 0.00085866 | 0.0008459 | 0.00083314 | 0.00082038 | 0.00080762 | 0.00079486 | 0.0007821 | 0.00076934 | 0.00075658 | 0.00074382 | 0.00073106 | 0.0007183 | 3.9371e-05 | 4.0145e-05 | 4.0767e-05 | 4.1195e-05 | 4.1239e-05 | 4.0568e-05 | 4.0491e-05 | 4.0563e-05 | 3.9787e-05 | 3.9196e-05 | 3.8604e-05 | 3.8013e-05 | 3.7422e-05 | 3.6831e-05 | 3.6239e-05 | 3.5648e-05 | 3.5057e-05 | 3.4466e-05 | 3.3874e-05 | 3.3283e-05 | 33070.0773 | 4814.9063 | 18.451 | 2.6864 | 281.1338 | 364.4116 | 265626.0758 | 293.3884
| WBL012-163162602 | 12 | WBL012 | WBL | South | 218169.4936 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.00046781 | 0.00047399 | 0.00048016 | 0.00048633 | 0.0004925 | 0.00048435 | 0.0004762 | 0.00046805 | 0.0004599 | 0.00045175 | 0.0004436 | 0.00043545 | 0.0004273 | 0.00041915 | 0.000411 | 0.00040285 | 0.0003947 | 0.00038655 | 0.0003784 | 0.00037025 | 2.0995e-05 | 2.1492e-05 | 2.1908e-05 | 2.2221e-05 | 2.2326e-05 | 2.1907e-05 | 2.1807e-05 | 2.1787e-05 | 2.131e-05 | 2.0932e-05 | 2.0555e-05 | 2.0177e-05 | 1.9799e-05 | 1.9422e-05 | 1.9044e-05 | 1.8666e-05 | 1.8289e-05 | 1.7911e-05 | 1.7534e-05 | 1.7156e-05 | 33070.0773 | 4814.9063 | 9.8257 | 1.4306 | 282.3362 | 365.9702 | 227679.4936 | 294.6432
| WBL012-163162797 | 19 | WBL012 | WBL | South | 345435.0315 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 360492.5315 | 0
| WBL012-163162997 | 6 | WBL012 | WBL | South | 109084.7468 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33070.0773 | 4814.9063 | 0 | 0 | 0 | 0 | 113839.7468 | 0
| WBL012-163205557 | 16 | WBL012 | WBL | South | 290892.6581 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 4.2808e-05 | 4.3266e-05 | 4.3724e-05 | 4.4182e-05 | 4.464e-05 | 4.36e-05 | 4.256e-05 | 4.152e-05 | 4.048e-05 | 3.944e-05 | 3.84e-05 | 3.736e-05 | 3.632e-05 | 3.528e-05 | 3.4239e-05 | 3.3199e-05 | 3.2159e-05 | 3.1119e-05 | 3.0079e-05 | 2.9039e-05 | 1.9212e-06 | 1.9618e-06 | 1.995e-06 | 2.0187e-06 | 2.0236e-06 | 1.972e-06 | 1.949e-06 | 1.9327e-06 | 1.8757e-06 | 1.8275e-06 | 1.7793e-06 | 1.7311e-06 | 1.6829e-06 | 1.6347e-06 | 1.5865e-06 | 1.5383e-06 | 1.4901e-06 | 1.4419e-06 | 1.3938e-06 | 1.3456e-06 | 33070.0773 | 4814.9063 | 0.85852 | 0.125 | 5.3071 | 6.8792 | 303572.6581 | 5.5385
| WBL012-163205740 | 15 | WBL012 | WBL | South | 272711.867 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 3.9136e-10 | 3.9464e-10 | 3.9793e-10 | 4.0121e-10 | 4.045e-10 | 4.004e-10 | 3.963e-10 | 3.922e-10 | 3.881e-10 | 3.84e-10 | 3.799e-10 | 3.758e-10 | 3.717e-10 | 3.676e-10 | 3.635e-10 | 3.594e-10 | 3.553e-10 | 3.512e-10 | 3.471e-10 | 3.43e-10 | 1.7564e-11 | 1.7894e-11 | 1.8156e-11 | 1.8332e-11 | 1.8337e-11 | 1.811e-11 | 1.8148e-11 | 1.8256e-11 | 1.7983e-11 | 1.7793e-11 | 1.7603e-11 | 1.7413e-11 | 1.7223e-11 | 1.7033e-11 | 1.6843e-11 | 1.6653e-11 | 1.6463e-11 | 1.6273e-11 | 1.6083e-11 | 1.5893e-11 | 33070.0773 | 4814.9063 | 8.3839e-06 | 1.2207e-06 | 0.00030106 | 0.00039024 | 284599.367 | 0.00031418
| WBL012-171331101 | 68 | WBL012 | WBL | South | 1236293.7969 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 0.0002834 | 1.2719e-05 | 1.285e-05 | 1.2931e-05 | 1.2949e-05 | 1.2847e-05 | 1.2818e-05 | 1.2978e-05 | 1.3192e-05 | 1.3132e-05 | 1.3132e-05 | 1.3132e-05 | 1.3132e-05 | 1.3132e-05 | 1.3132e-05 | 1.3132e-05 | 1.3132e-05 | 1.3132e-05 | 1.3132e-05 | 1.3132e-05 | 1.3132e-05 | 33070.0773 | 4814.9063 | 6.2261 | 0.90651 | 194.8435 | 252.5602 | 1290183.7969 | 203.3367
| WBL012-24598048 | 226 | WBL012 | WBL | South | 4108858.7957 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 1.9193 | 1.9265 | 1.9337 | 1.9409 | 1.9481 | 1.9353 | 1.9225 | 1.9097 | 1.8969 | 1.884 | 1.8712 | 1.8584 | 1.8456 | 1.8328 | 1.82 | 1.8072 | 1.7943 | 1.7815 | 1.7687 | 1.7559 | 0.086136 | 0.08735 | 0.088229 | 0.088682 | 0.088312 | 0.087531 | 0.08804 | 0.088891 | 0.087893 | 0.087299 | 0.086705 | 0.086112 | 0.085518 | 0.084924 | 0.08433 | 0.083737 | 0.083143 | 0.082549 | 0.081956 | 0.081362 | 33070.0773 | 4814.9063 | 41271.0747 | 6008.9475 | 66520.7362 | 86225.5859 | 4287963.7957 | 69420.3726
| WBL012-24611149 | 569 | WBL012 | WBL | South | 10344870.1538 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.25271 | 0.2552 | 0.25769 | 0.26018 | 0.26267 | 0.25934 | 0.25601 | 0.25269 | 0.24936 | 0.24603 | 0.24271 | 0.23938 | 0.23605 | 0.23273 | 0.2294 | 0.22607 | 0.22274 | 0.21942 | 0.21609 | 0.21276 | 0.011341 | 0.011571 | 0.011758 | 0.011888 | 0.011907 | 0.01173 | 0.011724 | 0.011762 | 0.011554 | 0.0114 | 0.011246 | 0.011092 | 0.010938 | 0.010784 | 0.010629 | 0.010475 | 0.010321 | 0.010167 | 0.010013 | 0.0098586 | 33070.0773 | 4814.9063 | 5365.196 | 781.1568 | 62695.319 | 81266.9992 | 10795802.6538 | 65428.2056
| WBL012-88823662 | 146 | WBL012 | WBL | South | 2654395.5052 | 0.0016121 | 0.0016287 | 0.0016389 | 0.0016412 | 0.0016283 | 0.0016246 | 0.0016449 | 0.001672 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.0016644 | 0.23852 | 0.23882 | 0.23912 | 0.23942 | 0.23972 | 0.23935 | 0.23899 | 0.23862 | 0.23826 | 0.23789 | 0.23753 | 0.23716 | 0.23679 | 0.23643 | 0.23606 | 0.2357 | 0.23533 | 0.23497 | 0.2346 | 0.23424 | 0.010705 | 0.010829 | 0.01091 | 0.010939 | 0.010867 | 0.010826 | 0.010944 | 0.011107 | 0.01104 | 0.011023 | 0.011006 | 0.010989 | 0.010972 | 0.010955 | 0.010938 | 0.010921 | 0.010904 | 0.010887 | 0.010871 | 0.010854 | 33070.0773 | 4814.9063 | 5221.573 | 760.2457 | 4027.1715 | 5220.1049 | 2770100.5052 | 4202.7157
| WIN011-124931073 | 87 | WIN011 | WIN | South | 1581728.8284 | 0.0010596 | 0.0010682 | 0.0010786 | 0.001084 | 0.0010872 | 0.0010971 | 0.001112 | 0.0011258 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.053928 | 0.054491 | 0.055053 | 0.055616 | 0.056178 | 0.056016 | 0.055853 | 0.05569 | 0.055528 | 0.055365 | 0.055202 | 0.05504 | 0.054877 | 0.054714 | 0.054552 | 0.054389 | 0.054226 | 0.054064 | 0.053901 | 0.053738 | 0.0015908 | 0.0016205 | 0.0016531 | 0.0016783 | 0.0017004 | 0.001711 | 0.0017291 | 0.0017455 | 0.0017394 | 0.0017343 | 0.0017292 | 0.0017241 | 0.001719 | 0.0017139 | 0.0017088 | 0.0017038 | 0.0016987 | 0.0016936 | 0.0016885 | 0.0016834 | 34660.2137 | 8508.3796 | 849.3035 | 208.4868 | 38111.2722 | 49400.6375 | 1650676.3284 | 39772.5411
| WIN011-154067565 | 82 | WIN011 | WIN | South | 1490824.8728 | 0.0010596 | 0.0010682 | 0.0010786 | 0.001084 | 0.0010872 | 0.0010971 | 0.001112 | 0.0011258 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 1.2816 | 1.2945 | 1.3074 | 1.3203 | 1.3331 | 1.3254 | 1.3176 | 1.3099 | 1.3021 | 1.2944 | 1.2866 | 1.2789 | 1.2711 | 1.2633 | 1.2556 | 1.2478 | 1.2401 | 1.2323 | 1.2246 | 1.2168 | 0.037807 | 0.038498 | 0.039258 | 0.039842 | 0.040351 | 0.040483 | 0.040792 | 0.041056 | 0.040789 | 0.040546 | 0.040303 | 0.04006 | 0.039817 | 0.039574 | 0.039331 | 0.039088 | 0.038846 | 0.038603 | 0.03836 | 0.038117 | 34660.2137 | 8508.3796 | 19852.0508 | 4873.2759 | 48680.598 | 63100.8213 | 1555809.8728 | 50802.5834
| WIN011-155049323 | 33 | WIN011 | WIN | South | 599966.1073 | 0.0010596 | 0.0010682 | 0.0010786 | 0.001084 | 0.0010872 | 0.0010971 | 0.001112 | 0.0011258 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.00058411 | 0.00059083 | 0.00059755 | 0.00060428 | 0.000611 | 0.00060833 | 0.00060567 | 0.000603 | 0.00060034 | 0.00059767 | 0.00059501 | 0.00059234 | 0.00058968 | 0.00058701 | 0.00058435 | 0.00058168 | 0.00057902 | 0.00057635 | 0.00057369 | 0.00057102 | 1.723e-05 | 1.7571e-05 | 1.7943e-05 | 1.8236e-05 | 1.8494e-05 | 1.8581e-05 | 1.8751e-05 | 1.89e-05 | 1.8806e-05 | 1.8722e-05 | 1.8639e-05 | 1.8555e-05 | 1.8472e-05 | 1.8388e-05 | 1.8305e-05 | 1.8221e-05 | 1.8138e-05 | 1.8054e-05 | 1.7971e-05 | 1.7888e-05 | 34660.2137 | 8508.3796 | 9.1606 | 2.2487 | 395.8404 | 513.0967 | 626118.6073 | 413.0951
| WIN011-157092882 | 119 | WIN011 | WIN | South | 2163514.1446 | 0.0010596 | 0.0010682 | 0.0010786 | 0.001084 | 0.0010872 | 0.0010971 | 0.001112 | 0.0011258 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.17408 | 0.1758 | 0.17752 | 0.17924 | 0.18096 | 0.18019 | 0.17942 | 0.17865 | 0.17788 | 0.17711 | 0.17634 | 0.17557 | 0.1748 | 0.17403 | 0.17326 | 0.17249 | 0.17172 | 0.17096 | 0.17019 | 0.16942 | 0.0051352 | 0.0052282 | 0.0053306 | 0.0054091 | 0.0054773 | 0.0055038 | 0.0055547 | 0.0055996 | 0.0055723 | 0.0055481 | 0.005524 | 0.0054999 | 0.0054758 | 0.0054517 | 0.0054276 | 0.0054034 | 0.0053793 | 0.0053552 | 0.0053311 | 0.005307 | 34660.2137 | 8508.3796 | 2717.3268 | 667.0486 | 144858.6203 | 187768.8091 | 2257821.6446 | 151173.0021
| WIN011-160628518 | 0 | WIN011 | WIN | South | 0 | 0.0010596 | 0.0010682 | 0.0010786 | 0.001084 | 0.0010872 | 0.0010971 | 0.001112 | 0.0011258 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34660.2137 | 8508.3796 | 0 | 0 | 0 | 0 | 0 | 0
| WIN011-160628528 | 844 | WIN011 | WIN | South | 15344587.715 | 0.0010596 | 0.0010682 | 0.0010786 | 0.001084 | 0.0010872 | 0.0010971 | 0.001112 | 0.0011258 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 20.8687 | 21.0708 | 21.273 | 21.4752 | 21.6774 | 21.5549 | 21.4325 | 21.3101 | 21.1877 | 21.0652 | 20.9428 | 20.8204 | 20.6979 | 20.5755 | 20.4531 | 20.3306 | 20.2082 | 20.0858 | 19.9633 | 19.8409 | 0.61559 | 0.62662 | 0.63877 | 0.64807 | 0.65612 | 0.65838 | 0.66352 | 0.66793 | 0.66371 | 0.65987 | 0.65604 | 0.6522 | 0.64837 | 0.64453 | 0.6407 | 0.63686 | 0.63303 | 0.62919 | 0.62536 | 0.62152 | 34660.2137 | 8508.3796 | 323161.9495 | 79329.7053 | 2301591.8797 | 2983372.0989 | 16013457.715 | 2401918.183
| WIN011-72970601 | 66 | WIN011 | WIN | South | 1199932.2147 | 0.0010596 | 0.0010682 | 0.0010786 | 0.001084 | 0.0010872 | 0.0010971 | 0.001112 | 0.0011258 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.085638 | 0.086516 | 0.087394 | 0.088271 | 0.089149 | 0.08933 | 0.089511 | 0.089693 | 0.089874 | 0.090055 | 0.090236 | 0.090417 | 0.090598 | 0.090779 | 0.09096 | 0.091141 | 0.091323 | 0.091504 | 0.091685 | 0.091866 | 0.0025262 | 0.0025729 | 0.0026242 | 0.0026638 | 0.0026983 | 0.0027285 | 0.0027712 | 0.0028113 | 0.0028153 | 0.002821 | 0.0028267 | 0.0028323 | 0.002838 | 0.0028437 | 0.0028494 | 0.002855 | 0.0028607 | 0.0028664 | 0.0028721 | 0.0028777 | 34660.2137 | 8508.3796 | 1382.5149 | 339.3794 | 47045.2756 | 60981.0818 | 1252237.2147 | 49095.9774
| WIN011-72970660 | 124 | WIN011 | WIN | South | 2254418.1003 | 0.0010596 | 0.0010682 | 0.0010786 | 0.001084 | 0.0010872 | 0.0010971 | 0.001112 | 0.0011258 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.12089 | 0.12234 | 0.12378 | 0.12523 | 0.12667 | 0.12648 | 0.12628 | 0.12608 | 0.12589 | 0.12569 | 0.12549 | 0.1253 | 0.1251 | 0.1249 | 0.12471 | 0.12451 | 0.12431 | 0.12412 | 0.12392 | 0.12372 | 0.0035662 | 0.0036382 | 0.0037169 | 0.0037791 | 0.0038341 | 0.0038631 | 0.0039095 | 0.0039519 | 0.0039434 | 0.0039373 | 0.0039311 | 0.0039249 | 0.0039188 | 0.0039126 | 0.0039064 | 0.0039003 | 0.0038941 | 0.003888 | 0.0038818 | 0.0038756 | 34660.2137 | 8508.3796 | 1926.7128 | 472.9689 | 73926.4103 | 95824.9775 | 2352688.1003 | 77148.8598
| WIN011-77738018 | 68 | WIN011 | WIN | South | 1236293.7969 | 0.0010596 | 0.0010682 | 0.0010786 | 0.001084 | 0.0010872 | 0.0010971 | 0.001112 | 0.0011258 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.0011252 | 0.07007 | 0.070864 | 0.071659 | 0.072453 | 0.073247 | 0.072776 | 0.072304 | 0.071833 | 0.071362 | 0.070891 | 0.07042 | 0.069949 | 0.069478 | 0.069007 | 0.068536 | 0.068065 | 0.067594 | 0.067123 | 0.066652 | 0.066181 | 0.002067 | 0.0021074 | 0.0021517 | 0.0021864 | 0.002217 | 0.0022229 | 0.0022385 | 0.0022515 | 0.0022354 | 0.0022207 | 0.0022059 | 0.0021912 | 0.0021764 | 0.0021617 | 0.0021469 | 0.0021322 | 0.0021174 | 0.0021026 | 0.0020879 | 0.0020731 | 34660.2137 | 8508.3796 | 1086.3381 | 266.674 | 34936.2331 | 45285.0847 | 1290183.7969 | 36459.1022
| WIN022-160628376 | 0 | WIN022 | WIN | South | 0 | 0.0012086 | 0.0012146 | 0.0012224 | 0.0012257 | 0.001221 | 0.0012229 | 0.0012353 | 0.0012446 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34660.2137 | 8508.3796 | 0 | 0 | 0 | 0 | 0 | 0
| WIN022-160628386 | 683 | WIN022 | WIN | South | 12417480.3428 | 0.0012086 | 0.0012146 | 0.0012224 | 0.0012257 | 0.001221 | 0.0012229 | 0.0012353 | 0.0012446 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 11.9332 | 12.0331 | 12.1331 | 12.233 | 12.3329 | 12.3096 | 12.2863 | 12.263 | 12.2397 | 12.2164 | 12.1931 | 12.1698 | 12.1465 | 12.1232 | 12.0999 | 12.0766 | 12.0533 | 12.03 | 12.0068 | 11.9835 | 0.40152 | 0.40689 | 0.41292 | 0.41742 | 0.41924 | 0.41908 | 0.42255 | 0.4249 | 0.42095 | 0.42015 | 0.41935 | 0.41855 | 0.41775 | 0.41694 | 0.41614 | 0.41534 | 0.41454 | 0.41374 | 0.41294 | 0.41214 | 34660.2137 | 8508.3796 | 208461.2564 | 51173.0111 | 2018704.9246 | 2616688.0415 | 12958757.8428 | 2106700.1962
| WIN022-164674921 | 1 | WIN022 | WIN | South | 18180.7911 | 0.0012086 | 0.0012146 | 0.0012224 | 0.0012257 | 0.001221 | 0.0012229 | 0.0012353 | 0.0012446 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 8.3371e-05 | 8.4229e-05 | 8.5086e-05 | 8.5943e-05 | 8.68e-05 | 8.665e-05 | 8.65e-05 | 8.635e-05 | 8.62e-05 | 8.605e-05 | 8.59e-05 | 8.575e-05 | 8.56e-05 | 8.545e-05 | 8.53e-05 | 8.515e-05 | 8.5e-05 | 8.485e-05 | 8.47e-05 | 8.455e-05 | 2.8052e-06 | 2.8481e-06 | 2.8957e-06 | 2.9326e-06 | 2.9507e-06 | 2.95e-06 | 2.9749e-06 | 2.9919e-06 | 2.9646e-06 | 2.9594e-06 | 2.9543e-06 | 2.9491e-06 | 2.944e-06 | 2.9388e-06 | 2.9336e-06 | 2.9285e-06 | 2.9233e-06 | 2.9182e-06 | 2.913e-06 | 2.9079e-06 | 34660.2137 | 8508.3796 | 1.4667 | 0.36004 | 1.1236 | 1.4564 | 18973.2911 | 1.1726
| WIN022-164675227 | 2 | WIN022 | WIN | South | 36361.5823 | 0.0012086 | 0.0012146 | 0.0012224 | 0.0012257 | 0.001221 | 0.0012229 | 0.0012353 | 0.0012446 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34660.2137 | 8508.3796 | 0 | 0 | 0 | 0 | 37946.5823 | 0
| WIN022-183128966 | 35 | WIN022 | WIN | South | 636327.6896 | 0.0012086 | 0.0012146 | 0.0012224 | 0.0012257 | 0.001221 | 0.0012229 | 0.0012353 | 0.0012446 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.002549 | 0.0025661 | 0.0025833 | 0.0026004 | 0.0026175 | 0.0026157 | 0.002614 | 0.0026123 | 0.0026105 | 0.0026088 | 0.002607 | 0.0026053 | 0.0026036 | 0.0026018 | 0.0026001 | 0.0025983 | 0.0025966 | 0.0025949 | 0.0025931 | 0.0025914 | 8.5767e-05 | 8.6771e-05 | 8.7914e-05 | 8.8731e-05 | 8.8978e-05 | 8.9054e-05 | 8.9901e-05 | 9.0512e-05 | 8.9781e-05 | 8.9721e-05 | 8.9662e-05 | 8.9602e-05 | 8.9542e-05 | 8.9482e-05 | 8.9422e-05 | 8.9362e-05 | 8.9302e-05 | 8.9242e-05 | 8.9183e-05 | 8.9123e-05 | 34660.2137 | 8508.3796 | 44.5658 | 10.94 | 995.7763 | 1290.7463 | 664065.1896 | 1039.1822
| WIN022-79032273 | 34 | WIN022 | WIN | South | 618146.8985 | 0.0012086 | 0.0012146 | 0.0012224 | 0.0012257 | 0.001221 | 0.0012229 | 0.0012353 | 0.0012446 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.00073894 | 0.00074546 | 0.00075197 | 0.00075849 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 0.000765 | 2.4863e-05 | 2.5207e-05 | 2.5591e-05 | 2.5881e-05 | 2.6005e-05 | 2.6045e-05 | 2.631e-05 | 2.6507e-05 | 2.631e-05 | 2.631e-05 | 2.631e-05 | 2.631e-05 | 2.631e-05 | 2.631e-05 | 2.631e-05 | 2.631e-05 | 2.631e-05 | 2.631e-05 | 2.631e-05 | 2.631e-05 | 34660.2137 | 8508.3796 | 13.0522 | 3.2041 | 226.6377 | 293.7726 | 645091.8985 | 236.5169
| WIN022-79245551 | 1 | WIN022 | WIN | South | 18180.7911 | 0.0012086 | 0.0012146 | 0.0012224 | 0.0012257 | 0.001221 | 0.0012229 | 0.0012353 | 0.0012446 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0.0012353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34660.2137 | 8508.3796 | 0 | 0 | 0 | 0 | 18973.2911 | 0
| WIN023-154876693 | 54 | WIN023 | WIN | South | 981762.7211 | 0.0015259 | 0.0015476 | 0.0015687 | 0.0015905 | 0.0015964 | 0.0016099 | 0.0016451 | 0.0016904 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.029934 | 0.03017 | 0.030406 | 0.030642 | 0.030877 | 0.030901 | 0.030924 | 0.030948 | 0.030971 | 0.030994 | 0.031018 | 0.031041 | 0.031064 | 0.031088 | 0.031111 | 0.031134 | 0.031158 | 0.031181 | 0.031205 | 0.031228 | 0.0012716 | 0.0012999 | 0.0013279 | 0.0013568 | 0.0013723 | 0.0013849 | 0.0014163 | 0.0014564 | 0.0014813 | 0.0014824 | 0.0014835 | 0.0014846 | 0.0014858 | 0.0014869 | 0.001488 | 0.0014891 | 0.0014902 | 0.0014914 | 0.0014925 | 0.0014936 | 34660.2137 | 8508.3796 | 713.5369 | 175.1588 | 12875.8849 | 16689.9945 | 1024557.7211 | 13437.1443
| WIN023-154908067 | 16 | WIN023 | WIN | South | 290892.6581 | 0.0015259 | 0.0015476 | 0.0015687 | 0.0015905 | 0.0015964 | 0.0016099 | 0.0016451 | 0.0016904 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.00012981 | 0.00013115 | 0.0001325 | 0.00013385 | 0.0001352 | 0.00013528 | 0.00013536 | 0.00013544 | 0.00013552 | 0.0001356 | 0.00013568 | 0.00013576 | 0.00013584 | 0.00013592 | 0.000136 | 0.00013608 | 0.00013616 | 0.00013624 | 0.00013632 | 0.0001364 | 5.5141e-06 | 5.6508e-06 | 5.7869e-06 | 5.9268e-06 | 6.0086e-06 | 6.0631e-06 | 6.1995e-06 | 6.3738e-06 | 6.4817e-06 | 6.4855e-06 | 6.4894e-06 | 6.4932e-06 | 6.497e-06 | 6.5009e-06 | 6.5047e-06 | 6.5085e-06 | 6.5123e-06 | 6.5162e-06 | 6.52e-06 | 6.5238e-06 | 34660.2137 | 8508.3796 | 3.1171 | 0.76519 | 70.8269 | 91.8073 | 303572.6581 | 73.9142
| WIN023-160628335 | 397 | WIN023 | WIN | South | 7217774.0792 | 0.0015259 | 0.0015476 | 0.0015687 | 0.0015905 | 0.0015964 | 0.0016099 | 0.0016451 | 0.0016904 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 6.582 | 6.6322 | 6.6824 | 6.7325 | 6.7827 | 6.7962 | 6.8097 | 6.8232 | 6.8367 | 6.8502 | 6.8637 | 6.8772 | 6.8906 | 6.9041 | 6.9176 | 6.9311 | 6.9446 | 6.9581 | 6.9716 | 6.9851 | 0.2796 | 0.28575 | 0.29184 | 0.29811 | 0.30144 | 0.3046 | 0.31189 | 0.3211 | 0.32699 | 0.32763 | 0.32828 | 0.32892 | 0.32957 | 0.33021 | 0.33086 | 0.3315 | 0.33215 | 0.33279 | 0.33344 | 0.33408 | 34660.2137 | 8508.3796 | 157766.564 | 38728.4922 | 857538.3254 | 1111559.324 | 7532396.5792 | 894918.3887
| WIN023-73352598 | 102 | WIN023 | WIN | South | 1854440.6954 | 0.0015259 | 0.0015476 | 0.0015687 | 0.0015905 | 0.0015964 | 0.0016099 | 0.0016451 | 0.0016904 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.0051598 | 0.0052311 | 0.0053025 | 0.0053738 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.0054452 | 0.00021918 | 0.00022538 | 0.00023158 | 0.00023795 | 0.000242 | 0.00024405 | 0.00024939 | 0.00025625 | 0.00026043 | 0.00026043 | 0.00026043 | 0.00026043 | 0.00026043 | 0.00026043 | 0.00026043 | 0.00026043 | 0.00026043 | 0.00026043 | 0.00026043 | 0.00026043 | 34660.2137 | 8508.3796 | 124.9135 | 30.6637 | 4257.2251 | 5518.3053 | 1935275.6954 | 4442.7974
| WIN023-84419247 | 50 | WIN023 | WIN | South | 909039.5566 | 0.0015259 | 0.0015476 | 0.0015687 | 0.0015905 | 0.0015964 | 0.0016099 | 0.0016451 | 0.0016904 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.001718 | 0.0015749 | 0.0015927 | 0.0016105 | 0.0016282 | 0.001646 | 0.001648 | 0.00165 | 0.001652 | 0.001654 | 0.001656 | 0.001658 | 0.00166 | 0.001662 | 0.001664 | 0.001666 | 0.001668 | 0.00167 | 0.001672 | 0.001674 | 0.001676 | 6.6902e-05 | 6.8621e-05 | 7.0335e-05 | 7.2096e-05 | 7.3152e-05 | 7.3861e-05 | 7.557e-05 | 7.7743e-05 | 7.9108e-05 | 7.9204e-05 | 7.93e-05 | 7.9395e-05 | 7.9491e-05 | 7.9587e-05 | 7.9682e-05 | 7.9778e-05 | 7.9874e-05 | 7.9969e-05 | 8.0065e-05 | 8.0161e-05 | 34660.2137 | 8508.3796 | 38.0537 | 9.3414 | 1080.6591 | 1400.7732 | 948664.5566 | 1127.765
| WMN013-117981106 | 53 | WMN013 | WMN | North | 1249015.2882 | 0.032336 | 0.032355 | 0.032171 | 0.031885 | 0.031336 | 0.030922 | 0.030935 | 0.031074 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.62948 | 0.63303 | 0.63659 | 0.64014 | 0.6437 | 0.64173 | 0.63976 | 0.6378 | 0.63583 | 0.63386 | 0.6319 | 0.62993 | 0.62796 | 0.62599 | 0.62403 | 0.62206 | 0.62009 | 0.61813 | 0.61616 | 0.61419 | 0.56669 | 0.57021 | 0.57015 | 0.56824 | 0.56156 | 0.55244 | 0.55099 | 0.55175 | 0.54173 | 0.54005 | 0.53838 | 0.5367 | 0.53503 | 0.53335 | 0.53168 | 0.53 | 0.52832 | 0.52665 | 0.52497 | 0.5233 | 30448.2673 | 2028.9521 | 240886.3016 | 16051.7103 | 117501.7226 | 117501.7226 | 1249015.2882 | 117501.7226
| WMN013-24614054 | 83 | WMN013 | WMN | North | 1956005.0739 | 0.032336 | 0.032355 | 0.032171 | 0.031885 | 0.031336 | 0.030922 | 0.030935 | 0.031074 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 0.030604 | 1.8633 | 1.8774 | 1.8915 | 1.9056 | 1.9196 | 1.9161 | 1.9127 | 1.9092 | 1.9057 | 1.9022 | 1.8987 | 1.8952 | 1.8918 | 1.8883 | 1.8848 | 1.8813 | 1.8778 | 1.8743 | 1.8708 | 1.8674 | 1.6774 | 1.6911 | 1.6941 | 1.6915 | 1.6747 | 1.6495 | 1.6473 | 1.6516 | 1.6237 | 1.6207 | 1.6177 | 1.6148 | 1.6118 | 1.6088 | 1.6058 | 1.6029 | 1.5999 | 1.5969 | 1.594 | 1.591 | 30448.2673 | 2028.9521 | 721954.654 | 48108.2023 | 754000.098 | 754000.098 | 1956005.0739 | 754000.098
| WMN014-122227235 | 183 | WMN014 | WMN | North | 4312637.6931 | 0.024742 | 0.025368 | 0.025684 | 0.025918 | 0.025761 | 0.025726 | 0.026076 | 0.026687 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 1.3716 | 1.3735 | 1.3754 | 1.3774 | 1.3793 | 1.3766 | 1.3738 | 1.371 | 1.3683 | 1.3655 | 1.3627 | 1.36 | 1.3572 | 1.3545 | 1.3517 | 1.3489 | 1.3462 | 1.3434 | 1.3406 | 1.3379 | 0.94476 | 0.97004 | 0.98351 | 0.99388 | 0.98922 | 0.98593 | 0.99733 | 1.0186 | 1.0138 | 1.0117 | 1.0097 | 1.0076 | 1.0056 | 1.0035 | 1.0015 | 0.99943 | 0.99738 | 0.99534 | 0.99329 | 0.99124 | 30448.2673 | 2028.9521 | 437602.2133 | 29160.0805 | 506337.4622 | 506337.4622 | 4312637.6931 | 506337.4622
| WMN014-164366245 | 35 | WMN014 | WMN | North | 824821.4167 | 0.024742 | 0.025368 | 0.025684 | 0.025918 | 0.025761 | 0.025726 | 0.026076 | 0.026687 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30448.2673 | 2028.9521 | 0 | 0 | 0 | 0 | 824821.4167 | 0
| WMN014-42253278 | 33 | WMN014 | WMN | North | 777688.7643 | 0.024742 | 0.025368 | 0.025684 | 0.025918 | 0.025761 | 0.025726 | 0.026076 | 0.026687 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.012478 | 0.012597 | 0.012715 | 0.012834 | 0.012952 | 0.012954 | 0.012955 | 0.012957 | 0.012958 | 0.012959 | 0.012961 | 0.012962 | 0.012964 | 0.012965 | 0.012967 | 0.012968 | 0.012969 | 0.012971 | 0.012972 | 0.012974 | 0.0085951 | 0.0088964 | 0.009092 | 0.0092605 | 0.0092891 | 0.0092778 | 0.009405 | 0.0096263 | 0.0096008 | 0.0096018 | 0.0096029 | 0.0096039 | 0.009605 | 0.009606 | 0.0096071 | 0.0096081 | 0.0096092 | 0.0096102 | 0.0096113 | 0.0096124 | 30448.2673 | 2028.9521 | 4133.6648 | 275.4511 | 14484.8027 | 14484.8027 | 777688.7643 | 14484.8027
| WMN014-62615661 | 35 | WMN014 | WMN | North | 824821.4167 | 0.024742 | 0.025368 | 0.025684 | 0.025918 | 0.025761 | 0.025726 | 0.026076 | 0.026687 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.026613 | 0.9741 | 0.98168 | 0.98927 | 0.99685 | 1.0044 | 1.0033 | 1.0022 | 1.0012 | 1.0001 | 0.99896 | 0.99786 | 0.99677 | 0.99567 | 0.99458 | 0.99348 | 0.99238 | 0.99129 | 0.99019 | 0.9891 | 0.988 | 0.67098 | 0.69332 | 0.70737 | 0.7193 | 0.72036 | 0.71862 | 0.7276 | 0.74382 | 0.74095 | 0.74014 | 0.73933 | 0.73852 | 0.7377 | 0.73689 | 0.73608 | 0.73527 | 0.73446 | 0.73364 | 0.73283 | 0.73202 | 30448.2673 | 2028.9521 | 318912.7712 | 21251.0855 | 64507.9221 | 64507.9221 | 824821.4167 | 64507.9221
| WMN021-160652994 | 109 | WMN021 | WMN | North | 2568729.5549 | 0.079173 | 0.079872 | 0.079571 | 0.079122 | 0.077949 | 0.076994 | 0.077141 | 0.077782 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.0072323 | 0.0073048 | 0.0073772 | 0.0074497 | 0.0075221 | 0.0075163 | 0.0075104 | 0.0075045 | 0.0074987 | 0.0074928 | 0.0074869 | 0.007481 | 0.0074752 | 0.0074693 | 0.0074634 | 0.0074576 | 0.0074517 | 0.0074458 | 0.00744 | 0.0074341 | 0.015941 | 0.016243 | 0.016342 | 0.01641 | 0.016324 | 0.016111 | 0.016129 | 0.016251 | 0.016081 | 0.016069 | 0.016056 | 0.016044 | 0.016031 | 0.016018 | 0.016006 | 0.015993 | 0.015981 | 0.015968 | 0.015956 | 0.015943 | 30448.2673 | 2028.9521 | 7094.1459 | 472.7258 | 13825.8899 | 13825.8899 | 2568729.5549 | 13825.8899
| WMN021-164365974 | 31 | WMN021 | WMN | North | 730556.1119 | 0.079173 | 0.079872 | 0.079571 | 0.079122 | 0.077949 | 0.076994 | 0.077141 | 0.077782 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.009799 | 0.0098753 | 0.0099516 | 0.010028 | 0.010104 | 0.010102 | 0.010101 | 0.010099 | 0.010097 | 0.010095 | 0.010093 | 0.010091 | 0.01009 | 0.010088 | 0.010086 | 0.010084 | 0.010082 | 0.01008 | 0.010078 | 0.010077 | 0.021599 | 0.021959 | 0.022045 | 0.022089 | 0.021927 | 0.021655 | 0.021692 | 0.021868 | 0.021654 | 0.02165 | 0.021646 | 0.021642 | 0.021638 | 0.021634 | 0.02163 | 0.021626 | 0.021622 | 0.021618 | 0.021614 | 0.02161 | 30448.2673 | 2028.9521 | 9571.474 | 637.8052 | 35368.298 | 35368.298 | 730556.1119 | 35368.298
| WMN021-24614498 | 53 | WMN021 | WMN | North | 1249015.2882 | 0.079173 | 0.079872 | 0.079571 | 0.079122 | 0.077949 | 0.076994 | 0.077141 | 0.077782 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.026867 | 0.027091 | 0.027316 | 0.02754 | 0.027765 | 0.027758 | 0.027752 | 0.027746 | 0.02774 | 0.027734 | 0.027728 | 0.027722 | 0.027716 | 0.02771 | 0.027704 | 0.027698 | 0.027692 | 0.027686 | 0.02768 | 0.027674 | 0.059219 | 0.060241 | 0.060511 | 0.060664 | 0.060252 | 0.0595 | 0.059601 | 0.060083 | 0.059491 | 0.059478 | 0.059465 | 0.059452 | 0.059439 | 0.059426 | 0.059413 | 0.0594 | 0.059387 | 0.059374 | 0.059361 | 0.059348 | 30448.2673 | 2028.9521 | 26286.318 | 1751.6163 | 62274.9249 | 62274.9249 | 1249015.2882 | 62274.9249
| WMN021-24614598 | 73 | WMN021 | WMN | North | 1720341.812 | 0.079173 | 0.079872 | 0.079571 | 0.079122 | 0.077949 | 0.076994 | 0.077141 | 0.077782 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.10129 | 0.10221 | 0.10313 | 0.10405 | 0.10497 | 0.10488 | 0.10479 | 0.1047 | 0.10461 | 0.10452 | 0.10443 | 0.10434 | 0.10425 | 0.10416 | 0.10407 | 0.10398 | 0.10389 | 0.1038 | 0.10371 | 0.10362 | 0.22327 | 0.22728 | 0.22846 | 0.22919 | 0.22779 | 0.2248 | 0.22504 | 0.22672 | 0.22434 | 0.22414 | 0.22395 | 0.22376 | 0.22356 | 0.22337 | 0.22318 | 0.22298 | 0.22279 | 0.2226 | 0.2224 | 0.22221 | 30448.2673 | 2028.9521 | 99015.5174 | 6598.0024 | 55735.143 | 55735.143 | 1720341.812 | 55735.143
| WMN021-65221877 | 10 | WMN021 | WMN | North | 235663.2619 | 0.079173 | 0.079872 | 0.079571 | 0.079122 | 0.077949 | 0.076994 | 0.077141 | 0.077782 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.077032 | 0.29411 | 0.29638 | 0.29865 | 0.30091 | 0.30318 | 0.30253 | 0.30188 | 0.30123 | 0.30058 | 0.29993 | 0.29927 | 0.29862 | 0.29797 | 0.29732 | 0.29667 | 0.29602 | 0.29537 | 0.29472 | 0.29407 | 0.29342 | 0.64828 | 0.65904 | 0.66157 | 0.66283 | 0.65792 | 0.64847 | 0.64831 | 0.65229 | 0.64461 | 0.64321 | 0.64182 | 0.64042 | 0.63903 | 0.63763 | 0.63624 | 0.63484 | 0.63344 | 0.63205 | 0.63065 | 0.62926 | 30448.2673 | 2028.9521 | 284383.1075 | 18950.1653 | 13197.2843 | 13197.2843 | 235663.2619 | 13197.2843
| WND011-15425526 | 0 | WND011 | WND | South | 0 | 0.0015478 | 0.0015666 | 0.0016041 | 0.0016285 | 0.0016604 | 0.0016792 | 0.0017223 | 0.0017598 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32906.3857 | 7805.0738 | 0 | 0 | 0 | 0 | 0 | 0
| WND011-200942344 | 142 | WND011 | WND | South | 2581672.3407 | 0.0015478 | 0.0015666 | 0.0016041 | 0.0016285 | 0.0016604 | 0.0016792 | 0.0017223 | 0.0017598 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 7.506 | 7.574 | 7.6419 | 7.7099 | 7.7779 | 7.8126 | 7.8474 | 7.8821 | 7.9169 | 7.9516 | 7.9864 | 8.0211 | 8.0559 | 8.0906 | 8.1254 | 8.1601 | 8.1949 | 8.2296 | 8.2644 | 8.2991 | 0.32345 | 0.33033 | 0.34128 | 0.34955 | 0.35954 | 0.36523 | 0.37628 | 0.38618 | 0.39202 | 0.39374 | 0.39546 | 0.39718 | 0.3989 | 0.40062 | 0.40234 | 0.40406 | 0.40578 | 0.4075 | 0.40922 | 0.41094 | 32906.3857 | 7805.0738 | 179546.7424 | 42586.7364 | 1144996.8109 | 1484169.0958 | 2694207.3407 | 1194907.1787
| WND011-74053613 | 29 | WND011 | WND | South | 527242.9428 | 0.0015478 | 0.0015666 | 0.0016041 | 0.0016285 | 0.0016604 | 0.0016792 | 0.0017223 | 0.0017598 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.09133 | 0.092199 | 0.093068 | 0.093937 | 0.094806 | 0.095546 | 0.096285 | 0.097025 | 0.097764 | 0.098504 | 0.099243 | 0.099983 | 0.10072 | 0.10146 | 0.1022 | 0.10294 | 0.10368 | 0.10442 | 0.10516 | 0.1059 | 0.0039356 | 0.0040212 | 0.0041563 | 0.0042589 | 0.0043825 | 0.0044666 | 0.0046168 | 0.0047537 | 0.0048409 | 0.0048776 | 0.0049142 | 0.0049508 | 0.0049874 | 0.005024 | 0.0050606 | 0.0050972 | 0.0051339 | 0.0051705 | 0.0052071 | 0.0052437 | 32906.3857 | 7805.0738 | 2225.2951 | 527.8183 | 25748.3802 | 33375.5953 | 550225.4428 | 26870.7511
| WND011-79727477 | 2 | WND011 | WND | South | 36361.5823 | 0.0015478 | 0.0015666 | 0.0016041 | 0.0016285 | 0.0016604 | 0.0016792 | 0.0017223 | 0.0017598 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0.0017786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32906.3857 | 7805.0738 | 0 | 0 | 0 | 0 | 37946.5823 | 0
| WND012-171309560 | 52 | WND012 | WND | South | 945401.1388 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.018465 | 0.018647 | 0.018829 | 0.019011 | 0.019193 | 0.01934 | 0.019487 | 0.019634 | 0.019781 | 0.019928 | 0.020075 | 0.020222 | 0.020369 | 0.020516 | 0.020663 | 0.02081 | 0.020957 | 0.021105 | 0.021252 | 0.021399 | 0.00028936 | 0.00029556 | 0.00030286 | 0.00030897 | 0.0003144 | 0.0003233 | 0.00033586 | 0.00034552 | 0.00035143 | 0.00035404 | 0.00035665 | 0.00035926 | 0.00036187 | 0.00036449 | 0.0003671 | 0.00036971 | 0.00037232 | 0.00037494 | 0.00037755 | 0.00038016 | 32906.3857 | 7805.0738 | 161.6457 | 38.3408 | 38688.3921 | 50148.7125 | 986611.1388 | 40374.8176
| WND012-200942480 | 127 | WND012 | WND | South | 2308960.4737 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 79.173 | 79.9014 | 80.6299 | 81.3583 | 82.0868 | 82.5062 | 82.9255 | 83.3449 | 83.7643 | 84.1837 | 84.603 | 85.0224 | 85.4418 | 85.8611 | 86.2805 | 86.6999 | 87.1193 | 87.5386 | 87.958 | 88.3774 | 1.2407 | 1.2665 | 1.2969 | 1.3223 | 1.3447 | 1.3792 | 1.4292 | 1.4667 | 1.4881 | 1.4956 | 1.503 | 1.5105 | 1.5179 | 1.5254 | 1.5328 | 1.5403 | 1.5477 | 1.5552 | 1.5626 | 1.5701 | 32906.3857 | 7805.0738 | 682713.551 | 161932.9966 | 849744.6563 | 1101457.0051 | 2409607.9737 | 886784.9938
| WND012-24611463 | 367 | WND012 | WND | South | 6672350.3452 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 9.2844 | 9.3568 | 9.4291 | 9.5015 | 9.5739 | 9.5933 | 9.6128 | 9.6323 | 9.6518 | 9.6713 | 9.6908 | 9.7102 | 9.7297 | 9.7492 | 9.7687 | 9.7882 | 9.8076 | 9.8271 | 9.8466 | 9.8661 | 0.1455 | 0.14831 | 0.15166 | 0.15442 | 0.15683 | 0.16037 | 0.16568 | 0.16951 | 0.17147 | 0.17182 | 0.17216 | 0.17251 | 0.17285 | 0.1732 | 0.17355 | 0.17389 | 0.17424 | 0.17459 | 0.17493 | 0.17528 | 32906.3857 | 7805.0738 | 78440.6892 | 18605.3665 | 1458198.2808 | 1890147.4687 | 6963197.8452 | 1521761.0888
| WND012-72499182 | 40 | WND012 | WND | South | 727231.6453 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.066794 | 0.067405 | 0.068016 | 0.068627 | 0.069238 | 0.069369 | 0.0695 | 0.06963 | 0.069761 | 0.069892 | 0.070023 | 0.070154 | 0.070285 | 0.070415 | 0.070546 | 0.070677 | 0.070808 | 0.070939 | 0.07107 | 0.071201 | 0.0010467 | 0.0010684 | 0.001094 | 0.0011153 | 0.0011342 | 0.0011596 | 0.0011978 | 0.0012254 | 0.0012394 | 0.0012417 | 0.001244 | 0.0012463 | 0.0012487 | 0.001251 | 0.0012533 | 0.0012556 | 0.001258 | 0.0012603 | 0.0012626 | 0.0012649 | 32906.3857 | 7805.0738 | 566.4202 | 134.3494 | 17822.5888 | 23102.0168 | 758931.6453 | 18599.4748
| WND012-72499328 | 48 | WND012 | WND | South | 872677.9743 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.34716 | 0.35016 | 0.35317 | 0.35617 | 0.35917 | 0.36171 | 0.36425 | 0.36678 | 0.36932 | 0.37186 | 0.3744 | 0.37694 | 0.37947 | 0.38201 | 0.38455 | 0.38709 | 0.38963 | 0.39216 | 0.3947 | 0.39724 | 0.0054404 | 0.0055503 | 0.0056805 | 0.0057886 | 0.0058836 | 0.0060465 | 0.0062779 | 0.0064546 | 0.0065612 | 0.0066063 | 0.0066514 | 0.0066965 | 0.0067416 | 0.0067867 | 0.0068318 | 0.0068769 | 0.006922 | 0.0069671 | 0.0070121 | 0.0070572 | 32906.3857 | 7805.0738 | 3017.9222 | 715.8217 | 77799.3418 | 100845.1532 | 910717.9743 | 81190.6122
| WND012-73767156 | 96 | WND012 | WND | South | 1745355.9486 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.18294 | 0.18459 | 0.18625 | 0.18791 | 0.18956 | 0.18987 | 0.19017 | 0.19048 | 0.19078 | 0.19108 | 0.19139 | 0.19169 | 0.192 | 0.1923 | 0.19261 | 0.19291 | 0.19321 | 0.19352 | 0.19382 | 0.19413 | 0.0028668 | 0.0029259 | 0.0029958 | 0.0030539 | 0.0031053 | 0.0031739 | 0.0032777 | 0.003352 | 0.0033893 | 0.0033947 | 0.0034001 | 0.0034055 | 0.0034109 | 0.0034164 | 0.0034218 | 0.0034272 | 0.0034326 | 0.003438 | 0.0034434 | 0.0034488 | 32906.3857 | 7805.0738 | 1548.5656 | 367.3047 | 97855.3061 | 126842.1185 | 1821435.9486 | 102120.8152
| WND012-74645078 | 88 | WND012 | WND | South | 1599909.6196 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.89266 | 0.90166 | 0.91066 | 0.91965 | 0.92865 | 0.9333 | 0.93795 | 0.94261 | 0.94726 | 0.95191 | 0.95656 | 0.96122 | 0.96587 | 0.97052 | 0.97517 | 0.97983 | 0.98448 | 0.98913 | 0.99378 | 0.99844 | 0.013989 | 0.014292 | 0.014648 | 0.014947 | 0.015212 | 0.015602 | 0.016166 | 0.016588 | 0.016829 | 0.016911 | 0.016994 | 0.017077 | 0.017159 | 0.017242 | 0.017325 | 0.017407 | 0.01749 | 0.017573 | 0.017655 | 0.017738 | 32906.3857 | 7805.0738 | 7715.9073 | 1830.138 | 321856.6505 | 417197.4012 | 1669649.6196 | 335886.3697
| WND012-74645220 | 23 | WND012 | WND | South | 418158.196 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.0439 | 0.044305 | 0.04471 | 0.045115 | 0.045521 | 0.04587 | 0.046219 | 0.046567 | 0.046916 | 0.047265 | 0.047614 | 0.047963 | 0.048312 | 0.048661 | 0.04901 | 0.049358 | 0.049707 | 0.050056 | 0.050405 | 0.050754 | 0.00068796 | 0.00070226 | 0.00071915 | 0.00073323 | 0.00074568 | 0.00076678 | 0.00079659 | 0.00081949 | 0.0008335 | 0.0008397 | 0.00084589 | 0.00085209 | 0.00085829 | 0.00086449 | 0.00087069 | 0.00087688 | 0.00088308 | 0.00088928 | 0.00089548 | 0.00090168 | 32906.3857 | 7805.0738 | 383.5183 | 90.9668 | 15789.3587 | 20466.5009 | 436385.696 | 16477.6163
| WND012-77737071 | 8 | WND012 | WND | South | 145446.3291 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.010129 | 0.010234 | 0.010339 | 0.010443 | 0.010548 | 0.010603 | 0.010658 | 0.010712 | 0.010767 | 0.010822 | 0.010877 | 0.010932 | 0.010987 | 0.011042 | 0.011097 | 0.011152 | 0.011206 | 0.011261 | 0.011316 | 0.011371 | 0.00015874 | 0.00016222 | 0.00016629 | 0.00016973 | 0.00017278 | 0.00017724 | 0.00018369 | 0.00018852 | 0.00019129 | 0.00019226 | 0.00019324 | 0.00019421 | 0.00019519 | 0.00019616 | 0.00019714 | 0.00019811 | 0.00019909 | 0.00020006 | 0.00020104 | 0.00020201 | 32906.3857 | 7805.0738 | 87.7135 | 20.8048 | 2513.0236 | 3257.4344 | 151786.3291 | 2622.5662
| WND012-78928850 | 14 | WND012 | WND | South | 254531.0758 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.0011911 | 0.0012025 | 0.001214 | 0.0012254 | 0.0012369 | 0.001241 | 0.0012452 | 0.0012493 | 0.0012534 | 0.0012576 | 0.0012617 | 0.0012658 | 0.0012699 | 0.0012741 | 0.0012782 | 0.0012823 | 0.0012865 | 0.0012906 | 0.0012947 | 0.0012989 | 1.8666e-05 | 1.9061e-05 | 1.9527e-05 | 1.9916e-05 | 2.0262e-05 | 2.0746e-05 | 2.1461e-05 | 2.1985e-05 | 2.2268e-05 | 2.2341e-05 | 2.2415e-05 | 2.2488e-05 | 2.2561e-05 | 2.2635e-05 | 2.2708e-05 | 2.2782e-05 | 2.2855e-05 | 2.2928e-05 | 2.3002e-05 | 2.3075e-05 | 32906.3857 | 7805.0738 | 10.1921 | 2.4175 | 575.0955 | 745.4509 | 265626.0758 | 600.1639
| WND012-85319302 | 45 | WND012 | WND | South | 818135.6009 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.095769 | 0.096802 | 0.097835 | 0.098867 | 0.0999 | 0.10038 | 0.10085 | 0.10133 | 0.1018 | 0.10228 | 0.10275 | 0.10323 | 0.1037 | 0.10418 | 0.10466 | 0.10513 | 0.10561 | 0.10608 | 0.10656 | 0.10703 | 0.0015008 | 0.0015344 | 0.0015736 | 0.0016068 | 0.0016365 | 0.0016779 | 0.0017382 | 0.0017831 | 0.0018086 | 0.001817 | 0.0018255 | 0.0018339 | 0.0018424 | 0.0018508 | 0.0018593 | 0.0018677 | 0.0018762 | 0.0018846 | 0.0018931 | 0.0019015 | 32906.3857 | 7805.0738 | 828.6659 | 196.5515 | 40066.1309 | 51934.5668 | 853798.1009 | 41812.6121
| WND012-88220025 | 45 | WND012 | WND | South | 818135.6009 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.33223 | 0.3351 | 0.33797 | 0.34084 | 0.34371 | 0.34519 | 0.34667 | 0.34815 | 0.34963 | 0.35111 | 0.35259 | 0.35407 | 0.35555 | 0.35703 | 0.35851 | 0.35999 | 0.36147 | 0.36295 | 0.36443 | 0.36591 | 0.0052064 | 0.0053115 | 0.0054361 | 0.0055395 | 0.0056304 | 0.0057704 | 0.005975 | 0.0061268 | 0.0062115 | 0.0062377 | 0.006264 | 0.0062903 | 0.0063166 | 0.0063429 | 0.0063692 | 0.0063955 | 0.0064218 | 0.0064481 | 0.0064744 | 0.0065007 | 32906.3857 | 7805.0738 | 2847.8387 | 675.4796 | 105936.4929 | 137317.1238 | 853798.1009 | 110554.2606
| WND012-93532503 | 150 | WND012 | WND | South | 2727118.6697 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 7.0576 | 7.132 | 7.2063 | 7.2806 | 7.355 | 7.3888 | 7.4227 | 7.4566 | 7.4904 | 7.5243 | 7.5582 | 7.5921 | 7.6259 | 7.6598 | 7.6937 | 7.7275 | 7.7614 | 7.7953 | 7.8291 | 7.863 | 0.1106 | 0.11305 | 0.11591 | 0.11833 | 0.12048 | 0.12352 | 0.12793 | 0.13122 | 0.13307 | 0.13367 | 0.13428 | 0.13488 | 0.13548 | 0.13608 | 0.13668 | 0.13728 | 0.13789 | 0.13849 | 0.13909 | 0.13969 | 32906.3857 | 7805.0738 | 60969.0029 | 14461.2529 | 237645.3157 | 308040.8871 | 2845993.6697 | 248004.2661
| WND012-93532641 | 60 | WND012 | WND | South | 1090847.4679 | 0.0005629 | 0.00056935 | 0.00057775 | 0.00058378 | 0.0005884 | 0.00060045 | 0.00061908 | 0.00063211 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 0.00063813 | 4.7741 | 4.8244 | 4.8746 | 4.9248 | 4.9751 | 4.9904 | 5.0056 | 5.0209 | 5.0361 | 5.0514 | 5.0667 | 5.0819 | 5.0972 | 5.1124 | 5.1277 | 5.143 | 5.1582 | 5.1735 | 5.1887 | 5.204 | 0.074816 | 0.076469 | 0.078406 | 0.08004 | 0.081497 | 0.083421 | 0.086273 | 0.088357 | 0.08947 | 0.089741 | 0.090012 | 0.090284 | 0.090555 | 0.090826 | 0.091097 | 0.091368 | 0.091639 | 0.09191 | 0.092181 | 0.092452 | 32906.3857 | 7805.0738 | 40917.0223 | 9705.1187 | 60047.5891 | 77834.9557 | 1138397.4679 | 62665.0613
| WND013-139460835 | 521 | WND013 | WND | South | 9472192.1795 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 12.2943 | 12.3994 | 12.5045 | 12.6095 | 12.7146 | 12.7766 | 12.8386 | 12.9006 | 12.9626 | 13.0246 | 13.0866 | 13.1486 | 13.2106 | 13.2726 | 13.3346 | 13.3966 | 13.4586 | 13.5206 | 13.5826 | 13.6446 | 0.4351 | 0.4589 | 0.48607 | 0.51119 | 0.53486 | 0.56331 | 0.59557 | 0.62497 | 0.64859 | 0.65169 | 0.65479 | 0.65789 | 0.66099 | 0.6641 | 0.6672 | 0.6703 | 0.6734 | 0.67651 | 0.67961 | 0.68271 | 32906.3857 | 7805.0738 | 283200.552 | 67172.4092 | 2168465.7254 | 2810811.1606 | 9885084.6795 | 2262989.0646
| WND013-163356845 | 11 | WND013 | WND | South | 199988.7024 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0053192 | 0.005379 | 0.0054387 | 0.0054985 | 0.0055582 | 0.0055959 | 0.0056337 | 0.0056714 | 0.0057091 | 0.0057469 | 0.0057846 | 0.0058223 | 0.0058601 | 0.0058978 | 0.0059355 | 0.0059733 | 0.006011 | 0.0060487 | 0.0060865 | 0.0061242 | 0.00018825 | 0.00019907 | 0.00021141 | 0.00022291 | 0.00023381 | 0.00024672 | 0.00026134 | 0.00027475 | 0.00028566 | 0.00028755 | 0.00028943 | 0.00029132 | 0.00029321 | 0.0002951 | 0.00029699 | 0.00029887 | 0.00030076 | 0.00030265 | 0.00030454 | 0.00030643 | 32906.3857 | 7805.0738 | 124.9073 | 29.6268 | 5502.2371 | 7132.1162 | 208706.2024 | 5742.0794
| WND013-172348741 | 10 | WND013 | WND | South | 181807.9113 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.011762 | 0.011881 | 0.012 | 0.012119 | 0.012238 | 0.012332 | 0.012426 | 0.012519 | 0.012613 | 0.012706 | 0.0128 | 0.012894 | 0.012987 | 0.013081 | 0.013174 | 0.013268 | 0.013362 | 0.013455 | 0.013549 | 0.013643 | 0.00041626 | 0.00043971 | 0.00046646 | 0.00049131 | 0.00051482 | 0.0005437 | 0.0005764 | 0.00060649 | 0.00063108 | 0.00063577 | 0.00064045 | 0.00064513 | 0.00064982 | 0.0006545 | 0.00065919 | 0.00066387 | 0.00066855 | 0.00067324 | 0.00067792 | 0.00068261 | 32906.3857 | 7805.0738 | 276.4247 | 65.5653 | 4743.0921 | 6148.0963 | 189732.9113 | 4949.8433
| WND013-200942552 | 296 | WND013 | WND | South | 5381514.1749 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 32.3802 | 32.6228 | 32.8654 | 33.108 | 33.3506 | 33.493 | 33.6353 | 33.7777 | 33.9201 | 34.0624 | 34.2048 | 34.3472 | 34.4895 | 34.6319 | 34.7743 | 34.9166 | 35.059 | 35.2014 | 35.3437 | 35.4861 | 1.146 | 1.2074 | 1.2775 | 1.3422 | 1.4029 | 1.4767 | 1.5603 | 1.6364 | 1.6972 | 1.7043 | 1.7114 | 1.7186 | 1.7257 | 1.7328 | 1.7399 | 1.7471 | 1.7542 | 1.7613 | 1.7684 | 1.7756 | 32906.3857 | 7805.0738 | 740808.7053 | 175712.6007 | 1274279.1241 | 1651747.5659 | 5616094.1749 | 1329824.9031
| WND013-76546155 | 117 | WND013 | WND | South | 2127152.5624 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.28694 | 0.28952 | 0.2921 | 0.29468 | 0.29726 | 0.29883 | 0.3004 | 0.30197 | 0.30353 | 0.3051 | 0.30667 | 0.30824 | 0.30981 | 0.31138 | 0.31295 | 0.31452 | 0.31608 | 0.31765 | 0.31922 | 0.32079 | 0.010155 | 0.010715 | 0.011355 | 0.011946 | 0.012505 | 0.013175 | 0.013935 | 0.014629 | 0.015187 | 0.015266 | 0.015344 | 0.015423 | 0.015501 | 0.01558 | 0.015658 | 0.015737 | 0.015815 | 0.015894 | 0.015972 | 0.016051 | 32906.3857 | 7805.0738 | 6633.8396 | 1573.4821 | 139296.2857 | 180558.7932 | 2219875.0624 | 145368.2055
| WND013-76546231 | 126 | WND013 | WND | South | 2290779.6826 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.52772 | 0.53225 | 0.53678 | 0.54131 | 0.54584 | 0.55036 | 0.55488 | 0.5594 | 0.56392 | 0.56844 | 0.57296 | 0.57748 | 0.582 | 0.58652 | 0.59104 | 0.59557 | 0.60009 | 0.60461 | 0.60913 | 0.61365 | 0.018677 | 0.019699 | 0.020866 | 0.021944 | 0.022961 | 0.024265 | 0.02574 | 0.0271 | 0.028216 | 0.028442 | 0.028668 | 0.028894 | 0.029121 | 0.029347 | 0.029573 | 0.029799 | 0.030025 | 0.030252 | 0.030478 | 0.030704 | 32906.3857 | 7805.0738 | 12378.9704 | 2936.1711 | 253146.6418 | 328134.0339 | 2390634.6826 | 264181.2943
| WND013-76546307 | 21 | WND013 | WND | South | 381796.6138 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.082613 | 0.083349 | 0.084085 | 0.084821 | 0.085557 | 0.086164 | 0.086771 | 0.087378 | 0.087986 | 0.088593 | 0.0892 | 0.089807 | 0.090414 | 0.091021 | 0.091629 | 0.092236 | 0.092843 | 0.09345 | 0.094057 | 0.094664 | 0.0029237 | 0.0030847 | 0.0032685 | 0.0034386 | 0.0035991 | 0.0037989 | 0.0040252 | 0.0042331 | 0.0044024 | 0.0044328 | 0.0044631 | 0.0044935 | 0.0045239 | 0.0045543 | 0.0045846 | 0.004615 | 0.0046454 | 0.0046758 | 0.0047062 | 0.0047365 | 32906.3857 | 7805.0738 | 1927.9493 | 457.2908 | 28615.9066 | 37092.5437 | 398439.1138 | 29863.2729
| WND013-76546404 | 95 | WND013 | WND | South | 1727175.1575 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.781 | 0.78801 | 0.79502 | 0.80203 | 0.80904 | 0.81501 | 0.82097 | 0.82694 | 0.8329 | 0.83887 | 0.84483 | 0.8508 | 0.85677 | 0.86273 | 0.8687 | 0.87466 | 0.88063 | 0.88659 | 0.89256 | 0.89852 | 0.02764 | 0.029164 | 0.030904 | 0.032514 | 0.034033 | 0.035933 | 0.038084 | 0.040061 | 0.041674 | 0.041973 | 0.042271 | 0.04257 | 0.042868 | 0.043167 | 0.043465 | 0.043764 | 0.044062 | 0.044361 | 0.044659 | 0.044958 | 32906.3857 | 7805.0738 | 18257.1294 | 4330.4131 | 274177.3382 | 355394.4677 | 1802462.6575 | 286128.718
| WND013-76546454 | 11 | WND013 | WND | South | 199988.7024 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.069963 | 0.070652 | 0.071342 | 0.072032 | 0.072721 | 0.073342 | 0.073962 | 0.074583 | 0.075203 | 0.075824 | 0.076444 | 0.077064 | 0.077685 | 0.078305 | 0.078926 | 0.079546 | 0.080166 | 0.080787 | 0.081407 | 0.082028 | 0.002476 | 0.0026148 | 0.0027732 | 0.0029201 | 0.0030591 | 0.0032336 | 0.003431 | 0.0036132 | 0.0037628 | 0.0037938 | 0.0038249 | 0.0038559 | 0.003887 | 0.003918 | 0.0039491 | 0.0039801 | 0.0040111 | 0.0040422 | 0.0040732 | 0.0041043 | 32906.3857 | 7805.0738 | 1650.3989 | 391.4585 | 16767.9368 | 21734.9545 | 208706.2024 | 17498.8505
| WND013-76546631 | 38 | WND013 | WND | South | 690870.063 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.031404 | 0.031685 | 0.031966 | 0.032246 | 0.032527 | 0.032791 | 0.033054 | 0.033318 | 0.033582 | 0.033845 | 0.034109 | 0.034372 | 0.034636 | 0.034899 | 0.035163 | 0.035426 | 0.03569 | 0.035953 | 0.036217 | 0.036481 | 0.0011114 | 0.0011726 | 0.0012426 | 0.0013073 | 0.0013683 | 0.0014457 | 0.0015334 | 0.0016141 | 0.0016803 | 0.0016934 | 0.0017066 | 0.0017198 | 0.001733 | 0.0017462 | 0.0017594 | 0.0017726 | 0.0017858 | 0.0017989 | 0.0018121 | 0.0018253 | 32906.3857 | 7805.0738 | 736.8591 | 174.7758 | 16815.1287 | 21796.1257 | 720985.063 | 17548.0996
| WND013-76546854 | 40 | WND013 | WND | South | 727231.6453 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.18477 | 0.18664 | 0.18852 | 0.19039 | 0.19226 | 0.19341 | 0.19457 | 0.19572 | 0.19688 | 0.19803 | 0.19919 | 0.20034 | 0.2015 | 0.20265 | 0.20381 | 0.20496 | 0.20612 | 0.20727 | 0.20843 | 0.20958 | 0.0065392 | 0.0069077 | 0.007328 | 0.0077182 | 0.0080876 | 0.0085274 | 0.0090258 | 0.0094819 | 0.0098509 | 0.0099086 | 0.0099664 | 0.010024 | 0.010082 | 0.01014 | 0.010198 | 0.010255 | 0.010313 | 0.010371 | 0.010429 | 0.010487 | 32906.3857 | 7805.0738 | 4304.9236 | 1021.0859 | 82786.6143 | 107309.7613 | 758931.6453 | 86395.2797
| WND013-78928894 | 54 | WND013 | WND | South | 981762.7211 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.020257 | 0.020482 | 0.020707 | 0.020932 | 0.021158 | 0.021345 | 0.021533 | 0.02172 | 0.021908 | 0.022096 | 0.022283 | 0.022471 | 0.022658 | 0.022846 | 0.023034 | 0.023221 | 0.023409 | 0.023596 | 0.023784 | 0.023972 | 0.0007169 | 0.00075803 | 0.00080493 | 0.00084859 | 0.00089002 | 0.00094109 | 0.00099888 | 0.0010523 | 0.0010962 | 0.0011056 | 0.0011149 | 0.0011243 | 0.0011337 | 0.0011431 | 0.0011525 | 0.0011619 | 0.0011713 | 0.0011807 | 0.00119 | 0.0011994 | 32906.3857 | 7805.0738 | 480.7288 | 114.0242 | 7419.3359 | 9617.1002 | 1024557.7211 | 7742.7445
| WND013-78928958 | 272 | WND013 | WND | South | 4945175.1878 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.41166 | 0.41531 | 0.41896 | 0.42261 | 0.42627 | 0.42954 | 0.43282 | 0.4361 | 0.43938 | 0.44266 | 0.44594 | 0.44922 | 0.4525 | 0.45577 | 0.45905 | 0.46233 | 0.46561 | 0.46889 | 0.47217 | 0.47545 | 0.014569 | 0.01537 | 0.016286 | 0.017133 | 0.017931 | 0.018938 | 0.020078 | 0.021127 | 0.021984 | 0.022149 | 0.022313 | 0.022477 | 0.022641 | 0.022805 | 0.022969 | 0.023133 | 0.023297 | 0.023461 | 0.023625 | 0.023789 | 32906.3857 | 7805.0738 | 9635.9057 | 2285.5429 | 1311862.3333 | 1700463.717 | 5160735.1878 | 1369046.3629
| WND013-78929121 | 38 | WND013 | WND | South | 690870.063 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.10831 | 0.1094 | 0.11049 | 0.11158 | 0.11267 | 0.11328 | 0.1139 | 0.11451 | 0.11513 | 0.11574 | 0.11635 | 0.11697 | 0.11758 | 0.11819 | 0.11881 | 0.11942 | 0.12003 | 0.12065 | 0.12126 | 0.12187 | 0.0038332 | 0.0040489 | 0.004295 | 0.0045235 | 0.0047397 | 0.0049946 | 0.0052836 | 0.0055475 | 0.0057603 | 0.005791 | 0.0058217 | 0.0058524 | 0.0058831 | 0.0059138 | 0.0059445 | 0.0059752 | 0.0060059 | 0.0060366 | 0.0060673 | 0.0060979 | 32906.3857 | 7805.0738 | 2515.385 | 596.6248 | 39624.9835 | 51362.7421 | 720985.063 | 41352.235
| WND013-78929255 | 79 | WND013 | WND | South | 1436282.4994 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.039875 | 0.040263 | 0.040651 | 0.04104 | 0.041428 | 0.041612 | 0.041796 | 0.04198 | 0.042164 | 0.042348 | 0.042532 | 0.042716 | 0.0429 | 0.043084 | 0.043268 | 0.043452 | 0.043636 | 0.04382 | 0.044004 | 0.044188 | 0.0014112 | 0.0014901 | 0.0015802 | 0.0016637 | 0.0017427 | 0.0018346 | 0.0019389 | 0.0020337 | 0.0021097 | 0.0021189 | 0.0021281 | 0.0021373 | 0.0021465 | 0.0021557 | 0.0021649 | 0.0021741 | 0.0021833 | 0.0021925 | 0.0022017 | 0.002211 | 32906.3857 | 7805.0738 | 920.0746 | 218.2327 | 36426.4009 | 47216.6717 | 1498889.9994 | 38014.2264
| WND013-78929377 | 72 | WND013 | WND | South | 1309016.9615 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.11628 | 0.11758 | 0.11887 | 0.12016 | 0.12145 | 0.12211 | 0.12276 | 0.12342 | 0.12407 | 0.12473 | 0.12538 | 0.12604 | 0.12669 | 0.12735 | 0.128 | 0.12866 | 0.12931 | 0.12997 | 0.13062 | 0.13128 | 0.0041154 | 0.0043515 | 0.0046207 | 0.0048713 | 0.0051091 | 0.0053837 | 0.0056949 | 0.0059791 | 0.0062081 | 0.0062408 | 0.0062736 | 0.0063064 | 0.0063391 | 0.0063719 | 0.0064047 | 0.0064375 | 0.0064702 | 0.006503 | 0.0065358 | 0.0065685 | 32906.3857 | 7805.0738 | 2709.3499 | 642.6314 | 55832.1212 | 72370.777 | 1366076.9615 | 58265.8412
| WND013-85319062 | 11 | WND013 | WND | South | 199988.7024 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0051103 | 0.005164 | 0.0052176 | 0.0052713 | 0.0053249 | 0.0053539 | 0.0053829 | 0.0054118 | 0.0054408 | 0.0054697 | 0.0054987 | 0.0055277 | 0.0055566 | 0.0055856 | 0.0056145 | 0.0056435 | 0.0056725 | 0.0057014 | 0.0057304 | 0.0057593 | 0.00018086 | 0.00019112 | 0.00020282 | 0.0002137 | 0.000224 | 0.00023605 | 0.0002497 | 0.00026218 | 0.00027223 | 0.00027368 | 0.00027513 | 0.00027658 | 0.00027803 | 0.00027948 | 0.00028092 | 0.00028237 | 0.00028382 | 0.00028527 | 0.00028672 | 0.00028817 | 32906.3857 | 7805.0738 | 118.8506 | 28.1902 | 683.3207 | 885.7347 | 208706.2024 | 713.1066
| WND013-85319560 | 13 | WND013 | WND | South | 236350.2847 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.024369 | 0.02461 | 0.024851 | 0.025092 | 0.025333 | 0.025526 | 0.02572 | 0.025913 | 0.026107 | 0.026301 | 0.026494 | 0.026688 | 0.026881 | 0.027075 | 0.027268 | 0.027462 | 0.027656 | 0.027849 | 0.028043 | 0.028236 | 0.00086245 | 0.00091082 | 0.00096601 | 0.0010172 | 0.0010657 | 0.0011254 | 0.0011931 | 0.0012554 | 0.0013063 | 0.001316 | 0.0013256 | 0.0013353 | 0.001345 | 0.0013547 | 0.0013644 | 0.0013741 | 0.0013838 | 0.0013934 | 0.0014031 | 0.0014128 | 32906.3857 | 7805.0738 | 572.2282 | 135.7269 | 8935.2965 | 11582.1204 | 246652.7847 | 9324.7857
| WND013-85319645 | 9 | WND013 | WND | South | 163627.1202 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0028143 | 0.002818 | 0.0028218 | 0.0028255 | 0.0028293 | 0.0028277 | 0.002826 | 0.0028244 | 0.0028228 | 0.0028211 | 0.0028195 | 0.0028179 | 0.0028163 | 0.0028146 | 0.002813 | 0.0028114 | 0.0028097 | 0.0028081 | 0.0028065 | 0.0028049 | 9.96e-05 | 0.00010429 | 0.00010969 | 0.00011455 | 0.00011902 | 0.00012467 | 0.0001311 | 0.00013683 | 0.00014124 | 0.00014116 | 0.00014108 | 0.00014099 | 0.00014091 | 0.00014083 | 0.00014075 | 0.00014067 | 0.00014059 | 0.0001405 | 0.00014042 | 0.00014034 | 32906.3857 | 7805.0738 | 61.4089 | 14.5656 | 1667.1439 | 2160.9872 | 170759.6202 | 1739.8147
| WND013-85319854 | 18 | WND013 | WND | South | 327254.2404 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.013651 | 0.013802 | 0.013953 | 0.014104 | 0.014255 | 0.014319 | 0.014383 | 0.014448 | 0.014512 | 0.014576 | 0.01464 | 0.014704 | 0.014769 | 0.014833 | 0.014897 | 0.014961 | 0.015025 | 0.015089 | 0.015154 | 0.015218 | 0.00048311 | 0.00051081 | 0.00054238 | 0.00057177 | 0.00059966 | 0.00063132 | 0.00066723 | 0.00069992 | 0.0007261 | 0.00072931 | 0.00073252 | 0.00073573 | 0.00073894 | 0.00074216 | 0.00074537 | 0.00074858 | 0.00075179 | 0.000755 | 0.00075821 | 0.00076142 | 32906.3857 | 7805.0738 | 316.4924 | 75.0689 | 5708.9218 | 7400.0253 | 341519.2404 | 5957.7735
| WND013-85833772 | 42 | WND013 | WND | South | 763593.2275 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.26047 | 0.26228 | 0.26409 | 0.2659 | 0.26771 | 0.26915 | 0.27058 | 0.27202 | 0.27346 | 0.2749 | 0.27633 | 0.27777 | 0.27921 | 0.28065 | 0.28208 | 0.28352 | 0.28496 | 0.2864 | 0.28784 | 0.28927 | 0.0092182 | 0.0097069 | 0.010266 | 0.010779 | 0.011262 | 0.011866 | 0.012552 | 0.013178 | 0.013683 | 0.013755 | 0.013826 | 0.013898 | 0.01397 | 0.014042 | 0.014114 | 0.014186 | 0.014258 | 0.01433 | 0.014402 | 0.014474 | 32906.3857 | 7805.0738 | 5983.2464 | 1419.1677 | 67162.0843 | 87056.9149 | 796878.2275 | 70089.677
| WND013-89020589 | 48 | WND013 | WND | South | 872677.9743 | 0.0012712 | 0.0013294 | 0.0013963 | 0.0014562 | 0.001511 | 0.0015837 | 0.0016663 | 0.0017401 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0017972 | 0.0099906 | 0.010102 | 0.010214 | 0.010326 | 0.010438 | 0.010531 | 0.010624 | 0.010717 | 0.010811 | 0.010904 | 0.010997 | 0.011091 | 0.011184 | 0.011277 | 0.011371 | 0.011464 | 0.011557 | 0.011651 | 0.011744 | 0.011837 | 0.00035357 | 0.00037388 | 0.00039704 | 0.0004186 | 0.00043907 | 0.00046429 | 0.00049284 | 0.00051921 | 0.00054092 | 0.00054559 | 0.00055026 | 0.00055493 | 0.0005596 | 0.00056427 | 0.00056894 | 0.00057361 | 0.00057828 | 0.00058295 | 0.00058762 | 0.00059229 | 32906.3857 | 7805.0738 | 237.2396 | 56.2709 | 4881.7399 | 6327.8146 | 910717.9743 | 5094.5348
| WND014-153585710 | 19 | WND014 | WND | South | 345435.0315 | 0.0011769 | 0.0011899 | 0.0012134 | 0.0012314 | 0.0012466 | 0.0012751 | 0.001316 | 0.0013491 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.71934 | 0.72647 | 0.73361 | 0.74074 | 0.74787 | 0.7519 | 0.75593 | 0.75995 | 0.76398 | 0.768 | 0.77203 | 0.77606 | 0.78008 | 0.78411 | 0.78813 | 0.79216 | 0.79619 | 0.80021 | 0.80424 | 0.80826 | 0.02357 | 0.024065 | 0.024782 | 0.025394 | 0.025954 | 0.026692 | 0.027695 | 0.028544 | 0.029031 | 0.029184 | 0.029337 | 0.02949 | 0.029643 | 0.029796 | 0.029949 | 0.030102 | 0.030255 | 0.030408 | 0.030561 | 0.030714 | 32906.3857 | 7805.0738 | 13240.0185 | 3140.4033 | 54470.4416 | 70605.739 | 360492.5315 | 56844.8061
| WND014-15425582 | 0 | WND014 | WND | South | 0 | 0.0011769 | 0.0011899 | 0.0012134 | 0.0012314 | 0.0012466 | 0.0012751 | 0.001316 | 0.0013491 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32906.3857 | 7805.0738 | 0 | 0 | 0 | 0 | 0 | 0
| WND014-200942632 | 474 | WND014 | WND | South | 8617694.9963 | 0.0011769 | 0.0011899 | 0.0012134 | 0.0012314 | 0.0012466 | 0.0012751 | 0.001316 | 0.0013491 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 87.708 | 88.4136 | 89.1191 | 89.8247 | 90.5302 | 90.9173 | 91.3045 | 91.6916 | 92.0787 | 92.4658 | 92.853 | 93.2401 | 93.6272 | 94.0143 | 94.4014 | 94.7886 | 95.1757 | 95.5628 | 95.9499 | 96.337 | 2.8738 | 2.9288 | 3.0106 | 3.0794 | 3.1418 | 3.2276 | 3.3452 | 3.4439 | 3.499 | 3.5137 | 3.5284 | 3.5431 | 3.5579 | 3.5726 | 3.5873 | 3.602 | 3.6167 | 3.6314 | 3.6461 | 3.6608 | 32906.3857 | 7805.0738 | 1595264.1405 | 378381.0975 | 3980881.3943 | 5160102.7034 | 8993339.9963 | 4154407.8642
| WND014-79365293 | 36 | WND014 | WND | South | 654508.4807 | 0.0011769 | 0.0011899 | 0.0012134 | 0.0012314 | 0.0012466 | 0.0012751 | 0.001316 | 0.0013491 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.12572 | 0.12701 | 0.12831 | 0.1296 | 0.13089 | 0.13165 | 0.13241 | 0.13316 | 0.13392 | 0.13467 | 0.13543 | 0.13618 | 0.13694 | 0.1377 | 0.13845 | 0.13921 | 0.13996 | 0.14072 | 0.14148 | 0.14223 | 0.0041193 | 0.0042075 | 0.0043344 | 0.0044431 | 0.0045426 | 0.0046736 | 0.0048511 | 0.0050016 | 0.0050889 | 0.0051176 | 0.0051463 | 0.0051751 | 0.0052038 | 0.0052325 | 0.0052612 | 0.0052899 | 0.0053187 | 0.0053474 | 0.0053761 | 0.0054048 | 32906.3857 | 7805.0738 | 2321.467 | 550.6293 | 48715.3863 | 63145.9146 | 683038.4807 | 50838.8881
| WND014-79365390 | 34 | WND014 | WND | South | 618146.8985 | 0.0011769 | 0.0011899 | 0.0012134 | 0.0012314 | 0.0012466 | 0.0012751 | 0.001316 | 0.0013491 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.023447 | 0.023684 | 0.023921 | 0.024159 | 0.024396 | 0.024599 | 0.024802 | 0.025005 | 0.025208 | 0.025411 | 0.025614 | 0.025817 | 0.02602 | 0.026223 | 0.026426 | 0.026629 | 0.026832 | 0.027035 | 0.027238 | 0.027441 | 0.00076824 | 0.00078456 | 0.00080811 | 0.00082823 | 0.00084665 | 0.00087327 | 0.00090869 | 0.00093919 | 0.00095791 | 0.00096562 | 0.00097334 | 0.00098105 | 0.00098876 | 0.00099647 | 0.0010042 | 0.0010119 | 0.0010196 | 0.0010273 | 0.001035 | 0.0010427 | 32906.3857 | 7805.0738 | 438.3425 | 103.9706 | 11882.3008 | 15402.0898 | 645091.8985 | 12400.2499
| WND014-79365841 | 90 | WND014 | WND | South | 1636271.2018 | 0.0011769 | 0.0011899 | 0.0012134 | 0.0012314 | 0.0012466 | 0.0012751 | 0.001316 | 0.0013491 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.001365 | 0.87982 | 0.88782 | 0.89582 | 0.90382 | 0.91183 | 0.9181 | 0.92437 | 0.93065 | 0.93692 | 0.94319 | 0.94947 | 0.95574 | 0.96201 | 0.96829 | 0.97456 | 0.98083 | 0.98711 | 0.99338 | 0.99965 | 1.0059 | 0.028828 | 0.02941 | 0.030262 | 0.030985 | 0.031644 | 0.032593 | 0.033867 | 0.034955 | 0.035603 | 0.035842 | 0.03608 | 0.036318 | 0.036557 | 0.036795 | 0.037034 | 0.037272 | 0.03751 | 0.037749 | 0.037987 | 0.038225 | 32906.3857 | 7805.0738 | 16273.4842 | 3859.9118 | 261102.595 | 338446.7089 | 1707596.2018 | 272484.0473
| WND021-15425634 | 0 | WND021 | WND | South | 0 | 0.0012385 | 0.0012748 | 0.0013231 | 0.0013593 | 0.0013913 | 0.0014378 | 0.001494 | 0.0015423 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32906.3857 | 7805.0738 | 0 | 0 | 0 | 0 | 0 | 0
| WND021-200942770 | 215 | WND021 | WND | South | 3908870.0933 | 0.0012385 | 0.0012748 | 0.0013231 | 0.0013593 | 0.0013913 | 0.0014378 | 0.001494 | 0.0015423 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 0.0015664 | 14.3916 | 14.5244 | 14.6573 | 14.7902 | 14.9231 | 14.9985 | 15.0739 | 15.1494 | 15.2248 | 15.3003 | 15.3757 | 15.4512 | 15.5266 | 15.6021 | 15.6775 | 15.753 | 15.8284 | 15.9039 | 15.9793 | 16.0548 | 0.49623 | 0.51546 | 0.53989 | 0.5597 | 0.57803 | 0.60037 | 0.62695 | 0.65047 | 0.66394 | 0.66723 | 0.67052 | 0.67381 | 0.6771 | 0.6804 | 0.68369 | 0.68698 | 0.69027 | 0.69356 | 0.69685 | 0.70014 | 32906.3857 | 7805.0738 | 297694.1381 | 70610.1465 | 1042309.9286 | 1351064.1859 | 4079257.5933 | 1087744.1791
| WND022-15425649 | 0 | WND022 | WND | South | 0 | 0.00097456 | 0.001016 | 0.0010618 | 0.0011054 | 0.001149 | 0.0011999 | 0.001258 | 0.001311 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 5.4839e-05 | 5.5529e-05 | 5.6219e-05 | 5.691e-05 | 5.76e-05 | 5.802e-05 | 5.844e-05 | 5.886e-05 | 5.928e-05 | 5.97e-05 | 6.012e-05 | 6.054e-05 | 6.096e-05 | 6.138e-05 | 6.18e-05 | 6.222e-05 | 6.264e-05 | 6.306e-05 | 6.348e-05 | 6.39e-05 | 1.4879e-06 | 1.5706e-06 | 1.6618e-06 | 1.7513e-06 | 1.8425e-06 | 1.9381e-06 | 2.0467e-06 | 2.1484e-06 | 2.2237e-06 | 2.2394e-06 | 2.2552e-06 | 2.2709e-06 | 2.2867e-06 | 2.3024e-06 | 2.3182e-06 | 2.3339e-06 | 2.3497e-06 | 2.3655e-06 | 2.3812e-06 | 2.397e-06 | 32906.3857 | 7805.0738 | 0 | 0 | 0 | 0 | 0 | 0
| WND022-200942838 | 122 | WND022 | WND | South | 2218056.518 | 0.00097456 | 0.001016 | 0.0010618 | 0.0011054 | 0.001149 | 0.0011999 | 0.001258 | 0.001311 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 0.0013474 | 28.1967 | 28.4871 | 28.7776 | 29.068 | 29.3584 | 29.5249 | 29.6914 | 29.8579 | 30.0244 | 30.1909 | 30.3575 | 30.524 | 30.6905 | 30.857 | 31.0235 | 31.19 | 31.3565 | 31.523 | 31.6895 | 31.856 | 0.76503 | 0.80576 | 0.85066 | 0.89453 | 0.93911 | 0.98625 | 1.0399 | 1.0898 | 1.1263 | 1.1325 | 1.1387 | 1.145 | 1.1512 | 1.1575 | 1.1637 | 1.17 | 1.1762 | 1.1825 | 1.1887 | 1.195 | 32906.3857 | 7805.0738 | 494605.9624 | 117315.711 | 1406793.4791 | 1823515.477 | 2314741.518 | 1468115.5538
| WND023-200942910 | 457 | WND023 | WND | South | 8308621.5471 | 0.0023526 | 0.0023875 | 0.0024459 | 0.002472 | 0.0024796 | 0.0025158 | 0.0025914 | 0.002655 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 48.6431 | 49.0717 | 49.5003 | 49.9289 | 50.3575 | 50.4639 | 50.5704 | 50.6769 | 50.7834 | 50.8899 | 50.9963 | 51.1028 | 51.2093 | 51.3158 | 51.4222 | 51.5287 | 51.6352 | 51.7417 | 51.8482 | 51.9546 | 3.1859 | 3.2617 | 3.3707 | 3.4361 | 3.4762 | 3.5345 | 3.6483 | 3.7458 | 3.729 | 3.7368 | 3.7446 | 3.7524 | 3.7602 | 3.7681 | 3.7759 | 3.7837 | 3.7915 | 3.7993 | 3.8072 | 3.815 | 32906.3857 | 7805.0738 | 1718352.1835 | 407576.3809 | 4086468.2694 | 5296966.6454 | 8670794.0471 | 4264597.2672
| WND023-73768060 | 114 | WND023 | WND | South | 2072610.189 | 0.0023526 | 0.0023875 | 0.0024459 | 0.002472 | 0.0024796 | 0.0025158 | 0.0025914 | 0.002655 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.16274 | 0.16402 | 0.1653 | 0.16657 | 0.16785 | 0.16823 | 0.16861 | 0.169 | 0.16938 | 0.16976 | 0.17014 | 0.17053 | 0.17091 | 0.17129 | 0.17168 | 0.17206 | 0.17244 | 0.17282 | 0.17321 | 0.17359 | 0.010659 | 0.010902 | 0.011256 | 0.011463 | 0.011587 | 0.011783 | 0.012164 | 0.012491 | 0.012437 | 0.012465 | 0.012494 | 0.012522 | 0.01255 | 0.012578 | 0.012606 | 0.012634 | 0.012662 | 0.01269 | 0.012718 | 0.012746 | 32906.3857 | 7805.0738 | 5735.5571 | 1360.4182 | 84375.3438 | 109369.1061 | 2162955.189 | 88053.2618
| WND023-73768112 | 68 | WND023 | WND | South | 1236293.7969 | 0.0023526 | 0.0023875 | 0.0024459 | 0.002472 | 0.0024796 | 0.0025158 | 0.0025914 | 0.002655 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.091781 | 0.092777 | 0.093772 | 0.094768 | 0.095764 | 0.096252 | 0.096741 | 0.09723 | 0.097718 | 0.098207 | 0.098696 | 0.099184 | 0.099673 | 0.10016 | 0.10065 | 0.10114 | 0.10163 | 0.10212 | 0.1026 | 0.10309 | 0.0060113 | 0.0061668 | 0.0063854 | 0.0065219 | 0.0066106 | 0.0067416 | 0.0069792 | 0.0071868 | 0.0071754 | 0.0072112 | 0.0072471 | 0.007283 | 0.0073189 | 0.0073548 | 0.0073906 | 0.0074265 | 0.0074624 | 0.0074983 | 0.0075342 | 0.00757 | 32906.3857 | 7805.0738 | 3314.1695 | 786.0887 | 58133.3863 | 75353.7255 | 1290183.7969 | 60667.4185
| WND023-73768165 | 62 | WND023 | WND | South | 1127209.0502 | 0.0023526 | 0.0023875 | 0.0024459 | 0.002472 | 0.0024796 | 0.0025158 | 0.0025914 | 0.002655 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.19722 | 0.19894 | 0.20067 | 0.20239 | 0.20411 | 0.20516 | 0.2062 | 0.20725 | 0.20829 | 0.20934 | 0.21038 | 0.21143 | 0.21247 | 0.21351 | 0.21456 | 0.2156 | 0.21665 | 0.21769 | 0.21874 | 0.21978 | 0.012917 | 0.013224 | 0.013664 | 0.013928 | 0.01409 | 0.014369 | 0.014876 | 0.015319 | 0.015295 | 0.015371 | 0.015448 | 0.015525 | 0.015601 | 0.015678 | 0.015755 | 0.015832 | 0.015908 | 0.015985 | 0.016062 | 0.016138 | 32906.3857 | 7805.0738 | 7072.7545 | 1677.5884 | 65264.3547 | 84597.0376 | 1176344.0502 | 68109.2254
| WND023-73948116 | 44 | WND023 | WND | South | 799954.8098 | 0.0023526 | 0.0023875 | 0.0024459 | 0.002472 | 0.0024796 | 0.0025158 | 0.0025914 | 0.002655 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.04247 | 0.042864 | 0.043258 | 0.043652 | 0.044046 | 0.044226 | 0.044407 | 0.044588 | 0.044769 | 0.044949 | 0.04513 | 0.045311 | 0.045492 | 0.045672 | 0.045853 | 0.046034 | 0.046215 | 0.046395 | 0.046576 | 0.046757 | 0.0027816 | 0.0028491 | 0.0029456 | 0.0030041 | 0.0030405 | 0.0030976 | 0.0032037 | 0.0032957 | 0.0032873 | 0.0033006 | 0.0033139 | 0.0033271 | 0.0033404 | 0.0033537 | 0.0033669 | 0.0033802 | 0.0033935 | 0.0034068 | 0.00342 | 0.0034333 | 32906.3857 | 7805.0738 | 1517.9422 | 360.0411 | 18462.9144 | 23932.0204 | 834824.8098 | 19267.7122
| WND023-73948154 | 48 | WND023 | WND | South | 872677.9743 | 0.0023526 | 0.0023875 | 0.0024459 | 0.002472 | 0.0024796 | 0.0025158 | 0.0025914 | 0.002655 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.0026375 | 0.05401 | 0.054446 | 0.054881 | 0.055317 | 0.055752 | 0.05589 | 0.056027 | 0.056164 | 0.056301 | 0.056439 | 0.056576 | 0.056713 | 0.056851 | 0.056988 | 0.057125 | 0.057262 | 0.0574 | 0.057537 | 0.057674 | 0.057811 | 0.0035374 | 0.003619 | 0.0037371 | 0.0038069 | 0.0038486 | 0.0039146 | 0.004042 | 0.0041514 | 0.0041342 | 0.0041442 | 0.0041543 | 0.0041644 | 0.0041745 | 0.0041845 | 0.0041946 | 0.0042047 | 0.0042148 | 0.0042249 | 0.0042349 | 0.004245 | 32906.3857 | 7805.0738 | 1906.6542 | 452.2398 | 35428.6384 | 45923.3508 | 910717.9743 | 36972.9714
| WND024-167870308 | 11 | WND024 | WND | South | 199988.7024 | 0.0014834 | 0.0015829 | 0.0016024 | 0.001613 | 0.001622 | 0.0016391 | 0.0016667 | 0.0016888 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.081093 | 0.0817 | 0.082308 | 0.082915 | 0.083523 | 0.084094 | 0.084664 | 0.085235 | 0.085806 | 0.086377 | 0.086948 | 0.087519 | 0.08809 | 0.08866 | 0.089231 | 0.089802 | 0.090373 | 0.090944 | 0.091515 | 0.092085 | 0.0033489 | 0.0036003 | 0.0036719 | 0.0037233 | 0.0037716 | 0.0038375 | 0.0039286 | 0.0040073 | 0.0040517 | 0.0040786 | 0.0041056 | 0.0041326 | 0.0041595 | 0.0041865 | 0.0042134 | 0.0042404 | 0.0042673 | 0.0042943 | 0.0043212 | 0.0043482 | 32906.3857 | 7805.0738 | 1885.4977 | 447.2217 | 6375.7131 | 8264.3342 | 208706.2024 | 6653.6302
| WND024-183316836 | 325 | WND024 | WND | South | 5908757.1177 | 0.0014834 | 0.0015829 | 0.0016024 | 0.001613 | 0.001622 | 0.0016391 | 0.0016667 | 0.0016888 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 28.8498 | 28.9989 | 29.1481 | 29.2972 | 29.4463 | 29.5464 | 29.6464 | 29.7464 | 29.8464 | 29.9464 | 30.0465 | 30.1465 | 30.2465 | 30.3465 | 30.4465 | 30.5466 | 30.6466 | 30.7466 | 30.8466 | 30.9466 | 1.1914 | 1.2779 | 1.3004 | 1.3156 | 1.3297 | 1.3483 | 1.3757 | 1.3985 | 1.4093 | 1.414 | 1.4188 | 1.4235 | 1.4282 | 1.4329 | 1.4377 | 1.4424 | 1.4471 | 1.4518 | 1.4565 | 1.4613 | 32906.3857 | 7805.0738 | 654205.5577 | 155171.1786 | 1662278.192 | 2154680.1683 | 6166319.6177 | 1734736.8358
| WND024-184539432 | 1 | WND024 | WND | South | 18180.7911 | 0.0014834 | 0.0015829 | 0.0016024 | 0.001613 | 0.001622 | 0.0016391 | 0.0016667 | 0.0016888 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.000346 | 0.00034941 | 0.00035283 | 0.00035624 | 0.00035966 | 0.00036473 | 0.0003698 | 0.00037487 | 0.00037995 | 0.00038502 | 0.00039009 | 0.00039516 | 0.00040023 | 0.0004053 | 0.00041037 | 0.00041545 | 0.00042052 | 0.00042559 | 0.00043066 | 0.00043573 | 1.4289e-05 | 1.5398e-05 | 1.574e-05 | 1.5997e-05 | 1.6241e-05 | 1.6644e-05 | 1.716e-05 | 1.7625e-05 | 1.7941e-05 | 1.818e-05 | 1.842e-05 | 1.8659e-05 | 1.8899e-05 | 1.9138e-05 | 1.9378e-05 | 1.9617e-05 | 1.9856e-05 | 2.0096e-05 | 2.0335e-05 | 2.0575e-05 | 32906.3857 | 7805.0738 | 8.403 | 1.9931 | 2.0541 | 2.6626 | 18973.2911 | 2.1436
| WND024-192414587 | 174 | WND024 | WND | South | 3163457.6569 | 0.0014834 | 0.0015829 | 0.0016024 | 0.001613 | 0.001622 | 0.0016391 | 0.0016667 | 0.0016888 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 13.5534 | 13.6274 | 13.7013 | 13.7753 | 13.8493 | 13.8943 | 13.9392 | 13.9841 | 14.0291 | 14.074 | 14.119 | 14.1639 | 14.2088 | 14.2538 | 14.2987 | 14.3437 | 14.3886 | 14.4335 | 14.4785 | 14.5234 | 0.55972 | 0.60052 | 0.61125 | 0.61858 | 0.62539 | 0.63404 | 0.64681 | 0.65746 | 0.66244 | 0.66456 | 0.66668 | 0.66881 | 0.67093 | 0.67305 | 0.67517 | 0.67729 | 0.67942 | 0.68154 | 0.68366 | 0.68578 | 32906.3857 | 7805.0738 | 307399.6486 | 72912.1989 | 1362149.5133 | 1765647.0239 | 3301352.6569 | 1421525.5593
| WND024-200942990 | 270 | WND024 | WND | South | 4908813.6055 | 0.0014834 | 0.0015829 | 0.0016024 | 0.001613 | 0.001622 | 0.0016391 | 0.0016667 | 0.0016888 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 27.2868 | 27.5251 | 27.7635 | 28.0019 | 28.2403 | 28.3633 | 28.4864 | 28.6095 | 28.7325 | 28.8556 | 28.9787 | 29.1018 | 29.2248 | 29.3479 | 29.471 | 29.594 | 29.7171 | 29.8402 | 29.9633 | 30.0863 | 1.1269 | 1.213 | 1.2386 | 1.2574 | 1.2752 | 1.2943 | 1.3218 | 1.3451 | 1.3567 | 1.3625 | 1.3683 | 1.3742 | 1.38 | 1.3858 | 1.3916 | 1.3974 | 1.4032 | 1.409 | 1.4148 | 1.4206 | 32906.3857 | 7805.0738 | 629185.4844 | 149236.6612 | 1199945.4528 | 1555394.6882 | 5122788.6055 | 1252251.0299
| WND024-79365148 | 15 | WND024 | WND | South | 272711.867 | 0.0014834 | 0.0015829 | 0.0016024 | 0.001613 | 0.001622 | 0.0016391 | 0.0016667 | 0.0016888 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.0016961 | 0.016303 | 0.01643 | 0.016557 | 0.016684 | 0.016811 | 0.016941 | 0.017071 | 0.017201 | 0.017331 | 0.017462 | 0.017592 | 0.017722 | 0.017852 | 0.017982 | 0.018113 | 0.018243 | 0.018373 | 0.018503 | 0.018633 | 0.018764 | 0.00067329 | 0.00072404 | 0.00073864 | 0.00074918 | 0.00075911 | 0.00077306 | 0.00079213 | 0.00080871 | 0.00081837 | 0.00082452 | 0.00083067 | 0.00083682 | 0.00084297 | 0.00084911 | 0.00085526 | 0.00086141 | 0.00086756 | 0.00087371 | 0.00087986 | 0.000886 | 32906.3857 | 7805.0738 | 381.158 | 90.407 | 7615.1447 | 9870.9117 | 284599.367 | 7947.0886
| WPD011-15399272 | 1 | WPD011 | WPD | South | 18180.7911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41943.1332 | 8049.4159 | 0 | 0 | 0 | 0 | 18973.2911 | 0
| WPD011-15399285 | 155 | WPD011 | WPD | South | 2818022.6254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0523 | 12.1233 | 12.1943 | 12.2653 | 12.3363 | 12.3467 | 12.3571 | 12.3674 | 12.3778 | 12.3882 | 12.3986 | 12.4089 | 12.4193 | 12.4297 | 12.44 | 12.4504 | 12.4608 | 12.4711 | 12.4815 | 12.4919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41943.1332 | 8049.4159 | 0 | 0 | 274045.5463 | 355223.6363 | 2940860.1254 | 285991.1814
| WPD012-15436728 | 186 | WPD012 | WPD | South | 3381627.1505 | 0.0015737 | 0.0016247 | 0.001668 | 0.001715 | 0.0017481 | 0.0017881 | 0.0018636 | 0.0019437 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 32.281 | 32.4961 | 32.7113 | 32.9264 | 33.1415 | 33.1489 | 33.1562 | 33.1636 | 33.1709 | 33.1783 | 33.1856 | 33.193 | 33.2003 | 33.2077 | 33.215 | 33.2224 | 33.2297 | 33.237 | 33.2444 | 33.2517 | 1.4143 | 1.4699 | 1.519 | 1.5721 | 1.6129 | 1.6501 | 1.7203 | 1.7946 | 1.8573 | 1.8577 | 1.8581 | 1.8585 | 1.8589 | 1.8594 | 1.8598 | 1.8602 | 1.8606 | 1.861 | 1.8614 | 1.8618 | 41943.1332 | 8049.4159 | 1047101.2665 | 200951.93 | 344432.8299 | 446461.1227 | 3529032.1505 | 359446.6439
| WPD012-24603816 | 130 | WPD012 | WPD | South | 2363502.8471 | 0.0015737 | 0.0016247 | 0.001668 | 0.001715 | 0.0017481 | 0.0017881 | 0.0018636 | 0.0019437 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 0.0020112 | 13.8653 | 13.9572 | 14.0491 | 14.141 | 14.2329 | 14.2386 | 14.2443 | 14.25 | 14.2557 | 14.2613 | 14.267 | 14.2727 | 14.2784 | 14.2841 | 14.2898 | 14.2955 | 14.3011 | 14.3068 | 14.3125 | 14.3182 | 0.60745 | 0.63132 | 0.65241 | 0.67518 | 0.69267 | 0.70879 | 0.73905 | 0.77111 | 0.7982 | 0.79852 | 0.79883 | 0.79915 | 0.79947 | 0.79979 | 0.80011 | 0.80043 | 0.80074 | 0.80106 | 0.80138 | 0.8017 | 41943.1332 | 8049.4159 | 450125.2073 | 86384.7004 | 214452.1451 | 277977.4085 | 2466527.8471 | 223800.106
| WPD013-178115477 | 4 | WPD013 | WPD | South | 72723.1645 | 0.069845 | 0.070409 | 0.0705 | 0.0705 | 0.0705 | 0.070527 | 0.070791 | 0.071091 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41943.1332 | 8049.4159 | 0 | 0 | 0 | 0 | 75893.1645 | 0
| WPD013-40657711 | 55 | WPD013 | WPD | South | 999943.5122 | 0.069845 | 0.070409 | 0.0705 | 0.0705 | 0.0705 | 0.070527 | 0.070791 | 0.071091 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.071364 | 0.18961 | 0.19083 | 0.19205 | 0.19327 | 0.19449 | 0.19455 | 0.1946 | 0.19465 | 0.19471 | 0.19476 | 0.19482 | 0.19487 | 0.19492 | 0.19498 | 0.19503 | 0.19508 | 0.19514 | 0.19519 | 0.19525 | 0.1953 | 0.36871 | 0.37407 | 0.37695 | 0.37934 | 0.38174 | 0.38199 | 0.38352 | 0.38526 | 0.38684 | 0.38695 | 0.38705 | 0.38716 | 0.38727 | 0.38737 | 0.38748 | 0.38759 | 0.38769 | 0.3878 | 0.38791 | 0.38802 | 41943.1332 | 8049.4159 | 232341.2609 | 44589.2162 | 50987.8918 | 66091.5844 | 1043531.0122 | 53210.4521
| WPD014-15399222 | 47 | WPD014 | WPD | South | 854497.1832 | 2.8466e-05 | 2.8466e-05 | 2.8466e-05 | 2.8466e-05 | 2.8466e-05 | 2.9385e-05 | 2.9385e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 13.3756 | 13.3829 | 13.3903 | 13.3976 | 13.405 | 13.3855 | 13.3661 | 13.3466 | 13.3271 | 13.3077 | 13.2882 | 13.2688 | 13.2493 | 13.2298 | 13.2104 | 13.1909 | 13.1715 | 13.152 | 13.1325 | 13.1131 | 0.0106 | 0.010606 | 0.010612 | 0.010618 | 0.010624 | 0.01095 | 0.010934 | 0.011715 | 0.011698 | 0.01168 | 0.011663 | 0.011646 | 0.011629 | 0.011612 | 0.011595 | 0.011578 | 0.011561 | 0.011544 | 0.011527 | 0.01151 | 41943.1332 | 8049.4159 | 6806.5789 | 1306.2683 | 102637.8733 | 133041.3833 | 891744.6832 | 107111.8543
| WPD014-15399233 | 3 | WPD014 | WPD | South | 54542.3734 | 2.8466e-05 | 2.8466e-05 | 2.8466e-05 | 2.8466e-05 | 2.8466e-05 | 2.9385e-05 | 2.9385e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 3.1527e-05 | 0.25838 | 0.25995 | 0.26152 | 0.26309 | 0.26466 | 0.26453 | 0.2644 | 0.26427 | 0.26414 | 0.26401 | 0.26388 | 0.26375 | 0.26361 | 0.26348 | 0.26335 | 0.26322 | 0.26309 | 0.26296 | 0.26283 | 0.2627 | 0.00020477 | 0.00020601 | 0.00020725 | 0.0002085 | 0.00020974 | 0.0002164 | 0.0002163 | 0.00023195 | 0.00023184 | 0.00023172 | 0.00023161 | 0.0002315 | 0.00023138 | 0.00023127 | 0.00023115 | 0.00023104 | 0.00023092 | 0.00023081 | 0.00023069 | 0.00023058 | 41943.1332 | 8049.4159 | 134.6109 | 25.8335 | 2439.8381 | 3162.5698 | 56919.8734 | 2546.1906
| WPD021-15399198 | 1 | WPD021 | WPD | South | 18180.7911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41943.1332 | 8049.4159 | 0 | 0 | 0 | 0 | 18973.2911 | 0
| WPD022-15399022 | 352 | WPD022 | WPD | South | 6399638.4783 | 0.0012335 | 0.0012971 | 0.0013518 | 0.0014055 | 0.0014529 | 0.0015146 | 0.0016034 | 0.0016976 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 170.4263 | 170.5077 | 170.589 | 170.6703 | 170.7517 | 170.5366 | 170.3216 | 170.1065 | 169.8914 | 169.6764 | 169.4613 | 169.2463 | 169.0312 | 168.8162 | 168.6011 | 168.3861 | 168.171 | 167.956 | 167.7409 | 167.5259 | 5.8526 | 6.1572 | 6.4199 | 6.6784 | 6.9069 | 7.1909 | 7.603 | 8.0395 | 8.413 | 8.4024 | 8.3917 | 8.3811 | 8.3704 | 8.3598 | 8.3491 | 8.3385 | 8.3278 | 8.3172 | 8.3065 | 8.2959 | 41943.1332 | 8049.4159 | 4612698.4726 | 885234.9722 | 3371474.825 | 4370177.0126 | 6678598.4783 | 3518437.2855
| WPD022-72495720 | 244 | WPD022 | WPD | South | 4436113.0361 | 0.0012335 | 0.0012971 | 0.0013518 | 0.0014055 | 0.0014529 | 0.0015146 | 0.0016034 | 0.0016976 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 0.0017787 | 7.4113 | 7.427 | 7.4426 | 7.4582 | 7.4738 | 7.4406 | 7.4073 | 7.374 | 7.3407 | 7.3074 | 7.2742 | 7.2409 | 7.2076 | 7.1743 | 7.141 | 7.1078 | 7.0745 | 7.0412 | 7.0079 | 6.9747 | 0.25451 | 0.26819 | 0.28009 | 0.29184 | 0.30232 | 0.31374 | 0.33065 | 0.34851 | 0.36351 | 0.36186 | 0.36022 | 0.35857 | 0.35692 | 0.35527 | 0.35362 | 0.35198 | 0.35033 | 0.34868 | 0.34703 | 0.34538 | 41943.1332 | 8049.4159 | 198145.3584 | 38026.5916 | 273367.5329 | 354344.781 | 4629483.0361 | 285283.6134
| WPD024-15398985 | 131 | WPD024 | WPD | South | 2381683.6382 | 0.0006014 | 0.0006173 | 0.00063045 | 0.00064442 | 0.00065849 | 0.00067595 | 0.00069645 | 0.00071943 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 0.00073635 | 74.2573 | 74.6096 | 74.9619 | 75.3142 | 75.6665 | 75.5445 | 75.4225 | 75.3005 | 75.1785 | 75.0564 | 74.9344 | 74.8124 | 74.6904 | 74.5684 | 74.4464 | 74.3244 | 74.2024 | 74.0804 | 73.9583 | 73.8363 | 1.2433 | 1.2822 | 1.3157 | 1.3512 | 1.3871 | 1.4216 | 1.4624 | 1.5082 | 1.5412 | 1.5387 | 1.5362 | 1.5337 | 1.5311 | 1.5286 | 1.5261 | 1.5236 | 1.5211 | 1.5186 | 1.5161 | 1.5136 | 41943.1332 | 8049.4159 | 878924.8013 | 168676.7467 | 473732.4426 | 614062.0168 | 2485501.1382 | 494382.4219
| WPD031-15399072 | 37 | WPD031 | WPD | South | 672689.2719 | 0.00076666 | 0.00079632 | 0.00082286 | 0.00085022 | 0.00087337 | 0.00092064 | 0.00097684 | 0.0010295 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41943.1332 | 8049.4159 | 0 | 0 | 0 | 0 | 702011.7719 | 0
| WPD031-80918872 | 99 | WPD031 | WPD | South | 1799898.322 | 0.00076666 | 0.00079632 | 0.00082286 | 0.00085022 | 0.00087337 | 0.00092064 | 0.00097684 | 0.0010295 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0.0010737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41943.1332 | 8049.4159 | 0 | 0 | 0 | 0 | 1878355.822 | 0
| WPD033-153773704 | 331 | WPD033 | WPD | South | 6017841.8645 | 0.0012102 | 0.0012374 | 0.0012609 | 0.0012877 | 0.0013511 | 0.0014322 | 0.0015174 | 0.0015927 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 1.8639 | 1.8794 | 1.8948 | 1.9103 | 1.9257 | 1.933 | 1.9404 | 1.9477 | 1.955 | 1.9624 | 1.9697 | 1.977 | 1.9844 | 1.9917 | 1.999 | 2.0064 | 2.0137 | 2.021 | 2.0284 | 2.0357 | 0.062799 | 0.064744 | 0.066512 | 0.068481 | 0.072433 | 0.077075 | 0.08197 | 0.086363 | 0.090072 | 0.09041 | 0.090748 | 0.091086 | 0.091424 | 0.091762 | 0.0921 | 0.092437 | 0.092775 | 0.093113 | 0.093451 | 0.093789 | 41943.1332 | 8049.4159 | 49843.7143 | 9565.637 | 779267.0978 | 1010102.5023 | 6280159.3645 | 813235.3212
| WPD033-15399135 | 387 | WPD033 | WPD | South | 7035966.1679 | 0.0012102 | 0.0012374 | 0.0012609 | 0.0012877 | 0.0013511 | 0.0014322 | 0.0015174 | 0.0015927 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 55.0929 | 55.3794 | 55.6659 | 55.9524 | 56.2388 | 56.3212 | 56.4036 | 56.4859 | 56.5683 | 56.6506 | 56.733 | 56.8153 | 56.8977 | 56.98 | 57.0624 | 57.1447 | 57.2271 | 57.3095 | 57.3918 | 57.4742 | 1.8562 | 1.9078 | 1.954 | 2.0058 | 2.1154 | 2.2457 | 2.3827 | 2.5046 | 2.6062 | 2.61 | 2.6138 | 2.6176 | 2.6214 | 2.6252 | 2.629 | 2.6328 | 2.6366 | 2.6404 | 2.6442 | 2.6479 | 41943.1332 | 8049.4159 | 1439497.1463 | 276257.6448 | 1744513.0477 | 2261274.7285 | 7342663.6679 | 1820556.3057
| WPD033-63732110 | 115 | WPD033 | WPD | South | 2090790.9801 | 0.0012102 | 0.0012374 | 0.0012609 | 0.0012877 | 0.0013511 | 0.0014322 | 0.0015174 | 0.0015927 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 0.0016549 | 21.0811 | 21.1563 | 21.2316 | 21.3068 | 21.382 | 21.3407 | 21.2993 | 21.258 | 21.2166 | 21.1753 | 21.134 | 21.0926 | 21.0513 | 21.0099 | 20.9686 | 20.9273 | 20.8859 | 20.8446 | 20.8032 | 20.7619 | 0.71027 | 0.72884 | 0.74528 | 0.76383 | 0.80426 | 0.85091 | 0.89978 | 0.9426 | 0.97749 | 0.97559 | 0.97368 | 0.97178 | 0.96987 | 0.96797 | 0.96606 | 0.96416 | 0.96225 | 0.96035 | 0.95845 | 0.95654 | 41943.1332 | 8049.4159 | 537610.2591 | 103174.1844 | 706440.3533 | 915702.9351 | 2181928.4801 | 737234.0617

## Calcs
Powercor
Pole bushfire resilience program
| Segment | Number of poles in segment | Option 2 capex ($ 2023) | Option 2 PV cost ($ 2023) | Option 1 PV of energy at risks and VNR ($ 2023) | Option 1 PV of unplanned pole replacement risk ($ 2023) | Option 1 PV of total risk ($ 2023) | Option 2 PV of energy at risks and VNR ($ 2023) | Option 2 PV of unplanned pole replacement risk ($ 2023) | Option 2 PV of total risk ($ 2023) | PV of Option 2 benefits ($ 2023) | Option 2 NPV ($ 2023) | Option 2 preferred | Option 2 NPV rank | Option 3 capex ($ 2023) | Option 3 PV cost ($ 2023) | Option 3 PV of energy at risks and VNR ($ 2023) | Option 3 PV of unplanned pole and mesh replacement risk ($ 2023) | Option 3 PV of total risk ($ 2023) | PV of Option 3 benefits ($ 2023) | Option 3 NPV ($ 2023) | Option 3 preferred | Preferred option | Preferred option NPV | Option 2and 3 NPV rank
| EHK033-15418024 | 420 | 8998051.8187 | -4863873.5889 | 18603067.6786 | 20431545.733 | 39034613.4116 | 653528.7676 | 717763.4965 | 1371292.2641 | 37663321.1475 | 32799447.5586 | TRUE | 1 | 332850 | -338624.7802 | 7284595.5388 | 8000591.5943 | 15285187.133 | 23749426.2785 | 23410801.4983 | TRUE | Option 2 | 32799447.5586 | 1
| EHK031-15417924 | 674 | 14439730.7757 | -7805359.045 | 7612738.6232 | 19503091.3522 | 27115829.9753 | 267436.7355 | 685146.7444 | 952583.4799 | 26163246.4954 | 18357887.4505 | TRUE | 2 | 534145 | -543412.1473 | 2980998.767 | 7637027.1135 | 10618025.8805 | 16497804.0948 | 15954391.9475 | TRUE | Option 2 | 18357887.4505 | 2
| BAS033-193428051 | 539 | 11547499.834 | -6241971.1057 | 3849097.2068 | 21742083.5463 | 25591180.7531 | 135219.4056 | 990057.4836 | 1125276.8892 | 24465903.864 | 18223932.7582 | TRUE | 3 | 427157.5 | -434568.468 | 1507230.7872 | 8884887.4543 | 10392118.2415 | 15199062.5116 | 14764494.0437 | TRUE | Option 2 | 18223932.7582 | 3
| GSB012-24607348 | 403 | 8633844.9594 | -4667002.515 | 10314400.2505 | 11863172.0117 | 22177572.2622 | 362346.5442 | 540206.8391 | 902553.3833 | 21275018.8789 | 16608016.3638 | TRUE | 4 | 319377.5 | -324918.5391 | 4038916.3415 | 4847877.0652 | 8886793.4068 | 13290778.8554 | 12965860.3162 | TRUE | Option 2 | 16608016.3638 | 4
| EHK023-15417824 | 270 | 5784461.8834 | -3126775.8786 | 7830674.8549 | 9792027.9479 | 17622702.8028 | 275092.8705 | 343995.5209 | 619088.3914 | 17003614.4114 | 13876838.5328 | TRUE | 5 | 213975 | -217687.3587 | 3066338.3104 | 3834365.6185 | 6900703.9289 | 10721998.8739 | 10504311.5152 | TRUE | Option 2 | 13876838.5328 | 5
| CMN002-15420512 | 525 | 11247564.7734 | -6079841.9861 | 2425409.9468 | 14546156.2596 | 16971566.2064 | 85205.0426 | 511008.8152 | 596213.8578 | 16375352.3486 | 10295510.3625 | TRUE | 6 | 416062.5 | -423280.9753 | 949742.848 | 5695988.792 | 6645731.64 | 10325834.5663 | 9902553.5911 | TRUE | Option 2 | 10295510.3625 | 6
| GSB013-74623435 | 348 | 7455528.6498 | -4030066.6879 | 6233570.6316 | 6456864.5806 | 12690435.2122 | 218986.3415 | 294022.7456 | 513009.0871 | 12177426.1251 | 8147359.4372 | TRUE | 7 | 275790 | -280574.8179 | 2440943.698 | 2638593.2601 | 5079536.9581 | 7610898.2541 | 7330323.4362 | TRUE | Option 2 | 8147359.4372 | 7
| BAS022-193385775 | 426 | 9126595.4161 | -4933357.4973 | 3735784.2889 | 9665077.3289 | 13400861.6177 | 131238.7045 | 440113.392 | 571352.0965 | 12829509.5212 | 7896152.024 | TRUE | 8 | 337605 | -343462.2771 | 1462859.6764 | 3949627.1883 | 5412486.8647 | 7988374.7531 | 7644912.476 | TRUE | Option 2 | 7896152.024 | 8
| CMN001-156820944 | 375 | 8033974.8381 | -4342744.2758 | 1101815.988 | 11040534.9336 | 12142350.9216 | 38706.9733 | 387855.7727 | 426562.746 | 11715788.1755 | 7373043.8998 | TRUE | 9 | 297187.5 | -302343.5538 | 431449.4775 | 4323256.4066 | 4754705.8841 | 7387645.0375 | 7085301.4837 | TRUE | Option 2 | 7373043.8998 | 9
| BAN003-15414742 | 373 | 7991126.9723 | -4319582.973 | 6724573.3859 | 5419737.9674 | 12144311.3533 | 236235.3475 | 246795.6726 | 483031.0201 | 11661280.3332 | 7341697.3602 | TRUE | 10 | 295602.5 | -300731.0548 | 2633210.7228 | 2214772.1845 | 4847982.9073 | 7296328.446 | 6995597.3912 | TRUE | Option 2 | 7341697.3602 | 10
| KGT003-84636133 | 428 | 9169443.2819 | -4956518.8001 | 636191.1206 | 11904901.361 | 12541092.4816 | 22349.4967 | 418221.1047 | 440570.6013 | 12100521.8803 | 7144003.0802 | TRUE | 12 | 339190 | -345074.776 | 249119.9344 | 4661725.3048 | 4910845.2391 | 7630247.2424 | 7285172.4664 | TRUE | Option 3 | 7285172.4664 | 11
| MLN022-160532221 | 220 | 4713265.2384 | -2547743.3085 | 5437630.9782 | 4703958.0155 | 10141588.9937 | 191024.8532 | 214201.5886 | 405226.4418 | 9736362.5519 | 7188619.2435 | TRUE | 11 | 174350 | -177374.8849 | 2129269.3791 | 1922269.2006 | 4051538.5797 | 6090050.414 | 5912675.5292 | TRUE | Option 2 | 7188619.2435 | 12
| BGO023-159428721 | 231 | 4948928.5003 | -2675130.4739 | 4704838.712 | 5325128.235 | 10029966.947 | 165281.7427 | 187072.6137 | 352354.3563 | 9677612.5906 | 7002482.1167 | TRUE | 13 | 183067.5 | -186243.6291 | 1842322.3354 | 2085215.5168 | 3927537.8523 | 6102429.0947 | 5916185.4656 | TRUE | Option 2 | 7002482.1167 | 13
| FNS022-15405419 | 388 | 8312485.9658 | -4493292.744 | 4193332.6401 | 6802755.3266 | 10996087.9667 | 147312.4519 | 309773.3851 | 457085.837 | 10539002.1297 | 6045709.3857 | TRUE | 14 | 307490 | -312824.797 | 1642026.6147 | 2779941.2751 | 4421967.8897 | 6574120.077 | 6261295.28 | TRUE | Option 3 | 6261295.28 | 14
| BET007-155326877 | 123 | 2635143.7469 | -1424420.1225 | 4538482.8977 | 3189885.1607 | 7728368.0583 | 159437.6361 | 112061.1801 | 271498.8162 | 7456869.2421 | 6032449.1196 | TRUE | 15 | 97477.5 | -99168.6856 | 1777180.6694 | 1249096.311 | 3026276.9803 | 4702091.078 | 4602922.3923 | TRUE | Option 2 | 6032449.1196 | 15
| BAS033-193428622 | 445 | 9533650.1412 | -5153389.8739 | 2292546.9228 | 8225980.93 | 10518527.8528 | 80537.5431 | 374582.0387 | 455119.5818 | 10063408.2711 | 4910018.3972 | TRUE | 18 | 352662.5 | -358781.0172 | 897716.3001 | 3361541.4368 | 4259257.7369 | 6259270.1159 | 5900489.0988 | TRUE | Option 3 | 5900489.0988 | 16
| CMN001-124828418 | 431 | 9233715.0806 | -4991260.7543 | 489253.2594 | 9184778.1172 | 9674031.3767 | 17187.5459 | 322662.7364 | 339850.2823 | 9334181.0943 | 4342920.34 | TRUE | 22 | 341567.5 | -347493.5245 | 191581.9569 | 3596578.5242 | 3788160.4812 | 5885870.8955 | 5538377.371 | TRUE | Option 3 | 5538377.371 | 17
| CMN004-15420549 | 464 | 9940704.8664 | -5373422.2505 | 1326908.636 | 8336382.0167 | 9663290.6527 | 46614.5144 | 292858.4446 | 339472.959 | 9323817.6937 | 3950395.4431 | TRUE | 28 | 367720 | -374099.7572 | 519591.3329 | 3264363.292 | 3783954.6248 | 5879336.0278 | 5505236.2706 | TRUE | Option 3 | 5505236.2706 | 18
| CMN003-123737154 | 330 | 7069897.8575 | -3821614.9627 | 1622620.1708 | 7635947.3402 | 9258567.511 | 57002.9083 | 268252.0615 | 325254.9697 | 8933312.5412 | 5111697.5785 | TRUE | 17 | 261525 | -266062.3273 | 635386.1557 | 2990086.8443 | 3625473 | 5633094.511 | 5367032.1836 | TRUE | Option 3 | 5367032.1836 | 19
| GSB012-74623277 | 140 | 2999350.6062 | -1621291.1963 | 4929946.2234 | 2173060.6562 | 7103006.8795 | 173189.8059 | 98953.4862 | 272143.2921 | 6830863.5875 | 5209572.3912 | TRUE | 16 | 110950 | -112874.9267 | 1930470.011 | 888019.7392 | 2818489.7502 | 4284517.1294 | 4171642.2026 | TRUE | Option 2 | 5209572.3912 | 20
| BAS022-131562724 | 613 | 13132870.8687 | -7098939.3095 | 573278.8297 | 8825525.3549 | 9398804.1846 | 20139.3777 | 401883.1684 | 422022.5462 | 8976781.6384 | 1877842.329 | TRUE | 59 | 485802.5 | -494230.9292 | 224484.7182 | 3606544.8528 | 3831029.571 | 5567774.6136 | 5073543.6844 | TRUE | Option 3 | 5073543.6844 | 21
| WPD022-15399022 | 352 | 7541224.3814 | -4076389.2935 | 5497933.4448 | 3371474.825 | 8869408.2698 | 193143.2885 | 153525.0232 | 346668.3118 | 8522739.958 | 4446350.6645 | TRUE | 21 | 278960 | -283799.8158 | 2152882.6394 | 1377750.8633 | 3530633.5026 | 5338774.7671 | 5054974.9513 | TRUE | Option 3 | 5054974.9513 | 22
| MLN022-83935111 | 388 | 8312485.9658 | -4493292.744 | 1518167.7137 | 7447354.51 | 8965522.2237 | 53333.4766 | 339126.149 | 392459.6257 | 8573062.598 | 4079769.854 | TRUE | 27 | 307490 | -312824.797 | 594484.6272 | 3043356.287 | 3637840.9142 | 5327681.3094 | 5014856.5125 | TRUE | Option 3 | 5014856.5125 | 23
| BET005-24614354 | 246 | 5270287.4938 | -2848840.2449 | 2561001.5505 | 5205092.6999 | 7766094.2504 | 89968.3975 | 182855.7459 | 272824.1434 | 7493270.107 | 4644429.8621 | TRUE | 19 | 194955 | -198337.3713 | 1002837.854 | 2038211.9614 | 3041049.8154 | 4725044.435 | 4526707.0637 | TRUE | Option 2 | 4644429.8621 | 24
| CME016-15423749 | 294 | 6298636.2731 | -3404711.5122 | 3009524.2752 | 4881418.116 | 7890942.3912 | 105725.0731 | 171485.0056 | 277210.0787 | 7613732.3125 | 4209020.8003 | TRUE | 24 | 232995 | -237037.3462 | 1178470.5344 | 1911467.3582 | 3089937.8927 | 4801004.4986 | 4563967.1524 | TRUE | Option 3 | 4563967.1524 | 25
| GSB014-194965507 | 235 | 5034624.2319 | -2721453.0795 | 1889454.8991 | 5613332.5346 | 7502787.4337 | 66376.8553 | 255611.2836 | 321988.1389 | 7180799.2948 | 4459346.2153 | TRUE | 20 | 186237.5 | -189468.627 | 739873.389 | 2293884.471 | 3033757.8599 | 4469029.5737 | 4279560.9467 | TRUE | Option 2 | 4459346.2153 | 26
| MLN033-196479827 | 490 | 10497727.1218 | -5674519.187 | 4730104.9209 | 3241247.7395 | 7971352.6604 | 166169.3487 | 147594.9429 | 313764.2916 | 7657588.3688 | 1983069.1818 | TRUE | 57 | 388325 | -395062.2436 | 1852216.0861 | 1324533.6546 | 3176749.7406 | 4794602.9198 | 4399540.6762 | TRUE | Option 3 | 4399540.6762 | 27
| HSM010-15416755 | 224 | 4798960.97 | -2594065.9141 | 3592523.6815 | 3554678.4036 | 7147202.0851 | 126205.9363 | 124876.4256 | 251082.3618 | 6896119.7232 | 4302053.8092 | TRUE | 23 | 177520 | -180599.8828 | 1406761.6393 | 1391942.1725 | 2798703.8118 | 4348498.2733 | 4167898.3905 | TRUE | Option 2 | 4302053.8092 | 28
| BAN009-15414553 | 446 | 9555074.0741 | -5164970.5253 | 2922796.5464 | 4856707.0706 | 7779503.6171 | 102678.314 | 221157.2396 | 323835.5536 | 7455668.0634 | 2290697.5381 | TRUE | 50 | 353455 | -359587.2666 | 1144509.661 | 1984689.9967 | 3129199.6577 | 4650303.9594 | 4290716.6927 | TRUE | Option 3 | 4290716.6927 | 29
| BET006-15436859 | 250 | 5355983.2254 | -2895162.8505 | 3984664.8131 | 3282086.3074 | 7266751.1205 | 139981.9175 | 115300.2213 | 255282.1387 | 7011468.9818 | 4116306.1312 | TRUE | 26 | 198125 | -201562.3692 | 1560316.3963 | 1285200.4672 | 2845516.8636 | 4421234.2569 | 4219671.8877 | TRUE | Option 3 | 4219671.8877 | 30
| CME014-15423849 | 204 | 4370482.3119 | -2362452.886 | 3442624.0844 | 3307370.8837 | 6749994.9681 | 120939.9393 | 116188.4725 | 237128.4118 | 6512866.5564 | 4150413.6703 | TRUE | 25 | 161670 | -164474.8933 | 1348063.9043 | 1295101.4102 | 2643165.3145 | 4106829.6536 | 3942354.7604 | TRUE | Option 2 | 4150413.6703 | 31
| BAN003-193118819 | 436 | 9340834.7451 | -5049164.0113 | 3036385.332 | 4446480.9282 | 7482866.2601 | 106668.7064 | 202476.9939 | 309145.7003 | 7173720.5598 | 2124556.5485 | TRUE | 56 | 345530 | -351524.7719 | 1188988.7961 | 1817051.3663 | 3006040.1624 | 4476826.0977 | 4125301.3258 | TRUE | Option 3 | 4125301.3258 | 32
| HTN012-24597770 | 1484 | 31793116.426 | -17185686.6806 | 337857.6549 | 8548909.9034 | 8886767.5583 | 11868.9939 | 389287.0804 | 401156.0743 | 8485611.484 | -8700075.1967 | FALSE | 2239 | 1176070 | -1196474.2235 | 132298.4149 | 3493506.1392 | 3625804.5541 | 5260963.0042 | 4064488.7807 | TRUE | Option 3 | 4064488.7807 | 33
| BET004-24611449 | 253 | 5420255.0241 | -2929904.8047 | 1240624.2733 | 5768052.3354 | 7008676.6086 | 43583.3308 | 202632.6087 | 246215.9395 | 6762460.6691 | 3832555.8644 | TRUE | 30 | 200502.5 | -203981.1176 | 485804.0729 | 2258655.886 | 2744459.9589 | 4264216.6497 | 4060235.5321 | TRUE | Option 3 | 4060235.5321 | 34
| HTN032-190418526 | 556 | 11911706.6933 | -6438842.1795 | 2016230.5857 | 5532466.961 | 7548697.5467 | 70830.5056 | 251928.9518 | 322759.4574 | 7225938.0893 | 787095.9097 | TRUE | 87 | 440630 | -448274.7091 | 789516.2553 | 2260838.81 | 3050355.0653 | 4498342.4814 | 4050067.7723 | TRUE | Option 3 | 4050067.7723 | 35
| BAN008-193386491 | 345 | 7391256.8511 | -3995324.7337 | 916756.1395 | 6091234.4423 | 7007990.5818 | 32205.791 | 277373.244 | 309579.035 | 6698411.5469 | 2703086.8132 | TRUE | 46 | 273412.5 | -278156.0695 | 358983.6794 | 2489178.7561 | 2848162.4356 | 4159828.1463 | 3881672.0768 | TRUE | Option 3 | 3881672.0768 | 36
| MBN023-94547273 | 176 | 3770612.1907 | -2038194.6468 | 3442280.2714 | 2672648.861 | 6114929.1324 | 120927.8611 | 93890.5855 | 214818.4465 | 5900110.6858 | 3861916.0391 | TRUE | 29 | 139480 | -141899.9079 | 1347929.2739 | 1046556.7457 | 2394486.0196 | 3720443.1128 | 3578543.2049 | TRUE | Option 2 | 3861916.0391 | 37
| BET005-54520179 | 249 | 5334559.2925 | -2883582.1991 | 840453.3272 | 5689516.9917 | 6529970.3189 | 29525.2609 | 199873.6494 | 229398.9104 | 6300571.4085 | 3416989.2094 | TRUE | 31 | 197332.5 | -200756.1197 | 329104.9984 | 2227902.9895 | 2557007.9879 | 3972962.331 | 3772206.2113 | TRUE | Option 3 | 3772206.2113 | 38
| CTN004-15418536 | 266 | 5698766.1518 | -3080453.2729 | 1087908.4559 | 5317182.6616 | 6405091.1175 | 38218.3995 | 186793.4844 | 225011.8839 | 6180079.2336 | 3099625.9607 | TRUE | 37 | 210805 | -214462.3608 | 426003.5614 | 2082104.1865 | 2508107.7479 | 3896983.3696 | 3682521.0088 | TRUE | Option 3 | 3682521.0088 | 39
| HSM005-15416442 | 282 | 6041549.0783 | -3265743.6954 | 1847022.5403 | 4442841.7848 | 6289864.3251 | 64886.1997 | 156077.7484 | 220963.9481 | 6068900.3771 | 2803156.6817 | TRUE | 43 | 223485 | -227362.3524 | 723257.7116 | 1739729.49 | 2462987.2016 | 3826877.1236 | 3599514.7711 | TRUE | Option 3 | 3599514.7711 | 40
| HSM004-15416655 | 283 | 6062973.0112 | -3277324.3468 | 1447912.1168 | 4842604.9732 | 6290517.09 | 50865.3862 | 170121.4937 | 220986.8798 | 6069530.2102 | 2792205.8634 | TRUE | 44 | 224277.5 | -228168.6019 | 566973.9168 | 1896268.8946 | 2463242.8115 | 3827274.2786 | 3599105.6766 | TRUE | Option 3 | 3599105.6766 | 41
| MNA034-24605112 | 338 | 7241289.3207 | -3914260.1739 | 863168.4745 | 5478053.1966 | 6341221.6711 | 30323.2477 | 192444.8922 | 222768.1399 | 6118453.5311 | 2204193.3572 | TRUE | 54 | 267865 | -272512.3231 | 337999.8034 | 2145097.925 | 2483097.7285 | 3858123.9426 | 3585611.6194 | TRUE | Option 3 | 3585611.6194 | 42
| MRO008-156506029 | 365 | 7819735.5091 | -4226937.7617 | 968742.681 | 5372786.8324 | 6341529.5134 | 34032.0866 | 188746.8679 | 222778.9545 | 6118750.5589 | 1891812.7971 | TRUE | 58 | 289262.5 | -294281.059 | 379340.5869 | 2103877.6865 | 2483218.2735 | 3858311.2399 | 3564030.1809 | TRUE | Option 3 | 3564030.1809 | 43
| ECA003-15422755 | 208 | 4456178.0435 | -2408775.4916 | 2476800.3995 | 3537499.5712 | 6014299.9707 | 87010.3975 | 124272.9304 | 211283.3279 | 5803016.6429 | 3394241.1512 | TRUE | 32 | 164840 | -167699.8912 | 969866.3389 | 1385215.2795 | 2355081.6184 | 3659218.3523 | 3491518.4612 | TRUE | Option 3 | 3491518.4612 | 44
| BET005-15436909 | 233 | 4991776.3661 | -2698291.7767 | 3264789.9115 | 2714991.1797 | 5979781.0911 | 114692.5961 | 95378.078 | 210070.6741 | 5769710.4171 | 3071418.6404 | TRUE | 38 | 184652.5 | -187856.1281 | 1278427.5387 | 1063137.1652 | 2341564.7038 | 3638216.3873 | 3450360.2592 | TRUE | Option 3 | 3450360.2592 | 45
| CTN002-15418512 | 243 | 5206015.6951 | -2814098.2907 | 977356.05 | 4966671.2784 | 5944027.3284 | 34334.6756 | 174479.963 | 208814.6386 | 5735212.6898 | 2921114.3991 | TRUE | 40 | 192577.5 | -195918.6228 | 382713.4129 | 1944850.8204 | 2327564.2333 | 3616463.0951 | 3420544.4722 | TRUE | Option 3 | 3420544.4722 | 46
| EHK024-15417874 | 193 | 4134819.05 | -2235065.7206 | 2778511.4455 | 3010638.4581 | 5789149.9037 | 97609.5552 | 105764.2145 | 203373.7697 | 5585776.134 | 3350710.4134 | TRUE | 33 | 152952.5 | -155606.149 | 1088010.4524 | 1178906.8266 | 2266917.2789 | 3522232.6248 | 3366626.4757 | TRUE | Option 3 | 3366626.4757 | 47
| BGO023-197650699 | 134 | 2870807.0088 | -1551807.2879 | 3364036.5436 | 1709181.0929 | 5073217.6364 | 118179.1463 | 60043.8074 | 178222.9537 | 4894994.6827 | 3343187.3949 | TRUE | 34 | 106195 | -108037.4299 | 1317290.5685 | 669281.7109 | 1986572.2794 | 3086645.3571 | 2978607.9272 | TRUE | Option 2 | 3343187.3949 | 48
| BAS032-155216556 | 241 | 5163167.8293 | -2790936.9879 | 2784610.7798 | 3114662.0635 | 5899272.8433 | 97823.8258 | 141830.6796 | 239654.5053 | 5659618.338 | 2868681.3501 | TRUE | 42 | 190992.5 | -194306.1239 | 1090398.8318 | 1272804.5053 | 2363203.3371 | 3536069.5062 | 3341763.3824 | TRUE | Option 3 | 3341763.3824 | 49
| WND023-200942910 | 457 | 9790737.336 | -5292357.6907 | 2125928.5644 | 4086468.2694 | 6212396.8338 | 74684.2133 | 186083.2925 | 260767.5058 | 5951629.3281 | 659271.6373 | TRUE | 94 | 362172.5 | -368456.0109 | 832471.8269 | 1669932.4415 | 2502404.2684 | 3709992.5655 | 3341536.5546 | TRUE | Option 3 | 3341536.5546 | 50
| HSM004-24604904 | 493 | 10561998.9205 | -5709261.1412 | 640835.1263 | 5480850.7864 | 6121685.9126 | 22512.6413 | 192543.172 | 215055.8133 | 5906630.0993 | 197368.9581 | TRUE | 111 | 390702.5 | -397480.992 | 250938.4357 | 2146193.4062 | 2397131.8419 | 3724554.0707 | 3327073.0787 | TRUE | Option 3 | 3327073.0787 | 51
| BET006-195895491 | 214 | 4584721.6409 | -2478259.4 | 0 | 5729067.2049 | 5729067.2049 | 0 | 201263.0548 | 201263.0548 | 5527804.1501 | 3049544.7501 | TRUE | 39 | 169595 | -172537.388 | 0 | 2243390.0754 | 2243390.0754 | 3485677.1295 | 3313139.7415 | TRUE | Option 3 | 3313139.7415 | 52
| FNS021-15405600 | 241 | 5163167.8293 | -2790936.9879 | 3896162.4796 | 1861452.7377 | 5757615.2173 | 136872.8162 | 84763.9652 | 221636.7814 | 5535978.4359 | 2745041.448 | TRUE | 45 | 190992.5 | -194306.1239 | 1525660.6226 | 760681.3781 | 2286342.0008 | 3471273.2165 | 3276967.0926 | TRUE | Option 3 | 3276967.0926 | 53
| MRO007-122640081 | 430 | 9212291.1477 | -4979680.1029 | 416165.627 | 5480710.8916 | 5896876.5186 | 14619.9656 | 192538.2575 | 207158.2231 | 5689718.2956 | 710038.1927 | TRUE | 91 | 340775 | -346687.275 | 162962.2771 | 2146138.6262 | 2309100.9033 | 3587775.6154 | 3241088.3404 | TRUE | Option 3 | 3241088.3404 | 54
| BAN009-201078585 | 884 | 18938756.685 | -10237295.8394 | 622846.154 | 5941169.8891 | 6564016.0432 | 21880.6858 | 270539.8357 | 292420.5215 | 6271595.5216 | -3965700.3178 | FALSE | 2191 | 700570 | -712724.5374 | 243894.3078 | 2427854.9799 | 2671749.2877 | 3892266.7554 | 3179542.218 | TRUE | Option 3 | 3179542.218 | 55
| WND014-200942632 | 474 | 10154944.1954 | -5489228.7646 | 1973645.238 | 3980881.3943 | 5954526.6322 | 69334.4755 | 181275.2401 | 250609.7156 | 5703916.9166 | 214688.152 | TRUE | 109 | 375645 | -382162.252 | 772840.6704 | 1626784.4377 | 2399625.1081 | 3554901.5241 | 3172739.2721 | TRUE | Option 3 | 3172739.2721 | 56
| BET006-195895699 | 90 | 1928153.9611 | -1042258.6262 | 2978654.3469 | 1389196.2062 | 4367850.5531 | 104640.6076 | 48802.6868 | 153443.2943 | 4214407.2588 | 3172148.6326 | TRUE | 35 | 71325 | -72562.4529 | 1166382.4774 | 543981.9207 | 1710364.3981 | 2657486.155 | 2584923.7021 | TRUE | Option 2 | 3172148.6326 | 57
| HTN032-187419014 | 819 | 17546201.0464 | -9484553.4983 | 432769.4482 | 6032925.2991 | 6465694.7473 | 15203.2605 | 274718.0521 | 289921.3126 | 6175773.4347 | -3308780.0636 | FALSE | 2155 | 649057.5 | -660318.3215 | 169464.007 | 2465350.765 | 2634814.772 | 3830879.9753 | 3170561.6539 | TRUE | Option 3 | 3170561.6539 | 58
| ECA010-15423016 | 186 | 3984851.5197 | -2154001.1608 | 2455272.0587 | 3000005.9019 | 5455277.9605 | 86254.1034 | 105390.6911 | 191644.7945 | 5263633.166 | 3109632.0052 | TRUE | 36 | 147405 | -149962.4027 | 961436.2639 | 1174743.3266 | 2136179.5904 | 3319098.3701 | 3169135.9674 | TRUE | Option 3 | 3169135.9674 | 59
| TNA011-155056985 | 315 | 6748538.864 | -3647905.1916 | 3794633.6012 | 1853786.8091 | 5648420.4103 | 133306.0904 | 84414.886 | 217720.9763 | 5430699.434 | 1782794.2423 | TRUE | 60 | 249637.5 | -253968.5852 | 1485903.9101 | 757548.7017 | 2243452.6118 | 3404967.7985 | 3150999.2134 | TRUE | Option 3 | 3150999.2134 | 60
| BAN003-193396423 | 365 | 7819735.5091 | -4226937.7617 | 1106463.5482 | 4636025.0117 | 5742488.5599 | 38870.2429 | 211108.1602 | 249978.4031 | 5492510.1568 | 1265572.3951 | TRUE | 71 | 289262.5 | -294281.059 | 433269.3707 | 1894508.4254 | 2327777.7961 | 3414710.7638 | 3120429.7047 | TRUE | Option 3 | 3120429.7047 | 61
| BET001-15424260 | 258 | 5527374.6886 | -2987808.0617 | 3105420.3285 | 2300439.0463 | 5405859.3747 | 109093.9169 | 80814.7947 | 189908.7116 | 5215950.6631 | 2228142.6014 | TRUE | 51 | 204465 | -208012.365 | 1216021.5434 | 900806.7005 | 2116828.2439 | 3289031.1309 | 3081018.7659 | TRUE | Option 3 | 3081018.7659 | 62
| CMN001-15420462 | 238 | 5098896.0306 | -2756195.0337 | 1211549.1931 | 3934932.6986 | 5146481.8917 | 42561.9185 | 138234.8203 | 180796.7388 | 4965685.1529 | 2209490.1192 | TRUE | 53 | 188615 | -191887.3755 | 474418.8431 | 1540842.2781 | 2015261.1212 | 3131220.7704 | 2939333.395 | TRUE | Option 3 | 2939333.395 | 63
| CMN005-15420597 | 160 | 3427829.2643 | -1852904.2243 | 2751431.3341 | 2151798.5841 | 4903229.9183 | 96658.2265 | 75593.0313 | 172251.2578 | 4730978.6605 | 2878074.4362 | TRUE | 41 | 126800 | -128999.9163 | 1077406.4132 | 842602.018 | 1920008.4312 | 2983221.4871 | 2854221.5708 | TRUE | Option 2 | 2878074.4362 | 64
| ART033-15411794 | 635 | 13604197.3925 | -7353713.6403 | 526791.7171 | 4995233.339 | 5522025.0561 | 18506.278 | 175483.3528 | 193989.6307 | 5328035.4253 | -2025678.215 | FALSE | 2004 | 503237.5 | -511968.4177 | 206281.2789 | 1956035.1618 | 2162316.4407 | 3359708.6154 | 2847740.1976 | TRUE | Option 3 | 2847740.1976 | 65
| BAS011-164206976 | 536 | 11483228.0353 | -6207229.1515 | 194606.4379 | 5319849.7881 | 5514456.226 | 6836.5555 | 242247.1187 | 249083.6743 | 5265372.5517 | -941856.5998 | FALSE | 1592 | 424780 | -432149.7195 | 76204.0548 | 2173952.9489 | 2250157.0037 | 3264299.2222 | 2832149.5027 | TRUE | Option 3 | 2832149.5027 | 66
| GLE013-15407017 | 406 | 8698116.7581 | -4701744.4692 | 3553364.0872 | 1670921.8246 | 5224285.9118 | 124830.2534 | 76087.8622 | 200918.1156 | 5023367.7962 | 321623.327 | TRUE | 104 | 321755 | -327337.2876 | 1391427.5121 | 682821.0519 | 2074248.5639 | 3150037.3479 | 2822700.0603 | TRUE | Option 3 | 2822700.0603 | 67
| GHP011-187048453 | 521 | 11161869.0417 | -6033519.3805 | 1902511.7348 | 3484862.0813 | 5387373.8161 | 66835.5441 | 158688.2773 | 225523.8213 | 5161849.9948 | -871669.3857 | FALSE | 1535 | 412892.5 | -420055.9774 | 744986.1891 | 1424086.4874 | 2169072.6765 | 3218301.1396 | 2798245.1622 | TRUE | Option 3 | 2798245.1622 | 68
| LV006-15406376 | 371 | 7948279.1065 | -4296421.6702 | 1864376.8528 | 3242441.2403 | 5106818.0931 | 65495.8595 | 147649.2907 | 213145.1502 | 4893672.9429 | 597251.2727 | TRUE | 95 | 294017.5 | -299118.5559 | 730053.3191 | 1325021.3778 | 2055074.6969 | 3051743.3962 | 2752624.8403 | TRUE | Option 3 | 2752624.8403 | 69
| CHA005-56710238 | 202 | 4327634.4461 | -2339291.5832 | 441565.2458 | 4288326.2617 | 4729891.5076 | 15512.2583 | 150649.5931 | 166161.8514 | 4563729.6562 | 2224438.0729 | TRUE | 52 | 160085 | -162862.3943 | 172908.2684 | 1679224.2492 | 1852132.5176 | 2877758.99 | 2714896.5957 | TRUE | Option 3 | 2714896.5957 | 70
| FNS011-15405543 | 341 | 7305561.1195 | -3949002.1281 | 2336322.8142 | 2641671.4775 | 4977994.2917 | 82075.3972 | 120292.3634 | 202367.7606 | 4775626.5311 | 826624.403 | TRUE | 85 | 270242.5 | -274931.0716 | 914858.0784 | 1079517.2284 | 1994375.3068 | 2983618.9849 | 2708687.9133 | TRUE | Option 3 | 2708687.9133 | 71
| BAN003-154067153 | 168 | 3599220.7275 | -1945549.4355 | 3051652.1177 | 1513719.8943 | 4565372.012 | 107205.031 | 68929.443 | 176134.4741 | 4389237.538 | 2443688.1024 | TRUE | 47 | 133140 | -135449.9121 | 1194966.9692 | 618580.5914 | 1813547.5606 | 2751824.4514 | 2616374.5393 | TRUE | Option 3 | 2616374.5393 | 72
| CMN003-15420649 | 166 | 3556372.8617 | -1922388.1327 | 2108174.0958 | 2354852.0435 | 4463026.1393 | 74060.496 | 82726.332 | 156786.828 | 4306239.3113 | 2383851.1785 | TRUE | 48 | 131555 | -133837.4131 | 825519.526 | 922113.7603 | 1747633.2864 | 2715392.8529 | 2581555.4398 | TRUE | Option 3 | 2581555.4398 | 73
| MRO007-15420070 | 448 | 9597921.9399 | -5188131.8281 | 803554.8032 | 3962369.3164 | 4765924.1196 | 28229.0098 | 139198.6731 | 167427.6829 | 4598496.4367 | -589635.3914 | FALSE | 1232 | 355040 | -361199.7656 | 314656.2618 | 1551585.9182 | 1866242.18 | 2899681.9396 | 2538482.174 | TRUE | Option 3 | 2538482.174 | 74
| MRO008-15411648 | 220 | 4713265.2384 | -2547743.3085 | 1697872.9986 | 2746918.8108 | 4444791.8095 | 59646.5522 | 96499.7008 | 156146.2531 | 4288645.5564 | 1740902.2479 | TRUE | 63 | 174350 | -177374.8849 | 664853.6835 | 1075639.3978 | 1740493.0813 | 2704298.7281 | 2526923.8432 | TRUE | Option 3 | 2526923.8432 | 75
| BMH003-155324907 | 380 | 8141094.5026 | -4400647.5328 | 38746.5628 | 4731166.8816 | 4769913.4444 | 1361.173 | 215440.584 | 216801.757 | 4553111.6874 | 152464.1546 | TRUE | 116 | 301150 | -306374.8012 | 15172.3922 | 1933388.085 | 1948560.4771 | 2821352.9673 | 2514978.1661 | TRUE | Option 3 | 2514978.1661 | 76
| HSM003-24601084 | 392 | 8398181.6974 | -4539615.3496 | 683610.3768 | 3942958.805 | 4626569.1818 | 24015.3428 | 138516.7787 | 162532.1215 | 4464037.0603 | -75578.2893 | FALSE | 339 | 310660 | -316049.7949 | 267688.3828 | 1543985.1436 | 1811673.5263 | 2814895.6555 | 2498845.8606 | TRUE | Option 3 | 2498845.8606 | 77
| SHN011-24605252 | 655 | 14032676.0506 | -7585326.6683 | 596118.4033 | 4377620.3544 | 4973738.7578 | 20941.7356 | 153786.509 | 174728.2447 | 4799010.5131 | -2786316.1552 | FALSE | 2108 | 519087.5 | -528093.4073 | 233428.2462 | 1714190.0602 | 1947618.3064 | 3026120.4514 | 2498027.0441 | TRUE | Option 3 | 2498027.0441 | 78
| KYM001-15421988 | 828 | 17739016.4425 | -9588779.3609 | 685817.1061 | 4496675.2645 | 5182492.3706 | 24092.8655 | 157968.9272 | 182061.7927 | 5000430.5779 | -4588348.783 | FALSE | 2206 | 656190 | -667574.5667 | 268552.4946 | 1760809.6222 | 2029362.1168 | 3153130.2538 | 2485555.6871 | TRUE | Option 3 | 2485555.6871 | 79
| GSB011-24597032 | 227 | 4863232.7687 | -2628807.8683 | 483892.4941 | 3954231.1846 | 4438123.6787 | 16999.2214 | 180061.684 | 197060.9053 | 4241062.7734 | 1612254.9051 | TRUE | 66 | 179897.5 | -183018.6312 | 189482.7866 | 1615893.8479 | 1805376.6346 | 2632747.0441 | 2449728.4129 | TRUE | Option 3 | 2449728.4129 | 80
| SHP014-24602550 | 341 | 7305561.1195 | -3949002.1281 | 675254.3335 | 3785674.7294 | 4460929.0629 | 23721.7936 | 132991.3637 | 156713.1574 | 4304215.9055 | 355213.7774 | TRUE | 102 | 270242.5 | -274931.0716 | 264416.3205 | 1482395.792 | 1746812.1125 | 2714116.9504 | 2439185.8788 | TRUE | Option 3 | 2439185.8788 | 81
| BET006-195895661 | 160 | 3427829.2643 | -1852904.2243 | 1011969.4175 | 3165061.5386 | 4177030.9561 | 35550.6488 | 111189.1223 | 146739.7711 | 4030291.185 | 2177386.9607 | TRUE | 55 | 126800 | -128999.9163 | 396267.3271 | 1239375.8687 | 1635643.1957 | 2541387.7604 | 2412387.8441 | TRUE | Option 3 | 2412387.8441 | 82
| BGO013-197650863 | 132 | 2827959.143 | -1528645.9851 | 2706533.7629 | 1270904.6095 | 3977438.3723 | 95080.9676 | 44647.0839 | 139728.0514 | 3837710.3209 | 2309064.3358 | TRUE | 49 | 104610 | -106424.9309 | 1059825.407 | 497661.2572 | 1557486.6642 | 2419951.7081 | 2313526.7772 | TRUE | Option 3 | 2313526.7772 | 83
| BAN009-77240394 | 436 | 9340834.7451 | -5049164.0113 | 47320.0856 | 4441967.7692 | 4489287.8548 | 1662.3622 | 202271.4807 | 203933.8429 | 4285354.0119 | -763809.9994 | FALSE | 1434 | 345530 | -351524.7719 | 18529.6151 | 1815207.067 | 1833736.6822 | 2655551.1727 | 2304026.4008 | TRUE | Option 3 | 2304026.4008 | 84
| ART034-15411844 | 338 | 7241289.3207 | -3914260.1739 | 1093068.1232 | 3113491.3682 | 4206559.4914 | 38399.6594 | 109377.4539 | 147777.1133 | 4058782.3781 | 144522.2042 | TRUE | 118 | 267865 | -272512.3231 | 428023.9857 | 1219182.0039 | 1647205.9896 | 2559353.5018 | 2286841.1787 | TRUE | Option 3 | 2286841.1787 | 85
| HSM002-24600694 | 666 | 14268339.3125 | -7712713.8338 | 180668.4823 | 4455824.0946 | 4636492.577 | 6346.9129 | 156533.819 | 162880.7319 | 4473611.845 | -3239101.9887 | FALSE | 2152 | 527805 | -536962.1515 | 70746.2255 | 1744813.1073 | 1815559.3328 | 2820933.2442 | 2283971.0927 | TRUE | Option 3 | 2283971.0927 | 86
| HTN034-182145724 | 484 | 10369183.5244 | -5605035.2786 | 514954.6515 | 3928851.5024 | 4443806.154 | 18090.44 | 178905.9831 | 196996.4231 | 4246809.7309 | -1358225.5477 | FALSE | 1825 | 383570 | -390224.7467 | 201646.1168 | 1605522.4583 | 1807168.5751 | 2636637.5789 | 2246412.8322 | TRUE | Option 3 | 2246412.8322 | 87
| HTN034-108340859 | 635 | 13604197.3925 | -7353713.6403 | 171136.2697 | 4468937.1771 | 4640073.4468 | 6012.0448 | 203499.572 | 209511.6167 | 4430561.8301 | -2923151.8102 | FALSE | 2123 | 503237.5 | -511968.4177 | 67013.5984 | 1826228.097 | 1893241.6954 | 2746831.7514 | 2234863.3337 | TRUE | Option 3 | 2234863.3337 | 88
| FNS013-15405406 | 441 | 9447954.4096 | -5107067.2683 | 2110233.3082 | 2162162.8299 | 4272396.1381 | 74132.8364 | 98457.2378 | 172590.0742 | 4099806.0638 | -1007261.2045 | FALSE | 1634 | 349492.5 | -355556.0192 | 826325.8732 | 883566.35 | 1709892.2232 | 2562503.9149 | 2206947.8957 | TRUE | Option 3 | 2206947.8957 | 89
| MLN013-196479162 | 226 | 4841808.8358 | -2617227.2169 | 2878606.8001 | 1003496.1366 | 3882102.9367 | 101125.9211 | 45695.6601 | 146821.5812 | 3735281.3555 | 1118054.1386 | TRUE | 77 | 179105 | -182212.3817 | 1127205.8252 | 410078.0045 | 1537283.8297 | 2344819.107 | 2162606.7252 | TRUE | Option 3 | 2162606.7252 | 90
| GHP022-188587433 | 623 | 13347110.1977 | -7214745.8235 | 633704.0164 | 3838507.2571 | 4472211.2735 | 22262.1243 | 174792.0261 | 197054.1504 | 4275157.123 | -2939588.7004 | FALSE | 2125 | 493727.5 | -502293.424 | 248146.0332 | 1568603.3447 | 1816749.378 | 2655461.8955 | 2153168.4715 | TRUE | Option 3 | 2153168.4715 | 91
| BMH004-15408369 | 234 | 5013200.299 | -2709872.4281 | 2477058.5516 | 1324583.5235 | 3801642.0751 | 87019.4664 | 60316.8426 | 147336.3089 | 3654305.7662 | 944433.3381 | TRUE | 80 | 185445 | -188662.3776 | 969967.4261 | 541290.1439 | 1511257.57 | 2290384.5052 | 2101722.1276 | TRUE | Option 3 | 2101722.1276 | 92
| SHP012-15432576 | 592 | 12682968.2778 | -6855745.63 | 721409.0825 | 3516662.771 | 4238071.8535 | 25343.2174 | 123540.9303 | 148884.1477 | 4089187.7059 | -2766557.9242 | FALSE | 2106 | 469160 | -477299.6902 | 282489.6127 | 1377055.9983 | 1659545.611 | 2578526.2425 | 2101226.5523 | TRUE | Option 3 | 2101226.5523 | 93
| TQY032-192995307 | 236 | 5056048.1648 | -2733033.7309 | 502782.6065 | 3317287.8153 | 3820070.4218 | 17662.834 | 151057.5387 | 168720.3727 | 3651350.0491 | 918316.3182 | TRUE | 81 | 187030 | -190274.8765 | 196879.7832 | 1355607.3791 | 1552487.1624 | 2267583.2595 | 2077308.3829 | TRUE | Option 3 | 2077308.3829 | 94
| BMH005-15408219 | 319 | 6834234.5956 | -3694227.7973 | 2321064.7884 | 1511233.0372 | 3832297.8256 | 81539.3803 | 68816.2004 | 150355.5807 | 3681942.2449 | -12285.5524 | FALSE | 253 | 252807.5 | -257193.5831 | 908883.3355 | 617564.339 | 1526447.6745 | 2305850.1511 | 2048656.568 | TRUE | Option 3 | 2048656.568 | 95
| MRO005-24606858 | 220 | 4713265.2384 | -2547743.3085 | 332595.1786 | 3295235.5417 | 3627830.7203 | 11684.1223 | 115762.156 | 127446.2782 | 3500384.4421 | 952641.1336 | TRUE | 79 | 174350 | -177374.8849 | 130237.7326 | 1290349.4489 | 1420587.1815 | 2207243.5388 | 2029868.6539 | TRUE | Option 3 | 2029868.6539 | 96
| FNS022-24604096 | 450 | 9640769.8057 | -5211293.1309 | 1031197.4942 | 2902084.2855 | 3933281.7797 | 36226.1343 | 132150.6404 | 168376.7747 | 3764905.005 | -1446388.1259 | FALSE | 1860 | 356625 | -362812.2645 | 403796.6638 | 1185934.7429 | 1589731.4067 | 2343550.373 | 1980738.1085 | TRUE | Option 3 | 1980738.1085 | 97
| MLN022-196479342 | 180 | 3856307.9223 | -2084517.2524 | 1877985.0124 | 1553078.7536 | 3431063.7661 | 65973.9163 | 70721.7061 | 136695.6224 | 3294368.1436 | 1209850.8913 | TRUE | 72 | 142650 | -145124.9058 | 735382.0069 | 634664.5621 | 1370046.569 | 2061017.1971 | 1915892.2913 | TRUE | Option 3 | 1915892.2913 | 98
| BAN015-24611936 | 392 | 8398181.6974 | -4539615.3496 | 1071835.6628 | 2644347.86 | 3716183.5228 | 37653.7597 | 120414.2364 | 158067.9961 | 3558115.5267 | -981499.8229 | FALSE | 1611 | 310660 | -316049.7949 | 419709.7717 | 1080610.9302 | 1500320.7019 | 2215862.8209 | 1899813.026 | TRUE | Option 3 | 1899813.026 | 99
| NHL015-154154899 | 423 | 9062323.6174 | -4898615.5431 | 12981.4457 | 3652231.0527 | 3665212.4984 | 456.0403 | 128303.4659 | 128759.5061 | 3536452.9923 | -1362162.5508 | FALSE | 1826 | 335227.5 | -341043.5287 | 5083.2789 | 1430141.8719 | 1435225.1508 | 2229987.3476 | 1888943.8189 | TRUE | Option 3 | 1888943.8189 | 100
| MRO004-15420205 | 160 | 3427829.2643 | -1852904.2243 | 1223825.6398 | 2090657.9312 | 3314483.571 | 42993.1921 | 73445.1503 | 116438.3424 | 3198045.2287 | 1345141.0043 | TRUE | 69 | 126800 | -128999.9163 | 479226.0583 | 818660.5404 | 1297886.5987 | 2016596.9723 | 1887597.056 | TRUE | Option 3 | 1887597.056 | 101
| MLN021-24600176 | 122 | 2613719.814 | -1412839.471 | 2788776.3542 | 480033.137 | 3268809.4912 | 97970.1631 | 21859.009 | 119829.172 | 3148980.3191 | 1736140.8481 | TRUE | 64 | 96685 | -98362.4362 | 1092029.9888 | 196165.2105 | 1288195.1993 | 1980614.2918 | 1882251.8557 | TRUE | Option 3 | 1882251.8557 | 102
| BET004-15424334 | 205 | 4391906.2448 | -2374033.5374 | 1761074.0644 | 1579430.1966 | 3340504.261 | 61866.8159 | 55485.6375 | 117352.4534 | 3223151.8076 | 849118.2702 | TRUE | 84 | 162462.5 | -165281.1427 | 689601.9783 | 618473.811 | 1308075.7893 | 2032428.4717 | 1867147.329 | TRUE | Option 3 | 1867147.329 | 103
| BBD021-24613487 | 121 | 2592295.8811 | -1401258.8196 | 1739335.4296 | 1488631.6545 | 3227967.0841 | 61103.1341 | 52295.8701 | 113399.0042 | 3114568.0799 | 1713309.2602 | TRUE | 65 | 95892.5 | -97556.1867 | 681089.5563 | 582918.8872 | 1264008.4435 | 1963958.6406 | 1866402.454 | TRUE | Option 3 | 1866402.454 | 104
| ART023-15411707 | 327 | 7005626.0588 | -3786873.0085 | 817583.3262 | 2654344.8312 | 3471928.1575 | 28721.8341 | 93247.562 | 121969.3961 | 3349958.7614 | -436914.2471 | FALSE | 1012 | 259147.5 | -263643.5789 | 320149.5556 | 1039389.2475 | 1359538.8032 | 2112389.3543 | 1848745.7754 | TRUE | Option 3 | 1848745.7754 | 105
| HSM009-15416379 | 252 | 5398831.0912 | -2918324.1533 | 1400585.5778 | 1936157.6721 | 3336743.25 | 49202.7972 | 68017.5313 | 117220.3285 | 3219522.9215 | 301198.7682 | TRUE | 105 | 199710 | -203174.8681 | 548441.7747 | 758161.2767 | 1306603.0513 | 2030140.1986 | 1826965.3305 | TRUE | Option 3 | 1826965.3305 | 106
| BAS022-164206998 | 294 | 6298636.2731 | -3404711.5122 | 377702.0032 | 3069990.8261 | 3447692.8293 | 13268.7323 | 139796.5096 | 153065.2419 | 3294627.5874 | -110083.9248 | FALSE | 403 | 232995 | -237037.3462 | 147900.6782 | 1254549.6349 | 1402450.3132 | 2045242.5161 | 1808205.1699 | TRUE | Option 3 | 1808205.1699 | 107
| RCT013-24605168 | 61 | 1306859.907 | -706419.7355 | 1160458.9188 | 1410923.4725 | 2571382.3913 | 40767.109 | 49565.9691 | 90333.0781 | 2481049.3132 | 1774629.5777 | TRUE | 61 | 48342.5 | -49181.2181 | 454412.8962 | 552489.891 | 1006902.7872 | 1564479.6041 | 1515298.386 | TRUE | Option 2 | 1774629.5777 | 108
| HSM006-201967868 | 234 | 5013200.299 | -2709872.4281 | 783929.676 | 2439092.8627 | 3223022.5388 | 27539.5759 | 85685.7256 | 113225.3015 | 3109797.2372 | 399924.8091 | TRUE | 100 | 185445 | -188662.3776 | 306971.4479 | 955100.8088 | 1262072.2567 | 1960950.282 | 1772287.9045 | TRUE | Option 3 | 1772287.9045 | 109
| BGO023-143335276 | 131 | 2806535.2101 | -1517065.3337 | 94954.9702 | 2988869.8286 | 3083824.7989 | 3335.7834 | 104999.4791 | 108335.2625 | 2975489.5364 | 1458424.2027 | TRUE | 67 | 103817.5 | -105618.6815 | 37182.4994 | 1170382.6592 | 1207565.1586 | 1876259.6402 | 1770640.9588 | TRUE | Option 3 | 1770640.9588 | 110
| CHA005-24606076 | 200 | 4284786.5803 | -2316130.2804 | 697650.2542 | 2472604.8079 | 3170255.0621 | 24508.5659 | 86863.0056 | 111371.5716 | 3058883.4905 | 742753.2101 | TRUE | 88 | 158500 | -161249.8953 | 273186.1227 | 968223.4277 | 1241409.5504 | 1928845.5118 | 1767595.6164 | TRUE | Option 3 | 1767595.6164 | 111
| CMN004-24614626 | 293 | 6277212.3402 | -3393130.8608 | 184049.333 | 3106512.8044 | 3290562.1374 | 6465.6827 | 109132.2958 | 115597.9785 | 3174964.1588 | -218166.702 | FALSE | 627 | 232202.5 | -236231.0967 | 72070.1001 | 1216449.3355 | 1288519.4356 | 2002042.7018 | 1765811.6051 | TRUE | Option 3 | 1765811.6051 | 112
| WPD033-15399135 | 387 | 8291062.0329 | -4481712.0926 | 1715754.7911 | 1744513.0477 | 3460267.8389 | 60274.7425 | 79438.9459 | 139713.6884 | 3320554.1505 | -1161157.9421 | FALSE | 1725 | 306697.5 | -312018.5475 | 671855.8419 | 712894.0545 | 1384749.8964 | 2075517.9425 | 1763499.395 | TRUE | Option 3 | 1763499.395 | 113
| MRO005-15420092 | 81 | 1735338.565 | -938032.7636 | 1700422.8595 | 1082095.421 | 2782518.2804 | 59736.1293 | 38014.1866 | 97750.3159 | 2684767.9645 | 1746735.201 | TRUE | 62 | 64192.5 | -65306.2076 | 665852.1589 | 423727.2912 | 1089579.4501 | 1692938.8303 | 1627632.6227 | TRUE | Option 2 | 1746735.201 | 114
| HSM002-24601420 | 462 | 9897857.0005 | -5350260.9477 | 346868.6678 | 3127922.0923 | 3474790.7601 | 12185.5522 | 109884.4075 | 122069.9598 | 3352720.8003 | -1997540.1474 | FALSE | 1997 | 366135 | -372487.2583 | 135826.9504 | 1224832.7917 | 1360659.7421 | 2114131.018 | 1741643.7598 | TRUE | Option 3 | 1741643.7598 | 115
| NKA006-15424841 | 514 | 11011901.5114 | -5952454.8207 | 775062.6464 | 2765164.2205 | 3540226.8669 | 27228.0758 | 97140.665 | 124368.7407 | 3415858.1261 | -2536596.6945 | FALSE | 2083 | 407345 | -414412.231 | 303499.2934 | 1082783.9415 | 1386283.2349 | 2153943.632 | 1739531.4009 | TRUE | Option 3 | 1739531.4009 | 116
| MRO005-24606286 | 242 | 5184591.7622 | -2802517.6393 | 246964.6202 | 2888580.6759 | 3135545.2961 | 8675.9069 | 101476.305 | 110152.2119 | 3025393.0842 | 222875.4449 | TRUE | 107 | 191785 | -195112.3734 | 96706.4896 | 1131111.3989 | 1227817.8884 | 1907727.4076 | 1712615.0343 | TRUE | Option 3 | 1712615.0343 | 117
| HSM003-15416492 | 188 | 4027699.3855 | -2177162.4636 | 1302411.2917 | 1714068.7664 | 3016480.0581 | 45753.9187 | 60215.5122 | 105969.4309 | 2910510.6272 | 733348.1636 | TRUE | 90 | 148990 | -151574.9016 | 509998.6545 | 671195.6278 | 1181194.2822 | 1835285.7759 | 1683710.8742 | TRUE | Option 3 | 1683710.8742 | 118
| GHP012-190579518 | 405 | 8676692.8252 | -4690163.8178 | 1548288.3061 | 1783995.7606 | 3332284.0667 | 54391.6179 | 81236.8488 | 135628.4667 | 3196655.6 | -1493508.2178 | FALSE | 1880 | 320962.5 | -326531.0381 | 606279.259 | 729028.6379 | 1335307.8968 | 1996976.1698 | 1670445.1317 | TRUE | Option 3 | 1670445.1317 | 119
| BAN008-15414979 | 463 | 9919280.9335 | -5361841.5991 | 313517.0545 | 3100221.2859 | 3413738.3404 | 11013.9047 | 141173.0977 | 152187.0024 | 3261551.338 | -2100290.2611 | FALSE | 2015 | 366927.5 | -373293.5077 | 122767.1143 | 1266903.2915 | 1389670.4058 | 2024067.9346 | 1650774.4269 | TRUE | Option 3 | 1650774.4269 | 120
| BET007-132469306 | 129 | 2763687.3443 | -1493904.0309 | 58010.2765 | 2821668.2283 | 2879678.5048 | 2037.9104 | 99125.6599 | 101163.5703 | 2778514.9345 | 1284610.9037 | TRUE | 70 | 102232.5 | -104006.1825 | 22715.6837 | 1104909.8 | 1127625.4837 | 1752053.0211 | 1648046.8386 | TRUE | Option 3 | 1648046.8386 | 121
| BAN006-193339124 | 580 | 12425881.0829 | -6716777.8132 | 226189.1523 | 3338991.4077 | 3565180.56 | 7946.0614 | 152045.8434 | 159991.9048 | 3405188.6552 | -3311589.158 | FALSE | 2156 | 459650 | -467624.6965 | 88571.2248 | 1364476.5372 | 1453047.762 | 2112132.798 | 1644508.1015 | TRUE | Option 3 | 1644508.1015 | 122
| SHL004-24604082 | 341 | 7305561.1195 | -3949002.1281 | 464505.9408 | 2656392.3273 | 3120898.2681 | 16318.1686 | 93319.4908 | 109637.6595 | 3011260.6086 | -937741.5195 | FALSE | 1589 | 270242.5 | -274931.0716 | 181891.3935 | 1040191.0067 | 1222082.4003 | 1898815.8678 | 1623884.7963 | TRUE | Option 3 | 1623884.7963 | 123
| CMN003-164373106 | 234 | 5013200.299 | -2709872.4281 | 262317.6231 | 2698969.3698 | 2961286.9929 | 9215.2604 | 94815.2292 | 104030.4896 | 2857256.5033 | 147384.0752 | TRUE | 117 | 185445 | -188662.3776 | 102718.4236 | 1056863.3394 | 1159581.7631 | 1801705.2298 | 1613042.8522 | TRUE | Option 3 | 1613042.8522 | 124
| NKA004-15424817 | 237 | 5077472.0977 | -2744614.3823 | 1324555.2204 | 1638287.8114 | 2962843.0319 | 46531.8385 | 57553.315 | 104085.1535 | 2858757.8783 | 114143.4961 | TRUE | 120 | 187822.5 | -191081.126 | 518669.7816 | 641521.2958 | 1160191.0773 | 1802651.9545 | 1611570.8285 | TRUE | Option 3 | 1611570.8285 | 125
| FNS012-15405393 | 260 | 5570222.5544 | -3010969.3645 | 1464307.9572 | 1538763.3626 | 3003071.3198 | 51441.3747 | 70069.8339 | 121511.2086 | 2881560.1113 | -129409.2533 | FALSE | 458 | 206050 | -209624.864 | 573394.2056 | 628814.5875 | 1202208.793 | 1800862.5268 | 1591237.6629 | TRUE | Option 3 | 1591237.6629 | 126
| GSB014-194965541 | 175 | 3749188.2578 | -2026613.9954 | 1073874.2834 | 1808468.4705 | 2882342.7539 | 37725.3768 | 82351.2493 | 120076.6261 | 2762266.1278 | 735652.1325 | TRUE | 89 | 138687.5 | -141093.6584 | 420508.0554 | 739029.3939 | 1159537.4493 | 1722805.3046 | 1581711.6462 | TRUE | Option 3 | 1581711.6462 | 127
| TNA021-154751071 | 135 | 2892230.9417 | -1563387.9393 | 2239101.6278 | 543218.8162 | 2782320.444 | 78660.0013 | 24736.261 | 103396.2623 | 2678924.1817 | 1115536.2424 | TRUE | 78 | 106987.5 | -108843.6794 | 876788.1734 | 221985.9948 | 1098774.1681 | 1683546.2758 | 1574702.5965 | TRUE | Option 3 | 1574702.5965 | 128
| GHP021-187048221 | 328 | 7027049.9917 | -3798453.6599 | 1302543.9577 | 1673641.1247 | 2976185.0824 | 45758.5793 | 76211.6895 | 121970.2688 | 2854214.8136 | -944238.8462 | FALSE | 1594 | 259940 | -264449.8284 | 510050.6039 | 683932.2919 | 1193982.8958 | 1782202.1866 | 1517752.3582 | TRUE | Option 3 | 1517752.3582 | 129
| SHL001-15428689 | 440 | 9426530.4767 | -5095486.6169 | 191654.561 | 2882921.3594 | 3074575.9204 | 6732.8556 | 101277.4923 | 108010.3479 | 2966565.5725 | -2128921.0444 | FALSE | 2020 | 348700 | -354749.7698 | 75048.1579 | 1128895.3218 | 1203943.4797 | 1870632.4407 | 1515882.671 | TRUE | Option 3 | 1515882.671 | 130
| NKA002-15424741 | 366 | 7841159.442 | -4238518.4131 | 641919.2123 | 2328630.0625 | 2970549.2749 | 22550.7254 | 81805.1496 | 104355.8751 | 2866193.3998 | -1372325.0134 | FALSE | 1831 | 290055 | -295087.3085 | 251362.9425 | 911845.7481 | 1163208.6906 | 1807340.5843 | 1512253.2758 | TRUE | Option 3 | 1512253.2758 | 131
| STL007-87836091 | 422 | 9040899.6845 | -4887034.8917 | 752528.4109 | 2278424.12 | 3030952.5309 | 26436.4444 | 80041.4068 | 106477.8512 | 2924474.6797 | -1962560.2119 | FALSE | 1992 | 334435 | -340237.2792 | 294675.3299 | 892186.0882 | 1186861.418 | 1844091.1129 | 1503853.8337 | TRUE | Option 3 | 1503853.8337 | 132
| WBE033-203217267 | 506 | 10840510.0482 | -5859809.6094 | 2059420.9067 | 1085767.6175 | 3145188.5242 | 72347.7886 | 49442.012 | 121789.8005 | 3023398.7237 | -2836410.8858 | FALSE | 2110 | 401005 | -407962.2352 | 806428.7358 | 443698.1885 | 1250126.9242 | 1895061.6 | 1487099.3648 | TRUE | Option 3 | 1487099.3648 | 133
| BAN008-193386514 | 223 | 4777537.0371 | -2582485.2627 | 180487.1381 | 2617722.8955 | 2798210.0336 | 6340.5423 | 119201.8298 | 125542.3721 | 2672667.6615 | 90182.3988 | TRUE | 121 | 176727.5 | -179793.6333 | 70675.2146 | 1069730.6568 | 1140405.8715 | 1657804.1621 | 1478010.5288 | TRUE | Option 3 | 1478010.5288 | 134
| NHL031-158093033 | 496 | 10626270.7192 | -5744003.0954 | 8184.5953 | 3066459.7367 | 3074644.3321 | 287.5262 | 107725.2251 | 108012.7512 | 2966631.5808 | -2777371.5146 | FALSE | 2107 | 393080 | -399899.7405 | 3204.9266 | 1200765.3417 | 1203970.2683 | 1870674.0637 | 1470774.3233 | TRUE | Option 3 | 1470774.3233 | 135
| MNA034-15421279 | 232 | 4970352.4332 | -2686711.1253 | 902208.0518 | 1798424.7906 | 2700632.8424 | 31694.7144 | 63178.9529 | 94873.6673 | 2605759.1751 | -80951.9502 | FALSE | 353 | 183860 | -187049.8786 | 353286.9343 | 704227.7883 | 1057514.7226 | 1643118.1198 | 1456068.2412 | TRUE | Option 3 | 1456068.2412 | 136
| GSB011-24613746 | 185 | 3963427.5868 | -2142420.5094 | 1256545.6812 | 1346273.1298 | 2602818.811 | 44142.6524 | 61304.5104 | 105447.1628 | 2497371.6481 | 354951.1388 | TRUE | 103 | 146612.5 | -149156.1532 | 492038.5832 | 550153.5865 | 1042192.1697 | 1560626.6413 | 1411470.4881 | TRUE | Option 3 | 1411470.4881 | 137
| TQY031-156447550 | 388 | 8312485.9658 | -4493292.744 | 1465968.3064 | 1400181.8738 | 2866150.1802 | 51499.703 | 63759.3237 | 115259.0267 | 2750891.1535 | -1742401.5905 | FALSE | 1947 | 307490 | -312824.797 | 574044.3656 | 572183.3576 | 1146227.7232 | 1719922.457 | 1407097.66 | TRUE | Option 3 | 1407097.66 | 138
| MLN021-196479276 | 107 | 2292360.8205 | -1239129.7 | 2211328.3153 | 246616.6715 | 2457944.9868 | 77684.3203 | 11230.0498 | 88914.3701 | 2369030.6166 | 1129900.9166 | TRUE | 76 | 84797.5 | -86268.694 | 865912.6902 | 100779.7328 | 966692.423 | 1491252.5637 | 1404983.8697 | TRUE | Option 3 | 1404983.8697 | 139
| MNA024-15421140 | 178 | 3813460.0565 | -2061355.9496 | 1239563.9734 | 1288037.3381 | 2527601.3115 | 43546.0823 | 45248.9594 | 88795.0417 | 2438806.2698 | 377450.3203 | TRUE | 101 | 141065 | -143512.4069 | 485388.8803 | 504370.0969 | 989758.9772 | 1537842.3344 | 1394329.9275 | TRUE | Option 3 | 1394329.9275 | 140
| ECA001-24613400 | 54 | 1156892.3767 | -625355.1757 | 1194201.1785 | 890083.0818 | 2084284.2603 | 41952.48 | 31268.7622 | 73221.2422 | 2011063.0182 | 1385707.8424 | TRUE | 68 | 42795 | -43537.4717 | 467625.7017 | 348539.0345 | 816164.7362 | 1268119.5241 | 1224582.0524 | TRUE | Option 2 | 1385707.8424 | 141
| BET006-195895635 | 266 | 5698766.1518 | -3080453.2729 | 408664.483 | 2211500.9146 | 2620165.3975 | 14356.4492 | 77690.3838 | 92046.833 | 2528118.5646 | -552334.7084 | FALSE | 1182 | 210805 | -214462.3608 | 160024.9766 | 865980.2767 | 1026005.2533 | 1594160.1442 | 1379697.7834 | TRUE | Option 3 | 1379697.7834 | 142
| CTN002-24605474 | 354 | 7584072.2472 | -4099550.5963 | 139038.4808 | 2589880.2128 | 2728918.6935 | 4884.4443 | 90982.9095 | 95867.3538 | 2633051.3397 | -1466499.2566 | FALSE | 1866 | 280545 | -285412.3148 | 54444.7354 | 1014146.1704 | 1068590.9058 | 1660327.7878 | 1374915.473 | TRUE | Option 3 | 1374915.473 | 143
| TQY021-192995237 | 545 | 11676043.4314 | -6311455.0141 | 1542475.3808 | 1472326.6973 | 3014802.0781 | 54187.4089 | 67044.5434 | 121231.9523 | 2893570.1258 | -3417884.8883 | FALSE | 2165 | 431912.5 | -439405.9648 | 604003.0318 | 601665.29 | 1205668.3217 | 1809133.7564 | 1369727.7916 | TRUE | Option 3 | 1369727.7916 | 144
| CTN001-24604306 | 353 | 7562648.3143 | -4087969.9449 | 491362.4154 | 2222381.4517 | 2713743.8671 | 17261.6409 | 78072.6188 | 95334.2597 | 2618409.6074 | -1469560.3375 | FALSE | 1868 | 279752.5 | -284606.0653 | 192407.8609 | 870240.8811 | 1062648.7421 | 1651095.125 | 1366489.0597 | TRUE | Option 3 | 1366489.0597 | 145
| MNA021-164301884 | 327 | 7005626.0588 | -3786873.0085 | 795240.7119 | 1872666.6255 | 2667907.3373 | 27936.9345 | 65787.0805 | 93724.015 | 2574183.3223 | -1212689.6861 | FALSE | 1758 | 259147.5 | -263643.5789 | 311400.6272 | 733299.4311 | 1044700.0583 | 1623207.2791 | 1359563.7002 | TRUE | Option 3 | 1359563.7002 | 146
| CTN003-47810169 | 408 | 8740964.6239 | -4724905.772 | 80694.5983 | 2655847.5638 | 2736542.1621 | 2834.8143 | 93300.3532 | 96135.1675 | 2640406.9946 | -2084498.7774 | FALSE | 2012 | 323340 | -328949.7865 | 31598.4181 | 1039977.688 | 1071576.1062 | 1664966.0559 | 1336016.2694 | TRUE | Option 3 | 1336016.2694 | 147
| BAS023-24612761 | 261 | 5591646.4873 | -3022550.0159 | 436507.1279 | 2162691.9963 | 2599199.1242 | 15334.5658 | 98481.3342 | 113815.9 | 2485383.2243 | -537166.7917 | FALSE | 1160 | 206842.5 | -210431.1134 | 170927.6089 | 883782.5935 | 1054710.2025 | 1544488.9218 | 1334057.8084 | TRUE | Option 3 | 1334057.8084 | 148
| RVL001-15418912 | 393 | 8419605.6303 | -4551196.001 | 785623.5079 | 1895333.6378 | 2680957.1457 | 27599.0805 | 66583.3763 | 94182.4569 | 2586774.6888 | -1964421.3122 | FALSE | 1994 | 311452.5 | -316856.0444 | 307634.7191 | 742175.3875 | 1049810.1066 | 1631147.0391 | 1314290.9947 | TRUE | Option 3 | 1314290.9947 | 149
| BAN003-193396225 | 299 | 6405755.9376 | -3462614.7692 | 254162.8759 | 2367251.0516 | 2621413.9274 | 8928.7828 | 107796.2291 | 116725.0119 | 2504688.9155 | -957925.8537 | FALSE | 1599 | 236957.5 | -241068.5935 | 99525.185 | 967375.5105 | 1066900.6954 | 1554513.232 | 1313444.6385 | TRUE | Option 3 | 1313444.6385 | 150
| NHL015-115332434 | 220 | 4713265.2384 | -2547743.3085 | 304738.4832 | 2142691.7771 | 2447430.2602 | 10705.5121 | 75273.1077 | 85978.6197 | 2361451.6405 | -186291.668 | FALSE | 569 | 174350 | -177374.8849 | 119329.5984 | 839035.9714 | 958365.5698 | 1489064.6905 | 1311689.8056 | TRUE | Option 3 | 1311689.8056 | 151
| GSB014-194965599 | 268 | 5741614.0176 | -3103614.5757 | 499408.1748 | 2044457.3797 | 2543865.5545 | 17544.2897 | 93097.3485 | 110641.6382 | 2433223.9163 | -670390.6595 | FALSE | 1326 | 212390 | -216074.8598 | 195558.4221 | 835466.099 | 1031024.5211 | 1512841.0334 | 1296766.1736 | TRUE | Option 3 | 1296766.1736 | 152
| SHN021-200219341 | 177 | 3792036.1236 | -2049775.2982 | 1039432.6431 | 1314261.9362 | 2353694.5793 | 36515.4364 | 46170.2338 | 82685.6701 | 2271008.9092 | 221233.611 | TRUE | 108 | 140272.5 | -142706.1574 | 407021.3862 | 514639.1339 | 921660.5201 | 1432034.0592 | 1289327.9018 | TRUE | Option 3 | 1289327.9018 | 153
| NHL015-24600722 | 200 | 4284786.5803 | -2316130.2804 | 356328.2305 | 2015030.4763 | 2371358.7068 | 12517.8682 | 70788.3456 | 83306.2138 | 2288052.493 | -28077.7874 | FALSE | 270 | 158500 | -161249.8953 | 139531.1291 | 789046.316 | 928577.4451 | 1442781.2617 | 1281531.3663 | TRUE | Option 3 | 1281531.3663 | 154
| RCT013-15430798 | 264 | 5655918.286 | -3057291.9701 | 995148.4407 | 1446388.1987 | 2441536.6394 | 34959.7252 | 50811.8507 | 85771.5759 | 2355765.0635 | -701526.9066 | FALSE | 1367 | 209220 | -212849.8619 | 389680.5633 | 566377.1805 | 956057.7437 | 1485478.8957 | 1272629.0338 | TRUE | Option 3 | 1272629.0338 | 155
| BGO023-159428755 | 191 | 4091971.1842 | -2211904.4178 | 894500.054 | 1413764.9537 | 2308265.0077 | 31423.9311 | 49665.7908 | 81089.722 | 2227175.2858 | 15270.868 | TRUE | 127 | 151367.5 | -153993.6501 | 350268.6339 | 553602.5591 | 903871.1931 | 1404393.8146 | 1250400.1646 | TRUE | Option 3 | 1250400.1646 | 156
| BAN003-24598790 | 259 | 5548798.6215 | -2999388.7131 | 335232.1983 | 2120878.0607 | 2456110.259 | 11776.7612 | 96577.2756 | 108354.0368 | 2347756.2221 | -651632.491 | FALSE | 1297 | 205257.5 | -208818.6145 | 131270.3377 | 866695.3576 | 997965.6952 | 1458144.5637 | 1249325.9492 | TRUE | Option 3 | 1249325.9492 | 157
| BBD014-97325263 | 228 | 4884656.7016 | -2640388.5197 | 857345.4426 | 1483591.0564 | 2340936.499 | 30118.6837 | 52118.7931 | 82237.4767 | 2258699.0223 | -381689.4974 | FALSE | 927 | 180690 | -183824.8807 | 335719.6186 | 580945.0881 | 916664.7067 | 1424271.7923 | 1240446.9116 | TRUE | Option 3 | 1240446.9116 | 158
| ART031-76433910 | 287 | 6148668.7428 | -3323646.9524 | 187774.7529 | 2198044.4062 | 2385819.1591 | 6596.5573 | 77217.6545 | 83814.2118 | 2302004.9473 | -1021642.0051 | FALSE | 1645 | 227447.5 | -231393.5998 | 73528.9013 | 860710.9726 | 934239.8739 | 1451579.2852 | 1220185.6853 | TRUE | Option 3 | 1220185.6853 | 159
| HTN011-24613192 | 839 | 17974679.7045 | -9716166.5263 | 133009.379 | 3066263.1224 | 3199272.5014 | 4672.6409 | 139626.7632 | 144299.4041 | 3054973.0973 | -6661193.429 | FALSE | 2230 | 664907.5 | -676443.311 | 52083.8577 | 1253026.3114 | 1305110.169 | 1894162.3324 | 1217719.0214 | TRUE | Option 3 | 1217719.0214 | 160
| WND024-183316836 | 325 | 6962778.193 | -3763711.7057 | 809376.7363 | 1662278.192 | 2471654.9284 | 28433.5353 | 75694.2618 | 104127.7971 | 2367527.1313 | -1396184.5744 | FALSE | 1841 | 257562.5 | -262031.0799 | 316936.0164 | 679288.8374 | 996224.8538 | 1475430.0746 | 1213398.9947 | TRUE | Option 3 | 1213398.9947 | 161
| HSM001-15416542 | 196 | 4199090.8487 | -2269807.6748 | 672811.8187 | 1569224.2248 | 2242036.0435 | 23635.9877 | 55127.1001 | 78763.0878 | 2163272.9557 | -106534.7191 | FALSE | 400 | 155330 | -158024.8974 | 263459.8797 | 614477.3531 | 877937.2328 | 1364098.8106 | 1206073.9132 | TRUE | Option 3 | 1206073.9132 | 162
| BAS011-164206954 | 465 | 9962128.7993 | -5385002.902 | 289780.7866 | 2367432.1274 | 2657212.914 | 10180.0458 | 107804.4747 | 117984.5204 | 2539228.3936 | -2845774.5084 | FALSE | 2114 | 368512.5 | -374906.0067 | 113472.4585 | 967449.507 | 1080921.9655 | 1576290.9485 | 1201384.9418 | TRUE | Option 3 | 1201384.9418 | 163
| TQY021-187647017 | 236 | 5056048.1648 | -2733033.7309 | 1581134.4666 | 713206.7359 | 2294341.2024 | 55545.5088 | 32476.9089 | 88022.4177 | 2206318.7847 | -526714.9461 | FALSE | 1141 | 187030 | -190274.8765 | 619141.1696 | 291451.441 | 910592.6106 | 1383748.5918 | 1193473.7153 | TRUE | Option 3 | 1193473.7153 | 164
| MNA034-181657157 | 231 | 4948928.5003 | -2675130.4739 | 620394.7313 | 1635322.8522 | 2255717.5835 | 21794.567 | 57449.1555 | 79243.7225 | 2176473.861 | -498656.6128 | FALSE | 1097 | 183067.5 | -186243.6291 | 242934.3789 | 640360.276 | 883294.6549 | 1372422.9286 | 1186179.2995 | TRUE | Option 3 | 1186179.2995 | 165
| GSB011-74623154 | 65 | 1392555.6386 | -752742.3411 | 1469569.7602 | 542280.2752 | 2011850.0354 | 51626.2227 | 24693.5232 | 76319.7459 | 1935530.2895 | 1182787.9484 | TRUE | 73 | 51512.5 | -52406.216 | 575454.6242 | 221602.4607 | 797057.0848 | 1214792.9506 | 1162386.7346 | TRUE | Option 2 | 1182787.9484 | 166
| HSM002-15416618 | 69 | 1478251.3702 | -799064.9467 | 964022.5945 | 1064143.0018 | 2028165.5962 | 33866.2692 | 37383.5153 | 71249.7845 | 1956915.8118 | 1157850.865 | TRUE | 74 | 54682.5 | -55631.2139 | 377492.2939 | 416697.4768 | 794189.7707 | 1233975.8255 | 1178344.6116 | TRUE | Option 3 | 1178344.6116 | 167
| EHK024-161138740 | 246 | 5270287.4938 | -2848840.2449 | 488380.0855 | 1746566.0185 | 2234946.104 | 17156.8712 | 61357.1459 | 78514.0171 | 2156432.087 | -692408.1579 | FALSE | 1355 | 194955 | -198337.3713 | 191240.0392 | 683920.9127 | 875160.9519 | 1359785.1521 | 1161447.7808 | TRUE | Option 3 | 1161447.7808 | 168
| BAS032-177751012 | 302 | 6470027.7363 | -3497356.7234 | 1314864.3743 | 996154.9064 | 2311019.2807 | 46191.3975 | 45361.3665 | 91552.764 | 2219466.5167 | -1277890.2067 | FALSE | 1795 | 239335 | -243487.342 | 514875.0368 | 407078.0158 | 921953.0526 | 1389066.2281 | 1145578.8861 | TRUE | Option 3 | 1145578.8861 | 169
| RCT011-15430907 | 198 | 4241938.7145 | -2292968.9776 | 608284.2973 | 1533490.2189 | 2141774.5162 | 21369.1255 | 53871.7587 | 75240.8841 | 2066533.6321 | -226435.3455 | FALSE | 647 | 156915 | -159637.3964 | 238192.171 | 600484.619 | 838676.7901 | 1303097.7262 | 1143460.3298 | TRUE | Option 3 | 1143460.3298 | 170
| BGO023-24604124 | 54 | 1156892.3767 | -625355.1757 | 910844.0643 | 911551.9572 | 1822396.0215 | 31998.0989 | 32022.9673 | 64021.0661 | 1758374.9554 | 1133019.7797 | TRUE | 75 | 42795 | -43537.4717 | 356668.627 | 356945.824 | 713614.451 | 1108781.5705 | 1065244.0988 | TRUE | Option 2 | 1133019.7797 | 171
| HSM005-121050437 | 400 | 8569573.1606 | -4632260.5608 | 489198.2595 | 1896536.7049 | 2385734.9644 | 17185.6137 | 66625.6403 | 83811.254 | 2301923.7104 | -2330336.8504 | FALSE | 2053 | 317000 | -322499.7907 | 191560.4201 | 742646.4849 | 934206.9049 | 1451528.0595 | 1129028.2688 | TRUE | Option 3 | 1129028.2688 | 172
| BAS023-41628847 | 403 | 8633844.9594 | -4667002.515 | 55717.9451 | 2384718.2455 | 2440436.1906 | 1957.3804 | 108591.6232 | 110549.0036 | 2329887.1869 | -2337115.3281 | FALSE | 2055 | 319377.5 | -324918.5391 | 21818.0518 | 974513.4672 | 996331.519 | 1444104.6715 | 1119186.1324 | TRUE | Option 3 | 1119186.1324 | 173
| WND022-200942838 | 122 | 2613719.814 | -1412839.471 | 611921.6733 | 1406793.4791 | 2018715.1524 | 21496.9071 | 64060.3928 | 85557.2998 | 1933157.8526 | 520318.3815 | TRUE | 97 | 96685 | -98362.4362 | 239616.496 | 574885.1855 | 814501.6815 | 1204213.4709 | 1105851.0348 | TRUE | Option 3 | 1105851.0348 | 174
| BAN011-15414529 | 89 | 1906730.0282 | -1030677.9748 | 1585126.7966 | 330696.3846 | 1915823.1813 | 55685.76 | 15058.7422 | 70744.5022 | 1845078.6791 | 814400.7043 | TRUE | 86 | 70532.5 | -71756.2034 | 620704.4876 | 135138.8496 | 755843.3372 | 1159979.844 | 1088223.6406 | TRUE | Option 3 | 1088223.6406 | 175
| BBD021-40480035 | 109 | 2335208.6863 | -1262291.0028 | 406974.0284 | 1512385.1705 | 1919359.1989 | 14297.0632 | 53130.3349 | 67427.3982 | 1851931.8008 | 589640.7979 | TRUE | 96 | 86382.5 | -87881.193 | 159363.0278 | 592220.297 | 751583.3248 | 1167775.8741 | 1079894.6811 | TRUE | Option 3 | 1079894.6811 | 176
| MRO005-24606314 | 254 | 5441678.957 | -2941485.4561 | 414669.8738 | 1693262.3443 | 2107932.218 | 14567.4195 | 59484.5792 | 74051.9988 | 2033880.2193 | -907605.2368 | FALSE | 1567 | 201295 | -204787.3671 | 162376.5695 | 663048.242 | 825424.8115 | 1282507.4066 | 1077720.0395 | TRUE | Option 3 | 1077720.0395 | 177
| WND013-139460835 | 521 | 11161869.0417 | -6033519.3805 | 350372.9612 | 2168465.7254 | 2518838.6866 | 12308.6586 | 98744.2494 | 111052.908 | 2407785.7786 | -3625733.6019 | FALSE | 2174 | 412892.5 | -420055.9774 | 137199.1627 | 886142.024 | 1023341.1867 | 1495497.4999 | 1075441.5225 | TRUE | Option 3 | 1075441.5225 | 178
| WND013-200942552 | 296 | 6341484.1389 | -3427872.815 | 916521.306 | 1274279.1241 | 2190800.4301 | 32197.5413 | 58026.1584 | 90223.6996 | 2100576.7304 | -1327296.0846 | FALSE | 1812 | 234580 | -238649.8451 | 358891.7232 | 520733.2857 | 879625.0089 | 1311175.4211 | 1072525.576 | TRUE | Option 3 | 1072525.576 | 179
| CHM011-187119686 | 372 | 7969703.0394 | -4308002.3216 | 256775.0509 | 1985838.0298 | 2242613.0807 | 9020.5489 | 69762.8102 | 78783.3592 | 2163829.7215 | -2144172.6 | FALSE | 2023 | 294810 | -299924.8053 | 100548.0613 | 777615.1279 | 878163.1893 | 1364449.8914 | 1064525.0861 | TRUE | Option 3 | 1064525.0861 | 180
| HSM001-24613473 | 228 | 4884656.7016 | -2640388.5197 | 210609.3439 | 1834373.3388 | 2044982.6827 | 7398.7402 | 64441.8312 | 71840.5714 | 1973142.1113 | -667246.4084 | FALSE | 1322 | 180690 | -183824.8807 | 82470.4782 | 718304.533 | 800775.0111 | 1244207.6716 | 1060382.7909 | TRUE | Option 3 | 1060382.7909 | 181
| TQY021-185165057 | 182 | 3899155.7881 | -2107678.5552 | 1404387.8579 | 593538.0214 | 1997925.8793 | 49336.3719 | 27027.6194 | 76363.9914 | 1921561.888 | -186116.6672 | FALSE | 568 | 144235 | -146737.4048 | 549930.6728 | 242548.9033 | 792479.5761 | 1205446.3032 | 1058708.8984 | TRUE | Option 3 | 1058708.8984 | 182
| BGO013-24606216 | 97 | 2078121.4915 | -1123323.186 | 571112.5301 | 1291210.6147 | 1862323.1448 | 20063.2753 | 45360.4371 | 65423.7124 | 1796899.4324 | 673576.2464 | TRUE | 92 | 76872.5 | -78206.1992 | 223636.4379 | 505612.6896 | 729249.1274 | 1133074.0173 | 1054867.8181 | TRUE | Option 3 | 1054867.8181 | 183
| TNA022-182581504 | 220 | 4713265.2384 | -2547743.3085 | 1119995.7075 | 929003.6813 | 2048999.3888 | 39345.6298 | 42303.5375 | 81649.1673 | 1967350.2215 | -580393.087 | FALSE | 1222 | 174350 | -177374.8849 | 438568.2983 | 379636.714 | 818205.0123 | 1230794.3766 | 1053419.4917 | TRUE | Option 3 | 1053419.4917 | 184
| MNA021-15421016 | 152 | 3256437.801 | -1760259.0131 | 956057.7 | 919705.911 | 1875763.6109 | 33586.4612 | 32309.417 | 65895.8781 | 1809867.7328 | 49608.7197 | TRUE | 122 | 120460 | -122549.9205 | 374373.3978 | 360138.7519 | 734512.1497 | 1141251.4612 | 1018701.5407 | TRUE | Option 3 | 1018701.5407 | 185
| DDL024-203514186 | 494 | 10583422.8534 | -5720841.7926 | 995135.0491 | 1368592.586 | 2363727.6351 | 34959.2548 | 62320.8594 | 97280.1142 | 2266447.5209 | -3454394.2717 | FALSE | 2169 | 391495 | -398287.2415 | 389675.3194 | 559274.4169 | 948949.7363 | 1414777.8988 | 1016490.6573 | TRUE | Option 3 | 1016490.6573 | 186
| BAS022-24598930 | 380 | 8141094.5026 | -4400647.5328 | 156083.7002 | 2067224.8695 | 2223308.5696 | 5483.2456 | 94134.0993 | 99617.3449 | 2123691.2247 | -2276956.308 | FALSE | 2047 | 301150 | -306374.8012 | 61119.3081 | 844770.018 | 905889.3261 | 1317419.2435 | 1011044.4424 | TRUE | Option 3 | 1011044.4424 | 187
| MRO007-24610986 | 173 | 3706340.392 | -2003452.6926 | 313456.0946 | 1573036.1572 | 1886492.2518 | 11011.7632 | 55261.0139 | 66272.777 | 1820219.4748 | -183233.2178 | FALSE | 554 | 137102.5 | -139481.1595 | 122743.2436 | 615970.0309 | 738713.2745 | 1147778.9773 | 1008297.8178 | TRUE | Option 3 | 1008297.8178 | 188
| RCT014-24611042 | 204 | 4370482.3119 | -2362452.886 | 649356.9327 | 1278144.956 | 1927501.8887 | 22812.0138 | 44901.4384 | 67713.4522 | 1859788.4365 | -502664.4495 | FALSE | 1100 | 161670 | -164474.8933 | 254275.4075 | 500496.4345 | 754771.842 | 1172730.0467 | 1008255.1534 | TRUE | Option 3 | 1008255.1534 | 189
| DDL014-197602155 | 612 | 13111446.9358 | -7087358.6581 | 967198.3194 | 1543211.4115 | 2510409.7309 | 33977.8329 | 70272.3823 | 104250.2152 | 2406159.5157 | -4681199.1424 | FALSE | 2208 | 485010 | -493424.6798 | 378735.8453 | 630632.2796 | 1009368.1249 | 1501041.606 | 1007616.9263 | TRUE | Option 3 | 1007616.9263 | 190
| HSM001-41021978 | 236 | 5056048.1648 | -2733033.7309 | 361588.0891 | 1586005.8597 | 1947593.9487 | 12702.6479 | 55716.6416 | 68419.2895 | 1879174.6592 | -853859.0716 | FALSE | 1519 | 187030 | -190274.8765 | 141590.7863 | 621048.7114 | 762639.4977 | 1184954.451 | 994679.5745 | TRUE | Option 3 | 994679.5745 | 191
| BAN006-193339179 | 361 | 7734039.7775 | -4180615.1561 | 370804.8001 | 1753780.4079 | 2124585.208 | 13026.4324 | 79860.9486 | 92887.3811 | 2031697.8269 | -2148917.3292 | FALSE | 2024 | 286092.5 | -291056.0611 | 145199.8691 | 716681.1548 | 861881.0239 | 1262704.184 | 971648.1229 | TRUE | Option 3 | 971648.1229 | 192
| EHK024-63048164 | 301 | 6448603.8034 | -3485776.072 | 351644.1522 | 1641466.7215 | 1993110.8737 | 12353.3158 | 57664.9906 | 70018.3064 | 1923092.5673 | -1562683.5047 | FALSE | 1904 | 238542.5 | -242681.0925 | 137696.9362 | 642766.0944 | 780463.0306 | 1212647.8431 | 969966.7506 | TRUE | Option 3 | 969966.7506 | 193
| WND024-200942990 | 270 | 5784461.8834 | -3126775.8786 | 778422.1456 | 1199945.4528 | 1978367.5984 | 27346.0955 | 54641.2662 | 81987.3617 | 1896380.2367 | -1230395.6419 | FALSE | 1766 | 213975 | -217687.3587 | 304814.8073 | 490356.8822 | 795171.6894 | 1183195.909 | 965508.5503 | TRUE | Option 3 | 965508.5503 | 194
| BBD013-15437974 | 200 | 4284786.5803 | -2316130.2804 | 907941.7304 | 935777.3834 | 1843719.1139 | 31896.1394 | 32874.0104 | 64770.1498 | 1778948.9641 | -537181.3163 | FALSE | 1162 | 158500 | -161249.8953 | 355532.1301 | 366432.0246 | 721964.1547 | 1121754.9592 | 960505.0638 | TRUE | Option 3 | 960505.0638 | 195
| MLN032-196479760 | 220 | 4713265.2384 | -2547743.3085 | 1244993.0049 | 630435.7046 | 1875428.7095 | 43736.805 | 28707.8093 | 72444.6143 | 1802984.0952 | -744759.2133 | FALSE | 1409 | 174350 | -177374.8849 | 487514.7823 | 257627.1161 | 745141.8984 | 1130286.8111 | 952911.9262 | TRUE | Option 3 | 952911.9262 | 196
| MNA014-15420920 | 225 | 4820384.9029 | -2605646.5655 | 846993.3377 | 982332.3684 | 1829325.7061 | 29755.0125 | 34509.4945 | 64264.5071 | 1765061.1991 | -840585.3664 | FALSE | 1508 | 178312.5 | -181406.1323 | 331665.9379 | 384662.0414 | 716327.9792 | 1112997.7269 | 931591.5946 | TRUE | Option 3 | 931591.5946 | 197
| KGT004-24605698 | 243 | 5206015.6951 | -2814098.2907 | 395980.0377 | 1450112.4788 | 1846092.5165 | 13910.8426 | 50942.6852 | 64853.5278 | 1781238.9887 | -1032859.302 | FALSE | 1649 | 192577.5 | -195918.6228 | 155057.9972 | 567835.5353 | 722893.5325 | 1123198.984 | 927280.3612 | TRUE | Option 3 | 927280.3612 | 198
| WIN011-160628528 | 844 | 18081799.369 | -9774069.7833 | 402491.6548 | 2301591.8797 | 2704083.5345 | 14139.5967 | 104806.3429 | 118945.9397 | 2585137.5948 | -7188932.1885 | FALSE | 2233 | 668870 | -680474.5584 | 157607.8184 | 940543.9351 | 1098151.7536 | 1605931.7809 | 925457.2226 | TRUE | Option 3 | 925457.2226 | 199
| EHK024-119636484 | 455 | 9747889.4702 | -5269196.3879 | 139076.2849 | 1979119.0367 | 2118195.3216 | 4885.7723 | 69526.7709 | 74412.5432 | 2043782.7783 | -3225413.6096 | FALSE | 2151 | 360587.5 | -366843.5119 | 54459.5387 | 774984.1023 | 829443.641 | 1288751.6805 | 921908.1686 | TRUE | Option 3 | 921908.1686 | 200
| FNS032-15405445 | 142 | 3042198.472 | -1644452.4991 | 1032657.1237 | 687551.8075 | 1720208.9312 | 36277.4113 | 31308.6743 | 67586.0856 | 1652622.8456 | 8170.3465 | TRUE | 128 | 112535 | -114487.4257 | 404368.226 | 280967.5722 | 685335.7983 | 1034873.1329 | 920385.7072 | TRUE | Option 3 | 920385.7072 | 201
| WND012-200942480 | 127 | 2720839.4785 | -1470742.7281 | 844646.5477 | 849744.6563 | 1694391.204 | 29672.5694 | 38694.3622 | 68366.9316 | 1626024.2723 | 155281.5443 | TRUE | 115 | 100647.5 | -102393.6835 | 330746.9811 | 347247.5681 | 677994.5491 | 1016396.6549 | 914002.9713 | TRUE | Option 3 | 914002.9713 | 202
| KGT002-15430186 | 244 | 5227439.628 | -2825678.9421 | 573507.836 | 1228906.4127 | 1802414.2487 | 20147.4228 | 43171.6805 | 63319.1032 | 1739095.1455 | -1086583.7966 | FALSE | 1672 | 193370 | -196724.8723 | 224574.3926 | 481215.5891 | 705789.9816 | 1096624.2671 | 899899.3947 | TRUE | Option 3 | 899899.3947 | 203
| BAN009-199768607 | 45 | 964076.9806 | -521129.3131 | 1230074.5124 | 243143.021 | 1473217.5334 | 43212.716 | 11071.8721 | 54284.5881 | 1418932.9454 | 897803.6323 | TRUE | 82 | 35662.5 | -36281.2265 | 481672.9939 | 99360.2279 | 581033.2219 | 892184.3115 | 855903.0851 | TRUE | Option 2 | 897803.6323 | 204
| WND024-192414587 | 174 | 3727764.3249 | -2015033.344 | 380311.8475 | 1362149.5133 | 1742461.3609 | 13360.4165 | 62027.4647 | 75387.8812 | 1667073.4796 | -347959.8643 | FALSE | 870 | 137895 | -140287.409 | 148922.642 | 556641.4597 | 705564.1017 | 1036897.2592 | 896609.8502 | TRUE | Option 3 | 896609.8502 | 205
| NKA006-152812929 | 226 | 4841808.8358 | -2617227.2169 | 392177.9475 | 1376749.7108 | 1768927.6584 | 13777.2745 | 48365.4394 | 62142.7139 | 1706784.9444 | -910442.2724 | FALSE | 1569 | 179105 | -182212.3817 | 153569.1735 | 539108.1178 | 692677.2912 | 1076250.3671 | 894037.9854 | TRUE | Option 3 | 894037.9854 | 206
| NHL031-111738437 | 389 | 8333909.8987 | -4504873.3954 | 76908.4777 | 1882648.4896 | 1959556.9673 | 2701.8072 | 66137.745 | 68839.5523 | 1890717.415 | -2614155.9804 | FALSE | 2090 | 308282.5 | -313631.0465 | 30115.8477 | 737208.1329 | 767323.9806 | 1192232.9867 | 878601.9403 | TRUE | Option 3 | 878601.9403 | 207
| MBN012-15419426 | 38 | 814109.4503 | -440064.7533 | 1148801.8235 | 217447.8719 | 1366249.6954 | 40357.5933 | 7638.9788 | 47996.5721 | 1318253.1233 | 878188.37 | TRUE | 83 | 30115 | -30637.4801 | 449848.2069 | 85148.3113 | 534996.5182 | 831253.1772 | 800615.6971 | TRUE | Option 2 | 878188.37 | 208
| BAS011-15414109 | 450 | 9640769.8057 | -5211293.1309 | 753458.7403 | 1321702.2356 | 2075160.9759 | 26469.1271 | 60185.6389 | 86654.766 | 1988506.2099 | -3222786.921 | FALSE | 2150 | 356625 | -362812.2645 | 295039.6286 | 540112.7075 | 835152.3361 | 1240008.6398 | 877196.3752 | TRUE | Option 3 | 877196.3752 | 209
| KGT004-55202181 | 251 | 5377407.1583 | -2906743.5019 | 278968.1508 | 1487263.1672 | 1766231.318 | 9800.1961 | 52247.7949 | 62047.991 | 1704183.3269 | -1202560.175 | FALSE | 1749 | 198917.5 | -202368.6187 | 109238.4429 | 582383.0145 | 691621.4574 | 1074609.8606 | 872241.2419 | TRUE | Option 3 | 872241.2419 | 210
| WMN013-24614054 | 83 | 1778186.4308 | -961194.0664 | 770062.8563 | 754000.098 | 1524062.9543 | 27052.4323 | 26488.145 | 53540.5774 | 1470522.377 | 509328.3106 | TRUE | 98 | 65777.5 | -66918.7066 | 301541.4739 | 295251.6136 | 596793.0876 | 927269.8668 | 860351.1602 | TRUE | Option 3 | 860351.1602 | 211
| ECA007-111138070 | 245 | 5248863.5609 | -2837259.5935 | 263605.8488 | 1472340.8425 | 1735946.6914 | 9260.516 | 51723.5712 | 60984.0872 | 1674962.6041 | -1162296.9894 | FALSE | 1727 | 194162.5 | -197531.1218 | 103222.8675 | 576539.7255 | 679762.593 | 1056184.0983 | 858652.9765 | TRUE | Option 3 | 858652.9765 | 212
| GSB014-74623507 | 69 | 1478251.3702 | -799064.9467 | 630498.3364 | 893247.5356 | 1523745.8721 | 22149.5082 | 40675.3293 | 62824.8375 | 1460921.0346 | 661856.0878 | TRUE | 93 | 54682.5 | -55631.2139 | 246890.752 | 365024.9897 | 611915.7417 | 911830.1303 | 856198.9165 | TRUE | Option 3 | 856198.9165 | 213
| PLD003-24597184 | 551 | 11804587.0288 | -6380938.9225 | 114517.2217 | 2071818.7784 | 2186336.0001 | 4023.0085 | 94343.2897 | 98366.2981 | 2087969.702 | -4292969.2205 | FALSE | 2198 | 436667.5 | -444243.4617 | 44842.6924 | 846647.3157 | 891490.0081 | 1294845.992 | 850602.5303 | TRUE | Option 3 | 850602.5303 | 214
| CLC013-161744857 | 350 | 7498376.5156 | -4053227.9907 | 691332.5748 | 1199351.1419 | 1890683.7166 | 24286.6248 | 54614.2034 | 78900.8283 | 1811782.8884 | -2241445.1023 | FALSE | 2037 | 277375 | -282187.3169 | 270712.2436 | 490114.0174 | 760826.2611 | 1129857.4556 | 847670.1387 | TRUE | Option 3 | 847670.1387 | 215
| NHL016-24601854 | 268 | 5741614.0176 | -3103614.5757 | 48487.1802 | 1646262.1339 | 1694749.314 | 1703.3625 | 57833.4542 | 59536.8167 | 1635212.4973 | -1468402.0784 | FALSE | 1867 | 212390 | -216074.8598 | 18986.6264 | 644643.8836 | 663630.5101 | 1031118.804 | 815043.9442 | TRUE | Option 3 | 815043.9442 | 216
| MLN012-84731779 | 202 | 4327634.4461 | -2339291.5832 | 247579.047 | 1396539.9316 | 1644118.9786 | 8697.4918 | 63593.4825 | 72290.9744 | 1571828.0043 | -767463.579 | FALSE | 1437 | 160085 | -162862.3943 | 96947.087 | 570695.0804 | 667642.1675 | 976476.8112 | 813614.4169 | TRUE | Option 3 | 813614.4169 | 217
| WPD012-15436728 | 186 | 3984851.5197 | -2154001.1608 | 1248053.1965 | 344432.8299 | 1592486.0263 | 43844.3101 | 15684.2512 | 59528.5613 | 1532957.465 | -621043.6957 | FALSE | 1266 | 147405 | -149962.4027 | 488713.0931 | 140752.2385 | 629465.3317 | 963020.6947 | 813058.292 | TRUE | Option 3 | 813058.292 | 218
| WPD024-15398985 | 131 | 2806535.2101 | -1517065.3337 | 1047601.548 | 473732.4426 | 1521333.9906 | 36802.4113 | 21572.0977 | 58374.509 | 1462959.4816 | -54105.852 | FALSE | 301 | 103817.5 | -105618.6815 | 410220.1688 | 193590.4361 | 603810.6049 | 917523.3857 | 811904.7043 | TRUE | Option 3 | 811904.7043 | 219
| WIN022-160628386 | 683 | 14632546.1718 | -7909584.9076 | 259634.2676 | 2018704.9246 | 2278339.1922 | 9120.9937 | 91924.6729 | 101045.6666 | 2177293.5256 | -5732291.382 | FALSE | 2219 | 541277.5 | -550668.3926 | 101667.6744 | 824942.3759 | 926610.0503 | 1351729.1419 | 801060.7492 | TRUE | Option 3 | 801060.7492 | 220
| BMH003-140036206 | 247 | 5291711.4267 | -2860420.8963 | 764737.016 | 897943.2528 | 1662680.2688 | 26865.3347 | 40889.1556 | 67754.4903 | 1594925.7785 | -1265495.1178 | FALSE | 1786 | 195747.5 | -199143.6208 | 299455.9796 | 366943.8913 | 666399.8709 | 996280.3979 | 797136.7772 | TRUE | Option 3 | 797136.7772 | 221
| CLC003-15400758 | 425 | 9105171.4832 | -4921776.8459 | 581143.7916 | 1313497.1126 | 1894640.9042 | 20415.6751 | 59812.0067 | 80227.6818 | 1814413.2224 | -3107363.6235 | FALSE | 2143 | 336812.5 | -342656.0276 | 227564.4826 | 536759.6897 | 764324.1723 | 1130316.7319 | 787660.7043 | TRUE | Option 3 | 787660.7043 | 222
| CTN003-24603160 | 273 | 5848733.6821 | -3161517.8328 | 63585.9706 | 1585669.6522 | 1649255.6228 | 2233.7854 | 55704.8306 | 57938.616 | 1591317.0068 | -1570200.8259 | FALSE | 1906 | 216352.5 | -220106.1072 | 24899.0159 | 620917.0592 | 645816.0751 | 1003439.5478 | 783333.4406 | TRUE | Option 3 | 783333.4406 | 223
| MLN014-196479219 | 192 | 4113395.1171 | -2223485.0692 | 1124680.672 | 402935.7865 | 1527616.4585 | 39510.2134 | 18348.2687 | 57858.4821 | 1469757.9765 | -753727.0927 | FALSE | 1425 | 152160 | -154799.8995 | 440402.8383 | 164659.4314 | 605062.2697 | 922554.1889 | 767754.2893 | TRUE | Option 3 | 767754.2893 | 224
| CTN001-155250997 | 374 | 8012550.9052 | -4331163.6244 | 12970.75 | 1741254.232 | 1754224.982 | 455.6645 | 61170.542 | 61626.2065 | 1692598.7755 | -2638564.8489 | FALSE | 2095 | 296395 | -301537.3043 | 5079.0907 | 681840.9216 | 686920.0123 | 1067304.9697 | 765767.6654 | TRUE | Option 3 | 765767.6654 | 225
| CHM011-24600540 | 754 | 16153645.4078 | -8731811.1571 | 51836.7695 | 2200878.0634 | 2252714.833 | 1821.0341 | 77317.2013 | 79138.2354 | 2173576.5976 | -6558234.5596 | FALSE | 2229 | 597545 | -607912.1055 | 20298.2598 | 861820.5771 | 882118.8368 | 1370595.9961 | 762683.8907 | TRUE | Option 3 | 762683.8907 | 226
| BAS022-15416117 | 132 | 2827959.143 | -1528645.9851 | 875397.2999 | 565041.2261 | 1440438.526 | 30752.8483 | 25729.9763 | 56482.8246 | 1383955.7014 | -144690.2837 | FALSE | 484 | 104610 | -106424.9309 | 342788.371 | 230903.7076 | 573692.0786 | 866746.4474 | 760321.5165 | TRUE | Option 3 | 760321.5165 | 227
| GB012-15403573 | 92 | 1971001.8269 | -1065419.929 | 918173.693 | 435696.7141 | 1353870.4071 | 32255.5899 | 19840.0853 | 52095.6752 | 1301774.7319 | 236354.8029 | TRUE | 106 | 72910 | -74174.9519 | 359538.7655 | 178047.1619 | 537585.9274 | 816284.4797 | 742109.5278 | TRUE | Option 3 | 742109.5278 | 228
| CHA006-95436119 | 161 | 3449253.1972 | -1864484.8757 | 100502.4382 | 1322180.8887 | 1422683.3269 | 3530.6669 | 46448.4278 | 49979.0947 | 1372704.2322 | -491780.6436 | FALSE | 1087 | 127592.5 | -129806.1658 | 39354.7788 | 517740.0399 | 557094.8187 | 865588.5081 | 735782.3424 | TRUE | Option 3 | 735782.3424 | 229
| SHL004-24612892 | 229 | 4906080.6345 | -2651969.1711 | 218473.3714 | 1289280.0786 | 1507753.45 | 7675.0048 | 45292.6171 | 52967.6218 | 1454785.8281 | -1197183.343 | FALSE | 1747 | 181482.5 | -184631.1302 | 85549.8767 | 504856.7296 | 590406.6063 | 917346.8436 | 732715.7135 | TRUE | Option 3 | 732715.7135 | 230
| HTN033-182145786 | 690 | 14782513.7021 | -7990649.4674 | 89015.0878 | 2080394.7191 | 2169409.8069 | 3127.1144 | 94733.8076 | 97860.922 | 2071548.8849 | -5919100.5825 | FALSE | 2222 | 546825 | -556312.139 | 34856.5582 | 850151.8679 | 885008.4262 | 1284401.3808 | 728089.2418 | TRUE | Option 3 | 728089.2418 | 231
| BET007-159943710 | 109 | 2335208.6863 | -1262291.0028 | 190948.5874 | 1141367.3669 | 1332315.9543 | 6708.0547 | 40096.4197 | 46804.4743 | 1285511.48 | 23220.4771 | TRUE | 126 | 86382.5 | -87881.193 | 74771.7125 | 446937.0199 | 521708.7324 | 810607.2219 | 722726.0289 | TRUE | Option 3 | 722726.0289 | 232
| BAN007-156954231 | 121 | 2592295.8811 | -1401258.8196 | 25767.7434 | 1353760.5547 | 1379528.2981 | 905.225 | 61645.4612 | 62550.6862 | 1316977.6119 | -84281.2078 | FALSE | 363 | 95892.5 | -97556.1867 | 10090.1417 | 553213.3175 | 563303.4592 | 816224.8389 | 718668.6522 | TRUE | Option 3 | 718668.6522 | 233
| WPD033-63732110 | 115 | 2463752.2837 | -1331774.9112 | 640784.4436 | 706440.3533 | 1347224.7969 | 22510.8608 | 32168.7918 | 54679.6526 | 1292545.1442 | -39229.767 | FALSE | 285 | 91137.5 | -92718.6898 | 250918.5893 | 288686.3634 | 539604.9527 | 807619.8441 | 714901.1543 | TRUE | Option 3 | 714901.1543 | 234
| OYN001-24604668 | 921 | 19731442.2024 | -10665779.9413 | 40741.4942 | 2335694.8494 | 2376436.3436 | 1431.2553 | 82053.3367 | 83484.592 | 2292951.7516 | -8372828.1896 | FALSE | 2237 | 729892.5 | -742555.7681 | 15953.5681 | 914612.1798 | 930565.7479 | 1445870.5958 | 703314.8277 | TRUE | Option 3 | 703314.8277 | 235
| MDA023-15412302 | 303 | 6491451.6692 | -3508937.3748 | 793213.8714 | 756015.5597 | 1549229.4311 | 27865.7312 | 26558.9485 | 54424.6798 | 1494804.7513 | -2014132.6235 | FALSE | 1999 | 240127.5 | -244293.5915 | 310606.9563 | 296040.8288 | 606647.785 | 942581.646 | 698288.0546 | TRUE | Option 3 | 698288.0546 | 236
| WND011-200942344 | 142 | 3042198.472 | -1644452.4991 | 222133.4788 | 1144996.8109 | 1367130.2897 | 7803.5849 | 52139.0997 | 59942.6846 | 1307187.6051 | -337264.894 | FALSE | 853 | 112535 | -114487.4257 | 86983.1028 | 467902.1575 | 554885.2603 | 812245.0294 | 697757.6037 | TRUE | Option 3 | 697757.6037 | 237
| FNS032-24606816 | 232 | 4970352.4332 | -2686711.1253 | 527180.218 | 950905.3695 | 1478085.5875 | 18519.9261 | 43300.8628 | 61820.7889 | 1416264.7986 | -1270446.3267 | FALSE | 1788 | 183860 | -187049.8786 | 206433.4082 | 388586.8238 | 595020.232 | 883065.3555 | 696015.4769 | TRUE | Option 3 | 696015.4769 | 238
| ECA012-15423053 | 138 | 2956502.7404 | -1598129.8935 | 593009.099 | 733800.3712 | 1326809.4702 | 20832.5053 | 25778.5254 | 46611.0307 | 1280198.4395 | -317931.454 | FALSE | 814 | 109365 | -111262.4278 | 232210.7037 | 287341.7977 | 519552.5015 | 807256.9687 | 695994.5409 | TRUE | Option 3 | 695994.5409 | 239
| BAN002-15414829 | 172 | 3684916.4591 | -1991872.0412 | 836358.6955 | 539959.7208 | 1376318.4163 | 29381.4158 | 24587.8534 | 53969.2692 | 1322349.147 | -669522.8941 | FALSE | 1324 | 136310 | -138674.91 | 327501.6211 | 220654.1677 | 548155.7888 | 828162.6275 | 689487.7175 | TRUE | Option 3 | 689487.7175 | 240
| SHL002-24604026 | 112 | 2399480.485 | -1297032.957 | 789012.0552 | 464586.7521 | 1253598.8073 | 27718.1207 | 16321.0075 | 44039.1283 | 1209559.679 | -87473.278 | FALSE | 365 | 88760 | -90299.9414 | 308961.6077 | 181923.0376 | 490884.6453 | 762714.162 | 672414.2206 | TRUE | Option 3 | 672414.2206 | 241
| WND021-200942770 | 215 | 4606145.5738 | -2489840.0514 | 368304.2846 | 1042309.9286 | 1410614.2131 | 12938.5889 | 47463.1027 | 60401.6916 | 1350212.5215 | -1139627.5299 | FALSE | 1711 | 170387.5 | -173343.6375 | 144220.7164 | 425939.2338 | 570159.9503 | 840454.2629 | 667110.6254 | TRUE | Option 3 | 667110.6254 | 242
| MRO005-24606328 | 249 | 5334559.2925 | -2883582.1991 | 136246.7387 | 1289190.7537 | 1425437.4924 | 4786.3699 | 45289.4791 | 50075.849 | 1375361.6434 | -1508220.5557 | FALSE | 1885 | 197332.5 | -200756.1197 | 53351.5441 | 504821.7517 | 558173.2958 | 867264.1966 | 666508.0769 | TRUE | Option 3 | 666508.0769 | 243
| KGT003-119555477 | 228 | 4884656.7016 | -2640388.5197 | 197791.1255 | 1197016.2009 | 1394807.3264 | 6948.4341 | 42051.3722 | 48999.8063 | 1345807.5201 | -1294580.9995 | FALSE | 1801 | 180690 | -183824.8807 | 77451.1159 | 468728.0092 | 546179.125 | 848628.2014 | 664803.3207 | TRUE | Option 3 | 664803.3207 | 244
| STL006-144632294 | 341 | 7305561.1195 | -3949002.1281 | 14962.961 | 1519152.8937 | 1534115.8547 | 525.6512 | 53368.0861 | 53893.7374 | 1480222.1173 | -2468780.0108 | FALSE | 2072 | 270242.5 | -274931.0716 | 5859.2013 | 594870.4043 | 600729.6057 | 933386.249 | 658455.1774 | TRUE | Option 3 | 658455.1774 | 245
| BMH006-15408306 | 163 | 3492101.063 | -1887646.1785 | 748292.6279 | 565107.0847 | 1313399.7126 | 26287.6407 | 25732.9753 | 52020.616 | 1261379.0966 | -626267.0819 | FALSE | 1274 | 129177.5 | -131418.6647 | 293016.6805 | 230930.6206 | 523947.3012 | 789452.4114 | 658033.7467 | TRUE | Option 3 | 658033.7467 | 246
| BGO023-24614382 | 83 | 1778186.4308 | -961194.0664 | 284418.1552 | 891462.6117 | 1175880.7669 | 9991.6557 | 31317.2253 | 41308.881 | 1134571.886 | 173377.8196 | TRUE | 113 | 65777.5 | -66918.7066 | 111372.5575 | 349079.2313 | 460451.7888 | 715428.9782 | 648510.2716 | TRUE | Option 3 | 648510.2716 | 247
| ART031-15411744 | 203 | 4349058.379 | -2350872.2346 | 354379.8097 | 955377.5772 | 1309757.3869 | 12449.4199 | 33562.5684 | 46011.9882 | 1263745.3987 | -1087126.8359 | FALSE | 1673 | 160877.5 | -163668.6438 | 138768.1658 | 374107.0751 | 512875.2409 | 796882.146 | 633213.5022 | TRUE | Option 3 | 633213.5022 | 248
| CLC006-15400532 | 507 | 10861933.9811 | -5871390.2608 | 616807.3863 | 1121928.5451 | 1738735.9314 | 21668.5429 | 51088.6526 | 72757.1955 | 1665978.7359 | -4205411.525 | FALSE | 2196 | 401797.5 | -408768.4847 | 241529.6451 | 458475.3266 | 700004.9717 | 1038730.9597 | 629962.4749 | TRUE | Option 3 | 629962.4749 | 249
| WND012-24611463 | 367 | 7862583.3749 | -4250099.0646 | 97046.0557 | 1458198.2808 | 1555244.3365 | 3409.2436 | 66401.1854 | 69810.429 | 1485433.9075 | -2764665.157 | FALSE | 2105 | 290847.5 | -295893.558 | 38001.3274 | 595891.7223 | 633893.0496 | 921351.2868 | 625457.7289 | TRUE | Option 3 | 625457.7289 | 250
| HTN034-182145765 | 419 | 8976627.8858 | -4852292.9375 | 32690.8484 | 1585035.6869 | 1617726.5353 | 1148.4348 | 72176.9117 | 73325.3464 | 1544401.1889 | -3307891.7486 | FALSE | 2153 | 332057.5 | -337818.5308 | 12801.0935 | 647723.7409 | 660524.8344 | 957201.7009 | 619383.1702 | TRUE | Option 3 | 619383.1702 | 251
| MDA024-15412265 | 142 | 3042198.472 | -1644452.4991 | 597443.3641 | 605004.9658 | 1202448.3298 | 20988.2817 | 21253.922 | 42242.2037 | 1160206.1261 | -484246.373 | FALSE | 1076 | 112535 | -114487.4257 | 233947.0747 | 236908.0493 | 470855.124 | 731593.2058 | 617105.7801 | TRUE | Option 3 | 617105.7801 | 252
| HTN033-190418479 | 421 | 9019475.7516 | -4875454.2403 | 550790.5964 | 1048322.0961 | 1599112.6925 | 19349.3625 | 47736.8755 | 67086.238 | 1532026.4545 | -3343427.7858 | FALSE | 2158 | 333642.5 | -339431.0297 | 215678.7682 | 428396.102 | 644074.8701 | 955037.8224 | 615606.7927 | TRUE | Option 3 | 615606.7927 | 253
| NKA003-15422579 | 268 | 5741614.0176 | -3103614.5757 | 312976.1139 | 1041842.191 | 1354818.3049 | 10994.9014 | 36600.0842 | 47594.9855 | 1307223.3194 | -1796391.2564 | FALSE | 1959 | 212390 | -216074.8598 | 122555.2926 | 407964.9178 | 530520.2104 | 824298.0944 | 608223.2347 | TRUE | Option 3 | 608223.2347 | 254
| BMH003-24599938 | 141 | 3020774.5391 | -1632871.8477 | 691246.5363 | 508292.2822 | 1199538.8185 | 24283.6023 | 23145.8304 | 47429.4327 | 1152109.3858 | -480762.4619 | FALSE | 1073 | 111742.5 | -113681.1762 | 270678.5527 | 207713.2907 | 478391.8434 | 721146.975 | 607465.7988 | TRUE | Option 3 | 607465.7988 | 255
| NKA002-24606244 | 142 | 3042198.472 | -1644452.4991 | 143062.8067 | 1026902.2668 | 1169965.0735 | 5025.8195 | 36075.2422 | 41101.0617 | 1128864.0118 | -515588.4873 | FALSE | 1120 | 112535 | -114487.4257 | 56020.5823 | 402114.7373 | 458135.3195 | 711829.754 | 597342.3283 | TRUE | Option 3 | 597342.3283 | 256
| HYT011-41829518 | 290 | 6212940.5415 | -3358388.9066 | 259060.1807 | 1137367.1153 | 1396427.2961 | 9100.8259 | 51791.6704 | 60892.4963 | 1335534.7998 | -2022854.1068 | FALSE | 2003 | 229825 | -233812.3483 | 101442.8733 | 464784.2877 | 566227.1609 | 830200.1351 | 596387.7868 | TRUE | Option 3 | 596387.7868 | 257
| SHL002-24614570 | 130 | 2785111.2772 | -1505484.6823 | 274891.6516 | 877146.3873 | 1152038.0389 | 9656.9881 | 30814.294 | 40471.2821 | 1111566.7568 | -393917.9255 | FALSE | 951 | 103025 | -104812.432 | 107642.166 | 343473.2792 | 451115.4452 | 700922.5936 | 596110.1617 | TRUE | Option 3 | 596110.1617 | 258
| MRO008-24606830 | 225 | 4820384.9029 | -2605646.5655 | 63030.8586 | 1213598.1543 | 1276629.0129 | 2214.2842 | 42633.8989 | 44848.1831 | 1231780.8298 | -1373865.7356 | FALSE | 1833 | 178312.5 | -181406.1323 | 24681.645 | 475221.1761 | 499902.821 | 776726.1919 | 595320.0596 | TRUE | Option 3 | 595320.0596 | 259
| CTN006-24605334 | 148 | 3170742.0694 | -1713936.4075 | 159753.1972 | 1013621.5005 | 1173374.6977 | 5612.1556 | 35608.6868 | 41220.8424 | 1132153.8554 | -581782.5521 | FALSE | 1225 | 117290 | -119324.9226 | 62556.211 | 396914.2503 | 459470.4613 | 713904.2364 | 594579.3139 | TRUE | Option 3 | 594579.3139 | 260
| RVL004-15418838 | 117 | 2506600.1495 | -1354936.214 | 745140.6943 | 381412.6372 | 1126553.3314 | 26176.9128 | 13399.0875 | 39576.0002 | 1086977.3312 | -267958.8828 | FALSE | 729 | 92722.5 | -94331.1888 | 291782.4453 | 149353.6896 | 441136.1349 | 685417.1966 | 591086.0078 | TRUE | Option 3 | 591086.0078 | 261
| MLN012-24607519 | 262 | 5613070.4202 | -3034130.6673 | 67411.866 | 1272796.2639 | 1340208.1299 | 2368.1897 | 57958.6342 | 60326.8239 | 1279881.306 | -1754249.3613 | FALSE | 1949 | 207635 | -211237.3629 | 26397.1613 | 520127.3159 | 546524.4772 | 793683.6527 | 582446.2898 | TRUE | Option 3 | 582446.2898 | 262
| CTN003-15418451 | 169 | 3620644.6604 | -1957130.0869 | 205927.8189 | 964399.3565 | 1170327.1755 | 7234.2775 | 33879.5049 | 41113.7824 | 1129213.3931 | -827916.6939 | FALSE | 1493 | 133932.5 | -136256.1616 | 80637.2851 | 377639.8265 | 458277.1115 | 712050.0639 | 575793.9024 | TRUE | Option 3 | 575793.9024 | 263
| BET007-24613316 | 163 | 3492101.063 | -1887646.1785 | 701926.7668 | 447763.4198 | 1149690.1865 | 24658.8005 | 15730.0011 | 40388.8017 | 1109301.3849 | -778344.7937 | FALSE | 1447 | 129177.5 | -131418.6647 | 274860.7209 | 175335.3515 | 450196.0724 | 699494.1141 | 568075.4494 | TRUE | Option 3 | 568075.4494 | 264
| CTN001-129145544 | 454 | 9726465.5373 | -5257615.7365 | 170527.572 | 1363510.6852 | 1534038.2572 | 5990.6611 | 47900.3503 | 53891.0114 | 1480147.2459 | -3777468.4907 | FALSE | 2180 | 359795 | -366037.2624 | 66775.2444 | 533923.9757 | 600699.22 | 933339.0372 | 567301.7747 | TRUE | Option 3 | 567301.7747 | 265
| WND013-78928958 | 272 | 5827309.7492 | -3149937.1814 | 11921.4485 | 1311862.3333 | 1323783.7818 | 418.8024 | 59737.5646 | 60156.367 | 1263627.4148 | -1886309.7666 | FALSE | 1976 | 215560 | -219299.8577 | 4668.2048 | 536091.6382 | 540759.8431 | 783023.9387 | 563724.081 | TRUE | Option 3 | 563724.081 | 266
| DDL011-193014102 | 329 | 7048473.9246 | -3810034.3113 | 761361.3412 | 598694.749 | 1360056.0902 | 26746.7467 | 27262.4386 | 54009.1852 | 1306046.905 | -2503987.4063 | FALSE | 2078 | 260732.5 | -265256.0778 | 298134.1317 | 244656.1965 | 542790.3282 | 817265.762 | 552009.6842 | TRUE | Option 3 | 552009.6842 | 267
| BBD021-24611491 | 107 | 2292360.8205 | -1239129.7 | 309563.9953 | 724244.6545 | 1033808.6498 | 10875.0331 | 25442.8315 | 36317.8646 | 997490.7852 | -241638.9148 | FALSE | 671 | 84797.5 | -86268.694 | 121219.1741 | 283599.967 | 404819.141 | 628989.5088 | 542720.8147 | TRUE | Option 3 | 542720.8147 | 268
| CMN001-132430534 | 123 | 2635143.7469 | -1424420.1225 | 193140.3771 | 836433.249 | 1029573.6261 | 6785.0526 | 29384.0349 | 36169.0875 | 993404.5386 | -431015.5839 | FALSE | 1007 | 97477.5 | -99168.6856 | 75629.9742 | 327530.8148 | 403160.789 | 626412.8371 | 527244.1514 | TRUE | Option 3 | 527244.1514 | 269
| NKA005-24606900 | 150 | 3213589.9352 | -1737097.7103 | 197810.6705 | 867257.7027 | 1065068.3732 | 6949.1208 | 30466.903 | 37416.0237 | 1027652.3495 | -709445.3608 | FALSE | 1377 | 118875 | -120937.4215 | 77458.7693 | 339601.0648 | 417059.8341 | 648008.5391 | 527071.1176 | TRUE | Option 3 | 527071.1176 | 270
| CHA006-202038162 | 339 | 7262713.2536 | -3925840.8253 | 48402.3557 | 1267036.4345 | 1315438.7902 | 1700.3826 | 44511.1943 | 46211.5768 | 1269227.2133 | -2656613.612 | FALSE | 2097 | 268657.5 | -273318.5726 | 18953.4108 | 496146.5559 | 515099.9667 | 800338.8234 | 527020.2508 | TRUE | Option 3 | 527020.2508 | 271
| CLC004-15400582 | 528 | 11311836.5721 | -6114583.9403 | 544773.0706 | 1049412.0174 | 1594185.088 | 19137.9658 | 47786.5067 | 66924.4725 | 1527260.6155 | -4587323.3248 | FALSE | 2205 | 418440 | -425699.7237 | 213322.4234 | 428841.4975 | 642163.9209 | 952021.1671 | 526321.4433 | TRUE | Option 3 | 526321.4433 | 272
| GHP021-190579468 | 260 | 5570222.5544 | -3010969.3645 | 472006.8227 | 753941.5262 | 1225948.3488 | 16581.6758 | 34331.827 | 50913.5028 | 1175034.8461 | -1835934.5184 | FALSE | 1968 | 206050 | -209624.864 | 184828.5914 | 308097.685 | 492926.2764 | 733022.0725 | 523397.2085 | TRUE | Option 3 | 523397.2085 | 273
| NHL031-15417259 | 164 | 3513524.9959 | -1899226.8299 | 232760.1693 | 841090.7037 | 1073850.873 | 8176.9023 | 29547.6521 | 37724.5543 | 1036126.3186 | -863100.5113 | FALSE | 1526 | 129970 | -132224.9142 | 91144.3059 | 329354.5825 | 420498.8883 | 653351.9846 | 521127.0704 | TRUE | Option 3 | 521127.0704 | 274
| KRT013-79724804 | 1028 | 22023803.0229 | -11904909.6413 | 100915.0411 | 2177365.9291 | 2278280.9702 | 3545.1617 | 99149.5331 | 102694.6948 | 2175586.2754 | -9729323.3659 | FALSE | 2243 | 814690 | -828824.4621 | 39516.346 | 889779.0861 | 929295.432 | 1348985.5382 | 520161.0761 | TRUE | Option 3 | 520161.0761 | 275
| TNA022-184844358 | 129 | 2763687.3443 | -1493904.0309 | 717868.0692 | 315842.1655 | 1033710.2347 | 25218.821 | 14382.3336 | 39601.1547 | 994109.08 | -499794.9509 | FALSE | 1099 | 102232.5 | -104006.1825 | 281103.0215 | 129068.6832 | 410171.7048 | 623538.5299 | 519532.3474 | TRUE | Option 3 | 519532.3474 | 276
| KYM003-24602826 | 330 | 7069897.8575 | -3821614.9627 | 107574.555 | 1182106.9871 | 1289681.5421 | 3779.1115 | 41527.6091 | 45306.7206 | 1244374.8215 | -2577240.1412 | FALSE | 2086 | 261525 | -266062.3273 | 42124.0806 | 462889.8542 | 505013.9348 | 784667.6073 | 518605.2799 | TRUE | Option 3 | 518605.2799 | 277
| GHP011-62939475 | 328 | 7027049.9917 | -3798453.6599 | 361632.7665 | 950614.3289 | 1312247.0953 | 12704.2174 | 43287.6099 | 55991.8273 | 1256255.2681 | -2542198.3918 | FALSE | 2084 | 259940 | -264449.8284 | 141608.2811 | 388467.8902 | 530076.1713 | 782170.924 | 517721.0956 | TRUE | Option 3 | 517721.0956 | 278
| STN021-193604803 | 253 | 5420255.0241 | -2929904.8047 | 205209.4429 | 976725.0708 | 1181934.5137 | 7209.0408 | 34312.5092 | 41521.5501 | 1140412.9636 | -1789491.8411 | FALSE | 1957 | 200502.5 | -203981.1176 | 80355.9831 | 382466.3338 | 462822.317 | 719112.1967 | 515131.0791 | TRUE | Option 3 | 515131.0791 | 279
| TQY022-88336509 | 39 | 835533.3832 | -451645.4047 | 836608.1423 | 60014.7823 | 896622.9246 | 29390.179 | 2732.8606 | 32123.0396 | 864499.885 | 412854.4803 | TRUE | 99 | 30907.5 | -31443.7296 | 327599.2995 | 24524.9994 | 352124.299 | 544498.6256 | 513054.896 | TRUE | Option 3 | 513054.896 | 280
| GHP022-190579440 | 300 | 6427179.8705 | -3474195.4206 | 311030.8227 | 947496.9688 | 1258527.7914 | 10926.563 | 43145.6563 | 54072.2193 | 1204455.5721 | -2269739.8485 | FALSE | 2045 | 237750 | -241874.843 | 121793.5548 | 387193.9832 | 508987.538 | 749540.2534 | 507665.4104 | TRUE | Option 3 | 507665.4104 | 281
| OYN005-24603482 | 316 | 6769962.7969 | -3659485.843 | 70661.9033 | 1180056.2664 | 1250718.1696 | 2482.3641 | 41455.5669 | 43937.931 | 1206780.2386 | -2452705.6044 | FALSE | 2070 | 250430 | -254774.8347 | 27669.812 | 462086.8322 | 489756.6442 | 760961.5254 | 506186.6908 | TRUE | Option 3 | 506186.6908 | 282
| CLC014-161744928 | 84 | 1799610.3637 | -972774.7178 | 625716.281 | 318491.3057 | 944207.5868 | 21981.5139 | 14502.9661 | 36484.48 | 907723.1068 | -65051.611 | FALSE | 322 | 66570 | -67724.956 | 245018.1931 | 130151.2526 | 375169.4457 | 569038.1411 | 501313.185 | TRUE | Option 3 | 501313.185 | 283
| MNA014-184029858 | 195 | 4177666.9158 | -2258227.0234 | 399814.8447 | 654145.4453 | 1053960.29 | 14045.56 | 22980.235 | 37025.795 | 1016934.4951 | -1241292.5283 | FALSE | 1774 | 154537.5 | -157218.648 | 156559.6322 | 256150.4949 | 412710.1271 | 641250.1629 | 484031.5149 | TRUE | Option 3 | 484031.5149 | 284
| BGO012-197683994 | 176 | 3770612.1907 | -2038194.6468 | 482011.5742 | 544038.1663 | 1026049.7405 | 16933.1443 | 19112.1485 | 36045.2928 | 990004.4476 | -1048190.1992 | FALSE | 1655 | 139480 | -141899.9079 | 188746.2554 | 213034.6493 | 401780.9047 | 624268.8358 | 482368.9279 | TRUE | Option 3 | 482368.9279 | 285
| RCT022-201142435 | 243 | 5206015.6951 | -2814098.2907 | 25472.4864 | 1088832.4426 | 1114304.929 | 894.8526 | 38250.8593 | 39145.7119 | 1075159.2171 | -1738939.0736 | FALSE | 1946 | 192577.5 | -195918.6228 | 9974.5249 | 426365.3764 | 436339.9013 | 677965.0277 | 482046.4049 | TRUE | Option 3 | 482046.4049 | 286
| ART023-24601770 | 275 | 5891581.5479 | -3184679.1356 | 111864.6247 | 1043308.5781 | 1155173.2029 | 3929.8223 | 36651.5986 | 40581.4209 | 1114591.782 | -2070087.3536 | FALSE | 2011 | 217937.5 | -221718.6061 | 43803.9876 | 408539.1262 | 452343.1138 | 702830.0891 | 481111.4829 | TRUE | Option 3 | 481111.4829 | 287
| SA011-15436594 | 85 | 1821034.2966 | -984355.3692 | 785224.1715 | 120578.2159 | 905802.3874 | 27585.0518 | 5490.7049 | 33075.7567 | 872726.6307 | -111628.7385 | FALSE | 408 | 67362.5 | -68531.2055 | 307478.3469 | 49274.2048 | 356752.5517 | 549049.8357 | 480518.6302 | TRUE | Option 3 | 480518.6302 | 288
| SHL005-24604390 | 141 | 3020774.5391 | -1632871.8477 | 69435.9683 | 903601.1756 | 973037.1439 | 2439.2968 | 31743.655 | 34182.9518 | 938854.1921 | -694017.6556 | FALSE | 1356 | 111742.5 | -113681.1762 | 27189.76 | 353832.4542 | 381022.2142 | 592014.9297 | 478333.7535 | TRUE | Option 3 | 478333.7535 | 289
| TQY031-192995335 | 329 | 7048473.9246 | -3810034.3113 | 615890.4114 | 622541.8015 | 1238432.2129 | 21636.3295 | 28348.3489 | 49984.6783 | 1188447.5346 | -2621586.7767 | FALSE | 2092 | 260732.5 | -265256.0778 | 241170.5758 | 254401.278 | 495571.8538 | 742860.3591 | 477604.2812 | TRUE | Option 3 | 477604.2812 | 290
| EHK031-156804528 | 231 | 4948928.5003 | -2675130.4739 | 112751.9365 | 961048.1976 | 1073800.1341 | 3960.9937 | 33761.7782 | 37722.7719 | 1036077.3622 | -1639053.1117 | FALSE | 1926 | 183067.5 | -186243.6291 | 44151.4415 | 376327.5785 | 420479.02 | 653321.1141 | 467077.485 | TRUE | Option 3 | 467077.485 | 291
| FNS013-73561266 | 231 | 4948928.5003 | -2675130.4739 | 48212.4493 | 1054267.114 | 1102479.5633 | 1693.7111 | 48007.5906 | 49701.3017 | 1052778.2615 | -1622352.2123 | FALSE | 1920 | 183067.5 | -186243.6291 | 18879.0472 | 430825.5294 | 449704.5766 | 652774.9866 | 466531.3575 | TRUE | Option 3 | 466531.3575 | 292
| RCT021-15430691 | 299 | 6405755.9376 | -3462614.7692 | 318387.4796 | 837214.2238 | 1155601.7034 | 11185.0035 | 29411.4707 | 40596.4742 | 1115005.2292 | -2347609.54 | FALSE | 2059 | 236957.5 | -241068.5935 | 124674.277 | 327836.6291 | 452510.9062 | 703090.7972 | 462022.2036 | TRUE | Option 3 | 462022.2036 | 293
| HSM004-24599758 | 354 | 7584072.2472 | -4099550.5963 | 64306.2507 | 1162315.8384 | 1226622.0891 | 2259.089 | 40832.3428 | 43091.4318 | 1183530.6573 | -2916019.939 | FALSE | 2122 | 280545 | -285412.3148 | 25181.0634 | 455140.0295 | 480321.0929 | 746300.9962 | 460888.6815 | TRUE | Option 3 | 460888.6815 | 294
| CLC006-156831394 | 640 | 13711317.057 | -7411616.8973 | 231235.8263 | 1412661.481 | 1643897.3074 | 8123.3519 | 64327.6008 | 72450.9527 | 1571446.3547 | -5840170.5426 | FALSE | 2221 | 507200 | -515999.6651 | 90547.4031 | 577283.1405 | 667830.5436 | 976066.7637 | 460067.0986 | TRUE | Option 3 | 460067.0986 | 295
| RCT022-109224755 | 348 | 7455528.6498 | -4030066.6879 | 394373.9598 | 821181.3737 | 1215555.3335 | 13854.4208 | 28848.2341 | 42702.6549 | 1172852.6786 | -2857214.0093 | FALSE | 2115 | 275790 | -280574.8179 | 154429.0887 | 321558.4803 | 475987.569 | 739567.7645 | 458992.9466 | TRUE | Option 3 | 458992.9466 | 296
| TQY022-192995279 | 150 | 3213589.9352 | -1737097.7103 | 643766.5811 | 318184.0535 | 961950.6346 | 22615.6238 | 14488.9749 | 37104.5987 | 924846.0358 | -812251.6745 | FALSE | 1479 | 118875 | -120937.4215 | 252086.3357 | 130025.6941 | 382112.0299 | 579838.6047 | 458901.1832 | TRUE | Option 3 | 458901.1832 | 297
| GHP021-130746528 | 89 | 1906730.0282 | -1030677.9748 | 679435.0221 | 189772.4919 | 869207.514 | 23868.6619 | 8641.5672 | 32510.2291 | 836697.2849 | -193980.6899 | FALSE | 576 | 70532.5 | -71756.2034 | 266053.396 | 77550.398 | 343603.7939 | 525603.7201 | 453847.5166 | TRUE | Option 3 | 453847.5166 | 298
| CHA006-24606426 | 180 | 3856307.9223 | -2084517.2524 | 111117.2281 | 870498.0764 | 981615.3046 | 3903.5661 | 30580.7378 | 34484.304 | 947131.0006 | -1137386.2517 | FALSE | 1708 | 142650 | -145124.9058 | 43511.3218 | 340869.9314 | 384381.2532 | 597234.0513 | 452109.1455 | TRUE | Option 3 | 452109.1455 | 299
| BAN006-15414916 | 352 | 7541224.3814 | -4076389.2935 | 619652.1841 | 598235.2446 | 1217887.4287 | 21768.4812 | 27241.5143 | 49009.9955 | 1168877.4332 | -2907511.8603 | FALSE | 2121 | 278960 | -283799.8158 | 242643.612 | 244468.4203 | 487112.0323 | 730775.3963 | 446975.5805 | TRUE | Option 3 | 446975.5805 | 300
| WMN014-122227235 | 183 | 3920579.721 | -2119259.2066 | 466762.2938 | 506337.4622 | 973099.756 | 16397.4347 | 17787.7167 | 34185.1514 | 938914.6046 | -1180344.6019 | FALSE | 1738 | 145027.5 | -147543.6542 | 182774.937 | 198271.7948 | 381046.7318 | 592053.0241 | 444509.3699 | TRUE | Option 3 | 444509.3699 | 301
| BET001-163510183 | 48 | 1028348.7793 | -555871.2673 | 112749.0072 | 681382.0895 | 794131.0967 | 3960.8908 | 23937.0627 | 27897.9535 | 766233.1432 | 210361.8759 | TRUE | 110 | 38040 | -38699.9749 | 44150.2944 | 266815.8293 | 310966.1237 | 483164.9731 | 444464.9982 | TRUE | Option 3 | 444464.9982 | 302
| GHP011-190579532 | 554 | 11868858.8275 | -6415680.8767 | 348485.0276 | 1148140.4274 | 1496625.455 | 12242.3352 | 52282.2488 | 64524.5841 | 1432100.8709 | -4983580.0058 | FALSE | 2212 | 439045 | -446662.2101 | 136459.8851 | 469186.7942 | 605646.6793 | 890978.7757 | 444316.5656 | TRUE | Option 3 | 444316.5656 | 303
| ECA005-88419875 | 224 | 4798960.97 | -2594065.9141 | 399759.9637 | 624357.2785 | 1024117.2422 | 14043.632 | 21933.7719 | 35977.4039 | 988139.8383 | -1605926.0757 | FALSE | 1914 | 177520 | -180599.8828 | 156538.1419 | 244486.0344 | 401024.1764 | 623093.0658 | 442493.183 | TRUE | Option 3 | 442493.183 | 304
| EHK021-15417698 | 64 | 1371131.7057 | -741161.6897 | 661381.1751 | 143006.3619 | 804387.537 | 23234.4273 | 5023.8366 | 28258.2639 | 776129.2731 | 34967.5834 | TRUE | 123 | 50720 | -51599.9665 | 258983.8644 | 55998.4796 | 314982.344 | 489405.193 | 437805.2265 | TRUE | Option 3 | 437805.2265 | 305
| BMH006-201878277 | 281 | 6020125.1454 | -3254163.044 | 180399.5827 | 937029.171 | 1117428.7537 | 6337.4664 | 42668.9899 | 49006.4563 | 1068422.2974 | -2185740.7466 | FALSE | 2030 | 222692.5 | -226556.103 | 70640.9297 | 382916.3248 | 453557.2545 | 663871.4992 | 437315.3963 | TRUE | Option 3 | 437315.3963 | 306
| GLE024-15407167 | 484 | 10369183.5244 | -5605035.2786 | 650665.4485 | 727849.3196 | 1378514.7681 | 22857.9821 | 33143.6803 | 56001.6624 | 1322513.1057 | -4282522.1729 | FALSE | 2197 | 383570 | -390224.7467 | 254787.7966 | 297435.1227 | 552222.9193 | 826291.8488 | 436067.102 | TRUE | Option 3 | 436067.102 | 307
| NHL031-202230824 | 191 | 4091971.1842 | -2211904.4178 | 174562.3965 | 792287.1811 | 966849.5776 | 6132.4051 | 27833.1764 | 33965.5816 | 932883.996 | -1279020.4218 | FALSE | 1797 | 151367.5 | -153993.6501 | 68355.2023 | 310244.0826 | 378599.2849 | 588250.2927 | 434256.6427 | TRUE | Option 3 | 434256.6427 | 308
| ART023-63832300 | 157 | 3363557.4656 | -1818162.2701 | 164182.9362 | 754142.2154 | 918325.1517 | 5767.773 | 26493.1376 | 32260.9107 | 886064.241 | -932098.0291 | FALSE | 1584 | 124422.5 | -126581.1678 | 64290.8098 | 295307.264 | 359598.0737 | 558727.0779 | 432145.9101 | TRUE | Option 3 | 432145.9101 | 309
| BAS033-177750890 | 210 | 4499025.9093 | -2431936.7944 | 461795.5167 | 535417.1896 | 997212.7063 | 16222.951 | 24381.0026 | 40603.9536 | 956608.7527 | -1475328.0417 | FALSE | 1873 | 166425 | -169312.3901 | 180830.0447 | 218797.8655 | 399627.9102 | 597584.7961 | 428272.406 | TRUE | Option 3 | 428272.406 | 310
| STL007-15415881 | 119 | 2549448.0153 | -1378097.5168 | 525151.6961 | 334733.125 | 859884.8211 | 18448.6638 | 11759.2287 | 30207.8924 | 829676.9287 | -548420.5882 | FALSE | 1173 | 94307.5 | -95943.6877 | 205639.0789 | 131074.9104 | 336713.9893 | 523170.8318 | 427227.144 | TRUE | Option 3 | 427227.144 | 311
| NHL016-15417067 | 157 | 3363557.4656 | -1818162.2701 | 248521.2194 | 659014.0127 | 907535.2322 | 8730.5905 | 23151.2685 | 31881.8591 | 875653.3731 | -942508.897 | FALSE | 1593 | 124422.5 | -126581.1678 | 97316.0232 | 258056.9302 | 355372.9534 | 552162.2788 | 425581.1109 | TRUE | Option 3 | 425581.1109 | 312
| NHL015-24600904 | 224 | 4798960.97 | -2594065.9141 | 92005.9613 | 898625.0325 | 990630.9938 | 3232.1843 | 31568.8423 | 34801.0266 | 955829.9672 | -1638235.9468 | FALSE | 1925 | 177520 | -180599.8828 | 36027.7255 | 351883.8944 | 387911.6199 | 602719.3739 | 422119.4911 | TRUE | Option 3 | 422119.4911 | 313
| CME015-182988165 | 113 | 2420904.4179 | -1308613.6084 | 405711.6228 | 419180.1085 | 824891.7313 | 14252.7147 | 14725.8648 | 28978.5795 | 795913.1518 | -512700.4567 | FALSE | 1113 | 89552.5 | -91106.1909 | 158868.6946 | 164142.6888 | 323011.3834 | 501880.3479 | 410774.1571 | TRUE | Option 3 | 410774.1571 | 314
| BET007-162663688 | 89 | 1906730.0282 | -1030677.9748 | 141376.0038 | 650963.8933 | 792339.8971 | 4966.5618 | 22868.4665 | 27835.0284 | 764504.8687 | -266173.1061 | FALSE | 725 | 70532.5 | -71756.2034 | 55360.0634 | 254904.6617 | 310264.7251 | 482075.172 | 410318.9685 | TRUE | Option 3 | 410318.9685 | 315
| SHL005-15428613 | 125 | 2677991.6127 | -1447581.4253 | 265271.558 | 553067.9003 | 818339.4583 | 9319.0326 | 19429.3645 | 28748.3971 | 789591.0611 | -657990.3641 | FALSE | 1307 | 99062.5 | -100781.1846 | 103875.1265 | 216570.5156 | 320445.6421 | 497893.8162 | 397112.6316 | TRUE | Option 3 | 397112.6316 | 316
| BAS033-193428108 | 305 | 6534299.535 | -3532098.6776 | 67393.4535 | 997950.9746 | 1065344.4282 | 2367.5429 | 45443.1531 | 47810.696 | 1017533.7322 | -2514564.9454 | FALSE | 2080 | 241712.5 | -245906.0904 | 26389.9514 | 407811.9779 | 434201.9293 | 631142.4989 | 385236.4085 | TRUE | Option 3 | 385236.4085 | 317
| STL005-24599604 | 140 | 2999350.6062 | -1621291.1963 | 183235.9578 | 632990.2528 | 816226.2106 | 6437.1087 | 22237.0497 | 28674.1584 | 787552.0522 | -833739.1441 | FALSE | 1501 | 110950 | -112874.9267 | 71751.5984 | 247866.5375 | 319618.1358 | 496608.0748 | 383733.148 | TRUE | Option 3 | 383733.148 | 318
| ART033-24601322 | 962 | 20609823.4514 | -11140586.6488 | 60166.3525 | 1843183.5821 | 1903349.9346 | 2113.6537 | 64751.3365 | 66864.9901 | 1836484.9445 | -9304101.7043 | FALSE | 2242 | 762385 | -775611.9966 | 23559.9607 | 721754.451 | 745314.4117 | 1158035.5229 | 382423.5263 | TRUE | Option 3 | 382423.5263 | 319
| STL006-15415768 | 56 | 1199740.2425 | -648516.4785 | 430409.1789 | 270763.0443 | 701172.2231 | 15120.3439 | 9511.9494 | 24632.2933 | 676539.9299 | 28023.4514 | TRUE | 124 | 44380 | -45149.9707 | 168539.772 | 106025.4845 | 274565.2565 | 426606.9667 | 381456.996 | TRUE | Option 3 | 381456.996 | 320
| BGO013-163795489 | 56 | 1199740.2425 | -648516.4785 | 162201.6158 | 538844.6444 | 701046.2602 | 5698.1689 | 18929.6993 | 24627.8682 | 676418.392 | 27901.9135 | TRUE | 125 | 44380 | -45149.9707 | 63514.9636 | 211000.9683 | 274515.9319 | 426530.3283 | 381380.3576 | TRUE | Option 3 | 381380.3576 | 321
| CTN006-157466858 | 238 | 5098896.0306 | -2756195.0337 | 178178.8536 | 764025.8823 | 942204.7359 | 6259.4519 | 26840.3525 | 33099.8043 | 909104.9316 | -1847090.1021 | FALSE | 1971 | 188615 | -191887.3755 | 69771.3358 | 299177.5136 | 368948.8494 | 573255.8865 | 381368.511 | TRUE | Option 3 | 381368.511 | 322
| AL014-200635260 | 264 | 5655918.286 | -3057291.9701 | 506723.7746 | 475637.2934 | 982361.068 | 17801.2879 | 21658.8378 | 39460.1258 | 942900.9422 | -2114391.0279 | FALSE | 2019 | 209220 | -212849.8619 | 198423.0672 | 194368.8521 | 392791.9193 | 589569.1487 | 376719.2869 | TRUE | Option 3 | 376719.2869 | 323
| ECA012-202230762 | 509 | 10904781.8469 | -5894551.5636 | 114173.7137 | 1164318.1461 | 1278491.8597 | 4010.941 | 40902.6842 | 44913.6252 | 1233578.2345 | -4660973.3291 | FALSE | 2207 | 403382.5 | -410380.9837 | 44708.1814 | 455924.0938 | 500632.2752 | 777859.5845 | 367478.6009 | TRUE | Option 3 | 367478.6009 | 324
| WBE022-203216606 | 193 | 4134819.05 | -2235065.7206 | 551895.2987 | 308917.5004 | 860812.7991 | 19388.1708 | 14067.0089 | 33455.1798 | 827357.6194 | -1407708.1012 | FALSE | 1845 | 152952.5 | -155606.149 | 216111.3479 | 126238.9236 | 342350.2715 | 518462.5276 | 362856.3786 | TRUE | Option 3 | 362856.3786 | 325
| CHM011-24600428 | 357 | 7648344.0459 | -4134292.5505 | 18864.7566 | 1043098.6963 | 1061963.4529 | 662.7219 | 36644.2254 | 37306.9474 | 1024656.5056 | -3109636.045 | FALSE | 2144 | 282922.5 | -287831.0632 | 7387.0678 | 408456.9406 | 415844.0084 | 646119.4445 | 358288.3813 | TRUE | Option 3 | 358288.3813 | 326
| CHA006-15429283 | 274 | 5870157.615 | -3173098.4842 | 234659.3393 | 709718.1854 | 944377.5247 | 8243.6204 | 24932.5143 | 33176.1347 | 911201.3899 | -2261897.0942 | FALSE | 2043 | 217145 | -220912.3566 | 91887.9835 | 277911.6873 | 369799.6708 | 574577.8539 | 353665.4973 | TRUE | Option 3 | 353665.4973 | 327
| OYN001-24603328 | 384 | 8226790.2342 | -4446970.1384 | 8661.2974 | 1081022.058 | 1089683.3554 | 304.2728 | 37976.4792 | 38280.752 | 1051402.6034 | -3395567.535 | FALSE | 2163 | 304320 | -309599.7991 | 3391.5938 | 423306.9834 | 426698.5772 | 662984.7782 | 353384.9792 | TRUE | Option 3 | 353384.9792 | 328
| WPD012-24603816 | 130 | 2785111.2772 | -1505484.6823 | 536509.9077 | 214452.1451 | 750962.0527 | 18847.6796 | 9765.3912 | 28613.0708 | 722348.9819 | -783135.7003 | FALSE | 1452 | 103025 | -104812.432 | 210086.7312 | 87635.7213 | 297722.4525 | 453239.6002 | 348427.1682 | TRUE | Option 3 | 348427.1682 | 329
| WBE023-139765778 | 486 | 10412031.3902 | -5628196.5814 | 161925.3956 | 1084649.5125 | 1246574.9081 | 5688.4653 | 49391.0974 | 55079.5627 | 1191495.3454 | -4436701.236 | FALSE | 2201 | 385155 | -391837.2457 | 63406.8012 | 443241.2756 | 506648.0768 | 739926.8312 | 348089.5855 | TRUE | Option 3 | 348089.5855 | 330
| DDL023-197602323 | 437 | 9362258.678 | -5060744.6627 | 600063.6083 | 556557.3012 | 1156620.9096 | 21080.3313 | 25343.6484 | 46423.9797 | 1110196.9298 | -3950547.7329 | FALSE | 2189 | 346322.5 | -352331.0213 | 234973.1109 | 227436.7575 | 462409.8684 | 694211.0412 | 341880.0199 | TRUE | Option 3 | 341880.0199 | 331
| BAS033-193428083 | 356 | 7626920.113 | -4122711.8991 | 30910.9221 | 1024639.1769 | 1055550.099 | 1085.9057 | 46658.4393 | 47744.345 | 1007805.7541 | -3114906.1451 | FALSE | 2145 | 282130 | -287024.8137 | 12104.1093 | 418718.0934 | 430822.2027 | 624727.8963 | 337703.0826 | TRUE | Option 3 | 337703.0826 | 332
| CMN001-182014538 | 100 | 2142393.2902 | -1158065.1402 | 54876.226 | 629648.6684 | 684524.8943 | 1927.8107 | 22119.6593 | 24047.4699 | 660477.4244 | -497587.7158 | FALSE | 1095 | 79250 | -80624.9477 | 21488.4511 | 246558.0387 | 268046.4898 | 416478.4045 | 335853.4568 | TRUE | Option 3 | 335853.4568 | 333
| KGT003-15424502 | 329 | 7048473.9246 | -3810034.3113 | 86565.4724 | 894217.6887 | 980783.1611 | 3041.059 | 31414.0116 | 34455.0706 | 946328.0904 | -2863706.2208 | FALSE | 2117 | 260732.5 | -265256.0778 | 33897.337 | 350158.0652 | 384055.4022 | 596727.7588 | 331471.681 | TRUE | Option 3 | 331471.681 | 334
| KYM004-24596836 | 143 | 3063622.4049 | -1656033.1505 | 54109.5849 | 676999.9216 | 731109.5065 | 1900.8784 | 23783.1164 | 25683.9949 | 705425.5116 | -950607.6388 | FALSE | 1597 | 113327.5 | -115293.6752 | 21188.2496 | 265099.8585 | 286288.108 | 444821.3985 | 329527.7233 | TRUE | Option 3 | 329527.7233 | 335
| SHP012-24612048 | 100 | 2142393.2902 | -1158065.1402 | 210198.6307 | 451954.0973 | 662152.728 | 7384.3118 | 15877.2203 | 23261.5321 | 638891.1959 | -519173.9443 | FALSE | 1131 | 79250 | -80624.9477 | 82309.651 | 176976.3384 | 259285.9894 | 402866.7386 | 322241.791 | TRUE | Option 3 | 322241.791 | 336
| BBD013-24614080 | 162 | 3470677.1301 | -1876065.5271 | 328701.933 | 408812.8126 | 737514.7456 | 11547.3519 | 14361.66 | 25909.0119 | 711605.7337 | -1164459.7934 | FALSE | 1728 | 128385 | -130612.4152 | 128713.2142 | 160083.0595 | 288796.2737 | 448718.4719 | 318106.0567 | TRUE | Option 3 | 318106.0567 | 337
| KYM003-15421938 | 452 | 9683617.6715 | -5234454.4337 | 169753.7537 | 945182.7729 | 1114936.5266 | 5963.4767 | 33204.4232 | 39167.9 | 1075768.6266 | -4158685.8071 | FALSE | 2194 | 358210 | -364424.7635 | 66472.2323 | 370114.9901 | 436587.2225 | 678349.3041 | 313924.5406 | TRUE | Option 3 | 313924.5406 | 338
| HSM003-24600316 | 185 | 3963427.5868 | -2142420.5094 | 148035.8787 | 602798.8136 | 750834.6924 | 5200.5243 | 21176.4195 | 26376.9438 | 724457.7485 | -1417962.7608 | FALSE | 1849 | 146612.5 | -149156.1532 | 57967.9395 | 236044.1635 | 294012.103 | 456822.5894 | 307666.4362 | TRUE | Option 3 | 307666.4362 | 339
| TQY021-24613536 | 275 | 5891581.5479 | -3184679.1356 | 447054.0672 | 433730.3102 | 880784.3774 | 15705.0815 | 19750.5422 | 35455.6237 | 845328.7537 | -2339350.3819 | FALSE | 2057 | 217937.5 | -221718.6061 | 175057.5829 | 177243.5923 | 352301.1752 | 528483.2021 | 306764.596 | TRUE | Option 3 | 306764.596 | 340
| WIN023-160628335 | 397 | 8505301.3619 | -4597518.6066 | 196495.0561 | 857538.3254 | 1054033.3816 | 6902.903 | 39049.2583 | 45952.1613 | 1008081.2202 | -3589437.3864 | FALSE | 2172 | 314622.5 | -320081.0423 | 76943.6006 | 350432.4456 | 427376.0462 | 626657.3354 | 306576.2931 | TRUE | Option 3 | 306576.2931 | 341
| STL006-24613426 | 134 | 2870807.0088 | -1551807.2879 | 299369.3022 | 377278.6373 | 676647.9395 | 10516.8919 | 13253.8594 | 23770.7512 | 652877.1883 | -898930.0996 | FALSE | 1562 | 106195 | -108037.4299 | 117227.1327 | 147734.8965 | 264962.0292 | 411685.9103 | 303648.4804 | TRUE | Option 3 | 303648.4804 | 342
| RVL008-24613925 | 109 | 2335208.6863 | -1262291.0028 | 308782.4565 | 324491.6528 | 633274.1093 | 10847.5775 | 11399.4441 | 22247.0216 | 611027.0877 | -651263.9151 | FALSE | 1296 | 86382.5 | -87881.193 | 120913.1388 | 127064.5513 | 247977.6901 | 385296.4192 | 297415.2263 | TRUE | Option 3 | 297415.2263 | 343
| KGT004-24605978 | 154 | 3299285.6668 | -1783420.3159 | 42783.4764 | 643728.5528 | 686512.0292 | 1502.9904 | 22614.2879 | 24117.2783 | 662394.7509 | -1121025.565 | FALSE | 1697 | 122045 | -124162.4194 | 16753.1682 | 252071.4446 | 268824.6128 | 417687.4164 | 293524.997 | TRUE | Option 3 | 293524.997 | 344
| HTN013-182145838 | 249 | 5334559.2925 | -2883582.1991 | 37287.7646 | 783483.0106 | 820770.7752 | 1309.9252 | 35677.0415 | 36986.9667 | 783783.8085 | -2099798.3906 | FALSE | 2014 | 197332.5 | -200756.1197 | 14601.1555 | 320169.7922 | 334770.9477 | 485999.8275 | 285243.7078 | TRUE | Option 3 | 285243.7078 | 345
| BBD022-15437908 | 28 | 599870.1212 | -324258.2393 | 405976.3176 | 97126.3411 | 503102.6587 | 14262.0135 | 3412.064 | 17674.0775 | 485428.5811 | 161170.3419 | TRUE | 114 | 22190 | -22574.9853 | 158972.3439 | 38032.7655 | 197005.1094 | 306097.5493 | 283522.5639 | TRUE | Option 3 | 283522.5639 | 346
| WBE032-24612505 | 80 | 1713914.6321 | -926452.1122 | 409648.956 | 162281.4005 | 571930.3565 | 14391.0339 | 7389.7202 | 21780.7541 | 550149.6023 | -376302.5098 | FALSE | 921 | 63400 | -64499.9581 | 160410.4768 | 66316.1825 | 226726.6593 | 345203.6972 | 280703.739 | TRUE | Option 3 | 280703.739 | 347
| HSM004-163582339 | 123 | 2635143.7469 | -1424420.1225 | 9843.294 | 606949.831 | 616793.1249 | 345.7965 | 21322.2454 | 21668.0419 | 595125.083 | -829295.0395 | FALSE | 1494 | 97477.5 | -99168.6856 | 3854.4404 | 237669.6203 | 241524.0606 | 375269.0643 | 276100.3786 | TRUE | Option 3 | 276100.3786 | 348
| BAS033-139662229 | 68 | 1456827.4373 | -787484.2953 | 18737.8973 | 537254.3843 | 555992.2816 | 658.2654 | 24464.6619 | 25122.9273 | 530869.3543 | -256614.9411 | FALSE | 711 | 53890 | -54824.9644 | 7337.3922 | 219548.6338 | 226886.026 | 329106.2556 | 274281.2912 | TRUE | Option 3 | 274281.2912 | 349
| BAN006-193339156 | 216 | 4627569.5068 | -2501420.7028 | 110028.2425 | 636249.476 | 746277.7184 | 3865.3099 | 28972.5478 | 32837.8577 | 713439.8607 | -1787980.8421 | FALSE | 1956 | 171180 | -174149.887 | 43084.8964 | 260002.9098 | 303087.8062 | 443189.9122 | 269040.0252 | TRUE | Option 3 | 269040.0252 | 350
| STL005-15415831 | 185 | 3963427.5868 | -2142420.5094 | 283358.7695 | 393362.2122 | 676720.9816 | 9954.4393 | 13818.8779 | 23773.3172 | 652947.6644 | -1489472.845 | FALSE | 1878 | 146612.5 | -149156.1532 | 110957.7229 | 154032.9082 | 264990.6311 | 411730.3506 | 262574.1974 | TRUE | Option 3 | 262574.1974 | 351
| BET007-63637518 | 164 | 3513524.9959 | -1899226.8299 | 396180.4105 | 251212.8986 | 647393.3091 | 13917.8817 | 8825.1496 | 22743.0314 | 624650.2778 | -1274576.5522 | FALSE | 1791 | 129970 | -132224.9142 | 155136.4593 | 98370.0319 | 253506.4911 | 393886.818 | 261661.9038 | TRUE | Option 3 | 261661.9038 | 352
| CHA005-15429107 | 164 | 3513524.9959 | -1899226.8299 | 150257.8122 | 495056.8808 | 645314.693 | 5278.5812 | 17391.4281 | 22670.0092 | 622644.6838 | -1276582.1462 | FALSE | 1794 | 129970 | -132224.9142 | 58838.005 | 193854.541 | 252692.5459 | 392622.1471 | 260397.2329 | TRUE | Option 3 | 260397.2329 | 353
| NKA001-24606104 | 258 | 5527374.6886 | -2987808.0617 | 51367.3616 | 706916.7129 | 758284.0745 | 1804.5437 | 24834.0981 | 26638.6418 | 731645.4327 | -2256162.629 | FALSE | 2040 | 204465 | -208012.365 | 20114.4488 | 276814.6857 | 296929.1346 | 461354.9399 | 253342.5749 | TRUE | Option 3 | 253342.5749 | 354
| TRG022-176898220 | 742 | 15896558.213 | -8592843.3403 | 181101.4583 | 1252649.7994 | 1433751.2576 | 6362.1234 | 57041.2355 | 63403.3589 | 1370347.8987 | -7222495.4416 | FALSE | 2234 | 588035 | -598237.1117 | 70915.7703 | 511894.4771 | 582810.2474 | 850941.0102 | 252703.8985 | TRUE | Option 3 | 252703.8985 | 355
| EHK031-156804503 | 105 | 2249512.9547 | -1215968.3972 | 108934.1747 | 444029.5805 | 552963.7551 | 3826.8751 | 15598.8308 | 19425.7059 | 533538.0492 | -682430.348 | FALSE | 1343 | 83212.5 | -84656.1951 | 42656.481 | 173873.2534 | 216529.7344 | 336434.0207 | 251777.8257 | TRUE | Option 3 | 251777.8257 | 356
| ECA007-15422655 | 59 | 1264012.0412 | -683258.4327 | 264123.5789 | 218393.365 | 482516.9439 | 9278.7039 | 7672.1941 | 16950.8981 | 465566.0458 | -217692.3869 | FALSE | 624 | 46757.5 | -47568.7191 | 103425.6004 | 85518.5478 | 188944.1482 | 293572.7957 | 246004.0765 | TRUE | Option 3 | 246004.0765 | 357
| GSB012-24607362 | 196 | 4199090.8487 | -2269807.6748 | 122220.6415 | 555748.4624 | 677969.1039 | 4293.6308 | 25306.8168 | 29600.4476 | 648368.6563 | -1621439.0185 | FALSE | 1919 | 155330 | -158024.8974 | 47859.2002 | 227106.2261 | 274965.4262 | 403003.6776 | 244978.7802 | TRUE | Option 3 | 244978.7802 | 358
| CLC013-24602784 | 227 | 4863232.7687 | -2628807.8683 | 122791.0624 | 596791.33 | 719582.3924 | 4313.6698 | 27175.7636 | 31489.4334 | 688092.959 | -1940714.9093 | FALSE | 1989 | 179897.5 | -183018.6312 | 48082.5658 | 243878.3656 | 291960.9314 | 427621.461 | 244602.8298 | TRUE | Option 3 | 244602.8298 | 359
| MRO008-24606844 | 91 | 1949577.894 | -1053839.2776 | 24977.2085 | 497274.8886 | 522252.097 | 877.4534 | 17469.347 | 18346.8004 | 503905.2966 | -549933.9809 | FALSE | 1175 | 72117.5 | -73368.7024 | 9780.5837 | 194723.0692 | 204503.6529 | 317748.4441 | 244379.7417 | TRUE | Option 3 | 244379.7417 | 360
| CLC004-24597506 | 654 | 14011252.1177 | -7573746.0169 | 123030.2419 | 1176726.4104 | 1299756.6524 | 4322.0722 | 53583.9533 | 57906.0255 | 1241850.6268 | -6331895.3901 | FALSE | 2225 | 518295 | -527287.1578 | 48176.2238 | 480868.4365 | 529044.6603 | 770711.9921 | 243424.8343 | TRUE | Option 3 | 243424.8343 | 361
| CTN006-158006328 | 153 | 3277861.7339 | -1771839.6645 | 127170.0967 | 469335.9699 | 596506.0666 | 4467.506 | 16487.8483 | 20955.3543 | 575550.7122 | -1196288.9523 | FALSE | 1746 | 121252.5 | -123356.1699 | 49797.3095 | 183782.7379 | 233580.0475 | 362926.0191 | 239569.8492 | TRUE | Option 3 | 239569.8492 | 362
| DDL022-197602273 | 248 | 5313135.3596 | -2872001.5477 | 466777.6674 | 262693.4475 | 729471.1149 | 16397.9747 | 11962.1292 | 28360.104 | 701111.0109 | -2170890.5368 | FALSE | 2028 | 196540 | -199949.8702 | 182780.957 | 107349.4962 | 290130.4533 | 439340.6617 | 239390.7914 | TRUE | Option 3 | 239390.7914 | 363
| HTN034-182145744 | 224 | 4798960.97 | -2594065.9141 | 55358.9017 | 652359.3623 | 707718.264 | 1944.7671 | 29706.135 | 31650.9021 | 676067.3618 | -1917998.5522 | FALSE | 1984 | 177520 | -180599.8828 | 21677.4575 | 266586.2037 | 288263.6612 | 419454.6028 | 238854.72 | TRUE | Option 3 | 238854.72 | 364
| GHP021-24614163 | 143 | 3063622.4049 | -1656033.1505 | 327981.7538 | 261309.5446 | 589291.2985 | 11522.0519 | 11899.1112 | 23421.1631 | 565870.1354 | -1090163.0151 | FALSE | 1677 | 113327.5 | -115293.6752 | 128431.2062 | 106783.9653 | 235215.1715 | 354076.127 | 238782.4518 | TRUE | Option 3 | 238782.4518 | 365
| ECA005-15422679 | 42 | 899805.1819 | -486387.3589 | 367824.8794 | 79304.7631 | 447129.6425 | 12921.7473 | 2785.9891 | 15707.7364 | 431421.906 | -54965.4528 | FALSE | 304 | 33285 | -33862.478 | 144032.9908 | 31054.186 | 175087.1768 | 272042.4657 | 238179.9877 | TRUE | Option 3 | 238179.9877 | 366
| HSM004-24599744 | 180 | 3856307.9223 | -2084517.2524 | 38430.6711 | 588609.6968 | 627040.3679 | 1350.0757 | 20677.9536 | 22028.0292 | 605012.3387 | -1479504.9137 | FALSE | 1875 | 142650 | -145124.9058 | 15048.6952 | 230487.9843 | 245536.6795 | 381503.6884 | 236378.7826 | TRUE | Option 3 | 236378.7826 | 367
| BAS011-24598608 | 421 | 9019475.7516 | -4875454.2403 | 50556.5157 | 918400.5736 | 968957.0893 | 1776.0585 | 41820.7095 | 43596.7681 | 925360.3212 | -3950093.919 | FALSE | 2188 | 333642.5 | -339431.0297 | 19796.9375 | 375303.7614 | 395100.6989 | 573856.3904 | 234425.3607 | TRUE | Option 3 | 234425.3607 | 368
| HTN013-190418811 | 224 | 4798960.97 | -2594065.9141 | 205695.2692 | 485179.4361 | 690874.7052 | 7226.108 | 22093.3532 | 29319.4612 | 661555.244 | -1932510.67 | FALSE | 1987 | 177520 | -180599.8828 | 80546.2231 | 198268.2421 | 278814.4652 | 412060.24 | 231460.3572 | TRUE | Option 3 | 231460.3572 | 369
| WPD033-153773704 | 331 | 7091321.7904 | -3833195.6141 | 59409.3513 | 779267.0978 | 838676.4491 | 2087.0601 | 35485.0638 | 37572.1239 | 801104.3252 | -3032091.2889 | FALSE | 2138 | 262317.5 | -266868.5768 | 23263.5339 | 318446.9624 | 341710.4962 | 496965.9528 | 230097.376 | TRUE | Option 3 | 230097.376 | 370
| BAN008-193386449 | 304 | 6512875.6021 | -3520518.0262 | 87491.9648 | 707935.9813 | 795427.9461 | 3073.6068 | 32236.8974 | 35310.5042 | 760117.4419 | -2760400.5843 | FALSE | 2104 | 240920 | -245099.8409 | 34260.1332 | 289297.5508 | 323557.684 | 471870.2621 | 226770.4212 | TRUE | Option 3 | 226770.4212 | 371
| NHL015-158008058 | 86 | 1842458.2295 | -995936.0206 | 4824.4132 | 476775.2378 | 481599.6509 | 169.4824 | 16749.191 | 16918.6734 | 464680.9775 | -531255.043 | FALSE | 1149 | 68155 | -69337.455 | 1889.1453 | 186695.809 | 188584.9543 | 293014.6966 | 223677.2416 | TRUE | Option 3 | 223677.2416 | 372
| CHA003-24606706 | 115 | 2463752.2837 | -1331774.9112 | 46880.1707 | 471806.096 | 518686.2667 | 1646.908 | 16574.6242 | 18221.5322 | 500464.7345 | -831310.1767 | FALSE | 1498 | 91137.5 | -92718.6898 | 18357.3531 | 184749.9908 | 203107.3439 | 315578.9228 | 222860.233 | TRUE | Option 3 | 222860.233 | 373
| STL005-24613578 | 128 | 2742263.4114 | -1482323.3795 | 53277.17 | 478064.7095 | 531341.8795 | 1871.6356 | 16794.4903 | 18666.1259 | 512675.7536 | -969647.6259 | FALSE | 1604 | 101440 | -103199.933 | 20862.2923 | 187200.7408 | 208063.033 | 323278.8465 | 220078.9134 | TRUE | Option 3 | 220078.9134 | 374
| HSM005-160318639 | 162 | 3470677.1301 | -1876065.5271 | 4523.7391 | 569276.0877 | 573799.8268 | 158.9197 | 19998.7608 | 20157.6804 | 553642.1464 | -1322423.3808 | FALSE | 1810 | 128385 | -130612.4152 | 1771.4073 | 222917.3231 | 224688.7304 | 349111.0964 | 218498.6812 | TRUE | Option 3 | 218498.6812 | 375
| CDN002-15400020 | 920 | 19710018.2695 | -10654199.2899 | 83072.8074 | 1537824.5069 | 1620897.3143 | 2918.3611 | 70027.0817 | 72945.4428 | 1547951.8715 | -9106247.4184 | FALSE | 2241 | 729100 | -741749.5186 | 32529.6781 | 628430.9247 | 660960.6028 | 959936.7116 | 218187.193 | TRUE | Option 3 | 218187.193 | 376
| WMN014-62615661 | 35 | 749837.6516 | -405322.7991 | 340163.8567 | 64507.9221 | 404671.7788 | 11950.0111 | 2266.1737 | 14216.1848 | 390455.594 | -14867.2051 | FALSE | 254 | 27737.5 | -28218.7317 | 133201.4782 | 25260.034 | 158461.5121 | 246210.2667 | 217991.535 | TRUE | Option 3 | 217991.535 | 377
| EHK024-63048145 | 238 | 5098896.0306 | -2756195.0337 | 68436.639 | 597562.22 | 665998.859 | 2404.1902 | 20992.4572 | 23396.6473 | 642602.2116 | -2113592.822 | FALSE | 2018 | 188615 | -191887.3755 | 26798.4423 | 233993.6164 | 260792.0586 | 405206.8003 | 213319.4249 | TRUE | Option 3 | 213319.4249 | 378
| AL006-200403372 | 209 | 4477601.9764 | -2420356.143 | 285172.1381 | 351087.5646 | 636259.7027 | 10018.1432 | 15987.2843 | 26005.4275 | 610254.2752 | -1810101.8678 | FALSE | 1964 | 165632.5 | -168506.1406 | 111667.8024 | 143471.6913 | 255139.4936 | 381120.2091 | 212614.0684 | TRUE | Option 3 | 212614.0684 | 379
| DDL021-193014245 | 425 | 9105171.4832 | -4921776.8459 | 383644.3585 | 537875.1271 | 921519.4856 | 13477.4882 | 24492.9284 | 37970.4165 | 883549.069 | -4038227.7768 | FALSE | 2193 | 336812.5 | -342656.0276 | 150227.5877 | 219802.2999 | 370029.8877 | 551489.5979 | 208833.5703 | TRUE | Option 3 | 208833.5703 | 380
| CTN006-24603272 | 174 | 3727764.3249 | -2015033.344 | 74146.3146 | 499400.5442 | 573546.8588 | 2604.772 | 17544.0217 | 20148.7936 | 553398.0652 | -1461635.2788 | FALSE | 1865 | 137895 | -140287.409 | 29034.239 | 195555.4342 | 224589.6731 | 348957.1857 | 208669.7768 | TRUE | Option 3 | 208669.7768 | 381
| HSM006-160439562 | 175 | 3749188.2578 | -2026613.9954 | 13703.1289 | 555485.4404 | 569188.5693 | 481.3931 | 19514.2931 | 19995.6862 | 549192.8831 | -1477421.1123 | FALSE | 1874 | 138687.5 | -141093.6584 | 5365.8759 | 217517.1768 | 222883.0526 | 346305.5167 | 205211.8582 | TRUE | Option 3 | 205211.8582 | 382
| SHL005-24613604 | 128 | 2742263.4114 | -1482323.3795 | 52483.68 | 452841.0848 | 505324.7649 | 1843.7601 | 15908.3803 | 17752.1405 | 487572.6244 | -994750.7551 | FALSE | 1620 | 101440 | -103199.933 | 20551.5772 | 177323.6653 | 197875.2425 | 307449.5224 | 204249.5894 | TRUE | Option 3 | 204249.5894 | 383
| HSM004-160424470 | 152 | 3256437.801 | -1760259.0131 | 12138.5983 | 524336.3432 | 536474.9416 | 426.4309 | 18420.0203 | 18846.4512 | 517628.4904 | -1242630.5227 | FALSE | 1776 | 120460 | -122549.9205 | 4753.2365 | 205319.8028 | 210073.0392 | 326401.9024 | 203851.9819 | TRUE | Option 3 | 203851.9819 | 384
| CME015-15423773 | 229 | 4906080.6345 | -2651969.1711 | 215499.3784 | 416956.2259 | 632455.6044 | 7570.5279 | 14647.7395 | 22218.2674 | 610237.337 | -2041731.8341 | FALSE | 2007 | 181482.5 | -184631.1302 | 84385.3196 | 163271.8601 | 247657.1796 | 384798.4247 | 200167.2945 | TRUE | Option 3 | 200167.2945 | 385
| HSM003-24601840 | 297 | 6362908.0718 | -3439453.4664 | 124755.3552 | 592923.1921 | 717678.5474 | 4382.6757 | 20829.4874 | 25212.1631 | 692466.3843 | -2746987.0821 | FALSE | 2103 | 235372.5 | -239456.0946 | 48851.7442 | 232177.0643 | 281028.8085 | 436649.7389 | 197193.6443 | TRUE | Option 3 | 197193.6443 | 386
| HSM002-158165458 | 51 | 1092620.578 | -590613.2215 | 12542.4102 | 374194.0627 | 386736.4728 | 440.6169 | 13145.4978 | 13586.1147 | 373150.3582 | -217462.8633 | FALSE | 622 | 40417.5 | -41118.7233 | 4911.3612 | 146527.0377 | 151438.3989 | 235298.0739 | 194179.3506 | TRUE | Option 3 | 194179.3506 | 387
| BET006-123629680 | 69 | 1478251.3702 | -799064.9467 | 36062.1438 | 370128.8135 | 406190.9573 | 1266.8689 | 13002.6849 | 14269.5538 | 391921.4035 | -407143.5432 | FALSE | 974 | 54682.5 | -55631.2139 | 14121.2265 | 144935.1661 | 159056.3926 | 247134.5648 | 191503.3509 | TRUE | Option 3 | 191503.3509 | 388
| SHL002-15428854 | 98 | 2099545.4244 | -1134903.8374 | 264712.2224 | 177284.6474 | 441996.8697 | 9299.3831 | 6228.0383 | 15527.4213 | 426469.4484 | -708434.389 | FALSE | 1375 | 77665 | -79012.4487 | 103656.1016 | 69421.1822 | 173077.2839 | 268919.5859 | 189907.1372 | TRUE | Option 3 | 189907.1372 | 389
| OYN005-159372302 | 271 | 5805885.8163 | -3138356.53 | 1681.132 | 669401.5811 | 671082.7132 | 59.0584 | 23516.1855 | 23575.2439 | 647507.4692 | -2490849.0607 | FALSE | 2077 | 214767.5 | -218493.6082 | 658.2982 | 262124.4977 | 262782.796 | 408299.9172 | 189806.309 | TRUE | Option 3 | 189806.309 | 390
| WMN021-65221877 | 10 | 214239.329 | -115806.514 | 303333.2728 | 13197.2843 | 316530.5571 | 10656.1468 | 463.6227 | 11119.7695 | 305410.7876 | 189604.2735 | TRUE | 112 | 7925 | -8062.4948 | 118779.3456 | 5167.797 | 123947.1427 | 192583.4144 | 184520.9196 | TRUE | Option 2 | 189604.2735 | 391
| HSM004-160294257 | 108 | 2313784.7534 | -1250710.3514 | 7501.2714 | 445595.8423 | 453097.1138 | 263.5209 | 15653.8538 | 15917.3747 | 437179.7391 | -813530.6123 | FALSE | 1480 | 85590 | -87074.9435 | 2937.3504 | 174486.5708 | 177423.9212 | 275673.1926 | 188598.2491 | TRUE | Option 3 | 188598.2491 | 392
| WMN013-117981106 | 53 | 1135468.4438 | -613774.5243 | 256938.0119 | 117501.7226 | 374439.7345 | 9026.2738 | 4127.8545 | 13154.1283 | 361285.6063 | -252488.918 | FALSE | 695 | 42002.5 | -42731.2223 | 100611.8737 | 46011.3643 | 146623.238 | 227816.4965 | 185085.2743 | TRUE | Option 3 | 185085.2743 | 393
| SHL004-15428865 | 187 | 4006275.4526 | -2165581.8122 | 217143.3986 | 333791.222 | 550934.6206 | 7628.2826 | 11726.1395 | 19354.4221 | 531580.1985 | -1634001.6137 | FALSE | 1924 | 148197.5 | -150768.6522 | 85029.0855 | 130706.0797 | 215735.1652 | 335199.4553 | 184430.8032 | TRUE | Option 3 | 184430.8032 | 394
| MBN013-24605754 | 80 | 1713914.6321 | -926452.1122 | 109564.0518 | 294328.4173 | 403892.4691 | 3849.0028 | 10339.8048 | 14188.8076 | 389703.6616 | -536748.4506 | FALSE | 1158 | 63400 | -64499.9581 | 42903.1285 | 115253.2213 | 158156.3498 | 245736.1194 | 181236.1612 | TRUE | Option 3 | 181236.1612 | 395
| BET001-163510254 | 16 | 342782.9264 | -185290.4224 | 160009.5361 | 158335.037 | 318344.5731 | 5621.1608 | 5562.3354 | 11183.4962 | 307161.0769 | 121870.6545 | TRUE | 119 | 12680 | -12899.9916 | 62656.5883 | 62000.8874 | 124657.4757 | 193687.0974 | 180787.1058 | TRUE | Option 3 | 180787.1058 | 396
| CMN004-76547682 | 90 | 1928153.9611 | -1042258.6262 | 0 | 416287.6613 | 416287.6613 | 0 | 14624.2527 | 14624.2527 | 401663.4086 | -640595.2176 | FALSE | 1287 | 71325 | -72562.4529 | 0 | 163010.0633 | 163010.0633 | 253277.5979 | 180715.145 | TRUE | Option 3 | 180715.145 | 397
| HTN011-190418905 | 140 | 2999350.6062 | -1621291.1963 | 101766.5888 | 390755.6037 | 492522.1924 | 3575.0767 | 17793.6263 | 21368.703 | 471153.4895 | -1150137.7068 | FALSE | 1717 | 110950 | -112874.9267 | 39849.7953 | 159682.0081 | 199531.8034 | 292990.3891 | 180115.4623 | TRUE | Option 3 | 180115.4623 | 398
| OYN005-161887259 | 283 | 6062973.0112 | -3277324.3468 | 30985.5576 | 636510.5672 | 667496.1248 | 1088.5276 | 22360.7189 | 23449.2465 | 644046.8783 | -2633277.4685 | FALSE | 2093 | 224277.5 | -228168.6019 | 12133.3351 | 249245.0234 | 261378.3585 | 406117.7663 | 177949.1644 | TRUE | Option 3 | 177949.1644 | 399
| KGT004-154878429 | 175 | 3749188.2578 | -2026613.9954 | 8088.1561 | 513721.8496 | 521810.0057 | 284.1382 | 18047.1314 | 18331.2696 | 503478.736 | -1523135.2593 | FALSE | 1892 | 138687.5 | -141093.6584 | 3167.1629 | 201163.3758 | 204330.5387 | 317479.467 | 176385.8086 | TRUE | Option 3 | 176385.8086 | 400
| CME021-15423564 | 76 | 1628218.9005 | -880129.5066 | 241645.776 | 143557.2855 | 385203.0615 | 8489.0551 | 5043.1906 | 13532.2457 | 371670.8158 | -508458.6907 | FALSE | 1105 | 60230 | -61274.9602 | 94623.7348 | 56214.2105 | 150837.9452 | 234365.1163 | 173090.156 | TRUE | Option 3 | 173090.156 | 401
| GHP012-77546539 | 142 | 3042198.472 | -1644452.4991 | 339216.4881 | 137111.7222 | 476328.2103 | 11916.7299 | 6243.5822 | 18160.3122 | 458167.8982 | -1186284.6009 | FALSE | 1741 | 112535 | -114487.4257 | 132830.5072 | 56030.6108 | 188861.118 | 287467.0923 | 172979.6666 | TRUE | Option 3 | 172979.6666 | 402
| BET006-130742783 | 101 | 2163817.2231 | -1169645.7916 | 8063.2752 | 409980.4296 | 418043.7048 | 283.2642 | 14402.6786 | 14685.9428 | 403357.762 | -766288.0296 | FALSE | 1436 | 80042.5 | -81431.1972 | 3157.42 | 160540.2754 | 163697.6954 | 254346.0094 | 172914.8122 | TRUE | Option 3 | 172914.8122 | 403
| RCT013-24605182 | 160 | 3427829.2643 | -1852904.2243 | 180594.835 | 315268.4959 | 495863.3309 | 6344.3257 | 11075.4331 | 17419.7588 | 478443.5721 | -1374460.6522 | FALSE | 1835 | 126800 | -128999.9163 | 70717.3866 | 123452.9443 | 194170.331 | 301692.9999 | 172693.0836 | TRUE | Option 3 | 172693.0836 | 404
| HSM006-24597826 | 72 | 1542523.1689 | -833806.9009 | 126507.6055 | 251675.1813 | 378182.7867 | 4444.2326 | 8841.3897 | 13285.6223 | 364897.1645 | -468909.7365 | FALSE | 1048 | 57060 | -58049.9623 | 49537.891 | 98551.0527 | 148088.9436 | 230093.8431 | 172043.8808 | TRUE | Option 3 | 172043.8808 | 405
| BAS033-78748025 | 81 | 1735338.565 | -938032.7636 | 16565.1341 | 374789.1766 | 391354.3107 | 581.9358 | 17066.5718 | 17648.5076 | 373705.8031 | -564326.9604 | FALSE | 1193 | 64192.5 | -65306.2076 | 6486.5808 | 153157.3387 | 159643.9195 | 231710.3912 | 166404.1836 | TRUE | Option 3 | 166404.1836 | 406
| SHP021-24614430 | 88 | 1885306.0953 | -1019097.3234 | 141822.751 | 245010.3295 | 386833.0805 | 4982.2561 | 8607.2524 | 13589.5085 | 373243.572 | -645853.7514 | FALSE | 1290 | 69740 | -70949.954 | 55535.0008 | 95941.2278 | 151476.2286 | 235356.8519 | 164406.8979 | TRUE | Option 3 | 164406.8979 | 407
| BMH005-65434147 | 152 | 3256437.801 | -1760259.0131 | 307457.8181 | 155370.4314 | 462828.2495 | 10801.0427 | 7075.0192 | 17876.0619 | 444952.1876 | -1315306.8255 | FALSE | 1807 | 120460 | -122549.9205 | 120394.4365 | 63492.0197 | 183886.4562 | 278941.7933 | 156391.8729 | TRUE | Option 3 | 156391.8729 | 408
| WPD013-40657711 | 55 | 1178316.3096 | -636935.8271 | 276930.4772 | 50987.8918 | 327918.369 | 9728.6123 | 2321.808 | 12050.4203 | 315867.9487 | -321067.8784 | FALSE | 816 | 43587.5 | -44343.7212 | 108440.53 | 20836.1669 | 129276.6968 | 198641.6722 | 154297.9509 | TRUE | Option 3 | 154297.9509 | 409
| BET004-72499638 | 44 | 942653.0477 | -509548.6617 | 23247.1611 | 284247.9818 | 307495.1429 | 816.6765 | 9985.6774 | 10802.354 | 296692.7889 | -212855.8727 | FALSE | 617 | 34870 | -35474.977 | 9103.1312 | 111305.9209 | 120409.0521 | 187086.0908 | 151611.1138 | TRUE | Option 3 | 151611.1138 | 410
| CME021-184455628 | 55 | 1178316.3096 | -636935.8271 | 190732.6565 | 129015.3725 | 319748.029 | 6700.469 | 4532.3308 | 11232.7998 | 308515.2292 | -328420.5979 | FALSE | 832 | 43587.5 | -44343.7212 | 74687.1582 | 50519.8832 | 125207.0414 | 194540.9876 | 150197.2663 | TRUE | Option 3 | 150197.2663 | 411
| ART023-76359967 | 101 | 2163817.2231 | -1169645.7916 | 29844.3914 | 342951.8467 | 372796.2382 | 1048.4383 | 12047.9537 | 13096.392 | 359699.8462 | -809945.9454 | FALSE | 1477 | 80042.5 | -81431.1972 | 11686.4769 | 134293.2002 | 145979.6771 | 226816.561 | 145385.3639 | TRUE | Option 3 | 145385.3639 | 412
| RCT023-24606802 | 146 | 3127894.2036 | -1690775.1047 | 24739.9509 | 405823.8645 | 430563.8155 | 869.1185 | 14256.6578 | 15125.7763 | 415438.0392 | -1275337.0655 | FALSE | 1792 | 115705 | -117712.4236 | 9687.6784 | 158912.6462 | 168600.3246 | 261963.4909 | 144251.0673 | TRUE | Option 3 | 144251.0673 | 413
| DDL012-193014212 | 314 | 6727114.9311 | -3636324.5402 | 333272.2079 | 324210.7337 | 657482.9416 | 11707.9064 | 14763.4086 | 26471.315 | 631011.6266 | -3005312.9136 | FALSE | 2136 | 248845 | -253162.3357 | 130502.844 | 132488.4928 | 262991.3368 | 394491.6048 | 141329.2691 | TRUE | Option 3 | 141329.2691 | 414
| STL005-84921818 | 71 | 1521099.236 | -822226.2495 | 110876.3542 | 208901.5246 | 319777.8788 | 3895.1042 | 7338.7442 | 11233.8485 | 308544.0304 | -513682.2192 | FALSE | 1117 | 56267.5 | -57243.7128 | 43417.0003 | 81801.7297 | 125218.73 | 194559.1488 | 137315.4359 | TRUE | Option 3 | 137315.4359 | 415
| HSM004-160438050 | 95 | 2035273.6257 | -1100161.8832 | 8056.9538 | 343476.8569 | 351533.8107 | 283.0421 | 12066.3974 | 12349.4395 | 339184.3713 | -760977.5119 | FALSE | 1431 | 75287.5 | -76593.7003 | 3154.9447 | 134498.7839 | 137653.7286 | 213880.0821 | 137286.3818 | TRUE | Option 3 | 137286.3818 | 416
| HTN034-161079325 | 137 | 2935078.8075 | -1586549.2421 | 3688.4076 | 411701.0147 | 415389.4223 | 129.5744 | 18747.4061 | 18876.9805 | 396512.4418 | -1190036.8003 | FALSE | 1743 | 108572.5 | -110456.1783 | 1444.3079 | 168241.3359 | 169685.6437 | 245703.7785 | 135247.6002 | TRUE | Option 3 | 135247.6002 | 417
| STL006-144106734 | 67 | 1435403.5044 | -775903.6439 | 21570.3142 | 289208.5704 | 310778.8846 | 757.7686 | 10159.9437 | 10917.7123 | 299861.1722 | -476042.4717 | FALSE | 1063 | 53097.5 | -54018.7149 | 8446.5109 | 113248.3899 | 121694.9008 | 189083.9838 | 135065.2688 | TRUE | Option 3 | 135065.2688 | 418
| SHL008-181581109 | 124 | 2656567.6798 | -1436000.7739 | 162904.0511 | 221938.3662 | 384842.4173 | 5722.8456 | 7796.7306 | 13519.5762 | 371322.8411 | -1064677.9328 | FALSE | 1663 | 98270 | -99974.9351 | 63790.0235 | 86906.7006 | 150696.724 | 234145.6933 | 134170.7581 | TRUE | Option 3 | 134170.7581 | 419
| BAS033-139662053 | 81 | 1735338.565 | -938032.7636 | 12417.0134 | 324185.9564 | 336602.9698 | 436.2117 | 14762.2803 | 15198.492 | 321404.4778 | -616628.2858 | FALSE | 1260 | 64192.5 | -65306.2076 | 4862.2583 | 132478.3676 | 137340.6259 | 199262.3439 | 133956.1362 | TRUE | Option 3 | 133956.1362 | 420
| RVL006-15418762 | 107 | 2292360.8205 | -1239129.7 | 202037.48 | 158763.6955 | 360801.1755 | 7097.6093 | 5577.3942 | 12675.0035 | 348126.172 | -891003.528 | FALSE | 1555 | 84797.5 | -86268.694 | 79113.9048 | 62168.7416 | 141282.6464 | 219518.5291 | 133249.8351 | TRUE | Option 3 | 133249.8351 | 421
| MNA013-15432136 | 250 | 5355983.2254 | -2895162.8505 | 225656.0154 | 322868.3202 | 548524.3355 | 7927.3322 | 11342.4162 | 19269.7484 | 529254.5872 | -2365908.2634 | FALSE | 2063 | 198125 | -201562.3692 | 88362.4589 | 126428.8861 | 214791.345 | 333732.9905 | 132170.6214 | TRUE | Option 3 | 132170.6214 | 422
| BAS022-193385657 | 44 | 942653.0477 | -509548.6617 | 131704.6502 | 146332.216 | 278036.8662 | 4626.8056 | 6663.4509 | 11290.2565 | 266746.6097 | -242802.0519 | FALSE | 675 | 34870 | -35474.977 | 51572.9515 | 59798.5592 | 111371.5107 | 166665.3555 | 131190.3785 | TRUE | Option 3 | 131190.3785 | 423
| WND012-74645078 | 88 | 1885306.0953 | -1019097.3234 | 9546.0452 | 321856.6505 | 331402.6957 | 335.3541 | 14656.212 | 14991.5661 | 316411.1296 | -702686.1937 | FALSE | 1369 | 69740 | -70949.954 | 3738.0436 | 131526.4984 | 135264.542 | 196138.1537 | 125188.1998 | TRUE | Option 3 | 125188.1998 | 424
| TNA012-182581784 | 169 | 3620644.6604 | -1957130.0869 | 86542.1022 | 351291.4166 | 437833.5188 | 3040.238 | 15996.567 | 19036.805 | 418796.7138 | -1538333.3732 | FALSE | 1896 | 133932.5 | -136256.1616 | 33888.1857 | 143554.9953 | 177443.1809 | 260390.3379 | 124134.1763 | TRUE | Option 3 | 124134.1763 | 425
| CLC013-40996443 | 233 | 4991776.3661 | -2698291.7767 | 276274.8019 | 238308.4806 | 514583.2825 | 9705.5783 | 10851.7242 | 20557.3026 | 494025.9799 | -2204265.7967 | FALSE | 2033 | 184652.5 | -187856.1281 | 108183.7805 | 97384.5963 | 205568.3768 | 309014.9057 | 121158.7776 | TRUE | Option 3 | 121158.7776 | 426
| STL006-155132685 | 131 | 2806535.2101 | -1517065.3337 | 9029.4575 | 360990.0158 | 370019.4733 | 317.2063 | 12681.6375 | 12998.8438 | 357020.6295 | -1160044.7041 | FALSE | 1724 | 103817.5 | -105618.6815 | 3535.758 | 141356.5926 | 144892.3506 | 225127.1227 | 119508.4412 | TRUE | Option 3 | 119508.4412 | 427
| CTN003-155063885 | 79 | 1692490.6992 | -914871.4608 | 2734.445 | 297847.204 | 300581.649 | 96.0615 | 10463.4203 | 10559.4818 | 290022.1672 | -624849.2936 | FALSE | 1272 | 62607.5 | -63693.7087 | 1070.7549 | 116631.109 | 117701.8639 | 182879.7851 | 119186.0765 | TRUE | Option 3 | 119186.0765 | 428
| FNS021-24604138 | 64 | 1371131.7057 | -741161.6897 | 203821.5331 | 76824.7872 | 280646.3203 | 7160.2833 | 3498.3287 | 10658.6121 | 269987.7082 | -471173.9815 | FALSE | 1053 | 50720 | -51599.9665 | 79812.5049 | 31394.3963 | 111206.9013 | 169439.419 | 117839.4525 | TRUE | Option 3 | 117839.4525 | 429
| KGT003-155165521 | 203 | 4349058.379 | -2350872.2346 | 2315.2304 | 460275.814 | 462591.0443 | 81.3344 | 16169.5636 | 16250.898 | 446340.1463 | -1904532.0883 | FALSE | 1981 | 160877.5 | -163668.6438 | 906.5987 | 180234.959 | 181141.5577 | 281449.4866 | 117780.8428 | TRUE | Option 3 | 117780.8428 | 430
| BAS011-79244446 | 57 | 1221164.1754 | -660097.1299 | 10944.4428 | 262876.6486 | 273821.0913 | 384.48 | 11970.4716 | 12354.9516 | 261466.1397 | -398630.9902 | FALSE | 956 | 45172.5 | -45956.2202 | 4285.6286 | 107424.3612 | 111709.9898 | 162111.1015 | 116154.8813 | TRUE | Option 3 | 116154.8813 | 431
| OYN001-157997885 | 348 | 7455528.6498 | -4030066.6879 | 821.5986 | 648086.1609 | 648907.7596 | 28.8629 | 22767.3713 | 22796.2342 | 626111.5253 | -3403955.1626 | FALSE | 2164 | 275790 | -280574.8179 | 321.7219 | 253777.7983 | 254099.5201 | 394808.2394 | 114233.4215 | TRUE | Option 3 | 114233.4215 | 432
| HSM001-157577658 | 107 | 2292360.8205 | -1239129.7 | 5592.5301 | 321917.103 | 327509.6331 | 196.4665 | 11308.9997 | 11505.4662 | 316004.1669 | -923125.5332 | FALSE | 1578 | 84797.5 | -86268.694 | 2189.9248 | 126056.4081 | 128246.333 | 199263.3001 | 112994.6061 | TRUE | Option 3 | 112994.6061 | 433
| BET006-143535450 | 84 | 1799610.3637 | -972774.7178 | 12889.1657 | 283402.4126 | 296291.5784 | 452.7985 | 9955.9725 | 10408.7709 | 285882.8074 | -686891.9103 | FALSE | 1348 | 66570 | -67724.956 | 5047.1439 | 110974.8127 | 116021.9566 | 180269.6218 | 112544.6658 | TRUE | Option 3 | 112544.6658 | 434
| HSM003-24601658 | 91 | 1949577.894 | -1053839.2776 | 20823.1586 | 284282.9243 | 305106.0828 | 731.5209 | 9986.905 | 10718.4259 | 294387.6569 | -759451.6206 | FALSE | 1430 | 72117.5 | -73368.7024 | 8153.9395 | 111319.6037 | 119473.5432 | 185632.5396 | 112263.8373 | TRUE | Option 3 | 112263.8373 | 435
| HSM001-157535228 | 108 | 2313784.7534 | -1250710.3514 | 7160.3627 | 320071.7863 | 327232.149 | 251.5447 | 11244.1735 | 11495.7182 | 315736.4308 | -934973.9206 | FALSE | 1587 | 85590 | -87074.9435 | 2803.8572 | 125333.8184 | 128137.6757 | 199094.4733 | 112019.5298 | TRUE | Option 3 | 112019.5298 | 436
| STL007-162910244 | 76 | 1628218.9005 | -880129.5066 | 39471.0167 | 244581.7019 | 284052.7185 | 1386.6232 | 8592.1946 | 9978.8178 | 274073.9007 | -606055.6058 | FALSE | 1246 | 60230 | -61274.9602 | 15456.0741 | 95773.3856 | 111229.4597 | 172823.2589 | 111548.2986 | TRUE | Option 3 | 111548.2986 | 437
| BET004-112026510 | 35 | 749837.6516 | -405322.7991 | 16235.6173 | 210506.6463 | 226742.2637 | 570.3599 | 7395.1324 | 7965.4923 | 218776.7714 | -186546.0277 | FALSE | 570 | 27737.5 | -28218.7317 | 6357.5485 | 82430.2638 | 88787.8124 | 137954.4513 | 109735.7196 | TRUE | Option 3 | 109735.7196 | 438
| OYN001-161991346 | 124 | 2656567.6798 | -1436000.7739 | 811.6602 | 342203.9951 | 343015.6552 | 28.5138 | 12021.6815 | 12050.1953 | 330965.4599 | -1105035.3139 | FALSE | 1685 | 98270 | -99974.9351 | 317.8302 | 134000.3562 | 134318.1864 | 208697.4688 | 108722.5337 | TRUE | Option 3 | 108722.5337 | 439
| WPD022-72495720 | 244 | 5227439.628 | -2825678.9421 | 236171.95 | 273367.5329 | 509539.4829 | 8296.7587 | 12448.1893 | 20744.948 | 488794.5349 | -2336884.4072 | FALSE | 2054 | 193370 | -196724.8723 | 92480.2921 | 111711.4539 | 204191.746 | 305347.7369 | 108622.8646 | TRUE | Option 3 | 108622.8646 | 440
| CMN001-74644085 | 67 | 1435403.5044 | -775903.6439 | 5578.7716 | 260611.409 | 266190.1806 | 195.9831 | 9155.3208 | 9351.304 | 256838.8766 | -519064.7673 | FALSE | 1128 | 53097.5 | -54018.7149 | 2184.5373 | 102050.3037 | 104234.841 | 161955.3396 | 107936.6246 | TRUE | Option 3 | 107936.6246 | 441
| EHK031-134953753 | 41 | 878381.249 | -474806.7075 | 22274.9753 | 204198.4506 | 226473.4259 | 782.5235 | 7173.5245 | 7956.048 | 218517.378 | -256289.3295 | FALSE | 710 | 32492.5 | -33056.2285 | 8722.4424 | 79960.0984 | 88682.5408 | 137790.8851 | 104734.6566 | TRUE | Option 3 | 104734.6566 | 442
| HSM003-160677450 | 111 | 2378056.5521 | -1285452.3056 | 5295.4547 | 313652.421 | 318947.8757 | 186.0302 | 11018.6601 | 11204.6903 | 307743.1854 | -977709.1202 | FALSE | 1607 | 87967.5 | -89493.6919 | 2073.596 | 122820.1212 | 124893.7171 | 194054.1586 | 104560.4666 | TRUE | Option 3 | 104560.4666 | 443
| NKA005-15422555 | 281 | 6020125.1454 | -3254163.044 | 104747.3931 | 438363.2213 | 543110.6145 | 3679.7928 | 15399.7707 | 19079.5635 | 524031.051 | -2730131.993 | FALSE | 2101 | 222692.5 | -226556.103 | 41017.0197 | 171654.4186 | 212671.4383 | 330439.1762 | 103883.0732 | TRUE | Option 3 | 103883.0732 | 444
| BAN003-193396210 | 47 | 1006924.8464 | -544290.6159 | 96008.3324 | 140668.5012 | 236676.8336 | 3372.7882 | 6405.5454 | 9778.3336 | 226898.5 | -317392.1159 | FALSE | 813 | 37247.5 | -37893.7254 | 37594.9753 | 57484.0861 | 95079.0614 | 141597.7722 | 103704.0468 | TRUE | Option 3 | 103704.0468 | 445
| BMH003-54311761 | 269 | 5763037.9505 | -3115195.2272 | 46056.5266 | 494248.0494 | 540304.576 | 1617.9732 | 22506.3058 | 24124.279 | 516180.297 | -2599014.9301 | FALSE | 2089 | 213182.5 | -216881.1092 | 18034.8303 | 201974.1247 | 220008.955 | 320295.621 | 103414.5118 | TRUE | Option 3 | 103414.5118 | 446
| CTN001-155191322 | 102 | 2185241.156 | -1181226.443 | 9010.8527 | 295781.5267 | 304792.3794 | 316.5527 | 10390.8527 | 10707.4054 | 294084.974 | -887141.4691 | FALSE | 1552 | 80835 | -82237.4466 | 3528.4727 | 115822.2303 | 119350.7031 | 185441.6763 | 103204.2297 | TRUE | Option 3 | 103204.2297 | 447
| BAS034-199849971 | 226 | 4841808.8358 | -2617227.2169 | 0 | 482460.9337 | 482460.9337 | 0 | 21969.5623 | 21969.5623 | 460491.3715 | -2156735.8454 | FALSE | 2025 | 179105 | -182212.3817 | 0 | 197157.328 | 197157.328 | 285303.6057 | 103091.224 | TRUE | Option 3 | 103091.224 | 448
| CDN001-15400083 | 618 | 13239990.5332 | -7156842.5665 | 265231.8654 | 743432.4646 | 1008664.3301 | 9317.6382 | 33853.2815 | 43170.9197 | 965493.4103 | -6191349.1561 | FALSE | 2224 | 489765 | -498262.1766 | 103859.5836 | 303803.1642 | 407662.7479 | 601001.5822 | 102739.4056 | TRUE | Option 3 | 102739.4056 | 449
| CHM011-163310655 | 42 | 899805.1819 | -486387.3589 | 1717.576 | 222342.5944 | 224060.1704 | 60.3387 | 7810.9312 | 7871.2699 | 216188.9005 | -270198.4584 | FALSE | 733 | 33285 | -33862.478 | 672.569 | 87064.9884 | 87737.5574 | 136322.613 | 102460.135 | TRUE | Option 3 | 102460.135 | 450
| CTN005-15418323 | 94 | 2013849.6928 | -1088581.2318 | 63390.9569 | 229344.1089 | 292735.0657 | 2226.9345 | 8056.8955 | 10283.8301 | 282451.2357 | -806129.9961 | FALSE | 1474 | 74495 | -75787.4508 | 24822.6524 | 89806.6438 | 114629.2961 | 178105.7696 | 102318.3188 | TRUE | Option 3 | 102318.3188 | 451
| CHM011-163198509 | 189 | 4049123.3184 | -2188743.115 | 3640.5087 | 414962.6877 | 418603.1964 | 127.8917 | 14577.7061 | 14705.5978 | 403897.5986 | -1784845.5164 | FALSE | 1955 | 149782.5 | -152381.1511 | 1425.5516 | 162491.2297 | 163916.7813 | 254686.415 | 102305.2639 | TRUE | Option 3 | 102305.2639 | 452
| HSM003-160931238 | 144 | 3085046.3378 | -1667613.8019 | 5236.1134 | 352047.6423 | 357283.7556 | 183.9455 | 12367.4904 | 12551.436 | 344732.3197 | -1322881.4822 | FALSE | 1811 | 114120 | -116099.9247 | 2050.359 | 137854.9349 | 139905.294 | 217378.4617 | 101278.537 | TRUE | Option 3 | 101278.537 | 453
| HTN034-161093808 | 105 | 2249512.9547 | -1215968.3972 | 3128.6122 | 309942.1126 | 313070.7248 | 109.9086 | 14113.6661 | 14223.5748 | 298847.15 | -917121.2472 | FALSE | 1575 | 83212.5 | -84656.1951 | 1225.103 | 126657.6307 | 127882.7337 | 185187.9911 | 100531.796 | TRUE | Option 3 | 100531.796 | 454
| WND013-76546404 | 95 | 2035273.6257 | -1100161.8832 | 22587.5425 | 274177.3382 | 296764.8806 | 793.504 | 12485.065 | 13278.569 | 283486.3117 | -816675.5715 | FALSE | 1481 | 75287.5 | -76593.7003 | 8844.8375 | 112042.3803 | 120887.2178 | 175877.6629 | 99283.9626 | TRUE | Option 3 | 99283.9626 | 455
| SHL002-24604040 | 34 | 728413.7187 | -393742.1477 | 121149.826 | 83143.602 | 204293.4281 | 4256.0129 | 2920.8481 | 7176.8611 | 197116.567 | -196625.5807 | FALSE | 582 | 26945 | -27412.4822 | 47439.8899 | 32557.3998 | 79997.2897 | 124296.1384 | 96883.6561 | TRUE | Option 3 | 96883.6561 | 456
| NHL015-157999738 | 128 | 2742263.4114 | -1482323.3795 | 3618.814 | 325224.7524 | 328843.5665 | 127.1295 | 11425.198 | 11552.3275 | 317291.239 | -1165032.1405 | FALSE | 1729 | 101440 | -103199.933 | 1417.0564 | 127351.6186 | 128768.6751 | 200074.8914 | 96874.9584 | TRUE | Option 3 | 96874.9584 | 457
| HSM005-160647192 | 70 | 1499675.3031 | -810645.5981 | 7844.0322 | 243747.7367 | 251591.7689 | 275.5621 | 8562.8973 | 8838.4594 | 242753.3095 | -567892.2887 | FALSE | 1204 | 55475 | -56437.4634 | 3071.5688 | 95446.8213 | 98518.39 | 153073.3789 | 96635.9155 | TRUE | Option 3 | 96635.9155 | 458
| NHL015-158146107 | 87 | 1863882.1624 | -1007516.672 | 2587.7767 | 271022.5536 | 273610.3303 | 90.909 | 9521.066 | 9611.975 | 263998.3553 | -743518.3167 | FALSE | 1405 | 68947.5 | -70143.7045 | 1013.3225 | 106127.1033 | 107140.4258 | 166469.9046 | 96326.2001 | TRUE | Option 3 | 96326.2001 | 459
| NKA002-24606230 | 207 | 4434754.1106 | -2397194.8402 | 27455.434 | 403356.9499 | 430812.3839 | 964.5138 | 14169.9947 | 15134.5085 | 415677.8754 | -1981516.9648 | FALSE | 1995 | 164047.5 | -166893.6417 | 10751.0082 | 157946.651 | 168697.6591 | 262114.7248 | 95221.0831 | TRUE | Option 3 | 95221.0831 | 460
| BET006-163864001 | 15 | 321358.9935 | -173709.771 | 17692.5566 | 157889.9443 | 175582.5009 | 621.5424 | 5546.6992 | 6168.2416 | 169414.2593 | -4295.5117 | FALSE | 220 | 11887.5 | -12093.7422 | 6928.0573 | 61826.5978 | 68754.6551 | 106827.8457 | 94734.1036 | TRUE | Option 3 | 94734.1036 | 461
| CME016-154143626 | 121 | 2592295.8811 | -1401258.8196 | 80378.2468 | 234614.2394 | 314992.4863 | 2823.7008 | 8242.0361 | 11065.7368 | 303926.7494 | -1097332.0702 | FALSE | 1680 | 95892.5 | -97556.1867 | 31474.5411 | 91870.3233 | 123344.8644 | 191647.6219 | 94091.4352 | TRUE | Option 3 | 94091.4352 | 462
| WND014-79365841 | 90 | 1928153.9611 | -1042258.6262 | 20133.3959 | 261102.595 | 281235.9909 | 707.2894 | 11889.6875 | 12596.9769 | 268639.014 | -773619.6122 | FALSE | 1442 | 71325 | -72562.4529 | 7883.842 | 106699.3955 | 114583.2375 | 166652.7535 | 94090.3006 | TRUE | Option 3 | 94090.3006 | 463
| DDL021-24613592 | 255 | 5463102.8899 | -2953066.1075 | 245457.7083 | 253661.139 | 499118.8473 | 8622.9689 | 11550.8299 | 20173.7988 | 478945.0485 | -2474121.059 | FALSE | 2073 | 202087.5 | -205593.6166 | 96116.4125 | 103658.4496 | 199774.8621 | 299343.9852 | 93750.3686 | TRUE | Option 3 | 93750.3686 | 464
| MRO007-129258735 | 43 | 921229.1148 | -497968.0103 | 7252.7578 | 202901.8414 | 210154.5993 | 254.7906 | 7127.9744 | 7382.765 | 202771.8343 | -295196.176 | FALSE | 776 | 34077.5 | -34668.7275 | 2840.0374 | 79452.3718 | 82292.4091 | 127862.1902 | 93193.4627 | TRUE | Option 3 | 93193.4627 | 465
| HSM004-96221391 | 87 | 1863882.1624 | -1007516.672 | 8864.429 | 257823.849 | 266688.278 | 311.4088 | 9057.3934 | 9368.8022 | 257319.4758 | -750197.1962 | FALSE | 1416 | 68947.5 | -70143.7045 | 3471.1361 | 100958.75 | 104429.8862 | 162258.3918 | 92114.6873 | TRUE | Option 3 | 92114.6873 | 466
| HTN034-158494823 | 246 | 5270287.4938 | -2848840.2449 | 5831.8954 | 485146.5491 | 490978.4446 | 204.8754 | 22091.8557 | 22296.7311 | 468681.7135 | -2380158.5314 | FALSE | 2065 | 194955 | -198337.3713 | 2283.6556 | 198254.8029 | 200538.4585 | 290439.9861 | 92102.6148 | TRUE | Option 3 | 92102.6148 | 467
| CTN001-24604862 | 87 | 1863882.1624 | -1007516.672 | 16264.2192 | 248351.1825 | 264615.4017 | 571.3646 | 8724.6171 | 9295.9817 | 255319.42 | -752197.252 | FALSE | 1420 | 68947.5 | -70143.7045 | 6368.7485 | 97249.4401 | 103618.1886 | 160997.2131 | 90853.5087 | TRUE | Option 3 | 90853.5087 | 468
| BET005-110828671 | 35 | 749837.6516 | -405322.7991 | 28683.8519 | 163941.4596 | 192625.3115 | 1007.6683 | 5759.2899 | 6766.9583 | 185858.3532 | -219464.4458 | FALSE | 629 | 27737.5 | -28218.7317 | 11232.0325 | 64196.2522 | 75428.2847 | 117197.0268 | 88978.2951 | TRUE | Option 3 | 88978.2951 | 469
| KYM004-24596780 | 314 | 6727114.9311 | -3636324.5402 | 35622.0241 | 525928.2583 | 561550.2824 | 1251.4075 | 18475.9445 | 19727.352 | 541822.9304 | -3094501.6099 | FALSE | 2142 | 248845 | -253162.3357 | 13948.8843 | 205943.1654 | 219892.0497 | 341658.2327 | 88495.897 | TRUE | Option 3 | 88495.897 | 470
| HSM005-159947157 | 74 | 1585371.0347 | -856968.2038 | 6181.6411 | 236900.6321 | 243082.2732 | 217.162 | 8322.3574 | 8539.5195 | 234542.7538 | -622425.45 | FALSE | 1270 | 58645 | -59662.4613 | 2420.6091 | 92765.6297 | 95186.2388 | 147896.0344 | 88233.5731 | TRUE | Option 3 | 88233.5731 | 471
| STL007-85224567 | 166 | 3556372.8617 | -1922388.1327 | 171088.4238 | 192927.3956 | 364015.8194 | 6010.3639 | 6777.5705 | 12787.9344 | 351227.8849 | -1571160.2478 | FALSE | 1907 | 131555 | -133837.4131 | 66994.8629 | 75546.5749 | 142541.4378 | 221474.3816 | 87636.9685 | TRUE | Option 3 | 87636.9685 | 472
| HSM006-153767042 | 101 | 2163817.2231 | -1169645.7916 | 3661.5113 | 269823.4284 | 273484.9396 | 128.6295 | 9478.9406 | 9607.57 | 263877.3696 | -905768.422 | FALSE | 1566 | 80042.5 | -81431.1972 | 1433.7758 | 105657.5494 | 107091.3252 | 166393.6144 | 84962.4172 | TRUE | Option 3 | 84962.4172 | 473
| HSM003-160653285 | 133 | 2849383.0759 | -1540226.6365 | 5998.1499 | 308258.9039 | 314257.0538 | 210.716 | 10829.185 | 11039.901 | 303217.1528 | -1237009.4836 | FALSE | 1769 | 105402.5 | -107231.1804 | 2348.7576 | 120708.1259 | 123056.8835 | 191200.1703 | 83968.9899 | TRUE | Option 3 | 83968.9899 | 474
| BET004-72500251 | 39 | 835533.3832 | -451645.4047 | 15666.4568 | 173366.1094 | 189032.5661 | 550.3652 | 6090.3794 | 6640.7445 | 182391.8216 | -269253.5831 | FALSE | 732 | 30907.5 | -31443.7296 | 6134.6764 | 67886.7598 | 74021.4362 | 115011.1299 | 83567.4003 | TRUE | Option 3 | 83567.4003 | 475
| CTN001-15418475 | 57 | 1221164.1754 | -660097.1299 | 136541.0346 | 76236.5072 | 212777.5418 | 4796.7086 | 2678.2008 | 7474.9094 | 205302.6324 | -454794.4975 | FALSE | 1034 | 45172.5 | -45956.2202 | 53466.7845 | 29852.7173 | 83319.5018 | 129458.0399 | 83501.8198 | TRUE | Option 3 | 83501.8198 | 476
| ECA007-24611056 | 35 | 749837.6516 | -405322.7991 | 94619.0897 | 88352.7772 | 182971.8669 | 3323.9839 | 3103.8473 | 6427.8312 | 176544.0357 | -228778.7634 | FALSE | 651 | 27737.5 | -28218.7317 | 37050.9752 | 34597.2104 | 71648.1856 | 111323.6813 | 83104.9496 | TRUE | Option 3 | 83104.9496 | 477
| CTN002-154876923 | 109 | 2335208.6863 | -1262291.0028 | 4380.2025 | 275777.2755 | 280157.478 | 153.8772 | 9688.1002 | 9841.9774 | 270315.5006 | -991975.5022 | FALSE | 1615 | 86382.5 | -87881.193 | 1715.2012 | 107988.9589 | 109704.1601 | 170453.3179 | 82572.125 | TRUE | Option 3 | 82572.125 | 478
| HSM005-160415406 | 104 | 2228089.0218 | -1204387.7458 | 6599.7306 | 266615.5912 | 273215.3218 | 231.8496 | 9366.2487 | 9598.0983 | 263617.2235 | -940770.5223 | FALSE | 1590 | 82420 | -83849.9456 | 2584.3248 | 104401.4235 | 106985.7482 | 166229.5736 | 82379.6281 | TRUE | Option 3 | 82379.6281 | 479
| BAN003-159380816 | 93 | 1992425.7599 | -1077000.5804 | 17028.4473 | 247546.5458 | 264574.9931 | 598.2121 | 11272.393 | 11870.6051 | 252704.388 | -824296.1924 | FALSE | 1489 | 73702.5 | -74981.2013 | 6668.0052 | 101159.7253 | 107827.7305 | 156747.2626 | 81766.0613 | TRUE | Option 3 | 81766.0613 | 480
| BAN003-141840240 | 41 | 878381.249 | -474806.7075 | 16207.3104 | 176719.3343 | 192926.6448 | 569.3654 | 8047.1726 | 8616.5381 | 184310.1067 | -290496.6008 | FALSE | 772 | 32492.5 | -33056.2285 | 6346.4641 | 72216.2342 | 78562.6983 | 114363.9465 | 81307.7179 | TRUE | Option 3 | 81307.7179 | 481
| BAS022-142437045 | 40 | 856957.3161 | -463226.0561 | 18630.4106 | 172520.0047 | 191150.4153 | 654.4893 | 7855.95 | 8510.4394 | 182639.9759 | -280586.0801 | FALSE | 749 | 31700 | -32249.9791 | 7295.3025 | 70500.181 | 77795.4835 | 113354.9318 | 81104.9527 | TRUE | Option 3 | 81104.9527 | 482
| BET004-72500100 | 65 | 1392555.6386 | -752742.3411 | 12863.2685 | 206515.6669 | 219378.9355 | 451.8887 | 7254.9287 | 7706.8174 | 211672.1181 | -541070.223 | FALSE | 1166 | 51512.5 | -52406.216 | 5037.003 | 80867.4748 | 85904.4778 | 133474.4577 | 81068.2417 | TRUE | Option 3 | 81068.2417 | 483
| BET006-160813078 | 94 | 2013849.6928 | -1088581.2318 | 9861.5151 | 247563.6992 | 257425.2144 | 346.4366 | 8696.9527 | 9043.3893 | 248381.8251 | -840199.4067 | FALSE | 1507 | 74495 | -75787.4508 | 3861.5754 | 96941.0771 | 100802.6526 | 156622.5618 | 80835.111 | TRUE | Option 3 | 80835.111 | 484
| HSM004-163606098 | 23 | 492750.4567 | -266354.9822 | 14985.7338 | 146921.1427 | 161906.8766 | 526.4512 | 5161.3634 | 5687.8147 | 156219.0619 | -110135.9203 | FALSE | 404 | 18227.5 | -18543.738 | 5868.1187 | 57531.4308 | 63399.5495 | 98507.327 | 79963.5891 | TRUE | Option 3 | 79963.5891 | 485
| CHA006-155747849 | 151 | 3235013.8681 | -1748678.3617 | 3037.65 | 327875.023 | 330912.673 | 106.7131 | 11518.3024 | 11625.0156 | 319287.6574 | -1429390.7043 | FALSE | 1854 | 119667.5 | -121743.671 | 1189.484 | 128389.4125 | 129578.8965 | 201333.7765 | 79590.1055 | TRUE | Option 3 | 79590.1055 | 486
| KGT004-24604166 | 47 | 1006924.8464 | -544290.6159 | 9239.5955 | 177789.6715 | 187029.267 | 324.5885 | 6245.7798 | 6570.3683 | 180458.8987 | -363831.7172 | FALSE | 900 | 37247.5 | -37893.7254 | 3618.0439 | 69618.9397 | 73236.9837 | 113792.2833 | 75898.5579 | TRUE | Option 3 | 75898.5579 | 487
| CMN001-74644167 | 32 | 685565.8529 | -370580.8449 | 3932.791 | 163086.3914 | 167019.1824 | 138.1596 | 5729.2512 | 5867.4108 | 161151.7716 | -209429.0733 | FALSE | 610 | 25360 | -25799.9833 | 1540.0036 | 63861.4244 | 65401.428 | 101617.7544 | 75817.7712 | TRUE | Option 3 | 75817.7712 | 488
| OYN001-41898846 | 299 | 6405755.9376 | -3462614.7692 | 3377.0321 | 517410.2362 | 520787.2683 | 118.6357 | 18176.705 | 18295.3407 | 502491.9276 | -2960122.8416 | FALSE | 2131 | 236957.5 | -241068.5935 | 1322.3794 | 202607.6754 | 203930.0548 | 316857.2135 | 75788.62 | TRUE | Option 3 | 75788.62 | 489
| HSM003-160720939 | 111 | 2378056.5521 | -1285452.3056 | 7020.2355 | 264611.371 | 271631.6065 | 246.622 | 9295.8401 | 9542.4621 | 262089.1443 | -1023363.1613 | FALSE | 1646 | 87967.5 | -89493.6919 | 2748.9862 | 103616.6102 | 106365.5964 | 165266.01 | 75772.3181 | TRUE | Option 3 | 75772.3181 | 490
| NHL015-158145995 | 78 | 1671066.7663 | -903290.8094 | 3941.5872 | 222028.5351 | 225970.1223 | 138.4686 | 7799.8982 | 7938.3668 | 218031.7555 | -685259.0539 | FALSE | 1346 | 61815 | -62887.4592 | 1543.4481 | 86942.0089 | 88485.457 | 137484.6653 | 74597.2062 | TRUE | Option 3 | 74597.2062 | 491
| BAS033-155176923 | 58 | 1242588.1083 | -671677.7813 | 8593.5804 | 196030.1221 | 204623.7025 | 301.8939 | 8926.5175 | 9228.4114 | 195395.2912 | -476282.4902 | FALSE | 1065 | 45965 | -46762.4697 | 3365.0771 | 80107.5743 | 83472.6514 | 121151.0511 | 74388.5815 | TRUE | Option 3 | 74388.5815 | 492
| CMN001-74644242 | 33 | 706989.7858 | -382161.4963 | 7077.8004 | 158094.7269 | 165172.5273 | 248.6443 | 5553.8933 | 5802.5375 | 159369.9898 | -222791.5065 | FALSE | 643 | 26152.5 | -26606.2327 | 2771.5275 | 61906.7867 | 64678.3141 | 100494.2131 | 73887.9804 | TRUE | Option 3 | 73887.9804 | 493
| NHL015-15417104 | 94 | 2013849.6928 | -1088581.2318 | 64123.5259 | 179508.8492 | 243632.375 | 2252.6698 | 6306.1748 | 8558.8446 | 235073.5304 | -853507.7014 | FALSE | 1518 | 74495 | -75787.4508 | 25109.512 | 70292.1359 | 95401.6479 | 148230.7271 | 72443.2763 | TRUE | Option 3 | 72443.2763 | 494
| NHL031-44808373 | 149 | 3192166.0023 | -1725517.0589 | 9175.2025 | 306601.8321 | 315777.0346 | 322.3263 | 10770.9718 | 11093.2981 | 304683.7364 | -1420833.3225 | FALSE | 1850 | 118082.5 | -120131.172 | 3592.8289 | 120059.2492 | 123652.0781 | 192124.9565 | 71993.7845 | TRUE | Option 3 | 71993.7845 | 495
| NKA005-154156915 | 28 | 599870.1212 | -324258.2393 | 84796.0035 | 69960.822 | 154756.8256 | 2978.8973 | 2457.735 | 5436.6322 | 149320.1933 | -174938.0459 | FALSE | 548 | 22190 | -22574.9853 | 33204.4478 | 27395.2824 | 60599.7301 | 94157.0954 | 71582.1101 | TRUE | Option 3 | 71582.1101 | 496
| CHA005-24606160 | 56 | 1199740.2425 | -648516.4785 | 20778.1202 | 170584.7026 | 191362.8229 | 729.9387 | 5992.6681 | 6722.6068 | 184640.216 | -463876.2625 | FALSE | 1045 | 44380 | -45149.9707 | 8136.3034 | 66797.6156 | 74933.919 | 116428.9039 | 71278.9332 | TRUE | Option 3 | 71278.9332 | 497
| COB011-15431815 | 541 | 11590347.6998 | -6265132.4085 | 179406.2051 | 673250.0394 | 852656.2445 | 6302.5689 | 30657.4224 | 36959.9913 | 815696.2532 | -5449436.1553 | FALSE | 2216 | 428742.5 | -436180.9669 | 70251.9425 | 275123.1645 | 345375.1071 | 507281.1375 | 71100.1705 | TRUE | Option 3 | 71100.1705 | 498
| ART033-155052342 | 81 | 1735338.565 | -938032.7636 | 4329.5026 | 218811.3905 | 223140.8931 | 152.0961 | 7686.8794 | 7838.9756 | 215301.9175 | -722730.8461 | FALSE | 1387 | 64192.5 | -65306.2076 | 1695.3481 | 85682.2384 | 87377.5864 | 135763.3066 | 70457.099 | TRUE | Option 3 | 70457.099 | 499
| AC026-200217919 | 15 | 321358.9935 | -173709.771 | 0 | 139039.9269 | 139039.9269 | 0 | 6331.3858 | 6331.3858 | 132708.541 | -41001.23 | FALSE | 286 | 11887.5 | -12093.7422 | 0 | 56818.5703 | 56818.5703 | 82221.3566 | 70127.6144 | TRUE | Option 3 | 70127.6144 | 500
| CLC003-24607110 | 150 | 3213589.9352 | -1737097.7103 | 68655.951 | 248689.0291 | 317344.9801 | 2411.8946 | 11324.4176 | 13736.3123 | 303608.6678 | -1433489.0425 | FALSE | 1855 | 118875 | -120937.4215 | 26884.3206 | 101626.6003 | 128510.9209 | 188834.0592 | 67896.6377 | TRUE | Option 3 | 67896.6377 | 501
| BAS011-158128939 | 316 | 6769962.7969 | -3659485.843 | 1019.0816 | 542800.954 | 543820.0356 | 35.8005 | 24717.2331 | 24753.0336 | 519067.002 | -3140418.841 | FALSE | 2147 | 250430 | -254774.8347 | 399.0523 | 221815.2357 | 222214.288 | 321605.7476 | 66830.9129 | TRUE | Option 3 | 66830.9129 | 502
| BGO023-76448224 | 68 | 1456827.4373 | -787484.2953 | 11991.7194 | 187039.4689 | 199031.1883 | 421.271 | 6570.7267 | 6991.9977 | 192039.1905 | -595445.1048 | FALSE | 1237 | 53890 | -54824.9644 | 4695.7215 | 73240.9785 | 77936.7001 | 121094.4882 | 66269.5238 | TRUE | Option 3 | 66269.5238 | 503
| HSM005-160319214 | 90 | 1928153.9611 | -1042258.6262 | 4003.0206 | 223906.2365 | 227909.2571 | 140.6268 | 7865.8622 | 8006.489 | 219902.7681 | -822355.858 | FALSE | 1487 | 71325 | -72562.4529 | 1567.5042 | 87677.2799 | 89244.784 | 138664.4731 | 66102.0201 | TRUE | Option 3 | 66102.0201 | 504
| PLD001-15398772 | 81 | 1735338.565 | -938032.7636 | 130049.6719 | 87869.5942 | 217919.2661 | 4568.6659 | 4001.2701 | 8569.9361 | 209349.3301 | -728683.4335 | FALSE | 1391 | 64192.5 | -65306.2076 | 50924.8946 | 35907.8491 | 86832.7437 | 131086.5225 | 65780.3149 | TRUE | Option 3 | 65780.3149 | 505
| WND012-93532503 | 150 | 3213589.9352 | -1737097.7103 | 75430.2558 | 237645.3157 | 313075.5716 | 2649.8771 | 10821.526 | 13471.4031 | 299604.1685 | -1437493.5418 | FALSE | 1857 | 118875 | -120937.4215 | 29537.0051 | 97113.5945 | 126650.5996 | 186424.972 | 65487.5505 | TRUE | Option 3 | 65487.5505 | 506
| STL006-24601812 | 297 | 6362908.0718 | -3439453.4664 | 52011.6993 | 448325.5516 | 500337.2509 | 1827.1794 | 15749.7489 | 17576.9283 | 482760.3226 | -2956693.1438 | FALSE | 2130 | 235372.5 | -239456.0946 | 20366.7588 | 175555.4713 | 195922.2301 | 304415.0208 | 64958.9262 | TRUE | Option 3 | 64958.9262 | 507
| CMN003-164373173 | 80 | 1713914.6321 | -926452.1122 | 24742.6311 | 187693.418 | 212436.0491 | 869.2126 | 6593.7 | 7462.9127 | 204973.1365 | -721478.9757 | FALSE | 1384 | 63400 | -64499.9581 | 9688.7279 | 73497.0522 | 83185.78 | 129250.2691 | 64750.311 | TRUE | Option 3 | 64750.311 | 508
| BAN003-24598720 | 161 | 3449253.1972 | -1864484.8757 | 25766.8259 | 302196.7581 | 327963.584 | 905.1927 | 13760.9701 | 14666.1629 | 313297.4211 | -1551187.4546 | FALSE | 1901 | 127592.5 | -129806.1658 | 10089.7824 | 123492.4969 | 133582.2793 | 194381.3047 | 64575.1389 | TRUE | Option 3 | 64575.1389 | 509
| BAS011-84621962 | 48 | 1028348.7793 | -555871.2673 | 9243.1126 | 164759.6764 | 174002.789 | 324.712 | 7502.5722 | 7827.2842 | 166175.5048 | -389695.7625 | FALSE | 942 | 38040 | -38699.9749 | 3619.4212 | 67328.9282 | 70948.3494 | 103054.4396 | 64354.4648 | TRUE | Option 3 | 64354.4648 | 510
| CMN002-78928472 | 44 | 942653.0477 | -509548.6617 | 4443.2342 | 157012.2337 | 161455.4679 | 156.0915 | 5515.8651 | 5671.9566 | 155783.5113 | -353765.1504 | FALSE | 877 | 34870 | -35474.977 | 1739.8831 | 61482.9036 | 63222.7868 | 98232.6811 | 62757.7041 | TRUE | Option 3 | 62757.7041 | 511
| BAN008-193386533 | 184 | 3942003.6539 | -2130839.858 | 3077.6439 | 353539.4427 | 356617.0866 | 108.1181 | 16098.9341 | 16207.0523 | 340410.0344 | -1790429.8236 | FALSE | 1958 | 145820 | -148349.9037 | 1205.1448 | 144473.6496 | 145678.7944 | 210938.2922 | 62588.3885 | TRUE | Option 3 | 62588.3885 | 512
| KGT004-24604180 | 74 | 1585371.0347 | -856968.2038 | 22896.1606 | 178000.9979 | 200897.1585 | 804.3458 | 6253.2038 | 7057.5496 | 193839.6089 | -663128.5948 | FALSE | 1316 | 58645 | -59662.4613 | 8965.6863 | 69701.691 | 78667.3773 | 122229.7812 | 62567.3199 | TRUE | Option 3 | 62567.3199 | 513
| CHA005-53118475 | 35 | 749837.6516 | -405322.7991 | 16626.4174 | 130558.0826 | 147184.5 | 584.0887 | 4586.5265 | 5170.6152 | 142013.8848 | -263308.9143 | FALSE | 718 | 27737.5 | -28218.7317 | 6510.5782 | 51123.9782 | 57634.5563 | 89549.9437 | 61331.212 | TRUE | Option 3 | 61331.212 | 514
| HTN013-153173736 | 261 | 5591646.4873 | -3022550.0159 | 54795.745 | 402601.1618 | 457396.9068 | 1924.9834 | 18333.0311 | 20258.0144 | 437138.8924 | -2585411.1235 | FALSE | 2088 | 206842.5 | -210431.1134 | 21456.9364 | 164522.6872 | 185979.6236 | 271417.2832 | 60986.1698 | TRUE | Option 3 | 60986.1698 | 515
| NHL031-187102650 | 106 | 2270936.8876 | -1227549.0486 | 47802.7519 | 191977.675 | 239780.4269 | 1679.3184 | 6744.2067 | 8423.5251 | 231356.9019 | -996192.1467 | FALSE | 1626 | 84005 | -85462.4445 | 18718.6178 | 75174.683 | 93893.3007 | 145887.1262 | 60424.6817 | TRUE | Option 3 | 60424.6817 | 516
| STN011-200055388 | 553 | 11847434.8946 | -6404100.2253 | 134935.4535 | 694052.785 | 828988.2385 | 4740.3042 | 24382.1863 | 29122.4905 | 799865.748 | -5604234.4773 | FALSE | 2218 | 438252.5 | -445855.9606 | 52838.0706 | 271777.4245 | 324615.495 | 504372.7434 | 58516.7828 | TRUE | Option 3 | 58516.7828 | 517
| BET006-74053924 | 30 | 642717.987 | -347419.5421 | 8711.9544 | 126689.5184 | 135401.4727 | 306.0524 | 4450.6232 | 4756.6756 | 130644.7972 | -216774.7449 | FALSE | 621 | 23775 | -24187.4843 | 3411.43 | 49609.1245 | 53020.5545 | 82380.9182 | 58193.4339 | TRUE | Option 3 | 58193.4339 | 518
| BAN003-79424384 | 77 | 1649642.8334 | -891710.158 | 18035.8994 | 184625.2549 | 202661.1544 | 633.6041 | 8407.1802 | 9040.7843 | 193620.3701 | -698089.7879 | FALSE | 1362 | 61022.5 | -62081.2097 | 7062.5036 | 75446.9832 | 82509.4868 | 120151.6676 | 58070.4579 | TRUE | Option 3 | 58070.4579 | 519
| BAN003-159380665 | 65 | 1392555.6386 | -752742.3411 | 8106.3094 | 177993.3905 | 186099.6999 | 284.776 | 8105.1886 | 8389.9646 | 177709.7353 | -575032.6058 | FALSE | 1211 | 51512.5 | -52406.216 | 3174.2714 | 72736.8763 | 75911.1477 | 110188.5522 | 57782.3362 | TRUE | Option 3 | 57782.3362 | 520
| MRO005-155391999 | 57 | 1221164.1754 | -660097.1299 | 8040.9484 | 162171.3821 | 170212.3305 | 282.4798 | 5697.1068 | 5979.5866 | 164232.7439 | -495864.386 | FALSE | 1092 | 45172.5 | -45956.2202 | 3148.6773 | 63503.1247 | 66651.802 | 103560.5285 | 57604.3084 | TRUE | Option 3 | 57604.3084 | 521
| WND013-76546231 | 126 | 2699415.5456 | -1459162.0767 | 15315.1415 | 253146.6418 | 268461.7833 | 538.0234 | 11527.4015 | 12065.4249 | 256396.3584 | -1202765.7183 | FALSE | 1750 | 99855 | -101587.4341 | 5997.1083 | 103448.2007 | 109445.309 | 159016.4743 | 57429.0402 | TRUE | Option 3 | 57429.0402 | 522
| BET005-143035406 | 23 | 492750.4567 | -266354.9822 | 18491.4058 | 105831.9314 | 124323.3373 | 649.6061 | 3717.8928 | 4367.4989 | 119955.8384 | -146399.1439 | FALSE | 489 | 18227.5 | -18543.738 | 7240.871 | 41441.7035 | 48682.5745 | 75640.7628 | 57097.0248 | TRUE | Option 3 | 57097.0248 | 523
| AC031-200217854 | 58 | 1242588.1083 | -671677.7813 | 79835.572 | 93435.621 | 173271.1931 | 2804.6365 | 4254.7273 | 7059.3638 | 166211.8293 | -505465.9521 | FALSE | 1102 | 45965 | -46762.4697 | 31262.0403 | 38182.4021 | 69444.4424 | 103826.7506 | 57064.281 | TRUE | Option 3 | 57064.281 | 524
| MRO005-73766637 | 45 | 964076.9806 | -521129.3131 | 8196.08 | 144235.2477 | 152431.3276 | 287.9296 | 5067.0075 | 5354.9371 | 147076.3905 | -374052.9226 | FALSE | 916 | 35662.5 | -36281.2265 | 3209.4238 | 56479.6871 | 59689.1109 | 92742.2168 | 56460.9903 | TRUE | Option 3 | 56460.9903 | 525
| CTN001-155143591 | 119 | 2549448.0153 | -1378097.5168 | 5915.7916 | 243369.6612 | 249285.4529 | 207.8227 | 8549.6154 | 8757.4382 | 240528.0147 | -1137569.5021 | FALSE | 1709 | 94307.5 | -95943.6877 | 2316.5077 | 95298.7743 | 97615.282 | 151670.1709 | 55726.4831 | TRUE | Option 3 | 55726.4831 | 526
| HSM001-157535060 | 76 | 1628218.9005 | -880129.5066 | 6111.3629 | 185108.6581 | 191220.021 | 214.6932 | 6502.897 | 6717.5902 | 184502.4308 | -695627.0757 | FALSE | 1360 | 60230 | -61274.9602 | 2393.0895 | 72484.911 | 74878.0006 | 116342.0205 | 55067.0602 | TRUE | Option 3 | 55067.0602 | 527
| FNS012-76065032 | 135 | 2892230.9417 | -1563387.9393 | 138883.3063 | 133769.9626 | 272653.269 | 4878.9929 | 6091.4103 | 10970.4033 | 261682.8657 | -1301705.0736 | FALSE | 1803 | 106987.5 | -108843.6794 | 54383.9721 | 54665.003 | 109048.9751 | 163604.2938 | 54760.6145 | TRUE | Option 3 | 54760.6145 | 528
| HTN012-160319327 | 65 | 1392555.6386 | -752742.3411 | 2441.717 | 177832.6281 | 180274.3451 | 85.7779 | 8097.8681 | 8183.646 | 172090.6991 | -580651.642 | FALSE | 1223 | 51512.5 | -52406.216 | 956.1284 | 72671.1809 | 73627.3093 | 106647.0359 | 54240.8199 | TRUE | Option 3 | 54240.8199 | 529
| KGT002-24605712 | 65 | 1392555.6386 | -752742.3411 | 5262.1823 | 169658.0673 | 174920.2496 | 184.8613 | 5960.1153 | 6144.9766 | 168775.273 | -583967.0681 | FALSE | 1226 | 51512.5 | -52406.216 | 2060.5671 | 66434.7634 | 68495.3305 | 106424.919 | 54018.7031 | TRUE | Option 3 | 54018.7031 | 530
| HSM004-159452345 | 63 | 1349707.7728 | -729581.0383 | 4526.3135 | 167653.0421 | 172179.3555 | 159.0101 | 5889.6784 | 6048.6885 | 166130.667 | -563450.3713 | FALSE | 1192 | 49927.5 | -50793.717 | 1772.4154 | 65649.635 | 67422.0503 | 104757.3052 | 53963.5882 | TRUE | Option 3 | 53963.5882 | 531
| HSM004-160438389 | 237 | 5077472.0977 | -2744614.3823 | 2772.086 | 399964.1324 | 402736.2184 | 97.3838 | 14050.8045 | 14148.1883 | 388588.0301 | -2356026.3522 | FALSE | 2062 | 187822.5 | -191081.126 | 1085.4944 | 156618.0904 | 157703.5847 | 245032.6337 | 53951.5077 | TRUE | Option 3 | 53951.5077 | 532
| RVL008-15418862 | 116 | 2485176.2166 | -1343355.5626 | 125256.8105 | 116695.1664 | 241951.9769 | 4400.292 | 4099.52 | 8499.812 | 233452.1649 | -1109903.3977 | FALSE | 1689 | 91930 | -93524.9393 | 49048.1042 | 45695.5328 | 94743.637 | 147208.3399 | 53683.4006 | TRUE | Option 3 | 53683.4006 | 533
| KGT004-15430149 | 74 | 1585371.0347 | -856968.2038 | 54833.1398 | 130813.3738 | 185646.5136 | 1926.297 | 4595.4949 | 6521.792 | 179124.7217 | -677843.4821 | FALSE | 1339 | 58645 | -59662.4613 | 21471.5795 | 51223.9452 | 72695.5247 | 112950.989 | 53288.5277 | TRUE | Option 3 | 53288.5277 | 534
| MRO005-155423773 | 50 | 1071196.6451 | -579032.5701 | 8949.9195 | 144555.8204 | 153505.7399 | 314.4121 | 5078.2693 | 5392.6814 | 148113.0585 | -430919.5116 | FALSE | 1005 | 39625 | -40312.4738 | 3504.6125 | 56605.2171 | 60109.8296 | 93395.9103 | 53083.4365 | TRUE | Option 3 | 53083.4365 | 535
| MRO007-76446321 | 55 | 1178316.3096 | -636935.8271 | 10450.4838 | 149608.049 | 160058.5328 | 367.1272 | 5255.7549 | 5622.8821 | 154435.6508 | -482500.1764 | FALSE | 1075 | 43587.5 | -44343.7212 | 4092.204 | 58583.5705 | 62675.7745 | 97382.7584 | 53039.0371 | TRUE | Option 3 | 53039.0371 | 536
| STL004-15415692 | 264 | 5655918.286 | -3057291.9701 | 156802.0206 | 280151.1388 | 436953.1593 | 5508.4803 | 9841.7547 | 15350.235 | 421602.9244 | -2635689.0458 | FALSE | 2094 | 209220 | -212849.8619 | 61400.5883 | 109701.6778 | 171102.266 | 265850.8933 | 53001.0314 | TRUE | Option 3 | 53001.0314 | 537
| OYN005-15412808 | 288 | 6170092.6757 | -3335227.6038 | 58491.5333 | 407304.929 | 465796.4623 | 2054.817 | 14308.6878 | 16363.5048 | 449432.9574 | -2885794.6463 | FALSE | 2118 | 228240 | -232199.8493 | 22904.1344 | 159492.602 | 182396.7364 | 283399.7259 | 51199.8766 | TRUE | Option 3 | 51199.8766 | 538
| DDL013-197602097 | 364 | 7798311.5762 | -4215357.1103 | 300484.8161 | 272380.2411 | 572865.0572 | 10556.08 | 12403.2315 | 22959.3116 | 549905.7456 | -3665451.3647 | FALSE | 2176 | 288470 | -293474.8095 | 117663.946 | 111307.9978 | 228971.9438 | 343893.1134 | 50418.3039 | TRUE | Option 3 | 50418.3039 | 539
| CTN001-161785823 | 97 | 2078121.4915 | -1123323.186 | 4761.6593 | 205264.7581 | 210026.4174 | 167.2779 | 7210.9841 | 7378.2619 | 202648.1555 | -920675.0305 | FALSE | 1576 | 76872.5 | -78206.1992 | 1864.5721 | 80377.6435 | 82242.2156 | 127784.2018 | 49578.0025 | TRUE | Option 3 | 49578.0025 | 540
| SHL001-160436010 | 118 | 2528024.0824 | -1366516.8654 | 5482.2031 | 231552.5328 | 237034.7358 | 192.5907 | 8134.4778 | 8327.0685 | 228707.6673 | -1137809.1981 | FALSE | 1710 | 93515 | -95137.4383 | 2146.7229 | 90671.4192 | 92818.1421 | 144216.5937 | 49079.1555 | TRUE | Option 3 | 49079.1555 | 541
| BGO023-76446934 | 65 | 1392555.6386 | -752742.3411 | 8863.1538 | 157152.0864 | 166015.2402 | 311.364 | 5520.7781 | 5832.1422 | 160183.0981 | -592559.2431 | FALSE | 1235 | 51512.5 | -52406.216 | 3470.6368 | 61537.6672 | 65008.304 | 101006.9363 | 48600.7203 | TRUE | Option 3 | 48600.7203 | 542
| FNS011-24604152 | 74 | 1585371.0347 | -856968.2038 | 59305.2799 | 121854.7813 | 181160.0612 | 2083.404 | 5548.8352 | 7632.2392 | 173527.822 | -683440.3818 | FALSE | 1345 | 58645 | -59662.4613 | 23222.7816 | 49795.8724 | 73018.654 | 108141.4072 | 48478.946 | TRUE | Option 3 | 48478.946 | 543
| HTN013-100723362 | 265 | 5677342.2189 | -3068872.6215 | 104613.6296 | 334696.4622 | 439310.0918 | 3675.0937 | 15240.8915 | 18915.9852 | 420394.1066 | -2648478.5149 | FALSE | 2096 | 210012.5 | -213656.1113 | 40964.6405 | 136773.4786 | 177738.1191 | 261571.9727 | 47915.8614 | TRUE | Option 3 | 47915.8614 | 544
| BAS011-164206932 | 334 | 7155593.5891 | -3867937.5683 | 100880.8637 | 432456.0887 | 533336.9524 | 3543.961 | 19692.5187 | 23236.4797 | 510100.4727 | -3357837.0956 | FALSE | 2160 | 264695 | -269287.3252 | 39502.9627 | 176722.8826 | 216225.8453 | 317111.1071 | 47823.7819 | TRUE | Option 3 | 47823.7819 | 545
| BET004-72500469 | 18 | 385630.7922 | -208451.7252 | 10665.1734 | 91460.0914 | 102125.2648 | 374.6693 | 3213.0078 | 3587.677 | 98537.5878 | -109914.1374 | FALSE | 402 | 14265 | -14512.4906 | 4176.2722 | 35813.9736 | 39990.2458 | 62135.0191 | 47622.5285 | TRUE | Option 3 | 47622.5285 | 546
| CHA006-185820630 | 198 | 4241938.7145 | -2292968.9776 | 77855.6936 | 262708.8951 | 340564.5887 | 2735.0831 | 9229.0059 | 11964.0889 | 328600.4998 | -1964368.4778 | FALSE | 1993 | 156915 | -159637.3964 | 30486.7589 | 102871.6381 | 133358.3969 | 207206.1918 | 47568.7954 | TRUE | Option 3 | 47568.7954 | 547
| CLC004-201015049 | 368 | 7884007.3078 | -4261679.716 | 42038.9189 | 538560.378 | 580599.2968 | 1476.834 | 24524.1323 | 26000.9663 | 554598.3306 | -3707081.3854 | FALSE | 2178 | 291640 | -296699.8074 | 16461.6141 | 220082.3272 | 236543.9413 | 344055.3555 | 47355.5481 | TRUE | Option 3 | 47355.5481 | 548
| HTN034-142233453 | 75 | 1606794.9676 | -868548.8552 | 2538.5579 | 179579.7443 | 182118.3021 | 89.1799 | 8177.4256 | 8266.6055 | 173851.6966 | -694697.1585 | FALSE | 1357 | 59437.5 | -60468.7108 | 994.0493 | 73385.1387 | 74379.1881 | 107739.1141 | 47270.4033 | TRUE | Option 3 | 47270.4033 | 549
| CTN006-155016482 | 73 | 1563947.1018 | -845387.5523 | 4757.1569 | 169570.3377 | 174327.4947 | 167.1197 | 5957.0333 | 6124.153 | 168203.3417 | -677184.2107 | FALSE | 1335 | 57852.5 | -58856.2118 | 1862.8091 | 66400.4103 | 68263.2194 | 106064.2753 | 47208.0635 | TRUE | Option 3 | 47208.0635 | 550
| CMN001-73948224 | 40 | 856957.3161 | -463226.0561 | 1913.1336 | 128480.4649 | 130393.5985 | 67.2087 | 4513.5395 | 4580.7481 | 125812.8503 | -337413.2057 | FALSE | 854 | 31700 | -32249.9791 | 749.1455 | 50310.4239 | 51059.5694 | 79334.029 | 47084.05 | TRUE | Option 3 | 47084.05 | 551
| EHK024-130742429 | 16 | 342782.9264 | -185290.4224 | 16344.7505 | 80676.9588 | 97021.7092 | 574.1937 | 2834.1946 | 3408.3883 | 93613.3209 | -91677.1015 | FALSE | 368 | 12680 | -12899.9916 | 6400.2829 | 31591.5108 | 37991.7937 | 59029.9155 | 46129.9239 | TRUE | Option 3 | 46129.9239 | 552
| BET005-76446537 | 66 | 1413979.5715 | -764322.9925 | 7014.0884 | 156031.3736 | 163045.462 | 246.4061 | 5481.4073 | 5727.8134 | 157317.6486 | -607005.3439 | FALSE | 1247 | 52305 | -53212.4655 | 2746.5791 | 61098.8181 | 63845.3972 | 99200.0648 | 45987.5993 | TRUE | Option 3 | 45987.5993 | 553
| HTN032-159443483 | 85 | 1821034.2966 | -984355.3692 | 5139.1544 | 187898.6054 | 193037.7598 | 180.5393 | 8556.237 | 8736.7764 | 184300.9834 | -800054.3858 | FALSE | 1470 | 67362.5 | -68531.2055 | 2012.3918 | 76784.6356 | 78797.0274 | 114240.7324 | 45709.5269 | TRUE | Option 3 | 45709.5269 | 554
| TNA022-194840439 | 115 | 2463752.2837 | -1331774.9112 | 103494.5711 | 126481.7845 | 229976.3557 | 3635.781 | 5759.5325 | 9395.3135 | 220581.0422 | -1111193.8691 | FALSE | 1691 | 91137.5 | -92718.6898 | 40526.4392 | 51686.6941 | 92213.1333 | 137763.2224 | 45044.5326 | TRUE | Option 3 | 45044.5326 | 555
| HTN034-158770892 | 249 | 5334559.2925 | -2883582.1991 | 5149.9864 | 410355.6723 | 415505.6588 | 180.9199 | 18686.144 | 18867.0639 | 396638.5949 | -2486943.6042 | FALSE | 2076 | 197332.5 | -200756.1197 | 2016.6334 | 167691.5626 | 169708.1961 | 245797.4627 | 45041.343 | TRUE | Option 3 | 45041.343 | 556
| HSM001-108341890 | 88 | 1885306.0953 | -1019097.3234 | 10090.421 | 180267.4392 | 190357.8602 | 354.4781 | 6332.8242 | 6687.3023 | 183670.5579 | -835426.7655 | FALSE | 1503 | 69740 | -70949.954 | 3951.2105 | 70589.1849 | 74540.3953 | 115817.4649 | 44867.5109 | TRUE | Option 3 | 44867.5109 | 557
| MLN022-84622495 | 18 | 385630.7922 | -208451.7252 | 15084.6847 | 84019.1522 | 99103.8369 | 529.9274 | 3825.9346 | 4355.862 | 94747.9748 | -113703.7504 | FALSE | 411 | 14265 | -14512.4906 | 5906.8659 | 34334.3686 | 40241.2346 | 58862.6023 | 44350.1117 | TRUE | Option 3 | 44350.1117 | 558
| CTN006-24605098 | 85 | 1821034.2966 | -984355.3692 | 9214.9544 | 176224.5314 | 185439.4858 | 323.7228 | 6190.7962 | 6514.519 | 178924.9667 | -805430.4024 | FALSE | 1473 | 67362.5 | -68531.2055 | 3608.395 | 69006.0617 | 72614.4566 | 112825.0292 | 44293.8236 | TRUE | Option 3 | 44293.8236 | 559
| BGO023-155521549 | 27 | 578446.1883 | -312677.5879 | 7050.6154 | 101081.2316 | 108131.847 | 247.6893 | 3551 | 3798.6892 | 104333.1578 | -208344.4301 | FALSE | 602 | 21397.5 | -21768.7359 | 2760.8824 | 39581.4229 | 42342.3052 | 65789.5417 | 44020.8059 | TRUE | Option 3 | 44020.8059 | 560
| BAS033-142953276 | 33 | 706989.7858 | -382161.4963 | 8129.638 | 110978.3721 | 119108.0101 | 285.5955 | 5053.562 | 5339.1575 | 113768.8526 | -268392.6437 | FALSE | 731 | 26152.5 | -26606.2327 | 3183.4064 | 45351.2353 | 48534.6417 | 70573.3685 | 43967.1357 | TRUE | Option 3 | 43967.1357 | 561
| BGO022-164367964 | 95 | 2035273.6257 | -1100161.8832 | 90367.5946 | 107581.3571 | 197948.9517 | 3174.6282 | 3779.3504 | 6953.9786 | 190994.9731 | -909166.9101 | FALSE | 1568 | 75287.5 | -76593.7003 | 35386.1733 | 42126.7442 | 77512.9175 | 120436.0342 | 43842.3339 | TRUE | Option 3 | 43842.3339 | 562
| CTN006-154972931 | 107 | 2292360.8205 | -1239129.7 | 2683.2756 | 210304.1555 | 212987.4311 | 94.2639 | 7388.0189 | 7482.2828 | 205505.1483 | -1033624.5517 | FALSE | 1650 | 84797.5 | -86268.694 | 1050.718 | 82350.9724 | 83401.6904 | 129585.7407 | 43317.0467 | TRUE | Option 3 | 43317.0467 | 563
| SHL001-160435873 | 118 | 2528024.0824 | -1366516.8654 | 6200.8385 | 220992.3713 | 227193.2098 | 217.8365 | 7763.4976 | 7981.3341 | 219211.8757 | -1147304.9898 | FALSE | 1715 | 93515 | -95137.4383 | 2428.1264 | 86536.2676 | 88964.394 | 138228.8158 | 43091.3775 | TRUE | Option 3 | 43091.3775 | 564
| SHN012-24613290 | 45 | 964076.9806 | -521129.3131 | 82675.9084 | 47647.8488 | 130323.7572 | 2904.418 | 1673.8766 | 4578.2946 | 125745.4626 | -395383.8505 | FALSE | 953 | 35662.5 | -36281.2265 | 32374.2602 | 18657.9608 | 51032.221 | 79291.5363 | 43010.3098 | TRUE | Option 3 | 43010.3098 | 565
| GSB012-77736949 | 36 | 771261.5845 | -416903.4505 | 16495.2695 | 104575.2125 | 121070.482 | 579.4815 | 4761.9848 | 5341.4663 | 115729.0157 | -301174.4348 | FALSE | 793 | 28530 | -29024.9812 | 6459.2232 | 42734.5885 | 49193.8117 | 71876.6703 | 42851.6891 | TRUE | Option 3 | 42851.6891 | 566
| CLC006-44811375 | 504 | 10797662.1824 | -5836648.3066 | 81085.9824 | 675875.5076 | 756961.49 | 2848.5636 | 30776.977 | 33625.5406 | 723335.9494 | -5113312.3573 | FALSE | 2214 | 399420 | -406349.7363 | 31751.6764 | 276196.0603 | 307947.7367 | 449013.7532 | 42664.017 | TRUE | Option 3 | 42664.017 | 567
| KGT003-155177979 | 14 | 299935.0606 | -162129.1196 | 4397.9621 | 83492.9786 | 87890.9407 | 154.5011 | 2933.1218 | 3087.6229 | 84803.3178 | -77325.8018 | FALSE | 341 | 11095 | -11287.4927 | 1722.1555 | 32694.2088 | 34416.3643 | 53474.5764 | 42187.0837 | TRUE | Option 3 | 42187.0837 | 568
| NHL031-47809173 | 72 | 1542523.1689 | -833806.9009 | 3482.5646 | 160898.5373 | 164381.1019 | 122.3431 | 5652.3916 | 5774.7346 | 158606.3673 | -675200.5336 | FALSE | 1333 | 57060 | -58049.9623 | 1363.7038 | 63004.7037 | 64368.4075 | 100012.6944 | 41962.7321 | TRUE | Option 3 | 41962.7321 | 569
| CTN002-154876793 | 70 | 1499675.3031 | -810645.5981 | 2821.9138 | 157332.0233 | 160153.9371 | 99.1343 | 5527.0993 | 5626.2336 | 154527.7034 | -656117.8947 | FALSE | 1302 | 55475 | -56437.4634 | 1105.006 | 61608.1269 | 62713.1329 | 97440.8042 | 41003.3408 | TRUE | Option 3 | 41003.3408 | 570
| SHP011-15432563 | 11 | 235663.2619 | -127387.1654 | 75250.3956 | 6060.5053 | 81310.9009 | 2643.5585 | 212.9065 | 2856.4651 | 78454.4358 | -48932.7296 | FALSE | 300 | 8717.5 | -8868.7442 | 29466.5754 | 2373.1747 | 31839.7501 | 49471.1508 | 40602.4065 | TRUE | Option 3 | 40602.4065 | 571
| HSM001-157598965 | 45 | 964076.9806 | -521129.3131 | 4463.3864 | 120070.0975 | 124533.4839 | 156.7995 | 4218.0819 | 4374.8814 | 120158.6025 | -400970.7105 | FALSE | 962 | 35662.5 | -36281.2265 | 1747.7744 | 47017.0894 | 48764.8638 | 75768.6201 | 39487.3937 | TRUE | Option 3 | 39487.3937 | 572
| HSM003-163378469 | 116 | 2485176.2166 | -1343355.5626 | 3798.46 | 214677.4078 | 218475.8678 | 133.4405 | 7541.652 | 7675.0925 | 210800.7753 | -1132554.7873 | FALSE | 1703 | 91930 | -93524.9393 | 1487.4022 | 84063.452 | 85550.8543 | 132925.0135 | 39400.0742 | TRUE | Option 3 | 39400.0742 | 573
| WMN021-24614598 | 73 | 1563947.1018 | -845387.5523 | 105613.5198 | 55735.143 | 161348.6628 | 3710.22 | 1957.9846 | 5668.2045 | 155680.4582 | -689707.0941 | FALSE | 1349 | 57852.5 | -58856.2118 | 41356.1778 | 21824.7862 | 63180.964 | 98167.6988 | 39311.487 | TRUE | Option 3 | 39311.487 | 574
| SHP012-153588795 | 79 | 1692490.6992 | -914871.4608 | 9869.5602 | 158978.0882 | 168847.6483 | 346.7192 | 5584.9259 | 5931.6451 | 162916.0032 | -751955.4575 | FALSE | 1419 | 62607.5 | -63693.7087 | 3864.7257 | 62252.6936 | 66117.4193 | 102730.229 | 39036.5204 | TRUE | Option 3 | 39036.5204 | 575
| HTN034-158095163 | 71 | 1521099.236 | -822226.2495 | 634.5612 | 161537.7436 | 162172.3048 | 22.2922 | 7355.8567 | 7378.149 | 154794.1558 | -667432.0937 | FALSE | 1323 | 56267.5 | -57243.7128 | 248.4817 | 66012.2876 | 66260.7693 | 95911.5355 | 38667.8227 | TRUE | Option 3 | 38667.8227 | 576
| DDL013-24612353 | 267 | 5720190.0847 | -3092033.9243 | 154450.5347 | 269741.4277 | 424191.9624 | 5425.8722 | 12283.0693 | 17708.9415 | 406483.0209 | -2685550.9035 | FALSE | 2098 | 211597.5 | -215268.6103 | 60479.7926 | 110229.6485 | 170709.4411 | 253482.5212 | 38213.9109 | TRUE | Option 3 | 38213.9109 | 577
| MRO005-155391898 | 39 | 835533.3832 | -451645.4047 | 3056.4337 | 110708.7016 | 113765.1353 | 107.373 | 3889.2145 | 3996.5876 | 109768.5478 | -341876.8569 | FALSE | 860 | 30907.5 | -31443.7296 | 1196.8393 | 43351.3509 | 44548.1902 | 69216.9451 | 37773.2155 | TRUE | Option 3 | 37773.2155 | 578
| BAS023-141849160 | 38 | 814109.4503 | -440064.7533 | 1743.0767 | 113352.0742 | 115095.1509 | 61.2346 | 5161.652 | 5222.8866 | 109872.2643 | -330192.489 | FALSE | 836 | 30115 | -30637.4801 | 682.5546 | 46321.247 | 47003.8015 | 68091.3493 | 37453.8692 | TRUE | Option 3 | 37453.8692 | 579
| HSM003-160683747 | 113 | 2420904.4179 | -1308613.6084 | 5363.2019 | 205794.1552 | 211157.357 | 188.4101 | 7229.5819 | 7417.992 | 203739.365 | -1104874.2434 | FALSE | 1684 | 89552.5 | -91106.1909 | 2100.1244 | 80584.9449 | 82685.0693 | 128472.2877 | 37366.0968 | TRUE | Option 3 | 37366.0968 | 580
| WPD011-15399285 | 155 | 3320709.5998 | -1795000.9673 | 0 | 274045.5463 | 274045.5463 | 0 | 12479.0636 | 12479.0636 | 261566.4827 | -1533434.4846 | FALSE | 1894 | 122837.5 | -124968.6689 | 0 | 111988.5236 | 111988.5236 | 162057.0227 | 37088.3538 | TRUE | Option 3 | 37088.3538 | 581
| BET005-76446461 | 46 | 985500.9135 | -532709.9645 | 13266.1722 | 108076.0257 | 121342.1979 | 466.0428 | 3796.7282 | 4262.771 | 117079.427 | -415630.5375 | FALSE | 983 | 36455 | -37087.4759 | 5194.7722 | 42320.4467 | 47515.2189 | 73826.979 | 36739.5031 | TRUE | Option 3 | 36739.5031 | 582
| CTN003-155024758 | 70 | 1499675.3031 | -810645.5981 | 1069.6167 | 151398.6307 | 152468.2475 | 37.5758 | 5318.6583 | 5356.2341 | 147112.0134 | -663533.5848 | FALSE | 1317 | 55475 | -56437.4634 | 418.8409 | 59284.7271 | 59703.568 | 92764.6795 | 36327.2161 | TRUE | Option 3 | 36327.2161 | 583
| EHK024-73766693 | 31 | 664141.92 | -359000.1935 | 12574.0586 | 87996.7142 | 100570.7728 | 441.7287 | 3091.3388 | 3533.0675 | 97037.7053 | -261962.4881 | FALSE | 715 | 24567.5 | -24993.7338 | 4923.7541 | 34457.7832 | 39381.5373 | 61189.2355 | 36195.5018 | TRUE | Option 3 | 36195.5018 | 584
| OYN005-160960634 | 91 | 1949577.894 | -1053839.2776 | 1863.2515 | 177912.5656 | 179775.8171 | 65.4563 | 6250.0971 | 6315.5534 | 173460.2637 | -880379.0139 | FALSE | 1548 | 72117.5 | -73368.7024 | 729.6127 | 69667.0627 | 70396.6753 | 109379.1418 | 36010.4394 | TRUE | Option 3 | 36010.4394 | 585
| BAN003-79424224 | 56 | 1199740.2425 | -648516.4785 | 8618.9572 | 128316.2855 | 136935.2427 | 302.7854 | 5843.0692 | 6145.8546 | 130789.3881 | -517727.0904 | FALSE | 1123 | 44380 | -45149.9707 | 3375.0142 | 52436.3616 | 55811.3758 | 81123.8669 | 35973.8962 | TRUE | Option 3 | 35973.8962 | 586
| PLD006-15398587 | 126 | 2699415.5456 | -1459162.0767 | 82967.7973 | 146208.5792 | 229176.3766 | 2914.6721 | 6657.8209 | 9572.493 | 219603.8836 | -1239558.1931 | FALSE | 1773 | 99855 | -101587.4341 | 32488.5582 | 59748.0351 | 92236.5933 | 136939.7833 | 35352.3492 | TRUE | Option 3 | 35352.3492 | 587
| NHL016-163161231 | 51 | 1092620.578 | -590613.2215 | 1535.2617 | 124013.7137 | 125548.9754 | 53.934 | 4356.6218 | 4410.5558 | 121138.4196 | -469474.8019 | FALSE | 1049 | 40417.5 | -41118.7233 | 601.1783 | 48561.332 | 49162.5103 | 76386.4651 | 35267.7418 | TRUE | Option 3 | 35267.7418 | 588
| BAS011-85724039 | 86 | 1842458.2295 | -995936.0206 | 5185.3892 | 171413.5066 | 176598.8958 | 182.1636 | 7805.564 | 7987.7276 | 168611.1682 | -827324.8523 | FALSE | 1491 | 68155 | -69337.455 | 2030.4965 | 70048.0113 | 72078.5078 | 104520.388 | 35182.933 | TRUE | Option 3 | 35182.933 | 589
| HSM006-160434642 | 27 | 578446.1883 | -312677.5879 | 2528.3053 | 90573.421 | 93101.7263 | 88.8198 | 3181.8589 | 3270.6787 | 89831.0476 | -222846.5402 | FALSE | 644 | 21397.5 | -21768.7359 | 990.0347 | 35466.7708 | 36456.8055 | 56644.9208 | 34876.1849 | TRUE | Option 3 | 34876.1849 | 590
| KGT003-155165638 | 50 | 1071196.6451 | -579032.5701 | 2182.7033 | 120233.2495 | 122415.9528 | 76.6787 | 4223.8134 | 4300.4922 | 118115.4606 | -460917.1095 | FALSE | 1038 | 39625 | -40312.4738 | 854.7037 | 47080.9765 | 47935.6802 | 74480.2726 | 34167.7987 | TRUE | Option 3 | 34167.7987 | 591
| BAN004-15414892 | 187 | 4006275.4526 | -2165581.8122 | 190344.9453 | 115390.0666 | 305735.012 | 6686.8486 | 5254.455 | 11941.3036 | 293793.7084 | -1871788.1038 | FALSE | 1975 | 148197.5 | -150768.6522 | 74535.3381 | 47154.0712 | 121689.4093 | 184045.6027 | 33276.9505 | TRUE | Option 3 | 33276.9505 | 592
| SHP014-24602868 | 117 | 2506600.1495 | -1354936.214 | 12495.5226 | 196754.6552 | 209250.1778 | 438.9697 | 6912.0228 | 7350.9925 | 201899.1853 | -1153037.0287 | FALSE | 1719 | 92722.5 | -94331.1888 | 4893.001 | 77045.2545 | 81938.2555 | 127311.9224 | 32980.7336 | TRUE | Option 3 | 32980.7336 | 593
| NHL015-158092654 | 61 | 1306859.907 | -706419.7355 | 2068.3009 | 132879.779 | 134948.0799 | 72.6597 | 4668.0881 | 4740.7478 | 130207.3321 | -576212.4034 | FALSE | 1212 | 48342.5 | -49181.2181 | 809.906 | 52033.1088 | 52843.0148 | 82105.0651 | 32923.847 | TRUE | Option 3 | 32923.847 | 594
| WBE011-203216132 | 271 | 5805885.8163 | -3138356.53 | 206276.2436 | 211936.845 | 418213.0886 | 7246.5177 | 9650.8533 | 16897.371 | 401315.7176 | -2737040.8124 | FALSE | 2102 | 214767.5 | -218493.6082 | 80773.7213 | 86607.8456 | 167381.5669 | 250831.5217 | 32337.9135 | TRUE | Option 3 | 32337.9135 | 595
| MRO007-161151299 | 25 | 535598.3225 | -289516.2851 | 2762.2407 | 82960.3686 | 85722.6093 | 97.038 | 2914.4111 | 3011.4491 | 82711.1602 | -206805.1248 | FALSE | 599 | 19812.5 | -20156.2369 | 1081.6391 | 32485.6492 | 33567.2884 | 52155.3209 | 31999.084 | TRUE | Option 3 | 31999.084 | 596
| HSM003-160683184 | 81 | 1735338.565 | -938032.7636 | 3278.5603 | 156622.6827 | 159901.243 | 115.1764 | 5502.1801 | 5617.3565 | 154283.8865 | -783748.877 | FALSE | 1453 | 64192.5 | -65306.2076 | 1283.8198 | 61330.3631 | 62614.1829 | 97287.0601 | 31980.8525 | TRUE | Option 3 | 31980.8525 | 597
| HTN032-159944977 | 78 | 1671066.7663 | -903290.8094 | 2882.1228 | 156552.4373 | 159434.5601 | 101.2494 | 7128.8436 | 7230.093 | 152204.4671 | -751086.3422 | FALSE | 1418 | 61815 | -62887.4592 | 1128.5826 | 63975.0456 | 65103.6282 | 94330.9319 | 31443.4727 | TRUE | Option 3 | 31443.4727 | 598
| BAS022-139345117 | 95 | 2035273.6257 | -1100161.8832 | 7212.9881 | 174300.408 | 181513.3961 | 253.3934 | 7937.0233 | 8190.4167 | 173322.9794 | -926838.9038 | FALSE | 1581 | 75287.5 | -76593.7003 | 2824.4643 | 71227.7416 | 74052.2059 | 107461.1902 | 30867.4899 | TRUE | Option 3 | 30867.4899 | 599
| KRT022-72389353 | 210 | 4499025.9093 | -2431936.7944 | 161116.2615 | 172401.4912 | 333517.7527 | 5660.0403 | 7850.5533 | 13510.5936 | 320007.1591 | -2111929.6353 | FALSE | 2016 | 166425 | -169312.3901 | 63089.9602 | 70451.7505 | 133541.7108 | 199976.042 | 30663.6518 | TRUE | Option 3 | 30663.6518 | 600
| HSM004-160438554 | 86 | 1842458.2295 | -995936.0206 | 3832.0113 | 160470.6747 | 164302.686 | 134.6192 | 5637.3607 | 5771.9799 | 158530.7061 | -837405.3144 | FALSE | 1504 | 68155 | -69337.455 | 1500.5403 | 62837.1611 | 64337.7014 | 99964.9846 | 30627.5296 | TRUE | Option 3 | 30627.5296 | 601
| BAS022-171331284 | 22 | 471326.5238 | -254774.3308 | 5849.7354 | 74944.1029 | 80793.8383 | 205.5021 | 3412.689 | 3618.1912 | 77175.6472 | -177598.6837 | FALSE | 550 | 17435 | -17737.4885 | 2290.6414 | 30625.856 | 32916.4974 | 47877.341 | 30139.8525 | TRUE | Option 3 | 30139.8525 | 602
| SHL001-162662856 | 67 | 1435403.5044 | -775903.6439 | 3275.6218 | 132491.0331 | 135766.6549 | 115.0731 | 4654.4314 | 4769.5045 | 130997.1504 | -644906.4935 | FALSE | 1288 | 53097.5 | -54018.7149 | 1282.6691 | 51880.8836 | 53163.5527 | 82603.1022 | 28584.3873 | TRUE | Option 3 | 28584.3873 | 603
| WND012-88220025 | 45 | 964076.9806 | -521129.3131 | 3523.3183 | 105936.4929 | 109459.8111 | 123.7747 | 4823.9727 | 4947.7474 | 104512.0637 | -416617.2494 | FALSE | 986 | 35662.5 | -36281.2265 | 1379.6622 | 43290.8748 | 44670.537 | 64789.2742 | 28508.0477 | TRUE | Option 3 | 28508.0477 | 604
| BAS023-155325011 | 39 | 835533.3832 | -451645.4047 | 2207.5309 | 98249.7675 | 100457.2984 | 77.5509 | 4473.9465 | 4551.4974 | 95905.8011 | -355739.6036 | FALSE | 880 | 30907.5 | -31443.7296 | 864.4257 | 40149.6998 | 41014.1255 | 59443.173 | 27999.4434 | TRUE | Option 3 | 27999.4434 | 605
| ART031-140150600 | 43 | 921229.1148 | -497968.0103 | 4795.26 | 98091.2154 | 102886.4753 | 168.4583 | 3445.9602 | 3614.4185 | 99272.0569 | -398695.9534 | FALSE | 957 | 34077.5 | -34668.7275 | 1877.7295 | 38410.5913 | 40288.3208 | 62598.1545 | 27929.427 | TRUE | Option 3 | 27929.427 | 606
| WPD014-15399222 | 47 | 1006924.8464 | -544290.6159 | 8112.8471 | 102637.8733 | 110750.7204 | 285.0056 | 4673.7652 | 4958.7709 | 105791.9495 | -438498.6664 | FALSE | 1013 | 37247.5 | -37893.7254 | 3176.8314 | 41942.8962 | 45119.7276 | 65630.9928 | 27737.2674 | TRUE | Option 3 | 27737.2674 | 607
| MDA023-24605266 | 304 | 6512875.6021 | -3520518.0262 | 93122.4838 | 354985.5556 | 448108.0394 | 3271.4079 | 12470.6998 | 15742.1077 | 432365.9317 | -3088152.0945 | FALSE | 2141 | 240920 | -245099.8409 | 36464.9337 | 139005.364 | 175470.2978 | 272637.7417 | 27537.9007 | TRUE | Option 3 | 27537.9007 | 608
| BAN003-141839757 | 47 | 1006924.8464 | -544290.6159 | 9092.5098 | 100855.4097 | 109947.9195 | 319.4213 | 4592.5982 | 4912.0195 | 105035.9 | -439254.7159 | FALSE | 1015 | 37247.5 | -37893.7254 | 3560.448 | 41214.4937 | 44774.9417 | 65172.9778 | 27279.2524 | TRUE | Option 3 | 27279.2524 | 609
| CTN004-155092123 | 34 | 728413.7187 | -393742.1477 | 2786.4602 | 86439.8979 | 89226.3581 | 97.8888 | 3036.6476 | 3134.5363 | 86091.8217 | -307650.3259 | FALSE | 797 | 26945 | -27412.4822 | 1091.123 | 33848.1645 | 34939.2875 | 54287.0706 | 26874.5884 | TRUE | Option 3 | 26874.5884 | 610
| WND014-153585710 | 19 | 407054.7251 | -220032.3766 | 16380.4218 | 54470.4416 | 70850.8634 | 575.4469 | 2480.391 | 3055.8379 | 67795.0255 | -152237.3511 | FALSE | 510 | 15057.5 | -15318.7401 | 6414.2511 | 22259.3084 | 28673.5595 | 42177.3038 | 26858.5638 | TRUE | Option 3 | 26858.5638 | 611
| HTN013-201063848 | 186 | 3984851.5197 | -2154001.1608 | 71942.778 | 224492.147 | 296434.925 | 2527.3614 | 10222.5773 | 12749.9387 | 283684.9863 | -1870316.1745 | FALSE | 1974 | 147405 | -149962.4027 | 28171.3774 | 91738.5611 | 119909.9385 | 176524.9865 | 26562.5838 | TRUE | Option 3 | 26562.5838 | 612
| BAN006-193339101 | 340 | 7284137.1866 | -3937421.4767 | 88574.5707 | 416988.7634 | 505563.3341 | 3111.639 | 18988.1915 | 22099.8304 | 483463.5037 | -3453957.973 | FALSE | 2168 | 269450 | -274124.8221 | 34684.0604 | 170402.1708 | 205086.2311 | 300477.103 | 26352.2809 | TRUE | Option 3 | 26352.2809 | 613
| CHA003-15429144 | 142 | 3042198.472 | -1644452.4991 | 67534.6601 | 163887.7686 | 231422.4287 | 2372.5035 | 5757.4037 | 8129.9072 | 223292.5215 | -1421159.9776 | FALSE | 1851 | 112535 | -114487.4257 | 26445.2451 | 64175.2279 | 90620.473 | 140801.9557 | 26314.53 | TRUE | Option 3 | 26314.53 | 614
| BET001-163979859 | 10 | 214239.329 | -115806.514 | 8576.1347 | 46908.5651 | 55484.6998 | 301.281 | 1647.9055 | 1949.1865 | 53535.5134 | -62271.0007 | FALSE | 321 | 7925 | -8062.4948 | 3358.2457 | 18368.4718 | 21726.7175 | 33757.9823 | 25695.4875 | TRUE | Option 3 | 25695.4875 | 615
| HSM002-158110691 | 106 | 2270936.8876 | -1227549.0486 | 3460.528 | 178828.2636 | 182288.7916 | 121.5689 | 6282.2657 | 6403.8346 | 175884.9569 | -1051664.0917 | FALSE | 1657 | 84005 | -85462.4445 | 1355.0747 | 70025.632 | 71380.7067 | 110908.0849 | 25445.6403 | TRUE | Option 3 | 25445.6403 | 616
| HTN033-159373599 | 64 | 1371131.7057 | -741161.6897 | 3605.0938 | 126450.7229 | 130055.8168 | 126.6475 | 5758.1181 | 5884.7656 | 124171.0512 | -616990.6386 | FALSE | 1261 | 50720 | -51599.9665 | 1411.6839 | 51674.0008 | 53085.6846 | 76970.1321 | 25370.1656 | TRUE | Option 3 | 25370.1656 | 617
| HTN013-142439156 | 48 | 1028348.7793 | -555871.2673 | 3242.0493 | 104432.4641 | 107674.5134 | 113.8937 | 4755.4846 | 4869.3783 | 102805.1351 | -453066.1322 | FALSE | 1033 | 38040 | -38699.9749 | 1269.5228 | 42676.2545 | 43945.7772 | 63728.7362 | 25028.7613 | TRUE | Option 3 | 25028.7613 | 618
| BAN006-72501281 | 96 | 2056697.5586 | -1111742.5346 | 7363.6319 | 164976.182 | 172339.8139 | 258.6856 | 7512.4311 | 7771.1166 | 164568.6972 | -947173.8373 | FALSE | 1595 | 76080 | -77399.9498 | 2883.4535 | 67417.4031 | 70300.8565 | 102038.9574 | 24639.0076 | TRUE | Option 3 | 24639.0076 | 619
| OYN005-164276023 | 151 | 3235013.8681 | -1748678.3617 | 2078.5176 | 238402.0757 | 240480.5933 | 73.0187 | 8375.1034 | 8448.122 | 232032.4713 | -1516645.8904 | FALSE | 1889 | 119667.5 | -121743.671 | 813.9066 | 93353.5655 | 94167.4721 | 146313.1212 | 24569.4502 | TRUE | Option 3 | 24569.4502 | 620
| MBN032-140148099 | 232 | 4970352.4332 | -2686711.1253 | 168582.8728 | 179034.635 | 347617.5078 | 5922.3435 | 6289.5156 | 12211.8591 | 335405.6487 | -2351305.4766 | FALSE | 2060 | 183860 | -187049.8786 | 66013.7384 | 70106.443 | 136120.1814 | 211497.3264 | 24447.4478 | TRUE | Option 3 | 24447.4478 | 621
| HSM003-160721106 | 78 | 1671066.7663 | -903290.8094 | 3358.223 | 139774.4974 | 143132.7203 | 117.9749 | 4910.3006 | 5028.2755 | 138104.4448 | -765186.3646 | FALSE | 1435 | 61815 | -62887.4592 | 1315.0141 | 54732.945 | 56047.9591 | 87084.7613 | 24197.3021 | TRUE | Option 3 | 24197.3021 | 622
| SHP014-15432602 | 154 | 3299285.6668 | -1783420.3159 | 77981.254 | 165647.3966 | 243628.6506 | 2739.494 | 5819.2198 | 8558.7138 | 235069.9368 | -1548350.3791 | FALSE | 1899 | 122045 | -124162.4194 | 30535.9258 | 64864.2636 | 95400.1895 | 148228.4611 | 24066.0417 | TRUE | Option 3 | 24066.0417 | 623
| HSM006-15416692 | 118 | 2528024.0824 | -1366516.8654 | 115547.8219 | 80348.0576 | 195895.8795 | 4059.2136 | 2822.6402 | 6881.8538 | 189014.0257 | -1177502.8398 | FALSE | 1735 | 93515 | -95137.4383 | 45246.2552 | 31462.7196 | 76708.9748 | 119186.9047 | 24049.4664 | TRUE | Option 3 | 24049.4664 | 624
| BGO023-76448158 | 38 | 814109.4503 | -440064.7533 | 7500.6068 | 82162.8073 | 89663.4142 | 263.4975 | 2886.3927 | 3149.8902 | 86513.524 | -353551.2293 | FALSE | 876 | 30115 | -30637.4801 | 2937.0902 | 32173.3399 | 35110.4301 | 54552.9841 | 23915.504 | TRUE | Option 3 | 23915.504 | 625
| STL006-144631935 | 72 | 1542523.1689 | -833806.9009 | 4299.4238 | 130304.2095 | 134603.6333 | 151.0395 | 4577.6079 | 4728.6473 | 129874.9859 | -703931.915 | FALSE | 1370 | 57060 | -58049.9623 | 1683.5698 | 51024.5665 | 52708.1363 | 81895.497 | 23845.5347 | TRUE | Option 3 | 23845.5347 | 626
| OYN005-84748828 | 93 | 1992425.7599 | -1077000.5804 | 16648.1926 | 144946.4722 | 161594.6648 | 584.8537 | 5091.9929 | 5676.8466 | 155917.8181 | -921082.7622 | FALSE | 1577 | 73702.5 | -74981.2013 | 6519.1049 | 56758.1886 | 63277.2935 | 98317.3712 | 23336.1699 | TRUE | Option 3 | 23336.1699 | 627
| BAN003-79424629 | 68 | 1456827.4373 | -787484.2953 | 11343.8077 | 120479.7942 | 131823.6018 | 398.5098 | 5486.2231 | 5884.7329 | 125938.8689 | -661545.4264 | FALSE | 1313 | 53890 | -54824.9644 | 4442.012 | 49233.9848 | 53675.9969 | 78147.605 | 23322.6405 | TRUE | Option 3 | 23322.6405 | 628
| MRO005-155505168 | 56 | 1199740.2425 | -648516.4785 | 4041.5029 | 108486.4473 | 112527.9503 | 141.9787 | 3811.1464 | 3953.125 | 108574.8252 | -539941.6533 | FALSE | 1165 | 44380 | -45149.9707 | 1582.5731 | 42481.1598 | 44063.7329 | 68464.2174 | 23314.2467 | TRUE | Option 3 | 23314.2467 | 629
| MRO007-76547638 | 59 | 1264012.0412 | -683258.4327 | 4722.3036 | 111562.0646 | 116284.3682 | 165.8953 | 3919.1933 | 4085.0886 | 112199.2796 | -571059.1531 | FALSE | 1205 | 46757.5 | -47568.7191 | 1849.1613 | 43685.511 | 45534.6723 | 70749.696 | 23180.9768 | TRUE | Option 3 | 23180.9768 | 630
| RCT015-15430944 | 25 | 535598.3225 | -289516.2851 | 46533.3687 | 24251.5738 | 70784.9425 | 1634.7247 | 851.9617 | 2486.6864 | 68298.2561 | -221218.029 | FALSE | 641 | 19812.5 | -20156.2369 | 18221.5523 | 9496.4395 | 27717.9918 | 43066.9508 | 22910.7139 | TRUE | Option 3 | 22910.7139 | 631
| HSM005-160419737 | 65 | 1392555.6386 | -752742.3411 | 2843.736 | 120938.2755 | 123782.0115 | 99.9009 | 4248.5811 | 4348.482 | 119433.5295 | -633308.8117 | FALSE | 1281 | 51512.5 | -52406.216 | 1113.5511 | 47357.0508 | 48470.602 | 75311.4095 | 22905.1935 | TRUE | Option 3 | 22905.1935 | 632
| CTN001-24611950 | 155 | 3320709.5998 | -1795000.9673 | 21741.5294 | 221006.251 | 242747.7803 | 763.7834 | 7763.9852 | 8527.7687 | 234220.0117 | -1560780.9556 | FALSE | 1903 | 122837.5 | -124968.6689 | 8513.5554 | 86541.7026 | 95055.258 | 147692.5223 | 22723.8534 | TRUE | Option 3 | 22723.8534 | 633
| BGO023-76447847 | 83 | 1778186.4308 | -961194.0664 | 6716.0682 | 140613.8931 | 147329.9613 | 235.9366 | 4939.7887 | 5175.7253 | 142154.236 | -819039.8304 | FALSE | 1482 | 65777.5 | -66918.7066 | 2629.8803 | 55061.6358 | 57691.5161 | 89638.4452 | 22719.7386 | TRUE | Option 3 | 22719.7386 | 634
| BAN009-77240588 | 124 | 2656567.6798 | -1436000.7739 | 6281.597 | 200360.3981 | 206641.9951 | 220.6735 | 9123.7029 | 9344.3765 | 197297.6186 | -1238703.1552 | FALSE | 1771 | 98270 | -99974.9351 | 2459.7499 | 81877.1386 | 84336.8884 | 122305.1066 | 22330.1715 | TRUE | Option 3 | 22330.1715 | 635
| KGT004-154878151 | 86 | 1842458.2295 | -995936.0206 | 2799.6276 | 147860.0854 | 150659.713 | 98.3514 | 5194.3486 | 5292.7 | 145367.013 | -850569.0076 | FALSE | 1515 | 68155 | -69337.455 | 1096.2791 | 57899.1023 | 58995.3814 | 91664.3316 | 22326.8766 | TRUE | Option 3 | 22326.8766 | 636
| HSM003-160653643 | 112 | 2399480.485 | -1297032.957 | 3181.9473 | 181524.6672 | 184706.6144 | 111.7823 | 6376.9908 | 6488.7732 | 178217.8413 | -1118815.1157 | FALSE | 1694 | 88760 | -90299.9414 | 1245.988 | 71081.4906 | 72327.4786 | 112379.1358 | 22079.1944 | TRUE | Option 3 | 22079.1944 | 637
| BET007-110330821 | 24 | 514174.3896 | -277935.6336 | 8157.6441 | 59698.5293 | 67856.1734 | 286.5794 | 2097.219 | 2383.7983 | 65472.3751 | -212463.2586 | FALSE | 616 | 19020 | -19349.9874 | 3194.373 | 23376.7703 | 26571.1434 | 41285.0301 | 21935.0426 | TRUE | Option 3 | 21935.0426 | 638
| HSM001-167869862 | 76 | 1628218.9005 | -880129.5066 | 3214.3382 | 131423.6144 | 134637.9525 | 112.9202 | 4616.9328 | 4729.853 | 129908.0995 | -750221.407 | FALSE | 1417 | 60230 | -61274.9602 | 1258.6716 | 51462.9034 | 52721.575 | 81916.3775 | 20641.4173 | TRUE | Option 3 | 20641.4173 | 639
| CTN001-24611782 | 45 | 964076.9806 | -521129.3131 | 46190.9862 | 47245.3953 | 93436.3815 | 1622.6968 | 1659.7384 | 3282.4352 | 90153.9464 | -430975.3667 | FALSE | 1006 | 35662.5 | -36281.2265 | 18087.482 | 18500.3679 | 36587.8499 | 56848.5316 | 20567.3052 | TRUE | Option 3 | 20567.3052 | 640
| NHL031-159317140 | 187 | 4006275.4526 | -2165581.8122 | 3481.5903 | 277985.8949 | 281467.4851 | 122.3088 | 9765.6893 | 9887.9981 | 271579.487 | -1894002.3252 | FALSE | 1978 | 148197.5 | -150768.6522 | 1363.3223 | 108853.8108 | 110217.1331 | 171250.352 | 20481.6999 | TRUE | Option 3 | 20481.6999 | 641
| OYN005-203082808 | 102 | 2185241.156 | -1181226.443 | 3940.2988 | 164752.5521 | 168692.8509 | 138.4233 | 5787.7837 | 5926.2071 | 162766.6438 | -1018459.7992 | FALSE | 1642 | 80835 | -82237.4466 | 1542.9435 | 64513.8601 | 66056.8037 | 102636.0472 | 20398.6006 | TRUE | Option 3 | 20398.6006 | 642
| BET001-143534818 | 32 | 685565.8529 | -370580.8449 | 4512.1369 | 71338.2388 | 75850.3757 | 158.5121 | 2506.1238 | 2664.6359 | 73185.7398 | -297395.1051 | FALSE | 778 | 25360 | -25799.9833 | 1766.8641 | 27934.6517 | 29701.5158 | 46148.8599 | 20348.8767 | TRUE | Option 3 | 20348.8767 | 643
| OYN005-160827931 | 217 | 4648993.4397 | -2513001.3542 | 1469.4204 | 319319.4875 | 320788.908 | 51.621 | 11217.7451 | 11269.3661 | 309519.5419 | -2203481.8123 | FALSE | 2032 | 171972.5 | -174956.1365 | 575.3962 | 125039.233 | 125614.6292 | 195174.2788 | 20218.1424 | TRUE | Option 3 | 20218.1424 | 644
| MRO008-77241511 | 72 | 1542523.1689 | -833806.9009 | 4822.326 | 123793.0531 | 128615.3791 | 169.4091 | 4348.8699 | 4518.279 | 124097.1001 | -709709.8009 | FALSE | 1378 | 57060 | -58049.9623 | 1888.328 | 48474.9256 | 50363.2537 | 78252.1254 | 20202.1631 | TRUE | Option 3 | 20202.1631 | 645
| HSM003-161008360 | 88 | 1885306.0953 | -1019097.3234 | 4706.5494 | 145040.2938 | 149746.8432 | 165.3418 | 5095.2889 | 5260.6308 | 144486.2125 | -874611.1109 | FALSE | 1540 | 69740 | -70949.954 | 1842.9922 | 56794.9273 | 58637.9196 | 91108.9237 | 20158.9697 | TRUE | Option 3 | 20158.9697 | 646
| WND013-76546854 | 40 | 856957.3161 | -463226.0561 | 5326.0096 | 82786.6143 | 88112.6238 | 187.1036 | 3769.8092 | 3956.9128 | 84155.7111 | -379070.345 | FALSE | 923 | 31700 | -32249.9791 | 2085.5606 | 33830.6929 | 35916.2535 | 52196.3704 | 19946.3913 | TRUE | Option 3 | 19946.3913 | 647
| BET004-163616866 | 9 | 192815.3961 | -104225.8626 | 9304.3632 | 34900.6809 | 44205.0441 | 326.8638 | 1226.0665 | 1552.9303 | 42652.1138 | -61573.7489 | FALSE | 320 | 7132.5 | -7256.2453 | 3643.4057 | 13666.4204 | 17309.8261 | 26895.218 | 19638.9727 | TRUE | Option 3 | 19638.9727 | 648
| BET007-132750977 | 39 | 835533.3832 | -451645.4047 | 6155.0241 | 76393.3747 | 82548.3988 | 216.227 | 2683.7116 | 2899.9386 | 79648.4603 | -371996.9444 | FALSE | 914 | 30907.5 | -31443.7296 | 2410.1864 | 29914.1435 | 32324.33 | 50224.0689 | 18780.3393 | TRUE | Option 3 | 18780.3393 | 649
| OYN005-160930950 | 123 | 2635143.7469 | -1424420.1225 | 1905.7895 | 191343.0176 | 193248.8071 | 66.9507 | 6721.9111 | 6788.8618 | 186459.9453 | -1237960.1771 | FALSE | 1770 | 97477.5 | -99168.6856 | 746.2697 | 74926.1636 | 75672.4333 | 117576.3738 | 18407.6881 | TRUE | Option 3 | 18407.6881 | 650
| PLD005-15398737 | 95 | 2035273.6257 | -1100161.8832 | 68618.8233 | 89951.7354 | 158570.5587 | 2410.5903 | 4096.0835 | 6506.6738 | 152063.8849 | -948097.9983 | FALSE | 1596 | 75287.5 | -76593.7003 | 26869.782 | 36758.7147 | 63628.4967 | 94942.062 | 18348.3617 | TRUE | Option 3 | 18348.3617 | 651
| BET005-143035691 | 14 | 299935.0606 | -162129.1196 | 2802.5321 | 45554.6513 | 48357.1834 | 98.4534 | 1600.3422 | 1698.7956 | 46658.3877 | -115470.7319 | FALSE | 413 | 11095 | -11287.4927 | 1097.4165 | 17838.3058 | 18935.7222 | 29421.4611 | 18133.9685 | TRUE | Option 3 | 18133.9685 | 652
| CTN003-155422079 | 107 | 2292360.8205 | -1239129.7 | 1287.853 | 170251.3816 | 171539.2346 | 45.2425 | 5980.9585 | 6026.201 | 165513.0336 | -1073616.6664 | FALSE | 1666 | 84797.5 | -86268.694 | 504.2979 | 66667.0936 | 67171.3916 | 104367.8431 | 18099.149 | TRUE | Option 3 | 18099.149 | 653
| CTN003-155024899 | 60 | 1285435.9741 | -694839.0841 | 1126.157 | 107873.3186 | 108999.4755 | 39.5621 | 3789.6071 | 3829.1692 | 105170.3064 | -589668.7777 | FALSE | 1233 | 47550 | -48374.9686 | 440.9809 | 42241.0706 | 42682.0515 | 66317.424 | 17942.4554 | TRUE | Option 3 | 17942.4554 | 654
| WND012-93532641 | 60 | 1285435.9741 | -694839.0841 | 50622.141 | 60047.5891 | 110669.7302 | 1778.364 | 2734.3545 | 4512.7185 | 106157.0116 | -588682.0725 | FALSE | 1231 | 47550 | -48374.9686 | 19822.6351 | 24538.4059 | 44361.041 | 66308.6891 | 17933.7205 | TRUE | Option 3 | 17933.7205 | 655
| CTN001-155822565 | 64 | 1371131.7057 | -741161.6897 | 2973.1872 | 110981.8048 | 113954.992 | 104.4485 | 3898.8087 | 4003.2572 | 109951.7347 | -631209.955 | FALSE | 1278 | 50720 | -51599.9665 | 1164.2416 | 43458.2927 | 44622.5343 | 69332.4576 | 17732.4911 | TRUE | Option 3 | 17732.4911 | 656
| KGT003-155165904 | 22 | 471326.5238 | -254774.3308 | 1888.1954 | 56327.8599 | 58216.0552 | 66.3326 | 1978.8068 | 2045.1394 | 56170.9158 | -198603.415 | FALSE | 590 | 17435 | -17737.4885 | 739.3802 | 22056.8824 | 22796.2626 | 35419.7926 | 17682.3041 | TRUE | Option 3 | 17682.3041 | 657
| BAS011-172348924 | 40 | 856957.3161 | -463226.0561 | 5952.289 | 76715.5111 | 82667.8001 | 209.1049 | 3493.3527 | 3702.4576 | 78965.3425 | -384260.7136 | FALSE | 935 | 31700 | -32249.9791 | 2330.7993 | 31349.7407 | 33680.5401 | 48987.26 | 16737.2809 | TRUE | Option 3 | 16737.2809 | 658
| STL006-155132926 | 43 | 921229.1148 | -497968.0103 | 2644.6516 | 81661.7725 | 84306.4241 | 92.907 | 2868.7912 | 2961.6983 | 81344.7258 | -416623.2845 | FALSE | 987 | 34077.5 | -34668.7275 | 1035.5936 | 31977.1445 | 33012.7381 | 51293.686 | 16624.9585 | TRUE | Option 3 | 16624.9585 | 659
| MBN031-52301620 | 129 | 2763687.3443 | -1493904.0309 | 19643.6031 | 178551.4484 | 198195.0515 | 690.0829 | 6272.5412 | 6962.6241 | 191232.4274 | -1302671.6035 | FALSE | 1806 | 102232.5 | -104006.1825 | 7692.0487 | 69917.2366 | 77609.2854 | 120585.7661 | 16579.5836 | TRUE | Option 3 | 16579.5836 | 660
| BET003-15424094 | 59 | 1264012.0412 | -683258.4327 | 57535.4807 | 47888.3084 | 105423.7891 | 2021.2307 | 1682.324 | 3703.5547 | 101720.2344 | -581538.1983 | FALSE | 1224 | 46757.5 | -47568.7191 | 22529.763 | 18752.12 | 41281.883 | 64141.9061 | 16573.1869 | TRUE | Option 3 | 16573.1869 | 661
| HTN034-190418432 | 29 | 621294.0541 | -335838.8907 | 38003.5943 | 27818.9835 | 65822.5777 | 1335.0724 | 1266.778 | 2601.8504 | 63220.7274 | -272618.1633 | FALSE | 736 | 22982.5 | -23381.2348 | 14881.4603 | 11368.2084 | 26249.6687 | 39572.909 | 16191.6742 | TRUE | Option 3 | 16191.6742 | 662
| CHA006-155618140 | 28 | 599870.1212 | -324258.2393 | 2855.0761 | 60315.4829 | 63170.5591 | 100.2993 | 2118.8926 | 2219.1919 | 60951.3671 | -263306.8721 | FALSE | 717 | 22190 | -22574.9853 | 1117.9917 | 23618.3572 | 24736.3489 | 38434.2102 | 15859.2248 | TRUE | Option 3 | 15859.2248 | 663
| HSM006-160439464 | 75 | 1606794.9676 | -868548.8552 | 2580.7114 | 122806.5971 | 125387.3085 | 90.6608 | 4314.2156 | 4404.8764 | 120982.4321 | -747566.4231 | FALSE | 1412 | 59437.5 | -60468.7108 | 1010.5558 | 48088.6489 | 49099.2047 | 76288.1038 | 15819.393 | TRUE | Option 3 | 15819.393 | 664
| NHL016-157328461 | 45 | 964076.9806 | -521129.3131 | 1259.9857 | 83793.9309 | 85053.9166 | 44.2635 | 2943.6943 | 2987.9578 | 82065.9588 | -439063.3543 | FALSE | 1014 | 35662.5 | -36281.2265 | 493.3856 | 32812.0558 | 33305.4415 | 51748.4752 | 15467.2487 | TRUE | Option 3 | 15467.2487 | 665
| CTN006-155062651 | 135 | 2892230.9417 | -1563387.9393 | 3218.765 | 201003.1292 | 204221.8942 | 113.0757 | 7061.2723 | 7174.3481 | 197047.5461 | -1366340.3932 | FALSE | 1829 | 106987.5 | -108843.6794 | 1260.4051 | 78708.8734 | 79969.2785 | 124252.6157 | 15408.9364 | TRUE | Option 3 | 15408.9364 | 666
| CRO033-15404721 | 62 | 1328283.8399 | -718000.3869 | 71711.6496 | 36546.4399 | 108258.0895 | 2519.2418 | 1664.1954 | 4183.4373 | 104074.6522 | -613925.7347 | FALSE | 1259 | 49135 | -49987.4676 | 28080.872 | 14934.6775 | 43015.5495 | 65242.54 | 15255.0724 | TRUE | Option 3 | 15255.0724 | 667
| BAN003-171330864 | 24 | 514174.3896 | -277935.6336 | 6554.8156 | 51719.2818 | 58274.0974 | 230.2717 | 2355.1129 | 2585.3847 | 55688.7127 | -222246.9209 | FALSE | 642 | 19020 | -19349.9874 | 2566.7369 | 21135.0489 | 23701.7858 | 34572.3116 | 15222.3242 | TRUE | Option 3 | 15222.3242 | 668
| CTN001-155143776 | 74 | 1585371.0347 | -856968.2038 | 5450.176 | 117616.6187 | 123066.7948 | 191.4656 | 4131.8908 | 4323.3563 | 118743.4384 | -738224.7653 | FALSE | 1402 | 58645 | -59662.4613 | 2134.1818 | 46056.3554 | 48190.5372 | 74876.2576 | 15213.7963 | TRUE | Option 3 | 15213.7963 | 669
| EHK031-134953882 | 30 | 642717.987 | -347419.5421 | 8758.0957 | 55816.1919 | 64574.2876 | 307.6733 | 1960.8318 | 2268.5051 | 62305.7825 | -285113.7596 | FALSE | 753 | 23775 | -24187.4843 | 3429.4981 | 21856.5233 | 25286.0214 | 39288.2662 | 15100.7819 | TRUE | Option 3 | 15100.7819 | 670
| CTN001-155821745 | 66 | 1413979.5715 | -764322.9925 | 3176.389 | 108697.7209 | 111874.1099 | 111.5871 | 3818.5685 | 3930.1555 | 107943.9544 | -656379.0381 | FALSE | 1303 | 52305 | -53212.4655 | 1243.8115 | 42563.8904 | 43807.7018 | 68066.4081 | 14853.9426 | TRUE | Option 3 | 14853.9426 | 671
| CTN006-155078364 | 68 | 1456827.4373 | -787484.2953 | 1228.7362 | 112989.1054 | 114217.8415 | 43.1657 | 3969.3255 | 4012.4912 | 110205.3503 | -677278.945 | FALSE | 1336 | 53890 | -54824.9644 | 481.1489 | 44244.3121 | 44725.461 | 69492.3805 | 14667.4161 | TRUE | Option 3 | 14667.4161 | 672
| CTN003-155025401 | 77 | 1649642.8334 | -891710.158 | 1598.4801 | 124411.0396 | 126009.5197 | 56.1549 | 4370.5799 | 4426.7347 | 121582.785 | -770127.373 | FALSE | 1441 | 61022.5 | -62081.2097 | 625.9334 | 48716.917 | 49342.8504 | 76666.6693 | 14585.4596 | TRUE | Option 3 | 14585.4596 | 673
| MRO008-129258570 | 27 | 578446.1883 | -312677.5879 | 2319.5834 | 57418.4138 | 59737.9972 | 81.4873 | 2017.1181 | 2098.6055 | 57639.3917 | -255038.1961 | FALSE | 708 | 21397.5 | -21768.7359 | 908.3033 | 22483.9219 | 23392.2252 | 36345.772 | 14577.0362 | TRUE | Option 3 | 14577.0362 | 674
| HSM002-163560034 | 139 | 2977926.6733 | -1609710.5449 | 5232.2442 | 202557.2649 | 207789.509 | 183.8096 | 7115.8694 | 7299.679 | 200489.8301 | -1409220.7148 | FALSE | 1848 | 110157.5 | -112068.6773 | 2048.8439 | 79317.4423 | 81366.2863 | 126423.2227 | 14354.5455 | TRUE | Option 3 | 14354.5455 | 675
| HSM002-155422817 | 22 | 471326.5238 | -254774.3308 | 1194.2321 | 51220.2498 | 52414.4819 | 41.9536 | 1799.3756 | 1841.3292 | 50573.1527 | -204201.1781 | FALSE | 595 | 17435 | -17737.4885 | 467.6378 | 20056.8428 | 20524.4806 | 31890.0013 | 14152.5129 | TRUE | Option 3 | 14152.5129 | 676
| KGT003-155165426 | 30 | 642717.987 | -347419.5421 | 1842.5684 | 60899.4713 | 62742.0397 | 64.7297 | 2139.4082 | 2204.138 | 60537.9017 | -286881.6403 | FALSE | 758 | 23775 | -24187.4843 | 721.5136 | 23847.0356 | 24568.5491 | 38173.4906 | 13986.0063 | TRUE | Option 3 | 13986.0063 | 677
| ECA001-24613414 | 55 | 1178316.3096 | -636935.8271 | 42577.0923 | 52948.1994 | 95525.2917 | 1495.7401 | 1860.0788 | 3355.8189 | 92169.4728 | -544766.3543 | FALSE | 1172 | 43587.5 | -44343.7212 | 16672.3522 | 20733.4738 | 37405.826 | 58119.4656 | 13775.7444 | TRUE | Option 3 | 13775.7444 | 678
| BET005-143035133 | 48 | 1028348.7793 | -555871.2673 | 7364.7439 | 78603.8489 | 85968.5928 | 258.7246 | 2761.3659 | 3020.0905 | 82948.5023 | -472922.765 | FALSE | 1056 | 38040 | -38699.9749 | 2883.8889 | 30779.7218 | 33663.6107 | 52304.9822 | 13605.0073 | TRUE | Option 3 | 13605.0073 | 679
| BAS011-76150666 | 47 | 1006924.8464 | -544290.6159 | 1900.4225 | 85098.8486 | 86999.2711 | 66.7621 | 3875.1002 | 3941.8623 | 83057.4088 | -461233.2071 | FALSE | 1039 | 37247.5 | -37893.7254 | 744.1681 | 34775.5858 | 35519.7539 | 51479.5172 | 13585.7918 | TRUE | Option 3 | 13585.7918 | 680
| BET005-142632215 | 35 | 749837.6516 | -405322.7991 | 4061.835 | 64585.7848 | 68647.6198 | 142.6929 | 2268.909 | 2411.602 | 66236.0178 | -339086.7812 | FALSE | 855 | 27737.5 | -28218.7317 | 1590.5347 | 25290.5235 | 26881.0582 | 41766.5616 | 13547.8299 | TRUE | Option 3 | 13547.8299 | 681
| RCT023-162905845 | 43 | 921229.1148 | -497968.0103 | 1400.5318 | 77351.6031 | 78752.135 | 49.2009 | 2717.3743 | 2766.5752 | 75985.5598 | -421982.4505 | FALSE | 995 | 34077.5 | -34668.7275 | 548.4207 | 30289.3669 | 30837.7877 | 47914.3473 | 13245.6198 | TRUE | Option 3 | 13245.6198 | 682
| BAS022-163916141 | 17 | 364206.8593 | -196871.0738 | 3346.3727 | 41079.6061 | 44425.9787 | 117.5586 | 1870.6198 | 1988.1784 | 42437.8003 | -154433.2735 | FALSE | 512 | 13472.5 | -13706.2411 | 1310.3737 | 16787.1527 | 18097.5264 | 26328.4523 | 12622.2112 | TRUE | Option 3 | 12622.2112 | 683
| BET007-154907735 | 14 | 299935.0606 | -162129.1196 | 3210.1048 | 35768.9856 | 38979.0903 | 112.7715 | 1256.5702 | 1369.3417 | 37609.7486 | -124519.371 | FALSE | 440 | 11095 | -11287.4927 | 1257.0139 | 14006.4315 | 15263.4454 | 23715.645 | 12428.1523 | TRUE | Option 3 | 12428.1523 | 684
| CMN003-76447191 | 12 | 257087.1948 | -138967.8168 | 2621.1025 | 33428.9237 | 36050.0261 | 92.0798 | 1174.3635 | 1266.4432 | 34783.5829 | -104184.2339 | FALSE | 388 | 9510 | -9674.9937 | 1026.3722 | 13090.1092 | 14116.4814 | 21933.5447 | 12258.551 | TRUE | Option 3 | 12258.551 | 685
| WMN021-24614498 | 53 | 1135468.4438 | -613774.5243 | 28037.9343 | 62274.9249 | 90312.8592 | 984.9772 | 2187.7282 | 3172.7053 | 87140.1539 | -526634.3704 | FALSE | 1139 | 42002.5 | -42731.2223 | 10979.1038 | 24385.6362 | 35364.74 | 54948.1192 | 12216.8969 | TRUE | Option 3 | 12216.8969 | 686
| BET007-154907496 | 17 | 364206.8593 | -196871.0738 | 5081.8308 | 37487.024 | 42568.8548 | 178.5255 | 1316.9252 | 1495.4507 | 41073.4041 | -155797.6698 | FALSE | 513 | 13472.5 | -13706.2411 | 1989.945 | 14679.1815 | 16669.1266 | 25899.7282 | 12193.4871 | TRUE | Option 3 | 12193.4871 | 687
| CLC003-24597492 | 148 | 3170742.0694 | -1713936.4075 | 68361.211 | 152016.2599 | 220377.4709 | 2401.5404 | 6922.2821 | 9323.8225 | 211053.6485 | -1502882.759 | FALSE | 1881 | 117290 | -119324.9226 | 26768.9062 | 62121.3398 | 88890.246 | 131487.2249 | 12162.3024 | TRUE | Option 3 | 12162.3024 | 688
| MNA014-203082790 | 99 | 2120969.3573 | -1146484.4888 | 29737.4844 | 120898.5809 | 150636.0653 | 1044.6826 | 4247.1866 | 5291.8693 | 145344.196 | -1001140.2928 | FALSE | 1631 | 78457.5 | -79818.6982 | 11644.6142 | 47341.5072 | 58986.1214 | 91649.9438 | 11831.2456 | TRUE | Option 3 | 11831.2456 | 689
| BMH003-137632826 | 70 | 1499675.3031 | -810645.5981 | 8376.5037 | 106510.5303 | 114887.0339 | 294.2679 | 4850.1123 | 5144.3803 | 109742.6537 | -700902.9445 | FALSE | 1366 | 55475 | -56437.4634 | 3280.0741 | 43525.4548 | 46805.5289 | 68081.505 | 11644.0417 | TRUE | Option 3 | 11644.0417 | 690
| GSB014-73768594 | 15 | 321358.9935 | -173709.771 | 5744.8977 | 33617.3334 | 39362.2311 | 201.8192 | 1530.8143 | 1732.6335 | 37629.5976 | -136080.1734 | FALSE | 463 | 11887.5 | -12093.7422 | 2249.589 | 13737.7001 | 15987.2891 | 23374.942 | 11281.1998 | TRUE | Option 3 | 11281.1998 | 691
| CTN003-155063034 | 55 | 1178316.3096 | -636935.8271 | 867.7815 | 90475.7658 | 91343.5472 | 30.4853 | 3178.4282 | 3208.9135 | 88134.6337 | -548801.1934 | FALSE | 1174 | 43587.5 | -44343.7212 | 339.8062 | 35428.531 | 35768.3371 | 55575.2101 | 11231.4889 | TRUE | Option 3 | 11231.4889 | 692
| BET007-154907629 | 7 | 149967.5303 | -81064.5598 | 3812.672 | 23890.242 | 27702.914 | 133.9398 | 839.2681 | 973.2078 | 26729.7062 | -54334.8537 | FALSE | 302 | 5547.5 | -5643.7463 | 1492.9674 | 9354.9491 | 10847.9164 | 16854.9976 | 11211.2512 | TRUE | Option 3 | 11211.2512 | 693
| CMN001-163864096 | 7 | 149967.5303 | -81064.5598 | 1931.5737 | 25547.4206 | 27478.9942 | 67.8565 | 897.485 | 965.3415 | 26513.6527 | -54550.9071 | FALSE | 303 | 5547.5 | -5643.7463 | 756.3663 | 10003.8676 | 10760.2339 | 16718.7604 | 11075.014 | TRUE | Option 3 | 11075.014 | 694
| CTN006-154973045 | 49 | 1049772.7122 | -567451.9187 | 850.269 | 81374.4544 | 82224.7234 | 29.8701 | 2858.6977 | 2888.5678 | 79336.1556 | -488115.7631 | FALSE | 1083 | 38832.5 | -39506.2244 | 332.9486 | 31864.6364 | 32197.585 | 50027.1384 | 10520.914 | TRUE | Option 3 | 10520.914 | 695
| HSM003-160683337 | 61 | 1306859.907 | -706419.7355 | 3592.2362 | 94443.2117 | 98035.448 | 126.1958 | 3317.8053 | 3444.0011 | 94591.4469 | -611828.2886 | FALSE | 1255 | 48342.5 | -49181.2181 | 1406.6491 | 36982.1048 | 38388.7539 | 59646.6941 | 10465.476 | TRUE | Option 3 | 10465.476 | 696
| MNA034-157168509 | 54 | 1156892.3767 | -625355.1757 | 3028.0597 | 85631.1859 | 88659.2456 | 106.3762 | 3008.2374 | 3114.6136 | 85544.632 | -539810.5437 | FALSE | 1164 | 42795 | -43537.4717 | 1185.7286 | 33531.4888 | 34717.2174 | 53942.0282 | 10404.5564 | TRUE | Option 3 | 10404.5564 | 697
| WND013-85833772 | 42 | 899805.1819 | -486387.3589 | 7402.4141 | 67162.0843 | 74564.4984 | 260.048 | 3058.3235 | 3318.3715 | 71246.1269 | -415141.232 | FALSE | 982 | 33285 | -33862.478 | 2898.6398 | 27445.7394 | 30344.3793 | 44220.1191 | 10357.6411 | TRUE | Option 3 | 10357.6411 | 698
| GSB012-72499395 | 45 | 964076.9806 | -521129.3131 | 6763.4825 | 71630.1967 | 78393.6792 | 237.6022 | 3261.7855 | 3499.3877 | 74894.2915 | -446235.0216 | FALSE | 1026 | 35662.5 | -36281.2265 | 2648.4467 | 29271.6305 | 31920.0773 | 46473.6019 | 10192.3755 | TRUE | Option 3 | 10192.3755 | 699
| WND012-72499328 | 48 | 1028348.7793 | -555871.2673 | 3733.744 | 77799.3418 | 81533.0858 | 131.167 | 3542.7065 | 3673.8735 | 77859.2122 | -478012.0551 | FALSE | 1068 | 38040 | -38699.9749 | 1462.0607 | 31792.6474 | 33254.7081 | 48278.3776 | 9578.4028 | TRUE | Option 3 | 9578.4028 | 700
| KGT003-155046250 | 26 | 557022.2554 | -301096.9365 | 1157.5675 | 48230.7409 | 49388.3084 | 40.6655 | 1694.3537 | 1735.0192 | 47653.2892 | -253443.6473 | FALSE | 696 | 20605 | -20962.4864 | 453.2807 | 18886.2098 | 19339.4905 | 30048.8179 | 9086.3315 | TRUE | Option 3 | 9086.3315 | 701
| MRO005-155391758 | 85 | 1821034.2966 | -984355.3692 | 3915.1888 | 123638.4469 | 127553.6357 | 137.5412 | 4343.4386 | 4480.9798 | 123072.6559 | -861282.7133 | FALSE | 1524 | 67362.5 | -68531.2055 | 1533.111 | 48414.3849 | 49947.4958 | 77606.1399 | 9074.9343 | TRUE | Option 3 | 9074.9343 | 702
| RCT022-160254223 | 67 | 1435403.5044 | -775903.6439 | 1523.0668 | 101969.0413 | 103492.1081 | 53.5056 | 3582.1889 | 3635.6944 | 99856.4136 | -676047.2303 | FALSE | 1334 | 53097.5 | -54018.7149 | 596.403 | 39929.0717 | 40525.4747 | 62966.6334 | 8947.9184 | TRUE | Option 3 | 8947.9184 | 703
| HSM003-163378579 | 42 | 899805.1819 | -486387.3589 | 2029.8522 | 68239.5909 | 70269.4431 | 71.309 | 2397.2678 | 2468.5769 | 67800.8662 | -418586.4927 | FALSE | 992 | 33285 | -33862.478 | 794.8502 | 26721.2821 | 27516.1323 | 42753.3108 | 8890.8328 | TRUE | Option 3 | 8890.8328 | 704
| BAS022-142437414 | 14 | 299935.0606 | -162129.1196 | 5125.3187 | 28791.3532 | 33916.6719 | 180.0533 | 1311.0563 | 1491.1095 | 32425.5624 | -129703.5572 | FALSE | 459 | 11095 | -11287.4927 | 2006.974 | 11765.5666 | 13772.5407 | 20144.1312 | 8856.6386 | TRUE | Option 3 | 8856.6386 | 705
| KGT003-155166153 | 13 | 278511.1277 | -150548.4682 | 938.8314 | 30734.9893 | 31673.8207 | 32.9813 | 1079.7251 | 1112.7064 | 30561.1143 | -119987.354 | FALSE | 431 | 10302.5 | -10481.2432 | 367.6279 | 12035.2175 | 12402.8454 | 19270.9753 | 8789.7321 | TRUE | Option 3 | 8789.7321 | 706
| HTN034-84443403 | 149 | 3192166.0023 | -1725517.0589 | 36863.5109 | 180080.6749 | 216944.1858 | 1295.0211 | 8200.2362 | 9495.2572 | 207448.9285 | -1518068.1304 | FALSE | 1891 | 118082.5 | -120131.172 | 14435.0261 | 73589.8437 | 88024.8697 | 128919.316 | 8788.144 | TRUE | Option 3 | 8788.144 | 707
| BAS022-144337084 | 48 | 1028348.7793 | -555871.2673 | 3665.4493 | 75613.6491 | 79279.0984 | 128.7678 | 3443.1778 | 3571.9456 | 75707.1528 | -480164.1145 | FALSE | 1071 | 38040 | -38699.9749 | 1435.3179 | 30899.4656 | 32334.7835 | 46944.3149 | 8244.3401 | TRUE | Option 3 | 8244.3401 | 708
| CTN004-134372186 | 89 | 1906730.0282 | -1030677.9748 | 2538.7294 | 128871.7918 | 131410.5212 | 89.186 | 4527.2868 | 4616.4728 | 126794.0484 | -903883.9264 | FALSE | 1564 | 70532.5 | -71756.2034 | 994.1165 | 50463.6599 | 51457.7764 | 79952.7448 | 8196.5414 | TRUE | Option 3 | 8196.5414 | 709
| BET004-72499720 | 21 | 449902.5909 | -243193.6794 | 3616.3856 | 37513.5705 | 41129.9561 | 127.0442 | 1317.8578 | 1444.902 | 39685.0541 | -203508.6253 | FALSE | 594 | 16642.5 | -16931.239 | 1416.1055 | 14689.5766 | 16105.6821 | 25024.274 | 8093.035 | TRUE | Option 3 | 8093.035 | 710
| BET005-117327746 | 9 | 192815.3961 | -104225.8626 | 2197.9765 | 22961.456 | 25159.4326 | 77.2153 | 806.6397 | 883.8549 | 24275.5776 | -79950.285 | FALSE | 346 | 7132.5 | -7256.2453 | 860.6844 | 8991.2547 | 9851.9391 | 15307.4934 | 8051.2482 | TRUE | Option 3 | 8051.2482 | 711
| MRO005-144335638 | 84 | 1799610.3637 | -972774.7178 | 3851.0654 | 120149.7988 | 124000.8643 | 135.2885 | 4220.8818 | 4356.1704 | 119644.6939 | -853130.0239 | FALSE | 1517 | 66570 | -67724.956 | 1508.0015 | 47048.2989 | 48556.3004 | 75444.5639 | 7719.6078 | TRUE | Option 3 | 7719.6078 | 712
| RCT023-24605614 | 21 | 449902.5909 | -243193.6794 | 20435.5526 | 19971.0834 | 40406.636 | 717.9043 | 701.5874 | 1419.4916 | 38987.1444 | -204206.5351 | FALSE | 596 | 16642.5 | -16931.239 | 8002.1606 | 7820.2836 | 15822.4442 | 24584.1918 | 7652.9528 | TRUE | Option 3 | 7652.9528 | 713
| BAS022-88324452 | 28 | 599870.1212 | -324258.2393 | 4231.0749 | 46496.6449 | 50727.7198 | 148.6383 | 2117.2925 | 2265.9309 | 48461.7889 | -275796.4503 | FALSE | 740 | 22190 | -22574.9853 | 1656.8057 | 19000.8219 | 20657.6276 | 30070.0922 | 7495.1068 | TRUE | Option 3 | 7495.1068 | 714
| BMH005-15408230 | 16 | 342782.9264 | -185290.4224 | 14416.5727 | 19567.8538 | 33984.4265 | 506.4565 | 891.0508 | 1397.5073 | 32586.9192 | -152703.5032 | FALSE | 511 | 12680 | -12899.9916 | 5645.2464 | 7996.39 | 13641.6364 | 20342.7901 | 7442.7985 | TRUE | Option 3 | 7442.7985 | 715
| MRO007-76548012 | 58 | 1242588.1083 | -671677.7813 | 4571.8835 | 84514.68 | 89086.5635 | 160.611 | 2969.0143 | 3129.6253 | 85956.9382 | -585720.8432 | FALSE | 1228 | 45965 | -46762.4697 | 1790.2597 | 33094.287 | 34884.5467 | 54202.0168 | 7439.5472 | TRUE | Option 3 | 7439.5472 | 716
| MRO005-163160605 | 18 | 385630.7922 | -208451.7252 | 1044.4917 | 34925.6648 | 35970.1565 | 36.6932 | 1226.9442 | 1263.6374 | 34706.5191 | -173745.2061 | FALSE | 547 | 14265 | -14512.4906 | 409.0024 | 13676.2036 | 14085.2061 | 21884.9504 | 7372.4599 | TRUE | Option 3 | 7372.4599 | 717
| NKA006-192419289 | 127 | 2720839.4785 | -1470742.7281 | 14092.3973 | 166267.2878 | 180359.6852 | 495.0682 | 5840.9966 | 6336.0648 | 174023.6203 | -1296719.1077 | FALSE | 1802 | 100647.5 | -102393.6835 | 5518.3057 | 65107.0008 | 70625.3066 | 109734.3786 | 7340.695 | TRUE | Option 3 | 7340.695 | 718
| CTN004-134372435 | 46 | 985500.9135 | -532709.9645 | 1622.0694 | 70925.6971 | 72547.7665 | 56.9836 | 2491.6312 | 2548.6147 | 69999.1517 | -462710.8128 | FALSE | 1040 | 36455 | -37087.4759 | 635.1705 | 27773.1085 | 28408.279 | 44139.4875 | 7052.0116 | TRUE | Option 3 | 7052.0116 | 719
| CHM011-159372576 | 30 | 642717.987 | -347419.5421 | 366.8114 | 50878.1447 | 51244.9561 | 12.8861 | 1787.3574 | 1800.2436 | 49444.7125 | -297974.8295 | FALSE | 781 | 23775 | -24187.4843 | 143.6361 | 19922.8811 | 20066.5173 | 31178.4388 | 6990.9545 | TRUE | Option 3 | 6990.9545 | 720
| BAS033-96330036 | 65 | 1392555.6386 | -752742.3411 | 3960.0257 | 96343.1005 | 100303.1261 | 139.1163 | 4387.1236 | 4526.2399 | 95776.8862 | -656965.4549 | FALSE | 1306 | 51512.5 | -52406.216 | 1550.6682 | 39370.5416 | 40921.2098 | 59381.9163 | 6975.7003 | TRUE | Option 3 | 6975.7003 | 721
| NKA001-15424578 | 77 | 1649642.8334 | -891710.158 | 29817.2115 | 83455.7217 | 113272.9332 | 1047.4834 | 2931.813 | 3979.2964 | 109293.6368 | -782416.5212 | FALSE | 1450 | 61022.5 | -62081.2097 | 11675.8338 | 32679.6197 | 44355.4535 | 68917.4797 | 6836.27 | TRUE | Option 3 | 6836.27 | 722
| ART031-78747795 | 34 | 728413.7187 | -393742.1477 | 0 | 55898.8055 | 55898.8055 | 0 | 1963.7341 | 1963.7341 | 53935.0715 | -339807.0762 | FALSE | 856 | 26945 | -27412.4822 | 0 | 21888.8732 | 21888.8732 | 34009.9324 | 6597.4501 | TRUE | Option 3 | 6597.4501 | 723
| BAN003-79424004 | 22 | 471326.5238 | -254774.3308 | 8827.7268 | 31933.802 | 40761.5288 | 310.1195 | 1454.1522 | 1764.2717 | 38997.2571 | -215777.0738 | FALSE | 620 | 17435 | -17737.4885 | 3456.7642 | 13049.7262 | 16506.4904 | 24255.0384 | 6517.5499 | TRUE | Option 3 | 6517.5499 | 724
| BET004-164487583 | 8 | 171391.4632 | -92645.2112 | 935.2117 | 19958.5148 | 20893.7265 | 32.8541 | 701.1458 | 734 | 20159.7265 | -72485.4847 | FALSE | 338 | 6340 | -6449.9958 | 366.2105 | 7815.362 | 8181.5725 | 12712.154 | 6262.1582 | TRUE | Option 3 | 6262.1582 | 725
| CTN006-155078558 | 74 | 1585371.0347 | -856968.2038 | 1637.3232 | 106487.6021 | 108124.9253 | 57.5194 | 3740.9266 | 3798.4461 | 104326.4792 | -752641.7246 | FALSE | 1421 | 58645 | -59662.4613 | 641.1436 | 41698.4513 | 42339.5948 | 65785.3304 | 6122.8691 | TRUE | Option 3 | 6122.8691 | 726
| CTN006-155018538 | 39 | 835533.3832 | -451645.4047 | 1061.2751 | 60639.307 | 61700.5821 | 37.2828 | 2130.2686 | 2167.5514 | 59533.0307 | -392112.374 | FALSE | 944 | 30907.5 | -31443.7296 | 415.5745 | 23745.1603 | 24160.7348 | 37539.8473 | 6096.1177 | TRUE | Option 3 | 6096.1177 | 727
| NHL031-158072703 | 55 | 1178316.3096 | -636935.8271 | 1428.4045 | 81173.5469 | 82601.9513 | 50.1801 | 2851.6398 | 2901.8199 | 79700.1315 | -557235.6956 | FALSE | 1189 | 43587.5 | -44343.7212 | 559.3351 | 31785.965 | 32345.3001 | 50256.6513 | 5912.93 | TRUE | Option 3 | 5912.93 | 728
| HSM005-160415504 | 41 | 878381.249 | -474806.7075 | 1109.0088 | 62800.0237 | 63909.0324 | 38.9597 | 2206.175 | 2245.1346 | 61663.8978 | -413142.8097 | FALSE | 980 | 32492.5 | -33056.2285 | 434.266 | 24591.2545 | 25025.5206 | 38883.5119 | 5827.2833 | TRUE | Option 3 | 5827.2833 | 729
| NHL015-158071333 | 110 | 2356632.6192 | -1273871.6542 | 1984.9257 | 153326.2109 | 155311.1366 | 69.7308 | 5386.3745 | 5456.1053 | 149855.0313 | -1124016.6229 | FALSE | 1700 | 87175 | -88687.4424 | 777.2579 | 60039.5296 | 60816.7874 | 94494.3492 | 5806.9067 | TRUE | Option 3 | 5806.9067 | 730
| SHP021-138133628 | 38 | 814109.4503 | -440064.7533 | 5513.4508 | 53272.2386 | 58785.6894 | 193.6884 | 1871.4623 | 2065.1507 | 56720.5387 | -383344.2146 | FALSE | 933 | 30115 | -30637.4801 | 2158.9589 | 20860.3612 | 23019.3202 | 35766.3693 | 5128.8891 | TRUE | Option 3 | 5128.8891 | 731
| KGT003-155166380 | 15 | 321358.9935 | -173709.771 | 925.304 | 27183.6346 | 28108.9387 | 32.5061 | 954.9655 | 987.4715 | 27121.4671 | -146588.3039 | FALSE | 490 | 11887.5 | -12093.7422 | 362.3309 | 10644.5769 | 11006.9077 | 17102.031 | 5008.2888 | TRUE | Option 3 | 5008.2888 | 732
| BET006-122234049 | 51 | 1092620.578 | -590613.2215 | 3362.6745 | 72409.7125 | 75772.387 | 118.1313 | 2543.7649 | 2661.8962 | 73110.4908 | -517502.7307 | FALSE | 1122 | 40417.5 | -41118.7233 | 1316.7572 | 28354.2197 | 29670.9769 | 46101.41 | 4982.6867 | TRUE | Option 3 | 4982.6867 | 733
| CTN006-138230928 | 78 | 1671066.7663 | -903290.8094 | 1679.2948 | 109646.837 | 111326.1317 | 58.9939 | 3851.9111 | 3910.905 | 107415.2268 | -795875.5826 | FALSE | 1466 | 61815 | -62887.4592 | 657.5788 | 42935.5455 | 43593.1243 | 67733.0074 | 4845.5482 | TRUE | Option 3 | 4845.5482 | 734
| BAS033-78748089 | 26 | 557022.2554 | -301096.9365 | 1925.9115 | 41446.7478 | 43372.6593 | 67.6576 | 1887.3381 | 1954.9957 | 41417.6636 | -259679.2728 | FALSE | 712 | 20605 | -20962.4864 | 754.1491 | 16937.1849 | 17691.334 | 25681.3253 | 4718.8389 | TRUE | Option 3 | 4718.8389 | 735
| CTN006-155018674 | 21 | 449902.5909 | -243193.6794 | 1185.5654 | 33662.7927 | 34848.3581 | 41.6491 | 1182.5793 | 1224.2284 | 33624.1297 | -209569.5498 | FALSE | 612 | 16642.5 | -16931.239 | 464.2441 | 13181.6878 | 13645.9319 | 21202.4263 | 4271.1872 | TRUE | Option 3 | 4271.1872 | 736
| CTN001-155143379 | 72 | 1542523.1689 | -833806.9009 | 3099.7952 | 99191.8544 | 102291.6496 | 108.8963 | 3484.6258 | 3593.5221 | 98698.1275 | -735108.7735 | FALSE | 1400 | 57060 | -58049.9623 | 1213.8189 | 38841.5799 | 40055.3988 | 62236.2508 | 4186.2885 | TRUE | Option 3 | 4186.2885 | 737
| HSM003-160875785 | 112 | 2399480.485 | -1297032.957 | 3028.6149 | 152047.4206 | 155076.0355 | 106.3957 | 5341.4504 | 5447.8461 | 149628.1894 | -1147404.7677 | FALSE | 1716 | 88760 | -90299.9414 | 1185.9461 | 59538.7804 | 60724.7265 | 94351.309 | 4051.3676 | TRUE | Option 3 | 4051.3676 | 738
| NKA006-24605964 | 79 | 1692490.6992 | -914871.4608 | 19662.0511 | 91533.9791 | 111196.0303 | 690.731 | 3215.6034 | 3906.3345 | 107289.6958 | -807581.765 | FALSE | 1475 | 62607.5 | -63693.7087 | 7699.2726 | 35842.9065 | 43542.1792 | 67653.8511 | 3960.1424 | TRUE | Option 3 | 3960.1424 | 739
| CHM011-159372020 | 97 | 2078121.4915 | -1123323.186 | 1338.5413 | 133401.2384 | 134739.7797 | 47.0232 | 4686.407 | 4733.4302 | 130006.3495 | -993316.8365 | FALSE | 1617 | 76872.5 | -78206.1992 | 524.1465 | 52237.3021 | 52761.4486 | 81978.3312 | 3772.1319 | TRUE | Option 3 | 3772.1319 | 740
| BAS022-139345255 | 60 | 1285435.9741 | -694839.0841 | 5674.4577 | 81985.3777 | 87659.8353 | 199.3446 | 3733.3237 | 3932.6684 | 83727.167 | -611111.9171 | FALSE | 1253 | 47550 | -48374.9686 | 2222.0061 | 33503.2681 | 35725.2741 | 51934.5612 | 3559.5926 | TRUE | Option 3 | 3559.5926 | 741
| CMN004-76446391 | 48 | 1028348.7793 | -555871.2673 | 1343.8967 | 67948.3217 | 69292.2184 | 47.2113 | 2387.0355 | 2434.2468 | 66857.9716 | -489013.2957 | FALSE | 1084 | 38040 | -38699.9749 | 526.2435 | 26607.2268 | 27133.4703 | 42158.748 | 3458.7732 | TRUE | Option 3 | 3458.7732 | 742
| MRO005-163160444 | 19 | 407054.7251 | -220032.3766 | 629.9889 | 29641.0891 | 30271.078 | 22.1316 | 1041.2962 | 1063.4279 | 29207.6502 | -190824.7265 | FALSE | 574 | 15057.5 | -15318.7401 | 246.6913 | 11606.8677 | 11853.559 | 18417.519 | 3098.779 | TRUE | Option 3 | 3098.779 | 743
| BET004-164487758 | 5 | 107119.6645 | -57903.257 | 1242.1623 | 10354.0961 | 11596.2585 | 43.6374 | 363.7411 | 407.3784 | 11188.88 | -46714.377 | FALSE | 299 | 3962.5 | -4031.2474 | 486.4063 | 4054.4605 | 4540.8668 | 7055.3916 | 3024.1443 | TRUE | Option 3 | 3024.1443 | 744
| NHL016-157284831 | 77 | 1649642.8334 | -891710.158 | 1300.3329 | 105687.2466 | 106987.5795 | 45.6809 | 3712.81 | 3758.4909 | 103229.0886 | -788481.0694 | FALSE | 1458 | 61022.5 | -62081.2097 | 509.1848 | 41385.0478 | 41894.2326 | 65093.3469 | 3012.1372 | TRUE | Option 3 | 3012.1372 | 745
| MNA034-157168656 | 54 | 1156892.3767 | -625355.1757 | 3591.1899 | 72913.1025 | 76504.2925 | 126.1591 | 2561.4491 | 2687.6081 | 73816.6843 | -551538.4914 | FALSE | 1181 | 42795 | -43537.4717 | 1406.2394 | 28551.3374 | 29957.5767 | 46546.7157 | 3009.244 | TRUE | Option 3 | 3009.244 | 746
| BAS022-88324187 | 3 | 64271.7987 | -34741.9542 | 4013.7694 | 4939.9825 | 8953.7519 | 141.0044 | 224.9493 | 365.9537 | 8587.7982 | -26154.156 | FALSE | 269 | 2377.5 | -2418.7484 | 1571.7132 | 2018.7205 | 3590.4336 | 5363.3183 | 2944.5699 | TRUE | Option 3 | 2944.5699 | 747
| STL006-24599342 | 97 | 2078121.4915 | -1123323.186 | 15948.8685 | 117132.0656 | 133080.9341 | 560.2863 | 4114.8684 | 4675.1547 | 128405.7794 | -994917.4066 | FALSE | 1624 | 76872.5 | -78206.1992 | 6245.2633 | 45866.6139 | 52111.8772 | 80969.0569 | 2762.8576 | TRUE | Option 3 | 2762.8576 | 748
| WMN021-164365974 | 31 | 664141.92 | -359000.1935 | 10209.2791 | 35368.298 | 45577.5771 | 358.6536 | 1242.494 | 1601.1476 | 43976.4295 | -315023.764 | FALSE | 810 | 24567.5 | -24993.7338 | 3997.753 | 13849.5301 | 17847.2831 | 27730.2941 | 2736.5603 | TRUE | Option 3 | 2736.5603 | 749
| WND013-76546454 | 11 | 235663.2619 | -127387.1654 | 2041.8575 | 16767.9368 | 18809.7942 | 71.7308 | 763.5525 | 835.2832 | 17974.511 | -109412.6544 | FALSE | 401 | 8717.5 | -8868.7442 | 799.5512 | 6852.2058 | 7651.757 | 11158.0372 | 2289.293 | TRUE | Option 3 | 2289.293 | 750
| STL006-155132358 | 150 | 3213589.9352 | -1737097.7103 | 6113.2605 | 196391.862 | 202505.1224 | 214.7598 | 6899.2778 | 7114.0376 | 195391.0848 | -1541706.6255 | FALSE | 1898 | 118875 | -120937.4215 | 2393.8326 | 76903.1918 | 79297.0244 | 123208.098 | 2270.6765 | TRUE | Option 3 | 2270.6765 | 751
| SA006-24612920 | 50 | 1071196.6451 | -579032.5701 | 47296.3294 | 23108.901 | 70405.2304 | 1661.5277 | 1052.2975 | 2713.8252 | 67691.4052 | -511341.1649 | FALSE | 1112 | 39625 | -40312.4738 | 18520.3127 | 9443.4365 | 27963.7491 | 42441.4813 | 2129.0074 | TRUE | Option 3 | 2129.0074 | 752
| MRO005-144336040 | 28 | 599870.1212 | -324258.2393 | 1137.4852 | 39441.3944 | 40578.8796 | 39.96 | 1385.5825 | 1425.5426 | 39153.337 | -285104.9023 | FALSE | 752 | 22190 | -22574.9853 | 445.4168 | 15444.4746 | 15889.8914 | 24688.9882 | 2114.0028 | TRUE | Option 3 | 2114.0028 | 753
| CHA006-155621164 | 17 | 364206.8593 | -196871.0738 | 1174.3183 | 24648.0901 | 25822.4084 | 41.254 | 865.8914 | 907.1454 | 24915.263 | -171955.8109 | FALSE | 535 | 13472.5 | -13706.2411 | 459.84 | 9651.7074 | 10111.5474 | 15710.8609 | 2004.6198 | TRUE | Option 3 | 2004.6198 | 754
| BGO023-154971917 | 15 | 321358.9935 | -173709.771 | 1290.9785 | 21715.3625 | 23006.341 | 45.3523 | 762.8642 | 808.2165 | 22198.1246 | -151511.6465 | FALSE | 508 | 11887.5 | -12093.7422 | 505.5218 | 8503.309 | 9008.8308 | 13997.5102 | 1903.7681 | TRUE | Option 3 | 1903.7681 | 755
| CTN003-155052230 | 40 | 856957.3161 | -463226.0561 | 367.4106 | 55717.7526 | 56085.1632 | 12.9072 | 1957.3736 | 1970.2808 | 54114.8824 | -409111.1737 | FALSE | 976 | 31700 | -32249.9791 | 143.8708 | 21817.9764 | 21961.8472 | 34123.316 | 1873.3369 | TRUE | Option 3 | 1873.3369 | 756
| CTN001-155668176 | 32 | 685565.8529 | -370580.8449 | 2169.2122 | 43187.1942 | 45356.4064 | 76.2048 | 1517.1731 | 1593.3779 | 43763.0286 | -326817.8163 | FALSE | 831 | 25360 | -25799.9833 | 849.4208 | 16911.2561 | 17760.677 | 27595.7294 | 1795.7462 | TRUE | Option 3 | 1795.7462 | 757
| WND014-79365293 | 36 | 771261.5845 | -416903.4505 | 2872.0963 | 48715.3863 | 51587.4826 | 100.8972 | 2218.3262 | 2319.2234 | 49268.2592 | -367635.1912 | FALSE | 908 | 28530 | -29024.9812 | 1124.6564 | 19907.509 | 21032.1655 | 30555.3171 | 1530.336 | TRUE | Option 3 | 1530.336 | 758
| CTN004-155092023 | 17 | 364206.8593 | -196871.0738 | 567.063 | 24436.7623 | 25003.8253 | 19.921 | 858.4674 | 878.3884 | 24125.4369 | -172745.6369 | FALSE | 536 | 13472.5 | -13706.2411 | 222.0507 | 9568.9557 | 9791.0064 | 15212.8189 | 1506.5778 | TRUE | Option 3 | 1506.5778 | 759
| GSB012-72499030 | 20 | 428478.658 | -231613.028 | 3062.8472 | 26581.2851 | 29644.1323 | 107.5983 | 1210.4176 | 1318.0159 | 28326.1164 | -203286.9117 | FALSE | 593 | 15850 | -16124.9895 | 1199.3507 | 10862.4238 | 12061.7746 | 17582.3577 | 1457.3682 | TRUE | Option 3 | 1457.3682 | 760
| WND013-76546307 | 21 | 449902.5909 | -243193.6794 | 2385.2401 | 28615.9066 | 31001.1468 | 83.7939 | 1303.067 | 1386.8609 | 29614.2858 | -213579.3936 | FALSE | 618 | 16642.5 | -16931.239 | 934.0131 | 11693.8705 | 12627.8837 | 18373.2631 | 1442.0241 | TRUE | Option 3 | 1442.0241 | 761
| BAN003-79424313 | 43 | 921229.1148 | -497968.0103 | 5875.5473 | 54423.2856 | 60298.8329 | 206.4089 | 2478.2437 | 2684.6526 | 57614.1803 | -440353.83 | FALSE | 1019 | 34077.5 | -34668.7275 | 2300.7488 | 22240.0381 | 24540.7869 | 35758.0459 | 1089.3184 | TRUE | Option 3 | 1089.3184 | 762
| SHP021-164488411 | 11 | 235663.2619 | -127387.1654 | 1620.4963 | 14732.0501 | 16352.5464 | 56.9283 | 517.5393 | 574.4676 | 15778.0788 | -111609.0866 | FALSE | 407 | 8717.5 | -8868.7442 | 634.5545 | 5768.7812 | 6403.3356 | 9949.2107 | 1080.4665 | TRUE | Option 3 | 1080.4665 | 763
| CTN002-158379241 | 50 | 1071196.6451 | -579032.5701 | 5253.5214 | 62777.3139 | 68030.8353 | 184.5571 | 2205.3772 | 2389.9342 | 65640.9011 | -513391.669 | FALSE | 1115 | 39625 | -40312.4738 | 2057.1757 | 24582.3618 | 26639.5375 | 41391.2978 | 1078.824 | TRUE | Option 3 | 1078.824 | 764
| HTN034-162617230 | 28 | 599870.1212 | -324258.2393 | 79.2998 | 39802.5091 | 39881.809 | 2.7858 | 1812.4653 | 1815.2511 | 38066.5578 | -286191.6814 | FALSE | 754 | 22190 | -22574.9853 | 31.0523 | 16265.2679 | 16296.3202 | 23585.4888 | 1010.5034 | TRUE | Option 3 | 1010.5034 | 765
| CMN002-78928402 | 1 | 21423.9329 | -11580.6514 | 1679.8111 | 1236.6524 | 2916.4635 | 59.012 | 43.4438 | 102.4558 | 2814.0076 | -8766.6438 | FALSE | 221 | 792.5 | -806.2495 | 657.781 | 484.2488 | 1142.0298 | 1774.4337 | 968.1842 | TRUE | Option 3 | 968.1842 | 766
| NHL015-158050824 | 121 | 2592295.8811 | -1401258.8196 | 1572.1872 | 160329.9528 | 161902.14 | 55.2312 | 5632.4171 | 5687.6483 | 156214.4917 | -1245044.3279 | FALSE | 1777 | 95892.5 | -97556.1867 | 615.6376 | 62782.0572 | 63397.6948 | 98504.4452 | 948.2585 | TRUE | Option 3 | 948.2585 | 767
| RCT023-24605628 | 152 | 3256437.801 | -1760259.0131 | 27879.601 | 175009.9981 | 202889.5991 | 979.4149 | 6148.1295 | 7127.5443 | 195762.0548 | -1564496.9583 | FALSE | 1905 | 120460 | -122549.9205 | 10917.1036 | 68530.4743 | 79447.5779 | 123442.0212 | 892.1008 | TRUE | Option 3 | 892.1008 | 768
| BGO023-95132601 | 51 | 1092620.578 | -590613.2215 | 4366.0208 | 64212.2548 | 68578.2757 | 153.379 | 2255.7869 | 2409.1659 | 66169.1098 | -524444.1117 | FALSE | 1138 | 40417.5 | -41118.7233 | 1709.6479 | 25144.2565 | 26853.9044 | 41724.3713 | 605.6479 | TRUE | Option 3 | 605.6479 | 769
| NHL015-158004482 | 29 | 621294.0541 | -335838.8907 | 521.1257 | 38203.0574 | 38724.1831 | 18.3072 | 1342.0796 | 1360.3868 | 37363.7963 | -298475.0944 | FALSE | 782 | 22982.5 | -23381.2348 | 204.0626 | 14959.5661 | 15163.6287 | 23560.5544 | 179.3195 | TRUE | Option 3 | 179.3195 | 770
| BAS011-164287379 | 4 | 85695.7316 | -46322.6056 | 5091.2332 | 420.0578 | 5511.291 | 178.8558 | 19.1279 | 197.9838 | 5313.3072 | -41009.2984 | FALSE | 287 | 3170 | -3224.9979 | 1993.6268 | 171.6563 | 2165.2832 | 3346.0079 | 121.01 | TRUE | Option 3 | 121.01 | 771
| MBN031-24605740 | 114 | 2442328.3508 | -1320194.2598 | 16657.4313 | 134547.0035 | 151204.4348 | 585.1782 | 4726.6579 | 5311.8362 | 145892.5986 | -1174301.6612 | FALSE | 1732 | 90345 | -91912.4403 | 6522.7226 | 52685.9612 | 59208.6838 | 91995.751 | 83.3107 | TRUE | Option 3 | 83.3107 | 772
| BAS022-155392787 | 13 | 278511.1277 | -150548.4682 | 2528.0683 | 15212.3456 | 17740.414 | 88.8114 | 692.7163 | 781.5278 | 16958.8862 | -133589.582 | FALSE | 461 | 10302.5 | -10481.2432 | 989.9419 | 6216.5146 | 7206.4564 | 10533.9576 | 52.7144 | TRUE | Option 3 | 52.7144 | 773
| AC024-200218081 | 35 | 749837.6516 | -405322.7991 | 349.9253 | 2106.9876 | 2456.9129 | 12.2929 | 95.9448 | 108.2377 | 2348.6752 | -402974.1239 | FALSE | 963 | 27737.5 | -28218.7317 | 137.0239 | 861.019 | 998.0429 | 1458.87 | -26759.8617 | FALSE | Option 1 | 0 | 774
| AC024-200218767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| AC024-200218825 | 3 | 64271.7987 | -34741.9542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -34741.9542 | FALSE | 281 | 2377.5 | -2418.7484 | 0 | 0 | 0 | 0 | -2418.7484 | FALSE | Option 1 | 0 | 774
| AC025-200218004 | 26 | 557022.2554 | -301096.9365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -301096.9365 | FALSE | 792 | 20605 | -20962.4864 | 0 | 0 | 0 | 0 | -20962.4864 | FALSE | Option 1 | 0 | 774
| AC032-200217768 | 18 | 385630.7922 | -208451.7252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -208451.7252 | FALSE | 607 | 14265 | -14512.4906 | 0 | 0 | 0 | 0 | -14512.4906 | FALSE | Option 1 | 0 | 774
| AL002-15404158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| AL002-200779408 | 159 | 3406405.3314 | -1841323.5729 | 64842.1622 | 76006.3875 | 140848.5496 | 2277.9156 | 3461.0617 | 5738.9773 | 135109.5723 | -1706214.0006 | FALSE | 1939 | 126007.5 | -128193.6668 | 25390.9158 | 31059.9578 | 56450.8737 | 84397.676 | -43795.9908 | FALSE | Option 1 | 0 | 774
| AL007-200403464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| AL007-200403526 | 117 | 2506600.1495 | -1354936.214 | 194.0068 | 195.4419 | 389.4487 | 6.8155 | 8.8997 | 15.7152 | 373.7335 | -1354562.4806 | FALSE | 1823 | 92722.5 | -94331.1888 | 75.9692 | 79.8672 | 155.8365 | 233.6123 | -94097.5765 | FALSE | Option 1 | 0 | 774
| AL011-200635544 | 73 | 1563947.1018 | -845387.5523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -845387.5523 | FALSE | 1511 | 57852.5 | -58856.2118 | 0 | 0 | 0 | 0 | -58856.2118 | FALSE | Option 1 | 0 | 774
| AL012-200635470 | 146 | 3127894.2036 | -1690775.1047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1690775.1047 | FALSE | 1933 | 115705 | -117712.4236 | 0 | 0 | 0 | 0 | -117712.4236 | FALSE | Option 1 | 0 | 774
| ART023-15411718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| ART023-154832740 | 7 | 149967.5303 | -81064.5598 | 271.4634 | 2189.2158 | 2460.6791 | 9.5366 | 76.9075 | 86.4441 | 2374.2351 | -78690.3248 | FALSE | 342 | 5547.5 | -5643.7463 | 106.2997 | 857.2538 | 963.5536 | 1497.1255 | -4146.6208 | FALSE | Option 1 | 0 | 774
| ART023-154832902 | 29 | 621294.0541 | -335838.8907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -335838.8907 | FALSE | 851 | 22982.5 | -23381.2348 | 0 | 0 | 0 | 0 | -23381.2348 | FALSE | Option 1 | 0 | 774
| ART031-155164001 | 5 | 107119.6645 | -57903.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -57903.257 | FALSE | 312 | 3962.5 | -4031.2474 | 0 | 0 | 0 | 0 | -4031.2474 | FALSE | Option 1 | 0 | 774
| ART031-155164103 | 17 | 364206.8593 | -196871.0738 | 5.2756 | 255.9841 | 261.2596 | 0.18533 | 8.9928 | 9.1781 | 252.0816 | -196618.9923 | FALSE | 581 | 13472.5 | -13706.2411 | 2.0658 | 100.2383 | 102.3041 | 158.9555 | -13547.2856 | FALSE | Option 1 | 0 | 774
| ART031-76359985 | 79 | 1692490.6992 | -914871.4608 | 1496.0722 | 49367.4287 | 50863.5009 | 52.5573 | 1734.2857 | 1786.843 | 49076.6579 | -865794.8028 | FALSE | 1529 | 62607.5 | -63693.7087 | 585.8325 | 19331.3145 | 19917.1469 | 30946.354 | -32747.3547 | FALSE | Option 1 | 0 | 774
| ART031-78747678 | 60 | 1285435.9741 | -694839.0841 | 2124.3585 | 72760.9338 | 74885.2922 | 74.6291 | 2556.1033 | 2630.7324 | 72254.5599 | -622584.5243 | FALSE | 1271 | 47550 | -48374.9686 | 831.857 | 28491.7511 | 29323.6081 | 45561.6842 | -2813.2844 | FALSE | Option 1 | 0 | 774
| ART033-154972245 | 71 | 1521099.236 | -822226.2495 | 709.8471 | 32319.7486 | 33029.5957 | 24.937 | 1135.398 | 1160.335 | 31869.2606 | -790356.9889 | FALSE | 1460 | 56267.5 | -57243.7128 | 277.9622 | 12655.7781 | 12933.7402 | 20095.8554 | -37147.8574 | FALSE | Option 1 | 0 | 774
| ART033-154972416 | 51 | 1092620.578 | -590613.2215 | 359.2896 | 26440.1825 | 26799.4721 | 12.6219 | 928.8479 | 941.4698 | 25858.0023 | -564755.2192 | FALSE | 1194 | 40417.5 | -41118.7233 | 140.6907 | 10353.4556 | 10494.1463 | 16305.3257 | -24813.3976 | FALSE | Option 1 | 0 | 774
| ART033-154972520 | 31 | 664141.92 | -359000.1935 | 148.0848 | 8831.4433 | 8979.5281 | 5.2022 | 310.25 | 315.4523 | 8664.0759 | -350336.1176 | FALSE | 872 | 24567.5 | -24993.7338 | 57.9871 | 3458.2196 | 3516.2067 | 5463.3215 | -19530.4123 | FALSE | Option 1 | 0 | 774
| ART033-154972637 | 61 | 1306859.907 | -706419.7355 | 2.5112 | 176.8337 | 179.3449 | 0.088218 | 6.2122 | 6.3004 | 173.0444 | -706246.6911 | FALSE | 1371 | 48342.5 | -49181.2181 | 0.98332 | 69.2446 | 70.2279 | 109.1169 | -49072.1011 | FALSE | Option 1 | 0 | 774
| ART033-155019358 | 92 | 1971001.8269 | -1065419.929 | 158.3444 | 7643.8621 | 7802.2065 | 5.5627 | 268.5301 | 274.0928 | 7528.1137 | -1057891.8152 | FALSE | 1661 | 72910 | -74174.9519 | 62.0046 | 2993.1861 | 3055.1907 | 4747.0158 | -69427.936 | FALSE | Option 1 | 0 | 774
| ART033-155019455 | 10 | 214239.329 | -115806.514 | 0 | 0.64466 | 0.64466 | 0 | 0.022647 | 0.022647 | 0.62201 | -115805.892 | FALSE | 422 | 7925 | -8062.4948 | 0 | 0.25244 | 0.25244 | 0.39222 | -8062.1025 | FALSE | Option 1 | 0 | 774
| ART033-155019644 | 82 | 1756762.4979 | -949613.415 | 1486.6602 | 46134.4191 | 47621.0792 | 52.2266 | 1620.7096 | 1672.9362 | 45948.143 | -903665.2719 | FALSE | 1563 | 64985 | -66112.4571 | 582.1469 | 18065.3314 | 18647.4783 | 28973.6009 | -37138.8562 | FALSE | Option 1 | 0 | 774
| ART033-155019780 | 11 | 235663.2619 | -127387.1654 | 47.148 | 5986.8227 | 6033.9707 | 1.6563 | 210.318 | 211.9744 | 5821.9964 | -121565.1691 | FALSE | 433 | 8717.5 | -8868.7442 | 18.4622 | 2344.3221 | 2362.7843 | 3671.1864 | -5197.5578 | FALSE | Option 1 | 0 | 774
| ART033-155019881 | 22 | 471326.5238 | -254774.3308 | 185.6553 | 10477.7834 | 10663.4387 | 6.5221 | 368.0862 | 374.6083 | 10288.8304 | -244485.5005 | FALSE | 688 | 17435 | -17737.4885 | 72.699 | 4102.894 | 4175.5929 | 6487.8458 | -11249.6427 | FALSE | Option 1 | 0 | 774
| ART033-155025562 | 85 | 1821034.2966 | -984355.3692 | 493.9552 | 17951.5914 | 18445.5466 | 17.3527 | 630.6423 | 647.995 | 17797.5516 | -966557.8176 | FALSE | 1602 | 67362.5 | -68531.2055 | 193.4232 | 7029.4902 | 7222.9134 | 11222.6332 | -57308.5723 | FALSE | Option 1 | 0 | 774
| ART033-155025764 | 18 | 385630.7922 | -208451.7252 | 1.0033 | 104.2185 | 105.2218 | 0.035245 | 3.6612 | 3.6965 | 101.5253 | -208350.1999 | FALSE | 603 | 14265 | -14512.4906 | 0.39286 | 40.8099 | 41.2028 | 64.019 | -14448.4716 | FALSE | Option 1 | 0 | 774
| ART033-155025850 | 55 | 1178316.3096 | -636935.8271 | 8.8515 | 295.7461 | 304.5976 | 0.31096 | 10.3896 | 10.7006 | 293.897 | -636641.9301 | FALSE | 1283 | 43587.5 | -44343.7212 | 3.4661 | 115.8083 | 119.2744 | 185.3232 | -44158.3981 | FALSE | Option 1 | 0 | 774
| ART033-155026277 | 122 | 2613719.814 | -1412839.471 | 63.5981 | 3893.9751 | 3957.5731 | 2.2342 | 136.796 | 139.0302 | 3818.5429 | -1409020.9281 | FALSE | 1847 | 96685 | -98362.4362 | 24.9037 | 1524.8041 | 1549.7078 | 2407.8653 | -95954.5709 | FALSE | Option 1 | 0 | 774
| ART033-155052479 | 50 | 1071196.6451 | -579032.5701 | 42.1776 | 2434.4073 | 2476.5849 | 1.4817 | 85.5211 | 87.0028 | 2389.5821 | -576642.988 | FALSE | 1213 | 39625 | -40312.4738 | 16.5159 | 953.2661 | 969.782 | 1506.803 | -38805.6709 | FALSE | Option 1 | 0 | 774
| ART033-155052606 | 18 | 385630.7922 | -208451.7252 | 0.38837 | 32.2806 | 32.669 | 0.013643 | 1.134 | 1.1477 | 31.5213 | -208420.2039 | FALSE | 604 | 14265 | -14512.4906 | 0.15208 | 12.6405 | 12.7925 | 19.8765 | -14492.6141 | FALSE | Option 1 | 0 | 774
| ART033-155052720 | 13 | 278511.1277 | -150548.4682 | 0.35235 | 17.6254 | 17.9777 | 0.012378 | 0.61918 | 0.63156 | 17.3461 | -150531.1221 | FALSE | 502 | 10302.5 | -10481.2432 | 0.13797 | 6.9017 | 7.0397 | 10.938 | -10470.3052 | FALSE | Option 1 | 0 | 774
| ART033-155062161 | 13 | 278511.1277 | -150548.4682 | 0.31417 | 15.7155 | 16.0297 | 0.011037 | 0.55209 | 0.56312 | 15.4665 | -150533.0017 | FALSE | 503 | 10302.5 | -10481.2432 | 0.12302 | 6.1539 | 6.2769 | 9.7528 | -10471.4904 | FALSE | Option 1 | 0 | 774
| ART033-155062324 | 15 | 321358.9935 | -173709.771 | 0.034026 | 3.9279 | 3.9619 | 0.0011953 | 0.13799 | 0.13918 | 3.8227 | -173705.9483 | FALSE | 542 | 11887.5 | -12093.7422 | 0.013324 | 1.5381 | 1.5514 | 2.4105 | -12091.3317 | FALSE | Option 1 | 0 | 774
| ART033-155062418 | 77 | 1649642.8334 | -891710.158 | 554.6234 | 25947.7226 | 26502.346 | 19.484 | 911.5477 | 931.0317 | 25571.3143 | -866138.8437 | FALSE | 1530 | 61022.5 | -62081.2097 | 217.1796 | 10160.618 | 10377.7976 | 16124.5484 | -45956.6613 | FALSE | Option 1 | 0 | 774
| ART033-155079125 | 98 | 2099545.4244 | -1134903.8374 | 197.574 | 19436.591 | 19634.165 | 6.9408 | 682.8106 | 689.7514 | 18944.4136 | -1115959.4238 | FALSE | 1693 | 77665 | -79012.4487 | 77.3661 | 7610.9869 | 7688.353 | 11945.812 | -67066.6367 | FALSE | Option 1 | 0 | 774
| ART033-155091128 | 93 | 1992425.7599 | -1077000.5804 | 441.483 | 28725.5502 | 29167.0332 | 15.5094 | 1009.1332 | 1024.6426 | 28142.3907 | -1048858.1897 | FALSE | 1656 | 73702.5 | -74981.2013 | 172.8761 | 11248.3607 | 11421.2368 | 17745.7965 | -57235.4048 | FALSE | Option 1 | 0 | 774
| ART033-155155386 | 11 | 235663.2619 | -127387.1654 | 46.6517 | 2369.5379 | 2416.1896 | 1.6389 | 83.2422 | 84.8811 | 2331.3085 | -125055.857 | FALSE | 443 | 8717.5 | -8868.7442 | 18.2679 | 927.8644 | 946.1323 | 1470.0573 | -7398.687 | FALSE | Option 1 | 0 | 774
| ART033-162913151 | 377 | 8076822.7039 | -4365905.5786 | 21216.9651 | 477584.3523 | 498801.3175 | 745.3554 | 16777.6153 | 17522.9707 | 481278.3467 | -3884627.2318 | FALSE | 2186 | 298772.5 | -303956.0527 | 8308.1464 | 187012.6423 | 195320.7887 | 303480.5287 | -475.524 | FALSE | Option 1 | 0 | 774
| ART033-183308941 | 17 | 364206.8593 | -196871.0738 | 0.094995 | 6.2141 | 6.3091 | 0.0033372 | 0.2183 | 0.22164 | 6.0875 | -196864.9863 | FALSE | 585 | 13472.5 | -13706.2411 | 0.037198 | 2.4333 | 2.4705 | 3.8386 | -13702.4025 | FALSE | Option 1 | 0 | 774
| ART033-80719107 | 41 | 878381.249 | -474806.7075 | 971.1291 | 26263.0352 | 27234.1643 | 34.1159 | 922.6247 | 956.7406 | 26277.4237 | -448529.2838 | FALSE | 1030 | 32492.5 | -33056.2285 | 380.2751 | 10284.0882 | 10664.3633 | 16569.801 | -16486.4275 | FALSE | Option 1 | 0 | 774
| ART034-15411868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| BAN001-15414753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| BAN001-15414766 | 143 | 3063622.4049 | -1656033.1505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1656033.1505 | FALSE | 1927 | 113327.5 | -115293.6752 | 0 | 0 | 0 | 0 | -115293.6752 | FALSE | Option 1 | 0 | 774
| BAN003-141839634 | 59 | 1264012.0412 | -683258.4327 | 871.537 | 26781.2493 | 27652.7864 | 30.6172 | 1219.5232 | 1250.1405 | 26402.6459 | -656855.7868 | FALSE | 1305 | 46757.5 | -47568.7191 | 341.2768 | 10944.1391 | 11285.4158 | 16367.3705 | -31201.3486 | FALSE | Option 1 | 0 | 774
| BAN003-141839920 | 28 | 599870.1212 | -324258.2393 | 509.3262 | 16208.8017 | 16718.1279 | 17.8927 | 738.0914 | 755.9841 | 15962.1438 | -308296.0955 | FALSE | 798 | 22190 | -22574.9853 | 199.4421 | 6623.7156 | 6823.1578 | 9894.9701 | -12680.0152 | FALSE | Option 1 | 0 | 774
| BAN003-163842570 | 14 | 299935.0606 | -162129.1196 | 1421.6457 | 11295.5436 | 12717.1893 | 49.9426 | 514.3591 | 564.3017 | 12152.8876 | -149976.232 | FALSE | 496 | 11095 | -11287.4927 | 556.6885 | 4615.9161 | 5172.6046 | 7544.5847 | -3742.908 | FALSE | Option 1 | 0 | 774
| BAN003-164488210 | 26 | 557022.2554 | -301096.9365 | 1472.2132 | 26556.427 | 28028.6402 | 51.7191 | 1209.2856 | 1261.0047 | 26767.6354 | -274329.301 | FALSE | 738 | 20605 | -20962.4864 | 576.4897 | 10852.2656 | 11428.7553 | 16599.8848 | -4362.6016 | FALSE | Option 1 | 0 | 774
| BAN003-24598678 | 71 | 1521099.236 | -822226.2495 | 891.1559 | 12549.7834 | 13440.9394 | 31.3065 | 571.4727 | 602.7791 | 12838.1602 | -809388.0893 | FALSE | 1476 | 56267.5 | -57243.7128 | 348.9591 | 5128.4604 | 5477.4195 | 7963.5199 | -49280.193 | FALSE | Option 1 | 0 | 774
| BAN003-24610965 | 25 | 535598.3225 | -289516.2851 | 2377.4531 | 23917.2198 | 26294.6729 | 83.5203 | 1089.1055 | 1172.6258 | 25122.0471 | -264394.238 | FALSE | 721 | 19812.5 | -20156.2369 | 930.9639 | 9773.7554 | 10704.7193 | 15589.9536 | -4566.2833 | FALSE | Option 1 | 0 | 774
| BAN003-79423703 | 27 | 578446.1883 | -312677.5879 | 1462.294 | 21453.7753 | 22916.0693 | 51.3706 | 976.9289 | 1028.2996 | 21887.7697 | -290789.8181 | FALSE | 773 | 21397.5 | -21768.7359 | 572.6056 | 8767.0705 | 9339.6761 | 13576.3932 | -8192.3426 | FALSE | Option 1 | 0 | 774
| BAN003-79424820 | 55 | 1178316.3096 | -636935.8271 | 3995.2796 | 70418.9218 | 74414.2014 | 140.3548 | 3206.6283 | 3346.9831 | 71067.2183 | -565868.6088 | FALSE | 1198 | 43587.5 | -44343.7212 | 1564.4729 | 28776.6439 | 30341.1168 | 44073.0846 | -270.6366 | FALSE | Option 1 | 0 | 774
| BAN004-15414853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| BAN004-15414866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| BAN005-15414666 | 148 | 3170742.0694 | -1713936.4075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1713936.4075 | FALSE | 1940 | 117290 | -119324.9226 | 0 | 0 | 0 | 0 | -119324.9226 | FALSE | Option 1 | 0 | 774
| BAN006-157281583 | 19 | 407054.7251 | -220032.3766 | 47.3199 | 2134.5697 | 2181.8896 | 1.6624 | 97.2007 | 98.8631 | 2083.0265 | -217949.3502 | FALSE | 625 | 15057.5 | -15318.7401 | 18.5295 | 872.2904 | 890.82 | 1291.0696 | -14027.6705 | FALSE | Option 1 | 0 | 774
| BAN006-161068079 | 65 | 1392555.6386 | -752742.3411 | 196.2679 | 8259.0336 | 8455.3015 | 6.8949 | 376.0871 | 382.9821 | 8072.3195 | -744670.0217 | FALSE | 1408 | 51512.5 | -52406.216 | 76.8547 | 3375.0484 | 3451.9031 | 5003.3985 | -47402.8175 | FALSE | Option 1 | 0 | 774
| BAN006-72501199 | 167 | 3577796.7946 | -1933968.7841 | 3775.716 | 154985.0153 | 158760.7312 | 132.6415 | 7057.4687 | 7190.1102 | 151570.621 | -1782398.1631 | FALSE | 1953 | 132347.5 | -134643.6626 | 1478.4961 | 63334.5197 | 64813.0158 | 93947.7154 | -40695.9472 | FALSE | Option 1 | 0 | 774
| BAN006-84647249 | 76 | 1628218.9005 | -880129.5066 | 2275.3336 | 44794.6023 | 47069.9359 | 79.9328 | 2039.7875 | 2119.7204 | 44950.2155 | -835179.291 | FALSE | 1502 | 60230 | -61274.9602 | 890.9759 | 18305.2833 | 19196.2593 | 27873.6766 | -33401.2836 | FALSE | Option 1 | 0 | 774
| BAN006-85222599 | 32 | 685565.8529 | -370580.8449 | 2061.4939 | 27622.5837 | 29684.0777 | 72.4206 | 1257.8346 | 1330.2553 | 28353.8224 | -342227.0224 | FALSE | 861 | 25360 | -25799.9833 | 807.2405 | 11287.9498 | 12095.1903 | 17588.8874 | -8211.0959 | FALSE | Option 1 | 0 | 774
| BAN007-15414603 | 30 | 642717.987 | -347419.5421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -347419.5421 | FALSE | 868 | 23775 | -24187.4843 | 0 | 0 | 0 | 0 | -24187.4843 | FALSE | Option 1 | 0 | 774
| BAN007-24598874 | 288 | 6170092.6757 | -3335227.6038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3335227.6038 | FALSE | 2157 | 228240 | -232199.8493 | 0 | 0 | 0 | 0 | -232199.8493 | FALSE | Option 1 | 0 | 774
| BAN007-24598888 | 18 | 385630.7922 | -208451.7252 | 3874.7545 | 8617.3156 | 12492.0701 | 136.1207 | 392.402 | 528.5228 | 11963.5473 | -196488.1779 | FALSE | 580 | 14265 | -14512.4906 | 1517.2777 | 3521.4601 | 5038.7378 | 7453.3323 | -7059.1582 | FALSE | Option 1 | 0 | 774
| BAN009-78742110 | 58 | 1242588.1083 | -671677.7813 | 1645.1911 | 52999.5306 | 54644.7217 | 57.7958 | 2413.4109 | 2471.2068 | 52173.515 | -619504.2663 | FALSE | 1265 | 45965 | -46762.4697 | 644.2245 | 21658.2216 | 22302.4461 | 32342.2756 | -14420.1941 | FALSE | Option 1 | 0 | 774
| BAN009-78742394 | 104 | 2228089.0218 | -1204387.7458 | 572.6254 | 17436.8061 | 18009.4315 | 20.1164 | 794.0104 | 814.1268 | 17195.3047 | -1187192.4411 | FALSE | 1742 | 82420 | -83849.9456 | 224.2288 | 7125.5388 | 7349.7677 | 10659.6639 | -73190.2817 | FALSE | Option 1 | 0 | 774
| BAN011-171348706 | 1 | 21423.9329 | -11580.6514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11580.6514 | FALSE | 234 | 792.5 | -806.2495 | 0 | 0 | 0 | 0 | -806.2495 | FALSE | Option 1 | 0 | 774
| BAN013-15414453 | 394 | 8441029.5632 | -4562776.6524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4562776.6524 | FALSE | 2203 | 312245 | -317662.2938 | 0 | 0 | 0 | 0 | -317662.2938 | FALSE | Option 1 | 0 | 774
| BAN015-15414416 | 194 | 4156242.9829 | -2246646.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2246646.372 | FALSE | 2038 | 153745 | -156412.3985 | 0 | 0 | 0 | 0 | -156412.3985 | FALSE | Option 1 | 0 | 774
| BAS011-111131839 | 6 | 128543.5974 | -69483.9084 | 95.2707 | 32.0285 | 127.2991 | 3.3469 | 1.4585 | 4.8053 | 122.4938 | -69361.4146 | FALSE | 325 | 4755 | -4837.4969 | 37.3061 | 13.0884 | 50.3945 | 76.9046 | -4760.5923 | FALSE | Option 1 | 0 | 774
| BAS011-134530801 | 23 | 492750.4567 | -266354.9822 | 1247.6868 | 24181.1667 | 25428.8535 | 43.8314 | 1101.1247 | 1144.9561 | 24283.8974 | -242071.0849 | FALSE | 672 | 18227.5 | -18543.738 | 488.5696 | 9881.6171 | 10370.1867 | 15058.6668 | -3485.0712 | FALSE | Option 1 | 0 | 774
| BAS011-140236715 | 92 | 1971001.8269 | -1065419.929 | 451.5808 | 22763.3226 | 23214.9034 | 15.8641 | 1036.5611 | 1052.4252 | 22162.4782 | -1043257.4508 | FALSE | 1654 | 72910 | -74174.9519 | 176.8302 | 9302.2161 | 9479.0463 | 13735.8572 | -60439.0947 | FALSE | Option 1 | 0 | 774
| BAS011-140237055 | 86 | 1842458.2295 | -995936.0206 | 268.4916 | 15337.7883 | 15606.2799 | 9.4322 | 698.4286 | 707.8607 | 14898.4192 | -981037.6014 | FALSE | 1610 | 68155 | -69337.455 | 105.136 | 6267.7766 | 6372.9126 | 9233.3672 | -60104.0878 | FALSE | Option 1 | 0 | 774
| BAS011-15414096 | 1 | 21423.9329 | -11580.6514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11580.6514 | FALSE | 234 | 792.5 | -806.2495 | 0 | 0 | 0 | 0 | -806.2495 | FALSE | Option 1 | 0 | 774
| BAS011-158493706 | 42 | 899805.1819 | -486387.3589 | 164.4157 | 10085.5672 | 10249.9829 | 5.776 | 459.261 | 465.037 | 9784.9459 | -476602.413 | FALSE | 1066 | 33285 | -33862.478 | 64.382 | 4121.4601 | 4185.842 | 6064.1408 | -27798.3372 | FALSE | Option 1 | 0 | 774
| BAS011-158493822 | 27 | 578446.1883 | -312677.5879 | 0.24571 | 16.1597 | 16.4054 | 0.0086319 | 0.73585 | 0.74449 | 15.6609 | -312661.927 | FALSE | 806 | 21397.5 | -21768.7359 | 0.096216 | 6.6036 | 6.6998 | 9.7055 | -21759.0304 | FALSE | Option 1 | 0 | 774
| BAS011-163842929 | 8 | 171391.4632 | -92645.2112 | 439.4177 | 6417.898 | 6857.3157 | 15.4368 | 292.2483 | 307.6852 | 6549.6305 | -86095.5807 | FALSE | 364 | 6340 | -6449.9958 | 172.0673 | 2622.6696 | 2794.7369 | 4062.5788 | -2387.4171 | FALSE | Option 1 | 0 | 774
| BAS011-163930345 | 45 | 964076.9806 | -521129.3131 | 40.1316 | 2639.1398 | 2679.2714 | 1.4098 | 120.1771 | 121.5869 | 2557.6845 | -518571.6286 | FALSE | 1126 | 35662.5 | -36281.2265 | 15.7148 | 1078.4826 | 1094.1974 | 1585.074 | -34696.1525 | FALSE | Option 1 | 0 | 774
| BAS011-163930441 | 28 | 599870.1212 | -324258.2393 | 0.10921 | 8.3813 | 8.4905 | 0.0038367 | 0.38166 | 0.38549 | 8.105 | -324250.1342 | FALSE | 823 | 22190 | -22574.9853 | 0.042766 | 3.425 | 3.4678 | 5.0228 | -22569.9626 | FALSE | Option 1 | 0 | 774
| BAS011-182896771 | 100 | 2142393.2902 | -1158065.1402 | 95.991 | 11297.622 | 11393.613 | 3.3722 | 514.4537 | 517.8259 | 10875.7871 | -1147189.3531 | FALSE | 1714 | 79250 | -80624.9477 | 37.5882 | 4616.7654 | 4654.3536 | 6739.2594 | -73885.6883 | FALSE | Option 1 | 0 | 774
| BAS011-24602396 | 29 | 621294.0541 | -335838.8907 | 916.4099 | 9847.9117 | 10764.3216 | 32.1936 | 448.439 | 480.6326 | 10283.6889 | -325555.2017 | FALSE | 830 | 22982.5 | -23381.2348 | 358.8481 | 4024.3423 | 4383.1904 | 6381.1312 | -17000.1037 | FALSE | Option 1 | 0 | 774
| BAS011-24608723 | 73 | 1563947.1018 | -845387.5523 | 171.8725 | 7428.6271 | 7600.4996 | 6.0379 | 338.2734 | 344.3113 | 7256.1883 | -838131.3641 | FALSE | 1505 | 57852.5 | -58856.2118 | 67.3019 | 3035.7033 | 3103.0052 | 4497.4943 | -54358.7175 | FALSE | Option 1 | 0 | 774
| BAS011-76148984 | 79 | 1692490.6992 | -914871.4608 | 52.8905 | 3981.0396 | 4033.9302 | 1.8581 | 181.2824 | 183.1405 | 3850.7897 | -911020.6711 | FALSE | 1570 | 62607.5 | -63693.7087 | 20.7109 | 1626.8491 | 1647.56 | 2386.3702 | -61307.3385 | FALSE | Option 1 | 0 | 774
| BAS011-76149624 | 50 | 1071196.6451 | -579032.5701 | 197.7812 | 12038.9935 | 12236.7748 | 6.9481 | 548.2131 | 555.1612 | 11681.6135 | -567350.9566 | FALSE | 1201 | 39625 | -40312.4738 | 77.4472 | 4919.7264 | 4997.1736 | 7239.6011 | -33072.8727 | FALSE | Option 1 | 0 | 774
| BAS011-76150176 | 138 | 2956502.7404 | -1598129.8935 | 794.8315 | 60095.5123 | 60890.3438 | 27.9226 | 2736.5368 | 2764.4594 | 58125.8844 | -1540004.0091 | FALSE | 1897 | 109365 | -111262.4278 | 311.2404 | 24557.9897 | 24869.23 | 36021.1137 | -75241.3141 | FALSE | Option 1 | 0 | 774
| BAS011-76150520 | 61 | 1306859.907 | -706419.7355 | 1026.734 | 52791.8825 | 53818.6165 | 36.0693 | 2403.9554 | 2440.0247 | 51378.5918 | -655041.1437 | FALSE | 1300 | 48342.5 | -49181.2181 | 402.0488 | 21573.3664 | 21975.4152 | 31843.2013 | -17338.0168 | FALSE | Option 1 | 0 | 774
| BAS011-79244341 | 58 | 1242588.1083 | -671677.7813 | 275.321 | 12956.488 | 13231.809 | 9.6721 | 589.9926 | 599.6646 | 12632.1444 | -659045.6369 | FALSE | 1308 | 45965 | -46762.4697 | 107.8103 | 5294.6599 | 5402.4702 | 7829.3388 | -38933.1308 | FALSE | Option 1 | 0 | 774
| BAS011-79244394 | 48 | 1028348.7793 | -555871.2673 | 805.9001 | 47089.2598 | 47895.1599 | 28.3114 | 2144.2781 | 2172.5895 | 45722.5704 | -510148.6969 | FALSE | 1110 | 38040 | -38699.9749 | 315.5746 | 19242.9935 | 19558.5682 | 28336.5917 | -10363.3832 | FALSE | Option 1 | 0 | 774
| BAS011-79244508 | 26 | 557022.2554 | -301096.9365 | 17.1612 | 814.7379 | 831.8991 | 0.60288 | 37.1003 | 37.7032 | 794.196 | -300302.7405 | FALSE | 789 | 20605 | -20962.4864 | 6.72 | 332.9421 | 339.6621 | 492.2371 | -20470.2493 | FALSE | Option 1 | 0 | 774
| BAS011-79244589 | 20 | 428478.658 | -231613.028 | 410.7842 | 13850.9405 | 14261.7247 | 14.4309 | 630.7228 | 645.1537 | 13616.571 | -217996.457 | FALSE | 626 | 15850 | -16124.9895 | 160.855 | 5660.1773 | 5821.0323 | 8440.6924 | -7684.2971 | FALSE | Option 1 | 0 | 774
| BAS011-79245218 | 33 | 706989.7858 | -382161.4963 | 26.5517 | 548.4841 | 575.0358 | 0.93276 | 24.976 | 25.9088 | 549.127 | -381612.3692 | FALSE | 926 | 26152.5 | -26606.2327 | 10.3971 | 224.1377 | 234.5348 | 340.501 | -26265.7317 | FALSE | Option 1 | 0 | 774
| BAS011-84427318 | 128 | 2742263.4114 | -1482323.3795 | 605.6638 | 32670.2196 | 33275.8834 | 21.2771 | 1487.6861 | 1508.9632 | 31766.9202 | -1450556.4592 | FALSE | 1862 | 101440 | -103199.933 | 237.166 | 13350.6627 | 13587.8288 | 19688.0546 | -83511.8784 | FALSE | Option 1 | 0 | 774
| BAS011-84622282 | 73 | 1563947.1018 | -845387.5523 | 2706.1954 | 77286.6435 | 79992.8389 | 95.0691 | 3519.36 | 3614.4291 | 76378.4098 | -769009.1425 | FALSE | 1439 | 57852.5 | -58856.2118 | 1059.6929 | 31583.1336 | 32642.8265 | 47350.0124 | -11506.1994 | FALSE | Option 1 | 0 | 774
| BAS011-84732066 | 67 | 1435403.5044 | -775903.6439 | 6.2822 | 341.6058 | 347.888 | 0.2207 | 15.5555 | 15.7762 | 332.1118 | -775571.5321 | FALSE | 1444 | 53097.5 | -54018.7149 | 2.46 | 139.597 | 142.057 | 205.831 | -53812.8839 | FALSE | Option 1 | 0 | 774
| BAS011-85028212 | 130 | 2785111.2772 | -1505484.6823 | 1840.6096 | 124843.7521 | 126684.3617 | 64.6609 | 5684.9423 | 5749.6032 | 120934.7585 | -1384549.9238 | FALSE | 1837 | 103025 | -104812.432 | 720.7465 | 51017.3132 | 51738.0598 | 74946.3019 | -29866.13 | FALSE | Option 1 | 0 | 774
| BAS011-85028323 | 19 | 407054.7251 | -220032.3766 | 0.2357 | 12.2607 | 12.4964 | 0.0082802 | 0.55831 | 0.56659 | 11.9298 | -220020.4469 | FALSE | 637 | 15057.5 | -15318.7401 | 0.092296 | 5.0103 | 5.1026 | 7.3938 | -15311.3463 | FALSE | Option 1 | 0 | 774
| BAS011-85029671 | 59 | 1264012.0412 | -683258.4327 | 439.8919 | 16724.7584 | 17164.6503 | 15.4535 | 761.5863 | 777.0397 | 16387.6106 | -666870.8222 | FALSE | 1321 | 46757.5 | -47568.7191 | 172.253 | 6834.561 | 7006.814 | 10157.8363 | -37410.8828 | FALSE | Option 1 | 0 | 774
| BAS011-85030316 | 61 | 1306859.907 | -706419.7355 | 222.7371 | 9021.219 | 9243.9561 | 7.8248 | 410.7944 | 418.6192 | 8825.3369 | -697594.3986 | FALSE | 1361 | 48342.5 | -49181.2181 | 87.2195 | 3686.5149 | 3773.7344 | 5470.2217 | -43710.9964 | FALSE | Option 1 | 0 | 774
| BAS011-85421065 | 38 | 814109.4503 | -440064.7533 | 1046.827 | 36317.4961 | 37364.3231 | 36.7752 | 1653.7701 | 1690.5454 | 35673.7777 | -404390.9755 | FALSE | 966 | 30115 | -30637.4801 | 409.9169 | 14841.1197 | 15251.0366 | 22113.2865 | -8524.1936 | FALSE | Option 1 | 0 | 774
| BAS011-85421256 | 75 | 1606794.9676 | -868548.8552 | 459.9447 | 37791.7304 | 38251.675 | 16.1579 | 1720.9016 | 1737.0595 | 36514.6155 | -832034.2396 | FALSE | 1499 | 59437.5 | -60468.7108 | 180.1053 | 15443.5646 | 15623.6698 | 22628.0052 | -37840.7056 | FALSE | Option 1 | 0 | 774
| BAS011-89021568 | 68 | 1456827.4373 | -787484.2953 | 1388.8404 | 40575.6028 | 41964.4432 | 48.7902 | 1847.6693 | 1896.4594 | 40067.9837 | -747416.3116 | FALSE | 1411 | 53890 | -54824.9644 | 543.8426 | 16581.1921 | 17125.0347 | 24839.4085 | -29985.5559 | FALSE | Option 1 | 0 | 774
| BAS011-99529198 | 43 | 921229.1148 | -497968.0103 | 109.054 | 7903.1651 | 8012.2191 | 3.8311 | 359.8822 | 363.7132 | 7648.5059 | -490319.5044 | FALSE | 1086 | 34077.5 | -34668.7275 | 42.7034 | 3229.623 | 3272.3264 | 4739.8927 | -29928.8348 | FALSE | Option 1 | 0 | 774
| BAS012-15414133 | 132 | 2827959.143 | -1528645.9851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1528645.9851 | FALSE | 1893 | 104610 | -106424.9309 | 0 | 0 | 0 | 0 | -106424.9309 | FALSE | Option 1 | 0 | 774
| BAS012-187042122 | 95 | 2035273.6257 | -1100161.8832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1100161.8832 | FALSE | 1682 | 75287.5 | -76593.7003 | 0 | 0 | 0 | 0 | -76593.7003 | FALSE | Option 1 | 0 | 774
| BAS013-15414170 | 5 | 107119.6645 | -57903.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -57903.257 | FALSE | 312 | 3962.5 | -4031.2474 | 0 | 0 | 0 | 0 | -4031.2474 | FALSE | Option 1 | 0 | 774
| BAS014-15414207 | 130 | 2785111.2772 | -1505484.6823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1505484.6823 | FALSE | 1882 | 103025 | -104812.432 | 0 | 0 | 0 | 0 | -104812.432 | FALSE | Option 1 | 0 | 774
| BAS014-74639994 | 141 | 3020774.5391 | -1632871.8477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1632871.8477 | FALSE | 1922 | 111742.5 | -113681.1762 | 0 | 0 | 0 | 0 | -113681.1762 | FALSE | Option 1 | 0 | 774
| BAS021-15414366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| BAS022-130430211 | 114 | 2442328.3508 | -1320194.2598 | 1291.5011 | 55382.6362 | 56674.1374 | 45.3706 | 2521.9291 | 2567.2998 | 54106.8376 | -1266087.4222 | FALSE | 1787 | 90345 | -91912.4403 | 505.7265 | 22632.0761 | 23137.8026 | 33536.3348 | -58376.1056 | FALSE | Option 1 | 0 | 774
| BAS022-139345594 | 144 | 3085046.3378 | -1667613.8019 | 3528.0392 | 116092.3045 | 119620.3436 | 123.9406 | 5286.4324 | 5410.373 | 114209.9706 | -1553403.8312 | FALSE | 1902 | 114120 | -116099.9247 | 1381.5108 | 47441.0402 | 48822.551 | 70797.7927 | -45302.132 | FALSE | Option 1 | 0 | 774
| BAS022-142437276 | 11 | 235663.2619 | -127387.1654 | 482.9853 | 4360.6866 | 4843.6719 | 16.9674 | 198.5702 | 215.5376 | 4628.1343 | -122759.0311 | FALSE | 437 | 8717.5 | -8868.7442 | 189.1276 | 1781.9916 | 1971.1191 | 2872.5528 | -5996.1915 | FALSE | Option 1 | 0 | 774
| BAS022-155392904 | 48 | 1028348.7793 | -555871.2673 | 632.2614 | 24901.9794 | 25534.2409 | 22.2114 | 1133.948 | 1156.1594 | 24378.0815 | -531493.1858 | FALSE | 1150 | 38040 | -38699.9749 | 247.5811 | 10176.1767 | 10423.7579 | 15110.483 | -23589.4919 | FALSE | Option 1 | 0 | 774
| BAS022-155393076 | 58 | 1242588.1083 | -671677.7813 | 2262.5293 | 49353.062 | 51615.5914 | 79.483 | 2247.3637 | 2326.8467 | 49288.7447 | -622389.0366 | FALSE | 1269 | 45965 | -46762.4697 | 885.962 | 20168.0948 | 21054.0568 | 30561.5346 | -16200.9351 | FALSE | Option 1 | 0 | 774
| BAS022-172349144 | 10 | 214239.329 | -115806.514 | 1.7386 | 104.59 | 106.3286 | 0.061077 | 4.7627 | 4.8237 | 101.5049 | -115705.0091 | FALSE | 417 | 7925 | -8062.4948 | 0.6808 | 42.7406 | 43.4214 | 62.9072 | -7999.5876 | FALSE | Option 1 | 0 | 774
| BAS022-72697775 | 19 | 407054.7251 | -220032.3766 | 419.8756 | 11079.6461 | 11499.5217 | 14.7503 | 504.5278 | 519.2781 | 10980.2435 | -209052.1331 | FALSE | 609 | 15057.5 | -15318.7401 | 164.415 | 4527.6897 | 4692.1048 | 6807.4169 | -8511.3232 | FALSE | Option 1 | 0 | 774
| BAS022-72698236 | 51 | 1092620.578 | -590613.2215 | 943.7198 | 34752.1613 | 35695.8811 | 33.153 | 1582.4903 | 1615.6434 | 34080.2377 | -556532.9838 | FALSE | 1188 | 40417.5 | -41118.7233 | 369.5421 | 14201.4467 | 14570.9889 | 21124.8922 | -19993.8311 | FALSE | Option 1 | 0 | 774
| BAS022-72698508 | 34 | 728413.7187 | -393742.1477 | 525.8266 | 17930.6579 | 18456.4845 | 18.4724 | 816.4987 | 834.971 | 17621.5135 | -376120.6342 | FALSE | 920 | 26945 | -27412.4822 | 205.9034 | 7327.351 | 7533.2543 | 10923.2301 | -16489.2521 | FALSE | Option 1 | 0 | 774
| BAS023-141849179 | 35 | 749837.6516 | -405322.7991 | 219.4999 | 20793.9323 | 21013.4322 | 7.7111 | 946.882 | 954.5931 | 20058.8391 | -385263.96 | FALSE | 937 | 27737.5 | -28218.7317 | 85.9518 | 8497.4261 | 8583.3779 | 12430.0542 | -15788.6775 | FALSE | Option 1 | 0 | 774
| BAS023-15416141 | 153 | 3277861.7339 | -1771839.6645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1771839.6645 | FALSE | 1950 | 121252.5 | -123356.1699 | 0 | 0 | 0 | 0 | -123356.1699 | FALSE | Option 1 | 0 | 774
| BAS024-15416191 | 179 | 3834883.9894 | -2072936.601 | 36388.496 | 17100.106 | 53488.6021 | 1278.3337 | 778.6783 | 2057.012 | 51431.5901 | -2021505.0109 | FALSE | 2002 | 141857.5 | -144318.6563 | 14249.0196 | 6987.9465 | 21236.9661 | 32251.6359 | -112067.0204 | FALSE | Option 1 | 0 | 774
| BAS033-140150122 | 24 | 514174.3896 | -277935.6336 | 1145.1056 | 21992.4798 | 23137.5854 | 40.2277 | 1001.4596 | 1041.6874 | 22095.898 | -255839.7356 | FALSE | 709 | 19020 | -19349.9874 | 448.4008 | 8987.2117 | 9435.6126 | 13701.9729 | -5648.0146 | FALSE | Option 1 | 0 | 774
| BAS033-155164312 | 49 | 1049772.7122 | -567451.9187 | 25.5567 | 806.7452 | 832.3019 | 0.89781 | 36.7363 | 37.6341 | 794.6677 | -566657.251 | FALSE | 1199 | 38832.5 | -39506.2244 | 10.0075 | 329.6759 | 339.6834 | 492.6185 | -39013.6059 | FALSE | Option 1 | 0 | 774
| BAS033-155190238 | 125 | 2677991.6127 | -1447581.4253 | 807.2294 | 57170.912 | 57978.1414 | 28.3581 | 2603.3609 | 2631.719 | 55346.4224 | -1392235.0028 | FALSE | 1840 | 99062.5 | -100781.1846 | 316.0952 | 23362.8538 | 23678.9489 | 34299.1924 | -66481.9922 | FALSE | Option 1 | 0 | 774
| BAS033-155190444 | 40 | 856957.3161 | -463226.0561 | 127.0248 | 5892.5256 | 6019.5503 | 4.4624 | 268.3247 | 272.7871 | 5746.7632 | -457479.2929 | FALSE | 1035 | 31700 | -32249.9791 | 49.7404 | 2407.9765 | 2457.7169 | 3561.8334 | -28688.1457 | FALSE | Option 1 | 0 | 774
| BAS033-155190566 | 42 | 899805.1819 | -486387.3589 | 246.6313 | 16026.4342 | 16273.0655 | 8.6642 | 729.7871 | 738.4513 | 15534.6143 | -470852.7446 | FALSE | 1051 | 33285 | -33862.478 | 96.576 | 6549.1913 | 6645.7673 | 9627.2983 | -24235.1798 | FALSE | Option 1 | 0 | 774
| BAS033-155190689 | 22 | 471326.5238 | -254774.3308 | 19.0072 | 970.0388 | 989.0461 | 0.66773 | 44.1721 | 44.8399 | 944.2062 | -253830.1247 | FALSE | 699 | 17435 | -17737.4885 | 7.4429 | 396.4057 | 403.8486 | 585.1975 | -17152.291 | FALSE | Option 1 | 0 | 774
| BAS033-155190801 | 20 | 428478.658 | -231613.028 | 2.0655 | 159.7536 | 161.8192 | 0.072563 | 7.2746 | 7.3472 | 154.472 | -231458.556 | FALSE | 659 | 15850 | -16124.9895 | 0.80882 | 65.2832 | 66.092 | 95.7271 | -16029.2624 | FALSE | Option 1 | 0 | 774
| BAS033-155250207 | 115 | 2463752.2837 | -1331774.9112 | 625.9757 | 47727.6428 | 48353.6185 | 21.9906 | 2173.3478 | 2195.3385 | 46158.2801 | -1285616.6312 | FALSE | 1798 | 91137.5 | -92718.6898 | 245.1198 | 19503.8683 | 19748.9881 | 28604.6304 | -64114.0594 | FALSE | Option 1 | 0 | 774
| BAS033-155250324 | 12 | 257087.1948 | -138967.8168 | 0.49754 | 23.075 | 23.5725 | 0.017479 | 1.0508 | 1.0682 | 22.5043 | -138945.3126 | FALSE | 474 | 9510 | -9674.9937 | 0.19483 | 9.4296 | 9.6244 | 13.9481 | -9661.0456 | FALSE | Option 1 | 0 | 774
| BAS033-78747898 | 6 | 128543.5974 | -69483.9084 | 11.0401 | 109.5504 | 120.5905 | 0.38784 | 4.9885 | 5.3764 | 115.2142 | -69368.6943 | FALSE | 326 | 4755 | -4837.4969 | 4.3231 | 44.7677 | 49.0908 | 71.4997 | -4765.9971 | FALSE | Option 1 | 0 | 774
| BAS033-78747960 | 7 | 149967.5303 | -81064.5598 | 36.2001 | 978.5183 | 1014.7184 | 1.2717 | 44.5583 | 45.83 | 968.8884 | -80095.6714 | FALSE | 347 | 5547.5 | -5643.7463 | 14.1752 | 399.8708 | 414.0461 | 600.6723 | -5043.074 | FALSE | Option 1 | 0 | 774
| BAS033-95730010 | 21 | 449902.5909 | -243193.6794 | 81.4558 | 7942.9105 | 8024.3662 | 2.8616 | 361.692 | 364.5536 | 7659.8127 | -235533.8668 | FALSE | 666 | 16642.5 | -16931.239 | 31.8965 | 3245.8649 | 3277.7614 | 4746.6049 | -12184.6341 | FALSE | Option 1 | 0 | 774
| BAS034-15416250 | 195 | 4177666.9158 | -2258227.0234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2258227.0234 | FALSE | 2041 | 154537.5 | -157218.648 | 0 | 0 | 0 | 0 | -157218.648 | FALSE | Option 1 | 0 | 774
| BBD014-15437952 | 127 | 2720839.4785 | -1470742.7281 | 68631.3732 | 52676.8764 | 121308.2496 | 2411.0312 | 1850.5472 | 4261.5784 | 117046.6712 | -1353696.0569 | FALSE | 1822 | 100647.5 | -102393.6835 | 26874.6964 | 20627.2291 | 47501.9254 | 73806.3241 | -28587.3594 | FALSE | Option 1 | 0 | 774
| BBD014-160682204 | 90 | 1928153.9611 | -1042258.6262 | 689.9553 | 4320.0304 | 5009.9857 | 24.2382 | 151.7634 | 176.0016 | 4833.9841 | -1037424.6421 | FALSE | 1653 | 71325 | -72562.4529 | 270.1729 | 1691.639 | 1961.8119 | 3048.1738 | -69514.2791 | FALSE | Option 1 | 0 | 774
| BBD014-162435599 | 133 | 2849383.0759 | -1540226.6365 | 0 | 72453.0497 | 72453.0497 | 0 | 2545.2873 | 2545.2873 | 69907.7624 | -1470318.8741 | FALSE | 1870 | 105402.5 | -107231.1804 | 0 | 28371.1897 | 28371.1897 | 44081.86 | -63149.3204 | FALSE | Option 1 | 0 | 774
| BBD014-96325732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| BBD014-96325958 | 28 | 599870.1212 | -324258.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -324258.2393 | FALSE | 824 | 22190 | -22574.9853 | 0 | 0 | 0 | 0 | -22574.9853 | FALSE | Option 1 | 0 | 774
| BBD021-15437930 | 27 | 578446.1883 | -312677.5879 | 384.2642 | 2653.3991 | 3037.6633 | 13.4993 | 93.2143 | 106.7136 | 2930.9497 | -309746.6381 | FALSE | 800 | 21397.5 | -21768.7359 | 150.4703 | 1039.0189 | 1189.4892 | 1848.1741 | -19920.5618 | FALSE | Option 1 | 0 | 774
| BET002-147836095 | 151 | 3235013.8681 | -1748678.3617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1748678.3617 | FALSE | 1948 | 119667.5 | -121743.671 | 0 | 0 | 0 | 0 | -121743.671 | FALSE | Option 1 | 0 | 774
| BET002-15424310 | 93 | 1992425.7599 | -1077000.5804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1077000.5804 | FALSE | 1668 | 73702.5 | -74981.2013 | 0 | 0 | 0 | 0 | -74981.2013 | FALSE | Option 1 | 0 | 774
| BET004-72499790 | 34 | 728413.7187 | -393742.1477 | 2816.6306 | 34514.5699 | 37331.2005 | 98.9487 | 1212.5024 | 1311.4511 | 36019.7494 | -357722.3982 | FALSE | 885 | 26945 | -27412.4822 | 1102.9372 | 13515.227 | 14618.1641 | 22713.0364 | -4699.4458 | FALSE | Option 1 | 0 | 774
| BET004-72500230 | 25 | 535598.3225 | -289516.2851 | 2776.817 | 25025.4989 | 27802.316 | 97.55 | 879.1498 | 976.6998 | 26825.6161 | -262690.6689 | FALSE | 716 | 19812.5 | -20156.2369 | 1087.347 | 9799.4933 | 10886.8403 | 16915.4757 | -3240.7612 | FALSE | Option 1 | 0 | 774
| BET005-142631975 | 7 | 149967.5303 | -81064.5598 | 154.5249 | 2260.2323 | 2414.7571 | 5.4285 | 79.4023 | 84.8308 | 2329.9263 | -78734.6335 | FALSE | 343 | 5547.5 | -5643.7463 | 60.5089 | 885.0625 | 945.5714 | 1469.1857 | -4174.5606 | FALSE | Option 1 | 0 | 774
| BET005-162764936 | 1 | 21423.9329 | -11580.6514 | 566.0648 | 591.5744 | 1157.6391 | 19.8859 | 20.7821 | 40.668 | 1116.9711 | -10463.6803 | FALSE | 222 | 792.5 | -806.2495 | 221.6598 | 231.6489 | 453.3087 | 704.3304 | -101.9191 | FALSE | Option 1 | 0 | 774
| BET006-143535036 | 45 | 964076.9806 | -521129.3131 | 2379.6007 | 46719.3713 | 49098.972 | 83.5958 | 1641.259 | 1724.8548 | 47374.1172 | -473755.1959 | FALSE | 1059 | 35662.5 | -36281.2265 | 931.8049 | 18294.3872 | 19226.1921 | 29872.7799 | -6408.4465 | FALSE | Option 1 | 0 | 774
| BET006-143535310 | 96 | 2056697.5586 | -1111742.5346 | 3183.6049 | 105247.4756 | 108431.0806 | 111.8406 | 3697.3608 | 3809.2013 | 104621.8792 | -1007120.6554 | FALSE | 1633 | 76080 | -77399.9498 | 1246.6371 | 41212.8421 | 42459.4792 | 65971.6013 | -11428.3484 | FALSE | Option 1 | 0 | 774
| BET006-74053669 | 9 | 192815.3961 | -104225.8626 | 3009.8842 | 7235.4367 | 10245.3209 | 105.7377 | 254.1821 | 359.9198 | 9885.4011 | -94340.4615 | FALSE | 380 | 7132.5 | -7256.2453 | 1178.6115 | 2833.2547 | 4011.8662 | 6233.4547 | -1022.7906 | FALSE | Option 1 | 0 | 774
| BET007-129159691 | 10 | 214239.329 | -115806.514 | 1747.1402 | 8073.0109 | 9820.1511 | 61.3773 | 283.6062 | 344.9835 | 9475.1676 | -106331.3464 | FALSE | 399 | 7925 | -8062.4948 | 684.1457 | 3161.2323 | 3845.3781 | 5974.773 | -2087.7218 | FALSE | Option 1 | 0 | 774
| BET007-132751049 | 11 | 235663.2619 | -127387.1654 | 487.3991 | 4797.4934 | 5284.8926 | 17.1224 | 168.5367 | 185.6591 | 5099.2335 | -122287.932 | FALSE | 436 | 8717.5 | -8868.7442 | 190.8559 | 1878.6041 | 2069.46 | 3215.4326 | -5653.3117 | FALSE | Option 1 | 0 | 774
| BET007-134953366 | 1 | 21423.9329 | -11580.6514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11580.6514 | FALSE | 234 | 792.5 | -806.2495 | 0 | 0 | 0 | 0 | -806.2495 | FALSE | Option 1 | 0 | 774
| BET007-154907875 | 14 | 299935.0606 | -162129.1196 | 2427.0878 | 14319.4632 | 16746.551 | 85.264 | 503.0451 | 588.309 | 16158.242 | -145970.8776 | FALSE | 487 | 11095 | -11287.4927 | 950.3999 | 5607.2202 | 6557.6201 | 10188.9309 | -1098.5618 | FALSE | Option 1 | 0 | 774
| BET008-94648877 | 218 | 4670417.3726 | -2524582.0056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2524582.0056 | FALSE | 2081 | 172765 | -175762.3859 | 0 | 0 | 0 | 0 | -175762.3859 | FALSE | Option 1 | 0 | 774
| BGO011-197684068 | 13 | 278511.1277 | -150548.4682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -150548.4682 | FALSE | 505 | 10302.5 | -10481.2432 | 0 | 0 | 0 | 0 | -10481.2432 | FALSE | Option 1 | 0 | 774
| BGO014-197650786 | 28 | 599870.1212 | -324258.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -324258.2393 | FALSE | 824 | 22190 | -22574.9853 | 0 | 0 | 0 | 0 | -22574.9853 | FALSE | Option 1 | 0 | 774
| BGO022-164368050 | 109 | 2335208.6863 | -1262291.0028 | 56928.6428 | 47648.2778 | 104576.9206 | 1999.9124 | 1673.8917 | 3673.8041 | 100903.1165 | -1161387.8863 | FALSE | 1726 | 86382.5 | -87881.193 | 22292.1372 | 18658.1288 | 40950.266 | 63626.6546 | -24254.5383 | FALSE | Option 1 | 0 | 774
| BGO022-197683907 | 84 | 1799610.3637 | -972774.7178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -972774.7178 | FALSE | 1606 | 66570 | -67724.956 | 0 | 0 | 0 | 0 | -67724.956 | FALSE | Option 1 | 0 | 774
| BGO023-143335516 | 58 | 1242588.1083 | -671677.7813 | 4882.6733 | 58329.9826 | 63212.6559 | 171.5291 | 2049.1417 | 2220.6708 | 60991.9851 | -610685.7962 | FALSE | 1252 | 45965 | -46762.4697 | 1911.9589 | 22840.8743 | 24752.8332 | 38459.8227 | -8302.6469 | FALSE | Option 1 | 0 | 774
| BGO023-154908179 | 58 | 1242588.1083 | -671677.7813 | 2758.4712 | 57674.2191 | 60432.6903 | 96.9055 | 2026.1046 | 2123.0102 | 58309.6802 | -613368.1012 | FALSE | 1257 | 45965 | -46762.4697 | 1080.1631 | 22584.0902 | 23664.2533 | 36768.437 | -9994.0327 | FALSE | Option 1 | 0 | 774
| BGO023-154971813 | 25 | 535598.3225 | -289516.2851 | 998.6377 | 27995.4309 | 28994.0686 | 35.0823 | 983.484 | 1018.5663 | 27975.5023 | -261540.7828 | FALSE | 714 | 19812.5 | -20156.2369 | 391.0469 | 10962.4603 | 11353.5072 | 17640.5614 | -2515.6755 | FALSE | Option 1 | 0 | 774
| BGO023-154972040 | 15 | 321358.9935 | -173709.771 | 1101.7936 | 15161.3591 | 16263.1527 | 38.7062 | 532.621 | 571.3272 | 15691.8256 | -158017.9455 | FALSE | 515 | 11887.5 | -12093.7422 | 431.4407 | 5936.8901 | 6368.3309 | 9894.8219 | -2198.9203 | FALSE | Option 1 | 0 | 774
| BGO023-95621561 | 11 | 235663.2619 | -127387.1654 | 210.7159 | 3897.2855 | 4108.0014 | 7.4025 | 136.9123 | 144.3148 | 3963.6866 | -123423.4788 | FALSE | 439 | 8717.5 | -8868.7442 | 82.5122 | 1526.1004 | 1608.6126 | 2499.3888 | -6369.3554 | FALSE | Option 1 | 0 | 774
| BLT016-15429893 | 181 | 3877731.8552 | -2096097.9038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2096097.9038 | FALSE | 2013 | 143442.5 | -145931.1553 | 0 | 0 | 0 | 0 | -145931.1553 | FALSE | Option 1 | 0 | 774
| BLT017-15429856 | 291 | 6234364.4744 | -3369969.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3369969.558 | FALSE | 2161 | 230617.5 | -234618.5977 | 0 | 0 | 0 | 0 | -234618.5977 | FALSE | Option 1 | 0 | 774
| BLT019-15429808 | 146 | 3127894.2036 | -1690775.1047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1690775.1047 | FALSE | 1933 | 115705 | -117712.4236 | 0 | 0 | 0 | 0 | -117712.4236 | FALSE | Option 1 | 0 | 774
| BLT020-15429758 | 100 | 2142393.2902 | -1158065.1402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1158065.1402 | FALSE | 1722 | 79250 | -80624.9477 | 0 | 0 | 0 | 0 | -80624.9477 | FALSE | Option 1 | 0 | 774
| BLT021-15429734 | 332 | 7112745.7233 | -3844776.2655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3844776.2655 | FALSE | 2185 | 263110 | -267674.8263 | 0 | 0 | 0 | 0 | -267674.8263 | FALSE | Option 1 | 0 | 774
| BLT022-15429547 | 139 | 2977926.6733 | -1609710.5449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1609710.5449 | FALSE | 1915 | 110157.5 | -112068.6773 | 0 | 0 | 0 | 0 | -112068.6773 | FALSE | Option 1 | 0 | 774
| BLT022-164443534 | 114 | 2442328.3508 | -1320194.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1320194.2598 | FALSE | 1808 | 90345 | -91912.4403 | 0 | 0 | 0 | 0 | -91912.4403 | FALSE | Option 1 | 0 | 774
| BLT030-15429658 | 245 | 5248863.5609 | -2837259.5935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2837259.5935 | FALSE | 2111 | 194162.5 | -197531.1218 | 0 | 0 | 0 | 0 | -197531.1218 | FALSE | Option 1 | 0 | 774
| BLT031-15429682 | 36 | 771261.5845 | -416903.4505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -416903.4505 | FALSE | 990 | 28530 | -29024.9812 | 0 | 0 | 0 | 0 | -29024.9812 | FALSE | Option 1 | 0 | 774
| BMH003-137632841 | 48 | 1028348.7793 | -555871.2673 | 2169.0678 | 20209.087 | 22378.1548 | 76.1997 | 920.2503 | 996.45 | 21381.7049 | -534489.5624 | FALSE | 1155 | 38040 | -38699.9749 | 849.3643 | 8258.4295 | 9107.7938 | 13270.361 | -25429.6139 | FALSE | Option 1 | 0 | 774
| BMH003-137632864 | 62 | 1328283.8399 | -718000.3869 | 1114.1103 | 23078.4256 | 24192.5359 | 39.1389 | 1050.9098 | 1090.0486 | 23102.4873 | -694897.8997 | FALSE | 1359 | 49135 | -49987.4676 | 436.2637 | 9430.9827 | 9867.2464 | 14325.2895 | -35662.1781 | FALSE | Option 1 | 0 | 774
| BMH003-137632887 | 31 | 664141.92 | -359000.1935 | 809.6055 | 13976.855 | 14786.4605 | 28.4416 | 636.4565 | 664.898 | 14121.5624 | -344878.631 | FALSE | 865 | 24567.5 | -24993.7338 | 317.0256 | 5711.6322 | 6028.6578 | 8757.8027 | -16235.931 | FALSE | Option 1 | 0 | 774
| BMH003-15408256 | 98 | 2099545.4244 | -1134903.8374 | 39004.4998 | 12066.9739 | 51071.4737 | 1370.2344 | 549.4873 | 1919.7216 | 49151.7521 | -1085752.0853 | FALSE | 1670 | 77665 | -79012.4487 | 15273.3952 | 4931.1606 | 20204.5558 | 30866.9179 | -48145.5308 | FALSE | Option 1 | 0 | 774
| BMH003-24599924 | 37 | 792685.5174 | -428484.1019 | 265.1706 | 4307.9321 | 4573.1027 | 9.3155 | 196.168 | 205.4835 | 4367.6192 | -424116.4826 | FALSE | 997 | 29322.5 | -29831.2306 | 103.8356 | 1760.4335 | 1864.2691 | 2708.8336 | -27122.397 | FALSE | Option 1 | 0 | 774
| BMH003-84023922 | 61 | 1306859.907 | -706419.7355 | 276.5189 | 3705.9341 | 3982.453 | 9.7142 | 168.7551 | 178.4693 | 3803.9837 | -702615.7518 | FALSE | 1368 | 48342.5 | -49181.2181 | 108.2794 | 1514.4274 | 1622.7068 | 2359.7462 | -46821.4719 | FALSE | Option 1 | 0 | 774
| BMH003-84426167 | 68 | 1456827.4373 | -787484.2953 | 2158.9454 | 55647.3423 | 57806.2878 | 75.8441 | 2533.9829 | 2609.827 | 55196.4608 | -732287.8346 | FALSE | 1396 | 53890 | -54824.9644 | 845.4006 | 22740.2481 | 23585.6487 | 34220.6391 | -20604.3253 | FALSE | Option 1 | 0 | 774
| BMH004-15408343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| BMH006-24602242 | 1 | 21423.9329 | -11580.6514 | 243.0521 | 315.7432 | 558.7952 | 8.5385 | 14.3778 | 22.9163 | 535.8789 | -11044.7725 | FALSE | 223 | 792.5 | -806.2495 | 95.1744 | 129.0282 | 224.2026 | 334.5926 | -471.6569 | FALSE | Option 1 | 0 | 774
| BMH006-74239819 | 31 | 664141.92 | -359000.1935 | 1462.2214 | 11774.9416 | 13237.163 | 51.3681 | 536.1891 | 587.5572 | 12649.6058 | -346350.5877 | FALSE | 866 | 24567.5 | -24993.7338 | 572.5771 | 4811.8218 | 5384.3989 | 7852.7641 | -17140.9697 | FALSE | Option 1 | 0 | 774
| BMH006-84024816 | 40 | 856957.3161 | -463226.0561 | 1674.34 | 21745.3097 | 23419.6498 | 58.8198 | 990.2044 | 1049.0242 | 22370.6255 | -440855.4306 | FALSE | 1020 | 31700 | -32249.9791 | 655.6386 | 8886.2058 | 9541.8445 | 13877.8053 | -18372.1738 | FALSE | Option 1 | 0 | 774
| BMH006-85029171 | 35 | 749837.6516 | -405322.7991 | 3489.3711 | 19039.494 | 22528.865 | 122.5822 | 866.9911 | 989.5733 | 21539.2917 | -383783.5074 | FALSE | 934 | 27737.5 | -28218.7317 | 1366.3691 | 7780.4761 | 9146.8452 | 13382.0198 | -14836.7119 | FALSE | Option 1 | 0 | 774
| BMH006-85031037 | 52 | 1114044.5109 | -602193.8729 | 1417.73 | 15963.5755 | 17381.3055 | 49.8051 | 726.9247 | 776.7298 | 16604.5757 | -585589.2972 | FALSE | 1227 | 41210 | -41924.9728 | 555.1552 | 6523.5041 | 7078.6593 | 10302.6462 | -31622.3266 | FALSE | Option 1 | 0 | 774
| CDN001-144336613 | 20 | 428478.658 | -231613.028 | 174.505 | 2386.2693 | 2560.7743 | 6.1304 | 108.6623 | 114.7926 | 2445.9817 | -229167.0464 | FALSE | 655 | 15850 | -16124.9895 | 68.3327 | 975.1473 | 1043.48 | 1517.2943 | -14607.6953 | FALSE | Option 1 | 0 | 774
| CDN001-147732702 | 28 | 599870.1212 | -324258.2393 | 111.0567 | 2658.2587 | 2769.3155 | 3.9014 | 121.0477 | 124.9491 | 2644.3664 | -321613.8729 | FALSE | 818 | 22190 | -22574.9853 | 43.4876 | 1086.2956 | 1129.7832 | 1639.5322 | -20935.4531 | FALSE | Option 1 | 0 | 774
| CDN001-147732747 | 31 | 664141.92 | -359000.1935 | 231.8147 | 6142.4555 | 6374.2702 | 8.1437 | 279.7057 | 287.8494 | 6086.4209 | -352913.7726 | FALSE | 874 | 24567.5 | -24993.7338 | 90.7741 | 2510.1102 | 2600.8843 | 3773.3859 | -21220.3479 | FALSE | Option 1 | 0 | 774
| CDN001-15400094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| CDN001-154719434 | 22 | 471326.5238 | -254774.3308 | 106.1335 | 939.2068 | 1045.3403 | 3.7285 | 42.7682 | 46.4966 | 998.8436 | -253775.4872 | FALSE | 698 | 17435 | -17737.4885 | 41.5598 | 383.8062 | 425.366 | 619.9743 | -17117.5142 | FALSE | Option 1 | 0 | 774
| CDN001-156321963 | 316 | 6769962.7969 | -3659485.843 | 53547.9227 | 276070.4564 | 329618.3791 | 1881.1472 | 12571.2709 | 14452.418 | 315165.9611 | -3344319.882 | FALSE | 2159 | 250430 | -254774.8347 | 20968.3137 | 112816.0017 | 133784.3154 | 195834.0637 | -58940.771 | FALSE | Option 1 | 0 | 774
| CDN001-158379454 | 32 | 685565.8529 | -370580.8449 | 751.2381 | 7146.3123 | 7897.5504 | 26.3911 | 325.4178 | 351.8089 | 7545.7415 | -363035.1033 | FALSE | 896 | 25360 | -25799.9833 | 294.1701 | 2920.3356 | 3214.5057 | 4683.0447 | -21116.9385 | FALSE | Option 1 | 0 | 774
| CDN001-160252941 | 45 | 964076.9806 | -521129.3131 | 35.7924 | 579.6765 | 615.4689 | 1.2574 | 26.3964 | 27.6538 | 587.8151 | -520541.498 | FALSE | 1133 | 35662.5 | -36281.2265 | 14.0156 | 236.8844 | 250.9 | 364.5689 | -35916.6575 | FALSE | Option 1 | 0 | 774
| CDN001-162435420 | 23 | 492750.4567 | -266354.9822 | 19.328 | 178.8287 | 198.1566 | 0.67899 | 8.1432 | 8.8222 | 189.3344 | -266165.6478 | FALSE | 724 | 18227.5 | -18543.738 | 7.5684 | 73.0782 | 80.6467 | 117.51 | -18426.228 | FALSE | Option 1 | 0 | 774
| CDN001-162435922 | 13 | 278511.1277 | -150548.4682 | 181.5642 | 1793.3242 | 1974.8884 | 6.3784 | 81.6616 | 88.04 | 1886.8484 | -148661.6198 | FALSE | 492 | 10302.5 | -10481.2432 | 71.097 | 732.8407 | 803.9377 | 1170.9508 | -9310.2924 | FALSE | Option 1 | 0 | 774
| CDN001-164044162 | 1 | 21423.9329 | -11580.6514 | 0 | 92.1529 | 92.1529 | 0 | 4.1963 | 4.1963 | 87.9566 | -11492.6948 | FALSE | 225 | 792.5 | -806.2495 | 0 | 37.6582 | 37.6582 | 54.4947 | -751.7548 | FALSE | Option 1 | 0 | 774
| CDN001-164044516 | 102 | 2185241.156 | -1181226.443 | 2071.1084 | 28832.8497 | 30903.9581 | 72.7584 | 1312.9459 | 1385.7042 | 29518.2538 | -1151708.1892 | FALSE | 1718 | 80835 | -82237.4466 | 811.0053 | 11782.5242 | 12593.5295 | 18310.4286 | -63927.018 | FALSE | Option 1 | 0 | 774
| CDN001-171348505 | 13 | 278511.1277 | -150548.4682 | 99.9592 | 2221.4238 | 2321.383 | 3.5116 | 101.1558 | 104.6674 | 2216.7157 | -148331.7526 | FALSE | 491 | 10302.5 | -10481.2432 | 39.1421 | 907.7833 | 946.9254 | 1374.4577 | -9106.7855 | FALSE | Option 1 | 0 | 774
| CDN001-177002783 | 16 | 342782.9264 | -185290.4224 | 416.8376 | 4560.6116 | 4977.4492 | 14.6436 | 207.6741 | 222.3177 | 4755.1315 | -180535.2909 | FALSE | 551 | 12680 | -12899.9916 | 163.2254 | 1863.6908 | 2026.9162 | 2950.533 | -9949.4586 | FALSE | Option 1 | 0 | 774
| CDN001-178141597 | 1 | 21423.9329 | -11580.6514 | 0.1611 | 0.013433 | 0.17454 | 0.0056596 | 0.00061169 | 0.0062713 | 0.16827 | -11580.4831 | FALSE | 232 | 792.5 | -806.2495 | 0.063086 | 0.0054894 | 0.068575 | 0.10596 | -806.1435 | FALSE | Option 1 | 0 | 774
| CDN001-202076817 | 312 | 6684267.0653 | -3613163.2374 | 16014.1216 | 119410.1832 | 135424.3049 | 562.5787 | 5437.5168 | 6000.0955 | 129424.2094 | -3483739.0281 | FALSE | 2171 | 247260 | -251549.8367 | 6270.8152 | 48796.8891 | 55067.7042 | 80356.6006 | -171193.2361 | FALSE | Option 1 | 0 | 774
| CDN002-15400044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| CDN002-162961049 | 26 | 557022.2554 | -301096.9365 | 95.4719 | 1561.4307 | 1656.9026 | 3.3539 | 71.102 | 74.456 | 1582.4467 | -299514.4898 | FALSE | 787 | 20605 | -20962.4864 | 37.3849 | 638.0776 | 675.4625 | 981.4401 | -19981.0463 | FALSE | Option 1 | 0 | 774
| CDN002-162961261 | 7 | 149967.5303 | -81064.5598 | 4.3181 | 44.3602 | 48.6784 | 0.1517 | 2.02 | 2.1717 | 46.5066 | -81018.0532 | FALSE | 355 | 5547.5 | -5643.7463 | 1.6909 | 18.1278 | 19.8187 | 28.8597 | -5614.8867 | FALSE | Option 1 | 0 | 774
| CDN002-162961458 | 5 | 107119.6645 | -57903.257 | 27.0376 | 595.1962 | 622.2338 | 0.94984 | 27.1031 | 28.053 | 594.1809 | -57309.0761 | FALSE | 306 | 3962.5 | -4031.2474 | 10.5874 | 243.2265 | 253.8139 | 368.4199 | -3662.8275 | FALSE | Option 1 | 0 | 774
| CDN002-163179235 | 29 | 621294.0541 | -335838.8907 | 518.8916 | 11042.5476 | 11561.4392 | 18.2287 | 502.8385 | 521.0673 | 11040.3719 | -324798.5188 | FALSE | 829 | 22982.5 | -23381.2348 | 203.1877 | 4512.5295 | 4715.7172 | 6845.722 | -16535.5129 | FALSE | Option 1 | 0 | 774
| CDN002-163194789 | 8 | 171391.4632 | -92645.2112 | 0.50514 | 35.5884 | 36.0935 | 0.017746 | 1.6206 | 1.6383 | 34.4552 | -92610.756 | FALSE | 372 | 6340 | -6449.9958 | 0.1978 | 14.5432 | 14.741 | 21.3525 | -6428.6433 | FALSE | Option 1 | 0 | 774
| CDN002-163309826 | 22 | 471326.5238 | -254774.3308 | 528.8907 | 20491.8637 | 21020.7544 | 18.58 | 933.1269 | 951.7069 | 20069.0475 | -234705.2833 | FALSE | 665 | 17435 | -17737.4885 | 207.1032 | 8373.986 | 8581.0892 | 12439.6652 | -5297.8233 | FALSE | Option 1 | 0 | 774
| CDN002-85030215 | 228 | 4884656.7016 | -2640388.5197 | 11636.1325 | 188561.3105 | 200197.4431 | 408.7792 | 8586.4143 | 8995.1935 | 191202.2496 | -2449186.2701 | FALSE | 2069 | 180690 | -183824.8807 | 4556.4807 | 77055.4496 | 81611.9303 | 118585.5128 | -65239.3679 | FALSE | Option 1 | 0 | 774
| CDN003-15400133 | 202 | 4327634.4461 | -2339291.5832 | 18016.5382 | 35558.911 | 53575.4492 | 632.9239 | 1619.2269 | 2252.1508 | 51323.2985 | -2287968.2848 | FALSE | 2050 | 160085 | -162862.3943 | 7054.9221 | 14531.1245 | 21586.0466 | 31989.4026 | -130872.9917 | FALSE | Option 1 | 0 | 774
| CDN004-139244393 | 68 | 1456827.4373 | -787484.2953 | 31.4052 | 2308.8949 | 2340.3001 | 1.1033 | 105.1389 | 106.2422 | 2234.0579 | -785250.2374 | FALSE | 1454 | 53890 | -54824.9644 | 12.2977 | 943.5283 | 955.826 | 1384.4741 | -53440.4903 | FALSE | Option 1 | 0 | 774
| CDN004-139244670 | 185 | 3963427.5868 | -2142420.5094 | 1523.9603 | 79952.7646 | 81476.7249 | 53.537 | 3640.7657 | 3694.3027 | 77782.4222 | -2064638.0872 | FALSE | 2010 | 146612.5 | -149156.1532 | 596.7529 | 32672.6421 | 33269.395 | 48207.3299 | -100948.8233 | FALSE | Option 1 | 0 | 774
| CDN004-139351301 | 30 | 642717.987 | -347419.5421 | 47.9944 | 2767.4932 | 2815.4877 | 1.6861 | 126.0218 | 127.7079 | 2687.7798 | -344731.7623 | FALSE | 863 | 23775 | -24187.4843 | 18.7937 | 1130.9342 | 1149.7279 | 1665.7598 | -22521.7245 | FALSE | Option 1 | 0 | 774
| CDN004-142953493 | 29 | 621294.0541 | -335838.8907 | 142.0764 | 4454.7097 | 4596.7861 | 4.9912 | 202.8517 | 207.8429 | 4388.9432 | -331449.9475 | FALSE | 840 | 22982.5 | -23381.2348 | 55.6343 | 1820.414 | 1876.0484 | 2720.7377 | -20660.4971 | FALSE | Option 1 | 0 | 774
| CDN004-15399970 | 220 | 4713265.2384 | -2547743.3085 | 30156.5961 | 157876.5794 | 188033.1755 | 1059.4061 | 7189.1403 | 8248.5464 | 179784.6291 | -2367958.6793 | FALSE | 2064 | 174350 | -177374.8849 | 11808.7301 | 64516.1553 | 76324.8855 | 111708.2901 | -65666.5948 | FALSE | Option 1 | 0 | 774
| CDN004-159428859 | 50 | 1071196.6451 | -579032.5701 | 27.0609 | 4681.2182 | 4708.2791 | 0.95065 | 213.1661 | 214.1168 | 4494.1623 | -574538.4078 | FALSE | 1210 | 39625 | -40312.4738 | 10.5965 | 1912.9766 | 1923.5731 | 2784.706 | -37527.7679 | FALSE | Option 1 | 0 | 774
| CDN004-159428956 | 65 | 1392555.6386 | -752742.3411 | 103.2165 | 4463.8227 | 4567.0392 | 3.626 | 203.2667 | 206.8927 | 4360.1465 | -748382.1946 | FALSE | 1413 | 51512.5 | -52406.216 | 40.4176 | 1824.1381 | 1864.5556 | 2702.4836 | -49703.7324 | FALSE | Option 1 | 0 | 774
| CDN004-159429052 | 27 | 578446.1883 | -312677.5879 | 8.3798 | 489.2446 | 497.6244 | 0.29438 | 22.2785 | 22.5728 | 475.0515 | -312202.5363 | FALSE | 803 | 21397.5 | -21768.7359 | 3.2814 | 199.9295 | 203.2108 | 294.4135 | -21474.3223 | FALSE | Option 1 | 0 | 774
| CDN004-162436765 | 93 | 1992425.7599 | -1077000.5804 | 61.009 | 2804.3144 | 2865.3234 | 2.1433 | 127.6985 | 129.8418 | 2735.4816 | -1074265.0988 | FALSE | 1667 | 73702.5 | -74981.2013 | 23.8899 | 1145.9811 | 1169.8711 | 1695.4523 | -73285.749 | FALSE | Option 1 | 0 | 774
| CDN004-202037935 | 218 | 4670417.3726 | -2524582.0056 | 8091.2748 | 83084.4172 | 91175.6921 | 284.2478 | 3783.3701 | 4067.6179 | 87108.0742 | -2437473.9315 | FALSE | 2067 | 172765 | -175762.3859 | 3168.3841 | 33952.3898 | 37120.774 | 54054.9181 | -121707.4678 | FALSE | Option 1 | 0 | 774
| CDN004-202768387 | 608 | 13025751.2042 | -7041036.0524 | 25562.1021 | 551330.0427 | 576892.1448 | 898.0008 | 25105.6176 | 26003.6183 | 550888.5265 | -6490147.5259 | FALSE | 2226 | 481840 | -490199.6819 | 10009.6166 | 225300.6419 | 235310.2585 | 341581.8863 | -148617.7955 | FALSE | Option 1 | 0 | 774
| CDN006-143338433 | 65 | 1392555.6386 | -752742.3411 | 377.4164 | 11166.2828 | 11543.6992 | 13.2587 | 508.473 | 521.7317 | 11021.9675 | -741720.3736 | FALSE | 1404 | 51512.5 | -52406.216 | 147.7888 | 4563.0938 | 4710.8826 | 6832.8166 | -45573.3994 | FALSE | Option 1 | 0 | 774
| CDN006-143338709 | 118 | 2528024.0824 | -1366516.8654 | 79.4465 | 2690.1957 | 2769.6423 | 2.791 | 122.502 | 125.293 | 2644.3493 | -1363872.5161 | FALSE | 1828 | 93515 | -95137.4383 | 31.1097 | 1099.3466 | 1130.4563 | 1639.1859 | -93498.2523 | FALSE | Option 1 | 0 | 774
| CDN006-143338924 | 47 | 1006924.8464 | -544290.6159 | 5.6249 | 290.789 | 296.4139 | 0.1976 | 13.2415 | 13.4391 | 282.9748 | -544007.6411 | FALSE | 1169 | 37247.5 | -37893.7254 | 2.2026 | 118.8307 | 121.0333 | 175.3806 | -37718.3448 | FALSE | Option 1 | 0 | 774
| CDN006-143339149 | 16 | 342782.9264 | -185290.4224 | 89.8941 | 2711.7055 | 2801.5996 | 3.158 | 123.4815 | 126.6395 | 2674.9601 | -182615.4623 | FALSE | 552 | 12680 | -12899.9916 | 35.2007 | 1108.1366 | 1143.3373 | 1658.2622 | -11241.7294 | FALSE | Option 1 | 0 | 774
| CDN006-15399920 | 304 | 6512875.6021 | -3520518.0262 | 33897.7727 | 188116.3865 | 222014.1592 | 1190.8342 | 8566.154 | 9756.9882 | 212257.171 | -3308260.8553 | FALSE | 2154 | 240920 | -245099.8409 | 13273.7013 | 76873.6317 | 90147.333 | 131866.8262 | -113233.0147 | FALSE | Option 1 | 0 | 774
| CDN006-158379713 | 120 | 2570871.9482 | -1389678.1682 | 311.2697 | 14087.3723 | 14398.642 | 10.935 | 641.489 | 652.424 | 13746.218 | -1375931.9502 | FALSE | 1836 | 95100 | -96749.9372 | 121.8871 | 5756.795 | 5878.6821 | 8519.9599 | -88229.9773 | FALSE | Option 1 | 0 | 774
| CDN006-158379840 | 43 | 921229.1148 | -497968.0103 | 85.1866 | 3453.7433 | 3538.9299 | 2.9926 | 157.2712 | 160.2639 | 3378.666 | -494589.3443 | FALSE | 1089 | 34077.5 | -34668.7275 | 33.3574 | 1411.3698 | 1444.7272 | 2094.2027 | -32574.5248 | FALSE | Option 1 | 0 | 774
| CDN006-160451043 | 78 | 1671066.7663 | -903290.8094 | 280.3972 | 10692.7627 | 10973.1599 | 9.8504 | 486.9105 | 496.7609 | 10476.3989 | -892814.4104 | FALSE | 1558 | 61815 | -62887.4592 | 109.798 | 4369.5901 | 4479.3881 | 6493.7717 | -56393.6874 | FALSE | Option 1 | 0 | 774
| CDN006-162450281 | 21 | 449902.5909 | -243193.6794 | 0.40468 | 18.6977 | 19.1024 | 0.014217 | 0.85143 | 0.86565 | 18.2368 | -243175.4427 | FALSE | 684 | 16642.5 | -16931.239 | 0.15847 | 7.6408 | 7.7993 | 11.3031 | -16919.9359 | FALSE | Option 1 | 0 | 774
| CDN006-162451240 | 22 | 471326.5238 | -254774.3308 | 12.4941 | 1209.2142 | 1221.7084 | 0.43892 | 55.0633 | 55.5023 | 1166.2061 | -253608.1247 | FALSE | 697 | 17435 | -17737.4885 | 4.8925 | 494.1446 | 499.037 | 722.6714 | -17014.8171 | FALSE | Option 1 | 0 | 774
| CDN006-162572514 | 25 | 535598.3225 | -289516.2851 | 1.3701 | 226.0731 | 227.4432 | 0.048131 | 10.2946 | 10.3427 | 217.1005 | -289299.1846 | FALSE | 764 | 19812.5 | -20156.2369 | 0.53649 | 92.3846 | 92.9211 | 134.5221 | -20021.7148 | FALSE | Option 1 | 0 | 774
| CDN006-162572817 | 7 | 149967.5303 | -81064.5598 | 1.1357 | 26.2213 | 27.357 | 0.039898 | 1.194 | 1.2339 | 26.1231 | -81038.4367 | FALSE | 356 | 5547.5 | -5643.7463 | 0.44472 | 10.7153 | 11.16 | 16.197 | -5627.5494 | FALSE | Option 1 | 0 | 774
| CDN006-162588679 | 20 | 428478.658 | -231613.028 | 68.3531 | 2576.2534 | 2644.6065 | 2.4013 | 117.3135 | 119.7147 | 2524.8918 | -229088.1362 | FALSE | 654 | 15850 | -16124.9895 | 26.7657 | 1052.7842 | 1079.5499 | 1565.0566 | -14559.9329 | FALSE | Option 1 | 0 | 774
| CDN006-162675220 | 27 | 578446.1883 | -312677.5879 | 0.30704 | 10.9393 | 11.2464 | 0.010786 | 0.49814 | 0.50893 | 10.7375 | -312666.8504 | FALSE | 807 | 21397.5 | -21768.7359 | 0.12023 | 4.4704 | 4.5906 | 6.6558 | -21762.0801 | FALSE | Option 1 | 0 | 774
| CDN006-162675596 | 11 | 235663.2619 | -127387.1654 | 0.091311 | 6.6293 | 6.7206 | 0.0032078 | 0.30187 | 0.30508 | 6.4155 | -127380.7499 | FALSE | 452 | 8717.5 | -8868.7442 | 0.035755 | 2.709 | 2.7448 | 3.9758 | -8864.7685 | FALSE | Option 1 | 0 | 774
| CDN006-183157401 | 11 | 235663.2619 | -127387.1654 | 3.2303 | 58.5888 | 61.8191 | 0.11348 | 2.6679 | 2.7814 | 59.0377 | -127328.1277 | FALSE | 450 | 8717.5 | -8868.7442 | 1.2649 | 23.9423 | 25.2072 | 36.6119 | -8832.1323 | FALSE | Option 1 | 0 | 774
| CDN006-202038054 | 709 | 15189568.4272 | -8210681.8441 | 23648.2028 | 425563.5722 | 449211.7751 | 830.7652 | 19378.6579 | 20209.4231 | 429002.352 | -7781679.4921 | FALSE | 2236 | 561882.5 | -571630.879 | 9260.1713 | 173906.2604 | 183166.4317 | 266045.3433 | -305585.5357 | FALSE | Option 1 | 0 | 774
| CDN006-202248649 | 316 | 6769962.7969 | -3659485.843 | 27643.7343 | 204212.2948 | 231856.0291 | 971.1288 | 9299.1047 | 10270.2335 | 221585.7956 | -3437900.0475 | FALSE | 2166 | 250430 | -254774.8347 | 10824.7428 | 83451.2135 | 94275.9563 | 137580.0727 | -117194.7619 | FALSE | Option 1 | 0 | 774
| CHA003-155052833 | 9 | 192815.3961 | -104225.8626 | 5.4282 | 119.7404 | 125.1685 | 0.19069 | 4.2065 | 4.3972 | 120.7714 | -104105.0913 | FALSE | 386 | 7132.5 | -7256.2453 | 2.1256 | 46.888 | 49.0135 | 76.155 | -7180.0903 | FALSE | Option 1 | 0 | 774
| CHA003-155052965 | 5 | 107119.6645 | -57903.257 | 16.6103 | 1628.4877 | 1645.098 | 0.58352 | 57.209 | 57.7926 | 1587.3054 | -56315.9516 | FALSE | 305 | 3962.5 | -4031.2474 | 6.5043 | 637.6838 | 644.188 | 1000.91 | -3030.3374 | FALSE | Option 1 | 0 | 774
| CHA005-155053189 | 7 | 149967.5303 | -81064.5598 | 8.8958 | 102.4386 | 111.3344 | 0.31251 | 3.5987 | 3.9112 | 107.4232 | -80957.1366 | FALSE | 354 | 5547.5 | -5643.7463 | 3.4834 | 40.1129 | 43.5964 | 67.738 | -5576.0083 | FALSE | Option 1 | 0 | 774
| CHA005-56709738 | 111 | 2378056.5521 | -1285452.3056 | 4011.7187 | 67971.6478 | 71983.3665 | 140.9323 | 2387.8549 | 2528.7873 | 69454.5792 | -1215997.7264 | FALSE | 1761 | 87967.5 | -89493.6919 | 1570.9102 | 26616.3609 | 28187.271 | 43796.0955 | -45697.5965 | FALSE | Option 1 | 0 | 774
| CHA006-120251163 | 114 | 2442328.3508 | -1320194.2598 | 2953.2026 | 95262.2966 | 98215.4992 | 103.7465 | 3346.5798 | 3450.3263 | 94765.1729 | -1225429.0869 | FALSE | 1763 | 90345 | -91912.4403 | 1156.4161 | 37302.8423 | 38459.2584 | 59756.2408 | -32156.1996 | FALSE | Option 1 | 0 | 774
| CHA006-130745345 | 29 | 621294.0541 | -335838.8907 | 14.5545 | 301.7291 | 316.2836 | 0.5113 | 10.5998 | 11.1111 | 305.1725 | -335533.7182 | FALSE | 846 | 22982.5 | -23381.2348 | 5.6992 | 118.1512 | 123.8504 | 192.4331 | -23188.8017 | FALSE | Option 1 | 0 | 774
| CHA006-138134893 | 15 | 321358.9935 | -173709.771 | 5.654 | 60.6252 | 66.2791 | 0.19862 | 2.1298 | 2.3284 | 63.9507 | -173645.8203 | FALSE | 539 | 11887.5 | -12093.7422 | 2.214 | 23.7396 | 25.9536 | 40.3255 | -12053.4166 | FALSE | Option 1 | 0 | 774
| CHA006-155505830 | 129 | 2763687.3443 | -1493904.0309 | 217.214 | 12276.4952 | 12493.7092 | 7.6308 | 431.2753 | 438.906 | 12054.8032 | -1481849.2277 | FALSE | 1876 | 102232.5 | -104006.1825 | 85.0567 | 4807.2341 | 4892.2909 | 7601.4183 | -96404.7642 | FALSE | Option 1 | 0 | 774
| CHA006-155506079 | 82 | 1756762.4979 | -949613.415 | 2576.7477 | 71742.0358 | 74318.7835 | 90.5216 | 2520.3093 | 2610.8309 | 71707.9527 | -877905.4623 | FALSE | 1544 | 64985 | -66112.4571 | 1009.0037 | 28092.7707 | 29101.7744 | 45217.0091 | -20895.448 | FALSE | Option 1 | 0 | 774
| CHA006-155506186 | 102 | 2185241.156 | -1181226.443 | 256.499 | 11104.1686 | 11360.6677 | 9.0109 | 390.0912 | 399.1021 | 10961.5656 | -1170264.8774 | FALSE | 1731 | 80835 | -82237.4466 | 100.44 | 4348.1741 | 4448.6141 | 6912.0536 | -75325.393 | FALSE | Option 1 | 0 | 774
| CHA006-155506347 | 42 | 899805.1819 | -486387.3589 | 311.5688 | 6128.5161 | 6440.0849 | 10.9455 | 215.2958 | 226.2412 | 6213.8437 | -480173.5152 | FALSE | 1072 | 33285 | -33862.478 | 122.0042 | 2399.8064 | 2521.8106 | 3918.2743 | -29944.2037 | FALSE | Option 1 | 0 | 774
| CHA006-155506472 | 23 | 492750.4567 | -266354.9822 | 502.4595 | 15695.5375 | 16197.997 | 17.6515 | 551.3868 | 569.0382 | 15628.9588 | -250726.0235 | FALSE | 692 | 18227.5 | -18543.738 | 196.7533 | 6146.0639 | 6342.8172 | 9855.1799 | -8688.5581 | FALSE | Option 1 | 0 | 774
| CHA006-155506614 | 48 | 1028348.7793 | -555871.2673 | 4.3661 | 569.2838 | 573.6499 | 0.15338 | 19.999 | 20.1524 | 553.4975 | -555317.7698 | FALSE | 1185 | 38040 | -38699.9749 | 1.7097 | 222.9204 | 224.63 | 349.0199 | -38350.955 | FALSE | Option 1 | 0 | 774
| CHA006-155618024 | 25 | 535598.3225 | -289516.2851 | 12.246 | 297.019 | 309.2651 | 0.4302 | 10.4343 | 10.8645 | 298.4005 | -289217.8845 | FALSE | 763 | 19812.5 | -20156.2369 | 4.7953 | 116.3068 | 121.1021 | 188.1629 | -19968.074 | FALSE | Option 1 | 0 | 774
| CHA006-155618314 | 209 | 4477601.9764 | -2420356.143 | 526.9586 | 67990.4871 | 68517.4457 | 18.5121 | 2388.5168 | 2407.0289 | 66110.4168 | -2354245.7263 | FALSE | 2061 | 165632.5 | -168506.1406 | 206.3466 | 26623.7379 | 26830.0846 | 41687.3611 | -126818.7795 | FALSE | Option 1 | 0 | 774
| CHA006-155668372 | 34 | 728413.7187 | -393742.1477 | 72.8782 | 4206.9505 | 4279.8286 | 2.5602 | 147.7908 | 150.3511 | 4129.4776 | -389612.6701 | FALSE | 941 | 26945 | -27412.4822 | 28.5377 | 1647.3591 | 1675.8967 | 2603.9319 | -24808.5503 | FALSE | Option 1 | 0 | 774
| CHA006-155668704 | 32 | 685565.8529 | -370580.8449 | 83.9872 | 4056.0302 | 4140.0174 | 2.9505 | 142.489 | 145.4395 | 3994.5779 | -366586.267 | FALSE | 905 | 25360 | -25799.9833 | 32.8877 | 1588.2617 | 1621.1494 | 2518.868 | -23281.1153 | FALSE | Option 1 | 0 | 774
| CHA006-155668831 | 85 | 1821034.2966 | -984355.3692 | 465.5457 | 19906.0467 | 20371.5924 | 16.3547 | 699.3026 | 715.6573 | 19655.9351 | -964699.4341 | FALSE | 1601 | 67362.5 | -68531.2055 | 182.2985 | 7794.8165 | 7977.1151 | 12394.4774 | -56136.7282 | FALSE | Option 1 | 0 | 774
| CHA006-155727138 | 26 | 557022.2554 | -301096.9365 | 53.8781 | 1902.6985 | 1956.5766 | 1.8927 | 66.8421 | 68.7349 | 1887.8417 | -299209.0947 | FALSE | 785 | 20605 | -20962.4864 | 21.0976 | 745.0593 | 766.1569 | 1190.4197 | -19772.0667 | FALSE | Option 1 | 0 | 774
| CHA006-156354256 | 25 | 535598.3225 | -289516.2851 | 105.6998 | 1560.5523 | 1666.2521 | 3.7133 | 54.8225 | 58.5357 | 1607.7164 | -287908.5687 | FALSE | 759 | 19812.5 | -20156.2369 | 41.39 | 611.0816 | 652.4716 | 1013.7805 | -19142.4564 | FALSE | Option 1 | 0 | 774
| CHA006-164004018 | 12 | 257087.1948 | -138967.8168 | 507.7246 | 6896.2012 | 7403.9258 | 17.8364 | 242.2647 | 260.1011 | 7143.8247 | -131823.9921 | FALSE | 460 | 9510 | -9674.9937 | 198.815 | 2700.4168 | 2899.2318 | 4504.694 | -5170.2997 | FALSE | Option 1 | 0 | 774
| CHA006-164004212 | 12 | 257087.1948 | -138967.8168 | 43.7463 | 713.029 | 756.7753 | 1.5368 | 25.0488 | 26.5856 | 730.1897 | -138237.6272 | FALSE | 466 | 9510 | -9674.9937 | 17.1302 | 279.2081 | 296.3383 | 460.437 | -9214.5568 | FALSE | Option 1 | 0 | 774
| CHA006-164004465 | 10 | 214239.329 | -115806.514 | 15.8786 | 269.5989 | 285.4775 | 0.55782 | 9.4711 | 10.0289 | 275.4487 | -115531.0653 | FALSE | 414 | 7925 | -8062.4948 | 6.2178 | 105.5696 | 111.7874 | 173.6902 | -7888.8046 | FALSE | Option 1 | 0 | 774
| CHA006-164281123 | 9 | 192815.3961 | -104225.8626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -104225.8626 | FALSE | 394 | 7132.5 | -7256.2453 | 0 | 0 | 0 | 0 | -7256.2453 | FALSE | Option 1 | 0 | 774
| CHA006-181783097 | 8 | 171391.4632 | -92645.2112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -92645.2112 | FALSE | 377 | 6340 | -6449.9958 | 0 | 0 | 0 | 0 | -6449.9958 | FALSE | Option 1 | 0 | 774
| CHA006-56709766 | 112 | 2399480.485 | -1297032.957 | 629.1993 | 8617.3799 | 9246.5792 | 22.1039 | 302.7299 | 324.8338 | 8921.7454 | -1288111.2116 | FALSE | 1800 | 88760 | -90299.9414 | 246.3821 | 3374.3965 | 3620.7786 | 5625.8006 | -84674.1408 | FALSE | Option 1 | 0 | 774
| CHA007-162618256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| CHA008-162618131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| CHM011-15436218 | 6 | 128543.5974 | -69483.9084 | 0.09645 | 5.3538 | 5.4503 | 0.0033883 | 0.18808 | 0.19147 | 5.2588 | -69478.6496 | FALSE | 329 | 4755 | -4837.4969 | 0.037768 | 2.0965 | 2.1342 | 3.3161 | -4834.1808 | FALSE | Option 1 | 0 | 774
| CHM011-159371854 | 31 | 664141.92 | -359000.1935 | 434.825 | 26709.3005 | 27144.1255 | 15.2755 | 938.302 | 953.5775 | 26190.548 | -332809.6455 | FALSE | 843 | 24567.5 | -24993.7338 | 170.2689 | 10458.8369 | 10629.1059 | 16515.0197 | -8478.7141 | FALSE | Option 1 | 0 | 774
| CHM011-159371937 | 84 | 1799610.3637 | -972774.7178 | 60.0941 | 10771.5201 | 10831.6142 | 2.1111 | 378.4052 | 380.5164 | 10451.0979 | -962323.6199 | FALSE | 1600 | 66570 | -67724.956 | 23.5317 | 4217.9155 | 4241.4472 | 6590.1671 | -61134.789 | FALSE | Option 1 | 0 | 774
| CHM011-159372116 | 38 | 814109.4503 | -440064.7533 | 142.0675 | 10697.0089 | 10839.0765 | 4.9909 | 375.7876 | 380.7785 | 10458.298 | -429606.4553 | FALSE | 1004 | 30115 | -30637.4801 | 55.6309 | 4188.7384 | 4244.3692 | 6594.7072 | -24042.7729 | FALSE | Option 1 | 0 | 774
| CHM011-159372219 | 117 | 2506600.1495 | -1354936.214 | 1079.6461 | 83434.9484 | 84514.5945 | 37.9281 | 2931.0832 | 2969.0113 | 81545.5832 | -1273390.6309 | FALSE | 1789 | 92722.5 | -94331.1888 | 422.7682 | 32671.4853 | 33094.2535 | 51420.341 | -42910.8478 | FALSE | Option 1 | 0 | 774
| CHM011-159372384 | 67 | 1435403.5044 | -775903.6439 | 153.6181 | 8158.5299 | 8312.1479 | 5.3966 | 286.6105 | 292.0071 | 8020.1408 | -767883.5031 | FALSE | 1438 | 53097.5 | -54018.7149 | 60.1538 | 3194.7199 | 3254.8737 | 5057.2742 | -48961.4407 | FALSE | Option 1 | 0 | 774
| CHM011-159372472 | 25 | 535598.3225 | -289516.2851 | 47.3638 | 2737.4833 | 2784.8471 | 1.6639 | 96.1682 | 97.8321 | 2687.015 | -286829.27 | FALSE | 757 | 19812.5 | -20156.2369 | 18.5467 | 1071.9446 | 1090.4914 | 1694.3557 | -18461.8812 | FALSE | Option 1 | 0 | 774
| CHM011-159372815 | 30 | 642717.987 | -347419.5421 | 4.0607 | 307.1823 | 311.243 | 0.14265 | 10.7914 | 10.934 | 300.3089 | -347119.2331 | FALSE | 867 | 23775 | -24187.4843 | 1.5901 | 120.2865 | 121.8766 | 189.3663 | -23998.118 | FALSE | Option 1 | 0 | 774
| CHM011-159372981 | 22 | 471326.5238 | -254774.3308 | 206.0652 | 8982.6651 | 9188.7303 | 7.2391 | 315.5625 | 322.8016 | 8865.9287 | -245908.4021 | FALSE | 689 | 17435 | -17737.4885 | 80.6911 | 3517.4351 | 3598.1261 | 5590.6042 | -12146.8843 | FALSE | Option 1 | 0 | 774
| CHM011-159373200 | 78 | 1671066.7663 | -903290.8094 | 922.3393 | 52516.4535 | 53438.7928 | 32.4019 | 1844.9115 | 1877.3134 | 51561.4794 | -851729.33 | FALSE | 1516 | 61815 | -62887.4592 | 361.1699 | 20564.4106 | 20925.5806 | 32513.2122 | -30374.247 | FALSE | Option 1 | 0 | 774
| CHM011-159373315 | 27 | 578446.1883 | -312677.5879 | 50.4963 | 2909.2122 | 2959.7085 | 1.7739 | 102.2011 | 103.975 | 2855.7335 | -309821.8544 | FALSE | 801 | 21397.5 | -21768.7359 | 19.7734 | 1139.1903 | 1158.9637 | 1800.7448 | -19967.991 | FALSE | Option 1 | 0 | 774
| CHM011-159373411 | 33 | 706989.7858 | -382161.4963 | 82.1017 | 6833.1791 | 6915.2808 | 2.8842 | 240.0507 | 242.9349 | 6672.3459 | -375489.1504 | FALSE | 919 | 26152.5 | -26606.2327 | 32.1494 | 2675.7386 | 2707.888 | 4207.3928 | -22398.8399 | FALSE | Option 1 | 0 | 774
| CHM011-160317885 | 74 | 1585371.0347 | -856968.2038 | 403.6579 | 34528.7104 | 34932.3683 | 14.1806 | 1212.9992 | 1227.1797 | 33705.1886 | -823263.0152 | FALSE | 1488 | 58645 | -59662.4613 | 158.0645 | 13520.7641 | 13678.8286 | 21253.5397 | -38408.9216 | FALSE | Option 1 | 0 | 774
| CHM011-160318163 | 12 | 257087.1948 | -138967.8168 | 1.5362 | 30.0808 | 31.617 | 0.053968 | 1.0567 | 1.1107 | 30.5063 | -138937.3106 | FALSE | 473 | 9510 | -9674.9937 | 0.60155 | 11.779 | 12.3806 | 19.2364 | -9655.7573 | FALSE | Option 1 | 0 | 774
| CHM011-160318338 | 60 | 1285435.9741 | -694839.0841 | 33.5651 | 3103.5282 | 3137.0932 | 1.1791 | 109.0274 | 110.2066 | 3026.8866 | -691812.1975 | FALSE | 1354 | 47550 | -48374.9686 | 13.1434 | 1215.2806 | 1228.424 | 1908.6692 | -46466.2994 | FALSE | Option 1 | 0 | 774
| CHM011-160677964 | 65 | 1392555.6386 | -752742.3411 | 570.1246 | 33164.1519 | 33734.2765 | 20.0286 | 1165.062 | 1185.0906 | 32549.1859 | -720193.1552 | FALSE | 1383 | 51512.5 | -52406.216 | 223.2496 | 12986.4298 | 13209.6794 | 20524.5971 | -31881.6189 | FALSE | Option 1 | 0 | 774
| CHM011-160678238 | 83 | 1778186.4308 | -961194.0664 | 502.1884 | 77086.1912 | 77588.3796 | 17.642 | 2708.0503 | 2725.6923 | 74862.6873 | -886331.3791 | FALSE | 1551 | 65777.5 | -66918.7066 | 196.6471 | 30185.4369 | 30382.0839 | 47206.2956 | -19712.4109 | FALSE | Option 1 | 0 | 774
| CHM011-160721783 | 32 | 685565.8529 | -370580.8449 | 2.8411 | 193.9954 | 196.8365 | 0.099808 | 6.8151 | 6.9149 | 189.9216 | -370390.9233 | FALSE | 909 | 25360 | -25799.9833 | 1.1125 | 75.9648 | 77.0773 | 119.7592 | -25680.2241 | FALSE | Option 1 | 0 | 774
| CHM011-163177271 | 34 | 728413.7187 | -393742.1477 | 78.0156 | 7357.2877 | 7435.3032 | 2.7407 | 258.4627 | 261.2034 | 7174.0998 | -386568.0478 | FALSE | 938 | 26945 | -27412.4822 | 30.5494 | 2880.9692 | 2911.5186 | 4523.7847 | -22888.6975 | FALSE | Option 1 | 0 | 774
| CHM011-163198394 | 40 | 856957.3161 | -463226.0561 | 226.614 | 14789.8367 | 15016.4507 | 7.961 | 519.5693 | 527.5303 | 14488.9204 | -448737.1357 | FALSE | 1031 | 31700 | -32249.9791 | 88.7376 | 5791.4093 | 5880.1468 | 9136.3038 | -23113.6752 | FALSE | Option 1 | 0 | 774
| CHM011-164238923 | 19 | 407054.7251 | -220032.3766 | 2.6747 | 140.9511 | 143.6258 | 0.093962 | 4.9516 | 5.0456 | 138.5802 | -219893.7964 | FALSE | 633 | 15057.5 | -15318.7401 | 1.0474 | 55.1937 | 56.241 | 87.3848 | -15231.3553 | FALSE | Option 1 | 0 | 774
| CHM011-164366730 | 19 | 407054.7251 | -220032.3766 | 102.0253 | 10754.9095 | 10856.9348 | 3.5842 | 377.8217 | 381.4059 | 10475.5289 | -209556.8477 | FALSE | 611 | 15057.5 | -15318.7401 | 39.9511 | 4211.4111 | 4251.3622 | 6605.5726 | -8713.1675 | FALSE | Option 1 | 0 | 774
| CLC001-15400682 | 169 | 3620644.6604 | -1957130.0869 | 37730.7131 | 25449.223 | 63179.9361 | 1325.486 | 1158.8675 | 2484.3535 | 60695.5826 | -1896434.5044 | FALSE | 1979 | 133932.5 | -136256.1616 | 14774.6054 | 10399.8074 | 25174.4128 | 38005.5232 | -98250.6383 | FALSE | Option 1 | 0 | 774
| CLC001-15400693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| CLC002-15400645 | 392 | 8398181.6974 | -4539615.3496 | 109918.1195 | 242476.105 | 352394.2245 | 3861.4413 | 11041.5031 | 14902.9443 | 337491.2802 | -4202124.0694 | FALSE | 2195 | 310660 | -316049.7949 | 43041.7744 | 99087.6932 | 142129.4676 | 210264.7569 | -105785.038 | FALSE | Option 1 | 0 | 774
| CLC003-119149948 | 26 | 557022.2554 | -301096.9365 | 85.3957 | 878.1017 | 963.4974 | 3 | 39.9856 | 42.9856 | 920.5118 | -300176.4247 | FALSE | 788 | 20605 | -20962.4864 | 33.4393 | 358.8357 | 392.2749 | 571.2224 | -20391.264 | FALSE | Option 1 | 0 | 774
| CLC003-123633044 | 23 | 492750.4567 | -266354.9822 | 256.5282 | 5832.6971 | 6089.2253 | 9.0119 | 265.6004 | 274.6122 | 5814.6131 | -260540.3692 | FALSE | 713 | 18227.5 | -18543.738 | 100.4514 | 2383.5276 | 2483.9791 | 3605.2463 | -14938.4917 | FALSE | Option 1 | 0 | 774
| CLC003-130014430 | 11 | 235663.2619 | -127387.1654 | 2.7364 | 104.1432 | 106.8797 | 0.096132 | 4.7423 | 4.8384 | 102.0412 | -127285.1242 | FALSE | 449 | 8717.5 | -8868.7442 | 1.0715 | 42.558 | 43.6296 | 63.2501 | -8805.4942 | FALSE | Option 1 | 0 | 774
| CLC003-130014725 | 19 | 407054.7251 | -220032.3766 | 21.4549 | 297.066 | 318.521 | 0.75372 | 13.5273 | 14.2811 | 304.2399 | -219728.1367 | FALSE | 632 | 15057.5 | -15318.7401 | 8.4013 | 121.3958 | 129.7972 | 188.7238 | -15130.0163 | FALSE | Option 1 | 0 | 774
| CLC003-130014949 | 14 | 299935.0606 | -162129.1196 | 69.8363 | 4510.1527 | 4579.989 | 2.4534 | 205.3764 | 207.8297 | 4372.1593 | -157756.9604 | FALSE | 514 | 11095 | -11287.4927 | 27.3465 | 1843.0708 | 1870.4173 | 2709.5717 | -8577.921 | FALSE | Option 1 | 0 | 774
| CLC003-130747301 | 18 | 385630.7922 | -208451.7252 | 108.7376 | 1128.6396 | 1237.3772 | 3.82 | 51.3942 | 55.2142 | 1182.163 | -207269.5622 | FALSE | 600 | 14265 | -14512.4906 | 42.5795 | 461.2178 | 503.7973 | 733.5799 | -13778.9107 | FALSE | Option 1 | 0 | 774
| CLC003-130748256 | 30 | 642717.987 | -347419.5421 | 115.5437 | 3198.2854 | 3313.8291 | 4.0591 | 145.6386 | 149.6977 | 3164.1315 | -344255.4106 | FALSE | 862 | 23775 | -24187.4843 | 45.2447 | 1306.9771 | 1352.2218 | 1961.6074 | -22225.8769 | FALSE | Option 1 | 0 | 774
| CLC003-152030196 | 29 | 621294.0541 | -335838.8907 | 451.0841 | 11313.1013 | 11764.1854 | 15.8467 | 515.1586 | 531.0052 | 11233.1801 | -324605.7105 | FALSE | 828 | 22982.5 | -23381.2348 | 176.6357 | 4623.091 | 4799.7267 | 6964.4587 | -16416.7762 | FALSE | Option 1 | 0 | 774
| CLC003-154876479 | 13 | 278511.1277 | -150548.4682 | 36.5353 | 1095.1473 | 1131.6826 | 1.2835 | 49.8691 | 51.1526 | 1080.53 | -149467.9382 | FALSE | 494 | 10302.5 | -10481.2432 | 14.3065 | 447.5312 | 461.8377 | 669.8449 | -9811.3983 | FALSE | Option 1 | 0 | 774
| CLC003-154908324 | 95 | 2035273.6257 | -1100161.8832 | 1305.7173 | 31206.6744 | 32512.3917 | 45.8701 | 1421.0414 | 1466.9115 | 31045.4802 | -1069116.403 | FALSE | 1665 | 75287.5 | -76593.7003 | 511.2932 | 12752.586 | 13263.8792 | 19248.5125 | -57345.1878 | FALSE | Option 1 | 0 | 774
| CLC003-154908634 | 13 | 278511.1277 | -150548.4682 | 10.1618 | 228.4393 | 238.6011 | 0.35699 | 10.4023 | 10.7593 | 227.8418 | -150320.6264 | FALSE | 498 | 10302.5 | -10481.2432 | 3.9792 | 93.3516 | 97.3307 | 141.2704 | -10339.9728 | FALSE | Option 1 | 0 | 774
| CLC003-154908755 | 10 | 214239.329 | -115806.514 | 4.3376 | 85.7631 | 90.1008 | 0.15238 | 3.9053 | 4.0577 | 86.043 | -115720.471 | FALSE | 418 | 7925 | -8062.4948 | 1.6985 | 35.047 | 36.7456 | 53.3552 | -8009.1396 | FALSE | Option 1 | 0 | 774
| CLC003-154908853 | 16 | 342782.9264 | -185290.4224 | 31.7367 | 439.1054 | 470.842 | 1.1149 | 19.9953 | 21.1102 | 449.7318 | -184840.6906 | FALSE | 558 | 12680 | -12899.9916 | 12.4275 | 179.4401 | 191.8676 | 278.9745 | -12621.0172 | FALSE | Option 1 | 0 | 774
| CLC003-154908977 | 32 | 685565.8529 | -370580.8449 | 808.5488 | 17047.8879 | 17856.4367 | 28.4044 | 776.3004 | 804.7049 | 17051.7318 | -353529.1131 | FALSE | 875 | 25360 | -25799.9833 | 316.6118 | 6966.6077 | 7283.2195 | 10573.2172 | -15226.766 | FALSE | Option 1 | 0 | 774
| CLC003-193886326 | 141 | 3020774.5391 | -1632871.8477 | 7546.1357 | 139583.9982 | 147130.1339 | 265.097 | 6356.1609 | 6621.2579 | 140508.876 | -1492362.9717 | FALSE | 1879 | 111742.5 | -113681.1762 | 2954.9184 | 57040.9047 | 59995.823 | 87134.3109 | -26546.8653 | FALSE | Option 1 | 0 | 774
| CLC003-198593463 | 79 | 1692490.6992 | -914871.4608 | 4346.3755 | 36090.7621 | 40437.1376 | 152.6889 | 1643.4455 | 1796.1344 | 38641.0032 | -876230.4575 | FALSE | 1542 | 62607.5 | -63693.7087 | 1701.9552 | 14748.4651 | 16450.4202 | 23986.7174 | -39706.9913 | FALSE | Option 1 | 0 | 774
| CLC003-24597520 | 118 | 2528024.0824 | -1366516.8654 | 15741.9986 | 68564.2288 | 84306.2274 | 553.0189 | 3122.1722 | 3675.1911 | 80631.0363 | -1285885.8291 | FALSE | 1799 | 93515 | -95137.4383 | 6164.2571 | 28018.7249 | 34182.982 | 50123.2454 | -45014.1928 | FALSE | Option 1 | 0 | 774
| CLC003-24597576 | 141 | 3020774.5391 | -1632871.8477 | 22901.3673 | 110288.9446 | 133190.3119 | 804.5287 | 5022.1679 | 5826.6967 | 127363.6153 | -1505508.2324 | FALSE | 1884 | 111742.5 | -113681.1762 | 8967.7252 | 45069.5012 | 54037.2264 | 79153.0856 | -34528.0907 | FALSE | Option 1 | 0 | 774
| CLC003-24607264 | 556 | 11911706.6933 | -6438842.1795 | 28972.0934 | 634205.6562 | 663177.7495 | 1017.7943 | 28879.4795 | 29897.2738 | 633280.4757 | -5805561.7038 | FALSE | 2220 | 440630 | -448274.7091 | 11344.9021 | 259167.7042 | 270512.6064 | 392665.1432 | -55609.5659 | FALSE | Option 1 | 0 | 774
| CLC003-24613704 | 138 | 2956502.7404 | -1598129.8935 | 4493.4361 | 85820.4229 | 90313.859 | 157.8551 | 3907.9581 | 4065.8133 | 86248.0458 | -1511881.8477 | FALSE | 1886 | 109365 | -111262.4278 | 1759.5412 | 35070.4567 | 36829.9979 | 53483.8611 | -57778.5667 | FALSE | Option 1 | 0 | 774
| CLC003-78545961 | 3 | 64271.7987 | -34741.9542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -34741.9542 | FALSE | 281 | 2377.5 | -2418.7484 | 0 | 0 | 0 | 0 | -2418.7484 | FALSE | Option 1 | 0 | 774
| CLC003-80120806 | 10 | 214239.329 | -115806.514 | 165.687 | 3821.1513 | 3986.8383 | 5.8206 | 174.0017 | 179.8223 | 3807.016 | -111999.498 | FALSE | 409 | 7925 | -8062.4948 | 64.8798 | 1561.5108 | 1626.3906 | 2360.4477 | -5702.0471 | FALSE | Option 1 | 0 | 774
| CLC003-80121007 | 12 | 257087.1948 | -138967.8168 | 5.8904 | 139.7247 | 145.6151 | 0.20693 | 6.3626 | 6.5695 | 139.0456 | -138828.7712 | FALSE | 471 | 9510 | -9674.9937 | 2.3066 | 57.0984 | 59.405 | 86.2101 | -9588.7836 | FALSE | Option 1 | 0 | 774
| CLC003-80919181 | 70 | 1499675.3031 | -810645.5981 | 5193.8834 | 75092.8558 | 80286.7392 | 182.462 | 3419.4627 | 3601.9247 | 76684.8145 | -733960.7836 | FALSE | 1398 | 55475 | -56437.4634 | 2033.8226 | 30686.6438 | 32720.4664 | 47566.2728 | -8871.1906 | FALSE | Option 1 | 0 | 774
| CLC004-176886107 | 21 | 449902.5909 | -243193.6794 | 34.4039 | 211.3138 | 245.7177 | 1.2086 | 9.6225 | 10.8311 | 234.8866 | -242958.7928 | FALSE | 677 | 16642.5 | -16931.239 | 13.4719 | 86.3532 | 99.8251 | 145.8926 | -16785.3464 | FALSE | Option 1 | 0 | 774
| CLC006-142438034 | 76 | 1628218.9005 | -880129.5066 | 159.2712 | 3281.7292 | 3441.0004 | 5.5952 | 149.4383 | 155.0335 | 3285.9669 | -876843.5397 | FALSE | 1543 | 60230 | -61274.9602 | 62.3675 | 1341.0764 | 1403.4439 | 2037.5566 | -59237.4037 | FALSE | Option 1 | 0 | 774
| CLC006-142438492 | 21 | 449902.5909 | -243193.6794 | 1674.4514 | 10091.4296 | 11765.881 | 58.8237 | 459.528 | 518.3517 | 11247.5293 | -231946.1502 | FALSE | 664 | 16642.5 | -16931.239 | 655.6823 | 4123.8557 | 4779.538 | 6986.343 | -9944.896 | FALSE | Option 1 | 0 | 774
| CLC006-144337956 | 80 | 1713914.6321 | -926452.1122 | 3696.2069 | 51512.2065 | 55208.4134 | 129.8483 | 2345.6835 | 2475.5318 | 52732.8816 | -873719.2305 | FALSE | 1538 | 63400 | -64499.9581 | 1447.3619 | 21050.4277 | 22497.7896 | 32710.6238 | -31789.3344 | FALSE | Option 1 | 0 | 774
| CLC006-144337978 | 42 | 899805.1819 | -486387.3589 | 953.9171 | 16289.3806 | 17243.2977 | 33.5113 | 741.7607 | 775.272 | 16468.0257 | -469919.3332 | FALSE | 1050 | 33285 | -33862.478 | 373.5352 | 6656.6442 | 7030.1793 | 10213.1184 | -23649.3597 | FALSE | Option 1 | 0 | 774
| CLC006-154827505 | 25 | 535598.3225 | -289516.2851 | 19.2535 | 195.7393 | 214.9928 | 0.67638 | 8.9133 | 9.5897 | 205.4031 | -289310.8819 | FALSE | 765 | 19812.5 | -20156.2369 | 7.5393 | 79.9887 | 87.528 | 127.4648 | -20028.7721 | FALSE | Option 1 | 0 | 774
| CLC006-154827674 | 21 | 449902.5909 | -243193.6794 | 1233.8301 | 6018.1181 | 7251.9482 | 43.3447 | 274.0438 | 317.3884 | 6934.5598 | -236259.1197 | FALSE | 667 | 16642.5 | -16931.239 | 483.1436 | 2459.2998 | 2942.4434 | 4309.5048 | -12621.7342 | FALSE | Option 1 | 0 | 774
| CLC006-154827847 | 14 | 299935.0606 | -162129.1196 | 269.8461 | 3686.0807 | 3955.9268 | 9.4797 | 167.8511 | 177.3308 | 3778.596 | -158350.5236 | FALSE | 516 | 11095 | -11287.4927 | 105.6664 | 1506.3143 | 1611.9808 | 2343.946 | -8943.5466 | FALSE | Option 1 | 0 | 774
| CLC006-154828072 | 127 | 2720839.4785 | -1470742.7281 | 2013.7445 | 35644.763 | 37658.5075 | 70.7432 | 1623.1363 | 1693.8794 | 35964.628 | -1434778.1 | FALSE | 1856 | 100647.5 | -102393.6835 | 788.5427 | 14566.2078 | 15354.7506 | 22303.7569 | -80089.9267 | FALSE | Option 1 | 0 | 774
| CLC006-154828287 | 65 | 1392555.6386 | -752742.3411 | 1567.2559 | 23666.1028 | 25233.3587 | 55.058 | 1077.6705 | 1132.7285 | 24100.6303 | -728641.7109 | FALSE | 1390 | 51512.5 | -52406.216 | 613.7066 | 9671.1366 | 10284.8432 | 14948.5155 | -37457.7005 | FALSE | Option 1 | 0 | 774
| CLC006-154828396 | 119 | 2549448.0153 | -1378097.5168 | 5426.4641 | 98448.2693 | 103874.7333 | 190.6326 | 4482.9855 | 4673.6181 | 99201.1153 | -1278896.4016 | FALSE | 1796 | 94307.5 | -95943.6877 | 2124.8966 | 40230.8174 | 42355.714 | 61519.0193 | -34424.6684 | FALSE | Option 1 | 0 | 774
| CLC006-154907356 | 24 | 514174.3896 | -277935.6336 | 446.8968 | 5232.862 | 5679.7588 | 15.6996 | 238.286 | 253.9856 | 5425.7732 | -272509.8604 | FALSE | 735 | 19020 | -19349.9874 | 174.996 | 2138.4055 | 2313.4014 | 3366.3573 | -15983.6301 | FALSE | Option 1 | 0 | 774
| CLC006-80819775 | 110 | 2356632.6192 | -1273871.6542 | 9781.4016 | 90502.5237 | 100283.9254 | 343.6222 | 4121.1644 | 4464.7866 | 95819.1387 | -1178052.5155 | FALSE | 1736 | 87175 | -88687.4424 | 3830.2046 | 36983.7939 | 40813.9985 | 59469.9269 | -29217.5156 | FALSE | Option 1 | 0 | 774
| CLC006-80819849 | 105 | 2249512.9547 | -1215968.3972 | 2236.7535 | 23870.886 | 26107.6395 | 78.5775 | 1086.9956 | 1165.5731 | 24942.0664 | -1191026.3308 | FALSE | 1744 | 83212.5 | -84656.1951 | 875.8687 | 9754.8211 | 10630.6898 | 15476.9497 | -69179.2454 | FALSE | Option 1 | 0 | 774
| CLC013-120141536 | 54 | 1156892.3767 | -625355.1757 | 1274.8767 | 29996.8525 | 31271.7292 | 44.7866 | 1365.9504 | 1410.7371 | 29860.9922 | -595494.1835 | FALSE | 1238 | 42795 | -43537.4717 | 499.2167 | 12258.1931 | 12757.4098 | 18514.3195 | -25023.1523 | FALSE | Option 1 | 0 | 774
| CLC013-155048935 | 17 | 364206.8593 | -196871.0738 | 18.8218 | 480.0126 | 498.8345 | 0.66121 | 21.8581 | 22.5193 | 476.3152 | -196394.7587 | FALSE | 579 | 13472.5 | -13706.2411 | 7.3703 | 196.1568 | 203.5271 | 295.3074 | -13410.9337 | FALSE | Option 1 | 0 | 774
| CLC013-155049125 | 36 | 771261.5845 | -416903.4505 | 2095.337 | 42440.9938 | 44536.3308 | 73.6095 | 1932.6126 | 2006.2221 | 42530.1087 | -374373.3417 | FALSE | 917 | 28530 | -29024.9812 | 820.4928 | 17343.4829 | 18163.9756 | 26372.3552 | -2652.626 | FALSE | Option 1 | 0 | 774
| CLC013-155049446 | 31 | 664141.92 | -359000.1935 | 658.6084 | 18381.7106 | 19040.319 | 23.137 | 837.038 | 860.175 | 18180.144 | -340820.0495 | FALSE | 857 | 24567.5 | -24993.7338 | 257.8981 | 7511.6734 | 7769.5715 | 11270.7475 | -13722.9863 | FALSE | Option 1 | 0 | 774
| CLC013-155049582 | 25 | 535598.3225 | -289516.2851 | 233.5493 | 3156.8584 | 3390.4077 | 8.2046 | 143.7522 | 151.9568 | 3238.4509 | -286277.8341 | FALSE | 755 | 19812.5 | -20156.2369 | 91.4533 | 1290.048 | 1381.5013 | 2008.9064 | -18147.3305 | FALSE | Option 1 | 0 | 774
| CLC013-155079387 | 16 | 342782.9264 | -185290.4224 | 58.7689 | 1814.8523 | 1873.6212 | 2.0646 | 82.6419 | 84.7065 | 1788.9147 | -183501.5077 | FALSE | 556 | 12680 | -12899.9916 | 23.0127 | 741.6381 | 764.6509 | 1108.9703 | -11791.0213 | FALSE | Option 1 | 0 | 774
| CLC013-155079659 | 23 | 492750.4567 | -266354.9822 | 582.8989 | 18104.2493 | 18687.1482 | 20.4773 | 824.4034 | 844.8807 | 17842.2675 | -248512.7147 | FALSE | 690 | 18227.5 | -18543.738 | 228.2518 | 7398.289 | 7626.5408 | 11060.6075 | -7483.1305 | FALSE | Option 1 | 0 | 774
| CLC013-24598538 | 68 | 1456827.4373 | -787484.2953 | 1628.9419 | 28223.0956 | 29852.0375 | 57.225 | 1285.1798 | 1342.4048 | 28509.6327 | -758974.6626 | FALSE | 1429 | 53890 | -54824.9644 | 637.8616 | 11533.3486 | 12171.2102 | 17680.8273 | -37144.1371 | FALSE | Option 1 | 0 | 774
| CLC013-24598566 | 64 | 1371131.7057 | -741161.6897 | 3451.9594 | 62151.1328 | 65603.0922 | 121.2679 | 2830.1425 | 2951.4104 | 62651.6818 | -678510.0079 | FALSE | 1340 | 50720 | -51599.9665 | 1351.7194 | 25398.0176 | 26749.737 | 38853.3552 | -12746.6113 | FALSE | Option 1 | 0 | 774
| CLC013-24602770 | 220 | 4713265.2384 | -2547743.3085 | 109059.4309 | 107934.6091 | 216994.0399 | 3831.2754 | 4914.9598 | 8746.2352 | 208247.8047 | -2339495.5038 | FALSE | 2058 | 174350 | -177374.8849 | 42705.5289 | 44107.4036 | 86812.9324 | 130181.1075 | -47193.7774 | FALSE | Option 1 | 0 | 774
| CLC013-77737876 | 21 | 449902.5909 | -243193.6794 | 34.0192 | 689.0387 | 723.058 | 1.1951 | 31.3764 | 32.5715 | 690.4865 | -242503.193 | FALSE | 673 | 16642.5 | -16931.239 | 13.3213 | 281.5752 | 294.8965 | 428.1615 | -16503.0775 | FALSE | Option 1 | 0 | 774
| CLC013-77738225 | 12 | 257087.1948 | -138967.8168 | 2.7161 | 146.6847 | 149.4007 | 0.095417 | 6.6795 | 6.7749 | 142.6258 | -138825.191 | FALSE | 470 | 9510 | -9674.9937 | 1.0636 | 59.9426 | 61.0061 | 88.3946 | -9586.5991 | FALSE | Option 1 | 0 | 774
| CLC014-119350337 | 56 | 1199740.2425 | -648516.4785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -648516.4785 | FALSE | 1293 | 44380 | -45149.9707 | 0 | 0 | 0 | 0 | -45149.9707 | FALSE | Option 1 | 0 | 774
| CME014-15423823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| CME014-24612269 | 41 | 878381.249 | -474806.7075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -474806.7075 | FALSE | 1061 | 32492.5 | -33056.2285 | 0 | 0 | 0 | 0 | -33056.2285 | FALSE | Option 1 | 0 | 774
| CME016-142932211 | 1 | 21423.9329 | -11580.6514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11580.6514 | FALSE | 234 | 792.5 | -806.2495 | 0 | 0 | 0 | 0 | -806.2495 | FALSE | Option 1 | 0 | 774
| CME016-142932557 | 49 | 1049772.7122 | -567451.9187 | 1271.607 | 34557.4361 | 35829.0431 | 44.6718 | 1214.0083 | 1258.6801 | 34570.3631 | -532881.5556 | FALSE | 1153 | 38832.5 | -39506.2244 | 497.9363 | 13532.0125 | 14029.9488 | 21799.0943 | -17707.1301 | FALSE | Option 1 | 0 | 774
| CME016-142932825 | 88 | 1885306.0953 | -1019097.3234 | 871.606 | 39510.8606 | 40382.4666 | 30.6197 | 1388.0229 | 1418.6426 | 38963.8241 | -980133.4993 | FALSE | 1609 | 69740 | -70949.954 | 341.3038 | 15471.6762 | 15812.9799 | 24569.4867 | -46380.4673 | FALSE | Option 1 | 0 | 774
| CME016-142933135 | 48 | 1028348.7793 | -555871.2673 | 2143.8224 | 42389.5954 | 44533.4177 | 75.3128 | 1489.1533 | 1564.4661 | 42968.9516 | -512902.3157 | FALSE | 1114 | 38040 | -38699.9749 | 839.4787 | 16598.9321 | 17438.4108 | 27095.007 | -11604.9679 | FALSE | Option 1 | 0 | 774
| CME016-163066872 | 79 | 1692490.6992 | -914871.4608 | 32.2122 | 764.024 | 796.2362 | 1.1316 | 26.8403 | 27.9719 | 768.2643 | -914103.1965 | FALSE | 1571 | 62607.5 | -63693.7087 | 12.6137 | 299.1768 | 311.7904 | 484.4458 | -63209.2629 | FALSE | Option 1 | 0 | 774
| CME016-171344649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| CME016-24605950 | 49 | 1049772.7122 | -567451.9187 | 1400.6698 | 718.033 | 2118.7029 | 49.2058 | 25.2246 | 74.4304 | 2044.2725 | -565407.6462 | FALSE | 1196 | 38832.5 | -39506.2244 | 548.4748 | 281.1676 | 829.6424 | 1289.0605 | -38217.1639 | FALSE | Option 1 | 0 | 774
| CME016-68675557 | 28 | 599870.1212 | -324258.2393 | 19395.4883 | 4696.596 | 24092.0842 | 681.3666 | 164.9922 | 846.3588 | 23245.7254 | -301012.5138 | FALSE | 790 | 22190 | -22574.9853 | 7594.8919 | 1839.0946 | 9433.9865 | 14658.0977 | -7916.8876 | FALSE | Option 1 | 0 | 774
| CME021-15423551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| CME022-15423527 | 41 | 878381.249 | -474806.7075 | 9435.7225 | 1946.6388 | 11382.3614 | 331.4785 | 68.3857 | 399.8642 | 10982.4972 | -463824.2103 | FALSE | 1044 | 32492.5 | -33056.2285 | 3694.8434 | 762.2655 | 4457.1089 | 6925.2525 | -26130.9761 | FALSE | Option 1 | 0 | 774
| CMN001-73767965 | 62 | 1328283.8399 | -718000.3869 | 1220.1502 | 79795.3226 | 81015.4728 | 42.8641 | 2803.2226 | 2846.0866 | 78169.3862 | -639831.0008 | FALSE | 1286 | 49135 | -49987.4676 | 477.7868 | 31246.2794 | 31724.0663 | 49291.4065 | -696.061 | FALSE | Option 1 | 0 | 774
| CMN001-73948442 | 11 | 235663.2619 | -127387.1654 | 152.5397 | 5425.9367 | 5578.4765 | 5.3587 | 190.614 | 195.9728 | 5382.5037 | -122004.6617 | FALSE | 435 | 8717.5 | -8868.7442 | 59.7316 | 2124.6901 | 2184.4217 | 3394.0548 | -5474.6895 | FALSE | Option 1 | 0 | 774
| CMN001-74644428 | 31 | 664141.92 | -359000.1935 | 460.187 | 26949.2161 | 27409.4031 | 16.1664 | 946.7303 | 962.8968 | 26446.5063 | -332553.6871 | FALSE | 842 | 24567.5 | -24993.7338 | 180.2002 | 10552.7832 | 10732.9833 | 16676.4198 | -8317.314 | FALSE | Option 1 | 0 | 774
| CMN002-138133472 | 31 | 664141.92 | -359000.1935 | 1257.6059 | 36253.3962 | 37511.002 | 44.1799 | 1273.5877 | 1317.7676 | 36193.2345 | -322806.959 | FALSE | 819 | 24567.5 | -24993.7338 | 492.4537 | 14196.1172 | 14688.5709 | 22822.4312 | -2171.3026 | FALSE | Option 1 | 0 | 774
| CMN002-15420523 | 1 | 21423.9329 | -11580.6514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11580.6514 | FALSE | 234 | 792.5 | -806.2495 | 0 | 0 | 0 | 0 | -806.2495 | FALSE | Option 1 | 0 | 774
| CMN002-87920200 | 21 | 449902.5909 | -243193.6794 | 1340.0443 | 19121.8703 | 20461.9146 | 47.076 | 671.7544 | 718.8304 | 19743.0842 | -223450.5952 | FALSE | 646 | 16642.5 | -16931.239 | 524.735 | 7487.7484 | 8012.4834 | 12449.4312 | -4481.8079 | FALSE | Option 1 | 0 | 774
| CMN003-15420636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| CMN003-75645317 | 9 | 192815.3961 | -104225.8626 | 313.3934 | 4492.6471 | 4806.0405 | 11.0096 | 157.8274 | 168.837 | 4637.2035 | -99588.6591 | FALSE | 382 | 7132.5 | -7256.2453 | 122.7187 | 1759.2323 | 1881.951 | 2924.0895 | -4332.1558 | FALSE | Option 1 | 0 | 774
| CMN003-75645537 | 19 | 407054.7251 | -220032.3766 | 411.1352 | 8295.6815 | 8706.8167 | 14.4432 | 291.4286 | 305.8719 | 8400.9448 | -211631.4319 | FALSE | 614 | 15057.5 | -15318.7401 | 160.9925 | 3248.4258 | 3409.4182 | 5297.3984 | -10021.3416 | FALSE | Option 1 | 0 | 774
| CMN003-76447226 | 35 | 749837.6516 | -405322.7991 | 600.1265 | 20916.8714 | 21516.9979 | 21.0825 | 734.8131 | 755.8956 | 20761.1023 | -384561.6968 | FALSE | 936 | 27737.5 | -28218.7317 | 234.9977 | 8190.6356 | 8425.6333 | 13091.3646 | -15127.3671 | FALSE | Option 1 | 0 | 774
| CMN004-74052344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| COB011-15431802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| COB011-162571445 | 5 | 107119.6645 | -57903.257 | 1.9116 | 7.9976 | 9.9092 | 0.067155 | 0.36418 | 0.43134 | 9.4778 | -57893.7792 | FALSE | 309 | 3962.5 | -4031.2474 | 0.74854 | 3.2682 | 4.0167 | 5.8924 | -4025.355 | FALSE | Option 1 | 0 | 774
| COB011-162571831 | 3 | 64271.7987 | -34741.9542 | 0.045399 | 0.68384 | 0.72924 | 0.0015949 | 0.03114 | 0.032735 | 0.69651 | -34741.2577 | FALSE | 277 | 2377.5 | -2418.7484 | 0.017777 | 0.27945 | 0.29723 | 0.43201 | -2418.3164 | FALSE | Option 1 | 0 | 774
| COB011-162572039 | 7 | 149967.5303 | -81064.5598 | 52.3133 | 459.421 | 511.7343 | 1.8378 | 20.9204 | 22.7582 | 488.9761 | -80575.5837 | FALSE | 350 | 5547.5 | -5643.7463 | 20.4849 | 187.7421 | 208.2269 | 303.5073 | -5340.239 | FALSE | Option 1 | 0 | 774
| COB011-162572240 | 20 | 428478.658 | -231613.028 | 44.1433 | 443.2682 | 487.4115 | 1.5508 | 20.1849 | 21.7356 | 465.6759 | -231147.3522 | FALSE | 658 | 15850 | -16124.9895 | 17.2857 | 181.1412 | 198.4269 | 288.9846 | -15836.0049 | FALSE | Option 1 | 0 | 774
| COB011-162572975 | 11 | 235663.2619 | -127387.1654 | 0.67611 | 4.1504 | 4.8265 | 0.023752 | 0.189 | 0.21275 | 4.6138 | -127382.5516 | FALSE | 453 | 8717.5 | -8868.7442 | 0.26475 | 1.6961 | 1.9608 | 2.8657 | -8865.8785 | FALSE | Option 1 | 0 | 774
| COB011-162661437 | 11 | 235663.2619 | -127387.1654 | 33.27 | 183.7371 | 217.0071 | 1.1688 | 8.3667 | 9.5355 | 207.4716 | -127179.6938 | FALSE | 448 | 8717.5 | -8868.7442 | 13.0279 | 75.084 | 88.1119 | 128.8952 | -8739.8491 | FALSE | Option 1 | 0 | 774
| COB011-162661589 | 49 | 1049772.7122 | -567451.9187 | 1088.6931 | 11644.8424 | 12733.5355 | 38.246 | 530.2649 | 568.5108 | 12165.0247 | -555286.894 | FALSE | 1184 | 38832.5 | -39506.2244 | 426.3108 | 4758.6568 | 5184.9676 | 7548.5679 | -31957.6565 | FALSE | Option 1 | 0 | 774
| COB011-162661811 | 25 | 535598.3225 | -289516.2851 | 4.3902 | 26.2476 | 30.6378 | 0.15423 | 1.1952 | 1.3494 | 29.2883 | -289486.9967 | FALSE | 768 | 19812.5 | -20156.2369 | 1.7191 | 10.726 | 12.4452 | 18.1926 | -20138.0443 | FALSE | Option 1 | 0 | 774
| COB011-162798633 | 17 | 364206.8593 | -196871.0738 | 168.6719 | 2878.4817 | 3047.1536 | 5.9255 | 131.0759 | 137.0013 | 2910.1523 | -193960.9215 | FALSE | 575 | 13472.5 | -13706.2411 | 66.0486 | 1176.2896 | 1242.3382 | 1804.8155 | -11901.4256 | FALSE | Option 1 | 0 | 774
| COB011-163103340 | 15 | 321358.9935 | -173709.771 | 305.1624 | 1531.9541 | 1837.1165 | 10.7204 | 69.7598 | 80.4802 | 1756.6363 | -171953.1347 | FALSE | 534 | 11887.5 | -12093.7422 | 119.4956 | 626.032 | 745.5276 | 1091.5889 | -11002.1532 | FALSE | Option 1 | 0 | 774
| COB011-164044294 | 1 | 21423.9329 | -11580.6514 | 0 | 0.2655 | 0.2655 | 0 | 0.01209 | 0.01209 | 0.25341 | -11580.398 | FALSE | 231 | 792.5 | -806.2495 | 0 | 0.1085 | 0.1085 | 0.15701 | -806.0925 | FALSE | Option 1 | 0 | 774
| COB011-201141604 | 77 | 1649642.8334 | -891710.158 | 12904.811 | 18492.764 | 31397.575 | 453.3481 | 842.095 | 1295.4431 | 30102.132 | -861608.026 | FALSE | 1525 | 61022.5 | -62081.2097 | 5053.2703 | 7557.0553 | 12610.3255 | 18787.2495 | -43293.9602 | FALSE | Option 1 | 0 | 774
| COB011-202349052 | 341 | 7305561.1195 | -3949002.1281 | 43444.5152 | 255279.3515 | 298723.8667 | 1526.2128 | 11624.5176 | 13150.7304 | 285573.1363 | -3663428.9918 | FALSE | 2175 | 270242.5 | -274931.0716 | 17012.018 | 104319.731 | 121331.749 | 177392.1177 | -97538.9538 | FALSE | Option 1 | 0 | 774
| COB012-15431852 | 87 | 1863882.1624 | -1007516.672 | 5337.7747 | 15893.3842 | 21231.1589 | 187.5169 | 723.7284 | 911.2453 | 20319.9136 | -987196.7584 | FALSE | 1612 | 68947.5 | -70143.7045 | 2090.1676 | 6494.8205 | 8584.9881 | 12646.1708 | -57497.5337 | FALSE | Option 1 | 0 | 774
| COB021-15436290 | 169 | 3620644.6604 | -1957130.0869 | 59857.3256 | 89226.9672 | 149084.2928 | 2102.7975 | 4063.0801 | 6165.8776 | 142918.4152 | -1814211.6717 | FALSE | 1965 | 133932.5 | -136256.1616 | 23438.9518 | 36462.5386 | 59901.4905 | 89182.8023 | -47073.3592 | FALSE | Option 1 | 0 | 774
| COB021-24613718 | 6 | 128543.5974 | -69483.9084 | 0 | 0.72582 | 0.72582 | 0 | 0.033051 | 0.033051 | 0.69277 | -69483.2156 | FALSE | 330 | 4755 | -4837.4969 | 0 | 0.29661 | 0.29661 | 0.42921 | -4837.0676 | FALSE | Option 1 | 0 | 774
| COB022-160576265 | 16 | 342782.9264 | -185290.4224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -185290.4224 | FALSE | 566 | 12680 | -12899.9916 | 0 | 0 | 0 | 0 | -12899.9916 | FALSE | Option 1 | 0 | 774
| CRO013-15404871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| CRO013-15404884 | 226 | 4841808.8358 | -2617227.2169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2617227.2169 | FALSE | 2091 | 179105 | -182212.3817 | 0 | 0 | 0 | 0 | -182212.3817 | FALSE | Option 1 | 0 | 774
| CRO014-15404821 | 30 | 642717.987 | -347419.5421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -347419.5421 | FALSE | 868 | 23775 | -24187.4843 | 0 | 0 | 0 | 0 | -24187.4843 | FALSE | Option 1 | 0 | 774
| CRO021-153844129 | 63 | 1349707.7728 | -729581.0383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -729581.0383 | FALSE | 1393 | 49927.5 | -50793.717 | 0 | 0 | 0 | 0 | -50793.717 | FALSE | Option 1 | 0 | 774
| CRO021-15404447 | 134 | 2870807.0088 | -1551807.2879 | 19346.9694 | 18203.2409 | 37550.2103 | 679.6622 | 828.9111 | 1508.5733 | 36041.637 | -1515765.6509 | FALSE | 1887 | 106195 | -108037.4299 | 7575.8928 | 7438.7418 | 15014.6347 | 22535.5756 | -85501.8543 | FALSE | Option 1 | 0 | 774
| CRO022-15404471 | 127 | 2720839.4785 | -1470742.7281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1470742.7281 | FALSE | 1871 | 100647.5 | -102393.6835 | 0 | 0 | 0 | 0 | -102393.6835 | FALSE | Option 1 | 0 | 774
| CRO022-24612421 | 91 | 1949577.894 | -1053839.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1053839.2776 | FALSE | 1659 | 72117.5 | -73368.7024 | 0 | 0 | 0 | 0 | -73368.7024 | FALSE | Option 1 | 0 | 774
| CRO023-15404521 | 98 | 2099545.4244 | -1134903.8374 | 121.1374 | 423.4295 | 544.5669 | 4.2556 | 19.2815 | 23.5371 | 521.0299 | -1134382.8075 | FALSE | 1705 | 77665 | -79012.4487 | 47.435 | 173.0342 | 220.4692 | 324.0977 | -78688.351 | FALSE | Option 1 | 0 | 774
| CRO031-15404634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | Option 1 | 0 | 774
| CRO031-15404660 | 23 | 492750.4567 | -266354.9822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -266354.9822 | FALSE | 727 | 18227.5 | -18543.738 | 0 | 0 | 0 | 0 | -18543.738 | FALSE | Option 1 | 0 | 774
| CRO032-15404697 | 40 | 856957.3161 | -463226.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -463226.0561 | FALSE | 1042 | 31700 | -32249.9791 | 0 | 0 | 0 | 0 | -32249.9791 | FALSE | Option 1 | 0 | 774
| CRO034-15404810 | 195 | 4177666.9158 | -2258227.0234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2258227.0234 | FALSE | 2041 | 154537.5 | -157218.648 | 0 | 0 | 0 | 0 | -157218.648 | FALSE | Option 1 | 0 | 774
| CTN001-155143905 | 4 | 85695.7316 | -46322.6056 | 21.4449 | 21.6314 | 43.0763 | 0.75336 | 0.75991 | 1.5133 | 41.563 | -46281.0426 | FALSE | 288 | 3170 | -3224.9979 | 8.3974 | 8.4704 | 16.8678 | 26.2085 | -3198.7895 | FALSE | Option 1 | 0 | 774
| CTN001-155145203 | 11 | 235663.2619 | -127387.1654 | 262.2926 | 6731.8046 | 6994.0972 | 9.2144 | 236.4894 | 245.7038 | 6748.3934 | -120638.772 | FALSE | 432 | 8717.5 | -8868.7442 | 102.7086 | 2636.0423 | 2738.751 | 4255.3463 | -4613.398 | FALSE | Option 1 | 0 | 774
| CTN001-155179699 | 26 | 557022.2554 | -301096.9365 | 260.7716 | 9039.0673 | 9299.8389 | 9.1609 | 317.5439 | 326.7048 | 8973.1341 | -292123.8024 | FALSE | 775 | 20605 | -20962.4864 | 102.113 | 3539.521 | 3641.6341 | 5658.2049 | -15304.2815 | FALSE | Option 1 | 0 | 774
| CTN001-155179789 | 31 | 664141.92 | -359000.1935 | 537.7768 | 14143.8004 | 14681.5772 | 18.8922 | 496.874 | 515.7662 | 14165.811 | -344834.3825 | FALSE | 864 | 24567.5 | -24993.7338 | 210.5828 | 5538.4341 | 5749.017 | 8932.5602 | -16061.1736 | FALSE | Option 1 | 0 | 774